## Instructions
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2
Latest Template Revision: | 2015-08-24
Tab Name: | Instructions
File Name: | Walk-In Panels - v1.2.xlsx
Reference Test Procedure
10 CFR Part 431 Subpart R 431.304: Uniform test method for the measurement of energy consumption of walk-in coolers and walk-in freezers [74 FR 12074, Mar. 23, 2009, as amended at 76 FR 21605, Apr. 15, 2011; 76 FR 33631, June 9, 2011; 76 FR 65365, Oct. 21, 2011; 79 FR 27412, May 13, 2014; 79 FR 32123, June 3, 2014]
Table of Contents
Tab | Contents
Instructions | Instructions and table of contents
General Info & Test Results | Lab information, product information and test results
Setup & Instrumentation | Instrumentation requirements and space for sensor placement descriptions
Test Conditions | Input for test condition measurements
Photos | Inputs for photographs
Raw Data | Input for raw data
Test Data Inputs & Calculations | Measurement inputs and automated calculations
Comments | Inputs for report template user to provide comments
Report Sign-Off Block | Report review history
Drop Downs | Drop-downs used
Version Control | Revision history
LEGEND
Tabs | Tabs with input cells
Tabs with space to paste raw data
Cells | Input cell
Auto-populated cell
Provided data
NOT USED
Instructions for Completing this Template
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THIS TAB:
Step 1 | General Info & Test Results
Step 2 | Setup & Instrumentation
Step 3 | Test Conditions
Step 4 | Photos
Step 5 | Raw Data
Step 6 | Test Data Inputs & Calculations
Step 7 | Comments
Step 8 | Report Sign-off Block

## General Info & Test Results
Title Block |  | Back to Instructions tab
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2
Latest Template Revision: | 2015-08-24
Tab Name: | General Info & Test Results
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Lab Information |  | Test results
Lab Name: |  | Variable | Result | Units
Lab Location: |  | Thermal Resistance- Freezer |  | (Hr-ft2-⁰F)/Btu
|  | Thermal Resistance- Cooler |  | (Hr-ft2-⁰F)/Btu
Test Information
Date Test Started: | [MM/DD/YYYY]
Date Test Finished: | [MM/DD/YYYY]
NOTE: This is only a copy; sign off is done in the Report Sign-Off Block tab
Product Information |  | Test Report Sign-Off Block
Brand: |  | We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Manufacturer:
Manufacturer model number:
Serial number: |  | Role |  | Date | Entity
Date of Manufacture (if available): |  | Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Date Product Received: | [MM/DD/YYYY] | Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Condition as received: |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Original Sample Dimensions (in) |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Height
Width
Depth

## Setup & Instrumentation
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2015-08-24
Tab Name: | Setup & Instrumentation
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Setup (This table should include a description of the sample used for calibration)
Sample Name | Material Type | Thickness | Thermal Conductance (Btu/Hr-ft²-°F) | Min Calibration Temp (°F) | Max Calibration Temp (°F) | Additonal Notes:
Setup (This table should include a description of the test sample preparation)
Parallelism Variance (inches) | Flatness Variance (inches) | Time Sample Facers were removed | Time test was started
Tolerance check (+/-0.03 in.) | Tolerance check (+/-0.03 in.)
Setup (This table should include instrumentation, sensors, and all equipment used during testing)
Instrument Type | Brand | Model # | Sensor Location | Accuracy | Date of Last Calibration | Deadline for Next Calibration

## Test Conditions
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2 |  |  | Back to Instructions tab
Latest Template Revision: | 2015-08-24
Tab Name: | Test Conditions
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Proper Foam Sample Thickness
| Measurement | Units
Original Foam Thickness |  | in.
Tested Foam Thickness |  | in.
Condition Met? |  | -
Proper Mean Temperature in Foam Sample
Paragraph (c) subparagraphs (3) and (4)
| Heat Flux Transducer plate Temperatures | [5 empty] | Units
| Freezer Conditions Test |  |  | Cooler Conditions Test
| Cold Plate | Hot Plate | Mean Temperature | Cold Plate | Hot Plate | Mean Temperature
Plate Temperatures | [6 empty] | °F
Condition Met? | [6 empty] | -

## Photos
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2 | Back to Instructions tab
Latest Template Revision: | 2015-08-24
Tab Name: | Photos
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
1. Nameplate showing model number and serial number (if applicable) |  |  | 2. FTC EnergyGuide label (if present)
3. Photos of test unit from all sides (including photo of control panel, if applicable)
4. Exact placement of all sensors on, in, or around the device
5. Additional photos (if necessary)

## Raw Data
Title Block |  |  | Input raw data into this tab.
Test Report Template Name: | Walk-In Panels | Back to Instructions tab | Include the following as a function of time for the duration of the test. Please indicate the units of each measure.
Version Number: | v1.2 |  | • Measured thickness
Latest Template Revision: | 2015-08-24 |  | • Upper plate temperature
Tab Name: | Raw Data |  | • Lower plate temperature
File Name: | Walk-In Panels - v1.2.xlsx |  | • Mean temperature
Test Completion Date: | [MM/DD/YYYY] |  | • Plate temperature difference
• Upper plate heat flux
• Lower plate heat flux
• K-value

## Test Data Inputs & Calculations
Title Block
Test Report Template Name: |  | Walk-In Panels
Version Number: |  | v1.2 |  | Back to Instructions tab
Latest Template Revision: |  | 2015-08-24
Tab Name: |  | Test Data Inputs & Calculations
File Name: |  | Walk-In Panels - v1.2.xlsx
Test Completion Date: |  | [MM/DD/YYYY]
Test Data Inputs
Heat Flux Transducer Calibration
|  |  | Measurement | Unit
| Heat Flux Transducer Output during calibration- Warm Plate |  |  | V
| Heat Flux Transducer Output during calibration- Cold Plate |  |  | V
| Total Heat Flux Transducer Output during calibration (Ec) |  | 0 | V
| Known Thermal Conductance of calibration sample (Cc) |  |  | (Btu/Hr-ft²-°F)
| Temperature Difference during calibration (∆Tc) |  |  | °F
Main Test- Freezers
|  |  | Measurement | Unit
| Heat Flux Transducer Output- Warm Plate |  |  | V
| Heat Flux Transducer Output- Cold Plate |  |  | V
| Total Heat Flux Transducer Output (E) |  | 0 | V
| Separation between the hot and cold plate assemblies during testing (L) |  |  | in.
| Temperature Difference (∆T) |  |  | °F
Main Test- Coolers
|  |  | Measurement | Unit
| Heat Flux Transducer Output- Warm Plate |  |  | V
| Heat Flux Transducer Output- Cold Plate |  |  | V
| Total Heat Flux Transducer Output (E) |  | 0 | V
| Separation between the hot and cold plate assemblies during testing (L) |  |  | in.
| Temperature Difference (∆T) |  |  | °F
Notes/Comments: (Please clarify any pertinent details, unusual events, etc.)
Calculations
R Value- Freezer
|  |  | Calculated Result (unrounded) | Unit | Calculated Result (rounded per significant figures conventions and instrumentation resolution) | Unit
| Calibration Factor (S) |  | #DIV/0! | Btu/(Hr-ft²-V)
| Thermal Conductivity (λ) |  | #DIV/0! | (Btu-in)/(Hr-ft²-°F)
| Thermal Resistance (R) |  | #DIV/0! | (Hr-ft²-°F)/Btu |  | (Hr-ft²-⁰F)/Btu
R Value- Cooler
|  |  | Calculated Result (unrounded) | Unit | Calculated Result (rounded per significant figures conventions and instrumentation resolution) | Unit
| Calibration Factor (S) |  | #DIV/0! | Btu/(Hr-ft²-V)
| Thermal Conductivity (λ) |  | #DIV/0! | (Btu-in)/(Hr-ft²-°F)
| Thermal Resistance (R) |  | #DIV/0! | (Hr-ft²-°F)/Btu |  | (Hr-ft²-°F)/Btu

## Comments
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2 | Back to Instructions tab
Latest Template Revision: | 2015-08-24
Tab Name: | Comments
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Comments

## Report Sign-Off Block
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2 |  | Back to Instructions tab
Latest Template Revision: | 2015-08-24
Tab Name: | Report Sign-Off Block
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]

## Drop-Downs
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2
Latest Template Revision: | 2015-08-24
Tab Name: | Drop-Downs
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
DD_Y_N
Yes
No

## Version Control
Title Block
Test Report Template Name: | Walk-In Panels
Version Number: | v1.2
Latest Template Revision: | 2015-08-24
Tab Name: | Version Control
File Name: | Walk-In Panels - v1.2.xlsx
Test Completion Date: | [MM/DD/YYYY]
Revisions List
Version | Date
v1.0_draft1 | 2014-02-21
v1.0_draft2 | 2014-02-24
v1.0_draft3 | 2014-02-24
v1.0_draft4 | 2014-02-25
v1.0_draft5 | 2014-02-26
v1.0_draft6 | 2014-02-27
v1.0_draft7 | 2014-07-29
v1.0 | 2015-03-06
v1.1_draft1 | 2015-03-24
v1.1_draft2 | 2015-06-05
v1.2 | 2015-08-24