WELDING, CUTTING AND BRAZING

Assessment Plan

NNSA/Nevada Site Office Facility Representative Division

Performance Objective:

This assessment is to verify hot work requirements associated with welding, cutting, burning, brazing, grinding and other spark- or flame-producing operations have been implemented.   Verify that the requirements implemented are appropriate for preventing loss of life and property from fire, and personal injury from contact with or exposure to molten metals, vapors, radiant energy, injurious rays and sparks.

Criteria:

Establish designated area in which routine and repetitive welding, cutting, and other spark- or flame producing operations are conducted  [1910.252(a)(2)(iv),1910.252(a)(2)(vi)(A), 1910.252(a)(2)(xv), General Requirements].

Suitable fire extinguisher equipment shall be maintained in a state of readiness and shall be

accessible for instant use; [1926.352 and 1910.252(a)(2)(ii), General Requirements]

A fire watch is required whenever spark- or flame producing operations are performed in locations where other than a minor fire might develop.  [1910.252(a)(2)(iii)(A), General Requirements].

Shielding shall be in place to protect personnel in the general vicinity from bright light rays or exposure to flames and sparks [1926.351, shielding and 1910.252(a)(1)(ii), General Requirements], and

The required personal protective equipment shall be available and used [1910.252(b)(3), General Requirements].

References:

Code of Federal Regulations, 1910 Subpart Q, Welding, Cutting, and Brazing.

Code of Federal Regulations, 1926.252, General requirements..

Code of Federal Regulations, 1926.253, Oxygen-fuel gas welding and cutting

Code of Federal Regulations, 1926.254, Arc welding and cutting.

Code of Federal Regulations, 1926 Subpart J, Welding and Cutting.

Code of Federal Regulations, 1926.350, Gas welding and cutting.

Code of Federal Regulations, 1926.351, Arc welding and cutting.

Code of Federal Regulations, 1926.352, Fire prevention.

Code of Federal Regulations, 1926.353, Ventilation and protection in welding, cutting, and heating.

Code of Federal Regulations, 1926.354, Welding, cutting, and heating in way of preservative coatings.

American Welding Society, “Recommended Safe Practices for the Preparation for Welding and Cutting of Containers That Have Held Hazardous Substances,” AWS F-4.1 (most recent edition)

National Fire Protection Association, “Standard for Fire Prevention in Use of Cutting and Welding

Processes,” NFPA 51B (most recent edition)

American National Standards Institute, “Safety in Welding, Cutting, and Allied Processes, ANSI Z49.1

(most recent edition)

Code of Federal Regulations, “Welding, Cutting, and Brazing,” 29 CFR 1910.252, Subpart Q, OSHA

(most recent edition)

Code of Federal Regulations, “Fire Protection,” 29 CFR 1926.150 (most recent edition)

Code of Federal Regulations, “Fire Prevention,” 29 CFR 1926.151 (most recent edition)

Code of Federal Regulations, “Fire Prevention,” 29 CFR 1926.352 (most recent edition)

U.S. Department of Energy, June 1997, “Fire Prevention Measures for Cutting, Welding, and Related

Activities, “DOE/EH-0196, Issue No. 97-3 (Issue No. 91-3 revised)

Approach:

Document Review:

Interviews:

Facility Manager / Supervisors

Operators / Maintenance personnel

Observations

Welding, Cutting and Brazing

Lines of Inquiry

NNSA/Nevada Site Office/Facility Representative Division

|  | YES | NO | N/A | COMMENTS |
| --- | --- | --- | --- | --- |
| 1. Are only authorized and trained personnel permitted to use welding, cutting or brazing equipment [1910.253(a)(4), Oxygen-fuel gas welding and cutting]? |  |  |  |  |
| 2. Does each operator have a copy of the appropriate operating instructions and are they directed to follow them [1910.2539a)(4), Oxygen-fuel gas welding and cutting]? |  |  |  |  |
| 3. Are compressed gas cylinders regularly examined for obvious signs of defects, deep rusting, or leakage [1926.350(c)(3), Gas Cutting and Welding]? |  |  |  |  |
| 4. Is care used in handling and storage of cylinders, safety valves, relief valves, etc., to prevent damage [1910.253(b)(5)(iii)(B), Oxygen-fuel gas welding and cutting]? |  |  |  |  |
| 5. Are precautions taken to prevent the mixture of air or oxygen with flammable gases, except at a burner or in a standard torch (1926.350, Treatment of Cylinders)? |  |  |  |  |
| 6. Are only approved apparatus (torches, regulators, pressure-reducing valves, acetylene generators, manifolds) used [1910.253(a)(3), Oxygen-fuel gas welding and cutting]? |  |  |  |  |
| 7. Are cylinders kept away from sources of heat [1926.350, Placing Cylinders, and 1926.350(b)(3), Gas Welding and Cutting]? |  |  |  |  |
| 8. Are the cylinders kept away from elevators, stairs, or gangways (1926.350, Transporting, Moving and Storing Compressed Gas Cylinders)? |  |  |  |  |
| 9. Is it prohibited to use cylinders as rollers or supports (1926.350, Treatment of Cylinders)? |  |  |  |  |
| 10. Are empty cylinders appropriately marked and their valves closed (1926.350, Transporting, Moving and Storing Compressed Gas Cylinders)? |  |  |  |  |
|  | YES | NO | N/A | COMMENTS |
| 11. Are postings placed near cylinders having leaking fuse plugs or other leaking safety devices so as not to approach them with a source of ignition [1910.253(b)(5)(iii)(G), Oxygen-fuel gas welding and cutting]? |  |  |  |  |
| 12. Are cylinders, cylinder valves, couplings, regulators, hoses, and apparatus kept free of oily or greasy substances [1926.350, Oil and Grease Hazards and 1926.350(i), Inert-Gas/Metal-Arc Welding]? |  |  |  |  |
| 13. Is care taken not to drop or strike cylinders [1926.350(a)(3), Inert-Gas/Metal-Arc Welding]? |  |  |  |  |
| 14. Unless secured on special trucks, are regulators removed and valve-protection caps put in place before moving cylinders [1926.350(a)(6), Gas Welding and Cutting]? |  |  |  |  |
| 15. Are liquefied gases stored and shipped valve-end up with valve covers in place [1926.350(a)(1), 1926.350(a)(4), 1926.350(a)(9), Gas Welding and Cutting]? |  |  |  |  |
| 16. Are provisions made to never crack a fuel-gas cylinder valve near sources of ignition [1926.350(b)(1), Gas Welding and Cutting]? |  |  |  |  |
| 17. Before a regulator is removed, is the valve closed and gas released from the regulator [1926.350(d)(4), Gas Welding and Cutting]? |  |  |  |  |
| 18. Is the fuel gas hose and oxygen gas hose easily distinguishable from each other, either by colors or by surface characteristics through the sense of touch [1926.350(f)(1), Gas Welding and Cutting]? |  |  |  |  |
| 19. Are gauges and pressure-reducing regulators in prime working order while in use [1926.350(h), Gas Welding and Cutting]? |  |  |  |  |
| 20. On arc welding equipment are there cables that are worn or in need of repair [1926.351(b)(4), Arc welding and Cutting]? |  |  |  |  |
| 21. In arc welding are the ground connections periodically inspected to ensure that they are mechanically strong and electrically adequate [1926.351, Arc Welding and Cutting]? |  |  |  |  |
|  | YES | NO | N/A | COMMENTS |
| 22. Are electrodes removed from the holders when not in use [1910.252(b)(4)(v), General Requirements and 1926.351, Arc Welding and Cutting]? |  |  |  |  |
| 23. Is it required that electric power to the welder be shut off when no one is in attendance [1910.252(b)(4)(v), General Requirements and 1926.351, Arc Welding and Cutting]? |  |  |  |  |
| 24. Is suitable fire extinguishing equipment available for immediate use [1910.252(a)(2)(ii), General Requirements]? |  |  |  |  |
| 25. Are work and electrode lead cables frequently inspected for wear and damage, and replaced when needed [1926.351, Arc Welding and Cutting? |  |  |  |  |
| 26. Do means for connecting cable lengths have adequate insulation [1926.351, Arc Welding and Cutting]? |  |  |  |  |
| 27. When the object to be welded cannot be moved and fire hazards cannot be removed, are shields used to confine heat, sparks, and slag [1926.352, Fire Prevention]? |  |  |  |  |
| 28. Are fire watchers assigned when welding or cutting is performed in locations where a serious fire might develop [1910.252(a)(2)(iii)(A), General Requirements]? |  |  |  |  |
| 29. Are combustible floors kept wet, covered by damp sand, or protected by fire-resistant shields [1910.252(a)(2)(v), General Requirements]? |  |  |  |  |
| 30. When floors are wet down, are personnel protected from possible electrical shock [1910.252(a)(2)(v), General Requirements]? |  |  |  |  |
| 31. When welding is done on metal walls, are precautions taken to protect combustibles on the other side [1910.252(a)(2)(iii)(A)(3), General Requirements]? |  |  |  |  |
| 32. Before hot work is begun, are used drums, barrels, tanks, and other containers so thoroughly cleaned that no substances remain that could explode, ignite, or produce toxic vapors [1910.252(a)(2)(vi)(B) and 1910.252(a)(3), General Requirements]? |  |  |  |  |
|  | YES | NO | N/A | COMMENTS |
| 33. Is it required that eye protection helmets, hand shields and goggles meet appropriate standards [1910.252(b)(2)(ii)(I), General Requirements]? |  |  |  |  |
| 34. Are employees exposed to the hazards created by welding, cutting or brazing operations protected with personal protective equipment and clothing [1910.252(b)(3), General Requirements]? |  |  |  |  |
| 35. Is a check made for adequate ventilation in and where welding or cutting is performed [1910.252(b)(4)(ii), General Requirements]? |  |  |  |  |
| 36. When working in confined places, are environmental monitoring tests taken and means provided for quick removal of welders in case of an emergency [1926.353, Ventilation and Protection in Welding, Cutting and Heating]? |  |  |  |  |