## Slide 1: Supercritical CO2 Power Cycles: Next-Gen Power for CSP?
Craig Turchi
Sr. Engineer, National Renewable Energy Laboratory
craig.turchi@nrel.gov

## Slide 2: Outline
History of closed Brayton Cycles
Attributes that are attractive for CSP
sCO2 Brayton Cycle designs tailored for CSP
Current state of development and the “STEP” initiative

## Slide 3: Open Brayton Power Cycle
GE LM6000 Combustion Turbine
Fuel
Fossil-fired combustion turbine power plant (www.tva.com)

## Slide 4: Closed Brayton Power Cycle
Recuperator
Heat
Indirect heating via an external source
Any gas or supercritical fluid can be used
Working fluid circulates in a closed loop

## Slide 5: Brief History of the Closed Brayton Cycle (CBC)
1939 First commercial air-CBC at Escher Wyss in Zurich
1949 Air-CBC efficiency greater than contemporary steam cycles
1956 Ravensburg air-CBC comes online. Plant accumulates 120,000 hrs operation at average 91% availability
Notes: Ernest G. Feher

## Slide 6: Ravensburg Plant (1956-1977)
10 MWth , 2.3 MWe
660 °C hot gas temp
Representation of the turboset: 3-stage radial compressor and 5-stage axial turbine
Images from Pasch, San Antonio, TX, 2012
Original reference: Frutschi, Closed-Cycle Gas Turbines (2005)
Notes: All information and pictures are taken from Closed-Cycle Gas Turbines: Operating Experience and Future Potential, By Hans Ulrich Frutschi, 2005, ASME Press

## Slide 7: Brief History of the Closed Brayton Cycle (CBC)
1939 First commercial air-CBC at Escher Wyss in Zurich
1949 Air-CBC efficiency greater than contemporary steam cycles
1956 Ravensburg air-CBC comes online. Plant accumulates 120,000 hrs operation at average 91% availability
1967 Feher catalogs candidate supercritical fluids for use in CBC
1968 Angelino proposes the “recompression” sCO2 power cycle
2004 Dostal rekindles interest in sCO2-CBC by examining its use for Gen IV nuclear power plants
2009 Sandia National Labs builds 250 kWe recompression cycle at Barber- Nichols in Arvada, CO
2012 Echogen Power Systems designs 7 MWe sCO2 system for waste heat recovery
2014 DOE forms Supercritical Transformational Electric Power (STEP) cross-cut initiative with Fossil, Nuclear, EERE, and Basic Energy Science programs
Notes: Ernest G. Feher

## Slide 8: Why sCO2?
1
3
5
2
4
6
Density and Heat Capacity
Yoo, 2012
CO2 inventory control
Notes: The thermophysical properties of CO2 versus temperature at P = 8 MPa: (a) density ρ and specific heat at constant pressure cp;
(b) thermal conductivity k, dynamic viscosity μ, and specific enthalpy h; (c) Prandtl number Pr and thermal expansion coefficient β; and
(d ) kinematic viscosity ν. Figure taken Yoo (2012) who references Bae et al. (2005, 2008).
The critical point is 7.38 MPa at 31.1 °C (304.3 K)

## Slide 9: Power Cycle Options for CSP
Chart: Temperature, C
| 300 | 400 | 500 | 560 | 600 | 650 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400
Current Parabolic Trough | 0.38
Current Power Tower | 0.43
Typical Engg Limit | 0.34031 | 0.40119 | 0.44631 | 0.46819 | 0.4811 | 0.49567 | 0.50874 | 0.53122 | 0.54987 | 0.56559 | 0.57902 | 0.59063 | 0.60076 | 0.60968
s-CO2 Brayton | 0.4328 | 0.458 | 0.4737 | 0.4909 | 0.5065
Supercritical Steam | 0.46 | 0.48
Ericsson
Air Brayton CC | 0.6
PETE/CSP
s-CO2 Brayton CC
Current Parabolic Trough
Current Power Tower
Air Brayton Combined Cycle (commercial for NG)
Supercritical Steam (commercial for coal)
Typical Engineering Limit (75% Carnot)
S-CO2 Brayton (recompression)
Power Tower Range

## Slide 10: Attractive features of sCO2 Brayton Cycle
  Higher efficiency than steam Rankine
  High density working fluid yields compact turbomachinery
  Optimum turbine size 10 to 300 MWe
  Low-cost, low toxicity, low corrosivity fluid
  Thermally stable fluid at temperatures of interest to CSP (550 °C to 750 °C)
  Single phase reduces operational complexity; integrates well with sensible heat storage in CSP systems
MIT depiction of 150 MWe recompression-cycle power system (2006)
  Simpler cycle design than steam Rankine

## Slide 11: Potential in Multiple Markets → Industry interest
Power Sector | Why? | Who?
Nuclear | Good match to Gen IV sodium fast reactor designs | Sandia, Argonne, INL
Fossil | Next generation coal plants with oxy-fuel combustion and CO2 capture | NETL, Gas Tech Institute (GTI), Toshiba, NetPower
Marine Power | Compact and fast responding turbomachinery | US Navy via Knolls and Bettis Atomic Power Labs
Waste Heat Recovery | Simple cycle design with high efficiency | Echogen, Dresser-Rand (Siemens), GE
Solar | Allows for higher conversion efficiency in high-temperature power towers | GE, Samsung, CSIRO, NREL
Grid Electricity Storage | Reversible cycle: heat pump/power turbine | ABB, GE, others

## Slide 12: sCO2 Cycle Design Considerations for CSP Conditions
Optimize for molten-salt thermal storage by maximizing ΔT across turbine and storage system
Neises and Turchi, “A comparison of supercritical carbon dioxide power cycle
configurations with an emphasis on CSP applications,” Energy Procedia 2014.
Notes: All cycles want to minimize heat exchanger area (Conductance) while maximizing thermal efficiency.
CSP-specific conditions are shown here.

## Slide 13: sCO2 Cycle Design Considerations for CSP Conditions
Gong, et al, “Analysis of Radial Compressor Options for
Supercritical CO2 Power Conversion Cycles,” 2006
Most sCO2 cycle designers plan for a wet-cooled system:
CIT ≈ 32 °C
CIP ≈ 7.7 MPa
MC = Main compressor
CIT = Compressor Inlet Temperature
CIP = Compressor Inlet Pressure
CSP will likely require a dry-cooled system, for example CIT ≈ 50 °C.
Compressor (and cycle) efficiency is optimized by increasing
CIP ≈ 10 MPa
Notes: All cycles want to minimize heat exchanger area (Conductance) while maximizing thermal efficiency.
CSP-specific conditions are shown here.

## Slide 14: CSP with sCO2 Conceptual Design – example one
Dry-cooled, “partial-cooling” cycle coupled to high-temperature molten salt power tower (or particle receiver)

## Slide 15: CSP with sCO2 Conceptual Design – example two
Direct-heated, small-capacity, tower-mounted “simple recuperated” cycle coupled to PCM thermal energy storage
Utilizes compact size of the sCO2 power system at ≈10 MWe capacity
Allows for factory-fabrication of power block
PCM or thermochemical storage with narrow ∆T

## Slide 16: sCO2 Brayton Cycle Research Activities
  Corrosion and materials compatibility data at high T, P
  Cost-effective and durable recuperators
  Design and validation of primary heat exchangers; understanding of sCO2/HTF interactions
  Validation of power turbine bearings, seals, stop-valves
  Modeling start/stop, off-design and other transient operations
  Cycle operating methodology for dry-cooled systems
  Demonstration of cycle operations and equipment durability at commercially relevant scale (10 MWe)

## Slide 17: Journal Publications
Chart: 
| 1980-2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
Column1 | 5 | 6 | 6 | 6 | 12 | 8 | 16 | 25 | 46 | 51 | 57
Web of Science search for: “supercritical brayton” OR “supercritical CO2 power cycle”
Notes: From Web of Science
You searched for: TOPIC: (supercritical brayton) OR TOPIC: (supercritical CO2 power cycle)

## Slide 18: Supercritical Transformational Electric Power (STEP)
10 MWe Pilot Plant Test Facility:
  sCO2 Recompression Brayton Cycle at turbine inlet operating temperatures of 700°C,
  Reconfigurable facility to support testing a variety of components or subsystems, and
  Capability to monitor and characterize primary components or subsystems (turbomachinery, heat exchangers, recuperators, bearings, seals, etc.)
Map pathway towards an overall power cycle efficiency of 50% or greater
Demonstrate steady-state, dynamic, transient load following, and limited endurance operations
Cross-program DOE initiative to demonstrate the sCO2 power cycle at commercial scale.
Up to $80M federal contribution, 20% industry cost share, and 6-year duration (see DE-FOA-0001457, released March 2016)
Notes: The U.S. Department of Energy’s Supercritical Transformational Electric Power (STEP) program awarded a total of $3.9 million to three competitively-selected teams to develop conceptual plans to support the design, cost and schedule for a 10 MWe sCO2 Brayton Cycle test facility. The awardees selected for funding are Echogen Power Systems in Ohio, the Gas Technology Institute in Illinois, and the Southwest Research Institute in Texas.

## Slide 19: Summary
The sCO2 power cycle is potentially simpler and more efficient than steam-Rankine cycles in many applications
  Applications include: advanced nuclear, fossil, solar-thermal, and waste-heat recovery heat sources
Major research institutions and power companies from around the world are engaged in its development
  E.g., GE, Dresser-Rand, Toshiba, Samsung
  The STEP initiative plans to demonstrate a commercial-scale system in five years
sCO2 power cycles optimized for CSP could provide the CAPEX and efficiency needed to achieve SunShot

## Slide 20: Thank you!

## Slide 21: Brief History of the Closed Brayton Cycle (CBC)
1939 First commercial air-CBC at Escher Wyss in Zurich
1949 Air-CBC efficiency greater than contemporary steam cycles
1956 Ravensburg air-CBC comes online. Plant accumulates 120,000 hrs operation at average 91% availability
1967 Feher catalogs candidate supercritical fluids for use in CBC
1968 Angelino proposes the “recompression” sCO2 power cycle
2004 Dostal rekindles interest in sCO2-CBC by examining its use for Gen IV nuclear power plants
2009 Sandia National Labs builds 250 kWe recompression cycle at Barber- Nichols in Arvada, CO
2012 Echogen Power Systems designs 7 MWe sCO2 system for waste heat recovery
2014 DOE forms Supercritical Transformational Electric Power (STEP) cross-cut initiative with Fossil, Nuclear, EERE, and Basic Energy Science programs
Notes: Ernest G. Feher

## Slide 22: 10 MWe Turbomachinery: Threshold for commercial viability
Notes: Lower radial efficiency due to:
The sharp turn in flow direction at the inlet
Vulnerability to secondary flows in their long passages
High outlet velocity and only moderate diffuser efficiency
Larger wetted area than axial machines