## File Description
This document details reference performance tests (RPTs) for Li-ion systems
> 100 kW, > 10h
It is assumed rated power is 100 kW, duration is 10 hours (since > has no upper limit)

## Capacity and pulse test
Reference Performace Test
BESS duration (h) | 10
RTE assumed (AC-AC) | 0.8
Estimated extra duration for taper during charge | 1
10h duration, 0.1 MW
RPT 1 - Energy capacity test at rated power - 3 cycles Perform twice a year
Initial SOC (assumed to be 50% here, please enter correct initial SOC) | 0.5
Recommended charge power as fraction of rated power | 1
| Estimated duration (h) | Comments
1) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS | 7.25 | Recommended charge power may be less than rated power. For estimation puroses, it is assumed charge power = rated power. Assume SOC is 50% before charge. Duration is estimated from RTE |  | Time (h) | Fraction of rated power | SOC
2) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0.33333 |  |  | 0 | 0 | 0.5
3) Discharge at rated power to lower SOC limit as dictated by BMS (which may be > 0% SOC) | 10 |  |  | 0.01 | -1 | 0.5
4) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0.33333 |  |  | 7.25 | -1 | 1
5) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS | 13.5 |  |  | 7.26 | 0
6) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0.33333 |  |  | 7.5833 | 0
7) Steps 3-6 form one cycle. Repeat steps 3-6 three times. |  |  |  | 7.5933 | 1 | 1 | start cycle
Total duration for test (h) = | 80.0833 |  |  | 17.5833 | 1 | 0
|  |  |  | 17.5933 | 0
|  |  |  | 17.9167 | 0
|  |  |  | 17.9267 | -1 | 0
|  |  |  | 31.4167 | -1 | 1
|  |  |  | 31.4267 | 0
|  |  |  | 31.75 | 0 |  | end cycle 1
|  |  |  | 31.76 | 1 | 1
|  |  |  | 41.75 | 1 | 0
|  |  |  | 41.76 | 0
|  |  |  | 42.0833 | 0
|  |  |  | 42.0933 | -1 | 0
|  |  |  | 55.5833 | -1 | 1
|  |  |  | 55.5933 | 0
|  |  |  | 55.9167 | 0 |  | end cycle 2
|  |  |  | 55.9267 | 1 | 1
|  |  |  | 65.9167 | 1 | 0
|  |  |  | 65.9267 | 0
|  |  |  | 66.25 | 0
|  |  |  | 66.26 | -1 | 0
RPT 2 - Energy capacity test at half rated power - 1 cycle performed once a year |  |  |  | 79.75 | -1 | 1
Initial SOC (assumed to be 100% please enter correct initial SOC) | 1 |  |  | 79.76 | 0
|  |  |  | 80.0833 | 0 |  | end cycle 3
Discharge power as a multiple of rated power | 0.5
| Estimated duration (h) |  |  | Time (h) | Fraction of rated power | SOC
1) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS | 1 | Assume BESS is at max SOC before this test |  | 0 | 0 | 0.95
2) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0.33333 |  |  | 0.01 | -1 | 0.95
3) Discharge at rated power to lower SOC limit as dictated by BMS (which may be > 0% SOC) | 20 |  |  | 1 | -1 | 1
4) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0 |  |  | 1.01 | 0
5) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS | 13.5 |  |  | 1.3333 | 0
6) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0.33333 |  |  | 1.3433 | 1 | 1
Total duration for test (h) | 35.1667 |  |  | 21.3333 | 1 | 0
|  |  |  | 21.3433 | 0
|  |  |  | 21.3333 | 0
Allows estimation of available energy at various meters, inteprpolation allows estimation in 10-20h range (or 24-48h range) |  |  |  | 21.3433 | -1 | 0
|  |  |  | 34.8333 | -1 | 1
|  |  |  | 35.01 | 0 | 1
Pulse test. Do annually
Start at 100% SOC. Measure resistance at Max SOC, 80%, 60%, 40%, 20%, Min SOC, with only discharge pulse at 100% SOC, and charge pulse at 0% SOC, and discharge, charge pulse at other SOCs. Rest 30 min between pulses, and after taking BESS to desired SOC. |  | Initial SOC (assumed) | 1
Calculation of pulse duration.
Assume discharge pulse applied at rated power. Keep delta SOC for pulse < 0.025% SOC. |  | Pulse duration added at the end | Estimated duration (h)
Rated Power*(Pulse duration delta T in hours for 10-h BESS) = Rated power*10h*0.00025 |  | Time to charge BESS to Max SOC | 1 | Assume start SOC is Vmax
Pulse duration in hours = 0.0025 hours or 9 sec. |  | Rest after charge (h) | 0.5
For same duration of 9 sec, delta SOC for 24-h BESS = 0.010% |  | Total discharge time to Min SOC | 10
|  | Delta SOC for each discharge | 20%
1) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS. Rest 30 min |  | # Discharges | 5
a. Apply discharge pulse at rated power for 9 sec. Rest 30 min. |  | Wait time after each discharge (h) | 0.5
2) Take BESS to 80% SOC by discharging at rated power. Rest for 30 min. |  | Total wait time after discharges | 2.5
a. Apply discharge pulse at rated power for 9 sec. Rest 30 min |  | # charge pulses | 5
b. Apply charge pulse at rated power for 9 sec. Rest 30 min |  | # discharge pulses | 5
3) Take BESS to 60% SOC by discharging at rated power. Rest for 30 min. |  | Total pulses | 10
a. Apply discharge pulse at rated power for 9 sec. Rest 30 min |  | Wait time after each pulse | 0.5
b. Apply charge pulse at rated power for 9 sec. Rest 30 min |  | Total wait time after pulses | 5
4) Take BESS to 40% SOC by discharging at rated power. Rest for 30 min. |  | Pulse duration (s) | 9
a. Apply discharge pulse at rated power for 9 sec. Rest 30 min |  | Total pulse duration | 0.025 | negligible
b. Apply charge pulse at rated power for 9 sec. Rest 30 min |  | Charge back to max SOC | 13.5
5) Take BESS to 20% SOC by discharging at rated power. Rest for 30 min.
a. Apply discharge pulse at rated power for 9 sec. Rest 30 min |  | Test duration (h) | 67.725
b. Apply charge pulse at rated power for 9 sec. Rest 30 min
6) Take BESS to min SOC by discharging at rated power. Rest for 30 min.
a. Apply charge pulse at rated power for 9 sec. Rest 30 min
7) Bring BESS to max SOC. Rest 30 min.
[6 empty] | Time (h) | Power | SOC
[6 empty] | 0 | 0 | 1 | 60%
[6 empty] | 0.01 | -1 | 1
[6 empty] | 1 | -1 | 1 | 100%
[6 empty] | 1.01 | 0 | 1
[6 empty] | 1.5 | 0 | 1
[6 empty] | 1.51 | 1 | 1 | 100%
[6 empty] | 1.5125 | 1 | 1 | 100%
[6 empty] | 1.5225 | 0 | 1
[6 empty] | 2.0125 | 0 | 1
[6 empty] | 2.0225 | 1 | 1
[6 empty] | 4.0125 | 1 | 0.8 | 80%
[6 empty] | 4.0225 | 0 | 0.8
[6 empty] | 4.5125 | 0 | 0.8
[6 empty] | 4.5225 | 1 | 0.8 | 80%
[6 empty] | 4.525 | 1 | 0.8 | 80%
[6 empty] | 4.535 | 0 | 0.8
[6 empty] | 5.025 | 0 | 0.8
[6 empty] | 5.035 | -1 | 0.8 | 80%
[6 empty] | 5.0375 | -1 | 0.8 | 80%
[6 empty] | 5.0475 | 0 | 0.8
[6 empty] | 5.5375 | 0 | 0.8
[6 empty] | 5.5475 | 1 | 0.8
[6 empty] | 7.5375 | 1 | 0.6 | 60%
[6 empty] | 7.5475 | 0 | 0.6
[6 empty] | 8.0375 | 0 | 0.6
[6 empty] | 8.0475 | 1 | 0.6 | 60%
[6 empty] | 8.05 | 1 | 0.6 | 60%
[6 empty] | 8.06 | 0 | 0.6
[6 empty] | 8.55 | 0 | 0.6
Data to determine how much power should EMS requested for the grid | [5 empty] | 8.56 | -1 | 0.6 | 60%
Tabulate Requested power and delivered power at various SOCs, power, mode and ambient T. Then develop Requested power as f(delivered power, mode, SOC, ambient T). This allows the EMS to determine what the requested power should be for the desired delivered power at the grid. As battery SOH decreases, see how this function changes. | [5 empty] | 8.5625 | -1 | 0.6 | 60%
[6 empty] | 8.5725 | 0 | 0.6
[6 empty] | 9.0625 | 0 | 0.6
[6 empty] | 9.0725 | 1 | 0.6
[6 empty] | 11.0625 | 1 | 0.4 | 40%
[6 empty] | 11.0725 | 0 | 0.4
[6 empty] | 11.5625 | 0 | 0.4
[6 empty] | 11.5725 | 1 | 0.4 | 40%
[6 empty] | 11.575 | 1 | 0.4 | 40%
[6 empty] | 11.585 | 0 | 0.4
[6 empty] | 12.075 | 0 | 0.4
[6 empty] | 12.085 | -1 | 0.4 | 40%
[6 empty] | 12.0875 | -1 | 0.4 | 40%
[6 empty] | 12.0975 | 0 | 0.4
[6 empty] | 12.5875 | 0 | 0.4
[6 empty] | 12.5975 | 1 | 0.4
[6 empty] | 14.5875 | 1 | 0.2 | 20%
[6 empty] | 14.5975 | 0 | 0.2
[6 empty] | 15.0875 | 0 | 0.2
[6 empty] | 15.0975 | 1 | 0.2 | 20%
[6 empty] | 15.1 | 1 | 0.2 | 20%
[6 empty] | 15.11 | 0 | 0.2
[6 empty] | 15.6 | 0 | 0.2
[6 empty] | 15.61 | -1 | 0.2 | 20%
[6 empty] | 15.6125 | -1 | 0.2 | 20%
[6 empty] | 15.6225 | 0 | 0.2
[6 empty] | 16.1125 | 0 | 0.2
[6 empty] | 16.1225 | 1 | 0.2
[6 empty] | 18.1125 | 1 | 0 | 0%
[6 empty] | 18.1225 | 0 | 0
[6 empty] | 18.6125 | 0 | 0
[6 empty] | 18.6225 | 1 | 0 | 0%
[6 empty] | 18.625 | 1 | 0 | 0%
[6 empty] | 18.635 | 0 | 0
[6 empty] | 19.125 | 0 | 0
[6 empty] | 19.135 | -1 | 0 | 100%
[6 empty] | 32.635 | -1 | 1 | 100%

## PV Firming Duty Cycle test
PV Firming Test procedure. Done once a year
Initial SOC | 1
Target SOC | 0.95
Do every year
1) Bring BESS to the required starting SOC of 95% Max SOC. Note: the BESS has a net discharge - in this case paverage power demand from grid is > average PV generation. Assumption is BESS gets charged by some other renewable source (wind) or from grid at night
a. Charge or discharge the BESS to 95% of max SOC. Compare the charge or discharge energy to the required energy to bring to start SOC based on the measured energy capacity from the RPT.
i. during charge, the charge energy = (Measured discharge energy capacity from RPT)*(95% SOC-BESS SOC)/(SOCmax-SOCmin)/RTE from RPT test
ii. during discharge, the discharge energy = (Measured discharge energy capacity from RPT)*( BESS SOC -95% SOC)/(SOCmax-SOCmin) | Estimated Duration (h) | Cum time | Comments
Discharge BESS to 95% of max SOC (assume battery is at 100% SOC | 0.5 | 5 | Assume BESS is at max SOC before this test
2) Rest for 20 min for 10-h duration, 10 min for 24-h duration | 0.33333 | 0.83333
3) Apply the PV firming signal | 10 | 10.8333
4) Rest for 10 min for 10-h duration, 5 min for 24-h duration | 0.33333 | 11.1667
5) Bring battery back to initial SOC | 3 | 14.1667 | This duration depends on SOC at end of PV firming duty cycle
Total duration (h) | 14.1667
| Time, hh:mm:ss, 10 hours in length at one second intervals | Time (h) | Duty Cycle as power normalized by ESS rated power | Comments
|  | 0 | 0 | Initial OCV
|  | 0.01 | -1 | Charge to SOC max Assume BESS is at max SOC before this test
|  | 1 | -1 | End charge
|  | 1.01 | 1 | Discharge to 95% SOC max
|  | 1.5 | 1 | End discharge
|  | 1.51 | 0 | Rest 20 min
|  | 1.8433 | 0 | End rest
| 0:00 | 1.8533 | 0.017784 | Start duty cycle with 1 sec time increment
| 0:00 | 1.8536 | 0.017837
| 0:00 | 1.8539 | 0.01789
| 0:00 | 1.8542 | 0.017943
| 0:00 | 1.8544 | 0.017996
| 0:00 | 1.8547 | 0.018048
| 0:00 | 1.855 | 0.0181
| 0:00 | 1.8553 | 0.018151
| 0:00 | 1.8556 | 0.018202
| 0:00 | 1.8558 | 0.018253
| 0:00 | 1.8561 | 0.018304
| 0:00 | 1.8564 | 0.018354
| 0:00 | 1.8567 | 0.018404
| 0:00 | 1.8569 | 0.018454
| 0:00 | 1.8572 | 0.018503
| 0:00 | 1.8575 | 0.018552
| 0:00 | 1.8578 | 0.018601
| 0:00 | 1.8581 | 0.01865
| 0:00 | 1.8583 | 0.018698
| 0:00 | 1.8586 | 0.018746
| 0:00 | 1.8589 | 0.018793
| 0:00 | 1.8592 | 0.01884
| 0:00 | 1.8594 | 0.018887
| 0:00 | 1.8597 | 0.018934
| 0:00 | 1.86 | 0.01898
| 0:00 | 1.8603 | 0.019026
| 0:00 | 1.8606 | 0.019072
| 0:00 | 1.8608 | 0.019117
| 0:00 | 1.8611 | 0.019162
| 0:00 | 1.8614 | 0.019207
| 0:00 | 1.8617 | 0.019251
| 0:01 | 1.8619 | 0.019295
| 0:01 | 1.8622 | 0.019339
| 0:01 | 1.8625 | 0.019383
| 0:01 | 1.8628 | 0.019426
| 0:01 | 1.8631 | 0.019469
| 0:01 | 1.8633 | 0.019511
| 0:01 | 1.8636 | 0.019553
| 0:01 | 1.8639 | 0.019595
| 0:01 | 1.8642 | 0.019636
| 0:01 | 1.8644 | 0.019678
| 0:01 | 1.8647 | 0.019719
| 0:01 | 1.865 | 0.019759
| 0:01 | 1.8653 | 0.019799
| 0:01 | 1.8656 | 0.019839
| 0:01 | 1.8658 | 0.019879
| 0:01 | 1.8661 | 0.019918
| 0:01 | 1.8664 | 0.019957
| 0:01 | 1.8667 | 0.019995
| 0:01 | 1.8669 | 0.020034
| 0:01 | 1.8672 | 0.020071
| 0:01 | 1.8675 | 0.020109
| 0:01 | 1.8678 | 0.020146
| 0:01 | 1.8681 | 0.020183
| 0:01 | 1.8683 | 0.020218
| 0:01 | 1.8686 | 0.020252
| 0:01 | 1.8689 | 0.020285
| 0:01 | 1.8692 | 0.020317
| 0:01 | 1.8694 | 0.020348
| 0:01 | 1.8697 | 0.020378
| 0:01 | 1.87 | 0.020407
| 0:01 | 1.8703 | 0.020434
| 0:01 | 1.8706 | 0.020461
| 0:01 | 1.8708 | 0.020486
| 0:01 | 1.8711 | 0.02051
| 0:01 | 1.8714 | 0.020533
| 0:01 | 1.8717 | 0.020555
| 0:01 | 1.8719 | 0.020575
| 0:01 | 1.8722 | 0.020595
| 0:01 | 1.8725 | 0.020613
| 0:01 | 1.8728 | 0.020632
| 0:01 | 1.8731 | 0.020651
| 0:01 | 1.8733 | 0.02067
| 0:01 | 1.8736 | 0.020689
| 0:01 | 1.8739 | 0.020708
| 0:01 | 1.8742 | 0.020728
| 0:01 | 1.8744 | 0.020748
| 0:01 | 1.8747 | 0.020768
| 0:01 | 1.875 | 0.020788
| 0:01 | 1.8753 | 0.020809
| 0:01 | 1.8756 | 0.020829
| 0:01 | 1.8758 | 0.02085
| 0:01 | 1.8761 | 0.020871
| 0:01 | 1.8764 | 0.020893
| 0:01 | 1.8767 | 0.020914
| 0:01 | 1.8769 | 0.020936
| 0:01 | 1.8772 | 0.020958
| 0:01 | 1.8775 | 0.02098
| 0:01 | 1.8778 | 0.021002
| 0:01 | 1.8781 | 0.021025
| 0:02 | 1.8783 | 0.021048
| 0:02 | 1.8786 | 0.021071
| 0:02 | 1.8789 | 0.021094
| 0:02 | 1.8792 | 0.021117
| 0:02 | 1.8794 | 0.021141
| 0:02 | 1.8797 | 0.021164
| 0:02 | 1.88 | 0.021188
| 0:02 | 1.8803 | 0.021213
| 0:02 | 1.8806 | 0.021237
| 0:02 | 1.8808 | 0.021262
| 0:02 | 1.8811 | 0.021286
| 0:02 | 1.8814 | 0.021311
| 0:02 | 1.8817 | 0.021337
| 0:02 | 1.8819 | 0.021362
| 0:02 | 1.8822 | 0.021388
| 0:02 | 1.8825 | 0.021413
| 0:02 | 1.8828 | 0.021439
| 0:02 | 1.8831 | 0.021466
| 0:02 | 1.8833 | 0.021492
| 0:02 | 1.8836 | 0.021519
| 0:02 | 1.8839 | 0.021546
| 0:02 | 1.8842 | 0.021573
| 0:02 | 1.8844 | 0.0216
| 0:02 | 1.8847 | 0.021627
| 0:02 | 1.885 | 0.021655
| 0:02 | 1.8853 | 0.021683
| 0:02 | 1.8856 | 0.021711
| 0:02 | 1.8858 | 0.021739
| 0:02 | 1.8861 | 0.021768
| 0:02 | 1.8864 | 0.021797
| 0:02 | 1.8867 | 0.021825
| 0:02 | 1.8869 | 0.021855
| 0:02 | 1.8872 | 0.021884
| 0:02 | 1.8875 | 0.021913
| 0:02 | 1.8878 | 0.021943
| 0:02 | 1.8881 | 0.021973
| 0:02 | 1.8883 | 0.022003
| 0:02 | 1.8886 | 0.022034
| 0:02 | 1.8889 | 0.022064
| 0:02 | 1.8892 | 0.022095
| 0:02 | 1.8894 | 0.022126
| 0:02 | 1.8897 | 0.022157
| 0:02 | 1.89 | 0.022189
| 0:02 | 1.8903 | 0.02222
| 0:02 | 1.8906 | 0.022252
| 0:02 | 1.8908 | 0.022284
| 0:02 | 1.8911 | 0.022316
| 0:02 | 1.8914 | 0.022349
| 0:02 | 1.8917 | 0.022381
| 0:02 | 1.8919 | 0.022414
| 0:02 | 1.8922 | 0.022447
| 0:02 | 1.8925 | 0.02248
| 0:02 | 1.8928 | 0.022514
| 0:02 | 1.8931 | 0.022548
| 0:02 | 1.8933 | 0.022582
| 0:02 | 1.8936 | 0.022616
| 0:02 | 1.8939 | 0.02265
| 0:02 | 1.8942 | 0.022684
| 0:02 | 1.8944 | 0.022719
| 0:02 | 1.8947 | 0.022754
| 0:02 | 1.895 | 0.022789
| 0:03 | 1.8953 | 0.022825
| 0:03 | 1.8956 | 0.02286
| 0:03 | 1.8958 | 0.022896
| 0:03 | 1.8961 | 0.022932
| 0:03 | 1.8964 | 0.022968
| 0:03 | 1.8967 | 0.023005
| 0:03 | 1.8969 | 0.023041
| 0:03 | 1.8972 | 0.023078
| 0:03 | 1.8975 | 0.023115
| 0:03 | 1.8978 | 0.023153
| 0:03 | 1.8981 | 0.02319
| 0:03 | 1.8983 | 0.023228
| 0:03 | 1.8986 | 0.023266
| 0:03 | 1.8989 | 0.023304
| 0:03 | 1.8992 | 0.023342
| 0:03 | 1.8994 | 0.023381
| 0:03 | 1.8997 | 0.02342
| 0:03 | 1.9 | 0.023459
| 0:03 | 1.9003 | 0.023498
| 0:03 | 1.9006 | 0.023537
| 0:03 | 1.9008 | 0.023577
| 0:03 | 1.9011 | 0.023617
| 0:03 | 1.9014 | 0.023657
| 0:03 | 1.9017 | 0.023697
| 0:03 | 1.9019 | 0.023738
| 0:03 | 1.9022 | 0.023779
| 0:03 | 1.9025 | 0.02382
| 0:03 | 1.9028 | 0.023861
| 0:03 | 1.9031 | 0.023902
| 0:03 | 1.9033 | 0.023944
| 0:03 | 1.9036 | 0.023986
| 0:03 | 1.9039 | 0.024028
| 0:03 | 1.9042 | 0.02407
| 0:03 | 1.9044 | 0.024113
| 0:03 | 1.9047 | 0.024155
| 0:03 | 1.905 | 0.024198
| 0:03 | 1.9053 | 0.024241
| 0:03 | 1.9056 | 0.024285
| 0:03 | 1.9058 | 0.024328
| 0:03 | 1.9061 | 0.024372
| 0:03 | 1.9064 | 0.024416
| 0:03 | 1.9067 | 0.02446
| 0:03 | 1.9069 | 0.024505
| 0:03 | 1.9072 | 0.024549
| 0:03 | 1.9075 | 0.024594
| 0:03 | 1.9078 | 0.024639
| 0:03 | 1.9081 | 0.024684
| 0:03 | 1.9083 | 0.02473
| 0:03 | 1.9086 | 0.024775
| 0:03 | 1.9089 | 0.02482
| 0:03 | 1.9092 | 0.024866
| 0:03 | 1.9094 | 0.024911
| 0:03 | 1.9097 | 0.024957
| 0:03 | 1.91 | 0.025002
| 0:03 | 1.9103 | 0.025048
| 0:03 | 1.9106 | 0.025094
| 0:03 | 1.9108 | 0.025139
| 0:03 | 1.9111 | 0.025185
| 0:03 | 1.9114 | 0.025231
| 0:04 | 1.9117 | 0.025277
| 0:04 | 1.9119 | 0.025323
| 0:04 | 1.9122 | 0.025369
| 0:04 | 1.9125 | 0.025415
| 0:04 | 1.9128 | 0.025461
| 0:04 | 1.9131 | 0.025507
| 0:04 | 1.9133 | 0.025553
| 0:04 | 1.9136 | 0.025599
| 0:04 | 1.9139 | 0.025645
| 0:04 | 1.9142 | 0.025692
| 0:04 | 1.9144 | 0.025738
| 0:04 | 1.9147 | 0.025784
| 0:04 | 1.915 | 0.025831
| 0:04 | 1.9153 | 0.025877
| 0:04 | 1.9156 | 0.025924
| 0:04 | 1.9158 | 0.025971
| 0:04 | 1.9161 | 0.026017
| 0:04 | 1.9164 | 0.026064
| 0:04 | 1.9167 | 0.026111
| 0:04 | 1.9169 | 0.026158
| 0:04 | 1.9172 | 0.026205
| 0:04 | 1.9175 | 0.026251
| 0:04 | 1.9178 | 0.026298
| 0:04 | 1.9181 | 0.026345
| 0:04 | 1.9183 | 0.026392
| 0:04 | 1.9186 | 0.02644
| 0:04 | 1.9189 | 0.026487
| 0:04 | 1.9192 | 0.026534
| 0:04 | 1.9194 | 0.026581
| 0:04 | 1.9197 | 0.026629
| 0:04 | 1.92 | 0.026676
| 0:04 | 1.9203 | 0.026723
| 0:04 | 1.9206 | 0.026771
| 0:04 | 1.9208 | 0.026818
| 0:04 | 1.9211 | 0.026866
| 0:04 | 1.9214 | 0.026914
| 0:04 | 1.9217 | 0.026961
| 0:04 | 1.9219 | 0.027009
| 0:04 | 1.9222 | 0.027057
| 0:04 | 1.9225 | 0.027105
| 0:04 | 1.9228 | 0.027153
| 0:04 | 1.9231 | 0.027201
| 0:04 | 1.9233 | 0.027249
| 0:04 | 1.9236 | 0.027297
| 0:04 | 1.9239 | 0.027345
| 0:04 | 1.9242 | 0.027393
| 0:04 | 1.9244 | 0.027441
| 0:04 | 1.9247 | 0.02749
| 0:04 | 1.925 | 0.027538
| 0:04 | 1.9253 | 0.027586
| 0:04 | 1.9256 | 0.027635
| 0:04 | 1.9258 | 0.027683
| 0:04 | 1.9261 | 0.027732
| 0:04 | 1.9264 | 0.02778
| 0:04 | 1.9267 | 0.027829
| 0:04 | 1.9269 | 0.027878
| 0:04 | 1.9272 | 0.027927
| 0:04 | 1.9275 | 0.027975
| 0:04 | 1.9278 | 0.028024
| 0:04 | 1.9281 | 0.028073
| 0:04 | 1.9283 | 0.028122
| 0:05 | 1.9286 | 0.028171
| 0:05 | 1.9289 | 0.02822
| 0:05 | 1.9292 | 0.028269
| 0:05 | 1.9294 | 0.028318
| 0:05 | 1.9297 | 0.028367
| 0:05 | 1.93 | 0.028417
| 0:05 | 1.9303 | 0.028466
| 0:05 | 1.9306 | 0.028515
| 0:05 | 1.9308 | 0.028565
| 0:05 | 1.9311 | 0.028614
| 0:05 | 1.9314 | 0.028663
| 0:05 | 1.9317 | 0.028713
| 0:05 | 1.9319 | 0.028762
| 0:05 | 1.9322 | 0.028812
| 0:05 | 1.9325 | 0.028862
| 0:05 | 1.9328 | 0.028911
| 0:05 | 1.9331 | 0.028961
| 0:05 | 1.9333 | 0.029011
| 0:05 | 1.9336 | 0.02906
| 0:05 | 1.9339 | 0.02911
| 0:05 | 1.9342 | 0.02916
| 0:05 | 1.9344 | 0.02921
| 0:05 | 1.9347 | 0.02926
| 0:05 | 1.935 | 0.02931
| 0:05 | 1.9353 | 0.02936
| 0:05 | 1.9356 | 0.02941
| 0:05 | 1.9358 | 0.02946
| 0:05 | 1.9361 | 0.02951
| 0:05 | 1.9364 | 0.02956
| 0:05 | 1.9367 | 0.029611
| 0:05 | 1.9369 | 0.029661
| 0:05 | 1.9372 | 0.029711
| 0:05 | 1.9375 | 0.029762
| 0:05 | 1.9378 | 0.029812
| 0:05 | 1.9381 | 0.029862
| 0:05 | 1.9383 | 0.029913
| 0:05 | 1.9386 | 0.029963
| 0:05 | 1.9389 | 0.030014
| 0:05 | 1.9392 | 0.030064
| 0:05 | 1.9394 | 0.030115
| 0:05 | 1.9397 | 0.030166
| 0:05 | 1.94 | 0.030216
| 0:05 | 1.9403 | 0.030267
| 0:05 | 1.9406 | 0.030318
| 0:05 | 1.9408 | 0.030369
| 0:05 | 1.9411 | 0.03042
| 0:05 | 1.9414 | 0.030471
| 0:05 | 1.9417 | 0.030522
| 0:05 | 1.9419 | 0.030573
| 0:05 | 1.9422 | 0.030624
| 0:05 | 1.9425 | 0.030675
| 0:05 | 1.9428 | 0.030726
| 0:05 | 1.9431 | 0.030777
| 0:05 | 1.9433 | 0.030828
| 0:05 | 1.9436 | 0.03088
| 0:05 | 1.9439 | 0.030931
| 0:05 | 1.9442 | 0.030982
| 0:05 | 1.9444 | 0.031034
| 0:05 | 1.9447 | 0.031085
| 0:06 | 1.945 | 0.031136
| 0:06 | 1.9453 | 0.031188
| 0:06 | 1.9456 | 0.031239
| 0:06 | 1.9458 | 0.031291
| 0:06 | 1.9461 | 0.031343
| 0:06 | 1.9464 | 0.031394
| 0:06 | 1.9467 | 0.031446
| 0:06 | 1.9469 | 0.031498
| 0:06 | 1.9472 | 0.031549
| 0:06 | 1.9475 | 0.031601
| 0:06 | 1.9478 | 0.031653
| 0:06 | 1.9481 | 0.031705
| 0:06 | 1.9483 | 0.031757
| 0:06 | 1.9486 | 0.031809
| 0:06 | 1.9489 | 0.031861
| 0:06 | 1.9492 | 0.031913
| 0:06 | 1.9494 | 0.031965
| 0:06 | 1.9497 | 0.032017
| 0:06 | 1.95 | 0.032069
| 0:06 | 1.9503 | 0.032121
| 0:06 | 1.9506 | 0.032174
| 0:06 | 1.9508 | 0.032226
| 0:06 | 1.9511 | 0.032278
| 0:06 | 1.9514 | 0.032331
| 0:06 | 1.9517 | 0.032383
| 0:06 | 1.9519 | 0.032435
| 0:06 | 1.9522 | 0.032488
| 0:06 | 1.9525 | 0.03254
| 0:06 | 1.9528 | 0.032593
| 0:06 | 1.9531 | 0.032646
| 0:06 | 1.9533 | 0.032698
| 0:06 | 1.9536 | 0.032751
| 0:06 | 1.9539 | 0.032804
| 0:06 | 1.9542 | 0.032857
| 0:06 | 1.9544 | 0.032909
| 0:06 | 1.9547 | 0.032962
| 0:06 | 1.955 | 0.033015
| 0:06 | 1.9553 | 0.033068
| 0:06 | 1.9556 | 0.033121
| 0:06 | 1.9558 | 0.033174
| 0:06 | 1.9561 | 0.033227
| 0:06 | 1.9564 | 0.03328
| 0:06 | 1.9567 | 0.033333
| 0:06 | 1.9569 | 0.033387
| 0:06 | 1.9572 | 0.03344
| 0:06 | 1.9575 | 0.033493
| 0:06 | 1.9578 | 0.033547
| 0:06 | 1.9581 | 0.033602
| 0:06 | 1.9583 | 0.033657
| 0:06 | 1.9586 | 0.033713
| 0:06 | 1.9589 | 0.033769
| 0:06 | 1.9592 | 0.033826
| 0:06 | 1.9594 | 0.033883
| 0:06 | 1.9597 | 0.033941
| 0:06 | 1.96 | 0.034
| 0:06 | 1.9603 | 0.034059
| 0:06 | 1.9606 | 0.034119
| 0:06 | 1.9608 | 0.034179
| 0:06 | 1.9611 | 0.03424
| 0:06 | 1.9614 | 0.034302
| 0:06 | 1.9617 | 0.034364
| 0:07 | 1.9619 | 0.034426
| 0:07 | 1.9622 | 0.03449
| 0:07 | 1.9625 | 0.034554
| 0:07 | 1.9628 | 0.034618
| 0:07 | 1.9631 | 0.034683
| 0:07 | 1.9633 | 0.034749
| 0:07 | 1.9636 | 0.034815
| 0:07 | 1.9639 | 0.034882
| 0:07 | 1.9642 | 0.034949
| 0:07 | 1.9644 | 0.035017
| 0:07 | 1.9647 | 0.035084
| 0:07 | 1.965 | 0.035151
| 0:07 | 1.9653 | 0.035218
| 0:07 | 1.9656 | 0.035284
| 0:07 | 1.9658 | 0.03535
| 0:07 | 1.9661 | 0.035416
| 0:07 | 1.9664 | 0.035481
| 0:07 | 1.9667 | 0.035545
| 0:07 | 1.9669 | 0.03561
| 0:07 | 1.9672 | 0.035674
| 0:07 | 1.9675 | 0.035737
| 0:07 | 1.9678 | 0.0358
| 0:07 | 1.9681 | 0.035863
| 0:07 | 1.9683 | 0.035925
| 0:07 | 1.9686 | 0.035987
| 0:07 | 1.9689 | 0.036049
| 0:07 | 1.9692 | 0.03611
| 0:07 | 1.9694 | 0.03617
| 0:07 | 1.9697 | 0.036231
| 0:07 | 1.97 | 0.036291
| 0:07 | 1.9703 | 0.03635
| 0:07 | 1.9706 | 0.036409
| 0:07 | 1.9708 | 0.036468
| 0:07 | 1.9711 | 0.036526
| 0:07 | 1.9714 | 0.036584
| 0:07 | 1.9717 | 0.036642
| 0:07 | 1.9719 | 0.036699
| 0:07 | 1.9722 | 0.036756
| 0:07 | 1.9725 | 0.036812
| 0:07 | 1.9728 | 0.036868
| 0:07 | 1.9731 | 0.036924
| 0:07 | 1.9733 | 0.036979
| 0:07 | 1.9736 | 0.037034
| 0:07 | 1.9739 | 0.037088
| 0:07 | 1.9742 | 0.037142
| 0:07 | 1.9744 | 0.037196
| 0:07 | 1.9747 | 0.037249
| 0:07 | 1.975 | 0.037302
| 0:07 | 1.9753 | 0.037354
| 0:07 | 1.9756 | 0.037406
| 0:07 | 1.9758 | 0.037458
| 0:07 | 1.9761 | 0.037509
| 0:07 | 1.9764 | 0.03756
| 0:07 | 1.9767 | 0.037611
| 0:07 | 1.9769 | 0.037662
| 0:07 | 1.9772 | 0.037713
| 0:07 | 1.9775 | 0.037764
| 0:07 | 1.9778 | 0.037816
| 0:07 | 1.9781 | 0.037867
| 0:08 | 1.9783 | 0.037918
| 0:08 | 1.9786 | 0.03797
| 0:08 | 1.9789 | 0.038021
| 0:08 | 1.9792 | 0.038072
| 0:08 | 1.9794 | 0.038124
| 0:08 | 1.9797 | 0.038175
| 0:08 | 1.98 | 0.038226
| 0:08 | 1.9803 | 0.038277
| 0:08 | 1.9806 | 0.038329
| 0:08 | 1.9808 | 0.03838
| 0:08 | 1.9811 | 0.038431
| 0:08 | 1.9814 | 0.038482
| 0:08 | 1.9817 | 0.038534
| 0:08 | 1.9819 | 0.038585
| 0:08 | 1.9822 | 0.038636
| 0:08 | 1.9825 | 0.038687
| 0:08 | 1.9828 | 0.038739
| 0:08 | 1.9831 | 0.03879
| 0:08 | 1.9833 | 0.038841
| 0:08 | 1.9836 | 0.038892
| 0:08 | 1.9839 | 0.038943
| 0:08 | 1.9842 | 0.038994
| 0:08 | 1.9844 | 0.039045
| 0:08 | 1.9847 | 0.039097
| 0:08 | 1.985 | 0.039148
| 0:08 | 1.9853 | 0.039199
| 0:08 | 1.9856 | 0.03925
| 0:08 | 1.9858 | 0.039301
| 0:08 | 1.9861 | 0.039352
| 0:08 | 1.9864 | 0.039403
| 0:08 | 1.9867 | 0.039454
| 0:08 | 1.9869 | 0.039505
| 0:08 | 1.9872 | 0.039555
| 0:08 | 1.9875 | 0.039602
| 0:08 | 1.9878 | 0.039646
| 0:08 | 1.9881 | 0.039688
| 0:08 | 1.9883 | 0.039727
| 0:08 | 1.9886 | 0.039764
| 0:08 | 1.9889 | 0.039797
| 0:08 | 1.9892 | 0.039829
| 0:08 | 1.9894 | 0.039857
| 0:08 | 1.9897 | 0.039883
| 0:08 | 1.99 | 0.039907
| 0:08 | 1.9903 | 0.039927
| 0:08 | 1.9906 | 0.039945
| 0:08 | 1.9908 | 0.039962
| 0:08 | 1.9911 | 0.03998
| 0:08 | 1.9914 | 0.039998
| 0:08 | 1.9917 | 0.040016
| 0:08 | 1.9919 | 0.040035
| 0:08 | 1.9922 | 0.040054
| 0:08 | 1.9925 | 0.040074
| 0:08 | 1.9928 | 0.040094
| 0:08 | 1.9931 | 0.040115
| 0:08 | 1.9933 | 0.040136
| 0:08 | 1.9936 | 0.040157
| 0:08 | 1.9939 | 0.040179
| 0:08 | 1.9942 | 0.040201
| 0:08 | 1.9944 | 0.040224
| 0:08 | 1.9947 | 0.040247
| 0:08 | 1.995 | 0.040271
| 0:09 | 1.9953 | 0.040295
| 0:09 | 1.9956 | 0.04032
| 0:09 | 1.9958 | 0.040347
| 0:09 | 1.9961 | 0.040377
| 0:09 | 1.9964 | 0.040409
| 0:09 | 1.9967 | 0.040445
| 0:09 | 1.9969 | 0.040483
| 0:09 | 1.9972 | 0.040524
| 0:09 | 1.9975 | 0.040567
| 0:09 | 1.9978 | 0.040613
| 0:09 | 1.9981 | 0.04066
| 0:09 | 1.9983 | 0.040709
| 0:09 | 1.9986 | 0.040759
| 0:09 | 1.9989 | 0.040809
| 0:09 | 1.9992 | 0.040861
| 0:09 | 1.9994 | 0.040915
| 0:09 | 1.9997 | 0.040969
| 0:09 | 2 | 0.041025
| 0:09 | 2.0003 | 0.041081
| 0:09 | 2.0006 | 0.041139
| 0:09 | 2.0008 | 0.041198
| 0:09 | 2.0011 | 0.041258
| 0:09 | 2.0014 | 0.041321
| 0:09 | 2.0017 | 0.041388
| 0:09 | 2.0019 | 0.041459
| 0:09 | 2.0022 | 0.041535
| 0:09 | 2.0025 | 0.041616
| 0:09 | 2.0028 | 0.041706
| 0:09 | 2.0031 | 0.041803
| 0:09 | 2.0033 | 0.041908
| 0:09 | 2.0036 | 0.042022
| 0:09 | 2.0039 | 0.042142
| 0:09 | 2.0042 | 0.042267
| 0:09 | 2.0044 | 0.042398
| 0:09 | 2.0047 | 0.042534
| 0:09 | 2.005 | 0.042675
| 0:09 | 2.0053 | 0.042821
| 0:09 | 2.0056 | 0.042973
| 0:09 | 2.0058 | 0.04313
| 0:09 | 2.0061 | 0.043285
| 0:09 | 2.0064 | 0.043439
| 0:09 | 2.0067 | 0.043589
| 0:09 | 2.0069 | 0.043738
| 0:09 | 2.0072 | 0.043884
| 0:09 | 2.0075 | 0.044027
| 0:09 | 2.0078 | 0.044169
| 0:09 | 2.0081 | 0.044308
| 0:09 | 2.0083 | 0.044444
| 0:09 | 2.0086 | 0.044578
| 0:09 | 2.0089 | 0.04471
| 0:09 | 2.0092 | 0.04484
| 0:09 | 2.0094 | 0.044966
| 0:09 | 2.0097 | 0.04509
| 0:09 | 2.01 | 0.045214
| 0:09 | 2.0103 | 0.04534
| 0:09 | 2.0106 | 0.045467
| 0:09 | 2.0108 | 0.045594
| 0:09 | 2.0111 | 0.045723
| 0:09 | 2.0114 | 0.045852
| 0:10 | 2.0117 | 0.046003
| 0:10 | 2.0119 | 0.046159
| 0:10 | 2.0122 | 0.046325
| 0:10 | 2.0125 | 0.046499
| 0:10 | 2.0128 | 0.046677
| 0:10 | 2.0131 | 0.046861
| 0:10 | 2.0133 | 0.047049
| 0:10 | 2.0136 | 0.047242
| 0:10 | 2.0139 | 0.047441
| 0:10 | 2.0142 | 0.047644
| 0:10 | 2.0144 | 0.047852
| 0:10 | 2.0147 | 0.048061
| 0:10 | 2.015 | 0.048269
| 0:10 | 2.0153 | 0.048478
| 0:10 | 2.0156 | 0.048686
| 0:10 | 2.0158 | 0.048894
| 0:10 | 2.0161 | 0.049102
| 0:10 | 2.0164 | 0.04931
| 0:10 | 2.0167 | 0.049517
| 0:10 | 2.0169 | 0.049725
| 0:10 | 2.0172 | 0.049932
| 0:10 | 2.0175 | 0.050139
| 0:10 | 2.0178 | 0.050346
| 0:10 | 2.0181 | 0.050553
| 0:10 | 2.0183 | 0.050759
| 0:10 | 2.0186 | 0.050966
| 0:10 | 2.0189 | 0.051172
| 0:10 | 2.0192 | 0.051378
| 0:10 | 2.0194 | 0.051584
| 0:10 | 2.0197 | 0.05179
| 0:10 | 2.02 | 0.051995
| 0:10 | 2.0203 | 0.052201
| 0:10 | 2.0206 | 0.052406
| 0:10 | 2.0208 | 0.052611
| 0:10 | 2.0211 | 0.052816
| 0:10 | 2.0214 | 0.053021
| 0:10 | 2.0217 | 0.053226
| 0:10 | 2.0219 | 0.05343
| 0:10 | 2.0222 | 0.053634
| 0:10 | 2.0225 | 0.053839
| 0:10 | 2.0228 | 0.054043
| 0:10 | 2.0231 | 0.054247
| 0:10 | 2.0233 | 0.054451
| 0:10 | 2.0236 | 0.054656
| 0:10 | 2.0239 | 0.054861
| 0:10 | 2.0242 | 0.055066
| 0:10 | 2.0244 | 0.055271
| 0:10 | 2.0247 | 0.055476
| 0:10 | 2.025 | 0.055681
| 0:10 | 2.0253 | 0.055887
| 0:10 | 2.0256 | 0.056092
| 0:10 | 2.0258 | 0.056298
| 0:10 | 2.0261 | 0.056503
| 0:10 | 2.0264 | 0.056709
| 0:10 | 2.0267 | 0.056914
| 0:10 | 2.0269 | 0.057119
| 0:10 | 2.0272 | 0.057325
| 0:10 | 2.0275 | 0.05753
| 0:10 | 2.0278 | 0.057735
| 0:10 | 2.0281 | 0.057941
| 0:10 | 2.0283 | 0.058146
| 0:11 | 2.0286 | 0.058351
| 0:11 | 2.0289 | 0.058557
| 0:11 | 2.0292 | 0.058762
| 0:11 | 2.0294 | 0.058967
| 0:11 | 2.0297 | 0.059173
| 0:11 | 2.03 | 0.059378
| 0:11 | 2.0303 | 0.059583
| 0:11 | 2.0306 | 0.059788
| 0:11 | 2.0308 | 0.059994
| 0:11 | 2.0311 | 0.060199
| 0:11 | 2.0314 | 0.060404
| 0:11 | 2.0317 | 0.060609
| 0:11 | 2.0319 | 0.060815
| 0:11 | 2.0322 | 0.06102
| 0:11 | 2.0325 | 0.061225
| 0:11 | 2.0328 | 0.06143
| 0:11 | 2.0331 | 0.061635
| 0:11 | 2.0333 | 0.06184
| 0:11 | 2.0336 | 0.062046
| 0:11 | 2.0339 | 0.062251
| 0:11 | 2.0342 | 0.062456
| 0:11 | 2.0344 | 0.062661
| 0:11 | 2.0347 | 0.062866
| 0:11 | 2.035 | 0.063071
| 0:11 | 2.0353 | 0.063276
| 0:11 | 2.0356 | 0.063481
| 0:11 | 2.0358 | 0.063686
| 0:11 | 2.0361 | 0.063891
| 0:11 | 2.0364 | 0.064096
| 0:11 | 2.0367 | 0.064302
| 0:11 | 2.0369 | 0.064507
| 0:11 | 2.0372 | 0.064712
| 0:11 | 2.0375 | 0.064917
| 0:11 | 2.0378 | 0.065122
| 0:11 | 2.0381 | 0.065327
| 0:11 | 2.0383 | 0.065532
| 0:11 | 2.0386 | 0.065737
| 0:11 | 2.0389 | 0.065942
| 0:11 | 2.0392 | 0.066147
| 0:11 | 2.0394 | 0.066351
| 0:11 | 2.0397 | 0.066556
| 0:11 | 2.04 | 0.066761
| 0:11 | 2.0403 | 0.066966
| 0:11 | 2.0406 | 0.067171
| 0:11 | 2.0408 | 0.067376
| 0:11 | 2.0411 | 0.067581
| 0:11 | 2.0414 | 0.067786
| 0:11 | 2.0417 | 0.067991
| 0:11 | 2.0419 | 0.068196
| 0:11 | 2.0422 | 0.0684
| 0:11 | 2.0425 | 0.068605
| 0:11 | 2.0428 | 0.06881
| 0:11 | 2.0431 | 0.069015
| 0:11 | 2.0433 | 0.06922
| 0:11 | 2.0436 | 0.069425
| 0:11 | 2.0439 | 0.069629
| 0:11 | 2.0442 | 0.069833
| 0:11 | 2.0444 | 0.070037
| 0:11 | 2.0447 | 0.070241
| 0:12 | 2.045 | 0.070445
| 0:12 | 2.0453 | 0.070648
| 0:12 | 2.0456 | 0.070851
| 0:12 | 2.0458 | 0.071054
| 0:12 | 2.0461 | 0.071257
| 0:12 | 2.0464 | 0.07146
| 0:12 | 2.0467 | 0.071662
| 0:12 | 2.0469 | 0.071864
| 0:12 | 2.0472 | 0.072066
| 0:12 | 2.0475 | 0.072268
| 0:12 | 2.0478 | 0.072469
| 0:12 | 2.0481 | 0.072671
| 0:12 | 2.0483 | 0.072872
| 0:12 | 2.0486 | 0.073073
| 0:12 | 2.0489 | 0.073274
| 0:12 | 2.0492 | 0.073474
| 0:12 | 2.0494 | 0.073675
| 0:12 | 2.0497 | 0.073875
| 0:12 | 2.05 | 0.074075
| 0:12 | 2.0503 | 0.074275
| 0:12 | 2.0506 | 0.074474
| 0:12 | 2.0508 | 0.074674
| 0:12 | 2.0511 | 0.074873
| 0:12 | 2.0514 | 0.075072
| 0:12 | 2.0517 | 0.075271
| 0:12 | 2.0519 | 0.075469
| 0:12 | 2.0522 | 0.075668
| 0:12 | 2.0525 | 0.075866
| 0:12 | 2.0528 | 0.076064
| 0:12 | 2.0531 | 0.076262
| 0:12 | 2.0533 | 0.076459
| 0:12 | 2.0536 | 0.076657
| 0:12 | 2.0539 | 0.076853
| 0:12 | 2.0542 | 0.077047
| 0:12 | 2.0544 | 0.07724
| 0:12 | 2.0547 | 0.077431
| 0:12 | 2.055 | 0.07762
| 0:12 | 2.0553 | 0.077807
| 0:12 | 2.0556 | 0.077992
| 0:12 | 2.0558 | 0.078176
| 0:12 | 2.0561 | 0.078359
| 0:12 | 2.0564 | 0.078542
| 0:12 | 2.0567 | 0.078726
| 0:12 | 2.0569 | 0.07891
| 0:12 | 2.0572 | 0.079095
| 0:12 | 2.0575 | 0.07928
| 0:12 | 2.0578 | 0.079465
| 0:12 | 2.0581 | 0.079651
| 0:12 | 2.0583 | 0.079837
| 0:12 | 2.0586 | 0.080023
| 0:12 | 2.0589 | 0.08021
| 0:12 | 2.0592 | 0.080397
| 0:12 | 2.0594 | 0.080585
| 0:12 | 2.0597 | 0.080773
| 0:12 | 2.06 | 0.080961
| 0:12 | 2.0603 | 0.081149
| 0:12 | 2.0606 | 0.081338
| 0:12 | 2.0608 | 0.081528
| 0:12 | 2.0611 | 0.081717
| 0:12 | 2.0614 | 0.081908
| 0:12 | 2.0617 | 0.082098
| 0:13 | 2.0619 | 0.082289
| 0:13 | 2.0622 | 0.08248
| 0:13 | 2.0625 | 0.082671
| 0:13 | 2.0628 | 0.082863
| 0:13 | 2.0631 | 0.083056
| 0:13 | 2.0633 | 0.083248
| 0:13 | 2.0636 | 0.083441
| 0:13 | 2.0639 | 0.083634
| 0:13 | 2.0642 | 0.083828
| 0:13 | 2.0644 | 0.084022
| 0:13 | 2.0647 | 0.084217
| 0:13 | 2.065 | 0.084413
| 0:13 | 2.0653 | 0.08461
| 0:13 | 2.0656 | 0.084807
| 0:13 | 2.0658 | 0.085006
| 0:13 | 2.0661 | 0.085206
| 0:13 | 2.0664 | 0.085407
| 0:13 | 2.0667 | 0.085608
| 0:13 | 2.0669 | 0.085811
| 0:13 | 2.0672 | 0.086014
| 0:13 | 2.0675 | 0.086219
| 0:13 | 2.0678 | 0.086425
| 0:13 | 2.0681 | 0.086631
| 0:13 | 2.0683 | 0.086839
| 0:13 | 2.0686 | 0.087048
| 0:13 | 2.0689 | 0.087261
| 0:13 | 2.0692 | 0.087477
| 0:13 | 2.0694 | 0.087696
| 0:13 | 2.0697 | 0.087918
| 0:13 | 2.07 | 0.088143
| 0:13 | 2.0703 | 0.088371
| 0:13 | 2.0706 | 0.088601
| 0:13 | 2.0708 | 0.088831
| 0:13 | 2.0711 | 0.089063
| 0:13 | 2.0714 | 0.089296
| 0:13 | 2.0717 | 0.089529
| 0:13 | 2.0719 | 0.089764
| 0:13 | 2.0722 | 0.09
| 0:13 | 2.0725 | 0.090236
| 0:13 | 2.0728 | 0.090473
| 0:13 | 2.0731 | 0.09071
| 0:13 | 2.0733 | 0.090946
| 0:13 | 2.0736 | 0.091183
| 0:13 | 2.0739 | 0.091419
| 0:13 | 2.0742 | 0.091655
| 0:13 | 2.0744 | 0.091892
| 0:13 | 2.0747 | 0.092127
| 0:13 | 2.075 | 0.092363
| 0:13 | 2.0753 | 0.092599
| 0:13 | 2.0756 | 0.092834
| 0:13 | 2.0758 | 0.09307
| 0:13 | 2.0761 | 0.093305
| 0:13 | 2.0764 | 0.09354
| 0:13 | 2.0767 | 0.093775
| 0:13 | 2.0769 | 0.09401
| 0:13 | 2.0772 | 0.094245
| 0:13 | 2.0775 | 0.094479
| 0:13 | 2.0778 | 0.094714
| 0:13 | 2.0781 | 0.094948
| 0:14 | 2.0783 | 0.095182
| 0:14 | 2.0786 | 0.095416
| 0:14 | 2.0789 | 0.095651
| 0:14 | 2.0792 | 0.095887
| 0:14 | 2.0794 | 0.096126
| 0:14 | 2.0797 | 0.096365
| 0:14 | 2.08 | 0.096607
| 0:14 | 2.0803 | 0.09685
| 0:14 | 2.0806 | 0.097095
| 0:14 | 2.0808 | 0.097342
| 0:14 | 2.0811 | 0.09759
| 0:14 | 2.0814 | 0.097839
| 0:14 | 2.0817 | 0.098087
| 0:14 | 2.0819 | 0.098336
| 0:14 | 2.0822 | 0.098586
| 0:14 | 2.0825 | 0.098835
| 0:14 | 2.0828 | 0.099085
| 0:14 | 2.0831 | 0.099334
| 0:14 | 2.0833 | 0.099584
| 0:14 | 2.0836 | 0.099835
| 0:14 | 2.0839 | 0.10009
| 0:14 | 2.0842 | 0.10034
| 0:14 | 2.0844 | 0.10059
| 0:14 | 2.0847 | 0.10084
| 0:14 | 2.085 | 0.10109
| 0:14 | 2.0853 | 0.10134
| 0:14 | 2.0856 | 0.10159
| 0:14 | 2.0858 | 0.10184
| 0:14 | 2.0861 | 0.1021
| 0:14 | 2.0864 | 0.10235
| 0:14 | 2.0867 | 0.1026
| 0:14 | 2.0869 | 0.10285
| 0:14 | 2.0872 | 0.10311
| 0:14 | 2.0875 | 0.10336
| 0:14 | 2.0878 | 0.10361
| 0:14 | 2.0881 | 0.10387
| 0:14 | 2.0883 | 0.10412
| 0:14 | 2.0886 | 0.10437
| 0:14 | 2.0889 | 0.10463
| 0:14 | 2.0892 | 0.10488
| 0:14 | 2.0894 | 0.10514
| 0:14 | 2.0897 | 0.10539
| 0:14 | 2.09 | 0.10565
| 0:14 | 2.0903 | 0.1059
| 0:14 | 2.0906 | 0.10616
| 0:14 | 2.0908 | 0.10641
| 0:14 | 2.0911 | 0.10667
| 0:14 | 2.0914 | 0.10693
| 0:14 | 2.0917 | 0.10718
| 0:14 | 2.0919 | 0.10744
| 0:14 | 2.0922 | 0.10769
| 0:14 | 2.0925 | 0.10795
| 0:14 | 2.0928 | 0.1082
| 0:14 | 2.0931 | 0.10846
| 0:14 | 2.0933 | 0.10872
| 0:14 | 2.0936 | 0.10897
| 0:14 | 2.0939 | 0.10923
| 0:14 | 2.0942 | 0.10948
| 0:14 | 2.0944 | 0.10974
| 0:14 | 2.0947 | 0.10999
| 0:15 | 2.095 | 0.11025
| 0:15 | 2.0953 | 0.1105
| 0:15 | 2.0956 | 0.11076
| 0:15 | 2.0958 | 0.11101
| 0:15 | 2.0961 | 0.11127
| 0:15 | 2.0964 | 0.11153
| 0:15 | 2.0967 | 0.1118
| 0:15 | 2.0969 | 0.11206
| 0:15 | 2.0972 | 0.11233
| 0:15 | 2.0975 | 0.11259
| 0:15 | 2.0978 | 0.11286
| 0:15 | 2.0981 | 0.11313
| 0:15 | 2.0983 | 0.1134
| 0:15 | 2.0986 | 0.11366
| 0:15 | 2.0989 | 0.11393
| 0:15 | 2.0992 | 0.11419
| 0:15 | 2.0994 | 0.11445
| 0:15 | 2.0997 | 0.11471
| 0:15 | 2.1 | 0.11497
| 0:15 | 2.1003 | 0.11523
| 0:15 | 2.1006 | 0.11549
| 0:15 | 2.1008 | 0.11575
| 0:15 | 2.1011 | 0.116
| 0:15 | 2.1014 | 0.11626
| 0:15 | 2.1017 | 0.11651
| 0:15 | 2.1019 | 0.11676
| 0:15 | 2.1022 | 0.11701
| 0:15 | 2.1025 | 0.11726
| 0:15 | 2.1028 | 0.11751
| 0:15 | 2.1031 | 0.11776
| 0:15 | 2.1033 | 0.11801
| 0:15 | 2.1036 | 0.11826
| 0:15 | 2.1039 | 0.1185
| 0:15 | 2.1042 | 0.11875
| 0:15 | 2.1044 | 0.11899
| 0:15 | 2.1047 | 0.11923
| 0:15 | 2.105 | 0.11947
| 0:15 | 2.1053 | 0.11971
| 0:15 | 2.1056 | 0.11994
| 0:15 | 2.1058 | 0.12017
| 0:15 | 2.1061 | 0.1204
| 0:15 | 2.1064 | 0.12063
| 0:15 | 2.1067 | 0.12086
| 0:15 | 2.1069 | 0.12109
| 0:15 | 2.1072 | 0.12132
| 0:15 | 2.1075 | 0.12155
| 0:15 | 2.1078 | 0.12178
| 0:15 | 2.1081 | 0.122
| 0:15 | 2.1083 | 0.12223
| 0:15 | 2.1086 | 0.12245
| 0:15 | 2.1089 | 0.12268
| 0:15 | 2.1092 | 0.1229
| 0:15 | 2.1094 | 0.12312
| 0:15 | 2.1097 | 0.12335
| 0:15 | 2.11 | 0.12357
| 0:15 | 2.1103 | 0.12379
| 0:15 | 2.1106 | 0.12401
| 0:15 | 2.1108 | 0.12423
| 0:15 | 2.1111 | 0.12444
| 0:15 | 2.1114 | 0.12466
| 0:16 | 2.1117 | 0.12487
| 0:16 | 2.1119 | 0.12508
| 0:16 | 2.1122 | 0.12528
| 0:16 | 2.1125 | 0.12548
| 0:16 | 2.1128 | 0.12569
| 0:16 | 2.1131 | 0.12589
| 0:16 | 2.1133 | 0.12609
| 0:16 | 2.1136 | 0.12629
| 0:16 | 2.1139 | 0.12649
| 0:16 | 2.1142 | 0.12669
| 0:16 | 2.1144 | 0.12689
| 0:16 | 2.1147 | 0.12709
| 0:16 | 2.115 | 0.12729
| 0:16 | 2.1153 | 0.12748
| 0:16 | 2.1156 | 0.12768
| 0:16 | 2.1158 | 0.12788
| 0:16 | 2.1161 | 0.12807
| 0:16 | 2.1164 | 0.12826
| 0:16 | 2.1167 | 0.12846
| 0:16 | 2.1169 | 0.12865
| 0:16 | 2.1172 | 0.12885
| 0:16 | 2.1175 | 0.12905
| 0:16 | 2.1178 | 0.12925
| 0:16 | 2.1181 | 0.12946
| 0:16 | 2.1183 | 0.12967
| 0:16 | 2.1186 | 0.12988
| 0:16 | 2.1189 | 0.13009
| 0:16 | 2.1192 | 0.13031
| 0:16 | 2.1194 | 0.13053
| 0:16 | 2.1197 | 0.13076
| 0:16 | 2.12 | 0.13099
| 0:16 | 2.1203 | 0.13122
| 0:16 | 2.1206 | 0.13145
| 0:16 | 2.1208 | 0.13169
| 0:16 | 2.1211 | 0.13192
| 0:16 | 2.1214 | 0.13216
| 0:16 | 2.1217 | 0.13239
| 0:16 | 2.1219 | 0.13263
| 0:16 | 2.1222 | 0.13287
| 0:16 | 2.1225 | 0.13311
| 0:16 | 2.1228 | 0.13335
| 0:16 | 2.1231 | 0.13358
| 0:16 | 2.1233 | 0.13382
| 0:16 | 2.1236 | 0.13406
| 0:16 | 2.1239 | 0.1343
| 0:16 | 2.1242 | 0.13453
| 0:16 | 2.1244 | 0.13477
| 0:16 | 2.1247 | 0.135
| 0:16 | 2.125 | 0.13524
| 0:16 | 2.1253 | 0.13547
| 0:16 | 2.1256 | 0.1357
| 0:16 | 2.1258 | 0.13594
| 0:16 | 2.1261 | 0.13617
| 0:16 | 2.1264 | 0.1364
| 0:16 | 2.1267 | 0.13663
| 0:16 | 2.1269 | 0.13687
| 0:16 | 2.1272 | 0.1371
| 0:16 | 2.1275 | 0.13733
| 0:16 | 2.1278 | 0.13756
| 0:16 | 2.1281 | 0.13779
| 0:16 | 2.1283 | 0.13801
| 0:17 | 2.1286 | 0.13824
| 0:17 | 2.1289 | 0.13847
| 0:17 | 2.1292 | 0.1387
| 0:17 | 2.1294 | 0.13892
| 0:17 | 2.1297 | 0.13915
| 0:17 | 2.13 | 0.13938
| 0:17 | 2.1303 | 0.1396
| 0:17 | 2.1306 | 0.13983
| 0:17 | 2.1308 | 0.14005
| 0:17 | 2.1311 | 0.14028
| 0:17 | 2.1314 | 0.1405
| 0:17 | 2.1317 | 0.14072
| 0:17 | 2.1319 | 0.14094
| 0:17 | 2.1322 | 0.14117
| 0:17 | 2.1325 | 0.14139
| 0:17 | 2.1328 | 0.14161
| 0:17 | 2.1331 | 0.14183
| 0:17 | 2.1333 | 0.14205
| 0:17 | 2.1336 | 0.14227
| 0:17 | 2.1339 | 0.14249
| 0:17 | 2.1342 | 0.14271
| 0:17 | 2.1344 | 0.14293
| 0:17 | 2.1347 | 0.14315
| 0:17 | 2.135 | 0.14337
| 0:17 | 2.1353 | 0.14359
| 0:17 | 2.1356 | 0.14381
| 0:17 | 2.1358 | 0.14404
| 0:17 | 2.1361 | 0.14426
| 0:17 | 2.1364 | 0.14448
| 0:17 | 2.1367 | 0.1447
| 0:17 | 2.1369 | 0.14492
| 0:17 | 2.1372 | 0.14514
| 0:17 | 2.1375 | 0.14536
| 0:17 | 2.1378 | 0.14559
| 0:17 | 2.1381 | 0.14581
| 0:17 | 2.1383 | 0.14603
| 0:17 | 2.1386 | 0.14625
| 0:17 | 2.1389 | 0.14647
| 0:17 | 2.1392 | 0.1467
| 0:17 | 2.1394 | 0.14692
| 0:17 | 2.1397 | 0.14714
| 0:17 | 2.14 | 0.14736
| 0:17 | 2.1403 | 0.14759
| 0:17 | 2.1406 | 0.14781
| 0:17 | 2.1408 | 0.14803
| 0:17 | 2.1411 | 0.14825
| 0:17 | 2.1414 | 0.14848
| 0:17 | 2.1417 | 0.1487
| 0:17 | 2.1419 | 0.14892
| 0:17 | 2.1422 | 0.14915
| 0:17 | 2.1425 | 0.14937
| 0:17 | 2.1428 | 0.14959
| 0:17 | 2.1431 | 0.14982
| 0:17 | 2.1433 | 0.15004
| 0:17 | 2.1436 | 0.15027
| 0:17 | 2.1439 | 0.15049
| 0:17 | 2.1442 | 0.15071
| 0:17 | 2.1444 | 0.15094
| 0:17 | 2.1447 | 0.15116
| 0:18 | 2.145 | 0.15138
| 0:18 | 2.1453 | 0.1516
| 0:18 | 2.1456 | 0.15182
| 0:18 | 2.1458 | 0.15204
| 0:18 | 2.1461 | 0.15226
| 0:18 | 2.1464 | 0.15248
| 0:18 | 2.1467 | 0.1527
| 0:18 | 2.1469 | 0.15292
| 0:18 | 2.1472 | 0.15313
| 0:18 | 2.1475 | 0.15335
| 0:18 | 2.1478 | 0.15357
| 0:18 | 2.1481 | 0.15378
| 0:18 | 2.1483 | 0.154
| 0:18 | 2.1486 | 0.15421
| 0:18 | 2.1489 | 0.15443
| 0:18 | 2.1492 | 0.15464
| 0:18 | 2.1494 | 0.15486
| 0:18 | 2.1497 | 0.15507
| 0:18 | 2.15 | 0.15528
| 0:18 | 2.1503 | 0.15549
| 0:18 | 2.1506 | 0.1557
| 0:18 | 2.1508 | 0.15592
| 0:18 | 2.1511 | 0.15613
| 0:18 | 2.1514 | 0.15634
| 0:18 | 2.1517 | 0.15655
| 0:18 | 2.1519 | 0.15675
| 0:18 | 2.1522 | 0.15696
| 0:18 | 2.1525 | 0.15717
| 0:18 | 2.1528 | 0.15738
| 0:18 | 2.1531 | 0.15759
| 0:18 | 2.1533 | 0.15779
| 0:18 | 2.1536 | 0.158
| 0:18 | 2.1539 | 0.1582
| 0:18 | 2.1542 | 0.15841
| 0:18 | 2.1544 | 0.15861
| 0:18 | 2.1547 | 0.15882
| 0:18 | 2.155 | 0.15902
| 0:18 | 2.1553 | 0.15922
| 0:18 | 2.1556 | 0.15943
| 0:18 | 2.1558 | 0.15963
| 0:18 | 2.1561 | 0.15983
| 0:18 | 2.1564 | 0.16003
| 0:18 | 2.1567 | 0.16023
| 0:18 | 2.1569 | 0.16043
| 0:18 | 2.1572 | 0.16063
| 0:18 | 2.1575 | 0.16083
| 0:18 | 2.1578 | 0.16103
| 0:18 | 2.1581 | 0.16123
| 0:18 | 2.1583 | 0.16143
| 0:18 | 2.1586 | 0.16162
| 0:18 | 2.1589 | 0.16182
| 0:18 | 2.1592 | 0.16202
| 0:18 | 2.1594 | 0.16221
| 0:18 | 2.1597 | 0.16241
| 0:18 | 2.16 | 0.16261
| 0:18 | 2.1603 | 0.1628
| 0:18 | 2.1606 | 0.163
| 0:18 | 2.1608 | 0.16319
| 0:18 | 2.1611 | 0.16339
| 0:18 | 2.1614 | 0.16358
| 0:18 | 2.1617 | 0.16377
| 0:19 | 2.1619 | 0.16396
| 0:19 | 2.1622 | 0.16415
| 0:19 | 2.1625 | 0.16433
| 0:19 | 2.1628 | 0.16451
| 0:19 | 2.1631 | 0.16469
| 0:19 | 2.1633 | 0.16487
| 0:19 | 2.1636 | 0.16504
| 0:19 | 2.1639 | 0.16521
| 0:19 | 2.1642 | 0.16539
| 0:19 | 2.1644 | 0.16555
| 0:19 | 2.1647 | 0.16572
| 0:19 | 2.165 | 0.16589
| 0:19 | 2.1653 | 0.16605
| 0:19 | 2.1656 | 0.16622
| 0:19 | 2.1658 | 0.16638
| 0:19 | 2.1661 | 0.16655
| 0:19 | 2.1664 | 0.16671
| 0:19 | 2.1667 | 0.16688
| 0:19 | 2.1669 | 0.16704
| 0:19 | 2.1672 | 0.16721
| 0:19 | 2.1675 | 0.16737
| 0:19 | 2.1678 | 0.16753
| 0:19 | 2.1681 | 0.1677
| 0:19 | 2.1683 | 0.16786
| 0:19 | 2.1686 | 0.16802
| 0:19 | 2.1689 | 0.16818
| 0:19 | 2.1692 | 0.16834
| 0:19 | 2.1694 | 0.1685
| 0:19 | 2.1697 | 0.16867
| 0:19 | 2.17 | 0.16883
| 0:19 | 2.1703 | 0.16899
| 0:19 | 2.1706 | 0.16915
| 0:19 | 2.1708 | 0.16931
| 0:19 | 2.1711 | 0.16947
| 0:19 | 2.1714 | 0.16962
| 0:19 | 2.1717 | 0.16978
| 0:19 | 2.1719 | 0.16994
| 0:19 | 2.1722 | 0.1701
| 0:19 | 2.1725 | 0.17026
| 0:19 | 2.1728 | 0.17041
| 0:19 | 2.1731 | 0.17057
| 0:19 | 2.1733 | 0.17073
| 0:19 | 2.1736 | 0.17088
| 0:19 | 2.1739 | 0.17104
| 0:19 | 2.1742 | 0.1712
| 0:19 | 2.1744 | 0.17135
| 0:19 | 2.1747 | 0.17151
| 0:19 | 2.175 | 0.17166
| 0:19 | 2.1753 | 0.17181
| 0:19 | 2.1756 | 0.17197
| 0:19 | 2.1758 | 0.17212
| 0:19 | 2.1761 | 0.17228
| 0:19 | 2.1764 | 0.17243
| 0:19 | 2.1767 | 0.17258
| 0:19 | 2.1769 | 0.17273
| 0:19 | 2.1772 | 0.17289
| 0:19 | 2.1775 | 0.17304
| 0:19 | 2.1778 | 0.17319
| 0:19 | 2.1781 | 0.17334
| 0:20 | 2.1783 | 0.17349
| 0:20 | 2.1786 | 0.17364
| 0:20 | 2.1789 | 0.17379
| 0:20 | 2.1792 | 0.17394
| 0:20 | 2.1794 | 0.17409
| 0:20 | 2.1797 | 0.17424
| 0:20 | 2.18 | 0.17438
| 0:20 | 2.1803 | 0.17453
| 0:20 | 2.1806 | 0.17467
| 0:20 | 2.1808 | 0.17481
| 0:20 | 2.1811 | 0.17495
| 0:20 | 2.1814 | 0.17509
| 0:20 | 2.1817 | 0.17523
| 0:20 | 2.1819 | 0.17536
| 0:20 | 2.1822 | 0.1755
| 0:20 | 2.1825 | 0.17563
| 0:20 | 2.1828 | 0.17577
| 0:20 | 2.1831 | 0.1759
| 0:20 | 2.1833 | 0.17603
| 0:20 | 2.1836 | 0.17616
| 0:20 | 2.1839 | 0.17629
| 0:20 | 2.1842 | 0.17641
| 0:20 | 2.1844 | 0.17654
| 0:20 | 2.1847 | 0.17666
| 0:20 | 2.185 | 0.17678
| 0:20 | 2.1853 | 0.17691
| 0:20 | 2.1856 | 0.17703
| 0:20 | 2.1858 | 0.17714
| 0:20 | 2.1861 | 0.17726
| 0:20 | 2.1864 | 0.17737
| 0:20 | 2.1867 | 0.17748
| 0:20 | 2.1869 | 0.17759
| 0:20 | 2.1872 | 0.17769
| 0:20 | 2.1875 | 0.17779
| 0:20 | 2.1878 | 0.17789
| 0:20 | 2.1881 | 0.178
| 0:20 | 2.1883 | 0.1781
| 0:20 | 2.1886 | 0.17821
| 0:20 | 2.1889 | 0.17831
| 0:20 | 2.1892 | 0.17842
| 0:20 | 2.1894 | 0.17853
| 0:20 | 2.1897 | 0.17864
| 0:20 | 2.19 | 0.17875
| 0:20 | 2.1903 | 0.17886
| 0:20 | 2.1906 | 0.17897
| 0:20 | 2.1908 | 0.17909
| 0:20 | 2.1911 | 0.1792
| 0:20 | 2.1914 | 0.17932
| 0:20 | 2.1917 | 0.17944
| 0:20 | 2.1919 | 0.17956
| 0:20 | 2.1922 | 0.17968
| 0:20 | 2.1925 | 0.17981
| 0:20 | 2.1928 | 0.17994
| 0:20 | 2.1931 | 0.18007
| 0:20 | 2.1933 | 0.1802
| 0:20 | 2.1936 | 0.18033
| 0:20 | 2.1939 | 0.18047
| 0:20 | 2.1942 | 0.1806
| 0:20 | 2.1944 | 0.18073
| 0:20 | 2.1947 | 0.18086
| 0:20 | 2.195 | 0.18099
| 0:21 | 2.1953 | 0.18112
| 0:21 | 2.1956 | 0.18126
| 0:21 | 2.1958 | 0.18139
| 0:21 | 2.1961 | 0.18152
| 0:21 | 2.1964 | 0.18165
| 0:21 | 2.1967 | 0.18178
| 0:21 | 2.1969 | 0.18192
| 0:21 | 2.1972 | 0.18205
| 0:21 | 2.1975 | 0.18218
| 0:21 | 2.1978 | 0.18231
| 0:21 | 2.1981 | 0.18245
| 0:21 | 2.1983 | 0.18258
| 0:21 | 2.1986 | 0.18271
| 0:21 | 2.1989 | 0.18285
| 0:21 | 2.1992 | 0.18298
| 0:21 | 2.1994 | 0.18311
| 0:21 | 2.1997 | 0.18325
| 0:21 | 2.2 | 0.18338
| 0:21 | 2.2003 | 0.18351
| 0:21 | 2.2006 | 0.18365
| 0:21 | 2.2008 | 0.18378
| 0:21 | 2.2011 | 0.18391
| 0:21 | 2.2014 | 0.18405
| 0:21 | 2.2017 | 0.18418
| 0:21 | 2.2019 | 0.18431
| 0:21 | 2.2022 | 0.18445
| 0:21 | 2.2025 | 0.18458
| 0:21 | 2.2028 | 0.18472
| 0:21 | 2.2031 | 0.18485
| 0:21 | 2.2033 | 0.18499
| 0:21 | 2.2036 | 0.18512
| 0:21 | 2.2039 | 0.18525
| 0:21 | 2.2042 | 0.18539
| 0:21 | 2.2044 | 0.18552
| 0:21 | 2.2047 | 0.18566
| 0:21 | 2.205 | 0.18579
| 0:21 | 2.2053 | 0.18593
| 0:21 | 2.2056 | 0.18606
| 0:21 | 2.2058 | 0.1862
| 0:21 | 2.2061 | 0.18633
| 0:21 | 2.2064 | 0.18647
| 0:21 | 2.2067 | 0.18661
| 0:21 | 2.2069 | 0.18674
| 0:21 | 2.2072 | 0.18688
| 0:21 | 2.2075 | 0.18701
| 0:21 | 2.2078 | 0.18715
| 0:21 | 2.2081 | 0.18728
| 0:21 | 2.2083 | 0.18742
| 0:21 | 2.2086 | 0.18755
| 0:21 | 2.2089 | 0.18768
| 0:21 | 2.2092 | 0.18782
| 0:21 | 2.2094 | 0.18795
| 0:21 | 2.2097 | 0.18808
| 0:21 | 2.21 | 0.18821
| 0:21 | 2.2103 | 0.18834
| 0:21 | 2.2106 | 0.18847
| 0:21 | 2.2108 | 0.1886
| 0:21 | 2.2111 | 0.18873
| 0:21 | 2.2114 | 0.18886
| 0:22 | 2.2117 | 0.18899
| 0:22 | 2.2119 | 0.18912
| 0:22 | 2.2122 | 0.18925
| 0:22 | 2.2125 | 0.18938
| 0:22 | 2.2128 | 0.1895
| 0:22 | 2.2131 | 0.18963
| 0:22 | 2.2133 | 0.18976
| 0:22 | 2.2136 | 0.18988
| 0:22 | 2.2139 | 0.19001
| 0:22 | 2.2142 | 0.19013
| 0:22 | 2.2144 | 0.19026
| 0:22 | 2.2147 | 0.19038
| 0:22 | 2.215 | 0.19051
| 0:22 | 2.2153 | 0.19064
| 0:22 | 2.2156 | 0.19076
| 0:22 | 2.2158 | 0.19089
| 0:22 | 2.2161 | 0.19102
| 0:22 | 2.2164 | 0.19115
| 0:22 | 2.2167 | 0.19127
| 0:22 | 2.2169 | 0.1914
| 0:22 | 2.2172 | 0.19153
| 0:22 | 2.2175 | 0.19166
| 0:22 | 2.2178 | 0.1918
| 0:22 | 2.2181 | 0.19193
| 0:22 | 2.2183 | 0.19206
| 0:22 | 2.2186 | 0.19219
| 0:22 | 2.2189 | 0.19233
| 0:22 | 2.2192 | 0.19246
| 0:22 | 2.2194 | 0.19259
| 0:22 | 2.2197 | 0.19273
| 0:22 | 2.22 | 0.19286
| 0:22 | 2.2203 | 0.193
| 0:22 | 2.2206 | 0.19314
| 0:22 | 2.2208 | 0.19327
| 0:22 | 2.2211 | 0.19341
| 0:22 | 2.2214 | 0.19355
| 0:22 | 2.2217 | 0.19369
| 0:22 | 2.2219 | 0.19383
| 0:22 | 2.2222 | 0.19397
| 0:22 | 2.2225 | 0.19411
| 0:22 | 2.2228 | 0.19425
| 0:22 | 2.2231 | 0.19439
| 0:22 | 2.2233 | 0.19453
| 0:22 | 2.2236 | 0.19468
| 0:22 | 2.2239 | 0.19482
| 0:22 | 2.2242 | 0.19497
| 0:22 | 2.2244 | 0.19511
| 0:22 | 2.2247 | 0.19526
| 0:22 | 2.225 | 0.19541
| 0:22 | 2.2253 | 0.19555
| 0:22 | 2.2256 | 0.1957
| 0:22 | 2.2258 | 0.19586
| 0:22 | 2.2261 | 0.19601
| 0:22 | 2.2264 | 0.19616
| 0:22 | 2.2267 | 0.19631
| 0:22 | 2.2269 | 0.19646
| 0:22 | 2.2272 | 0.19662
| 0:22 | 2.2275 | 0.19677
| 0:22 | 2.2278 | 0.19693
| 0:22 | 2.2281 | 0.19708
| 0:22 | 2.2283 | 0.19724
| 0:23 | 2.2286 | 0.19739
| 0:23 | 2.2289 | 0.19755
| 0:23 | 2.2292 | 0.19771
| 0:23 | 2.2294 | 0.19787
| 0:23 | 2.2297 | 0.19802
| 0:23 | 2.23 | 0.19818
| 0:23 | 2.2303 | 0.19834
| 0:23 | 2.2306 | 0.1985
| 0:23 | 2.2308 | 0.19866
| 0:23 | 2.2311 | 0.19882
| 0:23 | 2.2314 | 0.19898
| 0:23 | 2.2317 | 0.19915
| 0:23 | 2.2319 | 0.19932
| 0:23 | 2.2322 | 0.19949
| 0:23 | 2.2325 | 0.19967
| 0:23 | 2.2328 | 0.19985
| 0:23 | 2.2331 | 0.20002
| 0:23 | 2.2333 | 0.2002
| 0:23 | 2.2336 | 0.20038
| 0:23 | 2.2339 | 0.20055
| 0:23 | 2.2342 | 0.20073
| 0:23 | 2.2344 | 0.2009
| 0:23 | 2.2347 | 0.20108
| 0:23 | 2.235 | 0.20125
| 0:23 | 2.2353 | 0.20142
| 0:23 | 2.2356 | 0.20159
| 0:23 | 2.2358 | 0.20176
| 0:23 | 2.2361 | 0.20193
| 0:23 | 2.2364 | 0.2021
| 0:23 | 2.2367 | 0.20227
| 0:23 | 2.2369 | 0.20244
| 0:23 | 2.2372 | 0.20261
| 0:23 | 2.2375 | 0.20278
| 0:23 | 2.2378 | 0.20295
| 0:23 | 2.2381 | 0.20313
| 0:23 | 2.2383 | 0.20331
| 0:23 | 2.2386 | 0.20348
| 0:23 | 2.2389 | 0.20367
| 0:23 | 2.2392 | 0.20385
| 0:23 | 2.2394 | 0.20403
| 0:23 | 2.2397 | 0.20422
| 0:23 | 2.24 | 0.20441
| 0:23 | 2.2403 | 0.2046
| 0:23 | 2.2406 | 0.20479
| 0:23 | 2.2408 | 0.20498
| 0:23 | 2.2411 | 0.20517
| 0:23 | 2.2414 | 0.20536
| 0:23 | 2.2417 | 0.20555
| 0:23 | 2.2419 | 0.20573
| 0:23 | 2.2422 | 0.20592
| 0:23 | 2.2425 | 0.2061
| 0:23 | 2.2428 | 0.20628
| 0:23 | 2.2431 | 0.20646
| 0:23 | 2.2433 | 0.20664
| 0:23 | 2.2436 | 0.20681
| 0:23 | 2.2439 | 0.20698
| 0:23 | 2.2442 | 0.20716
| 0:23 | 2.2444 | 0.20733
| 0:23 | 2.2447 | 0.2075
| 0:24 | 2.245 | 0.20766
| 0:24 | 2.2453 | 0.20783
| 0:24 | 2.2456 | 0.20799
| 0:24 | 2.2458 | 0.20815
| 0:24 | 2.2461 | 0.20831
| 0:24 | 2.2464 | 0.20846
| 0:24 | 2.2467 | 0.20861
| 0:24 | 2.2469 | 0.20875
| 0:24 | 2.2472 | 0.20889
| 0:24 | 2.2475 | 0.20903
| 0:24 | 2.2478 | 0.20916
| 0:24 | 2.2481 | 0.2093
| 0:24 | 2.2483 | 0.20943
| 0:24 | 2.2486 | 0.20956
| 0:24 | 2.2489 | 0.20969
| 0:24 | 2.2492 | 0.20982
| 0:24 | 2.2494 | 0.20996
| 0:24 | 2.2497 | 0.21009
| 0:24 | 2.25 | 0.21022
| 0:24 | 2.2503 | 0.21035
| 0:24 | 2.2506 | 0.21048
| 0:24 | 2.2508 | 0.21061
| 0:24 | 2.2511 | 0.21074
| 0:24 | 2.2514 | 0.21086
| 0:24 | 2.2517 | 0.21099
| 0:24 | 2.2519 | 0.21111
| 0:24 | 2.2522 | 0.21123
| 0:24 | 2.2525 | 0.21134
| 0:24 | 2.2528 | 0.21144
| 0:24 | 2.2531 | 0.21154
| 0:24 | 2.2533 | 0.21163
| 0:24 | 2.2536 | 0.21171
| 0:24 | 2.2539 | 0.21179
| 0:24 | 2.2542 | 0.21186
| 0:24 | 2.2544 | 0.21192
| 0:24 | 2.2547 | 0.21198
| 0:24 | 2.255 | 0.21204
| 0:24 | 2.2553 | 0.21209
| 0:24 | 2.2556 | 0.21214
| 0:24 | 2.2558 | 0.21218
| 0:24 | 2.2561 | 0.21222
| 0:24 | 2.2564 | 0.21226
| 0:24 | 2.2567 | 0.21231
| 0:24 | 2.2569 | 0.21236
| 0:24 | 2.2572 | 0.21241
| 0:24 | 2.2575 | 0.21247
| 0:24 | 2.2578 | 0.21253
| 0:24 | 2.2581 | 0.21259
| 0:24 | 2.2583 | 0.21266
| 0:24 | 2.2586 | 0.21273
| 0:24 | 2.2589 | 0.21282
| 0:24 | 2.2592 | 0.21292
| 0:24 | 2.2594 | 0.21302
| 0:24 | 2.2597 | 0.21313
| 0:24 | 2.26 | 0.21325
| 0:24 | 2.2603 | 0.21338
| 0:24 | 2.2606 | 0.21351
| 0:24 | 2.2608 | 0.21365
| 0:24 | 2.2611 | 0.21379
| 0:24 | 2.2614 | 0.21393
| 0:24 | 2.2617 | 0.21405
| 0:25 | 2.2619 | 0.21417
| 0:25 | 2.2622 | 0.21428
| 0:25 | 2.2625 | 0.21439
| 0:25 | 2.2628 | 0.21449
| 0:25 | 2.2631 | 0.21459
| 0:25 | 2.2633 | 0.21468
| 0:25 | 2.2636 | 0.21477
| 0:25 | 2.2639 | 0.21486
| 0:25 | 2.2642 | 0.21494
| 0:25 | 2.2644 | 0.21502
| 0:25 | 2.2647 | 0.2151
| 0:25 | 2.265 | 0.21518
| 0:25 | 2.2653 | 0.21526
| 0:25 | 2.2656 | 0.21534
| 0:25 | 2.2658 | 0.21543
| 0:25 | 2.2661 | 0.21551
| 0:25 | 2.2664 | 0.21559
| 0:25 | 2.2667 | 0.21568
| 0:25 | 2.2669 | 0.21576
| 0:25 | 2.2672 | 0.21585
| 0:25 | 2.2675 | 0.21593
| 0:25 | 2.2678 | 0.21602
| 0:25 | 2.2681 | 0.21611
| 0:25 | 2.2683 | 0.2162
| 0:25 | 2.2686 | 0.21628
| 0:25 | 2.2689 | 0.21637
| 0:25 | 2.2692 | 0.21646
| 0:25 | 2.2694 | 0.21654
| 0:25 | 2.2697 | 0.21662
| 0:25 | 2.27 | 0.21671
| 0:25 | 2.2703 | 0.21679
| 0:25 | 2.2706 | 0.21687
| 0:25 | 2.2708 | 0.21695
| 0:25 | 2.2711 | 0.21703
| 0:25 | 2.2714 | 0.21711
| 0:25 | 2.2717 | 0.21718
| 0:25 | 2.2719 | 0.21726
| 0:25 | 2.2722 | 0.21733
| 0:25 | 2.2725 | 0.21741
| 0:25 | 2.2728 | 0.21748
| 0:25 | 2.2731 | 0.21755
| 0:25 | 2.2733 | 0.21762
| 0:25 | 2.2736 | 0.21769
| 0:25 | 2.2739 | 0.21776
| 0:25 | 2.2742 | 0.21783
| 0:25 | 2.2744 | 0.2179
| 0:25 | 2.2747 | 0.21796
| 0:25 | 2.275 | 0.21803
| 0:25 | 2.2753 | 0.21808
| 0:25 | 2.2756 | 0.21813
| 0:25 | 2.2758 | 0.21818
| 0:25 | 2.2761 | 0.21822
| 0:25 | 2.2764 | 0.21825
| 0:25 | 2.2767 | 0.21828
| 0:25 | 2.2769 | 0.21831
| 0:25 | 2.2772 | 0.21833
| 0:25 | 2.2775 | 0.21834
| 0:25 | 2.2778 | 0.21835
| 0:25 | 2.2781 | 0.21835
| 0:26 | 2.2783 | 0.21835
| 0:26 | 2.2786 | 0.21834
| 0:26 | 2.2789 | 0.21833
| 0:26 | 2.2792 | 0.21831
| 0:26 | 2.2794 | 0.2183
| 0:26 | 2.2797 | 0.21828
| 0:26 | 2.28 | 0.21827
| 0:26 | 2.2803 | 0.21825
| 0:26 | 2.2806 | 0.21823
| 0:26 | 2.2808 | 0.21821
| 0:26 | 2.2811 | 0.21819
| 0:26 | 2.2814 | 0.21817
| 0:26 | 2.2817 | 0.21815
| 0:26 | 2.2819 | 0.21812
| 0:26 | 2.2822 | 0.2181
| 0:26 | 2.2825 | 0.21808
| 0:26 | 2.2828 | 0.21807
| 0:26 | 2.2831 | 0.21805
| 0:26 | 2.2833 | 0.21803
| 0:26 | 2.2836 | 0.21801
| 0:26 | 2.2839 | 0.21799
| 0:26 | 2.2842 | 0.21797
| 0:26 | 2.2844 | 0.21796
| 0:26 | 2.2847 | 0.21794
| 0:26 | 2.285 | 0.21792
| 0:26 | 2.2853 | 0.21791
| 0:26 | 2.2856 | 0.21789
| 0:26 | 2.2858 | 0.21787
| 0:26 | 2.2861 | 0.21786
| 0:26 | 2.2864 | 0.21784
| 0:26 | 2.2867 | 0.21783
| 0:26 | 2.2869 | 0.21781
| 0:26 | 2.2872 | 0.2178
| 0:26 | 2.2875 | 0.21779
| 0:26 | 2.2878 | 0.21778
| 0:26 | 2.2881 | 0.21777
| 0:26 | 2.2883 | 0.21776
| 0:26 | 2.2886 | 0.21776
| 0:26 | 2.2889 | 0.21775
| 0:26 | 2.2892 | 0.21775
| 0:26 | 2.2894 | 0.21775
| 0:26 | 2.2897 | 0.21775
| 0:26 | 2.29 | 0.21774
| 0:26 | 2.2903 | 0.21774
| 0:26 | 2.2906 | 0.21773
| 0:26 | 2.2908 | 0.21771
| 0:26 | 2.2911 | 0.2177
| 0:26 | 2.2914 | 0.21768
| 0:26 | 2.2917 | 0.21767
| 0:26 | 2.2919 | 0.21765
| 0:26 | 2.2922 | 0.21763
| 0:26 | 2.2925 | 0.21761
| 0:26 | 2.2928 | 0.21759
| 0:26 | 2.2931 | 0.21757
| 0:26 | 2.2933 | 0.21754
| 0:26 | 2.2936 | 0.21752
| 0:26 | 2.2939 | 0.2175
| 0:26 | 2.2942 | 0.21747
| 0:26 | 2.2944 | 0.21745
| 0:26 | 2.2947 | 0.21742
| 0:26 | 2.295 | 0.2174
| 0:27 | 2.2953 | 0.21737
| 0:27 | 2.2956 | 0.21735
| 0:27 | 2.2958 | 0.21733
| 0:27 | 2.2961 | 0.21731
| 0:27 | 2.2964 | 0.21729
| 0:27 | 2.2967 | 0.21728
| 0:27 | 2.2969 | 0.21727
| 0:27 | 2.2972 | 0.21726
| 0:27 | 2.2975 | 0.21725
| 0:27 | 2.2978 | 0.21725
| 0:27 | 2.2981 | 0.21725
| 0:27 | 2.2983 | 0.21724
| 0:27 | 2.2986 | 0.21724
| 0:27 | 2.2989 | 0.21723
| 0:27 | 2.2992 | 0.21722
| 0:27 | 2.2994 | 0.21721
| 0:27 | 2.2997 | 0.21721
| 0:27 | 2.3 | 0.2172
| 0:27 | 2.3003 | 0.21719
| 0:27 | 2.3006 | 0.21717
| 0:27 | 2.3008 | 0.21716
| 0:27 | 2.3011 | 0.21715
| 0:27 | 2.3014 | 0.21713
| 0:27 | 2.3017 | 0.21712
| 0:27 | 2.3019 | 0.2171
| 0:27 | 2.3022 | 0.21709
| 0:27 | 2.3025 | 0.21707
| 0:27 | 2.3028 | 0.21705
| 0:27 | 2.3031 | 0.21703
| 0:27 | 2.3033 | 0.21701
| 0:27 | 2.3036 | 0.21699
| 0:27 | 2.3039 | 0.21697
| 0:27 | 2.3042 | 0.21695
| 0:27 | 2.3044 | 0.21693
| 0:27 | 2.3047 | 0.21691
| 0:27 | 2.305 | 0.2169
| 0:27 | 2.3053 | 0.21688
| 0:27 | 2.3056 | 0.21686
| 0:27 | 2.3058 | 0.21685
| 0:27 | 2.3061 | 0.21683
| 0:27 | 2.3064 | 0.21682
| 0:27 | 2.3067 | 0.2168
| 0:27 | 2.3069 | 0.21678
| 0:27 | 2.3072 | 0.21676
| 0:27 | 2.3075 | 0.21673
| 0:27 | 2.3078 | 0.21671
| 0:27 | 2.3081 | 0.21668
| 0:27 | 2.3083 | 0.21665
| 0:27 | 2.3086 | 0.21662
| 0:27 | 2.3089 | 0.21658
| 0:27 | 2.3092 | 0.21654
| 0:27 | 2.3094 | 0.2165
| 0:27 | 2.3097 | 0.21645
| 0:27 | 2.31 | 0.21641
| 0:27 | 2.3103 | 0.21636
| 0:27 | 2.3106 | 0.21632
| 0:27 | 2.3108 | 0.21627
| 0:27 | 2.3111 | 0.21622
| 0:27 | 2.3114 | 0.21617
| 0:28 | 2.3117 | 0.21612
| 0:28 | 2.3119 | 0.21607
| 0:28 | 2.3122 | 0.21602
| 0:28 | 2.3125 | 0.21597
| 0:28 | 2.3128 | 0.21592
| 0:28 | 2.3131 | 0.21587
| 0:28 | 2.3133 | 0.21582
| 0:28 | 2.3136 | 0.21576
| 0:28 | 2.3139 | 0.21571
| 0:28 | 2.3142 | 0.21566
| 0:28 | 2.3144 | 0.2156
| 0:28 | 2.3147 | 0.21555
| 0:28 | 2.315 | 0.21549
| 0:28 | 2.3153 | 0.21543
| 0:28 | 2.3156 | 0.21537
| 0:28 | 2.3158 | 0.21531
| 0:28 | 2.3161 | 0.21525
| 0:28 | 2.3164 | 0.21518
| 0:28 | 2.3167 | 0.21512
| 0:28 | 2.3169 | 0.21505
| 0:28 | 2.3172 | 0.21499
| 0:28 | 2.3175 | 0.21492
| 0:28 | 2.3178 | 0.21485
| 0:28 | 2.3181 | 0.21478
| 0:28 | 2.3183 | 0.21471
| 0:28 | 2.3186 | 0.21463
| 0:28 | 2.3189 | 0.21456
| 0:28 | 2.3192 | 0.21448
| 0:28 | 2.3194 | 0.21439
| 0:28 | 2.3197 | 0.21431
| 0:28 | 2.32 | 0.21422
| 0:28 | 2.3203 | 0.21412
| 0:28 | 2.3206 | 0.21403
| 0:28 | 2.3208 | 0.21393
| 0:28 | 2.3211 | 0.21383
| 0:28 | 2.3214 | 0.21373
| 0:28 | 2.3217 | 0.21363
| 0:28 | 2.3219 | 0.21353
| 0:28 | 2.3222 | 0.21343
| 0:28 | 2.3225 | 0.21332
| 0:28 | 2.3228 | 0.21322
| 0:28 | 2.3231 | 0.21311
| 0:28 | 2.3233 | 0.21301
| 0:28 | 2.3236 | 0.2129
| 0:28 | 2.3239 | 0.2128
| 0:28 | 2.3242 | 0.21269
| 0:28 | 2.3244 | 0.21259
| 0:28 | 2.3247 | 0.21248
| 0:28 | 2.325 | 0.21238
| 0:28 | 2.3253 | 0.21227
| 0:28 | 2.3256 | 0.21217
| 0:28 | 2.3258 | 0.21206
| 0:28 | 2.3261 | 0.21195
| 0:28 | 2.3264 | 0.21185
| 0:28 | 2.3267 | 0.21174
| 0:28 | 2.3269 | 0.21164
| 0:28 | 2.3272 | 0.21153
| 0:28 | 2.3275 | 0.21142
| 0:28 | 2.3278 | 0.21132
| 0:28 | 2.3281 | 0.21121
| 0:28 | 2.3283 | 0.2111
| 0:29 | 2.3286 | 0.211
| 0:29 | 2.3289 | 0.21089
| 0:29 | 2.3292 | 0.21078
| 0:29 | 2.3294 | 0.21067
| 0:29 | 2.3297 | 0.21056
| 0:29 | 2.33 | 0.21044
| 0:29 | 2.3303 | 0.21032
| 0:29 | 2.3306 | 0.2102
| 0:29 | 2.3308 | 0.21008
| 0:29 | 2.3311 | 0.20996
| 0:29 | 2.3314 | 0.20984
| 0:29 | 2.3317 | 0.20971
| 0:29 | 2.3319 | 0.20959
| 0:29 | 2.3322 | 0.20946
| 0:29 | 2.3325 | 0.20934
| 0:29 | 2.3328 | 0.20921
| 0:29 | 2.3331 | 0.20908
| 0:29 | 2.3333 | 0.20896
| 0:29 | 2.3336 | 0.20883
| 0:29 | 2.3339 | 0.2087
| 0:29 | 2.3342 | 0.20858
| 0:29 | 2.3344 | 0.20845
| 0:29 | 2.3347 | 0.20832
| 0:29 | 2.335 | 0.20819
| 0:29 | 2.3353 | 0.20806
| 0:29 | 2.3356 | 0.20793
| 0:29 | 2.3358 | 0.2078
| 0:29 | 2.3361 | 0.20767
| 0:29 | 2.3364 | 0.20753
| 0:29 | 2.3367 | 0.2074
| 0:29 | 2.3369 | 0.20727
| 0:29 | 2.3372 | 0.20714
| 0:29 | 2.3375 | 0.207
| 0:29 | 2.3378 | 0.20687
| 0:29 | 2.3381 | 0.20674
| 0:29 | 2.3383 | 0.2066
| 0:29 | 2.3386 | 0.20647
| 0:29 | 2.3389 | 0.20633
| 0:29 | 2.3392 | 0.20619
| 0:29 | 2.3394 | 0.20606
| 0:29 | 2.3397 | 0.20592
| 0:29 | 2.34 | 0.20578
| 0:29 | 2.3403 | 0.20565
| 0:29 | 2.3406 | 0.20551
| 0:29 | 2.3408 | 0.20537
| 0:29 | 2.3411 | 0.20523
| 0:29 | 2.3414 | 0.20509
| 0:29 | 2.3417 | 0.20495
| 0:29 | 2.3419 | 0.20481
| 0:29 | 2.3422 | 0.20467
| 0:29 | 2.3425 | 0.20453
| 0:29 | 2.3428 | 0.20439
| 0:29 | 2.3431 | 0.20424
| 0:29 | 2.3433 | 0.2041
| 0:29 | 2.3436 | 0.20396
| 0:29 | 2.3439 | 0.20382
| 0:29 | 2.3442 | 0.20367
| 0:29 | 2.3444 | 0.20353
| 0:29 | 2.3447 | 0.20338
| 0:30 | 2.345 | 0.20324
| 0:30 | 2.3453 | 0.20309
| 0:30 | 2.3456 | 0.20295
| 0:30 | 2.3458 | 0.20279
| 0:30 | 2.3461 | 0.20264
| 0:30 | 2.3464 | 0.20248
| 0:30 | 2.3467 | 0.20232
| 0:30 | 2.3469 | 0.20215
| 0:30 | 2.3472 | 0.20198
| 0:30 | 2.3475 | 0.20181
| 0:30 | 2.3478 | 0.20163
| 0:30 | 2.3481 | 0.20146
| 0:30 | 2.3483 | 0.20129
| 0:30 | 2.3486 | 0.20112
| 0:30 | 2.3489 | 0.20095
| 0:30 | 2.3492 | 0.20079
| 0:30 | 2.3494 | 0.20062
| 0:30 | 2.3497 | 0.20046
| 0:30 | 2.35 | 0.20031
| 0:30 | 2.3503 | 0.20015
| 0:30 | 2.3506 | 0.2
| 0:30 | 2.3508 | 0.19984
| 0:30 | 2.3511 | 0.19969
| 0:30 | 2.3514 | 0.19954
| 0:30 | 2.3517 | 0.19938
| 0:30 | 2.3519 | 0.19923
| 0:30 | 2.3522 | 0.19908
| 0:30 | 2.3525 | 0.19893
| 0:30 | 2.3528 | 0.19878
| 0:30 | 2.3531 | 0.19863
| 0:30 | 2.3533 | 0.19848
| 0:30 | 2.3536 | 0.19833
| 0:30 | 2.3539 | 0.19818
| 0:30 | 2.3542 | 0.19803
| 0:30 | 2.3544 | 0.19789
| 0:30 | 2.3547 | 0.19774
| 0:30 | 2.355 | 0.1976
| 0:30 | 2.3553 | 0.19746
| 0:30 | 2.3556 | 0.19733
| 0:30 | 2.3558 | 0.19719
| 0:30 | 2.3561 | 0.19706
| 0:30 | 2.3564 | 0.19692
| 0:30 | 2.3567 | 0.19679
| 0:30 | 2.3569 | 0.19666
| 0:30 | 2.3572 | 0.19653
| 0:30 | 2.3575 | 0.1964
| 0:30 | 2.3578 | 0.19626
| 0:30 | 2.3581 | 0.19613
| 0:30 | 2.3583 | 0.19601
| 0:30 | 2.3586 | 0.19588
| 0:30 | 2.3589 | 0.19575
| 0:30 | 2.3592 | 0.19562
| 0:30 | 2.3594 | 0.19549
| 0:30 | 2.3597 | 0.19537
| 0:30 | 2.36 | 0.19524
| 0:30 | 2.3603 | 0.19511
| 0:30 | 2.3606 | 0.19499
| 0:30 | 2.3608 | 0.19486
| 0:30 | 2.3611 | 0.19472
| 0:30 | 2.3614 | 0.19459
| 0:30 | 2.3617 | 0.19445
| 0:31 | 2.3619 | 0.19431
| 0:31 | 2.3622 | 0.19417
| 0:31 | 2.3625 | 0.19402
| 0:31 | 2.3628 | 0.19388
| 0:31 | 2.3631 | 0.19373
| 0:31 | 2.3633 | 0.19358
| 0:31 | 2.3636 | 0.19343
| 0:31 | 2.3639 | 0.19328
| 0:31 | 2.3642 | 0.19312
| 0:31 | 2.3644 | 0.19297
| 0:31 | 2.3647 | 0.19281
| 0:31 | 2.365 | 0.19266
| 0:31 | 2.3653 | 0.1925
| 0:31 | 2.3656 | 0.19235
| 0:31 | 2.3658 | 0.1922
| 0:31 | 2.3661 | 0.19205
| 0:31 | 2.3664 | 0.19191
| 0:31 | 2.3667 | 0.19176
| 0:31 | 2.3669 | 0.19161
| 0:31 | 2.3672 | 0.19146
| 0:31 | 2.3675 | 0.19131
| 0:31 | 2.3678 | 0.19116
| 0:31 | 2.3681 | 0.19101
| 0:31 | 2.3683 | 0.19085
| 0:31 | 2.3686 | 0.19069
| 0:31 | 2.3689 | 0.19053
| 0:31 | 2.3692 | 0.19037
| 0:31 | 2.3694 | 0.1902
| 0:31 | 2.3697 | 0.19004
| 0:31 | 2.37 | 0.18987
| 0:31 | 2.3703 | 0.1897
| 0:31 | 2.3706 | 0.18953
| 0:31 | 2.3708 | 0.18936
| 0:31 | 2.3711 | 0.18919
| 0:31 | 2.3714 | 0.18902
| 0:31 | 2.3717 | 0.18886
| 0:31 | 2.3719 | 0.18869
| 0:31 | 2.3722 | 0.18852
| 0:31 | 2.3725 | 0.18836
| 0:31 | 2.3728 | 0.18819
| 0:31 | 2.3731 | 0.18803
| 0:31 | 2.3733 | 0.18786
| 0:31 | 2.3736 | 0.1877
| 0:31 | 2.3739 | 0.18754
| 0:31 | 2.3742 | 0.18737
| 0:31 | 2.3744 | 0.18721
| 0:31 | 2.3747 | 0.18705
| 0:31 | 2.375 | 0.18689
| 0:31 | 2.3753 | 0.18673
| 0:31 | 2.3756 | 0.18657
| 0:31 | 2.3758 | 0.18641
| 0:31 | 2.3761 | 0.18625
| 0:31 | 2.3764 | 0.1861
| 0:31 | 2.3767 | 0.18594
| 0:31 | 2.3769 | 0.18578
| 0:31 | 2.3772 | 0.18563
| 0:31 | 2.3775 | 0.18547
| 0:31 | 2.3778 | 0.18531
| 0:31 | 2.3781 | 0.18516
| 0:31 | 2.3783 | 0.18501
| 0:32 | 2.3786 | 0.18485
| 0:32 | 2.3789 | 0.18471
| 0:32 | 2.3792 | 0.18457
| 0:32 | 2.3794 | 0.18443
| 0:32 | 2.3797 | 0.1843
| 0:32 | 2.38 | 0.18417
| 0:32 | 2.3803 | 0.18405
| 0:32 | 2.3806 | 0.18394
| 0:32 | 2.3808 | 0.18383
| 0:32 | 2.3811 | 0.18372
| 0:32 | 2.3814 | 0.18361
| 0:32 | 2.3817 | 0.18351
| 0:32 | 2.3819 | 0.1834
| 0:32 | 2.3822 | 0.18328
| 0:32 | 2.3825 | 0.18317
| 0:32 | 2.3828 | 0.18304
| 0:32 | 2.3831 | 0.18292
| 0:32 | 2.3833 | 0.18278
| 0:32 | 2.3836 | 0.18264
| 0:32 | 2.3839 | 0.18251
| 0:32 | 2.3842 | 0.18237
| 0:32 | 2.3844 | 0.18224
| 0:32 | 2.3847 | 0.18211
| 0:32 | 2.385 | 0.18198
| 0:32 | 2.3853 | 0.18185
| 0:32 | 2.3856 | 0.18172
| 0:32 | 2.3858 | 0.1816
| 0:32 | 2.3861 | 0.18147
| 0:32 | 2.3864 | 0.18135
| 0:32 | 2.3867 | 0.18124
| 0:32 | 2.3869 | 0.18112
| 0:32 | 2.3872 | 0.18101
| 0:32 | 2.3875 | 0.1809
| 0:32 | 2.3878 | 0.18079
| 0:32 | 2.3881 | 0.18068
| 0:32 | 2.3883 | 0.18057
| 0:32 | 2.3886 | 0.18046
| 0:32 | 2.3889 | 0.18035
| 0:32 | 2.3892 | 0.18024
| 0:32 | 2.3894 | 0.18013
| 0:32 | 2.3897 | 0.18002
| 0:32 | 2.39 | 0.17991
| 0:32 | 2.3903 | 0.17981
| 0:32 | 2.3906 | 0.1797
| 0:32 | 2.3908 | 0.17959
| 0:32 | 2.3911 | 0.17949
| 0:32 | 2.3914 | 0.17938
| 0:32 | 2.3917 | 0.17927
| 0:32 | 2.3919 | 0.17917
| 0:32 | 2.3922 | 0.17906
| 0:32 | 2.3925 | 0.17896
| 0:32 | 2.3928 | 0.17885
| 0:32 | 2.3931 | 0.17875
| 0:32 | 2.3933 | 0.17865
| 0:32 | 2.3936 | 0.17854
| 0:32 | 2.3939 | 0.17844
| 0:32 | 2.3942 | 0.17834
| 0:32 | 2.3944 | 0.17824
| 0:32 | 2.3947 | 0.17814
| 0:32 | 2.395 | 0.17805
| 0:33 | 2.3953 | 0.17797
| 0:33 | 2.3956 | 0.17789
| 0:33 | 2.3958 | 0.17781
| 0:33 | 2.3961 | 0.17774
| 0:33 | 2.3964 | 0.17767
| 0:33 | 2.3967 | 0.1776
| 0:33 | 2.3969 | 0.17754
| 0:33 | 2.3972 | 0.17748
| 0:33 | 2.3975 | 0.17742
| 0:33 | 2.3978 | 0.17737
| 0:33 | 2.3981 | 0.17732
| 0:33 | 2.3983 | 0.17727
| 0:33 | 2.3986 | 0.17722
| 0:33 | 2.3989 | 0.17717
| 0:33 | 2.3992 | 0.17712
| 0:33 | 2.3994 | 0.17708
| 0:33 | 2.3997 | 0.17703
| 0:33 | 2.4 | 0.17699
| 0:33 | 2.4003 | 0.17695
| 0:33 | 2.4006 | 0.17691
| 0:33 | 2.4008 | 0.17687
| 0:33 | 2.4011 | 0.17683
| 0:33 | 2.4014 | 0.17679
| 0:33 | 2.4017 | 0.17676
| 0:33 | 2.4019 | 0.17672
| 0:33 | 2.4022 | 0.17669
| 0:33 | 2.4025 | 0.17666
| 0:33 | 2.4028 | 0.17663
| 0:33 | 2.4031 | 0.1766
| 0:33 | 2.4033 | 0.17658
| 0:33 | 2.4036 | 0.17656
| 0:33 | 2.4039 | 0.17654
| 0:33 | 2.4042 | 0.17653
| 0:33 | 2.4044 | 0.17651
| 0:33 | 2.4047 | 0.1765
| 0:33 | 2.405 | 0.17648
| 0:33 | 2.4053 | 0.17647
| 0:33 | 2.4056 | 0.17646
| 0:33 | 2.4058 | 0.17645
| 0:33 | 2.4061 | 0.17644
| 0:33 | 2.4064 | 0.17643
| 0:33 | 2.4067 | 0.17642
| 0:33 | 2.4069 | 0.17641
| 0:33 | 2.4072 | 0.17641
| 0:33 | 2.4075 | 0.1764
| 0:33 | 2.4078 | 0.1764
| 0:33 | 2.4081 | 0.17639
| 0:33 | 2.4083 | 0.17639
| 0:33 | 2.4086 | 0.17639
| 0:33 | 2.4089 | 0.17639
| 0:33 | 2.4092 | 0.17639
| 0:33 | 2.4094 | 0.17639
| 0:33 | 2.4097 | 0.1764
| 0:33 | 2.41 | 0.1764
| 0:33 | 2.4103 | 0.17641
| 0:33 | 2.4106 | 0.17641
| 0:33 | 2.4108 | 0.17642
| 0:33 | 2.4111 | 0.17643
| 0:33 | 2.4114 | 0.17644
| 0:34 | 2.4117 | 0.17646
| 0:34 | 2.4119 | 0.17648
| 0:34 | 2.4122 | 0.1765
| 0:34 | 2.4125 | 0.17651
| 0:34 | 2.4128 | 0.17653
| 0:34 | 2.4131 | 0.17654
| 0:34 | 2.4133 | 0.17656
| 0:34 | 2.4136 | 0.17657
| 0:34 | 2.4139 | 0.17658
| 0:34 | 2.4142 | 0.17659
| 0:34 | 2.4144 | 0.1766
| 0:34 | 2.4147 | 0.17661
| 0:34 | 2.415 | 0.17662
| 0:34 | 2.4153 | 0.17664
| 0:34 | 2.4156 | 0.17665
| 0:34 | 2.4158 | 0.17666
| 0:34 | 2.4161 | 0.17667
| 0:34 | 2.4164 | 0.17668
| 0:34 | 2.4167 | 0.17669
| 0:34 | 2.4169 | 0.1767
| 0:34 | 2.4172 | 0.17672
| 0:34 | 2.4175 | 0.17673
| 0:34 | 2.4178 | 0.17674
| 0:34 | 2.4181 | 0.17675
| 0:34 | 2.4183 | 0.17676
| 0:34 | 2.4186 | 0.17678
| 0:34 | 2.4189 | 0.17679
| 0:34 | 2.4192 | 0.1768
| 0:34 | 2.4194 | 0.17682
| 0:34 | 2.4197 | 0.17683
| 0:34 | 2.42 | 0.17684
| 0:34 | 2.4203 | 0.17685
| 0:34 | 2.4206 | 0.17687
| 0:34 | 2.4208 | 0.17688
| 0:34 | 2.4211 | 0.1769
| 0:34 | 2.4214 | 0.17691
| 0:34 | 2.4217 | 0.17692
| 0:34 | 2.4219 | 0.17694
| 0:34 | 2.4222 | 0.17695
| 0:34 | 2.4225 | 0.17697
| 0:34 | 2.4228 | 0.17698
| 0:34 | 2.4231 | 0.177
| 0:34 | 2.4233 | 0.17701
| 0:34 | 2.4236 | 0.17703
| 0:34 | 2.4239 | 0.17704
| 0:34 | 2.4242 | 0.17706
| 0:34 | 2.4244 | 0.17707
| 0:34 | 2.4247 | 0.17709
| 0:34 | 2.425 | 0.1771
| 0:34 | 2.4253 | 0.17712
| 0:34 | 2.4256 | 0.17713
| 0:34 | 2.4258 | 0.17715
| 0:34 | 2.4261 | 0.17717
| 0:34 | 2.4264 | 0.17718
| 0:34 | 2.4267 | 0.1772
| 0:34 | 2.4269 | 0.17721
| 0:34 | 2.4272 | 0.17723
| 0:34 | 2.4275 | 0.17725
| 0:34 | 2.4278 | 0.17726
| 0:34 | 2.4281 | 0.17728
| 0:34 | 2.4283 | 0.1773
| 0:35 | 2.4286 | 0.17732
| 0:35 | 2.4289 | 0.17733
| 0:35 | 2.4292 | 0.17735
| 0:35 | 2.4294 | 0.17737
| 0:35 | 2.4297 | 0.17739
| 0:35 | 2.43 | 0.17741
| 0:35 | 2.4303 | 0.17744
| 0:35 | 2.4306 | 0.17746
| 0:35 | 2.4308 | 0.17748
| 0:35 | 2.4311 | 0.17751
| 0:35 | 2.4314 | 0.17754
| 0:35 | 2.4317 | 0.17756
| 0:35 | 2.4319 | 0.17759
| 0:35 | 2.4322 | 0.17762
| 0:35 | 2.4325 | 0.17765
| 0:35 | 2.4328 | 0.17769
| 0:35 | 2.4331 | 0.17772
| 0:35 | 2.4333 | 0.17775
| 0:35 | 2.4336 | 0.17779
| 0:35 | 2.4339 | 0.17782
| 0:35 | 2.4342 | 0.17785
| 0:35 | 2.4344 | 0.17789
| 0:35 | 2.4347 | 0.17792
| 0:35 | 2.435 | 0.17795
| 0:35 | 2.4353 | 0.17799
| 0:35 | 2.4356 | 0.17803
| 0:35 | 2.4358 | 0.17807
| 0:35 | 2.4361 | 0.17811
| 0:35 | 2.4364 | 0.17816
| 0:35 | 2.4367 | 0.17821
| 0:35 | 2.4369 | 0.17826
| 0:35 | 2.4372 | 0.17832
| 0:35 | 2.4375 | 0.17837
| 0:35 | 2.4378 | 0.17843
| 0:35 | 2.4381 | 0.17848
| 0:35 | 2.4383 | 0.17854
| 0:35 | 2.4386 | 0.17859
| 0:35 | 2.4389 | 0.17864
| 0:35 | 2.4392 | 0.17869
| 0:35 | 2.4394 | 0.17874
| 0:35 | 2.4397 | 0.17879
| 0:35 | 2.44 | 0.17884
| 0:35 | 2.4403 | 0.17889
| 0:35 | 2.4406 | 0.17894
| 0:35 | 2.4408 | 0.17898
| 0:35 | 2.4411 | 0.17903
| 0:35 | 2.4414 | 0.17907
| 0:35 | 2.4417 | 0.17911
| 0:35 | 2.4419 | 0.17915
| 0:35 | 2.4422 | 0.17919
| 0:35 | 2.4425 | 0.17922
| 0:35 | 2.4428 | 0.17925
| 0:35 | 2.4431 | 0.17927
| 0:35 | 2.4433 | 0.1793
| 0:35 | 2.4436 | 0.17933
| 0:35 | 2.4439 | 0.17936
| 0:35 | 2.4442 | 0.17939
| 0:35 | 2.4444 | 0.17942
| 0:35 | 2.4447 | 0.17945
| 0:36 | 2.445 | 0.17947
| 0:36 | 2.4453 | 0.1795
| 0:36 | 2.4456 | 0.17953
| 0:36 | 2.4458 | 0.17956
| 0:36 | 2.4461 | 0.17959
| 0:36 | 2.4464 | 0.17962
| 0:36 | 2.4467 | 0.17964
| 0:36 | 2.4469 | 0.17967
| 0:36 | 2.4472 | 0.1797
| 0:36 | 2.4475 | 0.17973
| 0:36 | 2.4478 | 0.17976
| 0:36 | 2.4481 | 0.17979
| 0:36 | 2.4483 | 0.17981
| 0:36 | 2.4486 | 0.17984
| 0:36 | 2.4489 | 0.17987
| 0:36 | 2.4492 | 0.1799
| 0:36 | 2.4494 | 0.17993
| 0:36 | 2.4497 | 0.17996
| 0:36 | 2.45 | 0.17998
| 0:36 | 2.4503 | 0.18001
| 0:36 | 2.4506 | 0.18004
| 0:36 | 2.4508 | 0.18007
| 0:36 | 2.4511 | 0.1801
| 0:36 | 2.4514 | 0.18013
| 0:36 | 2.4517 | 0.18015
| 0:36 | 2.4519 | 0.18018
| 0:36 | 2.4522 | 0.18021
| 0:36 | 2.4525 | 0.18024
| 0:36 | 2.4528 | 0.18027
| 0:36 | 2.4531 | 0.18029
| 0:36 | 2.4533 | 0.18032
| 0:36 | 2.4536 | 0.18035
| 0:36 | 2.4539 | 0.18038
| 0:36 | 2.4542 | 0.18041
| 0:36 | 2.4544 | 0.18044
| 0:36 | 2.4547 | 0.18047
| 0:36 | 2.455 | 0.1805
| 0:36 | 2.4553 | 0.18053
| 0:36 | 2.4556 | 0.18056
| 0:36 | 2.4558 | 0.1806
| 0:36 | 2.4561 | 0.18063
| 0:36 | 2.4564 | 0.18066
| 0:36 | 2.4567 | 0.18069
| 0:36 | 2.4569 | 0.18072
| 0:36 | 2.4572 | 0.18074
| 0:36 | 2.4575 | 0.18077
| 0:36 | 2.4578 | 0.18079
| 0:36 | 2.4581 | 0.18081
| 0:36 | 2.4583 | 0.18083
| 0:36 | 2.4586 | 0.18085
| 0:36 | 2.4589 | 0.18087
| 0:36 | 2.4592 | 0.18088
| 0:36 | 2.4594 | 0.1809
| 0:36 | 2.4597 | 0.18092
| 0:36 | 2.46 | 0.18093
| 0:36 | 2.4603 | 0.18095
| 0:36 | 2.4606 | 0.18097
| 0:36 | 2.4608 | 0.18099
| 0:36 | 2.4611 | 0.18101
| 0:36 | 2.4614 | 0.18102
| 0:36 | 2.4617 | 0.18104
| 0:37 | 2.4619 | 0.18106
| 0:37 | 2.4622 | 0.18108
| 0:37 | 2.4625 | 0.1811
| 0:37 | 2.4628 | 0.18112
| 0:37 | 2.4631 | 0.18114
| 0:37 | 2.4633 | 0.18116
| 0:37 | 2.4636 | 0.18118
| 0:37 | 2.4639 | 0.1812
| 0:37 | 2.4642 | 0.18122
| 0:37 | 2.4644 | 0.18124
| 0:37 | 2.4647 | 0.18126
| 0:37 | 2.465 | 0.18128
| 0:37 | 2.4653 | 0.1813
| 0:37 | 2.4656 | 0.18132
| 0:37 | 2.4658 | 0.18134
| 0:37 | 2.4661 | 0.18137
| 0:37 | 2.4664 | 0.18139
| 0:37 | 2.4667 | 0.18141
| 0:37 | 2.4669 | 0.18143
| 0:37 | 2.4672 | 0.18146
| 0:37 | 2.4675 | 0.18148
| 0:37 | 2.4678 | 0.1815
| 0:37 | 2.4681 | 0.18153
| 0:37 | 2.4683 | 0.18155
| 0:37 | 2.4686 | 0.18157
| 0:37 | 2.4689 | 0.1816
| 0:37 | 2.4692 | 0.18162
| 0:37 | 2.4694 | 0.18165
| 0:37 | 2.4697 | 0.18167
| 0:37 | 2.47 | 0.1817
| 0:37 | 2.4703 | 0.18172
| 0:37 | 2.4706 | 0.18175
| 0:37 | 2.4708 | 0.18177
| 0:37 | 2.4711 | 0.1818
| 0:37 | 2.4714 | 0.18183
| 0:37 | 2.4717 | 0.18185
| 0:37 | 2.4719 | 0.18188
| 0:37 | 2.4722 | 0.18191
| 0:37 | 2.4725 | 0.18193
| 0:37 | 2.4728 | 0.18196
| 0:37 | 2.4731 | 0.18199
| 0:37 | 2.4733 | 0.18201
| 0:37 | 2.4736 | 0.18204
| 0:37 | 2.4739 | 0.18206
| 0:37 | 2.4742 | 0.18208
| 0:37 | 2.4744 | 0.18211
| 0:37 | 2.4747 | 0.18213
| 0:37 | 2.475 | 0.18215
| 0:37 | 2.4753 | 0.18217
| 0:37 | 2.4756 | 0.18219
| 0:37 | 2.4758 | 0.18221
| 0:37 | 2.4761 | 0.18222
| 0:37 | 2.4764 | 0.18224
| 0:37 | 2.4767 | 0.18226
| 0:37 | 2.4769 | 0.18227
| 0:37 | 2.4772 | 0.18229
| 0:37 | 2.4775 | 0.1823
| 0:37 | 2.4778 | 0.18232
| 0:37 | 2.4781 | 0.18233
| 0:38 | 2.4783 | 0.18234
| 0:38 | 2.4786 | 0.18235
| 0:38 | 2.4789 | 0.18236
| 0:38 | 2.4792 | 0.18237
| 0:38 | 2.4794 | 0.18238
| 0:38 | 2.4797 | 0.18239
| 0:38 | 2.48 | 0.1824
| 0:38 | 2.4803 | 0.18241
| 0:38 | 2.4806 | 0.18241
| 0:38 | 2.4808 | 0.18242
| 0:38 | 2.4811 | 0.18242
| 0:38 | 2.4814 | 0.18243
| 0:38 | 2.4817 | 0.18243
| 0:38 | 2.4819 | 0.18242
| 0:38 | 2.4822 | 0.18241
| 0:38 | 2.4825 | 0.1824
| 0:38 | 2.4828 | 0.18239
| 0:38 | 2.4831 | 0.18237
| 0:38 | 2.4833 | 0.18236
| 0:38 | 2.4836 | 0.18235
| 0:38 | 2.4839 | 0.18233
| 0:38 | 2.4842 | 0.18232
| 0:38 | 2.4844 | 0.18231
| 0:38 | 2.4847 | 0.1823
| 0:38 | 2.485 | 0.18229
| 0:38 | 2.4853 | 0.18227
| 0:38 | 2.4856 | 0.18226
| 0:38 | 2.4858 | 0.18225
| 0:38 | 2.4861 | 0.18224
| 0:38 | 2.4864 | 0.18224
| 0:38 | 2.4867 | 0.18223
| 0:38 | 2.4869 | 0.18222
| 0:38 | 2.4872 | 0.18221
| 0:38 | 2.4875 | 0.1822
| 0:38 | 2.4878 | 0.1822
| 0:38 | 2.4881 | 0.18219
| 0:38 | 2.4883 | 0.18218
| 0:38 | 2.4886 | 0.18218
| 0:38 | 2.4889 | 0.18217
| 0:38 | 2.4892 | 0.18217
| 0:38 | 2.4894 | 0.18216
| 0:38 | 2.4897 | 0.18216
| 0:38 | 2.49 | 0.18216
| 0:38 | 2.4903 | 0.18215
| 0:38 | 2.4906 | 0.18215
| 0:38 | 2.4908 | 0.18215
| 0:38 | 2.4911 | 0.18215
| 0:38 | 2.4914 | 0.18215
| 0:38 | 2.4917 | 0.18215
| 0:38 | 2.4919 | 0.18215
| 0:38 | 2.4922 | 0.18216
| 0:38 | 2.4925 | 0.18216
| 0:38 | 2.4928 | 0.18216
| 0:38 | 2.4931 | 0.18215
| 0:38 | 2.4933 | 0.18215
| 0:38 | 2.4936 | 0.18215
| 0:38 | 2.4939 | 0.18215
| 0:38 | 2.4942 | 0.18214
| 0:38 | 2.4944 | 0.18213
| 0:38 | 2.4947 | 0.18213
| 0:38 | 2.495 | 0.18212
| 0:39 | 2.4953 | 0.18211
| 0:39 | 2.4956 | 0.1821
| 0:39 | 2.4958 | 0.18209
| 0:39 | 2.4961 | 0.18208
| 0:39 | 2.4964 | 0.18207
| 0:39 | 2.4967 | 0.18205
| 0:39 | 2.4969 | 0.18204
| 0:39 | 2.4972 | 0.18203
| 0:39 | 2.4975 | 0.18201
| 0:39 | 2.4978 | 0.182
| 0:39 | 2.4981 | 0.18198
| 0:39 | 2.4983 | 0.18196
| 0:39 | 2.4986 | 0.18194
| 0:39 | 2.4989 | 0.18192
| 0:39 | 2.4992 | 0.1819
| 0:39 | 2.4994 | 0.18188
| 0:39 | 2.4997 | 0.18185
| 0:39 | 2.5 | 0.18182
| 0:39 | 2.5003 | 0.1818
| 0:39 | 2.5006 | 0.18177
| 0:39 | 2.5008 | 0.18174
| 0:39 | 2.5011 | 0.1817
| 0:39 | 2.5014 | 0.18167
| 0:39 | 2.5017 | 0.18164
| 0:39 | 2.5019 | 0.1816
| 0:39 | 2.5022 | 0.18156
| 0:39 | 2.5025 | 0.18153
| 0:39 | 2.5028 | 0.18149
| 0:39 | 2.5031 | 0.18145
| 0:39 | 2.5033 | 0.1814
| 0:39 | 2.5036 | 0.18136
| 0:39 | 2.5039 | 0.18131
| 0:39 | 2.5042 | 0.18125
| 0:39 | 2.5044 | 0.18119
| 0:39 | 2.5047 | 0.18113
| 0:39 | 2.505 | 0.18106
| 0:39 | 2.5053 | 0.18099
| 0:39 | 2.5056 | 0.18091
| 0:39 | 2.5058 | 0.18083
| 0:39 | 2.5061 | 0.18075
| 0:39 | 2.5064 | 0.18066
| 0:39 | 2.5067 | 0.18058
| 0:39 | 2.5069 | 0.18049
| 0:39 | 2.5072 | 0.1804
| 0:39 | 2.5075 | 0.18032
| 0:39 | 2.5078 | 0.18023
| 0:39 | 2.5081 | 0.18014
| 0:39 | 2.5083 | 0.18004
| 0:39 | 2.5086 | 0.17994
| 0:39 | 2.5089 | 0.17983
| 0:39 | 2.5092 | 0.17971
| 0:39 | 2.5094 | 0.17958
| 0:39 | 2.5097 | 0.17945
| 0:39 | 2.51 | 0.17931
| 0:39 | 2.5103 | 0.17916
| 0:39 | 2.5106 | 0.17901
| 0:39 | 2.5108 | 0.17884
| 0:39 | 2.5111 | 0.17868
| 0:39 | 2.5114 | 0.17851
| 0:40 | 2.5117 | 0.17833
| 0:40 | 2.5119 | 0.17816
| 0:40 | 2.5122 | 0.17798
| 0:40 | 2.5125 | 0.1778
| 0:40 | 2.5128 | 0.17763
| 0:40 | 2.5131 | 0.17745
| 0:40 | 2.5133 | 0.17727
| 0:40 | 2.5136 | 0.17709
| 0:40 | 2.5139 | 0.17691
| 0:40 | 2.5142 | 0.17674
| 0:40 | 2.5144 | 0.17656
| 0:40 | 2.5147 | 0.17638
| 0:40 | 2.515 | 0.1762
| 0:40 | 2.5153 | 0.17602
| 0:40 | 2.5156 | 0.17584
| 0:40 | 2.5158 | 0.17566
| 0:40 | 2.5161 | 0.17548
| 0:40 | 2.5164 | 0.1753
| 0:40 | 2.5167 | 0.17512
| 0:40 | 2.5169 | 0.17494
| 0:40 | 2.5172 | 0.17476
| 0:40 | 2.5175 | 0.17458
| 0:40 | 2.5178 | 0.1744
| 0:40 | 2.5181 | 0.17422
| 0:40 | 2.5183 | 0.17403
| 0:40 | 2.5186 | 0.17385
| 0:40 | 2.5189 | 0.17368
| 0:40 | 2.5192 | 0.1735
| 0:40 | 2.5194 | 0.17332
| 0:40 | 2.5197 | 0.17315
| 0:40 | 2.52 | 0.17298
| 0:40 | 2.5203 | 0.17281
| 0:40 | 2.5206 | 0.17264
| 0:40 | 2.5208 | 0.17247
| 0:40 | 2.5211 | 0.1723
| 0:40 | 2.5214 | 0.17214
| 0:40 | 2.5217 | 0.17198
| 0:40 | 2.5219 | 0.17181
| 0:40 | 2.5222 | 0.17165
| 0:40 | 2.5225 | 0.1715
| 0:40 | 2.5228 | 0.17134
| 0:40 | 2.5231 | 0.17118
| 0:40 | 2.5233 | 0.17103
| 0:40 | 2.5236 | 0.17087
| 0:40 | 2.5239 | 0.17072
| 0:40 | 2.5242 | 0.17057
| 0:40 | 2.5244 | 0.17041
| 0:40 | 2.5247 | 0.17026
| 0:40 | 2.525 | 0.17012
| 0:40 | 2.5253 | 0.16998
| 0:40 | 2.5256 | 0.16984
| 0:40 | 2.5258 | 0.16971
| 0:40 | 2.5261 | 0.16959
| 0:40 | 2.5264 | 0.16947
| 0:40 | 2.5267 | 0.16936
| 0:40 | 2.5269 | 0.16926
| 0:40 | 2.5272 | 0.16915
| 0:40 | 2.5275 | 0.16906
| 0:40 | 2.5278 | 0.16897
| 0:40 | 2.5281 | 0.16889
| 0:40 | 2.5283 | 0.16881
| 0:41 | 2.5286 | 0.16874
| 0:41 | 2.5289 | 0.16867
| 0:41 | 2.5292 | 0.16859
| 0:41 | 2.5294 | 0.16852
| 0:41 | 2.5297 | 0.16844
| 0:41 | 2.53 | 0.16835
| 0:41 | 2.5303 | 0.16827
| 0:41 | 2.5306 | 0.16818
| 0:41 | 2.5308 | 0.16809
| 0:41 | 2.5311 | 0.168
| 0:41 | 2.5314 | 0.16791
| 0:41 | 2.5317 | 0.16782
| 0:41 | 2.5319 | 0.16774
| 0:41 | 2.5322 | 0.16766
| 0:41 | 2.5325 | 0.16758
| 0:41 | 2.5328 | 0.1675
| 0:41 | 2.5331 | 0.16742
| 0:41 | 2.5333 | 0.16734
| 0:41 | 2.5336 | 0.16726
| 0:41 | 2.5339 | 0.16717
| 0:41 | 2.5342 | 0.16709
| 0:41 | 2.5344 | 0.16701
| 0:41 | 2.5347 | 0.16693
| 0:41 | 2.535 | 0.16685
| 0:41 | 2.5353 | 0.16677
| 0:41 | 2.5356 | 0.16669
| 0:41 | 2.5358 | 0.1666
| 0:41 | 2.5361 | 0.16652
| 0:41 | 2.5364 | 0.16644
| 0:41 | 2.5367 | 0.16636
| 0:41 | 2.5369 | 0.16628
| 0:41 | 2.5372 | 0.16619
| 0:41 | 2.5375 | 0.16611
| 0:41 | 2.5378 | 0.16602
| 0:41 | 2.5381 | 0.16594
| 0:41 | 2.5383 | 0.16585
| 0:41 | 2.5386 | 0.16576
| 0:41 | 2.5389 | 0.16567
| 0:41 | 2.5392 | 0.16557
| 0:41 | 2.5394 | 0.16548
| 0:41 | 2.5397 | 0.16539
| 0:41 | 2.54 | 0.1653
| 0:41 | 2.5403 | 0.16521
| 0:41 | 2.5406 | 0.16513
| 0:41 | 2.5408 | 0.16504
| 0:41 | 2.5411 | 0.16497
| 0:41 | 2.5414 | 0.16489
| 0:41 | 2.5417 | 0.16481
| 0:41 | 2.5419 | 0.16474
| 0:41 | 2.5422 | 0.16467
| 0:41 | 2.5425 | 0.16459
| 0:41 | 2.5428 | 0.16452
| 0:41 | 2.5431 | 0.16446
| 0:41 | 2.5433 | 0.1644
| 0:41 | 2.5436 | 0.16435
| 0:41 | 2.5439 | 0.16431
| 0:41 | 2.5442 | 0.16427
| 0:41 | 2.5444 | 0.16423
| 0:41 | 2.5447 | 0.1642
| 0:42 | 2.545 | 0.16417
| 0:42 | 2.5453 | 0.16414
| 0:42 | 2.5456 | 0.16411
| 0:42 | 2.5458 | 0.16408
| 0:42 | 2.5461 | 0.16404
| 0:42 | 2.5464 | 0.164
| 0:42 | 2.5467 | 0.16395
| 0:42 | 2.5469 | 0.1639
| 0:42 | 2.5472 | 0.16384
| 0:42 | 2.5475 | 0.16378
| 0:42 | 2.5478 | 0.16371
| 0:42 | 2.5481 | 0.16364
| 0:42 | 2.5483 | 0.16357
| 0:42 | 2.5486 | 0.1635
| 0:42 | 2.5489 | 0.16343
| 0:42 | 2.5492 | 0.16336
| 0:42 | 2.5494 | 0.16328
| 0:42 | 2.5497 | 0.16321
| 0:42 | 2.55 | 0.16313
| 0:42 | 2.5503 | 0.16306
| 0:42 | 2.5506 | 0.16298
| 0:42 | 2.5508 | 0.16291
| 0:42 | 2.5511 | 0.16284
| 0:42 | 2.5514 | 0.16277
| 0:42 | 2.5517 | 0.1627
| 0:42 | 2.5519 | 0.16263
| 0:42 | 2.5522 | 0.16256
| 0:42 | 2.5525 | 0.1625
| 0:42 | 2.5528 | 0.16243
| 0:42 | 2.5531 | 0.16237
| 0:42 | 2.5533 | 0.16231
| 0:42 | 2.5536 | 0.16225
| 0:42 | 2.5539 | 0.16219
| 0:42 | 2.5542 | 0.16213
| 0:42 | 2.5544 | 0.16208
| 0:42 | 2.5547 | 0.16202
| 0:42 | 2.555 | 0.16197
| 0:42 | 2.5553 | 0.16191
| 0:42 | 2.5556 | 0.16186
| 0:42 | 2.5558 | 0.16181
| 0:42 | 2.5561 | 0.16176
| 0:42 | 2.5564 | 0.16172
| 0:42 | 2.5567 | 0.16167
| 0:42 | 2.5569 | 0.16163
| 0:42 | 2.5572 | 0.16158
| 0:42 | 2.5575 | 0.16154
| 0:42 | 2.5578 | 0.1615
| 0:42 | 2.5581 | 0.16146
| 0:42 | 2.5583 | 0.16142
| 0:42 | 2.5586 | 0.16139
| 0:42 | 2.5589 | 0.16136
| 0:42 | 2.5592 | 0.16134
| 0:42 | 2.5594 | 0.16131
| 0:42 | 2.5597 | 0.16129
| 0:42 | 2.56 | 0.16127
| 0:42 | 2.5603 | 0.16125
| 0:42 | 2.5606 | 0.16123
| 0:42 | 2.5608 | 0.16121
| 0:42 | 2.5611 | 0.16119
| 0:42 | 2.5614 | 0.16117
| 0:42 | 2.5617 | 0.16116
| 0:43 | 2.5619 | 0.16114
| 0:43 | 2.5622 | 0.16112
| 0:43 | 2.5625 | 0.1611
| 0:43 | 2.5628 | 0.16109
| 0:43 | 2.5631 | 0.16107
| 0:43 | 2.5633 | 0.16106
| 0:43 | 2.5636 | 0.16104
| 0:43 | 2.5639 | 0.16103
| 0:43 | 2.5642 | 0.16101
| 0:43 | 2.5644 | 0.161
| 0:43 | 2.5647 | 0.16099
| 0:43 | 2.565 | 0.16098
| 0:43 | 2.5653 | 0.16098
| 0:43 | 2.5656 | 0.16098
| 0:43 | 2.5658 | 0.16098
| 0:43 | 2.5661 | 0.16098
| 0:43 | 2.5664 | 0.16098
| 0:43 | 2.5667 | 0.16098
| 0:43 | 2.5669 | 0.16098
| 0:43 | 2.5672 | 0.16097
| 0:43 | 2.5675 | 0.16096
| 0:43 | 2.5678 | 0.16096
| 0:43 | 2.5681 | 0.16095
| 0:43 | 2.5683 | 0.16094
| 0:43 | 2.5686 | 0.16092
| 0:43 | 2.5689 | 0.16091
| 0:43 | 2.5692 | 0.16089
| 0:43 | 2.5694 | 0.16088
| 0:43 | 2.5697 | 0.16086
| 0:43 | 2.57 | 0.16084
| 0:43 | 2.5703 | 0.16082
| 0:43 | 2.5706 | 0.1608
| 0:43 | 2.5708 | 0.16077
| 0:43 | 2.5711 | 0.16075
| 0:43 | 2.5714 | 0.16073
| 0:43 | 2.5717 | 0.1607
| 0:43 | 2.5719 | 0.16068
| 0:43 | 2.5722 | 0.16065
| 0:43 | 2.5725 | 0.16063
| 0:43 | 2.5728 | 0.16061
| 0:43 | 2.5731 | 0.16059
| 0:43 | 2.5733 | 0.16057
| 0:43 | 2.5736 | 0.16056
| 0:43 | 2.5739 | 0.16055
| 0:43 | 2.5742 | 0.16054
| 0:43 | 2.5744 | 0.16053
| 0:43 | 2.5747 | 0.16053
| 0:43 | 2.575 | 0.16053
| 0:43 | 2.5753 | 0.16054
| 0:43 | 2.5756 | 0.16054
| 0:43 | 2.5758 | 0.16055
| 0:43 | 2.5761 | 0.16056
| 0:43 | 2.5764 | 0.16056
| 0:43 | 2.5767 | 0.16057
| 0:43 | 2.5769 | 0.16057
| 0:43 | 2.5772 | 0.16058
| 0:43 | 2.5775 | 0.16058
| 0:43 | 2.5778 | 0.16059
| 0:43 | 2.5781 | 0.16059
| 0:44 | 2.5783 | 0.16059
| 0:44 | 2.5786 | 0.1606
| 0:44 | 2.5789 | 0.1606
| 0:44 | 2.5792 | 0.1606
| 0:44 | 2.5794 | 0.1606
| 0:44 | 2.5797 | 0.1606
| 0:44 | 2.58 | 0.1606
| 0:44 | 2.5803 | 0.1606
| 0:44 | 2.5806 | 0.1606
| 0:44 | 2.5808 | 0.1606
| 0:44 | 2.5811 | 0.1606
| 0:44 | 2.5814 | 0.1606
| 0:44 | 2.5817 | 0.16059
| 0:44 | 2.5819 | 0.16059
| 0:44 | 2.5822 | 0.16059
| 0:44 | 2.5825 | 0.16058
| 0:44 | 2.5828 | 0.16058
| 0:44 | 2.5831 | 0.16058
| 0:44 | 2.5833 | 0.16057
| 0:44 | 2.5836 | 0.16056
| 0:44 | 2.5839 | 0.16056
| 0:44 | 2.5842 | 0.16055
| 0:44 | 2.5844 | 0.16054
| 0:44 | 2.5847 | 0.16054
| 0:44 | 2.585 | 0.16053
| 0:44 | 2.5853 | 0.16052
| 0:44 | 2.5856 | 0.16051
| 0:44 | 2.5858 | 0.1605
| 0:44 | 2.5861 | 0.16049
| 0:44 | 2.5864 | 0.16048
| 0:44 | 2.5867 | 0.16047
| 0:44 | 2.5869 | 0.16046
| 0:44 | 2.5872 | 0.16045
| 0:44 | 2.5875 | 0.16043
| 0:44 | 2.5878 | 0.16041
| 0:44 | 2.5881 | 0.16038
| 0:44 | 2.5883 | 0.16035
| 0:44 | 2.5886 | 0.16032
| 0:44 | 2.5889 | 0.16028
| 0:44 | 2.5892 | 0.16024
| 0:44 | 2.5894 | 0.1602
| 0:44 | 2.5897 | 0.16015
| 0:44 | 2.59 | 0.16009
| 0:44 | 2.5903 | 0.16004
| 0:44 | 2.5906 | 0.15998
| 0:44 | 2.5908 | 0.15992
| 0:44 | 2.5911 | 0.15987
| 0:44 | 2.5914 | 0.15981
| 0:44 | 2.5917 | 0.15975
| 0:44 | 2.5919 | 0.15969
| 0:44 | 2.5922 | 0.15963
| 0:44 | 2.5925 | 0.15958
| 0:44 | 2.5928 | 0.15952
| 0:44 | 2.5931 | 0.15946
| 0:44 | 2.5933 | 0.1594
| 0:44 | 2.5936 | 0.15934
| 0:44 | 2.5939 | 0.15928
| 0:44 | 2.5942 | 0.15922
| 0:44 | 2.5944 | 0.15916
| 0:44 | 2.5947 | 0.1591
| 0:44 | 2.595 | 0.15904
| 0:45 | 2.5953 | 0.15898
| 0:45 | 2.5956 | 0.15892
| 0:45 | 2.5958 | 0.15885
| 0:45 | 2.5961 | 0.15879
| 0:45 | 2.5964 | 0.15873
| 0:45 | 2.5967 | 0.15867
| 0:45 | 2.5969 | 0.15861
| 0:45 | 2.5972 | 0.15854
| 0:45 | 2.5975 | 0.15848
| 0:45 | 2.5978 | 0.15842
| 0:45 | 2.5981 | 0.15835
| 0:45 | 2.5983 | 0.15829
| 0:45 | 2.5986 | 0.15822
| 0:45 | 2.5989 | 0.15815
| 0:45 | 2.5992 | 0.15808
| 0:45 | 2.5994 | 0.15801
| 0:45 | 2.5997 | 0.15794
| 0:45 | 2.6 | 0.15787
| 0:45 | 2.6003 | 0.15779
| 0:45 | 2.6006 | 0.15772
| 0:45 | 2.6008 | 0.15764
| 0:45 | 2.6011 | 0.15757
| 0:45 | 2.6014 | 0.1575
| 0:45 | 2.6017 | 0.15743
| 0:45 | 2.6019 | 0.15736
| 0:45 | 2.6022 | 0.15729
| 0:45 | 2.6025 | 0.15722
| 0:45 | 2.6028 | 0.15715
| 0:45 | 2.6031 | 0.15708
| 0:45 | 2.6033 | 0.15701
| 0:45 | 2.6036 | 0.15695
| 0:45 | 2.6039 | 0.15688
| 0:45 | 2.6042 | 0.15682
| 0:45 | 2.6044 | 0.15675
| 0:45 | 2.6047 | 0.15669
| 0:45 | 2.605 | 0.15663
| 0:45 | 2.6053 | 0.15656
| 0:45 | 2.6056 | 0.1565
| 0:45 | 2.6058 | 0.15644
| 0:45 | 2.6061 | 0.15638
| 0:45 | 2.6064 | 0.15632
| 0:45 | 2.6067 | 0.15627
| 0:45 | 2.6069 | 0.15621
| 0:45 | 2.6072 | 0.15615
| 0:45 | 2.6075 | 0.1561
| 0:45 | 2.6078 | 0.15604
| 0:45 | 2.6081 | 0.15599
| 0:45 | 2.6083 | 0.15593
| 0:45 | 2.6086 | 0.15588
| 0:45 | 2.6089 | 0.15583
| 0:45 | 2.6092 | 0.15578
| 0:45 | 2.6094 | 0.15573
| 0:45 | 2.6097 | 0.15568
| 0:45 | 2.61 | 0.15563
| 0:45 | 2.6103 | 0.15558
| 0:45 | 2.6106 | 0.15553
| 0:45 | 2.6108 | 0.15549
| 0:45 | 2.6111 | 0.15546
| 0:45 | 2.6114 | 0.15543
| 0:46 | 2.6117 | 0.15541
| 0:46 | 2.6119 | 0.15539
| 0:46 | 2.6122 | 0.15538
| 0:46 | 2.6125 | 0.15537
| 0:46 | 2.6128 | 0.15536
| 0:46 | 2.6131 | 0.15535
| 0:46 | 2.6133 | 0.15535
| 0:46 | 2.6136 | 0.15534
| 0:46 | 2.6139 | 0.15534
| 0:46 | 2.6142 | 0.15535
| 0:46 | 2.6144 | 0.15535
| 0:46 | 2.6147 | 0.15536
| 0:46 | 2.615 | 0.15536
| 0:46 | 2.6153 | 0.15536
| 0:46 | 2.6156 | 0.15537
| 0:46 | 2.6158 | 0.15537
| 0:46 | 2.6161 | 0.15537
| 0:46 | 2.6164 | 0.15537
| 0:46 | 2.6167 | 0.15536
| 0:46 | 2.6169 | 0.15536
| 0:46 | 2.6172 | 0.15536
| 0:46 | 2.6175 | 0.15536
| 0:46 | 2.6178 | 0.15535
| 0:46 | 2.6181 | 0.15535
| 0:46 | 2.6183 | 0.15534
| 0:46 | 2.6186 | 0.15533
| 0:46 | 2.6189 | 0.15533
| 0:46 | 2.6192 | 0.15532
| 0:46 | 2.6194 | 0.15531
| 0:46 | 2.6197 | 0.1553
| 0:46 | 2.62 | 0.15529
| 0:46 | 2.6203 | 0.15528
| 0:46 | 2.6206 | 0.15527
| 0:46 | 2.6208 | 0.15526
| 0:46 | 2.6211 | 0.15525
| 0:46 | 2.6214 | 0.15525
| 0:46 | 2.6217 | 0.15524
| 0:46 | 2.6219 | 0.15524
| 0:46 | 2.6222 | 0.15523
| 0:46 | 2.6225 | 0.15523
| 0:46 | 2.6228 | 0.15523
| 0:46 | 2.6231 | 0.15522
| 0:46 | 2.6233 | 0.15522
| 0:46 | 2.6236 | 0.15522
| 0:46 | 2.6239 | 0.15522
| 0:46 | 2.6242 | 0.15522
| 0:46 | 2.6244 | 0.15523
| 0:46 | 2.6247 | 0.15523
| 0:46 | 2.625 | 0.15524
| 0:46 | 2.6253 | 0.15525
| 0:46 | 2.6256 | 0.15527
| 0:46 | 2.6258 | 0.15529
| 0:46 | 2.6261 | 0.15532
| 0:46 | 2.6264 | 0.15534
| 0:46 | 2.6267 | 0.15537
| 0:46 | 2.6269 | 0.1554
| 0:46 | 2.6272 | 0.15544
| 0:46 | 2.6275 | 0.15548
| 0:46 | 2.6278 | 0.15552
| 0:46 | 2.6281 | 0.15556
| 0:47 | 2.6283 | 0.15561
| 0:47 | 2.6286 | 0.15565
| 0:47 | 2.6289 | 0.1557
| 0:47 | 2.6292 | 0.15575
| 0:47 | 2.6294 | 0.15579
| 0:47 | 2.6297 | 0.15583
| 0:47 | 2.63 | 0.15587
| 0:47 | 2.6303 | 0.15591
| 0:47 | 2.6306 | 0.15595
| 0:47 | 2.6308 | 0.15599
| 0:47 | 2.6311 | 0.15603
| 0:47 | 2.6314 | 0.15607
| 0:47 | 2.6317 | 0.15612
| 0:47 | 2.6319 | 0.15617
| 0:47 | 2.6322 | 0.15623
| 0:47 | 2.6325 | 0.15629
| 0:47 | 2.6328 | 0.15637
| 0:47 | 2.6331 | 0.15645
| 0:47 | 2.6333 | 0.15654
| 0:47 | 2.6336 | 0.15663
| 0:47 | 2.6339 | 0.15672
| 0:47 | 2.6342 | 0.15681
| 0:47 | 2.6344 | 0.15691
| 0:47 | 2.6347 | 0.157
| 0:47 | 2.635 | 0.15709
| 0:47 | 2.6353 | 0.15717
| 0:47 | 2.6356 | 0.15726
| 0:47 | 2.6358 | 0.15735
| 0:47 | 2.6361 | 0.15744
| 0:47 | 2.6364 | 0.15752
| 0:47 | 2.6367 | 0.1576
| 0:47 | 2.6369 | 0.15768
| 0:47 | 2.6372 | 0.15776
| 0:47 | 2.6375 | 0.15784
| 0:47 | 2.6378 | 0.15792
| 0:47 | 2.6381 | 0.15801
| 0:47 | 2.6383 | 0.15809
| 0:47 | 2.6386 | 0.15817
| 0:47 | 2.6389 | 0.15826
| 0:47 | 2.6392 | 0.15835
| 0:47 | 2.6394 | 0.15843
| 0:47 | 2.6397 | 0.15852
| 0:47 | 2.64 | 0.15861
| 0:47 | 2.6403 | 0.1587
| 0:47 | 2.6406 | 0.1588
| 0:47 | 2.6408 | 0.15889
| 0:47 | 2.6411 | 0.15898
| 0:47 | 2.6414 | 0.15908
| 0:47 | 2.6417 | 0.15918
| 0:47 | 2.6419 | 0.15927
| 0:47 | 2.6422 | 0.15937
| 0:47 | 2.6425 | 0.15947
| 0:47 | 2.6428 | 0.15957
| 0:47 | 2.6431 | 0.15968
| 0:47 | 2.6433 | 0.15979
| 0:47 | 2.6436 | 0.15989
| 0:47 | 2.6439 | 0.16001
| 0:47 | 2.6442 | 0.16013
| 0:47 | 2.6444 | 0.16025
| 0:47 | 2.6447 | 0.16037
| 0:48 | 2.645 | 0.16049
| 0:48 | 2.6453 | 0.16061
| 0:48 | 2.6456 | 0.16073
| 0:48 | 2.6458 | 0.16084
| 0:48 | 2.6461 | 0.16095
| 0:48 | 2.6464 | 0.16105
| 0:48 | 2.6467 | 0.16114
| 0:48 | 2.6469 | 0.16123
| 0:48 | 2.6472 | 0.16131
| 0:48 | 2.6475 | 0.16138
| 0:48 | 2.6478 | 0.16144
| 0:48 | 2.6481 | 0.1615
| 0:48 | 2.6483 | 0.16156
| 0:48 | 2.6486 | 0.16161
| 0:48 | 2.6489 | 0.16166
| 0:48 | 2.6492 | 0.1617
| 0:48 | 2.6494 | 0.16174
| 0:48 | 2.6497 | 0.16178
| 0:48 | 2.65 | 0.16182
| 0:48 | 2.6503 | 0.16186
| 0:48 | 2.6506 | 0.16189
| 0:48 | 2.6508 | 0.16192
| 0:48 | 2.6511 | 0.16196
| 0:48 | 2.6514 | 0.16198
| 0:48 | 2.6517 | 0.16201
| 0:48 | 2.6519 | 0.16204
| 0:48 | 2.6522 | 0.16206
| 0:48 | 2.6525 | 0.16209
| 0:48 | 2.6528 | 0.1621
| 0:48 | 2.6531 | 0.16212
| 0:48 | 2.6533 | 0.16213
| 0:48 | 2.6536 | 0.16214
| 0:48 | 2.6539 | 0.16215
| 0:48 | 2.6542 | 0.16215
| 0:48 | 2.6544 | 0.16215
| 0:48 | 2.6547 | 0.16214
| 0:48 | 2.655 | 0.16213
| 0:48 | 2.6553 | 0.16212
| 0:48 | 2.6556 | 0.16211
| 0:48 | 2.6558 | 0.16209
| 0:48 | 2.6561 | 0.16206
| 0:48 | 2.6564 | 0.16204
| 0:48 | 2.6567 | 0.16201
| 0:48 | 2.6569 | 0.16197
| 0:48 | 2.6572 | 0.16194
| 0:48 | 2.6575 | 0.1619
| 0:48 | 2.6578 | 0.16185
| 0:48 | 2.6581 | 0.1618
| 0:48 | 2.6583 | 0.16175
| 0:48 | 2.6586 | 0.1617
| 0:48 | 2.6589 | 0.16164
| 0:48 | 2.6592 | 0.16158
| 0:48 | 2.6594 | 0.16151
| 0:48 | 2.6597 | 0.16145
| 0:48 | 2.66 | 0.16138
| 0:48 | 2.6603 | 0.16131
| 0:48 | 2.6606 | 0.16124
| 0:48 | 2.6608 | 0.16117
| 0:48 | 2.6611 | 0.16109
| 0:48 | 2.6614 | 0.16101
| 0:48 | 2.6617 | 0.16092
| 0:49 | 2.6619 | 0.16081
| 0:49 | 2.6622 | 0.1607
| 0:49 | 2.6625 | 0.16059
| 0:49 | 2.6628 | 0.16047
| 0:49 | 2.6631 | 0.16035
| 0:49 | 2.6633 | 0.16023
| 0:49 | 2.6636 | 0.1601
| 0:49 | 2.6639 | 0.15997
| 0:49 | 2.6642 | 0.15984
| 0:49 | 2.6644 | 0.15971
| 0:49 | 2.6647 | 0.15959
| 0:49 | 2.665 | 0.1595
| 0:49 | 2.6653 | 0.15942
| 0:49 | 2.6656 | 0.15935
| 0:49 | 2.6658 | 0.1593
| 0:49 | 2.6661 | 0.15924
| 0:49 | 2.6664 | 0.15919
| 0:49 | 2.6667 | 0.15914
| 0:49 | 2.6669 | 0.15909
| 0:49 | 2.6672 | 0.15904
| 0:49 | 2.6675 | 0.159
| 0:49 | 2.6678 | 0.15895
| 0:49 | 2.6681 | 0.15891
| 0:49 | 2.6683 | 0.15888
| 0:49 | 2.6686 | 0.15885
| 0:49 | 2.6689 | 0.15882
| 0:49 | 2.6692 | 0.1588
| 0:49 | 2.6694 | 0.15878
| 0:49 | 2.6697 | 0.15875
| 0:49 | 2.67 | 0.15873
| 0:49 | 2.6703 | 0.15871
| 0:49 | 2.6706 | 0.15868
| 0:49 | 2.6708 | 0.15866
| 0:49 | 2.6711 | 0.15863
| 0:49 | 2.6714 | 0.15861
| 0:49 | 2.6717 | 0.15858
| 0:49 | 2.6719 | 0.15855
| 0:49 | 2.6722 | 0.15853
| 0:49 | 2.6725 | 0.1585
| 0:49 | 2.6728 | 0.15847
| 0:49 | 2.6731 | 0.15844
| 0:49 | 2.6733 | 0.15841
| 0:49 | 2.6736 | 0.15838
| 0:49 | 2.6739 | 0.15834
| 0:49 | 2.6742 | 0.15831
| 0:49 | 2.6744 | 0.15828
| 0:49 | 2.6747 | 0.15824
| 0:49 | 2.675 | 0.15821
| 0:49 | 2.6753 | 0.15817
| 0:49 | 2.6756 | 0.15813
| 0:49 | 2.6758 | 0.15809
| 0:49 | 2.6761 | 0.15804
| 0:49 | 2.6764 | 0.15798
| 0:49 | 2.6767 | 0.15793
| 0:49 | 2.6769 | 0.15788
| 0:49 | 2.6772 | 0.15784
| 0:49 | 2.6775 | 0.15779
| 0:49 | 2.6778 | 0.15774
| 0:49 | 2.6781 | 0.1577
| 0:50 | 2.6783 | 0.15765
| 0:50 | 2.6786 | 0.15762
| 0:50 | 2.6789 | 0.15758
| 0:50 | 2.6792 | 0.15754
| 0:50 | 2.6794 | 0.1575
| 0:50 | 2.6797 | 0.15747
| 0:50 | 2.68 | 0.15743
| 0:50 | 2.6803 | 0.15739
| 0:50 | 2.6806 | 0.15735
| 0:50 | 2.6808 | 0.15731
| 0:50 | 2.6811 | 0.15726
| 0:50 | 2.6814 | 0.15722
| 0:50 | 2.6817 | 0.15718
| 0:50 | 2.6819 | 0.15713
| 0:50 | 2.6822 | 0.15709
| 0:50 | 2.6825 | 0.15703
| 0:50 | 2.6828 | 0.15697
| 0:50 | 2.6831 | 0.15691
| 0:50 | 2.6833 | 0.15684
| 0:50 | 2.6836 | 0.15678
| 0:50 | 2.6839 | 0.15672
| 0:50 | 2.6842 | 0.15666
| 0:50 | 2.6844 | 0.1566
| 0:50 | 2.6847 | 0.15654
| 0:50 | 2.685 | 0.15648
| 0:50 | 2.6853 | 0.15641
| 0:50 | 2.6856 | 0.15635
| 0:50 | 2.6858 | 0.15629
| 0:50 | 2.6861 | 0.15623
| 0:50 | 2.6864 | 0.15616
| 0:50 | 2.6867 | 0.1561
| 0:50 | 2.6869 | 0.15604
| 0:50 | 2.6872 | 0.15597
| 0:50 | 2.6875 | 0.15591
| 0:50 | 2.6878 | 0.15584
| 0:50 | 2.6881 | 0.15578
| 0:50 | 2.6883 | 0.15571
| 0:50 | 2.6886 | 0.15564
| 0:50 | 2.6889 | 0.15558
| 0:50 | 2.6892 | 0.15551
| 0:50 | 2.6894 | 0.15544
| 0:50 | 2.6897 | 0.15537
| 0:50 | 2.69 | 0.1553
| 0:50 | 2.6903 | 0.15523
| 0:50 | 2.6906 | 0.15516
| 0:50 | 2.6908 | 0.15509
| 0:50 | 2.6911 | 0.15502
| 0:50 | 2.6914 | 0.15495
| 0:50 | 2.6917 | 0.15488
| 0:50 | 2.6919 | 0.1548
| 0:50 | 2.6922 | 0.15473
| 0:50 | 2.6925 | 0.15466
| 0:50 | 2.6928 | 0.15458
| 0:50 | 2.6931 | 0.15451
| 0:50 | 2.6933 | 0.15443
| 0:50 | 2.6936 | 0.15436
| 0:50 | 2.6939 | 0.15428
| 0:50 | 2.6942 | 0.15421
| 0:50 | 2.6944 | 0.15413
| 0:50 | 2.6947 | 0.15405
| 0:50 | 2.695 | 0.15397
| 0:51 | 2.6953 | 0.1539
| 0:51 | 2.6956 | 0.15382
| 0:51 | 2.6958 | 0.15374
| 0:51 | 2.6961 | 0.15365
| 0:51 | 2.6964 | 0.15357
| 0:51 | 2.6967 | 0.15348
| 0:51 | 2.6969 | 0.1534
| 0:51 | 2.6972 | 0.15331
| 0:51 | 2.6975 | 0.15322
| 0:51 | 2.6978 | 0.15313
| 0:51 | 2.6981 | 0.15304
| 0:51 | 2.6983 | 0.15295
| 0:51 | 2.6986 | 0.15285
| 0:51 | 2.6989 | 0.15276
| 0:51 | 2.6992 | 0.15266
| 0:51 | 2.6994 | 0.15256
| 0:51 | 2.6997 | 0.15244
| 0:51 | 2.7 | 0.15233
| 0:51 | 2.7003 | 0.15222
| 0:51 | 2.7006 | 0.15211
| 0:51 | 2.7008 | 0.152
| 0:51 | 2.7011 | 0.15189
| 0:51 | 2.7014 | 0.15178
| 0:51 | 2.7017 | 0.15167
| 0:51 | 2.7019 | 0.15157
| 0:51 | 2.7022 | 0.15146
| 0:51 | 2.7025 | 0.15136
| 0:51 | 2.7028 | 0.15126
| 0:51 | 2.7031 | 0.15115
| 0:51 | 2.7033 | 0.15105
| 0:51 | 2.7036 | 0.15095
| 0:51 | 2.7039 | 0.15085
| 0:51 | 2.7042 | 0.15076
| 0:51 | 2.7044 | 0.15066
| 0:51 | 2.7047 | 0.15056
| 0:51 | 2.705 | 0.15046
| 0:51 | 2.7053 | 0.15036
| 0:51 | 2.7056 | 0.15026
| 0:51 | 2.7058 | 0.15017
| 0:51 | 2.7061 | 0.15007
| 0:51 | 2.7064 | 0.14998
| 0:51 | 2.7067 | 0.14989
| 0:51 | 2.7069 | 0.1498
| 0:51 | 2.7072 | 0.14971
| 0:51 | 2.7075 | 0.14963
| 0:51 | 2.7078 | 0.14955
| 0:51 | 2.7081 | 0.14947
| 0:51 | 2.7083 | 0.14939
| 0:51 | 2.7086 | 0.14931
| 0:51 | 2.7089 | 0.14923
| 0:51 | 2.7092 | 0.14915
| 0:51 | 2.7094 | 0.14907
| 0:51 | 2.7097 | 0.14899
| 0:51 | 2.71 | 0.1489
| 0:51 | 2.7103 | 0.14881
| 0:51 | 2.7106 | 0.14871
| 0:51 | 2.7108 | 0.14859
| 0:51 | 2.7111 | 0.14848
| 0:51 | 2.7114 | 0.14835
| 0:52 | 2.7117 | 0.14823
| 0:52 | 2.7119 | 0.1481
| 0:52 | 2.7122 | 0.14797
| 0:52 | 2.7125 | 0.14783
| 0:52 | 2.7128 | 0.14769
| 0:52 | 2.7131 | 0.14755
| 0:52 | 2.7133 | 0.1474
| 0:52 | 2.7136 | 0.14725
| 0:52 | 2.7139 | 0.1471
| 0:52 | 2.7142 | 0.14694
| 0:52 | 2.7144 | 0.14678
| 0:52 | 2.7147 | 0.14662
| 0:52 | 2.715 | 0.14646
| 0:52 | 2.7153 | 0.1463
| 0:52 | 2.7156 | 0.14614
| 0:52 | 2.7158 | 0.14598
| 0:52 | 2.7161 | 0.14583
| 0:52 | 2.7164 | 0.14567
| 0:52 | 2.7167 | 0.14552
| 0:52 | 2.7169 | 0.14536
| 0:52 | 2.7172 | 0.14521
| 0:52 | 2.7175 | 0.14506
| 0:52 | 2.7178 | 0.14491
| 0:52 | 2.7181 | 0.14475
| 0:52 | 2.7183 | 0.1446
| 0:52 | 2.7186 | 0.14444
| 0:52 | 2.7189 | 0.14428
| 0:52 | 2.7192 | 0.14411
| 0:52 | 2.7194 | 0.14395
| 0:52 | 2.7197 | 0.14378
| 0:52 | 2.72 | 0.14361
| 0:52 | 2.7203 | 0.14343
| 0:52 | 2.7206 | 0.14326
| 0:52 | 2.7208 | 0.14308
| 0:52 | 2.7211 | 0.14289
| 0:52 | 2.7214 | 0.14271
| 0:52 | 2.7217 | 0.14251
| 0:52 | 2.7219 | 0.14232
| 0:52 | 2.7222 | 0.14212
| 0:52 | 2.7225 | 0.14192
| 0:52 | 2.7228 | 0.14172
| 0:52 | 2.7231 | 0.14151
| 0:52 | 2.7233 | 0.14131
| 0:52 | 2.7236 | 0.14111
| 0:52 | 2.7239 | 0.1409
| 0:52 | 2.7242 | 0.14069
| 0:52 | 2.7244 | 0.14049
| 0:52 | 2.7247 | 0.14028
| 0:52 | 2.725 | 0.14007
| 0:52 | 2.7253 | 0.13986
| 0:52 | 2.7256 | 0.13965
| 0:52 | 2.7258 | 0.13944
| 0:52 | 2.7261 | 0.13922
| 0:52 | 2.7264 | 0.13901
| 0:52 | 2.7267 | 0.1388
| 0:52 | 2.7269 | 0.13858
| 0:52 | 2.7272 | 0.13837
| 0:52 | 2.7275 | 0.13815
| 0:52 | 2.7278 | 0.13794
| 0:52 | 2.7281 | 0.13772
| 0:52 | 2.7283 | 0.13751
| 0:53 | 2.7286 | 0.13729
| 0:53 | 2.7289 | 0.13701
| 0:53 | 2.7292 | 0.13673
| 0:53 | 2.7294 | 0.13646
| 0:53 | 2.7297 | 0.13618
| 0:53 | 2.73 | 0.1359
| 0:53 | 2.7303 | 0.13562
| 0:53 | 2.7306 | 0.13535
| 0:53 | 2.7308 | 0.13507
| 0:53 | 2.7311 | 0.1348
| 0:53 | 2.7314 | 0.13452
| 0:53 | 2.7317 | 0.13425
| 0:53 | 2.7319 | 0.13398
| 0:53 | 2.7322 | 0.1337
| 0:53 | 2.7325 | 0.13343
| 0:53 | 2.7328 | 0.13316
| 0:53 | 2.7331 | 0.13289
| 0:53 | 2.7333 | 0.13262
| 0:53 | 2.7336 | 0.13235
| 0:53 | 2.7339 | 0.13208
| 0:53 | 2.7342 | 0.13181
| 0:53 | 2.7344 | 0.13154
| 0:53 | 2.7347 | 0.13127
| 0:53 | 2.735 | 0.131
| 0:53 | 2.7353 | 0.13074
| 0:53 | 2.7356 | 0.13047
| 0:53 | 2.7358 | 0.1302
| 0:53 | 2.7361 | 0.12994
| 0:53 | 2.7364 | 0.12967
| 0:53 | 2.7367 | 0.12941
| 0:53 | 2.7369 | 0.12915
| 0:53 | 2.7372 | 0.12888
| 0:53 | 2.7375 | 0.12862
| 0:53 | 2.7378 | 0.12836
| 0:53 | 2.7381 | 0.1281
| 0:53 | 2.7383 | 0.12783
| 0:53 | 2.7386 | 0.12757
| 0:53 | 2.7389 | 0.12731
| 0:53 | 2.7392 | 0.12705
| 0:53 | 2.7394 | 0.12679
| 0:53 | 2.7397 | 0.12654
| 0:53 | 2.74 | 0.12628
| 0:53 | 2.7403 | 0.12602
| 0:53 | 2.7406 | 0.12576
| 0:53 | 2.7408 | 0.12551
| 0:53 | 2.7411 | 0.12525
| 0:53 | 2.7414 | 0.125
| 0:53 | 2.7417 | 0.12474
| 0:53 | 2.7419 | 0.12449
| 0:53 | 2.7422 | 0.12423
| 0:53 | 2.7425 | 0.12398
| 0:53 | 2.7428 | 0.12374
| 0:53 | 2.7431 | 0.12349
| 0:53 | 2.7433 | 0.12325
| 0:53 | 2.7436 | 0.12301
| 0:53 | 2.7439 | 0.12277
| 0:53 | 2.7442 | 0.12254
| 0:53 | 2.7444 | 0.12231
| 0:53 | 2.7447 | 0.12208
| 0:54 | 2.745 | 0.12185
| 0:54 | 2.7453 | 0.12162
| 0:54 | 2.7456 | 0.1214
| 0:54 | 2.7458 | 0.12118
| 0:54 | 2.7461 | 0.12096
| 0:54 | 2.7464 | 0.12074
| 0:54 | 2.7467 | 0.12053
| 0:54 | 2.7469 | 0.12032
| 0:54 | 2.7472 | 0.12011
| 0:54 | 2.7475 | 0.1199
| 0:54 | 2.7478 | 0.11969
| 0:54 | 2.7481 | 0.11949
| 0:54 | 2.7483 | 0.11928
| 0:54 | 2.7486 | 0.11908
| 0:54 | 2.7489 | 0.11888
| 0:54 | 2.7492 | 0.11868
| 0:54 | 2.7494 | 0.11847
| 0:54 | 2.7497 | 0.11827
| 0:54 | 2.75 | 0.11807
| 0:54 | 2.7503 | 0.11788
| 0:54 | 2.7506 | 0.11768
| 0:54 | 2.7508 | 0.11748
| 0:54 | 2.7511 | 0.11728
| 0:54 | 2.7514 | 0.11709
| 0:54 | 2.7517 | 0.11689
| 0:54 | 2.7519 | 0.1167
| 0:54 | 2.7522 | 0.11651
| 0:54 | 2.7525 | 0.11631
| 0:54 | 2.7528 | 0.11612
| 0:54 | 2.7531 | 0.11593
| 0:54 | 2.7533 | 0.11574
| 0:54 | 2.7536 | 0.11556
| 0:54 | 2.7539 | 0.11538
| 0:54 | 2.7542 | 0.11521
| 0:54 | 2.7544 | 0.11504
| 0:54 | 2.7547 | 0.11487
| 0:54 | 2.755 | 0.11471
| 0:54 | 2.7553 | 0.11456
| 0:54 | 2.7556 | 0.1144
| 0:54 | 2.7558 | 0.11426
| 0:54 | 2.7561 | 0.11411
| 0:54 | 2.7564 | 0.11397
| 0:54 | 2.7567 | 0.11383
| 0:54 | 2.7569 | 0.11368
| 0:54 | 2.7572 | 0.11354
| 0:54 | 2.7575 | 0.11341
| 0:54 | 2.7578 | 0.11327
| 0:54 | 2.7581 | 0.11313
| 0:54 | 2.7583 | 0.113
| 0:54 | 2.7586 | 0.11287
| 0:54 | 2.7589 | 0.11273
| 0:54 | 2.7592 | 0.1126
| 0:54 | 2.7594 | 0.11247
| 0:54 | 2.7597 | 0.11235
| 0:54 | 2.76 | 0.11222
| 0:54 | 2.7603 | 0.11209
| 0:54 | 2.7606 | 0.11197
| 0:54 | 2.7608 | 0.11185
| 0:54 | 2.7611 | 0.11173
| 0:54 | 2.7614 | 0.11161
| 0:54 | 2.7617 | 0.11149
| 0:55 | 2.7619 | 0.11137
| 0:55 | 2.7622 | 0.11125
| 0:55 | 2.7625 | 0.11113
| 0:55 | 2.7628 | 0.11101
| 0:55 | 2.7631 | 0.11089
| 0:55 | 2.7633 | 0.11077
| 0:55 | 2.7636 | 0.11065
| 0:55 | 2.7639 | 0.11052
| 0:55 | 2.7642 | 0.1104
| 0:55 | 2.7644 | 0.11028
| 0:55 | 2.7647 | 0.11016
| 0:55 | 2.765 | 0.11003
| 0:55 | 2.7653 | 0.10991
| 0:55 | 2.7656 | 0.10979
| 0:55 | 2.7658 | 0.10966
| 0:55 | 2.7661 | 0.10954
| 0:55 | 2.7664 | 0.10941
| 0:55 | 2.7667 | 0.10929
| 0:55 | 2.7669 | 0.10916
| 0:55 | 2.7672 | 0.10904
| 0:55 | 2.7675 | 0.10891
| 0:55 | 2.7678 | 0.10878
| 0:55 | 2.7681 | 0.10866
| 0:55 | 2.7683 | 0.10853
| 0:55 | 2.7686 | 0.1084
| 0:55 | 2.7689 | 0.10828
| 0:55 | 2.7692 | 0.10815
| 0:55 | 2.7694 | 0.10802
| 0:55 | 2.7697 | 0.10789
| 0:55 | 2.77 | 0.10776
| 0:55 | 2.7703 | 0.10763
| 0:55 | 2.7706 | 0.1075
| 0:55 | 2.7708 | 0.10737
| 0:55 | 2.7711 | 0.10724
| 0:55 | 2.7714 | 0.10711
| 0:55 | 2.7717 | 0.10698
| 0:55 | 2.7719 | 0.10685
| 0:55 | 2.7722 | 0.10671
| 0:55 | 2.7725 | 0.10658
| 0:55 | 2.7728 | 0.10645
| 0:55 | 2.7731 | 0.10632
| 0:55 | 2.7733 | 0.10619
| 0:55 | 2.7736 | 0.10605
| 0:55 | 2.7739 | 0.10592
| 0:55 | 2.7742 | 0.10579
| 0:55 | 2.7744 | 0.10566
| 0:55 | 2.7747 | 0.10553
| 0:55 | 2.775 | 0.1054
| 0:55 | 2.7753 | 0.10527
| 0:55 | 2.7756 | 0.10513
| 0:55 | 2.7758 | 0.105
| 0:55 | 2.7761 | 0.10487
| 0:55 | 2.7764 | 0.10474
| 0:55 | 2.7767 | 0.10461
| 0:55 | 2.7769 | 0.10448
| 0:55 | 2.7772 | 0.10435
| 0:55 | 2.7775 | 0.10422
| 0:55 | 2.7778 | 0.10409
| 0:55 | 2.7781 | 0.10395
| 0:56 | 2.7783 | 0.10382
| 0:56 | 2.7786 | 0.10369
| 0:56 | 2.7789 | 0.10356
| 0:56 | 2.7792 | 0.10344
| 0:56 | 2.7794 | 0.10331
| 0:56 | 2.7797 | 0.1032
| 0:56 | 2.78 | 0.10308
| 0:56 | 2.7803 | 0.10297
| 0:56 | 2.7806 | 0.10287
| 0:56 | 2.7808 | 0.10277
| 0:56 | 2.7811 | 0.10267
| 0:56 | 2.7814 | 0.10257
| 0:56 | 2.7817 | 0.10246
| 0:56 | 2.7819 | 0.10235
| 0:56 | 2.7822 | 0.10224
| 0:56 | 2.7825 | 0.10212
| 0:56 | 2.7828 | 0.10201
| 0:56 | 2.7831 | 0.10189
| 0:56 | 2.7833 | 0.10178
| 0:56 | 2.7836 | 0.10166
| 0:56 | 2.7839 | 0.10155
| 0:56 | 2.7842 | 0.10143
| 0:56 | 2.7844 | 0.10132
| 0:56 | 2.7847 | 0.1012
| 0:56 | 2.785 | 0.10108
| 0:56 | 2.7853 | 0.10097
| 0:56 | 2.7856 | 0.10085
| 0:56 | 2.7858 | 0.10073
| 0:56 | 2.7861 | 0.10061
| 0:56 | 2.7864 | 0.10049
| 0:56 | 2.7867 | 0.10038
| 0:56 | 2.7869 | 0.10026
| 0:56 | 2.7872 | 0.10014
| 0:56 | 2.7875 | 0.10002
| 0:56 | 2.7878 | 0.099898
| 0:56 | 2.7881 | 0.099778
| 0:56 | 2.7883 | 0.099657
| 0:56 | 2.7886 | 0.099536
| 0:56 | 2.7889 | 0.099415
| 0:56 | 2.7892 | 0.099293
| 0:56 | 2.7894 | 0.099172
| 0:56 | 2.7897 | 0.099049
| 0:56 | 2.79 | 0.098927
| 0:56 | 2.7903 | 0.098804
| 0:56 | 2.7906 | 0.098681
| 0:56 | 2.7908 | 0.098557
| 0:56 | 2.7911 | 0.098433
| 0:56 | 2.7914 | 0.098309
| 0:56 | 2.7917 | 0.098185
| 0:56 | 2.7919 | 0.09806
| 0:56 | 2.7922 | 0.097935
| 0:56 | 2.7925 | 0.097809
| 0:56 | 2.7928 | 0.09768
| 0:56 | 2.7931 | 0.097546
| 0:56 | 2.7933 | 0.097407
| 0:56 | 2.7936 | 0.097263
| 0:56 | 2.7939 | 0.097114
| 0:56 | 2.7942 | 0.096961
| 0:56 | 2.7944 | 0.096802
| 0:56 | 2.7947 | 0.09664
| 0:56 | 2.795 | 0.096477
| 0:57 | 2.7953 | 0.096313
| 0:57 | 2.7956 | 0.09615
| 0:57 | 2.7958 | 0.095989
| 0:57 | 2.7961 | 0.09583
| 0:57 | 2.7964 | 0.095673
| 0:57 | 2.7967 | 0.095519
| 0:57 | 2.7969 | 0.095367
| 0:57 | 2.7972 | 0.095216
| 0:57 | 2.7975 | 0.095068
| 0:57 | 2.7978 | 0.094923
| 0:57 | 2.7981 | 0.094779
| 0:57 | 2.7983 | 0.094638
| 0:57 | 2.7986 | 0.094498
| 0:57 | 2.7989 | 0.094361
| 0:57 | 2.7992 | 0.094226
| 0:57 | 2.7994 | 0.094094
| 0:57 | 2.7997 | 0.093963
| 0:57 | 2.8 | 0.093835
| 0:57 | 2.8003 | 0.093707
| 0:57 | 2.8006 | 0.093579
| 0:57 | 2.8008 | 0.093451
| 0:57 | 2.8011 | 0.093323
| 0:57 | 2.8014 | 0.093194
| 0:57 | 2.8017 | 0.093065
| 0:57 | 2.8019 | 0.092936
| 0:57 | 2.8022 | 0.092806
| 0:57 | 2.8025 | 0.092677
| 0:57 | 2.8028 | 0.092547
| 0:57 | 2.8031 | 0.092417
| 0:57 | 2.8033 | 0.092286
| 0:57 | 2.8036 | 0.092156
| 0:57 | 2.8039 | 0.092025
| 0:57 | 2.8042 | 0.091893
| 0:57 | 2.8044 | 0.091762
| 0:57 | 2.8047 | 0.09163
| 0:57 | 2.805 | 0.091498
| 0:57 | 2.8053 | 0.091366
| 0:57 | 2.8056 | 0.091234
| 0:57 | 2.8058 | 0.091101
| 0:57 | 2.8061 | 0.090968
| 0:57 | 2.8064 | 0.090835
| 0:57 | 2.8067 | 0.090702
| 0:57 | 2.8069 | 0.090568
| 0:57 | 2.8072 | 0.090434
| 0:57 | 2.8075 | 0.0903
| 0:57 | 2.8078 | 0.090166
| 0:57 | 2.8081 | 0.090031
| 0:57 | 2.8083 | 0.089896
| 0:57 | 2.8086 | 0.089761
| 0:57 | 2.8089 | 0.089626
| 0:57 | 2.8092 | 0.08949
| 0:57 | 2.8094 | 0.089354
| 0:57 | 2.8097 | 0.089218
| 0:57 | 2.81 | 0.089082
| 0:57 | 2.8103 | 0.088945
| 0:57 | 2.8106 | 0.088808
| 0:57 | 2.8108 | 0.088671
| 0:57 | 2.8111 | 0.088534
| 0:57 | 2.8114 | 0.088397
| 0:57 | 2.8117 | 0.088261
| 0:58 | 2.8119 | 0.088126
| 0:58 | 2.8122 | 0.087992
| 0:58 | 2.8125 | 0.087859
| 0:58 | 2.8128 | 0.087727
| 0:58 | 2.8131 | 0.087596
| 0:58 | 2.8133 | 0.087466
| 0:58 | 2.8136 | 0.087337
| 0:58 | 2.8139 | 0.087209
| 0:58 | 2.8142 | 0.087081
| 0:58 | 2.8144 | 0.086955
| 0:58 | 2.8147 | 0.086827
| 0:58 | 2.815 | 0.086696
| 0:58 | 2.8153 | 0.086562
| 0:58 | 2.8156 | 0.086423
| 0:58 | 2.8158 | 0.086284
| 0:58 | 2.8161 | 0.086145
| 0:58 | 2.8164 | 0.086009
| 0:58 | 2.8167 | 0.085873
| 0:58 | 2.8169 | 0.08574
| 0:58 | 2.8172 | 0.085607
| 0:58 | 2.8175 | 0.085476
| 0:58 | 2.8178 | 0.085346
| 0:58 | 2.8181 | 0.085218
| 0:58 | 2.8183 | 0.085091
| 0:58 | 2.8186 | 0.084965
| 0:58 | 2.8189 | 0.084841
| 0:58 | 2.8192 | 0.084718
| 0:58 | 2.8194 | 0.084597
| 0:58 | 2.8197 | 0.084477
| 0:58 | 2.82 | 0.084358
| 0:58 | 2.8203 | 0.084241
| 0:58 | 2.8206 | 0.084125
| 0:58 | 2.8208 | 0.084009
| 0:58 | 2.8211 | 0.083893
| 0:58 | 2.8214 | 0.083778
| 0:58 | 2.8217 | 0.083663
| 0:58 | 2.8219 | 0.083549
| 0:58 | 2.8222 | 0.083435
| 0:58 | 2.8225 | 0.083321
| 0:58 | 2.8228 | 0.083204
| 0:58 | 2.8231 | 0.083084
| 0:58 | 2.8233 | 0.082962
| 0:58 | 2.8236 | 0.082837
| 0:58 | 2.8239 | 0.082708
| 0:58 | 2.8242 | 0.082577
| 0:58 | 2.8244 | 0.082443
| 0:58 | 2.8247 | 0.082306
| 0:58 | 2.825 | 0.082166
| 0:58 | 2.8253 | 0.082023
| 0:58 | 2.8256 | 0.081878
| 0:58 | 2.8258 | 0.081731
| 0:58 | 2.8261 | 0.081585
| 0:58 | 2.8264 | 0.08144
| 0:58 | 2.8267 | 0.081294
| 0:58 | 2.8269 | 0.08115
| 0:58 | 2.8272 | 0.081005
| 0:58 | 2.8275 | 0.080861
| 0:58 | 2.8278 | 0.080718
| 0:58 | 2.8281 | 0.080575
| 0:58 | 2.8283 | 0.080432
| 0:59 | 2.8286 | 0.08029
| 0:59 | 2.8289 | 0.080148
| 0:59 | 2.8292 | 0.080006
| 0:59 | 2.8294 | 0.079865
| 0:59 | 2.8297 | 0.079725
| 0:59 | 2.83 | 0.079585
| 0:59 | 2.8303 | 0.079445
| 0:59 | 2.8306 | 0.079305
| 0:59 | 2.8308 | 0.079166
| 0:59 | 2.8311 | 0.079028
| 0:59 | 2.8314 | 0.07889
| 0:59 | 2.8317 | 0.078752
| 0:59 | 2.8319 | 0.078615
| 0:59 | 2.8322 | 0.078478
| 0:59 | 2.8325 | 0.078342
| 0:59 | 2.8328 | 0.078206
| 0:59 | 2.8331 | 0.07807
| 0:59 | 2.8333 | 0.077935
| 0:59 | 2.8336 | 0.0778
| 0:59 | 2.8339 | 0.077666
| 0:59 | 2.8342 | 0.077532
| 0:59 | 2.8344 | 0.077398
| 0:59 | 2.8347 | 0.077265
| 0:59 | 2.835 | 0.077133
| 0:59 | 2.8353 | 0.077
| 0:59 | 2.8356 | 0.076869
| 0:59 | 2.8358 | 0.076737
| 0:59 | 2.8361 | 0.076606
| 0:59 | 2.8364 | 0.076476
| 0:59 | 2.8367 | 0.076345
| 0:59 | 2.8369 | 0.076216
| 0:59 | 2.8372 | 0.076088
| 0:59 | 2.8375 | 0.075965
| 0:59 | 2.8378 | 0.075845
| 0:59 | 2.8381 | 0.075729
| 0:59 | 2.8383 | 0.075618
| 0:59 | 2.8386 | 0.07551
| 0:59 | 2.8389 | 0.075405
| 0:59 | 2.8392 | 0.075305
| 0:59 | 2.8394 | 0.075209
| 0:59 | 2.8397 | 0.075116
| 0:59 | 2.84 | 0.075027
| 0:59 | 2.8403 | 0.074942
| 0:59 | 2.8406 | 0.074858
| 0:59 | 2.8408 | 0.074773
| 0:59 | 2.8411 | 0.074689
| 0:59 | 2.8414 | 0.074604
| 0:59 | 2.8417 | 0.07452
| 0:59 | 2.8419 | 0.074436
| 0:59 | 2.8422 | 0.074353
| 0:59 | 2.8425 | 0.074269
| 0:59 | 2.8428 | 0.074186
| 0:59 | 2.8431 | 0.074103
| 0:59 | 2.8433 | 0.07402
| 0:59 | 2.8436 | 0.073937
| 0:59 | 2.8439 | 0.073854
| 0:59 | 2.8442 | 0.073772
| 0:59 | 2.8444 | 0.07369
| 0:59 | 2.8447 | 0.073608
| 1:00 | 2.845 | 0.073526
| 1:00 | 2.8453 | 0.073444
| 1:00 | 2.8456 | 0.073363
| 1:00 | 2.8458 | 0.073284
| 1:00 | 2.8461 | 0.073208
| 1:00 | 2.8464 | 0.073135
| 1:00 | 2.8467 | 0.073065
| 1:00 | 2.8469 | 0.072998
| 1:00 | 2.8472 | 0.072935
| 1:00 | 2.8475 | 0.072875
| 1:00 | 2.8478 | 0.072818
| 1:00 | 2.8481 | 0.072762
| 1:00 | 2.8483 | 0.072707
| 1:00 | 2.8486 | 0.072654
| 1:00 | 2.8489 | 0.072601
| 1:00 | 2.8492 | 0.072548
| 1:00 | 2.8494 | 0.072494
| 1:00 | 2.8497 | 0.072439
| 1:00 | 2.85 | 0.072384
| 1:00 | 2.8503 | 0.072328
| 1:00 | 2.8506 | 0.072271
| 1:00 | 2.8508 | 0.072214
| 1:00 | 2.8511 | 0.072156
| 1:00 | 2.8514 | 0.072097
| 1:00 | 2.8517 | 0.072038
| 1:00 | 2.8519 | 0.071978
| 1:00 | 2.8522 | 0.071918
| 1:00 | 2.8525 | 0.071857
| 1:00 | 2.8528 | 0.071795
| 1:00 | 2.8531 | 0.071733
| 1:00 | 2.8533 | 0.07167
| 1:00 | 2.8536 | 0.071606
| 1:00 | 2.8539 | 0.071542
| 1:00 | 2.8542 | 0.071477
| 1:00 | 2.8544 | 0.071412
| 1:00 | 2.8547 | 0.071347
| 1:00 | 2.855 | 0.071282
| 1:00 | 2.8553 | 0.071217
| 1:00 | 2.8556 | 0.071152
| 1:00 | 2.8558 | 0.071087
| 1:00 | 2.8561 | 0.071022
| 1:00 | 2.8564 | 0.070957
| 1:00 | 2.8567 | 0.070892
| 1:00 | 2.8569 | 0.070827
| 1:00 | 2.8572 | 0.070761
| 1:00 | 2.8575 | 0.070696
| 1:00 | 2.8578 | 0.070631
| 1:00 | 2.8581 | 0.070566
| 1:00 | 2.8583 | 0.070501
| 1:00 | 2.8586 | 0.070436
| 1:00 | 2.8589 | 0.070371
| 1:00 | 2.8592 | 0.070306
| 1:00 | 2.8594 | 0.070241
| 1:00 | 2.8597 | 0.070176
| 1:00 | 2.86 | 0.070111
| 1:00 | 2.8603 | 0.070046
| 1:00 | 2.8606 | 0.069981
| 1:00 | 2.8608 | 0.069916
| 1:00 | 2.8611 | 0.069851
| 1:00 | 2.8614 | 0.069786
| 1:01 | 2.8617 | 0.069722
| 1:01 | 2.8619 | 0.069659
| 1:01 | 2.8622 | 0.069597
| 1:01 | 2.8625 | 0.069536
| 1:01 | 2.8628 | 0.069476
| 1:01 | 2.8631 | 0.069416
| 1:01 | 2.8633 | 0.069357
| 1:01 | 2.8636 | 0.0693
| 1:01 | 2.8639 | 0.069243
| 1:01 | 2.8642 | 0.069187
| 1:01 | 2.8644 | 0.069132
| 1:01 | 2.8647 | 0.069078
| 1:01 | 2.865 | 0.069024
| 1:01 | 2.8653 | 0.068972
| 1:01 | 2.8656 | 0.06892
| 1:01 | 2.8658 | 0.068869
| 1:01 | 2.8661 | 0.068819
| 1:01 | 2.8664 | 0.06877
| 1:01 | 2.8667 | 0.068722
| 1:01 | 2.8669 | 0.068675
| 1:01 | 2.8672 | 0.068628
| 1:01 | 2.8675 | 0.068583
| 1:01 | 2.8678 | 0.068538
| 1:01 | 2.8681 | 0.068494
| 1:01 | 2.8683 | 0.068452
| 1:01 | 2.8686 | 0.068409
| 1:01 | 2.8689 | 0.068368
| 1:01 | 2.8692 | 0.068328
| 1:01 | 2.8694 | 0.068289
| 1:01 | 2.8697 | 0.06825
| 1:01 | 2.87 | 0.068212
| 1:01 | 2.8703 | 0.068173
| 1:01 | 2.8706 | 0.068133
| 1:01 | 2.8708 | 0.068092
| 1:01 | 2.8711 | 0.068051
| 1:01 | 2.8714 | 0.06801
| 1:01 | 2.8717 | 0.067967
| 1:01 | 2.8719 | 0.067924
| 1:01 | 2.8722 | 0.06788
| 1:01 | 2.8725 | 0.067836
| 1:01 | 2.8728 | 0.067791
| 1:01 | 2.8731 | 0.067745
| 1:01 | 2.8733 | 0.067698
| 1:01 | 2.8736 | 0.067651
| 1:01 | 2.8739 | 0.067603
| 1:01 | 2.8742 | 0.067555
| 1:01 | 2.8744 | 0.067506
| 1:01 | 2.8747 | 0.067454
| 1:01 | 2.875 | 0.067398
| 1:01 | 2.8753 | 0.067336
| 1:01 | 2.8756 | 0.067271
| 1:01 | 2.8758 | 0.067203
| 1:01 | 2.8761 | 0.067132
| 1:01 | 2.8764 | 0.067059
| 1:01 | 2.8767 | 0.066983
| 1:01 | 2.8769 | 0.066903
| 1:01 | 2.8772 | 0.066819
| 1:01 | 2.8775 | 0.066731
| 1:01 | 2.8778 | 0.066638
| 1:01 | 2.8781 | 0.066542
| 1:02 | 2.8783 | 0.066441
| 1:02 | 2.8786 | 0.066335
| 1:02 | 2.8789 | 0.066224
| 1:02 | 2.8792 | 0.066109
| 1:02 | 2.8794 | 0.065989
| 1:02 | 2.8797 | 0.065865
| 1:02 | 2.88 | 0.065735
| 1:02 | 2.8803 | 0.065601
| 1:02 | 2.8806 | 0.065463
| 1:02 | 2.8808 | 0.065319
| 1:02 | 2.8811 | 0.065171
| 1:02 | 2.8814 | 0.065018
| 1:02 | 2.8817 | 0.064861
| 1:02 | 2.8819 | 0.064699
| 1:02 | 2.8822 | 0.064532
| 1:02 | 2.8825 | 0.06436
| 1:02 | 2.8828 | 0.064186
| 1:02 | 2.8831 | 0.06401
| 1:02 | 2.8833 | 0.063831
| 1:02 | 2.8836 | 0.06365
| 1:02 | 2.8839 | 0.063467
| 1:02 | 2.8842 | 0.063282
| 1:02 | 2.8844 | 0.063094
| 1:02 | 2.8847 | 0.062904
| 1:02 | 2.885 | 0.062713
| 1:02 | 2.8853 | 0.06252
| 1:02 | 2.8856 | 0.062327
| 1:02 | 2.8858 | 0.062133
| 1:02 | 2.8861 | 0.061937
| 1:02 | 2.8864 | 0.061741
| 1:02 | 2.8867 | 0.061543
| 1:02 | 2.8869 | 0.061344
| 1:02 | 2.8872 | 0.061143
| 1:02 | 2.8875 | 0.060941
| 1:02 | 2.8878 | 0.060737
| 1:02 | 2.8881 | 0.060531
| 1:02 | 2.8883 | 0.060325
| 1:02 | 2.8886 | 0.060116
| 1:02 | 2.8889 | 0.059906
| 1:02 | 2.8892 | 0.059695
| 1:02 | 2.8894 | 0.059482
| 1:02 | 2.8897 | 0.059268
| 1:02 | 2.89 | 0.059052
| 1:02 | 2.8903 | 0.058835
| 1:02 | 2.8906 | 0.058616
| 1:02 | 2.8908 | 0.058396
| 1:02 | 2.8911 | 0.058174
| 1:02 | 2.8914 | 0.057951
| 1:02 | 2.8917 | 0.057726
| 1:02 | 2.8919 | 0.0575
| 1:02 | 2.8922 | 0.057272
| 1:02 | 2.8925 | 0.057042
| 1:02 | 2.8928 | 0.056809
| 1:02 | 2.8931 | 0.056574
| 1:02 | 2.8933 | 0.056335
| 1:02 | 2.8936 | 0.056094
| 1:02 | 2.8939 | 0.055849
| 1:02 | 2.8942 | 0.055599
| 1:02 | 2.8944 | 0.055344
| 1:02 | 2.8947 | 0.055084
| 1:02 | 2.895 | 0.054819
| 1:03 | 2.8953 | 0.054549
| 1:03 | 2.8956 | 0.054277
| 1:03 | 2.8958 | 0.05401
| 1:03 | 2.8961 | 0.053746
| 1:03 | 2.8964 | 0.053486
| 1:03 | 2.8967 | 0.05323
| 1:03 | 2.8969 | 0.052978
| 1:03 | 2.8972 | 0.052729
| 1:03 | 2.8975 | 0.052485
| 1:03 | 2.8978 | 0.052244
| 1:03 | 2.8981 | 0.052007
| 1:03 | 2.8983 | 0.051774
| 1:03 | 2.8986 | 0.051545
| 1:03 | 2.8989 | 0.05132
| 1:03 | 2.8992 | 0.051098
| 1:03 | 2.8994 | 0.050878
| 1:03 | 2.8997 | 0.050659
| 1:03 | 2.9 | 0.05044
| 1:03 | 2.9003 | 0.050222
| 1:03 | 2.9006 | 0.050006
| 1:03 | 2.9008 | 0.04979
| 1:03 | 2.9011 | 0.049575
| 1:03 | 2.9014 | 0.049361
| 1:03 | 2.9017 | 0.049149
| 1:03 | 2.9019 | 0.048938
| 1:03 | 2.9022 | 0.048728
| 1:03 | 2.9025 | 0.04852
| 1:03 | 2.9028 | 0.048313
| 1:03 | 2.9031 | 0.048108
| 1:03 | 2.9033 | 0.047904
| 1:03 | 2.9036 | 0.047701
| 1:03 | 2.9039 | 0.0475
| 1:03 | 2.9042 | 0.047303
| 1:03 | 2.9044 | 0.04711
| 1:03 | 2.9047 | 0.04692
| 1:03 | 2.905 | 0.046734
| 1:03 | 2.9053 | 0.046551
| 1:03 | 2.9056 | 0.046372
| 1:03 | 2.9058 | 0.046196
| 1:03 | 2.9061 | 0.046024
| 1:03 | 2.9064 | 0.045855
| 1:03 | 2.9067 | 0.04569
| 1:03 | 2.9069 | 0.045529
| 1:03 | 2.9072 | 0.04537
| 1:03 | 2.9075 | 0.045214
| 1:03 | 2.9078 | 0.045061
| 1:03 | 2.9081 | 0.044909
| 1:03 | 2.9083 | 0.044761
| 1:03 | 2.9086 | 0.044614
| 1:03 | 2.9089 | 0.04447
| 1:03 | 2.9092 | 0.044328
| 1:03 | 2.9094 | 0.044186
| 1:03 | 2.9097 | 0.044044
| 1:03 | 2.91 | 0.043903
| 1:03 | 2.9103 | 0.043763
| 1:03 | 2.9106 | 0.043624
| 1:03 | 2.9108 | 0.043485
| 1:03 | 2.9111 | 0.043347
| 1:03 | 2.9114 | 0.043216
| 1:04 | 2.9117 | 0.043094
| 1:04 | 2.9119 | 0.042982
| 1:04 | 2.9122 | 0.042876
| 1:04 | 2.9125 | 0.042776
| 1:04 | 2.9128 | 0.042683
| 1:04 | 2.9131 | 0.042595
| 1:04 | 2.9133 | 0.042514
| 1:04 | 2.9136 | 0.042439
| 1:04 | 2.9139 | 0.04237
| 1:04 | 2.9142 | 0.042306
| 1:04 | 2.9144 | 0.042241
| 1:04 | 2.9147 | 0.042167
| 1:04 | 2.915 | 0.042072
| 1:04 | 2.9153 | 0.041954
| 1:04 | 2.9156 | 0.041826
| 1:04 | 2.9158 | 0.041689
| 1:04 | 2.9161 | 0.04155
| 1:04 | 2.9164 | 0.041409
| 1:04 | 2.9167 | 0.041264
| 1:04 | 2.9169 | 0.041118
| 1:04 | 2.9172 | 0.040968
| 1:04 | 2.9175 | 0.040817
| 1:04 | 2.9178 | 0.040662
| 1:04 | 2.9181 | 0.040505
| 1:04 | 2.9183 | 0.040345
| 1:04 | 2.9186 | 0.04018
| 1:04 | 2.9189 | 0.040011
| 1:04 | 2.9192 | 0.039839
| 1:04 | 2.9194 | 0.039666
| 1:04 | 2.9197 | 0.039494
| 1:04 | 2.92 | 0.039323
| 1:04 | 2.9203 | 0.039154
| 1:04 | 2.9206 | 0.038986
| 1:04 | 2.9208 | 0.038819
| 1:04 | 2.9211 | 0.038653
| 1:04 | 2.9214 | 0.038488
| 1:04 | 2.9217 | 0.038325
| 1:04 | 2.9219 | 0.038163
| 1:04 | 2.9222 | 0.038002
| 1:04 | 2.9225 | 0.037842
| 1:04 | 2.9228 | 0.037684
| 1:04 | 2.9231 | 0.037527
| 1:04 | 2.9233 | 0.03737
| 1:04 | 2.9236 | 0.037216
| 1:04 | 2.9239 | 0.037062
| 1:04 | 2.9242 | 0.03691
| 1:04 | 2.9244 | 0.036758
| 1:04 | 2.9247 | 0.036608
| 1:04 | 2.925 | 0.036459
| 1:04 | 2.9253 | 0.036312
| 1:04 | 2.9256 | 0.036169
| 1:04 | 2.9258 | 0.036033
| 1:04 | 2.9261 | 0.035903
| 1:04 | 2.9264 | 0.035774
| 1:04 | 2.9267 | 0.035644
| 1:04 | 2.9269 | 0.035514
| 1:04 | 2.9272 | 0.035383
| 1:04 | 2.9275 | 0.035252
| 1:04 | 2.9278 | 0.035119
| 1:04 | 2.9281 | 0.034986
| 1:04 | 2.9283 | 0.034852
| 1:05 | 2.9286 | 0.034714
| 1:05 | 2.9289 | 0.034575
| 1:05 | 2.9292 | 0.034436
| 1:05 | 2.9294 | 0.034299
| 1:05 | 2.9297 | 0.034163
| 1:05 | 2.93 | 0.034029
| 1:05 | 2.9303 | 0.033895
| 1:05 | 2.9306 | 0.033763
| 1:05 | 2.9308 | 0.033632
| 1:05 | 2.9311 | 0.033502
| 1:05 | 2.9314 | 0.033373
| 1:05 | 2.9317 | 0.033245
| 1:05 | 2.9319 | 0.033119
| 1:05 | 2.9322 | 0.032998
| 1:05 | 2.9325 | 0.032883
| 1:05 | 2.9328 | 0.032773
| 1:05 | 2.9331 | 0.032669
| 1:05 | 2.9333 | 0.032567
| 1:05 | 2.9336 | 0.032465
| 1:05 | 2.9339 | 0.032364
| 1:05 | 2.9342 | 0.032264
| 1:05 | 2.9344 | 0.032165
| 1:05 | 2.9347 | 0.032067
| 1:05 | 2.935 | 0.031969
| 1:05 | 2.9353 | 0.031872
| 1:05 | 2.9356 | 0.031776
| 1:05 | 2.9358 | 0.03168
| 1:05 | 2.9361 | 0.031585
| 1:05 | 2.9364 | 0.031492
| 1:05 | 2.9367 | 0.031398
| 1:05 | 2.9369 | 0.031306
| 1:05 | 2.9372 | 0.031214
| 1:05 | 2.9375 | 0.031123
| 1:05 | 2.9378 | 0.031033
| 1:05 | 2.9381 | 0.030943
| 1:05 | 2.9383 | 0.030855
| 1:05 | 2.9386 | 0.030767
| 1:05 | 2.9389 | 0.030679
| 1:05 | 2.9392 | 0.030593
| 1:05 | 2.9394 | 0.030507
| 1:05 | 2.9397 | 0.030422
| 1:05 | 2.94 | 0.030338
| 1:05 | 2.9403 | 0.030255
| 1:05 | 2.9406 | 0.030172
| 1:05 | 2.9408 | 0.03009
| 1:05 | 2.9411 | 0.030009
| 1:05 | 2.9414 | 0.029928
| 1:05 | 2.9417 | 0.029848
| 1:05 | 2.9419 | 0.029769
| 1:05 | 2.9422 | 0.029691
| 1:05 | 2.9425 | 0.029614
| 1:05 | 2.9428 | 0.029537
| 1:05 | 2.9431 | 0.029461
| 1:05 | 2.9433 | 0.029386
| 1:05 | 2.9436 | 0.029312
| 1:05 | 2.9439 | 0.029238
| 1:05 | 2.9442 | 0.029165
| 1:05 | 2.9444 | 0.029093
| 1:05 | 2.9447 | 0.029021
| 1:06 | 2.945 | 0.028951
| 1:06 | 2.9453 | 0.028881
| 1:06 | 2.9456 | 0.028812
| 1:06 | 2.9458 | 0.028745
| 1:06 | 2.9461 | 0.02868
| 1:06 | 2.9464 | 0.028617
| 1:06 | 2.9467 | 0.028555
| 1:06 | 2.9469 | 0.028495
| 1:06 | 2.9472 | 0.028436
| 1:06 | 2.9475 | 0.028379
| 1:06 | 2.9478 | 0.028324
| 1:06 | 2.9481 | 0.028271
| 1:06 | 2.9483 | 0.028219
| 1:06 | 2.9486 | 0.028169
| 1:06 | 2.9489 | 0.02812
| 1:06 | 2.9492 | 0.028074
| 1:06 | 2.9494 | 0.028036
| 1:06 | 2.9497 | 0.028006
| 1:06 | 2.95 | 0.027979
| 1:06 | 2.9503 | 0.027953
| 1:06 | 2.9506 | 0.027926
| 1:06 | 2.9508 | 0.0279
| 1:06 | 2.9511 | 0.027875
| 1:06 | 2.9514 | 0.027849
| 1:06 | 2.9517 | 0.027824
| 1:06 | 2.9519 | 0.027799
| 1:06 | 2.9522 | 0.027774
| 1:06 | 2.9525 | 0.027749
| 1:06 | 2.9528 | 0.027725
| 1:06 | 2.9531 | 0.0277
| 1:06 | 2.9533 | 0.027676
| 1:06 | 2.9536 | 0.027652
| 1:06 | 2.9539 | 0.027629
| 1:06 | 2.9542 | 0.027606
| 1:06 | 2.9544 | 0.027582
| 1:06 | 2.9547 | 0.02756
| 1:06 | 2.955 | 0.027537
| 1:06 | 2.9553 | 0.027514
| 1:06 | 2.9556 | 0.027492
| 1:06 | 2.9558 | 0.02747
| 1:06 | 2.9561 | 0.027448
| 1:06 | 2.9564 | 0.027426
| 1:06 | 2.9567 | 0.027402
| 1:06 | 2.9569 | 0.027378
| 1:06 | 2.9572 | 0.027353
| 1:06 | 2.9575 | 0.027327
| 1:06 | 2.9578 | 0.027302
| 1:06 | 2.9581 | 0.027278
| 1:06 | 2.9583 | 0.027255
| 1:06 | 2.9586 | 0.027232
| 1:06 | 2.9589 | 0.027211
| 1:06 | 2.9592 | 0.027191
| 1:06 | 2.9594 | 0.027172
| 1:06 | 2.9597 | 0.027154
| 1:06 | 2.96 | 0.027137
| 1:06 | 2.9603 | 0.02713
| 1:06 | 2.9606 | 0.027136
| 1:06 | 2.9608 | 0.027149
| 1:06 | 2.9611 | 0.027166
| 1:06 | 2.9614 | 0.027187
| 1:06 | 2.9617 | 0.027211
| 1:07 | 2.9619 | 0.027239
| 1:07 | 2.9622 | 0.027271
| 1:07 | 2.9625 | 0.027307
| 1:07 | 2.9628 | 0.027347
| 1:07 | 2.9631 | 0.02739
| 1:07 | 2.9633 | 0.027437
| 1:07 | 2.9636 | 0.027488
| 1:07 | 2.9639 | 0.027542
| 1:07 | 2.9642 | 0.027601
| 1:07 | 2.9644 | 0.027662
| 1:07 | 2.9647 | 0.027722
| 1:07 | 2.965 | 0.027782
| 1:07 | 2.9653 | 0.02784
| 1:07 | 2.9656 | 0.027897
| 1:07 | 2.9658 | 0.027953
| 1:07 | 2.9661 | 0.028008
| 1:07 | 2.9664 | 0.028062
| 1:07 | 2.9667 | 0.028115
| 1:07 | 2.9669 | 0.028167
| 1:07 | 2.9672 | 0.028217
| 1:07 | 2.9675 | 0.028267
| 1:07 | 2.9678 | 0.028318
| 1:07 | 2.9681 | 0.028371
| 1:07 | 2.9683 | 0.028427
| 1:07 | 2.9686 | 0.028485
| 1:07 | 2.9689 | 0.028545
| 1:07 | 2.9692 | 0.028607
| 1:07 | 2.9694 | 0.028671
| 1:07 | 2.9697 | 0.028737
| 1:07 | 2.97 | 0.028806
| 1:07 | 2.9703 | 0.028876
| 1:07 | 2.9706 | 0.02895
| 1:07 | 2.9708 | 0.029027
| 1:07 | 2.9711 | 0.029107
| 1:07 | 2.9714 | 0.02919
| 1:07 | 2.9717 | 0.029277
| 1:07 | 2.9719 | 0.029367
| 1:07 | 2.9722 | 0.029461
| 1:07 | 2.9725 | 0.029558
| 1:07 | 2.9728 | 0.029655
| 1:07 | 2.9731 | 0.029754
| 1:07 | 2.9733 | 0.029855
| 1:07 | 2.9736 | 0.029956
| 1:07 | 2.9739 | 0.030058
| 1:07 | 2.9742 | 0.030162
| 1:07 | 2.9744 | 0.030267
| 1:07 | 2.9747 | 0.030373
| 1:07 | 2.975 | 0.03048
| 1:07 | 2.9753 | 0.030588
| 1:07 | 2.9756 | 0.030698
| 1:07 | 2.9758 | 0.030809
| 1:07 | 2.9761 | 0.03092
| 1:07 | 2.9764 | 0.031033
| 1:07 | 2.9767 | 0.031147
| 1:07 | 2.9769 | 0.031262
| 1:07 | 2.9772 | 0.031377
| 1:07 | 2.9775 | 0.031492
| 1:07 | 2.9778 | 0.031609
| 1:07 | 2.9781 | 0.031726
| 1:08 | 2.9783 | 0.031843
| 1:08 | 2.9786 | 0.031961
| 1:08 | 2.9789 | 0.032143
| 1:08 | 2.9792 | 0.032325
| 1:08 | 2.9794 | 0.032506
| 1:08 | 2.9797 | 0.032688
| 1:08 | 2.98 | 0.032869
| 1:08 | 2.9803 | 0.03305
| 1:08 | 2.9806 | 0.03323
| 1:08 | 2.9808 | 0.033411
| 1:08 | 2.9811 | 0.033591
| 1:08 | 2.9814 | 0.033771
| 1:08 | 2.9817 | 0.033951
| 1:08 | 2.9819 | 0.03413
| 1:08 | 2.9822 | 0.03431
| 1:08 | 2.9825 | 0.034489
| 1:08 | 2.9828 | 0.034668
| 1:08 | 2.9831 | 0.034847
| 1:08 | 2.9833 | 0.035025
| 1:08 | 2.9836 | 0.035204
| 1:08 | 2.9839 | 0.035382
| 1:08 | 2.9842 | 0.03556
| 1:08 | 2.9844 | 0.035738
| 1:08 | 2.9847 | 0.035915
| 1:08 | 2.985 | 0.036093
| 1:08 | 2.9853 | 0.03627
| 1:08 | 2.9856 | 0.036447
| 1:08 | 2.9858 | 0.036624
| 1:08 | 2.9861 | 0.0368
| 1:08 | 2.9864 | 0.036977
| 1:08 | 2.9867 | 0.037153
| 1:08 | 2.9869 | 0.037329
| 1:08 | 2.9872 | 0.037504
| 1:08 | 2.9875 | 0.03768
| 1:08 | 2.9878 | 0.037855
| 1:08 | 2.9881 | 0.03803
| 1:08 | 2.9883 | 0.038205
| 1:08 | 2.9886 | 0.03838
| 1:08 | 2.9889 | 0.038554
| 1:08 | 2.9892 | 0.038728
| 1:08 | 2.9894 | 0.038902
| 1:08 | 2.9897 | 0.039076
| 1:08 | 2.99 | 0.03925
| 1:08 | 2.9903 | 0.039423
| 1:08 | 2.9906 | 0.039596
| 1:08 | 2.9908 | 0.039769
| 1:08 | 2.9911 | 0.039942
| 1:08 | 2.9914 | 0.040115
| 1:08 | 2.9917 | 0.040287
| 1:08 | 2.9919 | 0.040459
| 1:08 | 2.9922 | 0.040631
| 1:08 | 2.9925 | 0.040803
| 1:08 | 2.9928 | 0.040974
| 1:08 | 2.9931 | 0.041145
| 1:08 | 2.9933 | 0.041316
| 1:08 | 2.9936 | 0.041487
| 1:08 | 2.9939 | 0.041658
| 1:08 | 2.9942 | 0.041828
| 1:08 | 2.9944 | 0.041998
| 1:08 | 2.9947 | 0.042168
| 1:08 | 2.995 | 0.042338
| 1:09 | 2.9953 | 0.042507
| 1:09 | 2.9956 | 0.042677
| 1:09 | 2.9958 | 0.042846
| 1:09 | 2.9961 | 0.043015
| 1:09 | 2.9964 | 0.043183
| 1:09 | 2.9967 | 0.043352
| 1:09 | 2.9969 | 0.04352
| 1:09 | 2.9972 | 0.043688
| 1:09 | 2.9975 | 0.043856
| 1:09 | 2.9978 | 0.044024
| 1:09 | 2.9981 | 0.044191
| 1:09 | 2.9983 | 0.044358
| 1:09 | 2.9986 | 0.044525
| 1:09 | 2.9989 | 0.044692
| 1:09 | 2.9992 | 0.044859
| 1:09 | 2.9994 | 0.045025
| 1:09 | 2.9997 | 0.045191
| 1:09 | 3 | 0.045357
| 1:09 | 3.0003 | 0.045523
| 1:09 | 3.0006 | 0.045688
| 1:09 | 3.0008 | 0.045854
| 1:09 | 3.0011 | 0.046019
| 1:09 | 3.0014 | 0.046183
| 1:09 | 3.0017 | 0.046348
| 1:09 | 3.0019 | 0.046513
| 1:09 | 3.0022 | 0.046677
| 1:09 | 3.0025 | 0.04684
| 1:09 | 3.0028 | 0.047003
| 1:09 | 3.0031 | 0.047166
| 1:09 | 3.0033 | 0.047328
| 1:09 | 3.0036 | 0.047489
| 1:09 | 3.0039 | 0.04765
| 1:09 | 3.0042 | 0.047811
| 1:09 | 3.0044 | 0.047971
| 1:09 | 3.0047 | 0.048131
| 1:09 | 3.005 | 0.04829
| 1:09 | 3.0053 | 0.048449
| 1:09 | 3.0056 | 0.048607
| 1:09 | 3.0058 | 0.048765
| 1:09 | 3.0061 | 0.048922
| 1:09 | 3.0064 | 0.049079
| 1:09 | 3.0067 | 0.049236
| 1:09 | 3.0069 | 0.049391
| 1:09 | 3.0072 | 0.049547
| 1:09 | 3.0075 | 0.049702
| 1:09 | 3.0078 | 0.049856
| 1:09 | 3.0081 | 0.05001
| 1:09 | 3.0083 | 0.050164
| 1:09 | 3.0086 | 0.050317
| 1:09 | 3.0089 | 0.050469
| 1:09 | 3.0092 | 0.050621
| 1:09 | 3.0094 | 0.050773
| 1:09 | 3.0097 | 0.050924
| 1:09 | 3.01 | 0.051074
| 1:09 | 3.0103 | 0.051224
| 1:09 | 3.0106 | 0.051374
| 1:09 | 3.0108 | 0.051523
| 1:09 | 3.0111 | 0.051672
| 1:09 | 3.0114 | 0.05182
| 1:10 | 3.0117 | 0.051968
| 1:10 | 3.0119 | 0.052115
| 1:10 | 3.0122 | 0.052262
| 1:10 | 3.0125 | 0.052408
| 1:10 | 3.0128 | 0.052554
| 1:10 | 3.0131 | 0.052699
| 1:10 | 3.0133 | 0.052844
| 1:10 | 3.0136 | 0.052988
| 1:10 | 3.0139 | 0.053132
| 1:10 | 3.0142 | 0.053275
| 1:10 | 3.0144 | 0.053418
| 1:10 | 3.0147 | 0.053561
| 1:10 | 3.015 | 0.053703
| 1:10 | 3.0153 | 0.053844
| 1:10 | 3.0156 | 0.053985
| 1:10 | 3.0158 | 0.054126
| 1:10 | 3.0161 | 0.054266
| 1:10 | 3.0164 | 0.054405
| 1:10 | 3.0167 | 0.054544
| 1:10 | 3.0169 | 0.054683
| 1:10 | 3.0172 | 0.054821
| 1:10 | 3.0175 | 0.054959
| 1:10 | 3.0178 | 0.055096
| 1:10 | 3.0181 | 0.055233
| 1:10 | 3.0183 | 0.055369
| 1:10 | 3.0186 | 0.055505
| 1:10 | 3.0189 | 0.05564
| 1:10 | 3.0192 | 0.055775
| 1:10 | 3.0194 | 0.055909
| 1:10 | 3.0197 | 0.056043
| 1:10 | 3.02 | 0.056176
| 1:10 | 3.0203 | 0.056309
| 1:10 | 3.0206 | 0.056442
| 1:10 | 3.0208 | 0.056574
| 1:10 | 3.0211 | 0.056705
| 1:10 | 3.0214 | 0.056836
| 1:10 | 3.0217 | 0.056967
| 1:10 | 3.0219 | 0.057097
| 1:10 | 3.0222 | 0.057227
| 1:10 | 3.0225 | 0.057356
| 1:10 | 3.0228 | 0.057484
| 1:10 | 3.0231 | 0.057613
| 1:10 | 3.0233 | 0.057741
| 1:10 | 3.0236 | 0.057868
| 1:10 | 3.0239 | 0.057995
| 1:10 | 3.0242 | 0.058121
| 1:10 | 3.0244 | 0.058247
| 1:10 | 3.0247 | 0.058372
| 1:10 | 3.025 | 0.058497
| 1:10 | 3.0253 | 0.058622
| 1:10 | 3.0256 | 0.058746
| 1:10 | 3.0258 | 0.05887
| 1:10 | 3.0261 | 0.058993
| 1:10 | 3.0264 | 0.059116
| 1:10 | 3.0267 | 0.059238
| 1:10 | 3.0269 | 0.05936
| 1:10 | 3.0272 | 0.059481
| 1:10 | 3.0275 | 0.059602
| 1:10 | 3.0278 | 0.059722
| 1:10 | 3.0281 | 0.059843
| 1:10 | 3.0283 | 0.059963
| 1:11 | 3.0286 | 0.060084
| 1:11 | 3.0289 | 0.060204
| 1:11 | 3.0292 | 0.060324
| 1:11 | 3.0294 | 0.060441
| 1:11 | 3.0297 | 0.060555
| 1:11 | 3.03 | 0.060667
| 1:11 | 3.0303 | 0.060777
| 1:11 | 3.0306 | 0.060884
| 1:11 | 3.0308 | 0.060988
| 1:11 | 3.0311 | 0.06109
| 1:11 | 3.0314 | 0.06119
| 1:11 | 3.0317 | 0.061288
| 1:11 | 3.0319 | 0.061384
| 1:11 | 3.0322 | 0.061478
| 1:11 | 3.0325 | 0.061571
| 1:11 | 3.0328 | 0.061662
| 1:11 | 3.0331 | 0.061752
| 1:11 | 3.0333 | 0.06184
| 1:11 | 3.0336 | 0.061926
| 1:11 | 3.0339 | 0.06201
| 1:11 | 3.0342 | 0.062093
| 1:11 | 3.0344 | 0.062174
| 1:11 | 3.0347 | 0.062254
| 1:11 | 3.035 | 0.062332
| 1:11 | 3.0353 | 0.06241
| 1:11 | 3.0356 | 0.062485
| 1:11 | 3.0358 | 0.06256
| 1:11 | 3.0361 | 0.062634
| 1:11 | 3.0364 | 0.062706
| 1:11 | 3.0367 | 0.062777
| 1:11 | 3.0369 | 0.062847
| 1:11 | 3.0372 | 0.062915
| 1:11 | 3.0375 | 0.062983
| 1:11 | 3.0378 | 0.063049
| 1:11 | 3.0381 | 0.063114
| 1:11 | 3.0383 | 0.063177
| 1:11 | 3.0386 | 0.06324
| 1:11 | 3.0389 | 0.063301
| 1:11 | 3.0392 | 0.063361
| 1:11 | 3.0394 | 0.063419
| 1:11 | 3.0397 | 0.063477
| 1:11 | 3.04 | 0.063533
| 1:11 | 3.0403 | 0.063588
| 1:11 | 3.0406 | 0.063642
| 1:11 | 3.0408 | 0.063694
| 1:11 | 3.0411 | 0.063745
| 1:11 | 3.0414 | 0.063795
| 1:11 | 3.0417 | 0.063844
| 1:11 | 3.0419 | 0.063892
| 1:11 | 3.0422 | 0.063938
| 1:11 | 3.0425 | 0.063983
| 1:11 | 3.0428 | 0.064027
| 1:11 | 3.0431 | 0.06407
| 1:11 | 3.0433 | 0.064111
| 1:11 | 3.0436 | 0.064152
| 1:11 | 3.0439 | 0.064192
| 1:11 | 3.0442 | 0.064233
| 1:11 | 3.0444 | 0.064274
| 1:11 | 3.0447 | 0.064315
| 1:12 | 3.045 | 0.064355
| 1:12 | 3.0453 | 0.064396
| 1:12 | 3.0456 | 0.064437
| 1:12 | 3.0458 | 0.064477
| 1:12 | 3.0461 | 0.064518
| 1:12 | 3.0464 | 0.064559
| 1:12 | 3.0467 | 0.064599
| 1:12 | 3.0469 | 0.06464
| 1:12 | 3.0472 | 0.064681
| 1:12 | 3.0475 | 0.064721
| 1:12 | 3.0478 | 0.064762
| 1:12 | 3.0481 | 0.064803
| 1:12 | 3.0483 | 0.064843
| 1:12 | 3.0486 | 0.064884
| 1:12 | 3.0489 | 0.064925
| 1:12 | 3.0492 | 0.064965
| 1:12 | 3.0494 | 0.065006
| 1:12 | 3.0497 | 0.065047
| 1:12 | 3.05 | 0.065087
| 1:12 | 3.0503 | 0.065128
| 1:12 | 3.0506 | 0.065168
| 1:12 | 3.0508 | 0.065209
| 1:12 | 3.0511 | 0.06525
| 1:12 | 3.0514 | 0.06529
| 1:12 | 3.0517 | 0.065331
| 1:12 | 3.0519 | 0.065372
| 1:12 | 3.0522 | 0.065412
| 1:12 | 3.0525 | 0.065453
| 1:12 | 3.0528 | 0.065493
| 1:12 | 3.0531 | 0.065534
| 1:12 | 3.0533 | 0.065575
| 1:12 | 3.0536 | 0.065615
| 1:12 | 3.0539 | 0.065656
| 1:12 | 3.0542 | 0.065696
| 1:12 | 3.0544 | 0.065737
| 1:12 | 3.0547 | 0.065778
| 1:12 | 3.055 | 0.065818
| 1:12 | 3.0553 | 0.065859
| 1:12 | 3.0556 | 0.0659
| 1:12 | 3.0558 | 0.06594
| 1:12 | 3.0561 | 0.065981
| 1:12 | 3.0564 | 0.066021
| 1:12 | 3.0567 | 0.066062
| 1:12 | 3.0569 | 0.066103
| 1:12 | 3.0572 | 0.066143
| 1:12 | 3.0575 | 0.066184
| 1:12 | 3.0578 | 0.066224
| 1:12 | 3.0581 | 0.066265
| 1:12 | 3.0583 | 0.066306
| 1:12 | 3.0586 | 0.066346
| 1:12 | 3.0589 | 0.066387
| 1:12 | 3.0592 | 0.066427
| 1:12 | 3.0594 | 0.066468
| 1:12 | 3.0597 | 0.066508
| 1:12 | 3.06 | 0.066549
| 1:12 | 3.0603 | 0.066589
| 1:12 | 3.0606 | 0.06663
| 1:12 | 3.0608 | 0.066671
| 1:12 | 3.0611 | 0.066711
| 1:12 | 3.0614 | 0.066751
| 1:12 | 3.0617 | 0.066789
| 1:13 | 3.0619 | 0.066827
| 1:13 | 3.0622 | 0.066863
| 1:13 | 3.0625 | 0.066899
| 1:13 | 3.0628 | 0.066939
| 1:13 | 3.0631 | 0.066982
| 1:13 | 3.0633 | 0.067029
| 1:13 | 3.0636 | 0.067079
| 1:13 | 3.0639 | 0.067133
| 1:13 | 3.0642 | 0.067189
| 1:13 | 3.0644 | 0.06725
| 1:13 | 3.0647 | 0.067313
| 1:13 | 3.065 | 0.067376
| 1:13 | 3.0653 | 0.067439
| 1:13 | 3.0656 | 0.067502
| 1:13 | 3.0658 | 0.067565
| 1:13 | 3.0661 | 0.067627
| 1:13 | 3.0664 | 0.06769
| 1:13 | 3.0667 | 0.067752
| 1:13 | 3.0669 | 0.067814
| 1:13 | 3.0672 | 0.067875
| 1:13 | 3.0675 | 0.067937
| 1:13 | 3.0678 | 0.067999
| 1:13 | 3.0681 | 0.06806
| 1:13 | 3.0683 | 0.068121
| 1:13 | 3.0686 | 0.068182
| 1:13 | 3.0689 | 0.068243
| 1:13 | 3.0692 | 0.068303
| 1:13 | 3.0694 | 0.068364
| 1:13 | 3.0697 | 0.068424
| 1:13 | 3.07 | 0.068484
| 1:13 | 3.0703 | 0.068544
| 1:13 | 3.0706 | 0.068604
| 1:13 | 3.0708 | 0.068664
| 1:13 | 3.0711 | 0.068723
| 1:13 | 3.0714 | 0.068782
| 1:13 | 3.0717 | 0.068842
| 1:13 | 3.0719 | 0.068901
| 1:13 | 3.0722 | 0.068959
| 1:13 | 3.0725 | 0.069018
| 1:13 | 3.0728 | 0.069077
| 1:13 | 3.0731 | 0.069135
| 1:13 | 3.0733 | 0.069193
| 1:13 | 3.0736 | 0.069251
| 1:13 | 3.0739 | 0.069309
| 1:13 | 3.0742 | 0.069367
| 1:13 | 3.0744 | 0.069424
| 1:13 | 3.0747 | 0.069482
| 1:13 | 3.075 | 0.069539
| 1:13 | 3.0753 | 0.069596
| 1:13 | 3.0756 | 0.069653
| 1:13 | 3.0758 | 0.069709
| 1:13 | 3.0761 | 0.069766
| 1:13 | 3.0764 | 0.069822
| 1:13 | 3.0767 | 0.069879
| 1:13 | 3.0769 | 0.069935
| 1:13 | 3.0772 | 0.06999
| 1:13 | 3.0775 | 0.070046
| 1:13 | 3.0778 | 0.070102
| 1:13 | 3.0781 | 0.070157
| 1:14 | 3.0783 | 0.070212
| 1:14 | 3.0786 | 0.070267
| 1:14 | 3.0789 | 0.070322
| 1:14 | 3.0792 | 0.070376
| 1:14 | 3.0794 | 0.070429
| 1:14 | 3.0797 | 0.07048
| 1:14 | 3.08 | 0.07053
| 1:14 | 3.0803 | 0.070578
| 1:14 | 3.0806 | 0.070624
| 1:14 | 3.0808 | 0.070669
| 1:14 | 3.0811 | 0.070713
| 1:14 | 3.0814 | 0.070755
| 1:14 | 3.0817 | 0.070795
| 1:14 | 3.0819 | 0.070834
| 1:14 | 3.0822 | 0.070871
| 1:14 | 3.0825 | 0.070907
| 1:14 | 3.0828 | 0.070941
| 1:14 | 3.0831 | 0.070974
| 1:14 | 3.0833 | 0.071005
| 1:14 | 3.0836 | 0.071035
| 1:14 | 3.0839 | 0.071063
| 1:14 | 3.0842 | 0.07109
| 1:14 | 3.0844 | 0.071115
| 1:14 | 3.0847 | 0.071139
| 1:14 | 3.085 | 0.071162
| 1:14 | 3.0853 | 0.071185
| 1:14 | 3.0856 | 0.071208
| 1:14 | 3.0858 | 0.07123
| 1:14 | 3.0861 | 0.071251
| 1:14 | 3.0864 | 0.071272
| 1:14 | 3.0867 | 0.071292
| 1:14 | 3.0869 | 0.071312
| 1:14 | 3.0872 | 0.071331
| 1:14 | 3.0875 | 0.07135
| 1:14 | 3.0878 | 0.071369
| 1:14 | 3.0881 | 0.071387
| 1:14 | 3.0883 | 0.071404
| 1:14 | 3.0886 | 0.071421
| 1:14 | 3.0889 | 0.071437
| 1:14 | 3.0892 | 0.071453
| 1:14 | 3.0894 | 0.071468
| 1:14 | 3.0897 | 0.071483
| 1:14 | 3.09 | 0.071497
| 1:14 | 3.0903 | 0.071511
| 1:14 | 3.0906 | 0.071525
| 1:14 | 3.0908 | 0.071537
| 1:14 | 3.0911 | 0.07155
| 1:14 | 3.0914 | 0.071562
| 1:14 | 3.0917 | 0.071573
| 1:14 | 3.0919 | 0.071584
| 1:14 | 3.0922 | 0.071594
| 1:14 | 3.0925 | 0.071604
| 1:14 | 3.0928 | 0.071613
| 1:14 | 3.0931 | 0.071622
| 1:14 | 3.0933 | 0.07163
| 1:14 | 3.0936 | 0.071638
| 1:14 | 3.0939 | 0.071645
| 1:14 | 3.0942 | 0.071652
| 1:14 | 3.0944 | 0.071659
| 1:14 | 3.0947 | 0.071664
| 1:14 | 3.095 | 0.07167
| 1:15 | 3.0953 | 0.071675
| 1:15 | 3.0956 | 0.071679
| 1:15 | 3.0958 | 0.071683
| 1:15 | 3.0961 | 0.071685
| 1:15 | 3.0964 | 0.071685
| 1:15 | 3.0967 | 0.071683
| 1:15 | 3.0969 | 0.071679
| 1:15 | 3.0972 | 0.071673
| 1:15 | 3.0975 | 0.071665
| 1:15 | 3.0978 | 0.071654
| 1:15 | 3.0981 | 0.071642
| 1:15 | 3.0983 | 0.071627
| 1:15 | 3.0986 | 0.07161
| 1:15 | 3.0989 | 0.071592
| 1:15 | 3.0992 | 0.071571
| 1:15 | 3.0994 | 0.071548
| 1:15 | 3.0997 | 0.071523
| 1:15 | 3.1 | 0.071496
| 1:15 | 3.1003 | 0.071463
| 1:15 | 3.1006 | 0.071421
| 1:15 | 3.1008 | 0.071378
| 1:15 | 3.1011 | 0.071335
| 1:15 | 3.1014 | 0.071292
| 1:15 | 3.1017 | 0.071248
| 1:15 | 3.1019 | 0.071203
| 1:15 | 3.1022 | 0.071158
| 1:15 | 3.1025 | 0.071113
| 1:15 | 3.1028 | 0.071067
| 1:15 | 3.1031 | 0.071021
| 1:15 | 3.1033 | 0.070974
| 1:15 | 3.1036 | 0.070926
| 1:15 | 3.1039 | 0.070878
| 1:15 | 3.1042 | 0.07083
| 1:15 | 3.1044 | 0.070781
| 1:15 | 3.1047 | 0.070731
| 1:15 | 3.105 | 0.070679
| 1:15 | 3.1053 | 0.070626
| 1:15 | 3.1056 | 0.070573
| 1:15 | 3.1058 | 0.070518
| 1:15 | 3.1061 | 0.070462
| 1:15 | 3.1064 | 0.070405
| 1:15 | 3.1067 | 0.070347
| 1:15 | 3.1069 | 0.070287
| 1:15 | 3.1072 | 0.070227
| 1:15 | 3.1075 | 0.070167
| 1:15 | 3.1078 | 0.070107
| 1:15 | 3.1081 | 0.070047
| 1:15 | 3.1083 | 0.069988
| 1:15 | 3.1086 | 0.069929
| 1:15 | 3.1089 | 0.06987
| 1:15 | 3.1092 | 0.069812
| 1:15 | 3.1094 | 0.069754
| 1:15 | 3.1097 | 0.069696
| 1:15 | 3.11 | 0.069639
| 1:15 | 3.1103 | 0.069582
| 1:15 | 3.1106 | 0.069525
| 1:15 | 3.1108 | 0.069469
| 1:15 | 3.1111 | 0.069413
| 1:15 | 3.1114 | 0.069358
| 1:16 | 3.1117 | 0.069302
| 1:16 | 3.1119 | 0.069248
| 1:16 | 3.1122 | 0.069193
| 1:16 | 3.1125 | 0.069141
| 1:16 | 3.1128 | 0.069093
| 1:16 | 3.1131 | 0.069048
| 1:16 | 3.1133 | 0.069006
| 1:16 | 3.1136 | 0.068967
| 1:16 | 3.1139 | 0.068931
| 1:16 | 3.1142 | 0.068899
| 1:16 | 3.1144 | 0.06887
| 1:16 | 3.1147 | 0.068844
| 1:16 | 3.115 | 0.068819
| 1:16 | 3.1153 | 0.068796
| 1:16 | 3.1156 | 0.068773
| 1:16 | 3.1158 | 0.068753
| 1:16 | 3.1161 | 0.068733
| 1:16 | 3.1164 | 0.068715
| 1:16 | 3.1167 | 0.068699
| 1:16 | 3.1169 | 0.068683
| 1:16 | 3.1172 | 0.068669
| 1:16 | 3.1175 | 0.068655
| 1:16 | 3.1178 | 0.068635
| 1:16 | 3.1181 | 0.068611
| 1:16 | 3.1183 | 0.068581
| 1:16 | 3.1186 | 0.068547
| 1:16 | 3.1189 | 0.068508
| 1:16 | 3.1192 | 0.068465
| 1:16 | 3.1194 | 0.068416
| 1:16 | 3.1197 | 0.068364
| 1:16 | 3.12 | 0.068313
| 1:16 | 3.1203 | 0.068263
| 1:16 | 3.1206 | 0.068213
| 1:16 | 3.1208 | 0.068164
| 1:16 | 3.1211 | 0.068116
| 1:16 | 3.1214 | 0.068068
| 1:16 | 3.1217 | 0.06802
| 1:16 | 3.1219 | 0.067974
| 1:16 | 3.1222 | 0.067928
| 1:16 | 3.1225 | 0.067882
| 1:16 | 3.1228 | 0.067841
| 1:16 | 3.1231 | 0.067804
| 1:16 | 3.1233 | 0.067767
| 1:16 | 3.1236 | 0.067731
| 1:16 | 3.1239 | 0.067696
| 1:16 | 3.1242 | 0.067662
| 1:16 | 3.1244 | 0.067629
| 1:16 | 3.1247 | 0.067596
| 1:16 | 3.125 | 0.067565
| 1:16 | 3.1253 | 0.067535
| 1:16 | 3.1256 | 0.067506
| 1:16 | 3.1258 | 0.067477
| 1:16 | 3.1261 | 0.067449
| 1:16 | 3.1264 | 0.06742
| 1:16 | 3.1267 | 0.06739
| 1:16 | 3.1269 | 0.06736
| 1:16 | 3.1272 | 0.06733
| 1:16 | 3.1275 | 0.0673
| 1:16 | 3.1278 | 0.067272
| 1:16 | 3.1281 | 0.067243
| 1:16 | 3.1283 | 0.067215
| 1:17 | 3.1286 | 0.067188
| 1:17 | 3.1289 | 0.067161
| 1:17 | 3.1292 | 0.067134
| 1:17 | 3.1294 | 0.067106
| 1:17 | 3.1297 | 0.067077
| 1:17 | 3.13 | 0.067047
| 1:17 | 3.1303 | 0.067016
| 1:17 | 3.1306 | 0.066984
| 1:17 | 3.1308 | 0.066951
| 1:17 | 3.1311 | 0.066917
| 1:17 | 3.1314 | 0.066882
| 1:17 | 3.1317 | 0.066851
| 1:17 | 3.1319 | 0.066825
| 1:17 | 3.1322 | 0.066805
| 1:17 | 3.1325 | 0.06679
| 1:17 | 3.1328 | 0.06678
| 1:17 | 3.1331 | 0.066776
| 1:17 | 3.1333 | 0.066777
| 1:17 | 3.1336 | 0.066783
| 1:17 | 3.1339 | 0.066793
| 1:17 | 3.1342 | 0.066803
| 1:17 | 3.1344 | 0.066813
| 1:17 | 3.1347 | 0.066824
| 1:17 | 3.135 | 0.066835
| 1:17 | 3.1353 | 0.066844
| 1:17 | 3.1356 | 0.066853
| 1:17 | 3.1358 | 0.066861
| 1:17 | 3.1361 | 0.066868
| 1:17 | 3.1364 | 0.066874
| 1:17 | 3.1367 | 0.066879
| 1:17 | 3.1369 | 0.066883
| 1:17 | 3.1372 | 0.066886
| 1:17 | 3.1375 | 0.066888
| 1:17 | 3.1378 | 0.066889
| 1:17 | 3.1381 | 0.066889
| 1:17 | 3.1383 | 0.066889
| 1:17 | 3.1386 | 0.066887
| 1:17 | 3.1389 | 0.066885
| 1:17 | 3.1392 | 0.066881
| 1:17 | 3.1394 | 0.066877
| 1:17 | 3.1397 | 0.066872
| 1:17 | 3.14 | 0.066865
| 1:17 | 3.1403 | 0.066859
| 1:17 | 3.1406 | 0.066854
| 1:17 | 3.1408 | 0.06685
| 1:17 | 3.1411 | 0.066847
| 1:17 | 3.1414 | 0.066846
| 1:17 | 3.1417 | 0.066846
| 1:17 | 3.1419 | 0.066847
| 1:17 | 3.1422 | 0.06685
| 1:17 | 3.1425 | 0.066854
| 1:17 | 3.1428 | 0.066859
| 1:17 | 3.1431 | 0.066865
| 1:17 | 3.1433 | 0.066871
| 1:17 | 3.1436 | 0.066877
| 1:17 | 3.1439 | 0.066883
| 1:17 | 3.1442 | 0.066888
| 1:17 | 3.1444 | 0.066894
| 1:17 | 3.1447 | 0.066899
| 1:18 | 3.145 | 0.066905
| 1:18 | 3.1453 | 0.06691
| 1:18 | 3.1456 | 0.066915
| 1:18 | 3.1458 | 0.06692
| 1:18 | 3.1461 | 0.066925
| 1:18 | 3.1464 | 0.06693
| 1:18 | 3.1467 | 0.066935
| 1:18 | 3.1469 | 0.06694
| 1:18 | 3.1472 | 0.066944
| 1:18 | 3.1475 | 0.066949
| 1:18 | 3.1478 | 0.066953
| 1:18 | 3.1481 | 0.066957
| 1:18 | 3.1483 | 0.066962
| 1:18 | 3.1486 | 0.066966
| 1:18 | 3.1489 | 0.06697
| 1:18 | 3.1492 | 0.066974
| 1:18 | 3.1494 | 0.066978
| 1:18 | 3.1497 | 0.066981
| 1:18 | 3.15 | 0.066985
| 1:18 | 3.1503 | 0.066989
| 1:18 | 3.1506 | 0.066992
| 1:18 | 3.1508 | 0.066995
| 1:18 | 3.1511 | 0.066999
| 1:18 | 3.1514 | 0.067002
| 1:18 | 3.1517 | 0.067004
| 1:18 | 3.1519 | 0.067006
| 1:18 | 3.1522 | 0.067007
| 1:18 | 3.1525 | 0.067007
| 1:18 | 3.1528 | 0.067007
| 1:18 | 3.1531 | 0.067007
| 1:18 | 3.1533 | 0.067006
| 1:18 | 3.1536 | 0.067004
| 1:18 | 3.1539 | 0.067002
| 1:18 | 3.1542 | 0.066999
| 1:18 | 3.1544 | 0.066996
| 1:18 | 3.1547 | 0.066992
| 1:18 | 3.155 | 0.066987
| 1:18 | 3.1553 | 0.066982
| 1:18 | 3.1556 | 0.066976
| 1:18 | 3.1558 | 0.06697
| 1:18 | 3.1561 | 0.066963
| 1:18 | 3.1564 | 0.066956
| 1:18 | 3.1567 | 0.066948
| 1:18 | 3.1569 | 0.066939
| 1:18 | 3.1572 | 0.066931
| 1:18 | 3.1575 | 0.066923
| 1:18 | 3.1578 | 0.066916
| 1:18 | 3.1581 | 0.066909
| 1:18 | 3.1583 | 0.066903
| 1:18 | 3.1586 | 0.066897
| 1:18 | 3.1589 | 0.066892
| 1:18 | 3.1592 | 0.066887
| 1:18 | 3.1594 | 0.066883
| 1:18 | 3.1597 | 0.06688
| 1:18 | 3.16 | 0.066877
| 1:18 | 3.1603 | 0.066875
| 1:18 | 3.1606 | 0.066873
| 1:18 | 3.1608 | 0.066872
| 1:18 | 3.1611 | 0.066871
| 1:18 | 3.1614 | 0.066871
| 1:18 | 3.1617 | 0.066872
| 1:19 | 3.1619 | 0.066873
| 1:19 | 3.1622 | 0.066874
| 1:19 | 3.1625 | 0.066876
| 1:19 | 3.1628 | 0.066879
| 1:19 | 3.1631 | 0.066883
| 1:19 | 3.1633 | 0.066886
| 1:19 | 3.1636 | 0.066891
| 1:19 | 3.1639 | 0.066896
| 1:19 | 3.1642 | 0.066901
| 1:19 | 3.1644 | 0.066907
| 1:19 | 3.1647 | 0.066914
| 1:19 | 3.165 | 0.066921
| 1:19 | 3.1653 | 0.066929
| 1:19 | 3.1656 | 0.066938
| 1:19 | 3.1658 | 0.066947
| 1:19 | 3.1661 | 0.066956
| 1:19 | 3.1664 | 0.066966
| 1:19 | 3.1667 | 0.066977
| 1:19 | 3.1669 | 0.066988
| 1:19 | 3.1672 | 0.067
| 1:19 | 3.1675 | 0.067012
| 1:19 | 3.1678 | 0.067025
| 1:19 | 3.1681 | 0.067038
| 1:19 | 3.1683 | 0.067052
| 1:19 | 3.1686 | 0.067065
| 1:19 | 3.1689 | 0.067078
| 1:19 | 3.1692 | 0.067091
| 1:19 | 3.1694 | 0.067104
| 1:19 | 3.1697 | 0.067118
| 1:19 | 3.17 | 0.067133
| 1:19 | 3.1703 | 0.06715
| 1:19 | 3.1706 | 0.067169
| 1:19 | 3.1708 | 0.067189
| 1:19 | 3.1711 | 0.06721
| 1:19 | 3.1714 | 0.067233
| 1:19 | 3.1717 | 0.067258
| 1:19 | 3.1719 | 0.067285
| 1:19 | 3.1722 | 0.067312
| 1:19 | 3.1725 | 0.067342
| 1:19 | 3.1728 | 0.067373
| 1:19 | 3.1731 | 0.067405
| 1:19 | 3.1733 | 0.067439
| 1:19 | 3.1736 | 0.067475
| 1:19 | 3.1739 | 0.067512
| 1:19 | 3.1742 | 0.067551
| 1:19 | 3.1744 | 0.067591
| 1:19 | 3.1747 | 0.067633
| 1:19 | 3.175 | 0.067678
| 1:19 | 3.1753 | 0.067727
| 1:19 | 3.1756 | 0.067779
| 1:19 | 3.1758 | 0.067835
| 1:19 | 3.1761 | 0.067892
| 1:19 | 3.1764 | 0.06795
| 1:19 | 3.1767 | 0.068007
| 1:19 | 3.1769 | 0.068063
| 1:19 | 3.1772 | 0.068119
| 1:19 | 3.1775 | 0.068175
| 1:19 | 3.1778 | 0.06823
| 1:19 | 3.1781 | 0.068285
| 1:20 | 3.1783 | 0.068339
| 1:20 | 3.1786 | 0.068393
| 1:20 | 3.1789 | 0.068447
| 1:20 | 3.1792 | 0.068499
| 1:20 | 3.1794 | 0.068546
| 1:20 | 3.1797 | 0.068588
| 1:20 | 3.18 | 0.068626
| 1:20 | 3.1803 | 0.068659
| 1:20 | 3.1806 | 0.068688
| 1:20 | 3.1808 | 0.068712
| 1:20 | 3.1811 | 0.068731
| 1:20 | 3.1814 | 0.068746
| 1:20 | 3.1817 | 0.068761
| 1:20 | 3.1819 | 0.068775
| 1:20 | 3.1822 | 0.068791
| 1:20 | 3.1825 | 0.068807
| 1:20 | 3.1828 | 0.068823
| 1:20 | 3.1831 | 0.068839
| 1:20 | 3.1833 | 0.068856
| 1:20 | 3.1836 | 0.068874
| 1:20 | 3.1839 | 0.068892
| 1:20 | 3.1842 | 0.06891
| 1:20 | 3.1844 | 0.068929
| 1:20 | 3.1847 | 0.068948
| 1:20 | 3.185 | 0.068968
| 1:20 | 3.1853 | 0.068988
| 1:20 | 3.1856 | 0.069009
| 1:20 | 3.1858 | 0.06903
| 1:20 | 3.1861 | 0.069051
| 1:20 | 3.1864 | 0.069073
| 1:20 | 3.1867 | 0.069095
| 1:20 | 3.1869 | 0.069118
| 1:20 | 3.1872 | 0.069141
| 1:20 | 3.1875 | 0.069164
| 1:20 | 3.1878 | 0.069189
| 1:20 | 3.1881 | 0.069213
| 1:20 | 3.1883 | 0.069238
| 1:20 | 3.1886 | 0.069263
| 1:20 | 3.1889 | 0.069289
| 1:20 | 3.1892 | 0.069315
| 1:20 | 3.1894 | 0.069342
| 1:20 | 3.1897 | 0.069369
| 1:20 | 3.19 | 0.069396
| 1:20 | 3.1903 | 0.069424
| 1:20 | 3.1906 | 0.069453
| 1:20 | 3.1908 | 0.069482
| 1:20 | 3.1911 | 0.069514
| 1:20 | 3.1914 | 0.069547
| 1:20 | 3.1917 | 0.069583
| 1:20 | 3.1919 | 0.069621
| 1:20 | 3.1922 | 0.069661
| 1:20 | 3.1925 | 0.069703
| 1:20 | 3.1928 | 0.069748
| 1:20 | 3.1931 | 0.069797
| 1:20 | 3.1933 | 0.069852
| 1:20 | 3.1936 | 0.069909
| 1:20 | 3.1939 | 0.069965
| 1:20 | 3.1942 | 0.07002
| 1:20 | 3.1944 | 0.070073
| 1:20 | 3.1947 | 0.070126
| 1:20 | 3.195 | 0.070177
| 1:21 | 3.1953 | 0.070226
| 1:21 | 3.1956 | 0.070275
| 1:21 | 3.1958 | 0.070323
| 1:21 | 3.1961 | 0.070375
| 1:21 | 3.1964 | 0.07043
| 1:21 | 3.1967 | 0.070488
| 1:21 | 3.1969 | 0.07055
| 1:21 | 3.1972 | 0.070615
| 1:21 | 3.1975 | 0.070682
| 1:21 | 3.1978 | 0.070753
| 1:21 | 3.1981 | 0.070828
| 1:21 | 3.1983 | 0.070898
| 1:21 | 3.1986 | 0.070963
| 1:21 | 3.1989 | 0.071022
| 1:21 | 3.1992 | 0.071079
| 1:21 | 3.1994 | 0.071134
| 1:21 | 3.1997 | 0.071187
| 1:21 | 3.2 | 0.071238
| 1:21 | 3.2003 | 0.071288
| 1:21 | 3.2006 | 0.071336
| 1:21 | 3.2008 | 0.071382
| 1:21 | 3.2011 | 0.071426
| 1:21 | 3.2014 | 0.071469
| 1:21 | 3.2017 | 0.07151
| 1:21 | 3.2019 | 0.071549
| 1:21 | 3.2022 | 0.071586
| 1:21 | 3.2025 | 0.071622
| 1:21 | 3.2028 | 0.071656
| 1:21 | 3.2031 | 0.071688
| 1:21 | 3.2033 | 0.071718
| 1:21 | 3.2036 | 0.071747
| 1:21 | 3.2039 | 0.071774
| 1:21 | 3.2042 | 0.071799
| 1:21 | 3.2044 | 0.071822
| 1:21 | 3.2047 | 0.071844
| 1:21 | 3.205 | 0.071864
| 1:21 | 3.2053 | 0.071882
| 1:21 | 3.2056 | 0.071898
| 1:21 | 3.2058 | 0.071913
| 1:21 | 3.2061 | 0.071926
| 1:21 | 3.2064 | 0.071938
| 1:21 | 3.2067 | 0.071949
| 1:21 | 3.2069 | 0.07196
| 1:21 | 3.2072 | 0.07197
| 1:21 | 3.2075 | 0.071979
| 1:21 | 3.2078 | 0.071988
| 1:21 | 3.2081 | 0.071995
| 1:21 | 3.2083 | 0.072002
| 1:21 | 3.2086 | 0.072009
| 1:21 | 3.2089 | 0.072014
| 1:21 | 3.2092 | 0.072019
| 1:21 | 3.2094 | 0.072023
| 1:21 | 3.2097 | 0.072027
| 1:21 | 3.21 | 0.072029
| 1:21 | 3.2103 | 0.072032
| 1:21 | 3.2106 | 0.072035
| 1:21 | 3.2108 | 0.072039
| 1:21 | 3.2111 | 0.072044
| 1:21 | 3.2114 | 0.07205
| 1:22 | 3.2117 | 0.072056
| 1:22 | 3.2119 | 0.072063
| 1:22 | 3.2122 | 0.072071
| 1:22 | 3.2125 | 0.072078
| 1:22 | 3.2128 | 0.072081
| 1:22 | 3.2131 | 0.07208
| 1:22 | 3.2133 | 0.072076
| 1:22 | 3.2136 | 0.072067
| 1:22 | 3.2139 | 0.072054
| 1:22 | 3.2142 | 0.072038
| 1:22 | 3.2144 | 0.072017
| 1:22 | 3.2147 | 0.071993
| 1:22 | 3.215 | 0.071965
| 1:22 | 3.2153 | 0.071933
| 1:22 | 3.2156 | 0.071889
| 1:22 | 3.2158 | 0.07184
| 1:22 | 3.2161 | 0.071785
| 1:22 | 3.2164 | 0.071724
| 1:22 | 3.2167 | 0.071657
| 1:22 | 3.2169 | 0.071576
| 1:22 | 3.2172 | 0.07149
| 1:22 | 3.2175 | 0.071398
| 1:22 | 3.2178 | 0.071303
| 1:22 | 3.2181 | 0.071212
| 1:22 | 3.2183 | 0.071125
| 1:22 | 3.2186 | 0.071044
| 1:22 | 3.2189 | 0.070976
| 1:22 | 3.2192 | 0.070921
| 1:22 | 3.2194 | 0.070875
| 1:22 | 3.2197 | 0.070829
| 1:22 | 3.22 | 0.070784
| 1:22 | 3.2203 | 0.07074
| 1:22 | 3.2206 | 0.070696
| 1:22 | 3.2208 | 0.070655
| 1:22 | 3.2211 | 0.070616
| 1:22 | 3.2214 | 0.07058
| 1:22 | 3.2217 | 0.070546
| 1:22 | 3.2219 | 0.070514
| 1:22 | 3.2222 | 0.070485
| 1:22 | 3.2225 | 0.070458
| 1:22 | 3.2228 | 0.070432
| 1:22 | 3.2231 | 0.070406
| 1:22 | 3.2233 | 0.070378
| 1:22 | 3.2236 | 0.070349
| 1:22 | 3.2239 | 0.07032
| 1:22 | 3.2242 | 0.07029
| 1:22 | 3.2244 | 0.070258
| 1:22 | 3.2247 | 0.070226
| 1:22 | 3.225 | 0.070193
| 1:22 | 3.2253 | 0.070159
| 1:22 | 3.2256 | 0.070123
| 1:22 | 3.2258 | 0.070084
| 1:22 | 3.2261 | 0.070032
| 1:22 | 3.2264 | 0.069969
| 1:22 | 3.2267 | 0.069905
| 1:22 | 3.2269 | 0.069843
| 1:22 | 3.2272 | 0.069781
| 1:22 | 3.2275 | 0.069721
| 1:22 | 3.2278 | 0.069661
| 1:22 | 3.2281 | 0.069603
| 1:22 | 3.2283 | 0.069546
| 1:23 | 3.2286 | 0.069491
| 1:23 | 3.2289 | 0.069438
| 1:23 | 3.2292 | 0.06939
| 1:23 | 3.2294 | 0.069348
| 1:23 | 3.2297 | 0.069311
| 1:23 | 3.23 | 0.069279
| 1:23 | 3.2303 | 0.069254
| 1:23 | 3.2306 | 0.069233
| 1:23 | 3.2308 | 0.069218
| 1:23 | 3.2311 | 0.069208
| 1:23 | 3.2314 | 0.069204
| 1:23 | 3.2317 | 0.069205
| 1:23 | 3.2319 | 0.069212
| 1:23 | 3.2322 | 0.069223
| 1:23 | 3.2325 | 0.069236
| 1:23 | 3.2328 | 0.069252
| 1:23 | 3.2331 | 0.069271
| 1:23 | 3.2333 | 0.069296
| 1:23 | 3.2336 | 0.06933
| 1:23 | 3.2339 | 0.069372
| 1:23 | 3.2342 | 0.06942
| 1:23 | 3.2344 | 0.069464
| 1:23 | 3.2347 | 0.069491
| 1:23 | 3.235 | 0.069505
| 1:23 | 3.2353 | 0.069517
| 1:23 | 3.2356 | 0.069532
| 1:23 | 3.2358 | 0.06955
| 1:23 | 3.2361 | 0.069571
| 1:23 | 3.2364 | 0.069595
| 1:23 | 3.2367 | 0.069621
| 1:23 | 3.2369 | 0.069653
| 1:23 | 3.2372 | 0.069692
| 1:23 | 3.2375 | 0.069733
| 1:23 | 3.2378 | 0.069774
| 1:23 | 3.2381 | 0.069815
| 1:23 | 3.2383 | 0.069858
| 1:23 | 3.2386 | 0.069901
| 1:23 | 3.2389 | 0.069944
| 1:23 | 3.2392 | 0.069989
| 1:23 | 3.2394 | 0.070033
| 1:23 | 3.2397 | 0.070076
| 1:23 | 3.24 | 0.070117
| 1:23 | 3.2403 | 0.070157
| 1:23 | 3.2406 | 0.070195
| 1:23 | 3.2408 | 0.070232
| 1:23 | 3.2411 | 0.070255
| 1:23 | 3.2414 | 0.070263
| 1:23 | 3.2417 | 0.07026
| 1:23 | 3.2419 | 0.070258
| 1:23 | 3.2422 | 0.070259
| 1:23 | 3.2425 | 0.070263
| 1:23 | 3.2428 | 0.070271
| 1:23 | 3.2431 | 0.070286
| 1:23 | 3.2433 | 0.070314
| 1:23 | 3.2436 | 0.070356
| 1:23 | 3.2439 | 0.070412
| 1:23 | 3.2442 | 0.07048
| 1:23 | 3.2444 | 0.07056
| 1:23 | 3.2447 | 0.070651
| 1:24 | 3.245 | 0.070754
| 1:24 | 3.2453 | 0.070876
| 1:24 | 3.2456 | 0.071004
| 1:24 | 3.2458 | 0.071135
| 1:24 | 3.2461 | 0.071265
| 1:24 | 3.2464 | 0.071393
| 1:24 | 3.2467 | 0.071521
| 1:24 | 3.2469 | 0.071648
| 1:24 | 3.2472 | 0.071774
| 1:24 | 3.2475 | 0.071899
| 1:24 | 3.2478 | 0.072023
| 1:24 | 3.2481 | 0.072146
| 1:24 | 3.2483 | 0.072268
| 1:24 | 3.2486 | 0.072389
| 1:24 | 3.2489 | 0.072509
| 1:24 | 3.2492 | 0.072628
| 1:24 | 3.2494 | 0.072747
| 1:24 | 3.2497 | 0.072864
| 1:24 | 3.25 | 0.07298
| 1:24 | 3.2503 | 0.073096
| 1:24 | 3.2506 | 0.07321
| 1:24 | 3.2508 | 0.073323
| 1:24 | 3.2511 | 0.073436
| 1:24 | 3.2514 | 0.073547
| 1:24 | 3.2517 | 0.073657
| 1:24 | 3.2519 | 0.073762
| 1:24 | 3.2522 | 0.073863
| 1:24 | 3.2525 | 0.07396
| 1:24 | 3.2528 | 0.074052
| 1:24 | 3.2531 | 0.07414
| 1:24 | 3.2533 | 0.074224
| 1:24 | 3.2536 | 0.074303
| 1:24 | 3.2539 | 0.07438
| 1:24 | 3.2542 | 0.074455
| 1:24 | 3.2544 | 0.074529
| 1:24 | 3.2547 | 0.074601
| 1:24 | 3.255 | 0.074673
| 1:24 | 3.2553 | 0.074743
| 1:24 | 3.2556 | 0.074812
| 1:24 | 3.2558 | 0.074879
| 1:24 | 3.2561 | 0.074946
| 1:24 | 3.2564 | 0.075011
| 1:24 | 3.2567 | 0.075075
| 1:24 | 3.2569 | 0.075138
| 1:24 | 3.2572 | 0.075193
| 1:24 | 3.2575 | 0.075239
| 1:24 | 3.2578 | 0.075279
| 1:24 | 3.2581 | 0.075313
| 1:24 | 3.2583 | 0.075346
| 1:24 | 3.2586 | 0.075378
| 1:24 | 3.2589 | 0.075409
| 1:24 | 3.2592 | 0.075438
| 1:24 | 3.2594 | 0.075465
| 1:24 | 3.2597 | 0.075491
| 1:24 | 3.26 | 0.075516
| 1:24 | 3.2603 | 0.07554
| 1:24 | 3.2606 | 0.075562
| 1:24 | 3.2608 | 0.075583
| 1:24 | 3.2611 | 0.075591
| 1:24 | 3.2614 | 0.075583
| 1:24 | 3.2617 | 0.075552
| 1:25 | 3.2619 | 0.075511
| 1:25 | 3.2622 | 0.075467
| 1:25 | 3.2625 | 0.075431
| 1:25 | 3.2628 | 0.075405
| 1:25 | 3.2631 | 0.07539
| 1:25 | 3.2633 | 0.075386
| 1:25 | 3.2636 | 0.075392
| 1:25 | 3.2639 | 0.075408
| 1:25 | 3.2642 | 0.075436
| 1:25 | 3.2644 | 0.075474
| 1:25 | 3.2647 | 0.075518
| 1:25 | 3.265 | 0.075559
| 1:25 | 3.2653 | 0.075596
| 1:25 | 3.2656 | 0.075624
| 1:25 | 3.2658 | 0.07564
| 1:25 | 3.2661 | 0.075636
| 1:25 | 3.2664 | 0.075621
| 1:25 | 3.2667 | 0.075601
| 1:25 | 3.2669 | 0.075586
| 1:25 | 3.2672 | 0.075577
| 1:25 | 3.2675 | 0.075573
| 1:25 | 3.2678 | 0.075572
| 1:25 | 3.2681 | 0.075572
| 1:25 | 3.2683 | 0.075573
| 1:25 | 3.2686 | 0.075575
| 1:25 | 3.2689 | 0.075579
| 1:25 | 3.2692 | 0.075584
| 1:25 | 3.2694 | 0.07559
| 1:25 | 3.2697 | 0.075598
| 1:25 | 3.27 | 0.075607
| 1:25 | 3.2703 | 0.075617
| 1:25 | 3.2706 | 0.075628
| 1:25 | 3.2708 | 0.07564
| 1:25 | 3.2711 | 0.075654
| 1:25 | 3.2714 | 0.075669
| 1:25 | 3.2717 | 0.075685
| 1:25 | 3.2719 | 0.075703
| 1:25 | 3.2722 | 0.075722
| 1:25 | 3.2725 | 0.075742
| 1:25 | 3.2728 | 0.075763
| 1:25 | 3.2731 | 0.075786
| 1:25 | 3.2733 | 0.075809
| 1:25 | 3.2736 | 0.075843
| 1:25 | 3.2739 | 0.075877
| 1:25 | 3.2742 | 0.075913
| 1:25 | 3.2744 | 0.07595
| 1:25 | 3.2747 | 0.075989
| 1:25 | 3.275 | 0.076028
| 1:25 | 3.2753 | 0.076069
| 1:25 | 3.2756 | 0.076112
| 1:25 | 3.2758 | 0.076155
| 1:25 | 3.2761 | 0.0762
| 1:25 | 3.2764 | 0.076246
| 1:25 | 3.2767 | 0.076294
| 1:25 | 3.2769 | 0.076343
| 1:25 | 3.2772 | 0.076394
| 1:25 | 3.2775 | 0.076448
| 1:25 | 3.2778 | 0.076505
| 1:25 | 3.2781 | 0.076574
| 1:26 | 3.2783 | 0.076659
| 1:26 | 3.2786 | 0.076759
| 1:26 | 3.2789 | 0.076872
| 1:26 | 3.2792 | 0.076992
| 1:26 | 3.2794 | 0.077115
| 1:26 | 3.2797 | 0.077242
| 1:26 | 3.28 | 0.077373
| 1:26 | 3.2803 | 0.077508
| 1:26 | 3.2806 | 0.077647
| 1:26 | 3.2808 | 0.07779
| 1:26 | 3.2811 | 0.077937
| 1:26 | 3.2814 | 0.078088
| 1:26 | 3.2817 | 0.078242
| 1:26 | 3.2819 | 0.078399
| 1:26 | 3.2822 | 0.078559
| 1:26 | 3.2825 | 0.078722
| 1:26 | 3.2828 | 0.078888
| 1:26 | 3.2831 | 0.079058
| 1:26 | 3.2833 | 0.079231
| 1:26 | 3.2836 | 0.079406
| 1:26 | 3.2839 | 0.079584
| 1:26 | 3.2842 | 0.079762
| 1:26 | 3.2844 | 0.079941
| 1:26 | 3.2847 | 0.080121
| 1:26 | 3.285 | 0.080302
| 1:26 | 3.2853 | 0.080483
| 1:26 | 3.2856 | 0.080665
| 1:26 | 3.2858 | 0.080848
| 1:26 | 3.2861 | 0.081031
| 1:26 | 3.2864 | 0.081214
| 1:26 | 3.2867 | 0.081398
| 1:26 | 3.2869 | 0.081583
| 1:26 | 3.2872 | 0.081768
| 1:26 | 3.2875 | 0.081954
| 1:26 | 3.2878 | 0.08214
| 1:26 | 3.2881 | 0.082327
| 1:26 | 3.2883 | 0.082515
| 1:26 | 3.2886 | 0.082703
| 1:26 | 3.2889 | 0.082891
| 1:26 | 3.2892 | 0.083081
| 1:26 | 3.2894 | 0.08327
| 1:26 | 3.2897 | 0.083461
| 1:26 | 3.29 | 0.083652
| 1:26 | 3.2903 | 0.083843
| 1:26 | 3.2906 | 0.084035
| 1:26 | 3.2908 | 0.084228
| 1:26 | 3.2911 | 0.084421
| 1:26 | 3.2914 | 0.084615
| 1:26 | 3.2917 | 0.084809
| 1:26 | 3.2919 | 0.085004
| 1:26 | 3.2922 | 0.085199
| 1:26 | 3.2925 | 0.085395
| 1:26 | 3.2928 | 0.085592
| 1:26 | 3.2931 | 0.085789
| 1:26 | 3.2933 | 0.085987
| 1:26 | 3.2936 | 0.086185
| 1:26 | 3.2939 | 0.086382
| 1:26 | 3.2942 | 0.086578
| 1:26 | 3.2944 | 0.086774
| 1:26 | 3.2947 | 0.086969
| 1:26 | 3.295 | 0.087163
| 1:27 | 3.2953 | 0.087357
| 1:27 | 3.2956 | 0.08755
| 1:27 | 3.2958 | 0.087743
| 1:27 | 3.2961 | 0.087934
| 1:27 | 3.2964 | 0.088125
| 1:27 | 3.2967 | 0.088316
| 1:27 | 3.2969 | 0.088505
| 1:27 | 3.2972 | 0.088694
| 1:27 | 3.2975 | 0.088883
| 1:27 | 3.2978 | 0.089071
| 1:27 | 3.2981 | 0.089258
| 1:27 | 3.2983 | 0.089444
| 1:27 | 3.2986 | 0.08963
| 1:27 | 3.2989 | 0.089815
| 1:27 | 3.2992 | 0.089999
| 1:27 | 3.2994 | 0.090183
| 1:27 | 3.2997 | 0.090365
| 1:27 | 3.3 | 0.090546
| 1:27 | 3.3003 | 0.090727
| 1:27 | 3.3006 | 0.090906
| 1:27 | 3.3008 | 0.091084
| 1:27 | 3.3011 | 0.091261
| 1:27 | 3.3014 | 0.091437
| 1:27 | 3.3017 | 0.091611
| 1:27 | 3.3019 | 0.091785
| 1:27 | 3.3022 | 0.091957
| 1:27 | 3.3025 | 0.092128
| 1:27 | 3.3028 | 0.092299
| 1:27 | 3.3031 | 0.092468
| 1:27 | 3.3033 | 0.092636
| 1:27 | 3.3036 | 0.092802
| 1:27 | 3.3039 | 0.092968
| 1:27 | 3.3042 | 0.093133
| 1:27 | 3.3044 | 0.093296
| 1:27 | 3.3047 | 0.093459
| 1:27 | 3.305 | 0.09362
| 1:27 | 3.3053 | 0.09378
| 1:27 | 3.3056 | 0.093939
| 1:27 | 3.3058 | 0.094097
| 1:27 | 3.3061 | 0.094254
| 1:27 | 3.3064 | 0.0944
| 1:27 | 3.3067 | 0.094548
| 1:27 | 3.3069 | 0.094699
| 1:27 | 3.3072 | 0.094866
| 1:27 | 3.3075 | 0.095048
| 1:27 | 3.3078 | 0.095226
| 1:27 | 3.3081 | 0.0954
| 1:27 | 3.3083 | 0.09557
| 1:27 | 3.3086 | 0.095725
| 1:27 | 3.3089 | 0.095859
| 1:27 | 3.3092 | 0.095978
| 1:27 | 3.3094 | 0.096084
| 1:27 | 3.3097 | 0.096186
| 1:27 | 3.31 | 0.096288
| 1:27 | 3.3103 | 0.096391
| 1:27 | 3.3106 | 0.096494
| 1:27 | 3.3108 | 0.096597
| 1:27 | 3.3111 | 0.096701
| 1:27 | 3.3114 | 0.096805
| 1:28 | 3.3117 | 0.096909
| 1:28 | 3.3119 | 0.097014
| 1:28 | 3.3122 | 0.097119
| 1:28 | 3.3125 | 0.09722
| 1:28 | 3.3128 | 0.097314
| 1:28 | 3.3131 | 0.097399
| 1:28 | 3.3133 | 0.097477
| 1:28 | 3.3136 | 0.097548
| 1:28 | 3.3139 | 0.09761
| 1:28 | 3.3142 | 0.097665
| 1:28 | 3.3144 | 0.097712
| 1:28 | 3.3147 | 0.097752
| 1:28 | 3.315 | 0.097788
| 1:28 | 3.3153 | 0.097821
| 1:28 | 3.3156 | 0.097852
| 1:28 | 3.3158 | 0.097879
| 1:28 | 3.3161 | 0.097905
| 1:28 | 3.3164 | 0.097927
| 1:28 | 3.3167 | 0.097947
| 1:28 | 3.3169 | 0.097963
| 1:28 | 3.3172 | 0.097978
| 1:28 | 3.3175 | 0.097989
| 1:28 | 3.3178 | 0.097997
| 1:28 | 3.3181 | 0.098005
| 1:28 | 3.3183 | 0.098016
| 1:28 | 3.3186 | 0.098029
| 1:28 | 3.3189 | 0.098045
| 1:28 | 3.3192 | 0.098063
| 1:28 | 3.3194 | 0.098089
| 1:28 | 3.3197 | 0.098118
| 1:28 | 3.32 | 0.098149
| 1:28 | 3.3203 | 0.098181
| 1:28 | 3.3206 | 0.098214
| 1:28 | 3.3208 | 0.098249
| 1:28 | 3.3211 | 0.098285
| 1:28 | 3.3214 | 0.098323
| 1:28 | 3.3217 | 0.098362
| 1:28 | 3.3219 | 0.098403
| 1:28 | 3.3222 | 0.098445
| 1:28 | 3.3225 | 0.098488
| 1:28 | 3.3228 | 0.098533
| 1:28 | 3.3231 | 0.098579
| 1:28 | 3.3233 | 0.098626
| 1:28 | 3.3236 | 0.098675
| 1:28 | 3.3239 | 0.098725
| 1:28 | 3.3242 | 0.098776
| 1:28 | 3.3244 | 0.098825
| 1:28 | 3.3247 | 0.09887
| 1:28 | 3.325 | 0.098899
| 1:28 | 3.3253 | 0.098912
| 1:28 | 3.3256 | 0.098917
| 1:28 | 3.3258 | 0.098918
| 1:28 | 3.3261 | 0.098919
| 1:28 | 3.3264 | 0.09892
| 1:28 | 3.3267 | 0.098919
| 1:28 | 3.3269 | 0.098919
| 1:28 | 3.3272 | 0.098917
| 1:28 | 3.3275 | 0.098915
| 1:28 | 3.3278 | 0.098913
| 1:28 | 3.3281 | 0.09891
| 1:28 | 3.3283 | 0.098906
| 1:29 | 3.3286 | 0.098901
| 1:29 | 3.3289 | 0.098896
| 1:29 | 3.3292 | 0.098891
| 1:29 | 3.3294 | 0.098887
| 1:29 | 3.3297 | 0.098883
| 1:29 | 3.33 | 0.09888
| 1:29 | 3.3303 | 0.098878
| 1:29 | 3.3306 | 0.098877
| 1:29 | 3.3308 | 0.098876
| 1:29 | 3.3311 | 0.098876
| 1:29 | 3.3314 | 0.098877
| 1:29 | 3.3317 | 0.098879
| 1:29 | 3.3319 | 0.098882
| 1:29 | 3.3322 | 0.098885
| 1:29 | 3.3325 | 0.098878
| 1:29 | 3.3328 | 0.098857
| 1:29 | 3.3331 | 0.098832
| 1:29 | 3.3333 | 0.098803
| 1:29 | 3.3336 | 0.09877
| 1:29 | 3.3339 | 0.098734
| 1:29 | 3.3342 | 0.098694
| 1:29 | 3.3344 | 0.09865
| 1:29 | 3.3347 | 0.098603
| 1:29 | 3.335 | 0.098554
| 1:29 | 3.3353 | 0.098502
| 1:29 | 3.3356 | 0.098447
| 1:29 | 3.3358 | 0.09839
| 1:29 | 3.3361 | 0.09833
| 1:29 | 3.3364 | 0.098269
| 1:29 | 3.3367 | 0.098208
| 1:29 | 3.3369 | 0.098148
| 1:29 | 3.3372 | 0.098087
| 1:29 | 3.3375 | 0.098026
| 1:29 | 3.3378 | 0.097966
| 1:29 | 3.3381 | 0.097906
| 1:29 | 3.3383 | 0.097846
| 1:29 | 3.3386 | 0.097786
| 1:29 | 3.3389 | 0.097726
| 1:29 | 3.3392 | 0.097666
| 1:29 | 3.3394 | 0.097606
| 1:29 | 3.3397 | 0.097546
| 1:29 | 3.34 | 0.097486
| 1:29 | 3.3403 | 0.097427
| 1:29 | 3.3406 | 0.097367
| 1:29 | 3.3408 | 0.097308
| 1:29 | 3.3411 | 0.097249
| 1:29 | 3.3414 | 0.09719
| 1:29 | 3.3417 | 0.097131
| 1:29 | 3.3419 | 0.097072
| 1:29 | 3.3422 | 0.097013
| 1:29 | 3.3425 | 0.096954
| 1:29 | 3.3428 | 0.096895
| 1:29 | 3.3431 | 0.096836
| 1:29 | 3.3433 | 0.096778
| 1:29 | 3.3436 | 0.096719
| 1:29 | 3.3439 | 0.096662
| 1:29 | 3.3442 | 0.096605
| 1:29 | 3.3444 | 0.096549
| 1:29 | 3.3447 | 0.096494
| 1:30 | 3.345 | 0.09644
| 1:30 | 3.3453 | 0.096387
| 1:30 | 3.3456 | 0.096335
| 1:30 | 3.3458 | 0.096285
| 1:30 | 3.3461 | 0.096237
| 1:30 | 3.3464 | 0.096192
| 1:30 | 3.3467 | 0.096148
| 1:30 | 3.3469 | 0.096107
| 1:30 | 3.3472 | 0.096068
| 1:30 | 3.3475 | 0.096032
| 1:30 | 3.3478 | 0.095997
| 1:30 | 3.3481 | 0.095966
| 1:30 | 3.3483 | 0.095941
| 1:30 | 3.3486 | 0.095924
| 1:30 | 3.3489 | 0.095909
| 1:30 | 3.3492 | 0.095899
| 1:30 | 3.3494 | 0.095891
| 1:30 | 3.3497 | 0.095888
| 1:30 | 3.35 | 0.095888
| 1:30 | 3.3503 | 0.095895
| 1:30 | 3.3506 | 0.095912
| 1:30 | 3.3508 | 0.095932
| 1:30 | 3.3511 | 0.095953
| 1:30 | 3.3514 | 0.095976
| 1:30 | 3.3517 | 0.096013
| 1:30 | 3.3519 | 0.096071
| 1:30 | 3.3522 | 0.096152
| 1:30 | 3.3525 | 0.09624
| 1:30 | 3.3528 | 0.09633
| 1:30 | 3.3531 | 0.09642
| 1:30 | 3.3533 | 0.096499
| 1:30 | 3.3536 | 0.096561
| 1:30 | 3.3539 | 0.096611
| 1:30 | 3.3542 | 0.096658
| 1:30 | 3.3544 | 0.096703
| 1:30 | 3.3547 | 0.096746
| 1:30 | 3.355 | 0.096787
| 1:30 | 3.3553 | 0.096826
| 1:30 | 3.3556 | 0.096864
| 1:30 | 3.3558 | 0.096899
| 1:30 | 3.3561 | 0.096933
| 1:30 | 3.3564 | 0.096968
| 1:30 | 3.3567 | 0.097004
| 1:30 | 3.3569 | 0.097041
| 1:30 | 3.3572 | 0.09708
| 1:30 | 3.3575 | 0.097118
| 1:30 | 3.3578 | 0.097156
| 1:30 | 3.3581 | 0.097194
| 1:30 | 3.3583 | 0.097231
| 1:30 | 3.3586 | 0.097268
| 1:30 | 3.3589 | 0.097305
| 1:30 | 3.3592 | 0.097341
| 1:30 | 3.3594 | 0.097377
| 1:30 | 3.3597 | 0.097413
| 1:30 | 3.36 | 0.097448
| 1:30 | 3.3603 | 0.097483
| 1:30 | 3.3606 | 0.097518
| 1:30 | 3.3608 | 0.097553
| 1:30 | 3.3611 | 0.097587
| 1:30 | 3.3614 | 0.097621
| 1:30 | 3.3617 | 0.097654
| 1:31 | 3.3619 | 0.097687
| 1:31 | 3.3622 | 0.09772
| 1:31 | 3.3625 | 0.097754
| 1:31 | 3.3628 | 0.097791
| 1:31 | 3.3631 | 0.097831
| 1:31 | 3.3633 | 0.097874
| 1:31 | 3.3636 | 0.097919
| 1:31 | 3.3639 | 0.097968
| 1:31 | 3.3642 | 0.098019
| 1:31 | 3.3644 | 0.098074
| 1:31 | 3.3647 | 0.098131
| 1:31 | 3.365 | 0.09819
| 1:31 | 3.3653 | 0.098255
| 1:31 | 3.3656 | 0.098333
| 1:31 | 3.3658 | 0.09842
| 1:31 | 3.3661 | 0.09852
| 1:31 | 3.3664 | 0.098634
| 1:31 | 3.3667 | 0.098758
| 1:31 | 3.3669 | 0.098891
| 1:31 | 3.3672 | 0.099026
| 1:31 | 3.3675 | 0.099163
| 1:31 | 3.3678 | 0.099308
| 1:31 | 3.3681 | 0.099459
| 1:31 | 3.3683 | 0.099622
| 1:31 | 3.3686 | 0.099798
| 1:31 | 3.3689 | 0.099988
| 1:31 | 3.3692 | 0.10018
| 1:31 | 3.3694 | 0.10038
| 1:31 | 3.3697 | 0.10059
| 1:31 | 3.37 | 0.10079
| 1:31 | 3.3703 | 0.10099
| 1:31 | 3.3706 | 0.10118
| 1:31 | 3.3708 | 0.10138
| 1:31 | 3.3711 | 0.10157
| 1:31 | 3.3714 | 0.10176
| 1:31 | 3.3717 | 0.10195
| 1:31 | 3.3719 | 0.10214
| 1:31 | 3.3722 | 0.10232
| 1:31 | 3.3725 | 0.10251
| 1:31 | 3.3728 | 0.10269
| 1:31 | 3.3731 | 0.10286
| 1:31 | 3.3733 | 0.10303
| 1:31 | 3.3736 | 0.1032
| 1:31 | 3.3739 | 0.10336
| 1:31 | 3.3742 | 0.10351
| 1:31 | 3.3744 | 0.10363
| 1:31 | 3.3747 | 0.10375
| 1:31 | 3.375 | 0.10385
| 1:31 | 3.3753 | 0.10395
| 1:31 | 3.3756 | 0.10403
| 1:31 | 3.3758 | 0.1041
| 1:31 | 3.3761 | 0.10415
| 1:31 | 3.3764 | 0.1042
| 1:31 | 3.3767 | 0.10424
| 1:31 | 3.3769 | 0.10427
| 1:31 | 3.3772 | 0.1043
| 1:31 | 3.3775 | 0.10432
| 1:31 | 3.3778 | 0.10433
| 1:31 | 3.3781 | 0.10434
| 1:32 | 3.3783 | 0.10434
| 1:32 | 3.3786 | 0.10434
| 1:32 | 3.3789 | 0.10433
| 1:32 | 3.3792 | 0.10432
| 1:32 | 3.3794 | 0.10431
| 1:32 | 3.3797 | 0.1043
| 1:32 | 3.38 | 0.10428
| 1:32 | 3.3803 | 0.10427
| 1:32 | 3.3806 | 0.10426
| 1:32 | 3.3808 | 0.10425
| 1:32 | 3.3811 | 0.10423
| 1:32 | 3.3814 | 0.10422
| 1:32 | 3.3817 | 0.1042
| 1:32 | 3.3819 | 0.10417
| 1:32 | 3.3822 | 0.10414
| 1:32 | 3.3825 | 0.1041
| 1:32 | 3.3828 | 0.10405
| 1:32 | 3.3831 | 0.104
| 1:32 | 3.3833 | 0.10394
| 1:32 | 3.3836 | 0.10387
| 1:32 | 3.3839 | 0.1038
| 1:32 | 3.3842 | 0.10373
| 1:32 | 3.3844 | 0.10366
| 1:32 | 3.3847 | 0.10359
| 1:32 | 3.385 | 0.10352
| 1:32 | 3.3853 | 0.10344
| 1:32 | 3.3856 | 0.10336
| 1:32 | 3.3858 | 0.10329
| 1:32 | 3.3861 | 0.10322
| 1:32 | 3.3864 | 0.10314
| 1:32 | 3.3867 | 0.10307
| 1:32 | 3.3869 | 0.10301
| 1:32 | 3.3872 | 0.10294
| 1:32 | 3.3875 | 0.10287
| 1:32 | 3.3878 | 0.10281
| 1:32 | 3.3881 | 0.10275
| 1:32 | 3.3883 | 0.10269
| 1:32 | 3.3886 | 0.10263
| 1:32 | 3.3889 | 0.10258
| 1:32 | 3.3892 | 0.10252
| 1:32 | 3.3894 | 0.10247
| 1:32 | 3.3897 | 0.10242
| 1:32 | 3.39 | 0.10238
| 1:32 | 3.3903 | 0.10234
| 1:32 | 3.3906 | 0.10229
| 1:32 | 3.3908 | 0.10225
| 1:32 | 3.3911 | 0.1022
| 1:32 | 3.3914 | 0.10216
| 1:32 | 3.3917 | 0.10211
| 1:32 | 3.3919 | 0.10206
| 1:32 | 3.3922 | 0.10201
| 1:32 | 3.3925 | 0.10196
| 1:32 | 3.3928 | 0.10191
| 1:32 | 3.3931 | 0.10187
| 1:32 | 3.3933 | 0.10183
| 1:32 | 3.3936 | 0.10179
| 1:32 | 3.3939 | 0.10176
| 1:32 | 3.3942 | 0.10174
| 1:32 | 3.3944 | 0.10171
| 1:32 | 3.3947 | 0.1017
| 1:32 | 3.395 | 0.10168
| 1:33 | 3.3953 | 0.10168
| 1:33 | 3.3956 | 0.10168
| 1:33 | 3.3958 | 0.10168
| 1:33 | 3.3961 | 0.10169
| 1:33 | 3.3964 | 0.10169
| 1:33 | 3.3967 | 0.10169
| 1:33 | 3.3969 | 0.10169
| 1:33 | 3.3972 | 0.10168
| 1:33 | 3.3975 | 0.10168
| 1:33 | 3.3978 | 0.10167
| 1:33 | 3.3981 | 0.10167
| 1:33 | 3.3983 | 0.10166
| 1:33 | 3.3986 | 0.10165
| 1:33 | 3.3989 | 0.10163
| 1:33 | 3.3992 | 0.10162
| 1:33 | 3.3994 | 0.1016
| 1:33 | 3.3997 | 0.10157
| 1:33 | 3.4 | 0.10154
| 1:33 | 3.4003 | 0.10151
| 1:33 | 3.4006 | 0.10148
| 1:33 | 3.4008 | 0.10144
| 1:33 | 3.4011 | 0.1014
| 1:33 | 3.4014 | 0.10136
| 1:33 | 3.4017 | 0.10131
| 1:33 | 3.4019 | 0.10126
| 1:33 | 3.4022 | 0.10121
| 1:33 | 3.4025 | 0.10115
| 1:33 | 3.4028 | 0.10109
| 1:33 | 3.4031 | 0.10102
| 1:33 | 3.4033 | 0.10096
| 1:33 | 3.4036 | 0.1009
| 1:33 | 3.4039 | 0.10083
| 1:33 | 3.4042 | 0.10076
| 1:33 | 3.4044 | 0.10069
| 1:33 | 3.4047 | 0.10063
| 1:33 | 3.405 | 0.10056
| 1:33 | 3.4053 | 0.10049
| 1:33 | 3.4056 | 0.10041
| 1:33 | 3.4058 | 0.10034
| 1:33 | 3.4061 | 0.10027
| 1:33 | 3.4064 | 0.10019
| 1:33 | 3.4067 | 0.10012
| 1:33 | 3.4069 | 0.10004
| 1:33 | 3.4072 | 0.099963
| 1:33 | 3.4075 | 0.099884
| 1:33 | 3.4078 | 0.099805
| 1:33 | 3.4081 | 0.099724
| 1:33 | 3.4083 | 0.099641
| 1:33 | 3.4086 | 0.099555
| 1:33 | 3.4089 | 0.099466
| 1:33 | 3.4092 | 0.099375
| 1:33 | 3.4094 | 0.099281
| 1:33 | 3.4097 | 0.099185
| 1:33 | 3.41 | 0.099086
| 1:33 | 3.4103 | 0.098984
| 1:33 | 3.4106 | 0.09888
| 1:33 | 3.4108 | 0.098773
| 1:33 | 3.4111 | 0.098663
| 1:33 | 3.4114 | 0.098551
| 1:34 | 3.4117 | 0.098438
| 1:34 | 3.4119 | 0.098325
| 1:34 | 3.4122 | 0.098212
| 1:34 | 3.4125 | 0.098099
| 1:34 | 3.4128 | 0.097987
| 1:34 | 3.4131 | 0.097874
| 1:34 | 3.4133 | 0.097762
| 1:34 | 3.4136 | 0.09765
| 1:34 | 3.4139 | 0.097538
| 1:34 | 3.4142 | 0.097426
| 1:34 | 3.4144 | 0.097314
| 1:34 | 3.4147 | 0.097203
| 1:34 | 3.415 | 0.097091
| 1:34 | 3.4153 | 0.09698
| 1:34 | 3.4156 | 0.096869
| 1:34 | 3.4158 | 0.096758
| 1:34 | 3.4161 | 0.096647
| 1:34 | 3.4164 | 0.096536
| 1:34 | 3.4167 | 0.096426
| 1:34 | 3.4169 | 0.096315
| 1:34 | 3.4172 | 0.096205
| 1:34 | 3.4175 | 0.096095
| 1:34 | 3.4178 | 0.095985
| 1:34 | 3.4181 | 0.095875
| 1:34 | 3.4183 | 0.095765
| 1:34 | 3.4186 | 0.095655
| 1:34 | 3.4189 | 0.095546
| 1:34 | 3.4192 | 0.095436
| 1:34 | 3.4194 | 0.095327
| 1:34 | 3.4197 | 0.095216
| 1:34 | 3.42 | 0.095104
| 1:34 | 3.4203 | 0.09499
| 1:34 | 3.4206 | 0.094874
| 1:34 | 3.4208 | 0.094757
| 1:34 | 3.4211 | 0.094638
| 1:34 | 3.4214 | 0.094517
| 1:34 | 3.4217 | 0.094395
| 1:34 | 3.4219 | 0.09427
| 1:34 | 3.4222 | 0.094145
| 1:34 | 3.4225 | 0.094017
| 1:34 | 3.4228 | 0.093888
| 1:34 | 3.4231 | 0.093757
| 1:34 | 3.4233 | 0.093624
| 1:34 | 3.4236 | 0.09349
| 1:34 | 3.4239 | 0.093354
| 1:34 | 3.4242 | 0.093216
| 1:34 | 3.4244 | 0.093077
| 1:34 | 3.4247 | 0.092936
| 1:34 | 3.425 | 0.092792
| 1:34 | 3.4253 | 0.092644
| 1:34 | 3.4256 | 0.092492
| 1:34 | 3.4258 | 0.092337
| 1:34 | 3.4261 | 0.092179
| 1:34 | 3.4264 | 0.092022
| 1:34 | 3.4267 | 0.091865
| 1:34 | 3.4269 | 0.091708
| 1:34 | 3.4272 | 0.091551
| 1:34 | 3.4275 | 0.091394
| 1:34 | 3.4278 | 0.091235
| 1:34 | 3.4281 | 0.091077
| 1:34 | 3.4283 | 0.090917
| 1:35 | 3.4286 | 0.090757
| 1:35 | 3.4289 | 0.090596
| 1:35 | 3.4292 | 0.090436
| 1:35 | 3.4294 | 0.090279
| 1:35 | 3.4297 | 0.090126
| 1:35 | 3.43 | 0.089977
| 1:35 | 3.4303 | 0.089831
| 1:35 | 3.4306 | 0.089688
| 1:35 | 3.4308 | 0.089549
| 1:35 | 3.4311 | 0.089414
| 1:35 | 3.4314 | 0.089282
| 1:35 | 3.4317 | 0.08915
| 1:35 | 3.4319 | 0.089016
| 1:35 | 3.4322 | 0.08888
| 1:35 | 3.4325 | 0.088743
| 1:35 | 3.4328 | 0.088604
| 1:35 | 3.4331 | 0.088464
| 1:35 | 3.4333 | 0.088322
| 1:35 | 3.4336 | 0.088179
| 1:35 | 3.4339 | 0.088034
| 1:35 | 3.4342 | 0.087887
| 1:35 | 3.4344 | 0.087738
| 1:35 | 3.4347 | 0.087587
| 1:35 | 3.435 | 0.087435
| 1:35 | 3.4353 | 0.08728
| 1:35 | 3.4356 | 0.087124
| 1:35 | 3.4358 | 0.086966
| 1:35 | 3.4361 | 0.086806
| 1:35 | 3.4364 | 0.086644
| 1:35 | 3.4367 | 0.086481
| 1:35 | 3.4369 | 0.086315
| 1:35 | 3.4372 | 0.086148
| 1:35 | 3.4375 | 0.085979
| 1:35 | 3.4378 | 0.085808
| 1:35 | 3.4381 | 0.085635
| 1:35 | 3.4383 | 0.08546
| 1:35 | 3.4386 | 0.085284
| 1:35 | 3.4389 | 0.085105
| 1:35 | 3.4392 | 0.084925
| 1:35 | 3.4394 | 0.084743
| 1:35 | 3.4397 | 0.084559
| 1:35 | 3.44 | 0.084374
| 1:35 | 3.4403 | 0.084186
| 1:35 | 3.4406 | 0.083996
| 1:35 | 3.4408 | 0.083805
| 1:35 | 3.4411 | 0.083609
| 1:35 | 3.4414 | 0.08341
| 1:35 | 3.4417 | 0.083208
| 1:35 | 3.4419 | 0.083002
| 1:35 | 3.4422 | 0.082793
| 1:35 | 3.4425 | 0.082582
| 1:35 | 3.4428 | 0.082367
| 1:35 | 3.4431 | 0.082148
| 1:35 | 3.4433 | 0.081923
| 1:35 | 3.4436 | 0.081695
| 1:35 | 3.4439 | 0.081468
| 1:35 | 3.4442 | 0.081242
| 1:35 | 3.4444 | 0.081017
| 1:35 | 3.4447 | 0.080793
| 1:36 | 3.445 | 0.08057
| 1:36 | 3.4453 | 0.080347
| 1:36 | 3.4456 | 0.080126
| 1:36 | 3.4458 | 0.079904
| 1:36 | 3.4461 | 0.079679
| 1:36 | 3.4464 | 0.07945
| 1:36 | 3.4467 | 0.079217
| 1:36 | 3.4469 | 0.078981
| 1:36 | 3.4472 | 0.078742
| 1:36 | 3.4475 | 0.078499
| 1:36 | 3.4478 | 0.078252
| 1:36 | 3.4481 | 0.078002
| 1:36 | 3.4483 | 0.077755
| 1:36 | 3.4486 | 0.077514
| 1:36 | 3.4489 | 0.077278
| 1:36 | 3.4492 | 0.077043
| 1:36 | 3.4494 | 0.076809
| 1:36 | 3.4497 | 0.076575
| 1:36 | 3.45 | 0.076342
| 1:36 | 3.4503 | 0.076109
| 1:36 | 3.4506 | 0.075877
| 1:36 | 3.4508 | 0.075645
| 1:36 | 3.4511 | 0.075414
| 1:36 | 3.4514 | 0.075183
| 1:36 | 3.4517 | 0.074953
| 1:36 | 3.4519 | 0.074723
| 1:36 | 3.4522 | 0.074494
| 1:36 | 3.4525 | 0.074265
| 1:36 | 3.4528 | 0.074036
| 1:36 | 3.4531 | 0.073809
| 1:36 | 3.4533 | 0.073581
| 1:36 | 3.4536 | 0.073354
| 1:36 | 3.4539 | 0.073128
| 1:36 | 3.4542 | 0.072902
| 1:36 | 3.4544 | 0.072676
| 1:36 | 3.4547 | 0.072451
| 1:36 | 3.455 | 0.072227
| 1:36 | 3.4553 | 0.072003
| 1:36 | 3.4556 | 0.071779
| 1:36 | 3.4558 | 0.071556
| 1:36 | 3.4561 | 0.071334
| 1:36 | 3.4564 | 0.071112
| 1:36 | 3.4567 | 0.07089
| 1:36 | 3.4569 | 0.070669
| 1:36 | 3.4572 | 0.070448
| 1:36 | 3.4575 | 0.070228
| 1:36 | 3.4578 | 0.070008
| 1:36 | 3.4581 | 0.069789
| 1:36 | 3.4583 | 0.069571
| 1:36 | 3.4586 | 0.069352
| 1:36 | 3.4589 | 0.069135
| 1:36 | 3.4592 | 0.068917
| 1:36 | 3.4594 | 0.0687
| 1:36 | 3.4597 | 0.068484
| 1:36 | 3.46 | 0.068268
| 1:36 | 3.4603 | 0.068052
| 1:36 | 3.4606 | 0.067836
| 1:36 | 3.4608 | 0.067618
| 1:36 | 3.4611 | 0.067399
| 1:36 | 3.4614 | 0.067179
| 1:36 | 3.4617 | 0.066958
| 1:37 | 3.4619 | 0.066736
| 1:37 | 3.4622 | 0.066513
| 1:37 | 3.4625 | 0.066291
| 1:37 | 3.4628 | 0.066072
| 1:37 | 3.4631 | 0.065857
| 1:37 | 3.4633 | 0.065646
| 1:37 | 3.4636 | 0.065438
| 1:37 | 3.4639 | 0.065234
| 1:37 | 3.4642 | 0.065034
| 1:37 | 3.4644 | 0.064837
| 1:37 | 3.4647 | 0.064645
| 1:37 | 3.465 | 0.064455
| 1:37 | 3.4653 | 0.06427
| 1:37 | 3.4656 | 0.064096
| 1:37 | 3.4658 | 0.063927
| 1:37 | 3.4661 | 0.063764
| 1:37 | 3.4664 | 0.063606
| 1:37 | 3.4667 | 0.063454
| 1:37 | 3.4669 | 0.063316
| 1:37 | 3.4672 | 0.063183
| 1:37 | 3.4675 | 0.063055
| 1:37 | 3.4678 | 0.06293
| 1:37 | 3.4681 | 0.062801
| 1:37 | 3.4683 | 0.062669
| 1:37 | 3.4686 | 0.062529
| 1:37 | 3.4689 | 0.062377
| 1:37 | 3.4692 | 0.062211
| 1:37 | 3.4694 | 0.062036
| 1:37 | 3.4697 | 0.061861
| 1:37 | 3.47 | 0.061685
| 1:37 | 3.4703 | 0.061509
| 1:37 | 3.4706 | 0.061332
| 1:37 | 3.4708 | 0.061153
| 1:37 | 3.4711 | 0.06097
| 1:37 | 3.4714 | 0.060786
| 1:37 | 3.4717 | 0.060599
| 1:37 | 3.4719 | 0.06041
| 1:37 | 3.4722 | 0.060218
| 1:37 | 3.4725 | 0.060024
| 1:37 | 3.4728 | 0.059829
| 1:37 | 3.4731 | 0.059634
| 1:37 | 3.4733 | 0.059441
| 1:37 | 3.4736 | 0.059248
| 1:37 | 3.4739 | 0.059057
| 1:37 | 3.4742 | 0.058866
| 1:37 | 3.4744 | 0.058676
| 1:37 | 3.4747 | 0.058487
| 1:37 | 3.475 | 0.058299
| 1:37 | 3.4753 | 0.058111
| 1:37 | 3.4756 | 0.057925
| 1:37 | 3.4758 | 0.057743
| 1:37 | 3.4761 | 0.057573
| 1:37 | 3.4764 | 0.057415
| 1:37 | 3.4767 | 0.057257
| 1:37 | 3.4769 | 0.057098
| 1:37 | 3.4772 | 0.056938
| 1:37 | 3.4775 | 0.056777
| 1:37 | 3.4778 | 0.056614
| 1:37 | 3.4781 | 0.056451
| 1:38 | 3.4783 | 0.056286
| 1:38 | 3.4786 | 0.056119
| 1:38 | 3.4789 | 0.055951
| 1:38 | 3.4792 | 0.055777
| 1:38 | 3.4794 | 0.055598
| 1:38 | 3.4797 | 0.055415
| 1:38 | 3.48 | 0.055227
| 1:38 | 3.4803 | 0.055034
| 1:38 | 3.4806 | 0.054836
| 1:38 | 3.4808 | 0.054634
| 1:38 | 3.4811 | 0.054426
| 1:38 | 3.4814 | 0.054214
| 1:38 | 3.4817 | 0.054
| 1:38 | 3.4819 | 0.053782
| 1:38 | 3.4822 | 0.053562
| 1:38 | 3.4825 | 0.053343
| 1:38 | 3.4828 | 0.053124
| 1:38 | 3.4831 | 0.052905
| 1:38 | 3.4833 | 0.052681
| 1:38 | 3.4836 | 0.05245
| 1:38 | 3.4839 | 0.052211
| 1:38 | 3.4842 | 0.051968
| 1:38 | 3.4844 | 0.051731
| 1:38 | 3.4847 | 0.051511
| 1:38 | 3.485 | 0.051305
| 1:38 | 3.4853 | 0.051102
| 1:38 | 3.4856 | 0.050898
| 1:38 | 3.4858 | 0.050692
| 1:38 | 3.4861 | 0.050485
| 1:38 | 3.4864 | 0.050275
| 1:38 | 3.4867 | 0.050064
| 1:38 | 3.4869 | 0.049848
| 1:38 | 3.4872 | 0.049625
| 1:38 | 3.4875 | 0.049401
| 1:38 | 3.4878 | 0.049178
| 1:38 | 3.4881 | 0.048954
| 1:38 | 3.4883 | 0.04873
| 1:38 | 3.4886 | 0.048506
| 1:38 | 3.4889 | 0.048282
| 1:38 | 3.4892 | 0.048058
| 1:38 | 3.4894 | 0.047834
| 1:38 | 3.4897 | 0.047612
| 1:38 | 3.49 | 0.047393
| 1:38 | 3.4903 | 0.047176
| 1:38 | 3.4906 | 0.046961
| 1:38 | 3.4908 | 0.046748
| 1:38 | 3.4911 | 0.046549
| 1:38 | 3.4914 | 0.046365
| 1:38 | 3.4917 | 0.046194
| 1:38 | 3.4919 | 0.046022
| 1:38 | 3.4922 | 0.045847
| 1:38 | 3.4925 | 0.045669
| 1:38 | 3.4928 | 0.045489
| 1:38 | 3.4931 | 0.045304
| 1:38 | 3.4933 | 0.045107
| 1:38 | 3.4936 | 0.044899
| 1:38 | 3.4939 | 0.044679
| 1:38 | 3.4942 | 0.044449
| 1:38 | 3.4944 | 0.044211
| 1:38 | 3.4947 | 0.043964
| 1:39 | 3.495 | 0.043704
| 1:39 | 3.4953 | 0.043426
| 1:39 | 3.4956 | 0.043139
| 1:39 | 3.4958 | 0.042849
| 1:39 | 3.4961 | 0.042558
| 1:39 | 3.4964 | 0.042267
| 1:39 | 3.4967 | 0.041976
| 1:39 | 3.4969 | 0.041684
| 1:39 | 3.4972 | 0.041392
| 1:39 | 3.4975 | 0.0411
| 1:39 | 3.4978 | 0.040808
| 1:39 | 3.4981 | 0.040515
| 1:39 | 3.4983 | 0.040217
| 1:39 | 3.4986 | 0.039913
| 1:39 | 3.4989 | 0.039603
| 1:39 | 3.4992 | 0.03929
| 1:39 | 3.4994 | 0.038973
| 1:39 | 3.4997 | 0.038654
| 1:39 | 3.5 | 0.038331
| 1:39 | 3.5003 | 0.038006
| 1:39 | 3.5006 | 0.037682
| 1:39 | 3.5008 | 0.037356
| 1:39 | 3.5011 | 0.037031
| 1:39 | 3.5014 | 0.036704
| 1:39 | 3.5017 | 0.036379
| 1:39 | 3.5019 | 0.036056
| 1:39 | 3.5022 | 0.035737
| 1:39 | 3.5025 | 0.03542
| 1:39 | 3.5028 | 0.035106
| 1:39 | 3.5031 | 0.034795
| 1:39 | 3.5033 | 0.034487
| 1:39 | 3.5036 | 0.034181
| 1:39 | 3.5039 | 0.033878
| 1:39 | 3.5042 | 0.033574
| 1:39 | 3.5044 | 0.033271
| 1:39 | 3.5047 | 0.032967
| 1:39 | 3.505 | 0.032663
| 1:39 | 3.5053 | 0.032358
| 1:39 | 3.5056 | 0.032054
| 1:39 | 3.5058 | 0.031749
| 1:39 | 3.5061 | 0.031445
| 1:39 | 3.5064 | 0.03114
| 1:39 | 3.5067 | 0.030835
| 1:39 | 3.5069 | 0.030529
| 1:39 | 3.5072 | 0.030232
| 1:39 | 3.5075 | 0.029945
| 1:39 | 3.5078 | 0.029664
| 1:39 | 3.5081 | 0.029388
| 1:39 | 3.5083 | 0.029114
| 1:39 | 3.5086 | 0.028842
| 1:39 | 3.5089 | 0.028572
| 1:39 | 3.5092 | 0.028303
| 1:39 | 3.5094 | 0.028036
| 1:39 | 3.5097 | 0.027771
| 1:39 | 3.51 | 0.027508
| 1:39 | 3.5103 | 0.027246
| 1:39 | 3.5106 | 0.026986
| 1:39 | 3.5108 | 0.026728
| 1:39 | 3.5111 | 0.026482
| 1:39 | 3.5114 | 0.026253
| 1:40 | 3.5117 | 0.026048
| 1:40 | 3.5119 | 0.025852
| 1:40 | 3.5122 | 0.02566
| 1:40 | 3.5125 | 0.025461
| 1:40 | 3.5128 | 0.025253
| 1:40 | 3.5131 | 0.025035
| 1:40 | 3.5133 | 0.024808
| 1:40 | 3.5136 | 0.024571
| 1:40 | 3.5139 | 0.024324
| 1:40 | 3.5142 | 0.024068
| 1:40 | 3.5144 | 0.023803
| 1:40 | 3.5147 | 0.023532
| 1:40 | 3.515 | 0.023266
| 1:40 | 3.5153 | 0.023004
| 1:40 | 3.5156 | 0.022753
| 1:40 | 3.5158 | 0.022514
| 1:40 | 3.5161 | 0.022298
| 1:40 | 3.5164 | 0.022092
| 1:40 | 3.5167 | 0.021893
| 1:40 | 3.5169 | 0.02169
| 1:40 | 3.5172 | 0.021482
| 1:40 | 3.5175 | 0.02127
| 1:40 | 3.5178 | 0.021057
| 1:40 | 3.5181 | 0.020843
| 1:40 | 3.5183 | 0.020629
| 1:40 | 3.5186 | 0.020415
| 1:40 | 3.5189 | 0.020201
| 1:40 | 3.5192 | 0.019986
| 1:40 | 3.5194 | 0.019772
| 1:40 | 3.5197 | 0.019557
| 1:40 | 3.52 | 0.019342
| 1:40 | 3.5203 | 0.019127
| 1:40 | 3.5206 | 0.018912
| 1:40 | 3.5208 | 0.018696
| 1:40 | 3.5211 | 0.01848
| 1:40 | 3.5214 | 0.018263
| 1:40 | 3.5217 | 0.018046
| 1:40 | 3.5219 | 0.017828
| 1:40 | 3.5222 | 0.017609
| 1:40 | 3.5225 | 0.01739
| 1:40 | 3.5228 | 0.017171
| 1:40 | 3.5231 | 0.016951
| 1:40 | 3.5233 | 0.01673
| 1:40 | 3.5236 | 0.016501
| 1:40 | 3.5239 | 0.016271
| 1:40 | 3.5242 | 0.01604
| 1:40 | 3.5244 | 0.015809
| 1:40 | 3.5247 | 0.015577
| 1:40 | 3.525 | 0.015345
| 1:40 | 3.5253 | 0.015112
| 1:40 | 3.5256 | 0.014878
| 1:40 | 3.5258 | 0.014644
| 1:40 | 3.5261 | 0.014409
| 1:40 | 3.5264 | 0.014174
| 1:40 | 3.5267 | 0.013938
| 1:40 | 3.5269 | 0.013701
| 1:40 | 3.5272 | 0.013463
| 1:40 | 3.5275 | 0.013223
| 1:40 | 3.5278 | 0.01298
| 1:40 | 3.5281 | 0.012726
| 1:40 | 3.5283 | 0.012457
| 1:41 | 3.5286 | 0.012174
| 1:41 | 3.5289 | 0.011877
| 1:41 | 3.5292 | 0.011576
| 1:41 | 3.5294 | 0.011272
| 1:41 | 3.5297 | 0.010966
| 1:41 | 3.53 | 0.010658
| 1:41 | 3.5303 | 0.010348
| 1:41 | 3.5306 | 0.010035
| 1:41 | 3.5308 | 0.0097197
| 1:41 | 3.5311 | 0.0094022
| 1:41 | 3.5314 | 0.0090824
| 1:41 | 3.5317 | 0.0087602
| 1:41 | 3.5319 | 0.0084357
| 1:41 | 3.5322 | 0.0081089
| 1:41 | 3.5325 | 0.0077797
| 1:41 | 3.5328 | 0.0074482
| 1:41 | 3.5331 | 0.0071144
| 1:41 | 3.5333 | 0.0067782
| 1:41 | 3.5336 | 0.0064397
| 1:41 | 3.5339 | 0.0061005
| 1:41 | 3.5342 | 0.005761
| 1:41 | 3.5344 | 0.0054212
| 1:41 | 3.5347 | 0.0050813
| 1:41 | 3.535 | 0.0047412
| 1:41 | 3.5353 | 0.0044008
| 1:41 | 3.5356 | 0.0040602
| 1:41 | 3.5358 | 0.0037194
| 1:41 | 3.5361 | 0.0033784
| 1:41 | 3.5364 | 0.0030372
| 1:41 | 3.5367 | 0.0026958
| 1:41 | 3.5369 | 0.0023541
| 1:41 | 3.5372 | 0.0020122
| 1:41 | 3.5375 | 0.0016701
| 1:41 | 3.5378 | 0.0013278
| 1:41 | 3.5381 | 0.00098527
| 1:41 | 3.5383 | 0.00064251
| 1:41 | 3.5386 | 0.00029952
| 1:41 | 3.5389 | -4.3685e-05
| 1:41 | 3.5392 | -0.00038711
| 1:41 | 3.5394 | -0.00073076
| 1:41 | 3.5397 | -0.0010746
| 1:41 | 3.54 | -0.0014187
| 1:41 | 3.5403 | -0.0017646
| 1:41 | 3.5406 | -0.0021138
| 1:41 | 3.5408 | -0.0024663
| 1:41 | 3.5411 | -0.0028222
| 1:41 | 3.5414 | -0.0031814
| 1:41 | 3.5417 | -0.0035439
| 1:41 | 3.5419 | -0.0039098
| 1:41 | 3.5422 | -0.004279
| 1:41 | 3.5425 | -0.0046516
| 1:41 | 3.5428 | -0.0050275
| 1:41 | 3.5431 | -0.0054067
| 1:41 | 3.5433 | -0.0057893
| 1:41 | 3.5436 | -0.006173
| 1:41 | 3.5439 | -0.0065555
| 1:41 | 3.5442 | -0.006937
| 1:41 | 3.5444 | -0.0073173
| 1:41 | 3.5447 | -0.0076966
| 1:42 | 3.545 | -0.0080747
| 1:42 | 3.5453 | -0.0084517
| 1:42 | 3.5456 | -0.0088276
| 1:42 | 3.5458 | -0.0092024
| 1:42 | 3.5461 | -0.0095761
| 1:42 | 3.5464 | -0.0099487
| 1:42 | 3.5467 | -0.01032
| 1:42 | 3.5469 | -0.01069
| 1:42 | 3.5472 | -0.01106
| 1:42 | 3.5475 | -0.011428
| 1:42 | 3.5478 | -0.011795
| 1:42 | 3.5481 | -0.012161
| 1:42 | 3.5483 | -0.012526
| 1:42 | 3.5486 | -0.012889
| 1:42 | 3.5489 | -0.013252
| 1:42 | 3.5492 | -0.013613
| 1:42 | 3.5494 | -0.013973
| 1:42 | 3.5497 | -0.014332
| 1:42 | 3.55 | -0.014689
| 1:42 | 3.5503 | -0.015045
| 1:42 | 3.5506 | -0.015399
| 1:42 | 3.5508 | -0.015751
| 1:42 | 3.5511 | -0.016102
| 1:42 | 3.5514 | -0.01645
| 1:42 | 3.5517 | -0.016794
| 1:42 | 3.5519 | -0.017133
| 1:42 | 3.5522 | -0.017468
| 1:42 | 3.5525 | -0.017798
| 1:42 | 3.5528 | -0.018125
| 1:42 | 3.5531 | -0.018443
| 1:42 | 3.5533 | -0.018753
| 1:42 | 3.5536 | -0.01906
| 1:42 | 3.5539 | -0.019363
| 1:42 | 3.5542 | -0.019662
| 1:42 | 3.5544 | -0.019958
| 1:42 | 3.5547 | -0.020251
| 1:42 | 3.555 | -0.02054
| 1:42 | 3.5553 | -0.020825
| 1:42 | 3.5556 | -0.021107
| 1:42 | 3.5558 | -0.021386
| 1:42 | 3.5561 | -0.02166
| 1:42 | 3.5564 | -0.021923
| 1:42 | 3.5567 | -0.022188
| 1:42 | 3.5569 | -0.022455
| 1:42 | 3.5572 | -0.022736
| 1:42 | 3.5575 | -0.023032
| 1:42 | 3.5578 | -0.023323
| 1:42 | 3.5581 | -0.023609
| 1:42 | 3.5583 | -0.02389
| 1:42 | 3.5586 | -0.024155
| 1:42 | 3.5589 | -0.024399
| 1:42 | 3.5592 | -0.024627
| 1:42 | 3.5594 | -0.024841
| 1:42 | 3.5597 | -0.02505
| 1:42 | 3.56 | -0.025258
| 1:42 | 3.5603 | -0.025466
| 1:42 | 3.5606 | -0.025674
| 1:42 | 3.5608 | -0.025881
| 1:42 | 3.5611 | -0.026088
| 1:42 | 3.5614 | -0.026294
| 1:42 | 3.5617 | -0.026503
| 1:43 | 3.5619 | -0.026712
| 1:43 | 3.5622 | -0.026923
| 1:43 | 3.5625 | -0.027133
| 1:43 | 3.5628 | -0.027341
| 1:43 | 3.5631 | -0.027546
| 1:43 | 3.5633 | -0.02775
| 1:43 | 3.5636 | -0.027951
| 1:43 | 3.5639 | -0.02815
| 1:43 | 3.5642 | -0.028347
| 1:43 | 3.5644 | -0.028542
| 1:43 | 3.5647 | -0.028734
| 1:43 | 3.565 | -0.028925
| 1:43 | 3.5653 | -0.029113
| 1:43 | 3.5656 | -0.029299
| 1:43 | 3.5658 | -0.029483
| 1:43 | 3.5661 | -0.029665
| 1:43 | 3.5664 | -0.029846
| 1:43 | 3.5667 | -0.030025
| 1:43 | 3.5669 | -0.030204
| 1:43 | 3.5672 | -0.030381
| 1:43 | 3.5675 | -0.030557
| 1:43 | 3.5678 | -0.030731
| 1:43 | 3.5681 | -0.030907
| 1:43 | 3.5683 | -0.031087
| 1:43 | 3.5686 | -0.031271
| 1:43 | 3.5689 | -0.031459
| 1:43 | 3.5692 | -0.031651
| 1:43 | 3.5694 | -0.031852
| 1:43 | 3.5697 | -0.032058
| 1:43 | 3.57 | -0.032267
| 1:43 | 3.5703 | -0.032479
| 1:43 | 3.5706 | -0.032694
| 1:43 | 3.5708 | -0.03291
| 1:43 | 3.5711 | -0.033129
| 1:43 | 3.5714 | -0.03335
| 1:43 | 3.5717 | -0.033573
| 1:43 | 3.5719 | -0.033799
| 1:43 | 3.5722 | -0.034026
| 1:43 | 3.5725 | -0.034255
| 1:43 | 3.5728 | -0.034487
| 1:43 | 3.5731 | -0.034719
| 1:43 | 3.5733 | -0.034951
| 1:43 | 3.5736 | -0.035183
| 1:43 | 3.5739 | -0.035415
| 1:43 | 3.5742 | -0.035646
| 1:43 | 3.5744 | -0.035875
| 1:43 | 3.5747 | -0.036098
| 1:43 | 3.575 | -0.036304
| 1:43 | 3.5753 | -0.036493
| 1:43 | 3.5756 | -0.036671
| 1:43 | 3.5758 | -0.036846
| 1:43 | 3.5761 | -0.037018
| 1:43 | 3.5764 | -0.037189
| 1:43 | 3.5767 | -0.037358
| 1:43 | 3.5769 | -0.037525
| 1:43 | 3.5772 | -0.037691
| 1:43 | 3.5775 | -0.037851
| 1:43 | 3.5778 | -0.038002
| 1:43 | 3.5781 | -0.038149
| 1:43 | 3.5783 | -0.038294
| 1:44 | 3.5786 | -0.038439
| 1:44 | 3.5789 | -0.038582
| 1:44 | 3.5792 | -0.038724
| 1:44 | 3.5794 | -0.038863
| 1:44 | 3.5797 | -0.038998
| 1:44 | 3.58 | -0.03913
| 1:44 | 3.5803 | -0.039259
| 1:44 | 3.5806 | -0.039385
| 1:44 | 3.5808 | -0.039508
| 1:44 | 3.5811 | -0.039628
| 1:44 | 3.5814 | -0.039744
| 1:44 | 3.5817 | -0.039858
| 1:44 | 3.5819 | -0.039968
| 1:44 | 3.5822 | -0.040075
| 1:44 | 3.5825 | -0.040159
| 1:44 | 3.5828 | -0.040221
| 1:44 | 3.5831 | -0.040274
| 1:44 | 3.5833 | -0.04031
| 1:44 | 3.5836 | -0.040328
| 1:44 | 3.5839 | -0.040335
| 1:44 | 3.5842 | -0.040333
| 1:44 | 3.5844 | -0.040324
| 1:44 | 3.5847 | -0.040309
| 1:44 | 3.585 | -0.040288
| 1:44 | 3.5853 | -0.040261
| 1:44 | 3.5856 | -0.040227
| 1:44 | 3.5858 | -0.040183
| 1:44 | 3.5861 | -0.040129
| 1:44 | 3.5864 | -0.040067
| 1:44 | 3.5867 | -0.040001
| 1:44 | 3.5869 | -0.039935
| 1:44 | 3.5872 | -0.03987
| 1:44 | 3.5875 | -0.039805
| 1:44 | 3.5878 | -0.039739
| 1:44 | 3.5881 | -0.039675
| 1:44 | 3.5883 | -0.03961
| 1:44 | 3.5886 | -0.039545
| 1:44 | 3.5889 | -0.039481
| 1:44 | 3.5892 | -0.039417
| 1:44 | 3.5894 | -0.039353
| 1:44 | 3.5897 | -0.039289
| 1:44 | 3.59 | -0.039238
| 1:44 | 3.5903 | -0.039193
| 1:44 | 3.5906 | -0.039155
| 1:44 | 3.5908 | -0.039134
| 1:44 | 3.5911 | -0.039121
| 1:44 | 3.5914 | -0.039127
| 1:44 | 3.5917 | -0.039142
| 1:44 | 3.5919 | -0.039162
| 1:44 | 3.5922 | -0.039182
| 1:44 | 3.5925 | -0.039203
| 1:44 | 3.5928 | -0.039226
| 1:44 | 3.5931 | -0.039249
| 1:44 | 3.5933 | -0.039272
| 1:44 | 3.5936 | -0.039297
| 1:44 | 3.5939 | -0.039323
| 1:44 | 3.5942 | -0.039351
| 1:44 | 3.5944 | -0.039381
| 1:44 | 3.5947 | -0.039412
| 1:45 | 3.595 | -0.039448
| 1:45 | 3.5953 | -0.039489
| 1:45 | 3.5956 | -0.039537
| 1:45 | 3.5958 | -0.039589
| 1:45 | 3.5961 | -0.039643
| 1:45 | 3.5964 | -0.039697
| 1:45 | 3.5967 | -0.039753
| 1:45 | 3.5969 | -0.03981
| 1:45 | 3.5972 | -0.039869
| 1:45 | 3.5975 | -0.039929
| 1:45 | 3.5978 | -0.03999
| 1:45 | 3.5981 | -0.040053
| 1:45 | 3.5983 | -0.040122
| 1:45 | 3.5986 | -0.040197
| 1:45 | 3.5989 | -0.040274
| 1:45 | 3.5992 | -0.040353
| 1:45 | 3.5994 | -0.040432
| 1:45 | 3.5997 | -0.040512
| 1:45 | 3.6 | -0.040593
| 1:45 | 3.6003 | -0.040674
| 1:45 | 3.6006 | -0.040757
| 1:45 | 3.6008 | -0.04084
| 1:45 | 3.6011 | -0.040925
| 1:45 | 3.6014 | -0.04101
| 1:45 | 3.6017 | -0.041108
| 1:45 | 3.6019 | -0.041226
| 1:45 | 3.6022 | -0.041365
| 1:45 | 3.6025 | -0.041512
| 1:45 | 3.6028 | -0.041658
| 1:45 | 3.6031 | -0.041804
| 1:45 | 3.6033 | -0.041938
| 1:45 | 3.6036 | -0.042053
| 1:45 | 3.6039 | -0.042156
| 1:45 | 3.6042 | -0.04225
| 1:45 | 3.6044 | -0.042338
| 1:45 | 3.6047 | -0.042421
| 1:45 | 3.605 | -0.042498
| 1:45 | 3.6053 | -0.042569
| 1:45 | 3.6056 | -0.042635
| 1:45 | 3.6058 | -0.042694
| 1:45 | 3.6061 | -0.042749
| 1:45 | 3.6064 | -0.042805
| 1:45 | 3.6067 | -0.042862
| 1:45 | 3.6069 | -0.042921
| 1:45 | 3.6072 | -0.042981
| 1:45 | 3.6075 | -0.043044
| 1:45 | 3.6078 | -0.043107
| 1:45 | 3.6081 | -0.043172
| 1:45 | 3.6083 | -0.043239
| 1:45 | 3.6086 | -0.043307
| 1:45 | 3.6089 | -0.043377
| 1:45 | 3.6092 | -0.043449
| 1:45 | 3.6094 | -0.043522
| 1:45 | 3.6097 | -0.043596
| 1:45 | 3.61 | -0.043672
| 1:45 | 3.6103 | -0.04375
| 1:45 | 3.6106 | -0.04383
| 1:45 | 3.6108 | -0.043913
| 1:45 | 3.6111 | -0.043998
| 1:45 | 3.6114 | -0.044086
| 1:46 | 3.6117 | -0.044177
| 1:46 | 3.6119 | -0.044271
| 1:46 | 3.6122 | -0.044368
| 1:46 | 3.6125 | -0.044471
| 1:46 | 3.6128 | -0.044584
| 1:46 | 3.6131 | -0.044705
| 1:46 | 3.6133 | -0.044835
| 1:46 | 3.6136 | -0.044974
| 1:46 | 3.6139 | -0.045123
| 1:46 | 3.6142 | -0.04528
| 1:46 | 3.6144 | -0.045446
| 1:46 | 3.6147 | -0.04562
| 1:46 | 3.615 | -0.045801
| 1:46 | 3.6153 | -0.045991
| 1:46 | 3.6156 | -0.046199
| 1:46 | 3.6158 | -0.04642
| 1:46 | 3.6161 | -0.046657
| 1:46 | 3.6164 | -0.046914
| 1:46 | 3.6167 | -0.047184
| 1:46 | 3.6169 | -0.047468
| 1:46 | 3.6172 | -0.047757
| 1:46 | 3.6175 | -0.048049
| 1:46 | 3.6178 | -0.048344
| 1:46 | 3.6181 | -0.048644
| 1:46 | 3.6183 | -0.04895
| 1:46 | 3.6186 | -0.049266
| 1:46 | 3.6189 | -0.049593
| 1:46 | 3.6192 | -0.049922
| 1:46 | 3.6194 | -0.050251
| 1:46 | 3.6197 | -0.050581
| 1:46 | 3.62 | -0.05091
| 1:46 | 3.6203 | -0.05124
| 1:46 | 3.6206 | -0.051569
| 1:46 | 3.6208 | -0.051899
| 1:46 | 3.6211 | -0.052228
| 1:46 | 3.6214 | -0.052558
| 1:46 | 3.6217 | -0.052887
| 1:46 | 3.6219 | -0.053216
| 1:46 | 3.6222 | -0.053546
| 1:46 | 3.6225 | -0.053875
| 1:46 | 3.6228 | -0.054205
| 1:46 | 3.6231 | -0.054533
| 1:46 | 3.6233 | -0.05486
| 1:46 | 3.6236 | -0.055184
| 1:46 | 3.6239 | -0.0555
| 1:46 | 3.6242 | -0.055803
| 1:46 | 3.6244 | -0.05609
| 1:46 | 3.6247 | -0.056367
| 1:46 | 3.625 | -0.056632
| 1:46 | 3.6253 | -0.056887
| 1:46 | 3.6256 | -0.057131
| 1:46 | 3.6258 | -0.057365
| 1:46 | 3.6261 | -0.057584
| 1:46 | 3.6264 | -0.057793
| 1:46 | 3.6267 | -0.057995
| 1:46 | 3.6269 | -0.058189
| 1:46 | 3.6272 | -0.058376
| 1:46 | 3.6275 | -0.058556
| 1:46 | 3.6278 | -0.058729
| 1:46 | 3.6281 | -0.058894
| 1:46 | 3.6283 | -0.059052
| 1:47 | 3.6286 | -0.059204
| 1:47 | 3.6289 | -0.05935
| 1:47 | 3.6292 | -0.059492
| 1:47 | 3.6294 | -0.059631
| 1:47 | 3.6297 | -0.059767
| 1:47 | 3.63 | -0.0599
| 1:47 | 3.6303 | -0.060031
| 1:47 | 3.6306 | -0.060158
| 1:47 | 3.6308 | -0.060283
| 1:47 | 3.6311 | -0.060405
| 1:47 | 3.6314 | -0.060524
| 1:47 | 3.6317 | -0.06064
| 1:47 | 3.6319 | -0.060754
| 1:47 | 3.6322 | -0.060864
| 1:47 | 3.6325 | -0.060972
| 1:47 | 3.6328 | -0.061076
| 1:47 | 3.6331 | -0.061178
| 1:47 | 3.6333 | -0.061278
| 1:47 | 3.6336 | -0.061375
| 1:47 | 3.6339 | -0.06147
| 1:47 | 3.6342 | -0.061564
| 1:47 | 3.6344 | -0.061655
| 1:47 | 3.6347 | -0.061743
| 1:47 | 3.635 | -0.061828
| 1:47 | 3.6353 | -0.061911
| 1:47 | 3.6356 | -0.06199
| 1:47 | 3.6358 | -0.062069
| 1:47 | 3.6361 | -0.062148
| 1:47 | 3.6364 | -0.062227
| 1:47 | 3.6367 | -0.062306
| 1:47 | 3.6369 | -0.062384
| 1:47 | 3.6372 | -0.062463
| 1:47 | 3.6375 | -0.062542
| 1:47 | 3.6378 | -0.062621
| 1:47 | 3.6381 | -0.062699
| 1:47 | 3.6383 | -0.062778
| 1:47 | 3.6386 | -0.062857
| 1:47 | 3.6389 | -0.062935
| 1:47 | 3.6392 | -0.063014
| 1:47 | 3.6394 | -0.063094
| 1:47 | 3.6397 | -0.063178
| 1:47 | 3.64 | -0.063263
| 1:47 | 3.6403 | -0.063349
| 1:47 | 3.6406 | -0.063434
| 1:47 | 3.6408 | -0.06352
| 1:47 | 3.6411 | -0.063606
| 1:47 | 3.6414 | -0.063693
| 1:47 | 3.6417 | -0.06378
| 1:47 | 3.6419 | -0.063867
| 1:47 | 3.6422 | -0.063954
| 1:47 | 3.6425 | -0.064042
| 1:47 | 3.6428 | -0.06413
| 1:47 | 3.6431 | -0.064221
| 1:47 | 3.6433 | -0.064318
| 1:47 | 3.6436 | -0.064421
| 1:47 | 3.6439 | -0.06453
| 1:47 | 3.6442 | -0.064643
| 1:47 | 3.6444 | -0.064759
| 1:47 | 3.6447 | -0.064879
| 1:48 | 3.645 | -0.065002
| 1:48 | 3.6453 | -0.065131
| 1:48 | 3.6456 | -0.06527
| 1:48 | 3.6458 | -0.06541
| 1:48 | 3.6461 | -0.065548
| 1:48 | 3.6464 | -0.065685
| 1:48 | 3.6467 | -0.06582
| 1:48 | 3.6469 | -0.065953
| 1:48 | 3.6472 | -0.066084
| 1:48 | 3.6475 | -0.066213
| 1:48 | 3.6478 | -0.066341
| 1:48 | 3.6481 | -0.066466
| 1:48 | 3.6483 | -0.06659
| 1:48 | 3.6486 | -0.066712
| 1:48 | 3.6489 | -0.066831
| 1:48 | 3.6492 | -0.066946
| 1:48 | 3.6494 | -0.067058
| 1:48 | 3.6497 | -0.067165
| 1:48 | 3.65 | -0.06727
| 1:48 | 3.6503 | -0.067369
| 1:48 | 3.6506 | -0.067462
| 1:48 | 3.6508 | -0.06755
| 1:48 | 3.6511 | -0.067632
| 1:48 | 3.6514 | -0.067708
| 1:48 | 3.6517 | -0.067778
| 1:48 | 3.6519 | -0.067843
| 1:48 | 3.6522 | -0.067902
| 1:48 | 3.6525 | -0.067953
| 1:48 | 3.6528 | -0.067994
| 1:48 | 3.6531 | -0.068026
| 1:48 | 3.6533 | -0.068056
| 1:48 | 3.6536 | -0.068085
| 1:48 | 3.6539 | -0.068115
| 1:48 | 3.6542 | -0.068145
| 1:48 | 3.6544 | -0.068175
| 1:48 | 3.6547 | -0.068205
| 1:48 | 3.655 | -0.068235
| 1:48 | 3.6553 | -0.068266
| 1:48 | 3.6556 | -0.068296
| 1:48 | 3.6558 | -0.068326
| 1:48 | 3.6561 | -0.068357
| 1:48 | 3.6564 | -0.068387
| 1:48 | 3.6567 | -0.068418
| 1:48 | 3.6569 | -0.068449
| 1:48 | 3.6572 | -0.06848
| 1:48 | 3.6575 | -0.068511
| 1:48 | 3.6578 | -0.068542
| 1:48 | 3.6581 | -0.068572
| 1:48 | 3.6583 | -0.068602
| 1:48 | 3.6586 | -0.06863
| 1:48 | 3.6589 | -0.068653
| 1:48 | 3.6592 | -0.068672
| 1:48 | 3.6594 | -0.068685
| 1:48 | 3.6597 | -0.068693
| 1:48 | 3.66 | -0.068695
| 1:48 | 3.6603 | -0.068693
| 1:48 | 3.6606 | -0.068685
| 1:48 | 3.6608 | -0.068671
| 1:48 | 3.6611 | -0.06865
| 1:48 | 3.6614 | -0.068624
| 1:48 | 3.6617 | -0.068592
| 1:49 | 3.6619 | -0.068559
| 1:49 | 3.6622 | -0.068526
| 1:49 | 3.6625 | -0.068493
| 1:49 | 3.6628 | -0.06846
| 1:49 | 3.6631 | -0.068427
| 1:49 | 3.6633 | -0.068394
| 1:49 | 3.6636 | -0.06836
| 1:49 | 3.6639 | -0.068327
| 1:49 | 3.6642 | -0.068293
| 1:49 | 3.6644 | -0.068259
| 1:49 | 3.6647 | -0.068225
| 1:49 | 3.665 | -0.068191
| 1:49 | 3.6653 | -0.068157
| 1:49 | 3.6656 | -0.068123
| 1:49 | 3.6658 | -0.068088
| 1:49 | 3.6661 | -0.068054
| 1:49 | 3.6664 | -0.068019
| 1:49 | 3.6667 | -0.067985
| 1:49 | 3.6669 | -0.06795
| 1:49 | 3.6672 | -0.067915
| 1:49 | 3.6675 | -0.06788
| 1:49 | 3.6678 | -0.067838
| 1:49 | 3.6681 | -0.067785
| 1:49 | 3.6683 | -0.067719
| 1:49 | 3.6686 | -0.067641
| 1:49 | 3.6689 | -0.06755
| 1:49 | 3.6692 | -0.067444
| 1:49 | 3.6694 | -0.067324
| 1:49 | 3.6697 | -0.067188
| 1:49 | 3.67 | -0.067038
| 1:49 | 3.6703 | -0.066877
| 1:49 | 3.6706 | -0.066712
| 1:49 | 3.6708 | -0.066548
| 1:49 | 3.6711 | -0.066384
| 1:49 | 3.6714 | -0.066222
| 1:49 | 3.6717 | -0.06606
| 1:49 | 3.6719 | -0.0659
| 1:49 | 3.6722 | -0.06574
| 1:49 | 3.6725 | -0.06558
| 1:49 | 3.6728 | -0.065422
| 1:49 | 3.6731 | -0.065264
| 1:49 | 3.6733 | -0.065108
| 1:49 | 3.6736 | -0.064952
| 1:49 | 3.6739 | -0.064796
| 1:49 | 3.6742 | -0.064642
| 1:49 | 3.6744 | -0.064489
| 1:49 | 3.6747 | -0.064336
| 1:49 | 3.675 | -0.064184
| 1:49 | 3.6753 | -0.064033
| 1:49 | 3.6756 | -0.063885
| 1:49 | 3.6758 | -0.063745
| 1:49 | 3.6761 | -0.06361
| 1:49 | 3.6764 | -0.063482
| 1:49 | 3.6767 | -0.06336
| 1:49 | 3.6769 | -0.063244
| 1:49 | 3.6772 | -0.063135
| 1:49 | 3.6775 | -0.063026
| 1:49 | 3.6778 | -0.062917
| 1:49 | 3.6781 | -0.062806
| 1:49 | 3.6783 | -0.062694
| 1:50 | 3.6786 | -0.06258
| 1:50 | 3.6789 | -0.062465
| 1:50 | 3.6792 | -0.062351
| 1:50 | 3.6794 | -0.062242
| 1:50 | 3.6797 | -0.062136
| 1:50 | 3.68 | -0.062034
| 1:50 | 3.6803 | -0.061935
| 1:50 | 3.6806 | -0.061841
| 1:50 | 3.6808 | -0.06175
| 1:50 | 3.6811 | -0.061663
| 1:50 | 3.6814 | -0.06158
| 1:50 | 3.6817 | -0.061499
| 1:50 | 3.6819 | -0.061421
| 1:50 | 3.6822 | -0.061345
| 1:50 | 3.6825 | -0.061272
| 1:50 | 3.6828 | -0.061201
| 1:50 | 3.6831 | -0.061134
| 1:50 | 3.6833 | -0.061071
| 1:50 | 3.6836 | -0.061012
| 1:50 | 3.6839 | -0.060954
| 1:50 | 3.6842 | -0.060897
| 1:50 | 3.6844 | -0.060841
| 1:50 | 3.6847 | -0.060786
| 1:50 | 3.685 | -0.060731
| 1:50 | 3.6853 | -0.060677
| 1:50 | 3.6856 | -0.060624
| 1:50 | 3.6858 | -0.060572
| 1:50 | 3.6861 | -0.06052
| 1:50 | 3.6864 | -0.060469
| 1:50 | 3.6867 | -0.060416
| 1:50 | 3.6869 | -0.060362
| 1:50 | 3.6872 | -0.060308
| 1:50 | 3.6875 | -0.06025
| 1:50 | 3.6878 | -0.060189
| 1:50 | 3.6881 | -0.060124
| 1:50 | 3.6883 | -0.060055
| 1:50 | 3.6886 | -0.059982
| 1:50 | 3.6889 | -0.059904
| 1:50 | 3.6892 | -0.059823
| 1:50 | 3.6894 | -0.059738
| 1:50 | 3.6897 | -0.059651
| 1:50 | 3.69 | -0.059564
| 1:50 | 3.6903 | -0.059478
| 1:50 | 3.6906 | -0.059392
| 1:50 | 3.6908 | -0.059307
| 1:50 | 3.6911 | -0.059223
| 1:50 | 3.6914 | -0.059139
| 1:50 | 3.6917 | -0.059056
| 1:50 | 3.6919 | -0.058973
| 1:50 | 3.6922 | -0.058893
| 1:50 | 3.6925 | -0.058821
| 1:50 | 3.6928 | -0.058755
| 1:50 | 3.6931 | -0.058704
| 1:50 | 3.6933 | -0.058653
| 1:50 | 3.6936 | -0.058602
| 1:50 | 3.6939 | -0.058552
| 1:50 | 3.6942 | -0.058501
| 1:50 | 3.6944 | -0.05845
| 1:50 | 3.6947 | -0.0584
| 1:50 | 3.695 | -0.05835
| 1:51 | 3.6953 | -0.058299
| 1:51 | 3.6956 | -0.058249
| 1:51 | 3.6958 | -0.058198
| 1:51 | 3.6961 | -0.058145
| 1:51 | 3.6964 | -0.05809
| 1:51 | 3.6967 | -0.058033
| 1:51 | 3.6969 | -0.057974
| 1:51 | 3.6972 | -0.057913
| 1:51 | 3.6975 | -0.05785
| 1:51 | 3.6978 | -0.057785
| 1:51 | 3.6981 | -0.057718
| 1:51 | 3.6983 | -0.057652
| 1:51 | 3.6986 | -0.057585
| 1:51 | 3.6989 | -0.057518
| 1:51 | 3.6992 | -0.057451
| 1:51 | 3.6994 | -0.057384
| 1:51 | 3.6997 | -0.057318
| 1:51 | 3.7 | -0.057251
| 1:51 | 3.7003 | -0.057184
| 1:51 | 3.7006 | -0.057117
| 1:51 | 3.7008 | -0.05705
| 1:51 | 3.7011 | -0.056984
| 1:51 | 3.7014 | -0.056917
| 1:51 | 3.7017 | -0.05685
| 1:51 | 3.7019 | -0.056783
| 1:51 | 3.7022 | -0.056717
| 1:51 | 3.7025 | -0.05665
| 1:51 | 3.7028 | -0.056583
| 1:51 | 3.7031 | -0.056516
| 1:51 | 3.7033 | -0.05645
| 1:51 | 3.7036 | -0.056383
| 1:51 | 3.7039 | -0.056316
| 1:51 | 3.7042 | -0.056247
| 1:51 | 3.7044 | -0.056175
| 1:51 | 3.7047 | -0.056098
| 1:51 | 3.705 | -0.056017
| 1:51 | 3.7053 | -0.055933
| 1:51 | 3.7056 | -0.055844
| 1:51 | 3.7058 | -0.055752
| 1:51 | 3.7061 | -0.055655
| 1:51 | 3.7064 | -0.055554
| 1:51 | 3.7067 | -0.05545
| 1:51 | 3.7069 | -0.055341
| 1:51 | 3.7072 | -0.055229
| 1:51 | 3.7075 | -0.055112
| 1:51 | 3.7078 | -0.054989
| 1:51 | 3.7081 | -0.054857
| 1:51 | 3.7083 | -0.054703
| 1:51 | 3.7086 | -0.054536
| 1:51 | 3.7089 | -0.054359
| 1:51 | 3.7092 | -0.054174
| 1:51 | 3.7094 | -0.053982
| 1:51 | 3.7097 | -0.053784
| 1:51 | 3.71 | -0.053582
| 1:51 | 3.7103 | -0.053376
| 1:51 | 3.7106 | -0.053165
| 1:51 | 3.7108 | -0.052953
| 1:51 | 3.7111 | -0.052744
| 1:51 | 3.7114 | -0.052536
| 1:52 | 3.7117 | -0.052332
| 1:52 | 3.7119 | -0.052129
| 1:52 | 3.7122 | -0.051929
| 1:52 | 3.7125 | -0.051728
| 1:52 | 3.7128 | -0.051524
| 1:52 | 3.7131 | -0.051317
| 1:52 | 3.7133 | -0.051107
| 1:52 | 3.7136 | -0.050893
| 1:52 | 3.7139 | -0.050676
| 1:52 | 3.7142 | -0.050455
| 1:52 | 3.7144 | -0.050232
| 1:52 | 3.7147 | -0.050005
| 1:52 | 3.715 | -0.04976
| 1:52 | 3.7153 | -0.04951
| 1:52 | 3.7156 | -0.049255
| 1:52 | 3.7158 | -0.048995
| 1:52 | 3.7161 | -0.048731
| 1:52 | 3.7164 | -0.048461
| 1:52 | 3.7167 | -0.048186
| 1:52 | 3.7169 | -0.047909
| 1:52 | 3.7172 | -0.04763
| 1:52 | 3.7175 | -0.04735
| 1:52 | 3.7178 | -0.047069
| 1:52 | 3.7181 | -0.046788
| 1:52 | 3.7183 | -0.046505
| 1:52 | 3.7186 | -0.046217
| 1:52 | 3.7189 | -0.045918
| 1:52 | 3.7192 | -0.045609
| 1:52 | 3.7194 | -0.045296
| 1:52 | 3.7197 | -0.044984
| 1:52 | 3.72 | -0.044673
| 1:52 | 3.7203 | -0.044363
| 1:52 | 3.7206 | -0.044054
| 1:52 | 3.7208 | -0.043746
| 1:52 | 3.7211 | -0.04344
| 1:52 | 3.7214 | -0.043135
| 1:52 | 3.7217 | -0.04283
| 1:52 | 3.7219 | -0.042527
| 1:52 | 3.7222 | -0.042226
| 1:52 | 3.7225 | -0.041925
| 1:52 | 3.7228 | -0.041625
| 1:52 | 3.7231 | -0.041327
| 1:52 | 3.7233 | -0.04103
| 1:52 | 3.7236 | -0.040733
| 1:52 | 3.7239 | -0.040438
| 1:52 | 3.7242 | -0.040142
| 1:52 | 3.7244 | -0.03984
| 1:52 | 3.7247 | -0.039533
| 1:52 | 3.725 | -0.039222
| 1:52 | 3.7253 | -0.038909
| 1:52 | 3.7256 | -0.038598
| 1:52 | 3.7258 | -0.038289
| 1:52 | 3.7261 | -0.037982
| 1:52 | 3.7264 | -0.037678
| 1:52 | 3.7267 | -0.037375
| 1:52 | 3.7269 | -0.037074
| 1:52 | 3.7272 | -0.036776
| 1:52 | 3.7275 | -0.036478
| 1:52 | 3.7278 | -0.036181
| 1:52 | 3.7281 | -0.035883
| 1:52 | 3.7283 | -0.035586
| 1:53 | 3.7286 | -0.035289
| 1:53 | 3.7289 | -0.034992
| 1:53 | 3.7292 | -0.035249
| 1:53 | 3.7294 | -0.035506
| 1:53 | 3.7297 | -0.035765
| 1:53 | 3.73 | -0.036024
| 1:53 | 3.7303 | -0.036283
| 1:53 | 3.7306 | -0.036544
| 1:53 | 3.7308 | -0.036805
| 1:53 | 3.7311 | -0.037067
| 1:53 | 3.7314 | -0.03733
| 1:53 | 3.7317 | -0.037596
| 1:53 | 3.7319 | -0.037864
| 1:53 | 3.7322 | -0.038135
| 1:53 | 3.7325 | -0.038409
| 1:53 | 3.7328 | -0.038685
| 1:53 | 3.7331 | -0.038964
| 1:53 | 3.7333 | -0.039245
| 1:53 | 3.7336 | -0.039528
| 1:53 | 3.7339 | -0.039812
| 1:53 | 3.7342 | -0.040096
| 1:53 | 3.7344 | -0.040383
| 1:53 | 3.7347 | -0.04067
| 1:53 | 3.735 | -0.040959
| 1:53 | 3.7353 | -0.041249
| 1:53 | 3.7356 | -0.04154
| 1:53 | 3.7358 | -0.041833
| 1:53 | 3.7361 | -0.042126
| 1:53 | 3.7364 | -0.042421
| 1:53 | 3.7367 | -0.042717
| 1:53 | 3.7369 | -0.043014
| 1:53 | 3.7372 | -0.043313
| 1:53 | 3.7375 | -0.043613
| 1:53 | 3.7378 | -0.043914
| 1:53 | 3.7381 | -0.044215
| 1:53 | 3.7383 | -0.044517
| 1:53 | 3.7386 | -0.04482
| 1:53 | 3.7389 | -0.045124
| 1:53 | 3.7392 | -0.045428
| 1:53 | 3.7394 | -0.045732
| 1:53 | 3.7397 | -0.046038
| 1:53 | 3.74 | -0.046344
| 1:53 | 3.7403 | -0.04665
| 1:53 | 3.7406 | -0.046958
| 1:53 | 3.7408 | -0.047266
| 1:53 | 3.7411 | -0.047574
| 1:53 | 3.7414 | -0.047884
| 1:53 | 3.7417 | -0.048194
| 1:53 | 3.7419 | -0.048504
| 1:53 | 3.7422 | -0.048815
| 1:53 | 3.7425 | -0.049127
| 1:53 | 3.7428 | -0.04944
| 1:53 | 3.7431 | -0.049754
| 1:53 | 3.7433 | -0.050071
| 1:53 | 3.7436 | -0.05039
| 1:53 | 3.7439 | -0.050711
| 1:53 | 3.7442 | -0.051036
| 1:53 | 3.7444 | -0.051362
| 1:53 | 3.7447 | -0.051691
| 1:54 | 3.745 | -0.052019
| 1:54 | 3.7453 | -0.052345
| 1:54 | 3.7456 | -0.052671
| 1:54 | 3.7458 | -0.052995
| 1:54 | 3.7461 | -0.053318
| 1:54 | 3.7464 | -0.053639
| 1:54 | 3.7467 | -0.05396
| 1:54 | 3.7469 | -0.054279
| 1:54 | 3.7472 | -0.054598
| 1:54 | 3.7475 | -0.054915
| 1:54 | 3.7478 | -0.05523
| 1:54 | 3.7481 | -0.055545
| 1:54 | 3.7483 | -0.055853
| 1:54 | 3.7486 | -0.056155
| 1:54 | 3.7489 | -0.056451
| 1:54 | 3.7492 | -0.056741
| 1:54 | 3.7494 | -0.057028
| 1:54 | 3.7497 | -0.05731
| 1:54 | 3.75 | -0.057589
| 1:54 | 3.7503 | -0.057865
| 1:54 | 3.7506 | -0.05814
| 1:54 | 3.7508 | -0.058413
| 1:54 | 3.7511 | -0.058685
| 1:54 | 3.7514 | -0.058956
| 1:54 | 3.7517 | -0.059226
| 1:54 | 3.7519 | -0.059494
| 1:54 | 3.7522 | -0.059761
| 1:54 | 3.7525 | -0.060027
| 1:54 | 3.7528 | -0.06029
| 1:54 | 3.7531 | -0.060551
| 1:54 | 3.7533 | -0.06081
| 1:54 | 3.7536 | -0.061069
| 1:54 | 3.7539 | -0.061325
| 1:54 | 3.7542 | -0.061581
| 1:54 | 3.7544 | -0.061835
| 1:54 | 3.7547 | -0.062088
| 1:54 | 3.755 | -0.06234
| 1:54 | 3.7553 | -0.062591
| 1:54 | 3.7556 | -0.06284
| 1:54 | 3.7558 | -0.063088
| 1:54 | 3.7561 | -0.063334
| 1:54 | 3.7564 | -0.063579
| 1:54 | 3.7567 | -0.063823
| 1:54 | 3.7569 | -0.064066
| 1:54 | 3.7572 | -0.064309
| 1:54 | 3.7575 | -0.064552
| 1:54 | 3.7578 | -0.064794
| 1:54 | 3.7581 | -0.065036
| 1:54 | 3.7583 | -0.065279
| 1:54 | 3.7586 | -0.065522
| 1:54 | 3.7589 | -0.065765
| 1:54 | 3.7592 | -0.066009
| 1:54 | 3.7594 | -0.066254
| 1:54 | 3.7597 | -0.066498
| 1:54 | 3.76 | -0.066743
| 1:54 | 3.7603 | -0.066989
| 1:54 | 3.7606 | -0.067235
| 1:54 | 3.7608 | -0.067482
| 1:54 | 3.7611 | -0.067728
| 1:54 | 3.7614 | -0.067976
| 1:54 | 3.7617 | -0.068224
| 1:55 | 3.7619 | -0.068472
| 1:55 | 3.7622 | -0.06872
| 1:55 | 3.7625 | -0.06897
| 1:55 | 3.7628 | -0.06922
| 1:55 | 3.7631 | -0.069472
| 1:55 | 3.7633 | -0.069724
| 1:55 | 3.7636 | -0.069978
| 1:55 | 3.7639 | -0.070232
| 1:55 | 3.7642 | -0.070487
| 1:55 | 3.7644 | -0.070743
| 1:55 | 3.7647 | -0.071
| 1:55 | 3.765 | -0.071258
| 1:55 | 3.7653 | -0.071517
| 1:55 | 3.7656 | -0.071777
| 1:55 | 3.7658 | -0.072038
| 1:55 | 3.7661 | -0.0723
| 1:55 | 3.7664 | -0.072563
| 1:55 | 3.7667 | -0.072828
| 1:55 | 3.7669 | -0.073094
| 1:55 | 3.7672 | -0.073361
| 1:55 | 3.7675 | -0.073629
| 1:55 | 3.7678 | -0.073898
| 1:55 | 3.7681 | -0.074168
| 1:55 | 3.7683 | -0.07444
| 1:55 | 3.7686 | -0.074712
| 1:55 | 3.7689 | -0.074986
| 1:55 | 3.7692 | -0.075261
| 1:55 | 3.7694 | -0.075537
| 1:55 | 3.7697 | -0.075815
| 1:55 | 3.77 | -0.076093
| 1:55 | 3.7703 | -0.076373
| 1:55 | 3.7706 | -0.076654
| 1:55 | 3.7708 | -0.076935
| 1:55 | 3.7711 | -0.077218
| 1:55 | 3.7714 | -0.077501
| 1:55 | 3.7717 | -0.077785
| 1:55 | 3.7719 | -0.078069
| 1:55 | 3.7722 | -0.078353
| 1:55 | 3.7725 | -0.078638
| 1:55 | 3.7728 | -0.078924
| 1:55 | 3.7731 | -0.07921
| 1:55 | 3.7733 | -0.079497
| 1:55 | 3.7736 | -0.079784
| 1:55 | 3.7739 | -0.080072
| 1:55 | 3.7742 | -0.080361
| 1:55 | 3.7744 | -0.080651
| 1:55 | 3.7747 | -0.080942
| 1:55 | 3.775 | -0.081233
| 1:55 | 3.7753 | -0.081526
| 1:55 | 3.7756 | -0.081819
| 1:55 | 3.7758 | -0.082112
| 1:55 | 3.7761 | -0.082407
| 1:55 | 3.7764 | -0.082702
| 1:55 | 3.7767 | -0.082999
| 1:55 | 3.7769 | -0.083295
| 1:55 | 3.7772 | -0.08359
| 1:55 | 3.7775 | -0.083887
| 1:55 | 3.7778 | -0.084184
| 1:55 | 3.7781 | -0.084482
| 1:56 | 3.7783 | -0.08478
| 1:56 | 3.7786 | -0.08508
| 1:56 | 3.7789 | -0.08538
| 1:56 | 3.7792 | -0.08568
| 1:56 | 3.7794 | -0.08598
| 1:56 | 3.7797 | -0.086278
| 1:56 | 3.78 | -0.086575
| 1:56 | 3.7803 | -0.086871
| 1:56 | 3.7806 | -0.087166
| 1:56 | 3.7808 | -0.08746
| 1:56 | 3.7811 | -0.087753
| 1:56 | 3.7814 | -0.088045
| 1:56 | 3.7817 | -0.088336
| 1:56 | 3.7819 | -0.088626
| 1:56 | 3.7822 | -0.088915
| 1:56 | 3.7825 | -0.089203
| 1:56 | 3.7828 | -0.089491
| 1:56 | 3.7831 | -0.089778
| 1:56 | 3.7833 | -0.090064
| 1:56 | 3.7836 | -0.090349
| 1:56 | 3.7839 | -0.090633
| 1:56 | 3.7842 | -0.090917
| 1:56 | 3.7844 | -0.0912
| 1:56 | 3.7847 | -0.091482
| 1:56 | 3.785 | -0.091763
| 1:56 | 3.7853 | -0.092043
| 1:56 | 3.7856 | -0.092323
| 1:56 | 3.7858 | -0.092602
| 1:56 | 3.7861 | -0.092878
| 1:56 | 3.7864 | -0.093153
| 1:56 | 3.7867 | -0.093427
| 1:56 | 3.7869 | -0.0937
| 1:56 | 3.7872 | -0.093973
| 1:56 | 3.7875 | -0.094244
| 1:56 | 3.7878 | -0.094515
| 1:56 | 3.7881 | -0.094785
| 1:56 | 3.7883 | -0.095053
| 1:56 | 3.7886 | -0.09532
| 1:56 | 3.7889 | -0.095587
| 1:56 | 3.7892 | -0.095852
| 1:56 | 3.7894 | -0.096116
| 1:56 | 3.7897 | -0.096379
| 1:56 | 3.79 | -0.096641
| 1:56 | 3.7903 | -0.096901
| 1:56 | 3.7906 | -0.097157
| 1:56 | 3.7908 | -0.097409
| 1:56 | 3.7911 | -0.097657
| 1:56 | 3.7914 | -0.097901
| 1:56 | 3.7917 | -0.09814
| 1:56 | 3.7919 | -0.098374
| 1:56 | 3.7922 | -0.098604
| 1:56 | 3.7925 | -0.098831
| 1:56 | 3.7928 | -0.099053
| 1:56 | 3.7931 | -0.099271
| 1:56 | 3.7933 | -0.099486
| 1:56 | 3.7936 | -0.099697
| 1:56 | 3.7939 | -0.099908
| 1:56 | 3.7942 | -0.10012
| 1:56 | 3.7944 | -0.10033
| 1:56 | 3.7947 | -0.10054
| 1:56 | 3.795 | -0.10076
| 1:57 | 3.7953 | -0.10097
| 1:57 | 3.7956 | -0.10118
| 1:57 | 3.7958 | -0.10139
| 1:57 | 3.7961 | -0.1016
| 1:57 | 3.7964 | -0.10182
| 1:57 | 3.7967 | -0.10203
| 1:57 | 3.7969 | -0.10224
| 1:57 | 3.7972 | -0.10246
| 1:57 | 3.7975 | -0.10267
| 1:57 | 3.7978 | -0.10288
| 1:57 | 3.7981 | -0.10309
| 1:57 | 3.7983 | -0.10331
| 1:57 | 3.7986 | -0.10352
| 1:57 | 3.7989 | -0.10373
| 1:57 | 3.7992 | -0.10395
| 1:57 | 3.7994 | -0.10416
| 1:57 | 3.7997 | -0.10438
| 1:57 | 3.8 | -0.10459
| 1:57 | 3.8003 | -0.10481
| 1:57 | 3.8006 | -0.10502
| 1:57 | 3.8008 | -0.10524
| 1:57 | 3.8011 | -0.10545
| 1:57 | 3.8014 | -0.10567
| 1:57 | 3.8017 | -0.10589
| 1:57 | 3.8019 | -0.10611
| 1:57 | 3.8022 | -0.10634
| 1:57 | 3.8025 | -0.10657
| 1:57 | 3.8028 | -0.1068
| 1:57 | 3.8031 | -0.10704
| 1:57 | 3.8033 | -0.10729
| 1:57 | 3.8036 | -0.10753
| 1:57 | 3.8039 | -0.10779
| 1:57 | 3.8042 | -0.10804
| 1:57 | 3.8044 | -0.10829
| 1:57 | 3.8047 | -0.10855
| 1:57 | 3.805 | -0.1088
| 1:57 | 3.8053 | -0.10907
| 1:57 | 3.8056 | -0.10933
| 1:57 | 3.8058 | -0.10959
| 1:57 | 3.8061 | -0.10986
| 1:57 | 3.8064 | -0.11013
| 1:57 | 3.8067 | -0.1104
| 1:57 | 3.8069 | -0.11066
| 1:57 | 3.8072 | -0.11094
| 1:57 | 3.8075 | -0.11121
| 1:57 | 3.8078 | -0.11148
| 1:57 | 3.8081 | -0.11175
| 1:57 | 3.8083 | -0.11202
| 1:57 | 3.8086 | -0.11229
| 1:57 | 3.8089 | -0.11257
| 1:57 | 3.8092 | -0.11284
| 1:57 | 3.8094 | -0.11312
| 1:57 | 3.8097 | -0.11339
| 1:57 | 3.81 | -0.11367
| 1:57 | 3.8103 | -0.11395
| 1:57 | 3.8106 | -0.11423
| 1:57 | 3.8108 | -0.1145
| 1:57 | 3.8111 | -0.11478
| 1:57 | 3.8114 | -0.11506
| 1:58 | 3.8117 | -0.11534
| 1:58 | 3.8119 | -0.11562
| 1:58 | 3.8122 | -0.11589
| 1:58 | 3.8125 | -0.11617
| 1:58 | 3.8128 | -0.11644
| 1:58 | 3.8131 | -0.11671
| 1:58 | 3.8133 | -0.11698
| 1:58 | 3.8136 | -0.11725
| 1:58 | 3.8139 | -0.11751
| 1:58 | 3.8142 | -0.11778
| 1:58 | 3.8144 | -0.11805
| 1:58 | 3.8147 | -0.11831
| 1:58 | 3.815 | -0.11857
| 1:58 | 3.8153 | -0.11884
| 1:58 | 3.8156 | -0.1191
| 1:58 | 3.8158 | -0.11936
| 1:58 | 3.8161 | -0.11962
| 1:58 | 3.8164 | -0.11987
| 1:58 | 3.8167 | -0.12013
| 1:58 | 3.8169 | -0.12038
| 1:58 | 3.8172 | -0.12063
| 1:58 | 3.8175 | -0.12087
| 1:58 | 3.8178 | -0.12112
| 1:58 | 3.8181 | -0.12136
| 1:58 | 3.8183 | -0.1216
| 1:58 | 3.8186 | -0.12184
| 1:58 | 3.8189 | -0.12208
| 1:58 | 3.8192 | -0.12232
| 1:58 | 3.8194 | -0.12255
| 1:58 | 3.8197 | -0.12278
| 1:58 | 3.82 | -0.12301
| 1:58 | 3.8203 | -0.12323
| 1:58 | 3.8206 | -0.12346
| 1:58 | 3.8208 | -0.12368
| 1:58 | 3.8211 | -0.1239
| 1:58 | 3.8214 | -0.12413
| 1:58 | 3.8217 | -0.12435
| 1:58 | 3.8219 | -0.12457
| 1:58 | 3.8222 | -0.12479
| 1:58 | 3.8225 | -0.125
| 1:58 | 3.8228 | -0.12522
| 1:58 | 3.8231 | -0.12544
| 1:58 | 3.8233 | -0.12565
| 1:58 | 3.8236 | -0.12587
| 1:58 | 3.8239 | -0.12609
| 1:58 | 3.8242 | -0.12631
| 1:58 | 3.8244 | -0.12653
| 1:58 | 3.8247 | -0.12675
| 1:58 | 3.825 | -0.12697
| 1:58 | 3.8253 | -0.12719
| 1:58 | 3.8256 | -0.12742
| 1:58 | 3.8258 | -0.12764
| 1:58 | 3.8261 | -0.12787
| 1:58 | 3.8264 | -0.12809
| 1:58 | 3.8267 | -0.12832
| 1:58 | 3.8269 | -0.12855
| 1:58 | 3.8272 | -0.12878
| 1:58 | 3.8275 | -0.12901
| 1:58 | 3.8278 | -0.12925
| 1:58 | 3.8281 | -0.12949
| 1:58 | 3.8283 | -0.12973
| 1:59 | 3.8286 | -0.12998
| 1:59 | 3.8289 | -0.13022
| 1:59 | 3.8292 | -0.13046
| 1:59 | 3.8294 | -0.13071
| 1:59 | 3.8297 | -0.13096
| 1:59 | 3.83 | -0.13121
| 1:59 | 3.8303 | -0.13146
| 1:59 | 3.8306 | -0.13171
| 1:59 | 3.8308 | -0.13197
| 1:59 | 3.8311 | -0.13222
| 1:59 | 3.8314 | -0.13248
| 1:59 | 3.8317 | -0.13275
| 1:59 | 3.8319 | -0.13301
| 1:59 | 3.8322 | -0.13327
| 1:59 | 3.8325 | -0.13355
| 1:59 | 3.8328 | -0.13383
| 1:59 | 3.8331 | -0.13412
| 1:59 | 3.8333 | -0.13441
| 1:59 | 3.8336 | -0.13472
| 1:59 | 3.8339 | -0.13503
| 1:59 | 3.8342 | -0.13535
| 1:59 | 3.8344 | -0.13567
| 1:59 | 3.8347 | -0.13598
| 1:59 | 3.835 | -0.1363
| 1:59 | 3.8353 | -0.13662
| 1:59 | 3.8356 | -0.13695
| 1:59 | 3.8358 | -0.13728
| 1:59 | 3.8361 | -0.13762
| 1:59 | 3.8364 | -0.13796
| 1:59 | 3.8367 | -0.1383
| 1:59 | 3.8369 | -0.13864
| 1:59 | 3.8372 | -0.13899
| 1:59 | 3.8375 | -0.13933
| 1:59 | 3.8378 | -0.13967
| 1:59 | 3.8381 | -0.14
| 1:59 | 3.8383 | -0.14034
| 1:59 | 3.8386 | -0.14067
| 1:59 | 3.8389 | -0.141
| 1:59 | 3.8392 | -0.14133
| 1:59 | 3.8394 | -0.14166
| 1:59 | 3.8397 | -0.14199
| 1:59 | 3.84 | -0.1423
| 1:59 | 3.8403 | -0.1426
| 1:59 | 3.8406 | -0.1429
| 1:59 | 3.8408 | -0.14318
| 1:59 | 3.8411 | -0.14345
| 1:59 | 3.8414 | -0.1437
| 1:59 | 3.8417 | -0.14394
| 1:59 | 3.8419 | -0.14417
| 1:59 | 3.8422 | -0.1444
| 1:59 | 3.8425 | -0.14463
| 1:59 | 3.8428 | -0.14486
| 1:59 | 3.8431 | -0.14509
| 1:59 | 3.8433 | -0.14531
| 1:59 | 3.8436 | -0.14553
| 1:59 | 3.8439 | -0.14575
| 1:59 | 3.8442 | -0.14597
| 1:59 | 3.8444 | -0.14618
| 1:59 | 3.8447 | -0.14639
| 2:00 | 3.845 | -0.14659
| 2:00 | 3.8453 | -0.14679
| 2:00 | 3.8456 | -0.14698
| 2:00 | 3.8458 | -0.14716
| 2:00 | 3.8461 | -0.14734
| 2:00 | 3.8464 | -0.14752
| 2:00 | 3.8467 | -0.1477
| 2:00 | 3.8469 | -0.14786
| 2:00 | 3.8472 | -0.14803
| 2:00 | 3.8475 | -0.14819
| 2:00 | 3.8478 | -0.14835
| 2:00 | 3.8481 | -0.1485
| 2:00 | 3.8483 | -0.14865
| 2:00 | 3.8486 | -0.1488
| 2:00 | 3.8489 | -0.14895
| 2:00 | 3.8492 | -0.1491
| 2:00 | 3.8494 | -0.14924
| 2:00 | 3.8497 | -0.14937
| 2:00 | 3.85 | -0.1495
| 2:00 | 3.8503 | -0.14962
| 2:00 | 3.8506 | -0.14974
| 2:00 | 3.8508 | -0.14985
| 2:00 | 3.8511 | -0.14995
| 2:00 | 3.8514 | -0.15005
| 2:00 | 3.8517 | -0.15014
| 2:00 | 3.8519 | -0.15022
| 2:00 | 3.8522 | -0.15029
| 2:00 | 3.8525 | -0.15035
| 2:00 | 3.8528 | -0.15041
| 2:00 | 3.8531 | -0.15046
| 2:00 | 3.8533 | -0.15051
| 2:00 | 3.8536 | -0.15054
| 2:00 | 3.8539 | -0.15058
| 2:00 | 3.8542 | -0.15061
| 2:00 | 3.8544 | -0.15064
| 2:00 | 3.8547 | -0.15066
| 2:00 | 3.855 | -0.15068
| 2:00 | 3.8553 | -0.15069
| 2:00 | 3.8556 | -0.1507
| 2:00 | 3.8558 | -0.15071
| 2:00 | 3.8561 | -0.15071
| 2:00 | 3.8564 | -0.1507
| 2:00 | 3.8567 | -0.15069
| 2:00 | 3.8569 | -0.15067
| 2:00 | 3.8572 | -0.15064
| 2:00 | 3.8575 | -0.1506
| 2:00 | 3.8578 | -0.15055
| 2:00 | 3.8581 | -0.1505
| 2:00 | 3.8583 | -0.15043
| 2:00 | 3.8586 | -0.15035
| 2:00 | 3.8589 | -0.15025
| 2:00 | 3.8592 | -0.15016
| 2:00 | 3.8594 | -0.15004
| 2:00 | 3.8597 | -0.14992
| 2:00 | 3.86 | -0.14979
| 2:00 | 3.8603 | -0.14966
| 2:00 | 3.8606 | -0.14951
| 2:00 | 3.8608 | -0.14935
| 2:00 | 3.8611 | -0.14918
| 2:00 | 3.8614 | -0.149
| 2:00 | 3.8617 | -0.14882
| 2:01 | 3.8619 | -0.14862
| 2:01 | 3.8622 | -0.14841
| 2:01 | 3.8625 | -0.14819
| 2:01 | 3.8628 | -0.14796
| 2:01 | 3.8631 | -0.14773
| 2:01 | 3.8633 | -0.14748
| 2:01 | 3.8636 | -0.14723
| 2:01 | 3.8639 | -0.14696
| 2:01 | 3.8642 | -0.14669
| 2:01 | 3.8644 | -0.1464
| 2:01 | 3.8647 | -0.14611
| 2:01 | 3.865 | -0.1458
| 2:01 | 3.8653 | -0.14549
| 2:01 | 3.8656 | -0.14516
| 2:01 | 3.8658 | -0.14483
| 2:01 | 3.8661 | -0.14449
| 2:01 | 3.8664 | -0.14414
| 2:01 | 3.8667 | -0.14378
| 2:01 | 3.8669 | -0.14342
| 2:01 | 3.8672 | -0.14304
| 2:01 | 3.8675 | -0.14266
| 2:01 | 3.8678 | -0.14227
| 2:01 | 3.8681 | -0.14187
| 2:01 | 3.8683 | -0.14147
| 2:01 | 3.8686 | -0.14106
| 2:01 | 3.8689 | -0.14064
| 2:01 | 3.8692 | -0.14022
| 2:01 | 3.8694 | -0.13979
| 2:01 | 3.8697 | -0.13936
| 2:01 | 3.87 | -0.13892
| 2:01 | 3.8703 | -0.13849
| 2:01 | 3.8706 | -0.13804
| 2:01 | 3.8708 | -0.13759
| 2:01 | 3.8711 | -0.13714
| 2:01 | 3.8714 | -0.13668
| 2:01 | 3.8717 | -0.13622
| 2:01 | 3.8719 | -0.13576
| 2:01 | 3.8722 | -0.13529
| 2:01 | 3.8725 | -0.13483
| 2:01 | 3.8728 | -0.13436
| 2:01 | 3.8731 | -0.13389
| 2:01 | 3.8733 | -0.13341
| 2:01 | 3.8736 | -0.13294
| 2:01 | 3.8739 | -0.13247
| 2:01 | 3.8742 | -0.13199
| 2:01 | 3.8744 | -0.13151
| 2:01 | 3.8747 | -0.13104
| 2:01 | 3.875 | -0.13057
| 2:01 | 3.8753 | -0.13009
| 2:01 | 3.8756 | -0.12961
| 2:01 | 3.8758 | -0.12913
| 2:01 | 3.8761 | -0.12866
| 2:01 | 3.8764 | -0.12818
| 2:01 | 3.8767 | -0.1277
| 2:01 | 3.8769 | -0.12722
| 2:01 | 3.8772 | -0.12674
| 2:01 | 3.8775 | -0.12626
| 2:01 | 3.8778 | -0.12578
| 2:01 | 3.8781 | -0.1253
| 2:02 | 3.8783 | -0.12482
| 2:02 | 3.8786 | -0.12434
| 2:02 | 3.8789 | -0.12386
| 2:02 | 3.8792 | -0.12337
| 2:02 | 3.8794 | -0.12289
| 2:02 | 3.8797 | -0.12241
| 2:02 | 3.88 | -0.12193
| 2:02 | 3.8803 | -0.12144
| 2:02 | 3.8806 | -0.12096
| 2:02 | 3.8808 | -0.12048
| 2:02 | 3.8811 | -0.12
| 2:02 | 3.8814 | -0.11952
| 2:02 | 3.8817 | -0.11904
| 2:02 | 3.8819 | -0.11856
| 2:02 | 3.8822 | -0.11808
| 2:02 | 3.8825 | -0.1176
| 2:02 | 3.8828 | -0.11712
| 2:02 | 3.8831 | -0.11664
| 2:02 | 3.8833 | -0.11616
| 2:02 | 3.8836 | -0.11568
| 2:02 | 3.8839 | -0.1152
| 2:02 | 3.8842 | -0.11472
| 2:02 | 3.8844 | -0.11425
| 2:02 | 3.8847 | -0.11377
| 2:02 | 3.885 | -0.1133
| 2:02 | 3.8853 | -0.11282
| 2:02 | 3.8856 | -0.11235
| 2:02 | 3.8858 | -0.11188
| 2:02 | 3.8861 | -0.1114
| 2:02 | 3.8864 | -0.11093
| 2:02 | 3.8867 | -0.11046
| 2:02 | 3.8869 | -0.10999
| 2:02 | 3.8872 | -0.10953
| 2:02 | 3.8875 | -0.10906
| 2:02 | 3.8878 | -0.10859
| 2:02 | 3.8881 | -0.10813
| 2:02 | 3.8883 | -0.10767
| 2:02 | 3.8886 | -0.1072
| 2:02 | 3.8889 | -0.10674
| 2:02 | 3.8892 | -0.10628
| 2:02 | 3.8894 | -0.10582
| 2:02 | 3.8897 | -0.10536
| 2:02 | 3.89 | -0.1049
| 2:02 | 3.8903 | -0.10444
| 2:02 | 3.8906 | -0.10399
| 2:02 | 3.8908 | -0.10353
| 2:02 | 3.8911 | -0.10307
| 2:02 | 3.8914 | -0.10262
| 2:02 | 3.8917 | -0.10217
| 2:02 | 3.8919 | -0.10172
| 2:02 | 3.8922 | -0.10127
| 2:02 | 3.8925 | -0.10082
| 2:02 | 3.8928 | -0.10038
| 2:02 | 3.8931 | -0.099943
| 2:02 | 3.8933 | -0.09951
| 2:02 | 3.8936 | -0.099082
| 2:02 | 3.8939 | -0.098662
| 2:02 | 3.8942 | -0.098244
| 2:02 | 3.8944 | -0.097834
| 2:02 | 3.8947 | -0.097435
| 2:02 | 3.895 | -0.097041
| 2:03 | 3.8953 | -0.096651
| 2:03 | 3.8956 | -0.096269
| 2:03 | 3.8958 | -0.095896
| 2:03 | 3.8961 | -0.09553
| 2:03 | 3.8964 | -0.095168
| 2:03 | 3.8967 | -0.094811
| 2:03 | 3.8969 | -0.09446
| 2:03 | 3.8972 | -0.094113
| 2:03 | 3.8975 | -0.093771
| 2:03 | 3.8978 | -0.093434
| 2:03 | 3.8981 | -0.093101
| 2:03 | 3.8983 | -0.092774
| 2:03 | 3.8986 | -0.092448
| 2:03 | 3.8989 | -0.092122
| 2:03 | 3.8992 | -0.091796
| 2:03 | 3.8994 | -0.091469
| 2:03 | 3.8997 | -0.091141
| 2:03 | 3.9 | -0.090811
| 2:03 | 3.9003 | -0.090483
| 2:03 | 3.9006 | -0.090153
| 2:03 | 3.9008 | -0.089825
| 2:03 | 3.9011 | -0.089497
| 2:03 | 3.9014 | -0.08917
| 2:03 | 3.9017 | -0.088845
| 2:03 | 3.9019 | -0.088518
| 2:03 | 3.9022 | -0.088188
| 2:03 | 3.9025 | -0.087861
| 2:03 | 3.9028 | -0.087537
| 2:03 | 3.9031 | -0.087218
| 2:03 | 3.9033 | -0.086898
| 2:03 | 3.9036 | -0.086575
| 2:03 | 3.9039 | -0.086247
| 2:03 | 3.9042 | -0.085916
| 2:03 | 3.9044 | -0.085583
| 2:03 | 3.9047 | -0.085249
| 2:03 | 3.905 | -0.084912
| 2:03 | 3.9053 | -0.084574
| 2:03 | 3.9056 | -0.084233
| 2:03 | 3.9058 | -0.083892
| 2:03 | 3.9061 | -0.083548
| 2:03 | 3.9064 | -0.083204
| 2:03 | 3.9067 | -0.08286
| 2:03 | 3.9069 | -0.082519
| 2:03 | 3.9072 | -0.082185
| 2:03 | 3.9075 | -0.081852
| 2:03 | 3.9078 | -0.081527
| 2:03 | 3.9081 | -0.081207
| 2:03 | 3.9083 | -0.080901
| 2:03 | 3.9086 | -0.0806
| 2:03 | 3.9089 | -0.080306
| 2:03 | 3.9092 | -0.080025
| 2:03 | 3.9094 | -0.079757
| 2:03 | 3.9097 | -0.0795
| 2:03 | 3.91 | -0.079255
| 2:03 | 3.9103 | -0.079019
| 2:03 | 3.9106 | -0.07879
| 2:03 | 3.9108 | -0.078573
| 2:03 | 3.9111 | -0.078365
| 2:03 | 3.9114 | -0.078166
| 2:04 | 3.9117 | -0.077973
| 2:04 | 3.9119 | -0.077784
| 2:04 | 3.9122 | -0.077596
| 2:04 | 3.9125 | -0.077408
| 2:04 | 3.9128 | -0.077221
| 2:04 | 3.9131 | -0.077033
| 2:04 | 3.9133 | -0.076845
| 2:04 | 3.9136 | -0.076658
| 2:04 | 3.9139 | -0.07647
| 2:04 | 3.9142 | -0.076282
| 2:04 | 3.9144 | -0.076095
| 2:04 | 3.9147 | -0.075907
| 2:04 | 3.915 | -0.075719
| 2:04 | 3.9153 | -0.075529
| 2:04 | 3.9156 | -0.075333
| 2:04 | 3.9158 | -0.07513
| 2:04 | 3.9161 | -0.074924
| 2:04 | 3.9164 | -0.074712
| 2:04 | 3.9167 | -0.074493
| 2:04 | 3.9169 | -0.074261
| 2:04 | 3.9172 | -0.074018
| 2:04 | 3.9175 | -0.073762
| 2:04 | 3.9178 | -0.073508
| 2:04 | 3.9181 | -0.073259
| 2:04 | 3.9183 | -0.073016
| 2:04 | 3.9186 | -0.07278
| 2:04 | 3.9189 | -0.072556
| 2:04 | 3.9192 | -0.072343
| 2:04 | 3.9194 | -0.072144
| 2:04 | 3.9197 | -0.07196
| 2:04 | 3.92 | -0.071791
| 2:04 | 3.9203 | -0.071632
| 2:04 | 3.9206 | -0.071476
| 2:04 | 3.9208 | -0.07132
| 2:04 | 3.9211 | -0.071165
| 2:04 | 3.9214 | -0.07101
| 2:04 | 3.9217 | -0.070856
| 2:04 | 3.9219 | -0.070702
| 2:04 | 3.9222 | -0.070549
| 2:04 | 3.9225 | -0.070397
| 2:04 | 3.9228 | -0.070245
| 2:04 | 3.9231 | -0.070094
| 2:04 | 3.9233 | -0.069942
| 2:04 | 3.9236 | -0.069787
| 2:04 | 3.9239 | -0.069632
| 2:04 | 3.9242 | -0.069474
| 2:04 | 3.9244 | -0.069313
| 2:04 | 3.9247 | -0.069143
| 2:04 | 3.925 | -0.068969
| 2:04 | 3.9253 | -0.068788
| 2:04 | 3.9256 | -0.068597
| 2:04 | 3.9258 | -0.068392
| 2:04 | 3.9261 | -0.068179
| 2:04 | 3.9264 | -0.067958
| 2:04 | 3.9267 | -0.067723
| 2:04 | 3.9269 | -0.067475
| 2:04 | 3.9272 | -0.067219
| 2:04 | 3.9275 | -0.066957
| 2:04 | 3.9278 | -0.066692
| 2:04 | 3.9281 | -0.066426
| 2:04 | 3.9283 | -0.06616
| 2:05 | 3.9286 | -0.065892
| 2:05 | 3.9289 | -0.065624
| 2:05 | 3.9292 | -0.065352
| 2:05 | 3.9294 | -0.065073
| 2:05 | 3.9297 | -0.06479
| 2:05 | 3.93 | -0.064501
| 2:05 | 3.9303 | -0.064208
| 2:05 | 3.9306 | -0.063909
| 2:05 | 3.9308 | -0.063606
| 2:05 | 3.9311 | -0.063298
| 2:05 | 3.9314 | -0.062985
| 2:05 | 3.9317 | -0.062668
| 2:05 | 3.9319 | -0.062348
| 2:05 | 3.9322 | -0.062024
| 2:05 | 3.9325 | -0.061697
| 2:05 | 3.9328 | -0.061368
| 2:05 | 3.9331 | -0.061033
| 2:05 | 3.9333 | -0.060695
| 2:05 | 3.9336 | -0.060351
| 2:05 | 3.9339 | -0.060005
| 2:05 | 3.9342 | -0.059658
| 2:05 | 3.9344 | -0.059311
| 2:05 | 3.9347 | -0.058962
| 2:05 | 3.935 | -0.058611
| 2:05 | 3.9353 | -0.058258
| 2:05 | 3.9356 | -0.057904
| 2:05 | 3.9358 | -0.057548
| 2:05 | 3.9361 | -0.05719
| 2:05 | 3.9364 | -0.056831
| 2:05 | 3.9367 | -0.056472
| 2:05 | 3.9369 | -0.056113
| 2:05 | 3.9372 | -0.055754
| 2:05 | 3.9375 | -0.055397
| 2:05 | 3.9378 | -0.055043
| 2:05 | 3.9381 | -0.054693
| 2:05 | 3.9383 | -0.054346
| 2:05 | 3.9386 | -0.054002
| 2:05 | 3.9389 | -0.053661
| 2:05 | 3.9392 | -0.053324
| 2:05 | 3.9394 | -0.05299
| 2:05 | 3.9397 | -0.052657
| 2:05 | 3.94 | -0.052322
| 2:05 | 3.9403 | -0.051986
| 2:05 | 3.9406 | -0.051649
| 2:05 | 3.9408 | -0.05131
| 2:05 | 3.9411 | -0.050972
| 2:05 | 3.9414 | -0.050633
| 2:05 | 3.9417 | -0.05029
| 2:05 | 3.9419 | -0.049945
| 2:05 | 3.9422 | -0.049596
| 2:05 | 3.9425 | -0.04924
| 2:05 | 3.9428 | -0.048878
| 2:05 | 3.9431 | -0.048501
| 2:05 | 3.9433 | -0.048124
| 2:05 | 3.9436 | -0.047747
| 2:05 | 3.9439 | -0.047371
| 2:05 | 3.9442 | -0.046994
| 2:05 | 3.9444 | -0.04662
| 2:05 | 3.9447 | -0.046245
| 2:06 | 3.945 | -0.045871
| 2:06 | 3.9453 | -0.045496
| 2:06 | 3.9456 | -0.045122
| 2:06 | 3.9458 | -0.044748
| 2:06 | 3.9461 | -0.044377
| 2:06 | 3.9464 | -0.044008
| 2:06 | 3.9467 | -0.043642
| 2:06 | 3.9469 | -0.043277
| 2:06 | 3.9472 | -0.042916
| 2:06 | 3.9475 | -0.042556
| 2:06 | 3.9478 | -0.042199
| 2:06 | 3.9481 | -0.041844
| 2:06 | 3.9483 | -0.041489
| 2:06 | 3.9486 | -0.041135
| 2:06 | 3.9489 | -0.040783
| 2:06 | 3.9492 | -0.040431
| 2:06 | 3.9494 | -0.040079
| 2:06 | 3.9497 | -0.039727
| 2:06 | 3.95 | -0.039375
| 2:06 | 3.9503 | -0.039023
| 2:06 | 3.9506 | -0.038671
| 2:06 | 3.9508 | -0.038319
| 2:06 | 3.9511 | -0.03797
| 2:06 | 3.9514 | -0.03762
| 2:06 | 3.9517 | -0.037269
| 2:06 | 3.9519 | -0.036915
| 2:06 | 3.9522 | -0.036562
| 2:06 | 3.9525 | -0.036208
| 2:06 | 3.9528 | -0.035855
| 2:06 | 3.9531 | -0.035502
| 2:06 | 3.9533 | -0.035149
| 2:06 | 3.9536 | -0.034795
| 2:06 | 3.9539 | -0.03444
| 2:06 | 3.9542 | -0.034089
| 2:06 | 3.9544 | -0.033742
| 2:06 | 3.9547 | -0.0334
| 2:06 | 3.955 | -0.033061
| 2:06 | 3.9553 | -0.032727
| 2:06 | 3.9556 | -0.032396
| 2:06 | 3.9558 | -0.03207
| 2:06 | 3.9561 | -0.031747
| 2:06 | 3.9564 | -0.031429
| 2:06 | 3.9567 | -0.031115
| 2:06 | 3.9569 | -0.030805
| 2:06 | 3.9572 | -0.030499
| 2:06 | 3.9575 | -0.030197
| 2:06 | 3.9578 | -0.029902
| 2:06 | 3.9581 | -0.029615
| 2:06 | 3.9583 | -0.029351
| 2:06 | 3.9586 | -0.0291
| 2:06 | 3.9589 | -0.02886
| 2:06 | 3.9592 | -0.028627
| 2:06 | 3.9594 | -0.028401
| 2:06 | 3.9597 | -0.028181
| 2:06 | 3.96 | -0.027966
| 2:06 | 3.9603 | -0.027755
| 2:06 | 3.9606 | -0.027549
| 2:06 | 3.9608 | -0.027343
| 2:06 | 3.9611 | -0.027136
| 2:06 | 3.9614 | -0.026926
| 2:06 | 3.9617 | -0.026714
| 2:07 | 3.9619 | -0.0265
| 2:07 | 3.9622 | -0.026283
| 2:07 | 3.9625 | -0.026067
| 2:07 | 3.9628 | -0.025855
| 2:07 | 3.9631 | -0.025645
| 2:07 | 3.9633 | -0.02544
| 2:07 | 3.9636 | -0.025237
| 2:07 | 3.9639 | -0.025038
| 2:07 | 3.9642 | -0.024843
| 2:07 | 3.9644 | -0.02465
| 2:07 | 3.9647 | -0.024462
| 2:07 | 3.965 | -0.024291
| 2:07 | 3.9653 | -0.024125
| 2:07 | 3.9656 | -0.023965
| 2:07 | 3.9658 | -0.023809
| 2:07 | 3.9661 | -0.02366
| 2:07 | 3.9664 | -0.023517
| 2:07 | 3.9667 | -0.023378
| 2:07 | 3.9669 | -0.023241
| 2:07 | 3.9672 | -0.023105
| 2:07 | 3.9675 | -0.02297
| 2:07 | 3.9678 | -0.022837
| 2:07 | 3.9681 | -0.022707
| 2:07 | 3.9683 | -0.022575
| 2:07 | 3.9686 | -0.022449
| 2:07 | 3.9689 | -0.022333
| 2:07 | 3.9692 | -0.022229
| 2:07 | 3.9694 | -0.022131
| 2:07 | 3.9697 | -0.022032
| 2:07 | 3.97 | -0.021929
| 2:07 | 3.9703 | -0.021825
| 2:07 | 3.9706 | -0.02172
| 2:07 | 3.9708 | -0.021617
| 2:07 | 3.9711 | -0.021512
| 2:07 | 3.9714 | -0.021406
| 2:07 | 3.9717 | -0.021299
| 2:07 | 3.9719 | -0.021191
| 2:07 | 3.9722 | -0.021082
| 2:07 | 3.9725 | -0.020972
| 2:07 | 3.9728 | -0.020861
| 2:07 | 3.9731 | -0.020749
| 2:07 | 3.9733 | -0.020636
| 2:07 | 3.9736 | -0.020522
| 2:07 | 3.9739 | -0.020406
| 2:07 | 3.9742 | -0.020293
| 2:07 | 3.9744 | -0.020185
| 2:07 | 3.9747 | -0.020081
| 2:07 | 3.975 | -0.019983
| 2:07 | 3.9753 | -0.019886
| 2:07 | 3.9756 | -0.019787
| 2:07 | 3.9758 | -0.019687
| 2:07 | 3.9761 | -0.019586
| 2:07 | 3.9764 | -0.019484
| 2:07 | 3.9767 | -0.019379
| 2:07 | 3.9769 | -0.019273
| 2:07 | 3.9772 | -0.019165
| 2:07 | 3.9775 | -0.019056
| 2:07 | 3.9778 | -0.018946
| 2:07 | 3.9781 | -0.018837
| 2:08 | 3.9783 | -0.018728
| 2:08 | 3.9786 | -0.018619
| 2:08 | 3.9789 | -0.018509
| 2:08 | 3.9792 | -0.017847
| 2:08 | 3.9794 | -0.017185
| 2:08 | 3.9797 | -0.016523
| 2:08 | 3.98 | -0.015862
| 2:08 | 3.9803 | -0.015202
| 2:08 | 3.9806 | -0.014542
| 2:08 | 3.9808 | -0.013883
| 2:08 | 3.9811 | -0.013224
| 2:08 | 3.9814 | -0.012566
| 2:08 | 3.9817 | -0.011908
| 2:08 | 3.9819 | -0.01125
| 2:08 | 3.9822 | -0.010592
| 2:08 | 3.9825 | -0.0099348
| 2:08 | 3.9828 | -0.0092794
| 2:08 | 3.9831 | -0.008624
| 2:08 | 3.9833 | -0.0079665
| 2:08 | 3.9836 | -0.007309
| 2:08 | 3.9839 | -0.0066516
| 2:08 | 3.9842 | -0.0059965
| 2:08 | 3.9844 | -0.0053413
| 2:08 | 3.9847 | -0.0046863
| 2:08 | 3.985 | -0.0040312
| 2:08 | 3.9853 | -0.0033762
| 2:08 | 3.9856 | -0.0027213
| 2:08 | 3.9858 | -0.0020664
| 2:08 | 3.9861 | -0.0014138
| 2:08 | 3.9864 | -0.00076116
| 2:08 | 3.9867 | -0.00010859
| 2:08 | 3.9869 | 0.00054394
| 2:08 | 3.9872 | 0.001198
| 2:08 | 3.9875 | 0.0018527
| 2:08 | 3.9878 | 0.002507
| 2:08 | 3.9881 | 0.003161
| 2:08 | 3.9883 | 0.0038147
| 2:08 | 3.9886 | 0.004468
| 2:08 | 3.9889 | 0.005121
| 2:08 | 3.9892 | 0.0057736
| 2:08 | 3.9894 | 0.0064259
| 2:08 | 3.9897 | 0.0070781
| 2:08 | 3.99 | 0.0077301
| 2:08 | 3.9903 | 0.0083822
| 2:08 | 3.9906 | 0.0090342
| 2:08 | 3.9908 | 0.0096861
| 2:08 | 3.9911 | 0.010338
| 2:08 | 3.9914 | 0.01099
| 2:08 | 3.9917 | 0.011642
| 2:08 | 3.9919 | 0.012294
| 2:08 | 3.9922 | 0.012944
| 2:08 | 3.9925 | 0.013594
| 2:08 | 3.9928 | 0.014243
| 2:08 | 3.9931 | 0.014893
| 2:08 | 3.9933 | 0.015542
| 2:08 | 3.9936 | 0.016191
| 2:08 | 3.9939 | 0.016841
| 2:08 | 3.9942 | 0.01749
| 2:08 | 3.9944 | 0.018139
| 2:08 | 3.9947 | 0.018788
| 2:08 | 3.995 | 0.019435
| 2:09 | 3.9953 | 0.020079
| 2:09 | 3.9956 | 0.020724
| 2:09 | 3.9958 | 0.021369
| 2:09 | 3.9961 | 0.022013
| 2:09 | 3.9964 | 0.022657
| 2:09 | 3.9967 | 0.023301
| 2:09 | 3.9969 | 0.023944
| 2:09 | 3.9972 | 0.024587
| 2:09 | 3.9975 | 0.02523
| 2:09 | 3.9978 | 0.025873
| 2:09 | 3.9981 | 0.026515
| 2:09 | 3.9983 | 0.027157
| 2:09 | 3.9986 | 0.027799
| 2:09 | 3.9989 | 0.028441
| 2:09 | 3.9992 | 0.029083
| 2:09 | 3.9994 | 0.029725
| 2:09 | 3.9997 | 0.030366
| 2:09 | 4 | 0.031008
| 2:09 | 4.0003 | 0.03165
| 2:09 | 4.0006 | 0.032292
| 2:09 | 4.0008 | 0.032933
| 2:09 | 4.0011 | 0.033573
| 2:09 | 4.0014 | 0.034212
| 2:09 | 4.0017 | 0.034851
| 2:09 | 4.0019 | 0.035491
| 2:09 | 4.0022 | 0.03613
| 2:09 | 4.0025 | 0.036769
| 2:09 | 4.0028 | 0.037406
| 2:09 | 4.0031 | 0.038041
| 2:09 | 4.0033 | 0.038676
| 2:09 | 4.0036 | 0.039312
| 2:09 | 4.0039 | 0.039947
| 2:09 | 4.0042 | 0.040582
| 2:09 | 4.0044 | 0.041216
| 2:09 | 4.0047 | 0.04185
| 2:09 | 4.005 | 0.042484
| 2:09 | 4.0053 | 0.043117
| 2:09 | 4.0056 | 0.04375
| 2:09 | 4.0058 | 0.044383
| 2:09 | 4.0061 | 0.045015
| 2:09 | 4.0064 | 0.045647
| 2:09 | 4.0067 | 0.046281
| 2:09 | 4.0069 | 0.046913
| 2:09 | 4.0072 | 0.047545
| 2:09 | 4.0075 | 0.048177
| 2:09 | 4.0078 | 0.048807
| 2:09 | 4.0081 | 0.049437
| 2:09 | 4.0083 | 0.050066
| 2:09 | 4.0086 | 0.050696
| 2:09 | 4.0089 | 0.051326
| 2:09 | 4.0092 | 0.051954
| 2:09 | 4.0094 | 0.052582
| 2:09 | 4.0097 | 0.053209
| 2:09 | 4.01 | 0.053836
| 2:09 | 4.0103 | 0.054466
| 2:09 | 4.0106 | 0.055095
| 2:09 | 4.0108 | 0.055722
| 2:09 | 4.0111 | 0.056349
| 2:09 | 4.0114 | 0.056977
| 2:10 | 4.0117 | 0.057606
| 2:10 | 4.0119 | 0.058235
| 2:10 | 4.0122 | 0.058864
| 2:10 | 4.0125 | 0.059493
| 2:10 | 4.0128 | 0.060122
| 2:10 | 4.0131 | 0.060751
| 2:10 | 4.0133 | 0.06138
| 2:10 | 4.0136 | 0.062008
| 2:10 | 4.0139 | 0.062637
| 2:10 | 4.0142 | 0.063264
| 2:10 | 4.0144 | 0.063892
| 2:10 | 4.0147 | 0.064519
| 2:10 | 4.015 | 0.065146
| 2:10 | 4.0153 | 0.065773
| 2:10 | 4.0156 | 0.0664
| 2:10 | 4.0158 | 0.067026
| 2:10 | 4.0161 | 0.067653
| 2:10 | 4.0164 | 0.068279
| 2:10 | 4.0167 | 0.068906
| 2:10 | 4.0169 | 0.069533
| 2:10 | 4.0172 | 0.070159
| 2:10 | 4.0175 | 0.070786
| 2:10 | 4.0178 | 0.07141
| 2:10 | 4.0181 | 0.072032
| 2:10 | 4.0183 | 0.072654
| 2:10 | 4.0186 | 0.073274
| 2:10 | 4.0189 | 0.073888
| 2:10 | 4.0192 | 0.074498
| 2:10 | 4.0194 | 0.075106
| 2:10 | 4.0197 | 0.075713
| 2:10 | 4.02 | 0.076319
| 2:10 | 4.0203 | 0.076926
| 2:10 | 4.0206 | 0.077532
| 2:10 | 4.0208 | 0.078138
| 2:10 | 4.0211 | 0.078745
| 2:10 | 4.0214 | 0.079352
| 2:10 | 4.0217 | 0.07996
| 2:10 | 4.0219 | 0.080569
| 2:10 | 4.0222 | 0.081179
| 2:10 | 4.0225 | 0.081789
| 2:10 | 4.0228 | 0.0824
| 2:10 | 4.0231 | 0.083013
| 2:10 | 4.0233 | 0.083628
| 2:10 | 4.0236 | 0.084247
| 2:10 | 4.0239 | 0.084866
| 2:10 | 4.0242 | 0.085487
| 2:10 | 4.0244 | 0.086108
| 2:10 | 4.0247 | 0.086729
| 2:10 | 4.025 | 0.087351
| 2:10 | 4.0253 | 0.087973
| 2:10 | 4.0256 | 0.088595
| 2:10 | 4.0258 | 0.089218
| 2:10 | 4.0261 | 0.089841
| 2:10 | 4.0264 | 0.090463
| 2:10 | 4.0267 | 0.091084
| 2:10 | 4.0269 | 0.091704
| 2:10 | 4.0272 | 0.092323
| 2:10 | 4.0275 | 0.09294
| 2:10 | 4.0278 | 0.093557
| 2:10 | 4.0281 | 0.094173
| 2:10 | 4.0283 | 0.09479
| 2:11 | 4.0286 | 0.095406
| 2:11 | 4.0289 | 0.096023
| 2:11 | 4.0292 | 0.096639
| 2:11 | 4.0294 | 0.097254
| 2:11 | 4.0297 | 0.097867
| 2:11 | 4.03 | 0.098479
| 2:11 | 4.0303 | 0.09909
| 2:11 | 4.0306 | 0.0997
| 2:11 | 4.0308 | 0.10031
| 2:11 | 4.0311 | 0.10092
| 2:11 | 4.0314 | 0.10152
| 2:11 | 4.0317 | 0.10213
| 2:11 | 4.0319 | 0.10273
| 2:11 | 4.0322 | 0.10333
| 2:11 | 4.0325 | 0.10392
| 2:11 | 4.0328 | 0.10451
| 2:11 | 4.0331 | 0.1051
| 2:11 | 4.0333 | 0.10569
| 2:11 | 4.0336 | 0.10628
| 2:11 | 4.0339 | 0.10687
| 2:11 | 4.0342 | 0.10745
| 2:11 | 4.0344 | 0.10804
| 2:11 | 4.0347 | 0.10862
| 2:11 | 4.035 | 0.10921
| 2:11 | 4.0353 | 0.10979
| 2:11 | 4.0356 | 0.11038
| 2:11 | 4.0358 | 0.11097
| 2:11 | 4.0361 | 0.11155
| 2:11 | 4.0364 | 0.11214
| 2:11 | 4.0367 | 0.11273
| 2:11 | 4.0369 | 0.11332
| 2:11 | 4.0372 | 0.11391
| 2:11 | 4.0375 | 0.1145
| 2:11 | 4.0378 | 0.1151
| 2:11 | 4.0381 | 0.11569
| 2:11 | 4.0383 | 0.11628
| 2:11 | 4.0386 | 0.11687
| 2:11 | 4.0389 | 0.11747
| 2:11 | 4.0392 | 0.11807
| 2:11 | 4.0394 | 0.11866
| 2:11 | 4.0397 | 0.11926
| 2:11 | 4.04 | 0.11986
| 2:11 | 4.0403 | 0.12045
| 2:11 | 4.0406 | 0.12105
| 2:11 | 4.0408 | 0.12166
| 2:11 | 4.0411 | 0.12226
| 2:11 | 4.0414 | 0.12286
| 2:11 | 4.0417 | 0.12346
| 2:11 | 4.0419 | 0.12406
| 2:11 | 4.0422 | 0.12466
| 2:11 | 4.0425 | 0.12527
| 2:11 | 4.0428 | 0.12587
| 2:11 | 4.0431 | 0.12648
| 2:11 | 4.0433 | 0.12708
| 2:11 | 4.0436 | 0.12768
| 2:11 | 4.0439 | 0.12828
| 2:11 | 4.0442 | 0.12889
| 2:11 | 4.0444 | 0.12949
| 2:11 | 4.0447 | 0.13009
| 2:12 | 4.045 | 0.13069
| 2:12 | 4.0453 | 0.13129
| 2:12 | 4.0456 | 0.13189
| 2:12 | 4.0458 | 0.13249
| 2:12 | 4.0461 | 0.13309
| 2:12 | 4.0464 | 0.13369
| 2:12 | 4.0467 | 0.13429
| 2:12 | 4.0469 | 0.1349
| 2:12 | 4.0472 | 0.1355
| 2:12 | 4.0475 | 0.1361
| 2:12 | 4.0478 | 0.13671
| 2:12 | 4.0481 | 0.13731
| 2:12 | 4.0483 | 0.13792
| 2:12 | 4.0486 | 0.13852
| 2:12 | 4.0489 | 0.13913
| 2:12 | 4.0492 | 0.13974
| 2:12 | 4.0494 | 0.14035
| 2:12 | 4.0497 | 0.14096
| 2:12 | 4.05 | 0.14157
| 2:12 | 4.0503 | 0.14218
| 2:12 | 4.0506 | 0.14279
| 2:12 | 4.0508 | 0.14339
| 2:12 | 4.0511 | 0.144
| 2:12 | 4.0514 | 0.14461
| 2:12 | 4.0517 | 0.14522
| 2:12 | 4.0519 | 0.14582
| 2:12 | 4.0522 | 0.14643
| 2:12 | 4.0525 | 0.14704
| 2:12 | 4.0528 | 0.14764
| 2:12 | 4.0531 | 0.14825
| 2:12 | 4.0533 | 0.14886
| 2:12 | 4.0536 | 0.14947
| 2:12 | 4.0539 | 0.15007
| 2:12 | 4.0542 | 0.15068
| 2:12 | 4.0544 | 0.15128
| 2:12 | 4.0547 | 0.15188
| 2:12 | 4.055 | 0.15248
| 2:12 | 4.0553 | 0.15309
| 2:12 | 4.0556 | 0.15369
| 2:12 | 4.0558 | 0.15429
| 2:12 | 4.0561 | 0.1549
| 2:12 | 4.0564 | 0.1555
| 2:12 | 4.0567 | 0.1561
| 2:12 | 4.0569 | 0.1567
| 2:12 | 4.0572 | 0.15731
| 2:12 | 4.0575 | 0.15791
| 2:12 | 4.0578 | 0.15851
| 2:12 | 4.0581 | 0.15911
| 2:12 | 4.0583 | 0.15971
| 2:12 | 4.0586 | 0.16031
| 2:12 | 4.0589 | 0.16091
| 2:12 | 4.0592 | 0.16151
| 2:12 | 4.0594 | 0.16211
| 2:12 | 4.0597 | 0.16271
| 2:12 | 4.06 | 0.16331
| 2:12 | 4.0603 | 0.16391
| 2:12 | 4.0606 | 0.1645
| 2:12 | 4.0608 | 0.1651
| 2:12 | 4.0611 | 0.16569
| 2:12 | 4.0614 | 0.16629
| 2:12 | 4.0617 | 0.16688
| 2:13 | 4.0619 | 0.16748
| 2:13 | 4.0622 | 0.16807
| 2:13 | 4.0625 | 0.16866
| 2:13 | 4.0628 | 0.16924
| 2:13 | 4.0631 | 0.16983
| 2:13 | 4.0633 | 0.17041
| 2:13 | 4.0636 | 0.17099
| 2:13 | 4.0639 | 0.17156
| 2:13 | 4.0642 | 0.17214
| 2:13 | 4.0644 | 0.17271
| 2:13 | 4.0647 | 0.17328
| 2:13 | 4.065 | 0.17384
| 2:13 | 4.0653 | 0.17441
| 2:13 | 4.0656 | 0.17497
| 2:13 | 4.0658 | 0.17553
| 2:13 | 4.0661 | 0.1761
| 2:13 | 4.0664 | 0.17666
| 2:13 | 4.0667 | 0.17722
| 2:13 | 4.0669 | 0.17778
| 2:13 | 4.0672 | 0.17835
| 2:13 | 4.0675 | 0.17891
| 2:13 | 4.0678 | 0.17948
| 2:13 | 4.0681 | 0.18005
| 2:13 | 4.0683 | 0.18063
| 2:13 | 4.0686 | 0.18121
| 2:13 | 4.0689 | 0.18179
| 2:13 | 4.0692 | 0.18237
| 2:13 | 4.0694 | 0.18296
| 2:13 | 4.0697 | 0.18355
| 2:13 | 4.07 | 0.18414
| 2:13 | 4.0703 | 0.18473
| 2:13 | 4.0706 | 0.18532
| 2:13 | 4.0708 | 0.18591
| 2:13 | 4.0711 | 0.1865
| 2:13 | 4.0714 | 0.18709
| 2:13 | 4.0717 | 0.18768
| 2:13 | 4.0719 | 0.18828
| 2:13 | 4.0722 | 0.18887
| 2:13 | 4.0725 | 0.18946
| 2:13 | 4.0728 | 0.19005
| 2:13 | 4.0731 | 0.19064
| 2:13 | 4.0733 | 0.19123
| 2:13 | 4.0736 | 0.19182
| 2:13 | 4.0739 | 0.19241
| 2:13 | 4.0742 | 0.193
| 2:13 | 4.0744 | 0.19359
| 2:13 | 4.0747 | 0.19417
| 2:13 | 4.075 | 0.19476
| 2:13 | 4.0753 | 0.19535
| 2:13 | 4.0756 | 0.19594
| 2:13 | 4.0758 | 0.19653
| 2:13 | 4.0761 | 0.19712
| 2:13 | 4.0764 | 0.19771
| 2:13 | 4.0767 | 0.1983
| 2:13 | 4.0769 | 0.19889
| 2:13 | 4.0772 | 0.19948
| 2:13 | 4.0775 | 0.20006
| 2:13 | 4.0778 | 0.20065
| 2:13 | 4.0781 | 0.20124
| 2:14 | 4.0783 | 0.20183
| 2:14 | 4.0786 | 0.20241
| 2:14 | 4.0789 | 0.203
| 2:14 | 4.0792 | 0.20359
| 2:14 | 4.0794 | 0.20417
| 2:14 | 4.0797 | 0.20476
| 2:14 | 4.08 | 0.20535
| 2:14 | 4.0803 | 0.20594
| 2:14 | 4.0806 | 0.20652
| 2:14 | 4.0808 | 0.20711
| 2:14 | 4.0811 | 0.20769
| 2:14 | 4.0814 | 0.20828
| 2:14 | 4.0817 | 0.20886
| 2:14 | 4.0819 | 0.20945
| 2:14 | 4.0822 | 0.21003
| 2:14 | 4.0825 | 0.21062
| 2:14 | 4.0828 | 0.2112
| 2:14 | 4.0831 | 0.21179
| 2:14 | 4.0833 | 0.21237
| 2:14 | 4.0836 | 0.21295
| 2:14 | 4.0839 | 0.21353
| 2:14 | 4.0842 | 0.21412
| 2:14 | 4.0844 | 0.2147
| 2:14 | 4.0847 | 0.21528
| 2:14 | 4.085 | 0.21585
| 2:14 | 4.0853 | 0.21643
| 2:14 | 4.0856 | 0.21701
| 2:14 | 4.0858 | 0.21759
| 2:14 | 4.0861 | 0.21817
| 2:14 | 4.0864 | 0.21874
| 2:14 | 4.0867 | 0.21932
| 2:14 | 4.0869 | 0.21989
| 2:14 | 4.0872 | 0.22046
| 2:14 | 4.0875 | 0.22104
| 2:14 | 4.0878 | 0.22161
| 2:14 | 4.0881 | 0.22218
| 2:14 | 4.0883 | 0.22275
| 2:14 | 4.0886 | 0.22332
| 2:14 | 4.0889 | 0.22389
| 2:14 | 4.0892 | 0.22445
| 2:14 | 4.0894 | 0.22502
| 2:14 | 4.0897 | 0.22559
| 2:14 | 4.09 | 0.22615
| 2:14 | 4.0903 | 0.22672
| 2:14 | 4.0906 | 0.22728
| 2:14 | 4.0908 | 0.22785
| 2:14 | 4.0911 | 0.22841
| 2:14 | 4.0914 | 0.22897
| 2:14 | 4.0917 | 0.22954
| 2:14 | 4.0919 | 0.2301
| 2:14 | 4.0922 | 0.23066
| 2:14 | 4.0925 | 0.23122
| 2:14 | 4.0928 | 0.23178
| 2:14 | 4.0931 | 0.23235
| 2:14 | 4.0933 | 0.23291
| 2:14 | 4.0936 | 0.23346
| 2:14 | 4.0939 | 0.23402
| 2:14 | 4.0942 | 0.23458
| 2:14 | 4.0944 | 0.23513
| 2:14 | 4.0947 | 0.23569
| 2:14 | 4.095 | 0.23624
| 2:15 | 4.0953 | 0.23679
| 2:15 | 4.0956 | 0.23734
| 2:15 | 4.0958 | 0.23788
| 2:15 | 4.0961 | 0.23843
| 2:15 | 4.0964 | 0.23897
| 2:15 | 4.0967 | 0.2395
| 2:15 | 4.0969 | 0.24003
| 2:15 | 4.0972 | 0.24056
| 2:15 | 4.0975 | 0.24109
| 2:15 | 4.0978 | 0.24161
| 2:15 | 4.0981 | 0.24212
| 2:15 | 4.0983 | 0.24264
| 2:15 | 4.0986 | 0.24315
| 2:15 | 4.0989 | 0.24366
| 2:15 | 4.0992 | 0.24416
| 2:15 | 4.0994 | 0.24466
| 2:15 | 4.0997 | 0.24516
| 2:15 | 4.1 | 0.24565
| 2:15 | 4.1003 | 0.24613
| 2:15 | 4.1006 | 0.24661
| 2:15 | 4.1008 | 0.24708
| 2:15 | 4.1011 | 0.24754
| 2:15 | 4.1014 | 0.248
| 2:15 | 4.1017 | 0.24844
| 2:15 | 4.1019 | 0.24888
| 2:15 | 4.1022 | 0.24931
| 2:15 | 4.1025 | 0.24974
| 2:15 | 4.1028 | 0.25015
| 2:15 | 4.1031 | 0.25056
| 2:15 | 4.1033 | 0.25096
| 2:15 | 4.1036 | 0.25135
| 2:15 | 4.1039 | 0.25174
| 2:15 | 4.1042 | 0.25213
| 2:15 | 4.1044 | 0.25251
| 2:15 | 4.1047 | 0.25288
| 2:15 | 4.105 | 0.25324
| 2:15 | 4.1053 | 0.2536
| 2:15 | 4.1056 | 0.25395
| 2:15 | 4.1058 | 0.25429
| 2:15 | 4.1061 | 0.25462
| 2:15 | 4.1064 | 0.25494
| 2:15 | 4.1067 | 0.25526
| 2:15 | 4.1069 | 0.25557
| 2:15 | 4.1072 | 0.25587
| 2:15 | 4.1075 | 0.25616
| 2:15 | 4.1078 | 0.25644
| 2:15 | 4.1081 | 0.25671
| 2:15 | 4.1083 | 0.25698
| 2:15 | 4.1086 | 0.25723
| 2:15 | 4.1089 | 0.25746
| 2:15 | 4.1092 | 0.2577
| 2:15 | 4.1094 | 0.25792
| 2:15 | 4.1097 | 0.25814
| 2:15 | 4.11 | 0.25835
| 2:15 | 4.1103 | 0.25855
| 2:15 | 4.1106 | 0.25874
| 2:15 | 4.1108 | 0.25892
| 2:15 | 4.1111 | 0.2591
| 2:15 | 4.1114 | 0.25927
| 2:16 | 4.1117 | 0.25943
| 2:16 | 4.1119 | 0.25958
| 2:16 | 4.1122 | 0.25973
| 2:16 | 4.1125 | 0.25987
| 2:16 | 4.1128 | 0.26001
| 2:16 | 4.1131 | 0.26015
| 2:16 | 4.1133 | 0.26027
| 2:16 | 4.1136 | 0.26039
| 2:16 | 4.1139 | 0.2605
| 2:16 | 4.1142 | 0.2606
| 2:16 | 4.1144 | 0.26069
| 2:16 | 4.1147 | 0.26078
| 2:16 | 4.115 | 0.26085
| 2:16 | 4.1153 | 0.26092
| 2:16 | 4.1156 | 0.26099
| 2:16 | 4.1158 | 0.26104
| 2:16 | 4.1161 | 0.26109
| 2:16 | 4.1164 | 0.26113
| 2:16 | 4.1167 | 0.26116
| 2:16 | 4.1169 | 0.26119
| 2:16 | 4.1172 | 0.26121
| 2:16 | 4.1175 | 0.26124
| 2:16 | 4.1178 | 0.26125
| 2:16 | 4.1181 | 0.26126
| 2:16 | 4.1183 | 0.26125
| 2:16 | 4.1186 | 0.26124
| 2:16 | 4.1189 | 0.26121
| 2:16 | 4.1192 | 0.26118
| 2:16 | 4.1194 | 0.26114
| 2:16 | 4.1197 | 0.26108
| 2:16 | 4.12 | 0.26102
| 2:16 | 4.1203 | 0.26094
| 2:16 | 4.1206 | 0.26086
| 2:16 | 4.1208 | 0.26076
| 2:16 | 4.1211 | 0.26065
| 2:16 | 4.1214 | 0.26054
| 2:16 | 4.1217 | 0.26041
| 2:16 | 4.1219 | 0.26028
| 2:16 | 4.1222 | 0.26013
| 2:16 | 4.1225 | 0.25998
| 2:16 | 4.1228 | 0.25982
| 2:16 | 4.1231 | 0.25966
| 2:16 | 4.1233 | 0.25949
| 2:16 | 4.1236 | 0.25932
| 2:16 | 4.1239 | 0.25914
| 2:16 | 4.1242 | 0.25897
| 2:16 | 4.1244 | 0.2588
| 2:16 | 4.1247 | 0.25863
| 2:16 | 4.125 | 0.25847
| 2:16 | 4.1253 | 0.25831
| 2:16 | 4.1256 | 0.25815
| 2:16 | 4.1258 | 0.25799
| 2:16 | 4.1261 | 0.25784
| 2:16 | 4.1264 | 0.25769
| 2:16 | 4.1267 | 0.25754
| 2:16 | 4.1269 | 0.25739
| 2:16 | 4.1272 | 0.25724
| 2:16 | 4.1275 | 0.25708
| 2:16 | 4.1278 | 0.25692
| 2:16 | 4.1281 | 0.25676
| 2:16 | 4.1283 | 0.25659
| 2:17 | 4.1286 | 0.25642
| 2:17 | 4.1289 | 0.25624
| 2:17 | 4.1292 | 0.25606
| 2:17 | 4.1294 | 0.25589
| 2:17 | 4.1297 | 0.25571
| 2:17 | 4.13 | 0.25554
| 2:17 | 4.1303 | 0.25538
| 2:17 | 4.1306 | 0.25522
| 2:17 | 4.1308 | 0.25506
| 2:17 | 4.1311 | 0.25491
| 2:17 | 4.1314 | 0.25476
| 2:17 | 4.1317 | 0.25462
| 2:17 | 4.1319 | 0.25448
| 2:17 | 4.1322 | 0.25435
| 2:17 | 4.1325 | 0.25422
| 2:17 | 4.1328 | 0.25411
| 2:17 | 4.1331 | 0.25401
| 2:17 | 4.1333 | 0.25391
| 2:17 | 4.1336 | 0.25381
| 2:17 | 4.1339 | 0.25372
| 2:17 | 4.1342 | 0.25363
| 2:17 | 4.1344 | 0.25354
| 2:17 | 4.1347 | 0.25344
| 2:17 | 4.135 | 0.25335
| 2:17 | 4.1353 | 0.25325
| 2:17 | 4.1356 | 0.25315
| 2:17 | 4.1358 | 0.25304
| 2:17 | 4.1361 | 0.25293
| 2:17 | 4.1364 | 0.25281
| 2:17 | 4.1367 | 0.25269
| 2:17 | 4.1369 | 0.25256
| 2:17 | 4.1372 | 0.25243
| 2:17 | 4.1375 | 0.25229
| 2:17 | 4.1378 | 0.25215
| 2:17 | 4.1381 | 0.252
| 2:17 | 4.1383 | 0.25184
| 2:17 | 4.1386 | 0.25168
| 2:17 | 4.1389 | 0.25152
| 2:17 | 4.1392 | 0.25135
| 2:17 | 4.1394 | 0.25117
| 2:17 | 4.1397 | 0.25099
| 2:17 | 4.14 | 0.25081
| 2:17 | 4.1403 | 0.25063
| 2:17 | 4.1406 | 0.25045
| 2:17 | 4.1408 | 0.25027
| 2:17 | 4.1411 | 0.25009
| 2:17 | 4.1414 | 0.24992
| 2:17 | 4.1417 | 0.24975
| 2:17 | 4.1419 | 0.24957
| 2:17 | 4.1422 | 0.2494
| 2:17 | 4.1425 | 0.24923
| 2:17 | 4.1428 | 0.24906
| 2:17 | 4.1431 | 0.24889
| 2:17 | 4.1433 | 0.24872
| 2:17 | 4.1436 | 0.24854
| 2:17 | 4.1439 | 0.24838
| 2:17 | 4.1442 | 0.24821
| 2:17 | 4.1444 | 0.24804
| 2:17 | 4.1447 | 0.24788
| 2:18 | 4.145 | 0.24772
| 2:18 | 4.1453 | 0.24756
| 2:18 | 4.1456 | 0.2474
| 2:18 | 4.1458 | 0.24726
| 2:18 | 4.1461 | 0.24711
| 2:18 | 4.1464 | 0.24697
| 2:18 | 4.1467 | 0.24684
| 2:18 | 4.1469 | 0.24671
| 2:18 | 4.1472 | 0.24659
| 2:18 | 4.1475 | 0.24647
| 2:18 | 4.1478 | 0.24636
| 2:18 | 4.1481 | 0.24625
| 2:18 | 4.1483 | 0.24614
| 2:18 | 4.1486 | 0.24603
| 2:18 | 4.1489 | 0.24592
| 2:18 | 4.1492 | 0.24581
| 2:18 | 4.1494 | 0.2457
| 2:18 | 4.1497 | 0.24558
| 2:18 | 4.15 | 0.24546
| 2:18 | 4.1503 | 0.24533
| 2:18 | 4.1506 | 0.2452
| 2:18 | 4.1508 | 0.24507
| 2:18 | 4.1511 | 0.24494
| 2:18 | 4.1514 | 0.24481
| 2:18 | 4.1517 | 0.24467
| 2:18 | 4.1519 | 0.24454
| 2:18 | 4.1522 | 0.2444
| 2:18 | 4.1525 | 0.24426
| 2:18 | 4.1528 | 0.24412
| 2:18 | 4.1531 | 0.24398
| 2:18 | 4.1533 | 0.24383
| 2:18 | 4.1536 | 0.24368
| 2:18 | 4.1539 | 0.24351
| 2:18 | 4.1542 | 0.24334
| 2:18 | 4.1544 | 0.24315
| 2:18 | 4.1547 | 0.24295
| 2:18 | 4.155 | 0.24274
| 2:18 | 4.1553 | 0.24251
| 2:18 | 4.1556 | 0.24228
| 2:18 | 4.1558 | 0.24203
| 2:18 | 4.1561 | 0.24177
| 2:18 | 4.1564 | 0.2415
| 2:18 | 4.1567 | 0.24123
| 2:18 | 4.1569 | 0.24096
| 2:18 | 4.1572 | 0.24069
| 2:18 | 4.1575 | 0.24043
| 2:18 | 4.1578 | 0.24017
| 2:18 | 4.1581 | 0.23992
| 2:18 | 4.1583 | 0.23968
| 2:18 | 4.1586 | 0.23944
| 2:18 | 4.1589 | 0.23921
| 2:18 | 4.1592 | 0.23899
| 2:18 | 4.1594 | 0.23877
| 2:18 | 4.1597 | 0.23855
| 2:18 | 4.16 | 0.23835
| 2:18 | 4.1603 | 0.23814
| 2:18 | 4.1606 | 0.23793
| 2:18 | 4.1608 | 0.23773
| 2:18 | 4.1611 | 0.23753
| 2:18 | 4.1614 | 0.23733
| 2:18 | 4.1617 | 0.23713
| 2:19 | 4.1619 | 0.23693
| 2:19 | 4.1622 | 0.23672
| 2:19 | 4.1625 | 0.23652
| 2:19 | 4.1628 | 0.23631
| 2:19 | 4.1631 | 0.2361
| 2:19 | 4.1633 | 0.23589
| 2:19 | 4.1636 | 0.23568
| 2:19 | 4.1639 | 0.23546
| 2:19 | 4.1642 | 0.23525
| 2:19 | 4.1644 | 0.23503
| 2:19 | 4.1647 | 0.23482
| 2:19 | 4.165 | 0.2346
| 2:19 | 4.1653 | 0.23438
| 2:19 | 4.1656 | 0.23416
| 2:19 | 4.1658 | 0.23393
| 2:19 | 4.1661 | 0.23371
| 2:19 | 4.1664 | 0.23347
| 2:19 | 4.1667 | 0.23323
| 2:19 | 4.1669 | 0.23298
| 2:19 | 4.1672 | 0.23272
| 2:19 | 4.1675 | 0.23244
| 2:19 | 4.1678 | 0.23215
| 2:19 | 4.1681 | 0.23186
| 2:19 | 4.1683 | 0.23156
| 2:19 | 4.1686 | 0.23126
| 2:19 | 4.1689 | 0.23096
| 2:19 | 4.1692 | 0.23066
| 2:19 | 4.1694 | 0.23036
| 2:19 | 4.1697 | 0.23008
| 2:19 | 4.17 | 0.2298
| 2:19 | 4.1703 | 0.22954
| 2:19 | 4.1706 | 0.22928
| 2:19 | 4.1708 | 0.22902
| 2:19 | 4.1711 | 0.22877
| 2:19 | 4.1714 | 0.22852
| 2:19 | 4.1717 | 0.22826
| 2:19 | 4.1719 | 0.228
| 2:19 | 4.1722 | 0.22774
| 2:19 | 4.1725 | 0.22748
| 2:19 | 4.1728 | 0.22722
| 2:19 | 4.1731 | 0.22695
| 2:19 | 4.1733 | 0.22668
| 2:19 | 4.1736 | 0.2264
| 2:19 | 4.1739 | 0.22611
| 2:19 | 4.1742 | 0.22583
| 2:19 | 4.1744 | 0.22554
| 2:19 | 4.1747 | 0.22524
| 2:19 | 4.175 | 0.22494
| 2:19 | 4.1753 | 0.22463
| 2:19 | 4.1756 | 0.22431
| 2:19 | 4.1758 | 0.22399
| 2:19 | 4.1761 | 0.22367
| 2:19 | 4.1764 | 0.22335
| 2:19 | 4.1767 | 0.22302
| 2:19 | 4.1769 | 0.22269
| 2:19 | 4.1772 | 0.22235
| 2:19 | 4.1775 | 0.22202
| 2:19 | 4.1778 | 0.22168
| 2:19 | 4.1781 | 0.22134
| 2:20 | 4.1783 | 0.22101
| 2:20 | 4.1786 | 0.22067
| 2:20 | 4.1789 | 0.22033
| 2:20 | 4.1792 | 0.22
| 2:20 | 4.1794 | 0.21966
| 2:20 | 4.1797 | 0.21932
| 2:20 | 4.18 | 0.21898
| 2:20 | 4.1803 | 0.21864
| 2:20 | 4.1806 | 0.2183
| 2:20 | 4.1808 | 0.21796
| 2:20 | 4.1811 | 0.21762
| 2:20 | 4.1814 | 0.21728
| 2:20 | 4.1817 | 0.21694
| 2:20 | 4.1819 | 0.2166
| 2:20 | 4.1822 | 0.21626
| 2:20 | 4.1825 | 0.21591
| 2:20 | 4.1828 | 0.21557
| 2:20 | 4.1831 | 0.21523
| 2:20 | 4.1833 | 0.21488
| 2:20 | 4.1836 | 0.21454
| 2:20 | 4.1839 | 0.2142
| 2:20 | 4.1842 | 0.21386
| 2:20 | 4.1844 | 0.21353
| 2:20 | 4.1847 | 0.21319
| 2:20 | 4.185 | 0.21286
| 2:20 | 4.1853 | 0.21254
| 2:20 | 4.1856 | 0.21222
| 2:20 | 4.1858 | 0.2119
| 2:20 | 4.1861 | 0.21159
| 2:20 | 4.1864 | 0.21129
| 2:20 | 4.1867 | 0.21099
| 2:20 | 4.1869 | 0.21069
| 2:20 | 4.1872 | 0.2104
| 2:20 | 4.1875 | 0.21011
| 2:20 | 4.1878 | 0.20982
| 2:20 | 4.1881 | 0.20953
| 2:20 | 4.1883 | 0.20924
| 2:20 | 4.1886 | 0.20896
| 2:20 | 4.1889 | 0.20867
| 2:20 | 4.1892 | 0.20838
| 2:20 | 4.1894 | 0.20809
| 2:20 | 4.1897 | 0.2078
| 2:20 | 4.19 | 0.20749
| 2:20 | 4.1903 | 0.20719
| 2:20 | 4.1906 | 0.20687
| 2:20 | 4.1908 | 0.20655
| 2:20 | 4.1911 | 0.20623
| 2:20 | 4.1914 | 0.20591
| 2:20 | 4.1917 | 0.20557
| 2:20 | 4.1919 | 0.20523
| 2:20 | 4.1922 | 0.20488
| 2:20 | 4.1925 | 0.20452
| 2:20 | 4.1928 | 0.20416
| 2:20 | 4.1931 | 0.2038
| 2:20 | 4.1933 | 0.20342
| 2:20 | 4.1936 | 0.20304
| 2:20 | 4.1939 | 0.20266
| 2:20 | 4.1942 | 0.20227
| 2:20 | 4.1944 | 0.20187
| 2:20 | 4.1947 | 0.20148
| 2:20 | 4.195 | 0.20107
| 2:21 | 4.1953 | 0.20066
| 2:21 | 4.1956 | 0.20025
| 2:21 | 4.1958 | 0.19983
| 2:21 | 4.1961 | 0.19941
| 2:21 | 4.1964 | 0.19899
| 2:21 | 4.1967 | 0.19856
| 2:21 | 4.1969 | 0.19814
| 2:21 | 4.1972 | 0.19771
| 2:21 | 4.1975 | 0.19728
| 2:21 | 4.1978 | 0.19685
| 2:21 | 4.1981 | 0.19642
| 2:21 | 4.1983 | 0.19598
| 2:21 | 4.1986 | 0.19554
| 2:21 | 4.1989 | 0.1951
| 2:21 | 4.1992 | 0.19467
| 2:21 | 4.1994 | 0.19422
| 2:21 | 4.1997 | 0.19378
| 2:21 | 4.2 | 0.19334
| 2:21 | 4.2003 | 0.19289
| 2:21 | 4.2006 | 0.19245
| 2:21 | 4.2008 | 0.192
| 2:21 | 4.2011 | 0.19156
| 2:21 | 4.2014 | 0.19111
| 2:21 | 4.2017 | 0.19066
| 2:21 | 4.2019 | 0.1902
| 2:21 | 4.2022 | 0.18974
| 2:21 | 4.2025 | 0.18928
| 2:21 | 4.2028 | 0.18882
| 2:21 | 4.2031 | 0.18835
| 2:21 | 4.2033 | 0.18788
| 2:21 | 4.2036 | 0.18741
| 2:21 | 4.2039 | 0.18693
| 2:21 | 4.2042 | 0.18645
| 2:21 | 4.2044 | 0.18597
| 2:21 | 4.2047 | 0.18549
| 2:21 | 4.205 | 0.185
| 2:21 | 4.2053 | 0.18452
| 2:21 | 4.2056 | 0.18402
| 2:21 | 4.2058 | 0.18353
| 2:21 | 4.2061 | 0.18303
| 2:21 | 4.2064 | 0.18254
| 2:21 | 4.2067 | 0.18204
| 2:21 | 4.2069 | 0.18154
| 2:21 | 4.2072 | 0.18103
| 2:21 | 4.2075 | 0.18052
| 2:21 | 4.2078 | 0.18001
| 2:21 | 4.2081 | 0.1795
| 2:21 | 4.2083 | 0.17899
| 2:21 | 4.2086 | 0.17847
| 2:21 | 4.2089 | 0.17796
| 2:21 | 4.2092 | 0.17744
| 2:21 | 4.2094 | 0.17692
| 2:21 | 4.2097 | 0.17641
| 2:21 | 4.21 | 0.17589
| 2:21 | 4.2103 | 0.17537
| 2:21 | 4.2106 | 0.17485
| 2:21 | 4.2108 | 0.17434
| 2:21 | 4.2111 | 0.17382
| 2:21 | 4.2114 | 0.1733
| 2:22 | 4.2117 | 0.17279
| 2:22 | 4.2119 | 0.17227
| 2:22 | 4.2122 | 0.17175
| 2:22 | 4.2125 | 0.17124
| 2:22 | 4.2128 | 0.17072
| 2:22 | 4.2131 | 0.1702
| 2:22 | 4.2133 | 0.16969
| 2:22 | 4.2136 | 0.16917
| 2:22 | 4.2139 | 0.16866
| 2:22 | 4.2142 | 0.16814
| 2:22 | 4.2144 | 0.16763
| 2:22 | 4.2147 | 0.16711
| 2:22 | 4.215 | 0.1666
| 2:22 | 4.2153 | 0.16608
| 2:22 | 4.2156 | 0.16557
| 2:22 | 4.2158 | 0.16506
| 2:22 | 4.2161 | 0.16456
| 2:22 | 4.2164 | 0.16406
| 2:22 | 4.2167 | 0.16356
| 2:22 | 4.2169 | 0.16306
| 2:22 | 4.2172 | 0.16257
| 2:22 | 4.2175 | 0.16208
| 2:22 | 4.2178 | 0.16159
| 2:22 | 4.2181 | 0.16111
| 2:22 | 4.2183 | 0.16062
| 2:22 | 4.2186 | 0.16014
| 2:22 | 4.2189 | 0.15966
| 2:22 | 4.2192 | 0.15919
| 2:22 | 4.2194 | 0.15873
| 2:22 | 4.2197 | 0.15827
| 2:22 | 4.22 | 0.15781
| 2:22 | 4.2203 | 0.15737
| 2:22 | 4.2206 | 0.15692
| 2:22 | 4.2208 | 0.15648
| 2:22 | 4.2211 | 0.15605
| 2:22 | 4.2214 | 0.15561
| 2:22 | 4.2217 | 0.15518
| 2:22 | 4.2219 | 0.15474
| 2:22 | 4.2222 | 0.1543
| 2:22 | 4.2225 | 0.15386
| 2:22 | 4.2228 | 0.15342
| 2:22 | 4.2231 | 0.15297
| 2:22 | 4.2233 | 0.15253
| 2:22 | 4.2236 | 0.15208
| 2:22 | 4.2239 | 0.15163
| 2:22 | 4.2242 | 0.15118
| 2:22 | 4.2244 | 0.15073
| 2:22 | 4.2247 | 0.15028
| 2:22 | 4.225 | 0.14983
| 2:22 | 4.2253 | 0.14938
| 2:22 | 4.2256 | 0.14893
| 2:22 | 4.2258 | 0.14847
| 2:22 | 4.2261 | 0.14802
| 2:22 | 4.2264 | 0.14757
| 2:22 | 4.2267 | 0.14712
| 2:22 | 4.2269 | 0.14668
| 2:22 | 4.2272 | 0.14623
| 2:22 | 4.2275 | 0.14579
| 2:22 | 4.2278 | 0.14535
| 2:22 | 4.2281 | 0.14491
| 2:22 | 4.2283 | 0.14447
| 2:23 | 4.2286 | 0.14402
| 2:23 | 4.2289 | 0.14357
| 2:23 | 4.2292 | 0.14312
| 2:23 | 4.2294 | 0.14266
| 2:23 | 4.2297 | 0.1422
| 2:23 | 4.23 | 0.14173
| 2:23 | 4.2303 | 0.14126
| 2:23 | 4.2306 | 0.14079
| 2:23 | 4.2308 | 0.14031
| 2:23 | 4.2311 | 0.13983
| 2:23 | 4.2314 | 0.13935
| 2:23 | 4.2317 | 0.13886
| 2:23 | 4.2319 | 0.13837
| 2:23 | 4.2322 | 0.13787
| 2:23 | 4.2325 | 0.13737
| 2:23 | 4.2328 | 0.13686
| 2:23 | 4.2331 | 0.13635
| 2:23 | 4.2333 | 0.13583
| 2:23 | 4.2336 | 0.13531
| 2:23 | 4.2339 | 0.13479
| 2:23 | 4.2342 | 0.13426
| 2:23 | 4.2344 | 0.13374
| 2:23 | 4.2347 | 0.13321
| 2:23 | 4.235 | 0.13269
| 2:23 | 4.2353 | 0.13216
| 2:23 | 4.2356 | 0.13163
| 2:23 | 4.2358 | 0.1311
| 2:23 | 4.2361 | 0.13057
| 2:23 | 4.2364 | 0.13004
| 2:23 | 4.2367 | 0.12951
| 2:23 | 4.2369 | 0.12897
| 2:23 | 4.2372 | 0.12844
| 2:23 | 4.2375 | 0.12792
| 2:23 | 4.2378 | 0.12739
| 2:23 | 4.2381 | 0.12686
| 2:23 | 4.2383 | 0.12633
| 2:23 | 4.2386 | 0.12581
| 2:23 | 4.2389 | 0.12529
| 2:23 | 4.2392 | 0.12476
| 2:23 | 4.2394 | 0.12424
| 2:23 | 4.2397 | 0.12372
| 2:23 | 4.24 | 0.1232
| 2:23 | 4.2403 | 0.12269
| 2:23 | 4.2406 | 0.12218
| 2:23 | 4.2408 | 0.12167
| 2:23 | 4.2411 | 0.12118
| 2:23 | 4.2414 | 0.12069
| 2:23 | 4.2417 | 0.12022
| 2:23 | 4.2419 | 0.11976
| 2:23 | 4.2422 | 0.11931
| 2:23 | 4.2425 | 0.11887
| 2:23 | 4.2428 | 0.11843
| 2:23 | 4.2431 | 0.11799
| 2:23 | 4.2433 | 0.11754
| 2:23 | 4.2436 | 0.1171
| 2:23 | 4.2439 | 0.11664
| 2:23 | 4.2442 | 0.11618
| 2:23 | 4.2444 | 0.11572
| 2:23 | 4.2447 | 0.11525
| 2:24 | 4.245 | 0.11477
| 2:24 | 4.2453 | 0.1143
| 2:24 | 4.2456 | 0.11382
| 2:24 | 4.2458 | 0.11334
| 2:24 | 4.2461 | 0.11285
| 2:24 | 4.2464 | 0.11236
| 2:24 | 4.2467 | 0.11187
| 2:24 | 4.2469 | 0.11138
| 2:24 | 4.2472 | 0.11088
| 2:24 | 4.2475 | 0.11038
| 2:24 | 4.2478 | 0.10988
| 2:24 | 4.2481 | 0.10937
| 2:24 | 4.2483 | 0.10886
| 2:24 | 4.2486 | 0.10835
| 2:24 | 4.2489 | 0.10784
| 2:24 | 4.2492 | 0.10733
| 2:24 | 4.2494 | 0.10682
| 2:24 | 4.2497 | 0.10631
| 2:24 | 4.25 | 0.1058
| 2:24 | 4.2503 | 0.10529
| 2:24 | 4.2506 | 0.10479
| 2:24 | 4.2508 | 0.10428
| 2:24 | 4.2511 | 0.10378
| 2:24 | 4.2514 | 0.10328
| 2:24 | 4.2517 | 0.10278
| 2:24 | 4.2519 | 0.10227
| 2:24 | 4.2522 | 0.10177
| 2:24 | 4.2525 | 0.10127
| 2:24 | 4.2528 | 0.10077
| 2:24 | 4.2531 | 0.10027
| 2:24 | 4.2533 | 0.099763
| 2:24 | 4.2536 | 0.099257
| 2:24 | 4.2539 | 0.098753
| 2:24 | 4.2542 | 0.098252
| 2:24 | 4.2544 | 0.097756
| 2:24 | 4.2547 | 0.097268
| 2:24 | 4.255 | 0.096787
| 2:24 | 4.2553 | 0.096314
| 2:24 | 4.2556 | 0.095848
| 2:24 | 4.2558 | 0.095389
| 2:24 | 4.2561 | 0.094938
| 2:24 | 4.2564 | 0.094492
| 2:24 | 4.2567 | 0.094061
| 2:24 | 4.2569 | 0.093656
| 2:24 | 4.2572 | 0.093268
| 2:24 | 4.2575 | 0.092898
| 2:24 | 4.2578 | 0.092564
| 2:24 | 4.2581 | 0.092236
| 2:24 | 4.2583 | 0.091941
| 2:24 | 4.2586 | 0.091668
| 2:24 | 4.2589 | 0.091422
| 2:24 | 4.2592 | 0.091207
| 2:24 | 4.2594 | 0.091026
| 2:24 | 4.2597 | 0.090858
| 2:24 | 4.26 | 0.090713
| 2:24 | 4.2603 | 0.090584
| 2:24 | 4.2606 | 0.090477
| 2:24 | 4.2608 | 0.090388
| 2:24 | 4.2611 | 0.09032
| 2:24 | 4.2614 | 0.090275
| 2:24 | 4.2617 | 0.090239
| 2:25 | 4.2619 | 0.090216
| 2:25 | 4.2622 | 0.090209
| 2:25 | 4.2625 | 0.090214
| 2:25 | 4.2628 | 0.090219
| 2:25 | 4.2631 | 0.090222
| 2:25 | 4.2633 | 0.090224
| 2:25 | 4.2636 | 0.090225
| 2:25 | 4.2639 | 0.090224
| 2:25 | 4.2642 | 0.090223
| 2:25 | 4.2644 | 0.09022
| 2:25 | 4.2647 | 0.090216
| 2:25 | 4.265 | 0.090212
| 2:25 | 4.2653 | 0.090207
| 2:25 | 4.2656 | 0.090205
| 2:25 | 4.2658 | 0.090213
| 2:25 | 4.2661 | 0.090225
| 2:25 | 4.2664 | 0.090243
| 2:25 | 4.2667 | 0.090263
| 2:25 | 4.2669 | 0.090291
| 2:25 | 4.2672 | 0.090316
| 2:25 | 4.2675 | 0.090337
| 2:25 | 4.2678 | 0.09036
| 2:25 | 4.2681 | 0.090378
| 2:25 | 4.2683 | 0.09039
| 2:25 | 4.2686 | 0.090383
| 2:25 | 4.2689 | 0.090356
| 2:25 | 4.2692 | 0.090324
| 2:25 | 4.2694 | 0.09028
| 2:25 | 4.2697 | 0.090214
| 2:25 | 4.27 | 0.090137
| 2:25 | 4.2703 | 0.090053
| 2:25 | 4.2706 | 0.089945
| 2:25 | 4.2708 | 0.089837
| 2:25 | 4.2711 | 0.089727
| 2:25 | 4.2714 | 0.089615
| 2:25 | 4.2717 | 0.089502
| 2:25 | 4.2719 | 0.089386
| 2:25 | 4.2722 | 0.089269
| 2:25 | 4.2725 | 0.089149
| 2:25 | 4.2728 | 0.089028
| 2:25 | 4.2731 | 0.088905
| 2:25 | 4.2733 | 0.088783
| 2:25 | 4.2736 | 0.088661
| 2:25 | 4.2739 | 0.088547
| 2:25 | 4.2742 | 0.088435
| 2:25 | 4.2744 | 0.088332
| 2:25 | 4.2747 | 0.088234
| 2:25 | 4.275 | 0.088139
| 2:25 | 4.2753 | 0.088041
| 2:25 | 4.2756 | 0.087939
| 2:25 | 4.2758 | 0.087828
| 2:25 | 4.2761 | 0.087713
| 2:25 | 4.2764 | 0.087596
| 2:25 | 4.2767 | 0.087475
| 2:25 | 4.2769 | 0.087354
| 2:25 | 4.2772 | 0.087233
| 2:25 | 4.2775 | 0.087116
| 2:25 | 4.2778 | 0.087001
| 2:25 | 4.2781 | 0.086886
| 2:26 | 4.2783 | 0.086772
| 2:26 | 4.2786 | 0.086656
| 2:26 | 4.2789 | 0.086539
| 2:26 | 4.2792 | 0.086423
| 2:26 | 4.2794 | 0.086308
| 2:26 | 4.2797 | 0.086202
| 2:26 | 4.28 | 0.086104
| 2:26 | 4.2803 | 0.086014
| 2:26 | 4.2806 | 0.085932
| 2:26 | 4.2808 | 0.085858
| 2:26 | 4.2811 | 0.085792
| 2:26 | 4.2814 | 0.085733
| 2:26 | 4.2817 | 0.085683
| 2:26 | 4.2819 | 0.085644
| 2:26 | 4.2822 | 0.085633
| 2:26 | 4.2825 | 0.085663
| 2:26 | 4.2828 | 0.085715
| 2:26 | 4.2831 | 0.085783
| 2:26 | 4.2833 | 0.085878
| 2:26 | 4.2836 | 0.085985
| 2:26 | 4.2839 | 0.086116
| 2:26 | 4.2842 | 0.086252
| 2:26 | 4.2844 | 0.086399
| 2:26 | 4.2847 | 0.08655
| 2:26 | 4.285 | 0.086705
| 2:26 | 4.2853 | 0.086861
| 2:26 | 4.2856 | 0.087016
| 2:26 | 4.2858 | 0.087175
| 2:26 | 4.2861 | 0.087333
| 2:26 | 4.2864 | 0.087488
| 2:26 | 4.2867 | 0.087645
| 2:26 | 4.2869 | 0.087805
| 2:26 | 4.2872 | 0.087966
| 2:26 | 4.2875 | 0.088129
| 2:26 | 4.2878 | 0.088295
| 2:26 | 4.2881 | 0.088463
| 2:26 | 4.2883 | 0.088635
| 2:26 | 4.2886 | 0.088809
| 2:26 | 4.2889 | 0.088986
| 2:26 | 4.2892 | 0.089165
| 2:26 | 4.2894 | 0.089347
| 2:26 | 4.2897 | 0.089532
| 2:26 | 4.29 | 0.089716
| 2:26 | 4.2903 | 0.089899
| 2:26 | 4.2906 | 0.090078
| 2:26 | 4.2908 | 0.090254
| 2:26 | 4.2911 | 0.090426
| 2:26 | 4.2914 | 0.090595
| 2:26 | 4.2917 | 0.090756
| 2:26 | 4.2919 | 0.090913
| 2:26 | 4.2922 | 0.091066
| 2:26 | 4.2925 | 0.091214
| 2:26 | 4.2928 | 0.091357
| 2:26 | 4.2931 | 0.091498
| 2:26 | 4.2933 | 0.091637
| 2:26 | 4.2936 | 0.091776
| 2:26 | 4.2939 | 0.091916
| 2:26 | 4.2942 | 0.092056
| 2:26 | 4.2944 | 0.092198
| 2:26 | 4.2947 | 0.092342
| 2:26 | 4.295 | 0.09249
| 2:27 | 4.2953 | 0.09264
| 2:27 | 4.2956 | 0.092795
| 2:27 | 4.2958 | 0.092954
| 2:27 | 4.2961 | 0.093118
| 2:27 | 4.2964 | 0.093282
| 2:27 | 4.2967 | 0.093447
| 2:27 | 4.2969 | 0.093611
| 2:27 | 4.2972 | 0.093776
| 2:27 | 4.2975 | 0.093942
| 2:27 | 4.2978 | 0.094107
| 2:27 | 4.2981 | 0.094273
| 2:27 | 4.2983 | 0.094439
| 2:27 | 4.2986 | 0.094602
| 2:27 | 4.2989 | 0.094764
| 2:27 | 4.2992 | 0.094926
| 2:27 | 4.2994 | 0.095088
| 2:27 | 4.2997 | 0.09525
| 2:27 | 4.3 | 0.095412
| 2:27 | 4.3003 | 0.095576
| 2:27 | 4.3006 | 0.095738
| 2:27 | 4.3008 | 0.0959
| 2:27 | 4.3011 | 0.096063
| 2:27 | 4.3014 | 0.096227
| 2:27 | 4.3017 | 0.096389
| 2:27 | 4.3019 | 0.096551
| 2:27 | 4.3022 | 0.096712
| 2:27 | 4.3025 | 0.096872
| 2:27 | 4.3028 | 0.097031
| 2:27 | 4.3031 | 0.09719
| 2:27 | 4.3033 | 0.097348
| 2:27 | 4.3036 | 0.097506
| 2:27 | 4.3039 | 0.097661
| 2:27 | 4.3042 | 0.097819
| 2:27 | 4.3044 | 0.097975
| 2:27 | 4.3047 | 0.09813
| 2:27 | 4.305 | 0.098282
| 2:27 | 4.3053 | 0.098433
| 2:27 | 4.3056 | 0.098582
| 2:27 | 4.3058 | 0.09873
| 2:27 | 4.3061 | 0.098875
| 2:27 | 4.3064 | 0.09902
| 2:27 | 4.3067 | 0.099161
| 2:27 | 4.3069 | 0.099301
| 2:27 | 4.3072 | 0.099441
| 2:27 | 4.3075 | 0.09958
| 2:27 | 4.3078 | 0.09972
| 2:27 | 4.3081 | 0.099858
| 2:27 | 4.3083 | 0.099994
| 2:27 | 4.3086 | 0.10013
| 2:27 | 4.3089 | 0.10026
| 2:27 | 4.3092 | 0.1004
| 2:27 | 4.3094 | 0.10053
| 2:27 | 4.3097 | 0.10066
| 2:27 | 4.31 | 0.10079
| 2:27 | 4.3103 | 0.10092
| 2:27 | 4.3106 | 0.10105
| 2:27 | 4.3108 | 0.10118
| 2:27 | 4.3111 | 0.10132
| 2:27 | 4.3114 | 0.10145
| 2:28 | 4.3117 | 0.10158
| 2:28 | 4.3119 | 0.10171
| 2:28 | 4.3122 | 0.10185
| 2:28 | 4.3125 | 0.10198
| 2:28 | 4.3128 | 0.10212
| 2:28 | 4.3131 | 0.10226
| 2:28 | 4.3133 | 0.10241
| 2:28 | 4.3136 | 0.10255
| 2:28 | 4.3139 | 0.1027
| 2:28 | 4.3142 | 0.10285
| 2:28 | 4.3144 | 0.103
| 2:28 | 4.3147 | 0.10316
| 2:28 | 4.315 | 0.10331
| 2:28 | 4.3153 | 0.10347
| 2:28 | 4.3156 | 0.10363
| 2:28 | 4.3158 | 0.10379
| 2:28 | 4.3161 | 0.10395
| 2:28 | 4.3164 | 0.10411
| 2:28 | 4.3167 | 0.10427
| 2:28 | 4.3169 | 0.10442
| 2:28 | 4.3172 | 0.10458
| 2:28 | 4.3175 | 0.10474
| 2:28 | 4.3178 | 0.10489
| 2:28 | 4.3181 | 0.10504
| 2:28 | 4.3183 | 0.10519
| 2:28 | 4.3186 | 0.10533
| 2:28 | 4.3189 | 0.10548
| 2:28 | 4.3192 | 0.10562
| 2:28 | 4.3194 | 0.10575
| 2:28 | 4.3197 | 0.10589
| 2:28 | 4.32 | 0.10602
| 2:28 | 4.3203 | 0.10616
| 2:28 | 4.3206 | 0.10629
| 2:28 | 4.3208 | 0.10643
| 2:28 | 4.3211 | 0.10657
| 2:28 | 4.3214 | 0.10671
| 2:28 | 4.3217 | 0.10685
| 2:28 | 4.3219 | 0.10699
| 2:28 | 4.3222 | 0.10713
| 2:28 | 4.3225 | 0.10728
| 2:28 | 4.3228 | 0.10742
| 2:28 | 4.3231 | 0.10757
| 2:28 | 4.3233 | 0.10771
| 2:28 | 4.3236 | 0.10786
| 2:28 | 4.3239 | 0.10801
| 2:28 | 4.3242 | 0.10816
| 2:28 | 4.3244 | 0.10832
| 2:28 | 4.3247 | 0.10848
| 2:28 | 4.325 | 0.10864
| 2:28 | 4.3253 | 0.10881
| 2:28 | 4.3256 | 0.10897
| 2:28 | 4.3258 | 0.10914
| 2:28 | 4.3261 | 0.10931
| 2:28 | 4.3264 | 0.10948
| 2:28 | 4.3267 | 0.10965
| 2:28 | 4.3269 | 0.10982
| 2:28 | 4.3272 | 0.10999
| 2:28 | 4.3275 | 0.11016
| 2:28 | 4.3278 | 0.11034
| 2:28 | 4.3281 | 0.11052
| 2:28 | 4.3283 | 0.1107
| 2:29 | 4.3286 | 0.11089
| 2:29 | 4.3289 | 0.11107
| 2:29 | 4.3292 | 0.11125
| 2:29 | 4.3294 | 0.11144
| 2:29 | 4.3297 | 0.11163
| 2:29 | 4.33 | 0.11181
| 2:29 | 4.3303 | 0.112
| 2:29 | 4.3306 | 0.11219
| 2:29 | 4.3308 | 0.11238
| 2:29 | 4.3311 | 0.11256
| 2:29 | 4.3314 | 0.11275
| 2:29 | 4.3317 | 0.11294
| 2:29 | 4.3319 | 0.11313
| 2:29 | 4.3322 | 0.11332
| 2:29 | 4.3325 | 0.11351
| 2:29 | 4.3328 | 0.1137
| 2:29 | 4.3331 | 0.11389
| 2:29 | 4.3333 | 0.11408
| 2:29 | 4.3336 | 0.11427
| 2:29 | 4.3339 | 0.11446
| 2:29 | 4.3342 | 0.11465
| 2:29 | 4.3344 | 0.11484
| 2:29 | 4.3347 | 0.11503
| 2:29 | 4.335 | 0.11522
| 2:29 | 4.3353 | 0.11541
| 2:29 | 4.3356 | 0.1156
| 2:29 | 4.3358 | 0.11579
| 2:29 | 4.3361 | 0.11598
| 2:29 | 4.3364 | 0.11617
| 2:29 | 4.3367 | 0.11636
| 2:29 | 4.3369 | 0.11654
| 2:29 | 4.3372 | 0.11673
| 2:29 | 4.3375 | 0.11691
| 2:29 | 4.3378 | 0.11708
| 2:29 | 4.3381 | 0.11725
| 2:29 | 4.3383 | 0.11741
| 2:29 | 4.3386 | 0.11757
| 2:29 | 4.3389 | 0.11772
| 2:29 | 4.3392 | 0.11786
| 2:29 | 4.3394 | 0.11799
| 2:29 | 4.3397 | 0.11811
| 2:29 | 4.34 | 0.11822
| 2:29 | 4.3403 | 0.1183
| 2:29 | 4.3406 | 0.11838
| 2:29 | 4.3408 | 0.11845
| 2:29 | 4.3411 | 0.11852
| 2:29 | 4.3414 | 0.11857
| 2:29 | 4.3417 | 0.1186
| 2:29 | 4.3419 | 0.11862
| 2:29 | 4.3422 | 0.11863
| 2:29 | 4.3425 | 0.11862
| 2:29 | 4.3428 | 0.1186
| 2:29 | 4.3431 | 0.11858
| 2:29 | 4.3433 | 0.11854
| 2:29 | 4.3436 | 0.11848
| 2:29 | 4.3439 | 0.11842
| 2:29 | 4.3442 | 0.11834
| 2:29 | 4.3444 | 0.11826
| 2:29 | 4.3447 | 0.11815
| 2:30 | 4.345 | 0.11805
| 2:30 | 4.3453 | 0.11792
| 2:30 | 4.3456 | 0.11778
| 2:30 | 4.3458 | 0.11764
| 2:30 | 4.3461 | 0.11748
| 2:30 | 4.3464 | 0.1173
| 2:30 | 4.3467 | 0.11712
| 2:30 | 4.3469 | 0.11692
| 2:30 | 4.3472 | 0.11672
| 2:30 | 4.3475 | 0.1165
| 2:30 | 4.3478 | 0.11627
| 2:30 | 4.3481 | 0.11602
| 2:30 | 4.3483 | 0.11577
| 2:30 | 4.3486 | 0.1155
| 2:30 | 4.3489 | 0.11524
| 2:30 | 4.3492 | 0.11496
| 2:30 | 4.3494 | 0.11467
| 2:30 | 4.3497 | 0.11437
| 2:30 | 4.35 | 0.11406
| 2:30 | 4.3503 | 0.11375
| 2:30 | 4.3506 | 0.11342
| 2:30 | 4.3508 | 0.11309
| 2:30 | 4.3511 | 0.11274
| 2:30 | 4.3514 | 0.11239
| 2:30 | 4.3517 | 0.11203
| 2:30 | 4.3519 | 0.11167
| 2:30 | 4.3522 | 0.11129
| 2:30 | 4.3525 | 0.11092
| 2:30 | 4.3528 | 0.11054
| 2:30 | 4.3531 | 0.11016
| 2:30 | 4.3533 | 0.10977
| 2:30 | 4.3536 | 0.10938
| 2:30 | 4.3539 | 0.10898
| 2:30 | 4.3542 | 0.10858
| 2:30 | 4.3544 | 0.10818
| 2:30 | 4.3547 | 0.10778
| 2:30 | 4.355 | 0.10737
| 2:30 | 4.3553 | 0.10697
| 2:30 | 4.3556 | 0.10656
| 2:30 | 4.3558 | 0.10615
| 2:30 | 4.3561 | 0.10573
| 2:30 | 4.3564 | 0.10532
| 2:30 | 4.3567 | 0.10491
| 2:30 | 4.3569 | 0.1045
| 2:30 | 4.3572 | 0.10408
| 2:30 | 4.3575 | 0.10367
| 2:30 | 4.3578 | 0.10326
| 2:30 | 4.3581 | 0.10285
| 2:30 | 4.3583 | 0.10244
| 2:30 | 4.3586 | 0.10202
| 2:30 | 4.3589 | 0.10161
| 2:30 | 4.3592 | 0.10119
| 2:30 | 4.3594 | 0.10078
| 2:30 | 4.3597 | 0.10036
| 2:30 | 4.36 | 0.099949
| 2:30 | 4.3603 | 0.099534
| 2:30 | 4.3606 | 0.099117
| 2:30 | 4.3608 | 0.0987
| 2:30 | 4.3611 | 0.098282
| 2:30 | 4.3614 | 0.097865
| 2:30 | 4.3617 | 0.097447
| 2:31 | 4.3619 | 0.097027
| 2:31 | 4.3622 | 0.096605
| 2:31 | 4.3625 | 0.096178
| 2:31 | 4.3628 | 0.095752
| 2:31 | 4.3631 | 0.095326
| 2:31 | 4.3633 | 0.0949
| 2:31 | 4.3636 | 0.094474
| 2:31 | 4.3639 | 0.094048
| 2:31 | 4.3642 | 0.093623
| 2:31 | 4.3644 | 0.093198
| 2:31 | 4.3647 | 0.092772
| 2:31 | 4.365 | 0.092348
| 2:31 | 4.3653 | 0.091925
| 2:31 | 4.3656 | 0.091502
| 2:31 | 4.3658 | 0.091081
| 2:31 | 4.3661 | 0.090663
| 2:31 | 4.3664 | 0.090244
| 2:31 | 4.3667 | 0.089826
| 2:31 | 4.3669 | 0.089403
| 2:31 | 4.3672 | 0.088978
| 2:31 | 4.3675 | 0.088551
| 2:31 | 4.3678 | 0.088123
| 2:31 | 4.3681 | 0.087696
| 2:31 | 4.3683 | 0.087272
| 2:31 | 4.3686 | 0.086853
| 2:31 | 4.3689 | 0.086441
| 2:31 | 4.3692 | 0.086034
| 2:31 | 4.3694 | 0.085632
| 2:31 | 4.3697 | 0.085236
| 2:31 | 4.37 | 0.084848
| 2:31 | 4.3703 | 0.084466
| 2:31 | 4.3706 | 0.084091
| 2:31 | 4.3708 | 0.083725
| 2:31 | 4.3711 | 0.083365
| 2:31 | 4.3714 | 0.083011
| 2:31 | 4.3717 | 0.082664
| 2:31 | 4.3719 | 0.082323
| 2:31 | 4.3722 | 0.081989
| 2:31 | 4.3725 | 0.081661
| 2:31 | 4.3728 | 0.081339
| 2:31 | 4.3731 | 0.081021
| 2:31 | 4.3733 | 0.080705
| 2:31 | 4.3736 | 0.08039
| 2:31 | 4.3739 | 0.080075
| 2:31 | 4.3742 | 0.079758
| 2:31 | 4.3744 | 0.07944
| 2:31 | 4.3747 | 0.079118
| 2:31 | 4.375 | 0.078796
| 2:31 | 4.3753 | 0.078467
| 2:31 | 4.3756 | 0.078132
| 2:31 | 4.3758 | 0.077792
| 2:31 | 4.3761 | 0.077448
| 2:31 | 4.3764 | 0.077103
| 2:31 | 4.3767 | 0.076755
| 2:31 | 4.3769 | 0.076404
| 2:31 | 4.3772 | 0.076054
| 2:31 | 4.3775 | 0.075711
| 2:31 | 4.3778 | 0.075372
| 2:31 | 4.3781 | 0.075036
| 2:32 | 4.3783 | 0.074704
| 2:32 | 4.3786 | 0.074372
| 2:32 | 4.3789 | 0.074042
| 2:32 | 4.3792 | 0.073713
| 2:32 | 4.3794 | 0.073384
| 2:32 | 4.3797 | 0.073051
| 2:32 | 4.38 | 0.072714
| 2:32 | 4.3803 | 0.072372
| 2:32 | 4.3806 | 0.072026
| 2:32 | 4.3808 | 0.071676
| 2:32 | 4.3811 | 0.071322
| 2:32 | 4.3814 | 0.070964
| 2:32 | 4.3817 | 0.070601
| 2:32 | 4.3819 | 0.070233
| 2:32 | 4.3822 | 0.069855
| 2:32 | 4.3825 | 0.069466
| 2:32 | 4.3828 | 0.069069
| 2:32 | 4.3831 | 0.068664
| 2:32 | 4.3833 | 0.068254
| 2:32 | 4.3836 | 0.067842
| 2:32 | 4.3839 | 0.067426
| 2:32 | 4.3842 | 0.067008
| 2:32 | 4.3844 | 0.066591
| 2:32 | 4.3847 | 0.066177
| 2:32 | 4.385 | 0.065764
| 2:32 | 4.3853 | 0.065354
| 2:32 | 4.3856 | 0.064945
| 2:32 | 4.3858 | 0.064541
| 2:32 | 4.3861 | 0.06414
| 2:32 | 4.3864 | 0.063746
| 2:32 | 4.3867 | 0.063357
| 2:32 | 4.3869 | 0.062973
| 2:32 | 4.3872 | 0.062594
| 2:32 | 4.3875 | 0.062219
| 2:32 | 4.3878 | 0.06185
| 2:32 | 4.3881 | 0.061487
| 2:32 | 4.3883 | 0.061129
| 2:32 | 4.3886 | 0.060778
| 2:32 | 4.3889 | 0.060433
| 2:32 | 4.3892 | 0.060093
| 2:32 | 4.3894 | 0.059759
| 2:32 | 4.3897 | 0.059426
| 2:32 | 4.39 | 0.059094
| 2:32 | 4.3903 | 0.058761
| 2:32 | 4.3906 | 0.058427
| 2:32 | 4.3908 | 0.058092
| 2:32 | 4.3911 | 0.057756
| 2:32 | 4.3914 | 0.057421
| 2:32 | 4.3917 | 0.057086
| 2:32 | 4.3919 | 0.056751
| 2:32 | 4.3922 | 0.056416
| 2:32 | 4.3925 | 0.056083
| 2:32 | 4.3928 | 0.055754
| 2:32 | 4.3931 | 0.055432
| 2:32 | 4.3933 | 0.055114
| 2:32 | 4.3936 | 0.054797
| 2:32 | 4.3939 | 0.054484
| 2:32 | 4.3942 | 0.054174
| 2:32 | 4.3944 | 0.05387
| 2:32 | 4.3947 | 0.053569
| 2:32 | 4.395 | 0.053272
| 2:33 | 4.3953 | 0.05298
| 2:33 | 4.3956 | 0.052692
| 2:33 | 4.3958 | 0.052405
| 2:33 | 4.3961 | 0.052118
| 2:33 | 4.3964 | 0.051831
| 2:33 | 4.3967 | 0.051543
| 2:33 | 4.3969 | 0.051256
| 2:33 | 4.3972 | 0.050968
| 2:33 | 4.3975 | 0.050679
| 2:33 | 4.3978 | 0.050391
| 2:33 | 4.3981 | 0.050102
| 2:33 | 4.3983 | 0.049813
| 2:33 | 4.3986 | 0.049524
| 2:33 | 4.3989 | 0.049238
| 2:33 | 4.3992 | 0.048953
| 2:33 | 4.3994 | 0.048673
| 2:33 | 4.3997 | 0.048394
| 2:33 | 4.4 | 0.048116
| 2:33 | 4.4003 | 0.04784
| 2:33 | 4.4006 | 0.047564
| 2:33 | 4.4008 | 0.047288
| 2:33 | 4.4011 | 0.047011
| 2:33 | 4.4014 | 0.046737
| 2:33 | 4.4017 | 0.046462
| 2:33 | 4.4019 | 0.046184
| 2:33 | 4.4022 | 0.045904
| 2:33 | 4.4025 | 0.045621
| 2:33 | 4.4028 | 0.045338
| 2:33 | 4.4031 | 0.045055
| 2:33 | 4.4033 | 0.044774
| 2:33 | 4.4036 | 0.044495
| 2:33 | 4.4039 | 0.044227
| 2:33 | 4.4042 | 0.043965
| 2:33 | 4.4044 | 0.043714
| 2:33 | 4.4047 | 0.043475
| 2:33 | 4.405 | 0.043247
| 2:33 | 4.4053 | 0.043031
| 2:33 | 4.4056 | 0.042826
| 2:33 | 4.4058 | 0.042633
| 2:33 | 4.4061 | 0.042452
| 2:33 | 4.4064 | 0.042278
| 2:33 | 4.4067 | 0.042113
| 2:33 | 4.4069 | 0.04195
| 2:33 | 4.4072 | 0.041788
| 2:33 | 4.4075 | 0.041627
| 2:33 | 4.4078 | 0.041469
| 2:33 | 4.4081 | 0.041311
| 2:33 | 4.4083 | 0.041155
| 2:33 | 4.4086 | 0.041
| 2:33 | 4.4089 | 0.040849
| 2:33 | 4.4092 | 0.040703
| 2:33 | 4.4094 | 0.040561
| 2:33 | 4.4097 | 0.040424
| 2:33 | 4.41 | 0.040289
| 2:33 | 4.4103 | 0.040161
| 2:33 | 4.4106 | 0.040036
| 2:33 | 4.4108 | 0.039916
| 2:33 | 4.4111 | 0.0398
| 2:33 | 4.4114 | 0.039687
| 2:34 | 4.4117 | 0.03958
| 2:34 | 4.4119 | 0.039475
| 2:34 | 4.4122 | 0.039374
| 2:34 | 4.4125 | 0.039275
| 2:34 | 4.4128 | 0.039179
| 2:34 | 4.4131 | 0.039084
| 2:34 | 4.4133 | 0.038991
| 2:34 | 4.4136 | 0.038898
| 2:34 | 4.4139 | 0.038806
| 2:34 | 4.4142 | 0.038715
| 2:34 | 4.4144 | 0.038625
| 2:34 | 4.4147 | 0.038537
| 2:34 | 4.415 | 0.038448
| 2:34 | 4.4153 | 0.03836
| 2:34 | 4.4156 | 0.038269
| 2:34 | 4.4158 | 0.038177
| 2:34 | 4.4161 | 0.038083
| 2:34 | 4.4164 | 0.037988
| 2:34 | 4.4167 | 0.037895
| 2:34 | 4.4169 | 0.037802
| 2:34 | 4.4172 | 0.037712
| 2:34 | 4.4175 | 0.037623
| 2:34 | 4.4178 | 0.037535
| 2:34 | 4.4181 | 0.037448
| 2:34 | 4.4183 | 0.037363
| 2:34 | 4.4186 | 0.037275
| 2:34 | 4.4189 | 0.037185
| 2:34 | 4.4192 | 0.03709
| 2:34 | 4.4194 | 0.036986
| 2:34 | 4.4197 | 0.036874
| 2:34 | 4.42 | 0.036757
| 2:34 | 4.4203 | 0.036629
| 2:34 | 4.4206 | 0.036496
| 2:34 | 4.4208 | 0.036356
| 2:34 | 4.4211 | 0.036217
| 2:34 | 4.4214 | 0.036081
| 2:34 | 4.4217 | 0.03595
| 2:34 | 4.4219 | 0.035822
| 2:34 | 4.4222 | 0.035699
| 2:34 | 4.4225 | 0.03558
| 2:34 | 4.4228 | 0.035465
| 2:34 | 4.4231 | 0.035355
| 2:34 | 4.4233 | 0.035255
| 2:34 | 4.4236 | 0.03516
| 2:34 | 4.4239 | 0.035068
| 2:34 | 4.4242 | 0.034979
| 2:34 | 4.4244 | 0.034893
| 2:34 | 4.4247 | 0.034811
| 2:34 | 4.425 | 0.03473
| 2:34 | 4.4253 | 0.034653
| 2:34 | 4.4256 | 0.034578
| 2:34 | 4.4258 | 0.034505
| 2:34 | 4.4261 | 0.03443
| 2:34 | 4.4264 | 0.034356
| 2:34 | 4.4267 | 0.034281
| 2:34 | 4.4269 | 0.034204
| 2:34 | 4.4272 | 0.034127
| 2:34 | 4.4275 | 0.034048
| 2:34 | 4.4278 | 0.033973
| 2:34 | 4.4281 | 0.033898
| 2:34 | 4.4283 | 0.033821
| 2:35 | 4.4286 | 0.033743
| 2:35 | 4.4289 | 0.033661
| 2:35 | 4.4292 | 0.033577
| 2:35 | 4.4294 | 0.033492
| 2:35 | 4.4297 | 0.033406
| 2:35 | 4.43 | 0.033319
| 2:35 | 4.4303 | 0.033231
| 2:35 | 4.4306 | 0.033142
| 2:35 | 4.4308 | 0.033052
| 2:35 | 4.4311 | 0.032961
| 2:35 | 4.4314 | 0.032869
| 2:35 | 4.4317 | 0.032775
| 2:35 | 4.4319 | 0.032681
| 2:35 | 4.4322 | 0.032579
| 2:35 | 4.4325 | 0.032476
| 2:35 | 4.4328 | 0.032372
| 2:35 | 4.4331 | 0.032264
| 2:35 | 4.4333 | 0.032151
| 2:35 | 4.4336 | 0.032036
| 2:35 | 4.4339 | 0.031915
| 2:35 | 4.4342 | 0.031793
| 2:35 | 4.4344 | 0.031667
| 2:35 | 4.4347 | 0.031536
| 2:35 | 4.435 | 0.031397
| 2:35 | 4.4353 | 0.031258
| 2:35 | 4.4356 | 0.031108
| 2:35 | 4.4358 | 0.030957
| 2:35 | 4.4361 | 0.030794
| 2:35 | 4.4364 | 0.030626
| 2:35 | 4.4367 | 0.030456
| 2:35 | 4.4369 | 0.030279
| 2:35 | 4.4372 | 0.030097
| 2:35 | 4.4375 | 0.029912
| 2:35 | 4.4378 | 0.029723
| 2:35 | 4.4381 | 0.029534
| 2:35 | 4.4383 | 0.029344
| 2:35 | 4.4386 | 0.029153
| 2:35 | 4.4389 | 0.02896
| 2:35 | 4.4392 | 0.028768
| 2:35 | 4.4394 | 0.028574
| 2:35 | 4.4397 | 0.028385
| 2:35 | 4.44 | 0.028204
| 2:35 | 4.4403 | 0.028026
| 2:35 | 4.4406 | 0.027854
| 2:35 | 4.4408 | 0.027687
| 2:35 | 4.4411 | 0.027521
| 2:35 | 4.4414 | 0.027359
| 2:35 | 4.4417 | 0.027209
| 2:35 | 4.4419 | 0.027063
| 2:35 | 4.4422 | 0.02692
| 2:35 | 4.4425 | 0.026784
| 2:35 | 4.4428 | 0.026653
| 2:35 | 4.4431 | 0.026529
| 2:35 | 4.4433 | 0.02641
| 2:35 | 4.4436 | 0.026296
| 2:35 | 4.4439 | 0.026186
| 2:35 | 4.4442 | 0.026081
| 2:35 | 4.4444 | 0.025982
| 2:35 | 4.4447 | 0.025887
| 2:36 | 4.445 | 0.0258
| 2:36 | 4.4453 | 0.025715
| 2:36 | 4.4456 | 0.025633
| 2:36 | 4.4458 | 0.025556
| 2:36 | 4.4461 | 0.025481
| 2:36 | 4.4464 | 0.025408
| 2:36 | 4.4467 | 0.025337
| 2:36 | 4.4469 | 0.025268
| 2:36 | 4.4472 | 0.025201
| 2:36 | 4.4475 | 0.025136
| 2:36 | 4.4478 | 0.025073
| 2:36 | 4.4481 | 0.025013
| 2:36 | 4.4483 | 0.024955
| 2:36 | 4.4486 | 0.024897
| 2:36 | 4.4489 | 0.024841
| 2:36 | 4.4492 | 0.024788
| 2:36 | 4.4494 | 0.024737
| 2:36 | 4.4497 | 0.024685
| 2:36 | 4.45 | 0.024635
| 2:36 | 4.4503 | 0.024588
| 2:36 | 4.4506 | 0.024541
| 2:36 | 4.4508 | 0.024495
| 2:36 | 4.4511 | 0.024451
| 2:36 | 4.4514 | 0.024408
| 2:36 | 4.4517 | 0.024367
| 2:36 | 4.4519 | 0.02433
| 2:36 | 4.4522 | 0.024291
| 2:36 | 4.4525 | 0.024255
| 2:36 | 4.4528 | 0.024222
| 2:36 | 4.4531 | 0.024194
| 2:36 | 4.4533 | 0.024169
| 2:36 | 4.4536 | 0.024146
| 2:36 | 4.4539 | 0.024123
| 2:36 | 4.4542 | 0.024104
| 2:36 | 4.4544 | 0.024088
| 2:36 | 4.4547 | 0.024075
| 2:36 | 4.455 | 0.024064
| 2:36 | 4.4553 | 0.024056
| 2:36 | 4.4556 | 0.02405
| 2:36 | 4.4558 | 0.024047
| 2:36 | 4.4561 | 0.024047
| 2:36 | 4.4564 | 0.024048
| 2:36 | 4.4567 | 0.024051
| 2:36 | 4.4569 | 0.024055
| 2:36 | 4.4572 | 0.024068
| 2:36 | 4.4575 | 0.02408
| 2:36 | 4.4578 | 0.024093
| 2:36 | 4.4581 | 0.024111
| 2:36 | 4.4583 | 0.024129
| 2:36 | 4.4586 | 0.024148
| 2:36 | 4.4589 | 0.024169
| 2:36 | 4.4592 | 0.024192
| 2:36 | 4.4594 | 0.024215
| 2:36 | 4.4597 | 0.024238
| 2:36 | 4.46 | 0.024261
| 2:36 | 4.4603 | 0.024284
| 2:36 | 4.4606 | 0.024307
| 2:36 | 4.4608 | 0.02433
| 2:36 | 4.4611 | 0.024354
| 2:36 | 4.4614 | 0.024379
| 2:36 | 4.4617 | 0.024404
| 2:37 | 4.4619 | 0.024431
| 2:37 | 4.4622 | 0.024458
| 2:37 | 4.4625 | 0.024486
| 2:37 | 4.4628 | 0.024515
| 2:37 | 4.4631 | 0.024545
| 2:37 | 4.4633 | 0.024577
| 2:37 | 4.4636 | 0.02461
| 2:37 | 4.4639 | 0.024644
| 2:37 | 4.4642 | 0.024679
| 2:37 | 4.4644 | 0.024716
| 2:37 | 4.4647 | 0.024754
| 2:37 | 4.465 | 0.024793
| 2:37 | 4.4653 | 0.024835
| 2:37 | 4.4656 | 0.024879
| 2:37 | 4.4658 | 0.024924
| 2:37 | 4.4661 | 0.024968
| 2:37 | 4.4664 | 0.02501
| 2:37 | 4.4667 | 0.025048
| 2:37 | 4.4669 | 0.025079
| 2:37 | 4.4672 | 0.025107
| 2:37 | 4.4675 | 0.025132
| 2:37 | 4.4678 | 0.025154
| 2:37 | 4.4681 | 0.025174
| 2:37 | 4.4683 | 0.025193
| 2:37 | 4.4686 | 0.025208
| 2:37 | 4.4689 | 0.025216
| 2:37 | 4.4692 | 0.02522
| 2:37 | 4.4694 | 0.025216
| 2:37 | 4.4697 | 0.025209
| 2:37 | 4.47 | 0.025194
| 2:37 | 4.4703 | 0.025172
| 2:37 | 4.4706 | 0.025146
| 2:37 | 4.4708 | 0.025113
| 2:37 | 4.4711 | 0.025075
| 2:37 | 4.4714 | 0.025038
| 2:37 | 4.4717 | 0.025002
| 2:37 | 4.4719 | 0.024965
| 2:37 | 4.4722 | 0.024929
| 2:37 | 4.4725 | 0.024893
| 2:37 | 4.4728 | 0.024858
| 2:37 | 4.4731 | 0.02482
| 2:37 | 4.4733 | 0.024783
| 2:37 | 4.4736 | 0.024746
| 2:37 | 4.4739 | 0.024708
| 2:37 | 4.4742 | 0.024669
| 2:37 | 4.4744 | 0.024632
| 2:37 | 4.4747 | 0.024595
| 2:37 | 4.475 | 0.024558
| 2:37 | 4.4753 | 0.024521
| 2:37 | 4.4756 | 0.024486
| 2:37 | 4.4758 | 0.024452
| 2:37 | 4.4761 | 0.024416
| 2:37 | 4.4764 | 0.024376
| 2:37 | 4.4767 | 0.024336
| 2:37 | 4.4769 | 0.024295
| 2:37 | 4.4772 | 0.024248
| 2:37 | 4.4775 | 0.024198
| 2:37 | 4.4778 | 0.024148
| 2:37 | 4.4781 | 0.024097
| 2:38 | 4.4783 | 0.024048
| 2:38 | 4.4786 | 0.024004
| 2:38 | 4.4789 | 0.023963
| 2:38 | 4.4792 | 0.023925
| 2:38 | 4.4794 | 0.023891
| 2:38 | 4.4797 | 0.023861
| 2:38 | 4.48 | 0.023835
| 2:38 | 4.4803 | 0.023814
| 2:38 | 4.4806 | 0.023796
| 2:38 | 4.4808 | 0.023783
| 2:38 | 4.4811 | 0.023774
| 2:38 | 4.4814 | 0.023769
| 2:38 | 4.4817 | 0.023768
| 2:38 | 4.4819 | 0.023772
| 2:38 | 4.4822 | 0.02378
| 2:38 | 4.4825 | 0.023792
| 2:38 | 4.4828 | 0.023814
| 2:38 | 4.4831 | 0.023841
| 2:38 | 4.4833 | 0.023868
| 2:38 | 4.4836 | 0.023899
| 2:38 | 4.4839 | 0.023933
| 2:38 | 4.4842 | 0.023968
| 2:38 | 4.4844 | 0.024005
| 2:38 | 4.4847 | 0.024045
| 2:38 | 4.485 | 0.024084
| 2:38 | 4.4853 | 0.024124
| 2:38 | 4.4856 | 0.024167
| 2:38 | 4.4858 | 0.024211
| 2:38 | 4.4861 | 0.024255
| 2:38 | 4.4864 | 0.0243
| 2:38 | 4.4867 | 0.024346
| 2:38 | 4.4869 | 0.02439
| 2:38 | 4.4872 | 0.024432
| 2:38 | 4.4875 | 0.024473
| 2:38 | 4.4878 | 0.024514
| 2:38 | 4.4881 | 0.024554
| 2:38 | 4.4883 | 0.024593
| 2:38 | 4.4886 | 0.02463
| 2:38 | 4.4889 | 0.024666
| 2:38 | 4.4892 | 0.024701
| 2:38 | 4.4894 | 0.024734
| 2:38 | 4.4897 | 0.024767
| 2:38 | 4.49 | 0.024799
| 2:38 | 4.4903 | 0.024829
| 2:38 | 4.4906 | 0.024852
| 2:38 | 4.4908 | 0.024868
| 2:38 | 4.4911 | 0.024876
| 2:38 | 4.4914 | 0.024874
| 2:38 | 4.4917 | 0.024856
| 2:38 | 4.4919 | 0.02483
| 2:38 | 4.4922 | 0.024792
| 2:38 | 4.4925 | 0.024746
| 2:38 | 4.4928 | 0.024698
| 2:38 | 4.4931 | 0.024651
| 2:38 | 4.4933 | 0.024607
| 2:38 | 4.4936 | 0.024565
| 2:38 | 4.4939 | 0.024529
| 2:38 | 4.4942 | 0.0245
| 2:38 | 4.4944 | 0.024477
| 2:38 | 4.4947 | 0.024456
| 2:38 | 4.495 | 0.024441
| 2:39 | 4.4953 | 0.024429
| 2:39 | 4.4956 | 0.02442
| 2:39 | 4.4958 | 0.024416
| 2:39 | 4.4961 | 0.024415
| 2:39 | 4.4964 | 0.024417
| 2:39 | 4.4967 | 0.024421
| 2:39 | 4.4969 | 0.024429
| 2:39 | 4.4972 | 0.02444
| 2:39 | 4.4975 | 0.024453
| 2:39 | 4.4978 | 0.02447
| 2:39 | 4.4981 | 0.024489
| 2:39 | 4.4983 | 0.024512
| 2:39 | 4.4986 | 0.024537
| 2:39 | 4.4989 | 0.024561
| 2:39 | 4.4992 | 0.024586
| 2:39 | 4.4994 | 0.02461
| 2:39 | 4.4997 | 0.024635
| 2:39 | 4.5 | 0.024657
| 2:39 | 4.5003 | 0.024677
| 2:39 | 4.5006 | 0.024697
| 2:39 | 4.5008 | 0.024717
| 2:39 | 4.5011 | 0.024735
| 2:39 | 4.5014 | 0.024753
| 2:39 | 4.5017 | 0.02477
| 2:39 | 4.5019 | 0.024788
| 2:39 | 4.5022 | 0.024806
| 2:39 | 4.5025 | 0.024824
| 2:39 | 4.5028 | 0.024844
| 2:39 | 4.5031 | 0.024864
| 2:39 | 4.5033 | 0.024885
| 2:39 | 4.5036 | 0.024907
| 2:39 | 4.5039 | 0.024929
| 2:39 | 4.5042 | 0.024949
| 2:39 | 4.5044 | 0.024963
| 2:39 | 4.5047 | 0.024969
| 2:39 | 4.505 | 0.024968
| 2:39 | 4.5053 | 0.02496
| 2:39 | 4.5056 | 0.024944
| 2:39 | 4.5058 | 0.024921
| 2:39 | 4.5061 | 0.02489
| 2:39 | 4.5064 | 0.024854
| 2:39 | 4.5067 | 0.024803
| 2:39 | 4.5069 | 0.024726
| 2:39 | 4.5072 | 0.024632
| 2:39 | 4.5075 | 0.024521
| 2:39 | 4.5078 | 0.024373
| 2:39 | 4.5081 | 0.02422
| 2:39 | 4.5083 | 0.024031
| 2:39 | 4.5086 | 0.02382
| 2:39 | 4.5089 | 0.023583
| 2:39 | 4.5092 | 0.023315
| 2:39 | 4.5094 | 0.023014
| 2:39 | 4.5097 | 0.022701
| 2:39 | 4.51 | 0.022364
| 2:39 | 4.5103 | 0.02201
| 2:39 | 4.5106 | 0.021634
| 2:39 | 4.5108 | 0.021241
| 2:39 | 4.5111 | 0.020828
| 2:39 | 4.5114 | 0.020391
| 2:40 | 4.5117 | 0.019943
| 2:40 | 4.5119 | 0.019481
| 2:40 | 4.5122 | 0.019002
| 2:40 | 4.5125 | 0.018511
| 2:40 | 4.5128 | 0.01802
| 2:40 | 4.5131 | 0.017531
| 2:40 | 4.5133 | 0.017042
| 2:40 | 4.5136 | 0.016554
| 2:40 | 4.5139 | 0.016067
| 2:40 | 4.5142 | 0.015581
| 2:40 | 4.5144 | 0.015096
| 2:40 | 4.5147 | 0.014612
| 2:40 | 4.515 | 0.014129
| 2:40 | 4.5153 | 0.013645
| 2:40 | 4.5156 | 0.013157
| 2:40 | 4.5158 | 0.012659
| 2:40 | 4.5161 | 0.012157
| 2:40 | 4.5164 | 0.011649
| 2:40 | 4.5167 | 0.011139
| 2:40 | 4.5169 | 0.01062
| 2:40 | 4.5172 | 0.010106
| 2:40 | 4.5175 | 0.0095935
| 2:40 | 4.5178 | 0.0090807
| 2:40 | 4.5181 | 0.0085746
| 2:40 | 4.5183 | 0.0080748
| 2:40 | 4.5186 | 0.0075954
| 2:40 | 4.5189 | 0.0071426
| 2:40 | 4.5192 | 0.0066991
| 2:40 | 4.5194 | 0.0062687
| 2:40 | 4.5197 | 0.005859
| 2:40 | 4.52 | 0.0054616
| 2:40 | 4.5203 | 0.0050707
| 2:40 | 4.5206 | 0.0047044
| 2:40 | 4.5208 | 0.0043383
| 2:40 | 4.5211 | 0.0039727
| 2:40 | 4.5214 | 0.0036077
| 2:40 | 4.5217 | 0.0032434
| 2:40 | 4.5219 | 0.0028795
| 2:40 | 4.5222 | 0.0025163
| 2:40 | 4.5225 | 0.0021537
| 2:40 | 4.5228 | 0.0017916
| 2:40 | 4.5231 | 0.0014297
| 2:40 | 4.5233 | 0.0010632
| 2:40 | 4.5236 | 0.00069288
| 2:40 | 4.5239 | 0.00031538
| 2:40 | 4.5242 | -6.6828e-05
| 2:40 | 4.5244 | -0.00045858
| 2:40 | 4.5247 | -0.00085498
| 2:40 | 4.525 | -0.0012569
| 2:40 | 4.5253 | -0.0016558
| 2:40 | 4.5256 | -0.0020511
| 2:40 | 4.5258 | -0.0024388
| 2:40 | 4.5261 | -0.002823
| 2:40 | 4.5264 | -0.0032026
| 2:40 | 4.5267 | -0.0035779
| 2:40 | 4.5269 | -0.0039532
| 2:40 | 4.5272 | -0.0043294
| 2:40 | 4.5275 | -0.004707
| 2:40 | 4.5278 | -0.0050861
| 2:40 | 4.5281 | -0.0054659
| 2:40 | 4.5283 | -0.0058457
| 2:41 | 4.5286 | -0.0062243
| 2:41 | 4.5289 | -0.0066041
| 2:41 | 4.5292 | -0.0069839
| 2:41 | 4.5294 | -0.007365
| 2:41 | 4.5297 | -0.007753
| 2:41 | 4.53 | -0.008148
| 2:41 | 4.5303 | -0.0085498
| 2:41 | 4.5306 | -0.0089586
| 2:41 | 4.5308 | -0.0093743
| 2:41 | 4.5311 | -0.0097969
| 2:41 | 4.5314 | -0.010226
| 2:41 | 4.5317 | -0.010663
| 2:41 | 4.5319 | -0.011109
| 2:41 | 4.5322 | -0.011578
| 2:41 | 4.5325 | -0.012087
| 2:41 | 4.5328 | -0.012613
| 2:41 | 4.5331 | -0.013156
| 2:41 | 4.5333 | -0.013725
| 2:41 | 4.5336 | -0.014305
| 2:41 | 4.5339 | -0.014908
| 2:41 | 4.5342 | -0.015513
| 2:41 | 4.5344 | -0.01613
| 2:41 | 4.5347 | -0.016751
| 2:41 | 4.535 | -0.017375
| 2:41 | 4.5353 | -0.018001
| 2:41 | 4.5356 | -0.018628
| 2:41 | 4.5358 | -0.019259
| 2:41 | 4.5361 | -0.019891
| 2:41 | 4.5364 | -0.020523
| 2:41 | 4.5367 | -0.021159
| 2:41 | 4.5369 | -0.0218
| 2:41 | 4.5372 | -0.022442
| 2:41 | 4.5375 | -0.023085
| 2:41 | 4.5378 | -0.023733
| 2:41 | 4.5381 | -0.024384
| 2:41 | 4.5383 | -0.02504
| 2:41 | 4.5386 | -0.0257
| 2:41 | 4.5389 | -0.026364
| 2:41 | 4.5392 | -0.027032
| 2:41 | 4.5394 | -0.027705
| 2:41 | 4.5397 | -0.028381
| 2:41 | 4.54 | -0.029057
| 2:41 | 4.5403 | -0.029732
| 2:41 | 4.5406 | -0.030406
| 2:41 | 4.5408 | -0.031078
| 2:41 | 4.5411 | -0.031746
| 2:41 | 4.5414 | -0.032411
| 2:41 | 4.5417 | -0.033071
| 2:41 | 4.5419 | -0.033728
| 2:41 | 4.5422 | -0.034383
| 2:41 | 4.5425 | -0.035033
| 2:41 | 4.5428 | -0.035679
| 2:41 | 4.5431 | -0.036322
| 2:41 | 4.5433 | -0.036964
| 2:41 | 4.5436 | -0.037607
| 2:41 | 4.5439 | -0.038251
| 2:41 | 4.5442 | -0.038896
| 2:41 | 4.5444 | -0.039543
| 2:41 | 4.5447 | -0.040192
| 2:42 | 4.545 | -0.040846
| 2:42 | 4.5453 | -0.041501
| 2:42 | 4.5456 | -0.042161
| 2:42 | 4.5458 | -0.042827
| 2:42 | 4.5461 | -0.043499
| 2:42 | 4.5464 | -0.044172
| 2:42 | 4.5467 | -0.044847
| 2:42 | 4.5469 | -0.045523
| 2:42 | 4.5472 | -0.046201
| 2:42 | 4.5475 | -0.04688
| 2:42 | 4.5478 | -0.047561
| 2:42 | 4.5481 | -0.048243
| 2:42 | 4.5483 | -0.048926
| 2:42 | 4.5486 | -0.049609
| 2:42 | 4.5489 | -0.050291
| 2:42 | 4.5492 | -0.050974
| 2:42 | 4.5494 | -0.051659
| 2:42 | 4.5497 | -0.052344
| 2:42 | 4.55 | -0.053031
| 2:42 | 4.5503 | -0.05372
| 2:42 | 4.5506 | -0.054407
| 2:42 | 4.5508 | -0.055094
| 2:42 | 4.5511 | -0.055782
| 2:42 | 4.5514 | -0.056471
| 2:42 | 4.5517 | -0.057158
| 2:42 | 4.5519 | -0.057845
| 2:42 | 4.5522 | -0.058532
| 2:42 | 4.5525 | -0.059219
| 2:42 | 4.5528 | -0.059906
| 2:42 | 4.5531 | -0.060592
| 2:42 | 4.5533 | -0.061276
| 2:42 | 4.5536 | -0.061961
| 2:42 | 4.5539 | -0.062646
| 2:42 | 4.5542 | -0.063331
| 2:42 | 4.5544 | -0.064014
| 2:42 | 4.5547 | -0.064696
| 2:42 | 4.555 | -0.065376
| 2:42 | 4.5553 | -0.066055
| 2:42 | 4.5556 | -0.066733
| 2:42 | 4.5558 | -0.067409
| 2:42 | 4.5561 | -0.068083
| 2:42 | 4.5564 | -0.068756
| 2:42 | 4.5567 | -0.069427
| 2:42 | 4.5569 | -0.070096
| 2:42 | 4.5572 | -0.070768
| 2:42 | 4.5575 | -0.071438
| 2:42 | 4.5578 | -0.072107
| 2:42 | 4.5581 | -0.072773
| 2:42 | 4.5583 | -0.073439
| 2:42 | 4.5586 | -0.074104
| 2:42 | 4.5589 | -0.074769
| 2:42 | 4.5592 | -0.075434
| 2:42 | 4.5594 | -0.076097
| 2:42 | 4.5597 | -0.07676
| 2:42 | 4.56 | -0.077423
| 2:42 | 4.5603 | -0.078086
| 2:42 | 4.5606 | -0.078747
| 2:42 | 4.5608 | -0.079408
| 2:42 | 4.5611 | -0.080069
| 2:42 | 4.5614 | -0.080729
| 2:42 | 4.5617 | -0.081388
| 2:43 | 4.5619 | -0.082046
| 2:43 | 4.5622 | -0.082707
| 2:43 | 4.5625 | -0.083368
| 2:43 | 4.5628 | -0.084029
| 2:43 | 4.5631 | -0.08469
| 2:43 | 4.5633 | -0.085351
| 2:43 | 4.5636 | -0.086013
| 2:43 | 4.5639 | -0.086675
| 2:43 | 4.5642 | -0.087337
| 2:43 | 4.5644 | -0.088
| 2:43 | 4.5647 | -0.088662
| 2:43 | 4.565 | -0.089325
| 2:43 | 4.5653 | -0.089986
| 2:43 | 4.5656 | -0.090647
| 2:43 | 4.5658 | -0.09131
| 2:43 | 4.5661 | -0.091973
| 2:43 | 4.5664 | -0.092636
| 2:43 | 4.5667 | -0.093299
| 2:43 | 4.5669 | -0.093962
| 2:43 | 4.5672 | -0.094629
| 2:43 | 4.5675 | -0.095296
| 2:43 | 4.5678 | -0.095963
| 2:43 | 4.5681 | -0.096631
| 2:43 | 4.5683 | -0.097298
| 2:43 | 4.5686 | -0.097966
| 2:43 | 4.5689 | -0.098635
| 2:43 | 4.5692 | -0.099305
| 2:43 | 4.5694 | -0.099974
| 2:43 | 4.5697 | -0.10064
| 2:43 | 4.57 | -0.10132
| 2:43 | 4.5703 | -0.10199
| 2:43 | 4.5706 | -0.10266
| 2:43 | 4.5708 | -0.10334
| 2:43 | 4.5711 | -0.10402
| 2:43 | 4.5714 | -0.1047
| 2:43 | 4.5717 | -0.10538
| 2:43 | 4.5719 | -0.10606
| 2:43 | 4.5722 | -0.10674
| 2:43 | 4.5725 | -0.10743
| 2:43 | 4.5728 | -0.10811
| 2:43 | 4.5731 | -0.1088
| 2:43 | 4.5733 | -0.10949
| 2:43 | 4.5736 | -0.11017
| 2:43 | 4.5739 | -0.11086
| 2:43 | 4.5742 | -0.11156
| 2:43 | 4.5744 | -0.11226
| 2:43 | 4.5747 | -0.11296
| 2:43 | 4.575 | -0.11366
| 2:43 | 4.5753 | -0.11437
| 2:43 | 4.5756 | -0.11508
| 2:43 | 4.5758 | -0.11579
| 2:43 | 4.5761 | -0.1165
| 2:43 | 4.5764 | -0.11721
| 2:43 | 4.5767 | -0.11792
| 2:43 | 4.5769 | -0.11864
| 2:43 | 4.5772 | -0.11935
| 2:43 | 4.5775 | -0.12007
| 2:43 | 4.5778 | -0.12079
| 2:43 | 4.5781 | -0.12151
| 2:44 | 4.5783 | -0.12224
| 2:44 | 4.5786 | -0.12296
| 2:44 | 4.5789 | -0.12369
| 2:44 | 4.5792 | -0.12442
| 2:44 | 4.5794 | -0.12514
| 2:44 | 4.5797 | -0.12587
| 2:44 | 4.58 | -0.1266
| 2:44 | 4.5803 | -0.12733
| 2:44 | 4.5806 | -0.12807
| 2:44 | 4.5808 | -0.1288
| 2:44 | 4.5811 | -0.12953
| 2:44 | 4.5814 | -0.13027
| 2:44 | 4.5817 | -0.131
| 2:44 | 4.5819 | -0.13174
| 2:44 | 4.5822 | -0.13247
| 2:44 | 4.5825 | -0.13321
| 2:44 | 4.5828 | -0.13394
| 2:44 | 4.5831 | -0.13468
| 2:44 | 4.5833 | -0.13541
| 2:44 | 4.5836 | -0.13615
| 2:44 | 4.5839 | -0.13688
| 2:44 | 4.5842 | -0.13762
| 2:44 | 4.5844 | -0.13836
| 2:44 | 4.5847 | -0.13909
| 2:44 | 4.585 | -0.13983
| 2:44 | 4.5853 | -0.14056
| 2:44 | 4.5856 | -0.1413
| 2:44 | 4.5858 | -0.14203
| 2:44 | 4.5861 | -0.14277
| 2:44 | 4.5864 | -0.14351
| 2:44 | 4.5867 | -0.14424
| 2:44 | 4.5869 | -0.14497
| 2:44 | 4.5872 | -0.1457
| 2:44 | 4.5875 | -0.14643
| 2:44 | 4.5878 | -0.14716
| 2:44 | 4.5881 | -0.14787
| 2:44 | 4.5883 | -0.14858
| 2:44 | 4.5886 | -0.14929
| 2:44 | 4.5889 | -0.14998
| 2:44 | 4.5892 | -0.15067
| 2:44 | 4.5894 | -0.15135
| 2:44 | 4.5897 | -0.15202
| 2:44 | 4.59 | -0.15267
| 2:44 | 4.5903 | -0.15331
| 2:44 | 4.5906 | -0.15394
| 2:44 | 4.5908 | -0.15456
| 2:44 | 4.5911 | -0.15518
| 2:44 | 4.5914 | -0.15577
| 2:44 | 4.5917 | -0.15636
| 2:44 | 4.5919 | -0.15693
| 2:44 | 4.5922 | -0.15749
| 2:44 | 4.5925 | -0.15804
| 2:44 | 4.5928 | -0.15857
| 2:44 | 4.5931 | -0.15909
| 2:44 | 4.5933 | -0.15961
| 2:44 | 4.5936 | -0.1601
| 2:44 | 4.5939 | -0.16059
| 2:44 | 4.5942 | -0.16107
| 2:44 | 4.5944 | -0.16154
| 2:44 | 4.5947 | -0.16199
| 2:44 | 4.595 | -0.16244
| 2:45 | 4.5953 | -0.16286
| 2:45 | 4.5956 | -0.16328
| 2:45 | 4.5958 | -0.16369
| 2:45 | 4.5961 | -0.16408
| 2:45 | 4.5964 | -0.16446
| 2:45 | 4.5967 | -0.16484
| 2:45 | 4.5969 | -0.1652
| 2:45 | 4.5972 | -0.16554
| 2:45 | 4.5975 | -0.16588
| 2:45 | 4.5978 | -0.16621
| 2:45 | 4.5981 | -0.16652
| 2:45 | 4.5983 | -0.16683
| 2:45 | 4.5986 | -0.16712
| 2:45 | 4.5989 | -0.16741
| 2:45 | 4.5992 | -0.16769
| 2:45 | 4.5994 | -0.16796
| 2:45 | 4.5997 | -0.16823
| 2:45 | 4.6 | -0.16848
| 2:45 | 4.6003 | -0.16873
| 2:45 | 4.6006 | -0.16896
| 2:45 | 4.6008 | -0.16919
| 2:45 | 4.6011 | -0.16941
| 2:45 | 4.6014 | -0.16961
| 2:45 | 4.6017 | -0.16982
| 2:45 | 4.6019 | -0.17001
| 2:45 | 4.6022 | -0.1702
| 2:45 | 4.6025 | -0.17039
| 2:45 | 4.6028 | -0.17057
| 2:45 | 4.6031 | -0.17075
| 2:45 | 4.6033 | -0.17093
| 2:45 | 4.6036 | -0.1711
| 2:45 | 4.6039 | -0.17127
| 2:45 | 4.6042 | -0.17143
| 2:45 | 4.6044 | -0.1716
| 2:45 | 4.6047 | -0.17176
| 2:45 | 4.605 | -0.17192
| 2:45 | 4.6053 | -0.17208
| 2:45 | 4.6056 | -0.17224
| 2:45 | 4.6058 | -0.17239
| 2:45 | 4.6061 | -0.17255
| 2:45 | 4.6064 | -0.1727
| 2:45 | 4.6067 | -0.17285
| 2:45 | 4.6069 | -0.173
| 2:45 | 4.6072 | -0.17314
| 2:45 | 4.6075 | -0.17329
| 2:45 | 4.6078 | -0.17344
| 2:45 | 4.6081 | -0.17358
| 2:45 | 4.6083 | -0.17373
| 2:45 | 4.6086 | -0.17387
| 2:45 | 4.6089 | -0.17401
| 2:45 | 4.6092 | -0.17416
| 2:45 | 4.6094 | -0.1743
| 2:45 | 4.6097 | -0.17444
| 2:45 | 4.61 | -0.17458
| 2:45 | 4.6103 | -0.17473
| 2:45 | 4.6106 | -0.17487
| 2:45 | 4.6108 | -0.17501
| 2:45 | 4.6111 | -0.17515
| 2:45 | 4.6114 | -0.17529
| 2:46 | 4.6117 | -0.17543
| 2:46 | 4.6119 | -0.17557
| 2:46 | 4.6122 | -0.17571
| 2:46 | 4.6125 | -0.17585
| 2:46 | 4.6128 | -0.17599
| 2:46 | 4.6131 | -0.17613
| 2:46 | 4.6133 | -0.17627
| 2:46 | 4.6136 | -0.17641
| 2:46 | 4.6139 | -0.17655
| 2:46 | 4.6142 | -0.17669
| 2:46 | 4.6144 | -0.17683
| 2:46 | 4.6147 | -0.17697
| 2:46 | 4.615 | -0.17711
| 2:46 | 4.6153 | -0.17725
| 2:46 | 4.6156 | -0.17739
| 2:46 | 4.6158 | -0.17753
| 2:46 | 4.6161 | -0.17768
| 2:46 | 4.6164 | -0.17782
| 2:46 | 4.6167 | -0.17796
| 2:46 | 4.6169 | -0.1781
| 2:46 | 4.6172 | -0.17824
| 2:46 | 4.6175 | -0.17838
| 2:46 | 4.6178 | -0.17852
| 2:46 | 4.6181 | -0.17866
| 2:46 | 4.6183 | -0.1788
| 2:46 | 4.6186 | -0.17894
| 2:46 | 4.6189 | -0.17908
| 2:46 | 4.6192 | -0.17922
| 2:46 | 4.6194 | -0.17936
| 2:46 | 4.6197 | -0.1795
| 2:46 | 4.62 | -0.17964
| 2:46 | 4.6203 | -0.17978
| 2:46 | 4.6206 | -0.17992
| 2:46 | 4.6208 | -0.18006
| 2:46 | 4.6211 | -0.18021
| 2:46 | 4.6214 | -0.18035
| 2:46 | 4.6217 | -0.18049
| 2:46 | 4.6219 | -0.18063
| 2:46 | 4.6222 | -0.18077
| 2:46 | 4.6225 | -0.18091
| 2:46 | 4.6228 | -0.18105
| 2:46 | 4.6231 | -0.18119
| 2:46 | 4.6233 | -0.18133
| 2:46 | 4.6236 | -0.18147
| 2:46 | 4.6239 | -0.18161
| 2:46 | 4.6242 | -0.18175
| 2:46 | 4.6244 | -0.18189
| 2:46 | 4.6247 | -0.18203
| 2:46 | 4.625 | -0.18217
| 2:46 | 4.6253 | -0.18231
| 2:46 | 4.6256 | -0.18245
| 2:46 | 4.6258 | -0.18258
| 2:46 | 4.6261 | -0.18272
| 2:46 | 4.6264 | -0.18286
| 2:46 | 4.6267 | -0.183
| 2:46 | 4.6269 | -0.18314
| 2:46 | 4.6272 | -0.18327
| 2:46 | 4.6275 | -0.18341
| 2:46 | 4.6278 | -0.18355
| 2:46 | 4.6281 | -0.18369
| 2:46 | 4.6283 | -0.18383
| 2:47 | 4.6286 | -0.18396
| 2:47 | 4.6289 | -0.1841
| 2:47 | 4.6292 | -0.18424
| 2:47 | 4.6294 | -0.18438
| 2:47 | 4.6297 | -0.18452
| 2:47 | 4.63 | -0.18466
| 2:47 | 4.6303 | -0.18479
| 2:47 | 4.6306 | -0.18493
| 2:47 | 4.6308 | -0.18507
| 2:47 | 4.6311 | -0.18521
| 2:47 | 4.6314 | -0.18535
| 2:47 | 4.6317 | -0.18548
| 2:47 | 4.6319 | -0.18562
| 2:47 | 4.6322 | -0.18576
| 2:47 | 4.6325 | -0.1859
| 2:47 | 4.6328 | -0.18603
| 2:47 | 4.6331 | -0.18617
| 2:47 | 4.6333 | -0.18631
| 2:47 | 4.6336 | -0.18645
| 2:47 | 4.6339 | -0.18659
| 2:47 | 4.6342 | -0.18673
| 2:47 | 4.6344 | -0.18687
| 2:47 | 4.6347 | -0.187
| 2:47 | 4.635 | -0.18714
| 2:47 | 4.6353 | -0.18728
| 2:47 | 4.6356 | -0.18742
| 2:47 | 4.6358 | -0.18756
| 2:47 | 4.6361 | -0.1877
| 2:47 | 4.6364 | -0.18783
| 2:47 | 4.6367 | -0.18797
| 2:47 | 4.6369 | -0.18811
| 2:47 | 4.6372 | -0.18824
| 2:47 | 4.6375 | -0.18838
| 2:47 | 4.6378 | -0.18852
| 2:47 | 4.6381 | -0.18866
| 2:47 | 4.6383 | -0.18879
| 2:47 | 4.6386 | -0.18893
| 2:47 | 4.6389 | -0.18907
| 2:47 | 4.6392 | -0.1892
| 2:47 | 4.6394 | -0.18934
| 2:47 | 4.6397 | -0.18948
| 2:47 | 4.64 | -0.18961
| 2:47 | 4.6403 | -0.18975
| 2:47 | 4.6406 | -0.18989
| 2:47 | 4.6408 | -0.19002
| 2:47 | 4.6411 | -0.19016
| 2:47 | 4.6414 | -0.1903
| 2:47 | 4.6417 | -0.19043
| 2:47 | 4.6419 | -0.19057
| 2:47 | 4.6422 | -0.19071
| 2:47 | 4.6425 | -0.19085
| 2:47 | 4.6428 | -0.19099
| 2:47 | 4.6431 | -0.19113
| 2:47 | 4.6433 | -0.19127
| 2:47 | 4.6436 | -0.1914
| 2:47 | 4.6439 | -0.19154
| 2:47 | 4.6442 | -0.19168
| 2:47 | 4.6444 | -0.19182
| 2:47 | 4.6447 | -0.19196
| 2:48 | 4.645 | -0.1921
| 2:48 | 4.6453 | -0.19223
| 2:48 | 4.6456 | -0.19237
| 2:48 | 4.6458 | -0.19251
| 2:48 | 4.6461 | -0.19265
| 2:48 | 4.6464 | -0.19279
| 2:48 | 4.6467 | -0.19293
| 2:48 | 4.6469 | -0.19307
| 2:48 | 4.6472 | -0.19321
| 2:48 | 4.6475 | -0.19335
| 2:48 | 4.6478 | -0.19348
| 2:48 | 4.6481 | -0.19362
| 2:48 | 4.6483 | -0.19376
| 2:48 | 4.6486 | -0.1939
| 2:48 | 4.6489 | -0.19404
| 2:48 | 4.6492 | -0.19417
| 2:48 | 4.6494 | -0.19431
| 2:48 | 4.6497 | -0.19445
| 2:48 | 4.65 | -0.19459
| 2:48 | 4.6503 | -0.19473
| 2:48 | 4.6506 | -0.19486
| 2:48 | 4.6508 | -0.195
| 2:48 | 4.6511 | -0.19514
| 2:48 | 4.6514 | -0.19528
| 2:48 | 4.6517 | -0.19541
| 2:48 | 4.6519 | -0.19555
| 2:48 | 4.6522 | -0.19569
| 2:48 | 4.6525 | -0.19583
| 2:48 | 4.6528 | -0.19597
| 2:48 | 4.6531 | -0.19611
| 2:48 | 4.6533 | -0.19625
| 2:48 | 4.6536 | -0.19639
| 2:48 | 4.6539 | -0.19652
| 2:48 | 4.6542 | -0.19666
| 2:48 | 4.6544 | -0.1968
| 2:48 | 4.6547 | -0.19694
| 2:48 | 4.655 | -0.19708
| 2:48 | 4.6553 | -0.19722
| 2:48 | 4.6556 | -0.19736
| 2:48 | 4.6558 | -0.1975
| 2:48 | 4.6561 | -0.19764
| 2:48 | 4.6564 | -0.19778
| 2:48 | 4.6567 | -0.19792
| 2:48 | 4.6569 | -0.19806
| 2:48 | 4.6572 | -0.19821
| 2:48 | 4.6575 | -0.19835
| 2:48 | 4.6578 | -0.19849
| 2:48 | 4.6581 | -0.19863
| 2:48 | 4.6583 | -0.19878
| 2:48 | 4.6586 | -0.19892
| 2:48 | 4.6589 | -0.19907
| 2:48 | 4.6592 | -0.19921
| 2:48 | 4.6594 | -0.19936
| 2:48 | 4.6597 | -0.1995
| 2:48 | 4.66 | -0.19965
| 2:48 | 4.6603 | -0.19979
| 2:48 | 4.6606 | -0.19994
| 2:48 | 4.6608 | -0.20009
| 2:48 | 4.6611 | -0.20024
| 2:48 | 4.6614 | -0.20039
| 2:48 | 4.6617 | -0.20054
| 2:49 | 4.6619 | -0.20069
| 2:49 | 4.6622 | -0.20084
| 2:49 | 4.6625 | -0.20099
| 2:49 | 4.6628 | -0.20114
| 2:49 | 4.6631 | -0.20129
| 2:49 | 4.6633 | -0.20144
| 2:49 | 4.6636 | -0.2016
| 2:49 | 4.6639 | -0.20175
| 2:49 | 4.6642 | -0.2019
| 2:49 | 4.6644 | -0.20206
| 2:49 | 4.6647 | -0.20221
| 2:49 | 4.665 | -0.20237
| 2:49 | 4.6653 | -0.20252
| 2:49 | 4.6656 | -0.20268
| 2:49 | 4.6658 | -0.20283
| 2:49 | 4.6661 | -0.20299
| 2:49 | 4.6664 | -0.20315
| 2:49 | 4.6667 | -0.20331
| 2:49 | 4.6669 | -0.20347
| 2:49 | 4.6672 | -0.20363
| 2:49 | 4.6675 | -0.2038
| 2:49 | 4.6678 | -0.20396
| 2:49 | 4.6681 | -0.20413
| 2:49 | 4.6683 | -0.20429
| 2:49 | 4.6686 | -0.20446
| 2:49 | 4.6689 | -0.20462
| 2:49 | 4.6692 | -0.20479
| 2:49 | 4.6694 | -0.20495
| 2:49 | 4.6697 | -0.20512
| 2:49 | 4.67 | -0.20529
| 2:49 | 4.6703 | -0.20546
| 2:49 | 4.6706 | -0.20563
| 2:49 | 4.6708 | -0.2058
| 2:49 | 4.6711 | -0.20597
| 2:49 | 4.6714 | -0.20614
| 2:49 | 4.6717 | -0.20631
| 2:49 | 4.6719 | -0.20649
| 2:49 | 4.6722 | -0.20667
| 2:49 | 4.6725 | -0.20684
| 2:49 | 4.6728 | -0.20702
| 2:49 | 4.6731 | -0.2072
| 2:49 | 4.6733 | -0.20739
| 2:49 | 4.6736 | -0.20757
| 2:49 | 4.6739 | -0.20776
| 2:49 | 4.6742 | -0.20794
| 2:49 | 4.6744 | -0.20813
| 2:49 | 4.6747 | -0.20833
| 2:49 | 4.675 | -0.20852
| 2:49 | 4.6753 | -0.20871
| 2:49 | 4.6756 | -0.20891
| 2:49 | 4.6758 | -0.20911
| 2:49 | 4.6761 | -0.20932
| 2:49 | 4.6764 | -0.20952
| 2:49 | 4.6767 | -0.20973
| 2:49 | 4.6769 | -0.20994
| 2:49 | 4.6772 | -0.21014
| 2:49 | 4.6775 | -0.21035
| 2:49 | 4.6778 | -0.21056
| 2:49 | 4.6781 | -0.21078
| 2:50 | 4.6783 | -0.21099
| 2:50 | 4.6786 | -0.21121
| 2:50 | 4.6789 | -0.21142
| 2:50 | 4.6792 | -0.21163
| 2:50 | 4.6794 | -0.21184
| 2:50 | 4.6797 | -0.21205
| 2:50 | 4.68 | -0.21226
| 2:50 | 4.6803 | -0.21247
| 2:50 | 4.6806 | -0.21268
| 2:50 | 4.6808 | -0.21289
| 2:50 | 4.6811 | -0.2131
| 2:50 | 4.6814 | -0.2133
| 2:50 | 4.6817 | -0.21351
| 2:50 | 4.6819 | -0.21371
| 2:50 | 4.6822 | -0.21391
| 2:50 | 4.6825 | -0.2141
| 2:50 | 4.6828 | -0.2143
| 2:50 | 4.6831 | -0.21448
| 2:50 | 4.6833 | -0.21467
| 2:50 | 4.6836 | -0.21485
| 2:50 | 4.6839 | -0.21504
| 2:50 | 4.6842 | -0.21521
| 2:50 | 4.6844 | -0.21539
| 2:50 | 4.6847 | -0.21557
| 2:50 | 4.685 | -0.21574
| 2:50 | 4.6853 | -0.21591
| 2:50 | 4.6856 | -0.21608
| 2:50 | 4.6858 | -0.21625
| 2:50 | 4.6861 | -0.21642
| 2:50 | 4.6864 | -0.21659
| 2:50 | 4.6867 | -0.21676
| 2:50 | 4.6869 | -0.21692
| 2:50 | 4.6872 | -0.21709
| 2:50 | 4.6875 | -0.21725
| 2:50 | 4.6878 | -0.21741
| 2:50 | 4.6881 | -0.21757
| 2:50 | 4.6883 | -0.21773
| 2:50 | 4.6886 | -0.21789
| 2:50 | 4.6889 | -0.21805
| 2:50 | 4.6892 | -0.21821
| 2:50 | 4.6894 | -0.21836
| 2:50 | 4.6897 | -0.21851
| 2:50 | 4.69 | -0.21867
| 2:50 | 4.6903 | -0.21882
| 2:50 | 4.6906 | -0.21897
| 2:50 | 4.6908 | -0.21913
| 2:50 | 4.6911 | -0.21928
| 2:50 | 4.6914 | -0.21943
| 2:50 | 4.6917 | -0.21958
| 2:50 | 4.6919 | -0.21973
| 2:50 | 4.6922 | -0.21987
| 2:50 | 4.6925 | -0.22002
| 2:50 | 4.6928 | -0.22017
| 2:50 | 4.6931 | -0.22031
| 2:50 | 4.6933 | -0.22046
| 2:50 | 4.6936 | -0.22061
| 2:50 | 4.6939 | -0.22075
| 2:50 | 4.6942 | -0.22089
| 2:50 | 4.6944 | -0.22104
| 2:50 | 4.6947 | -0.22118
| 2:50 | 4.695 | -0.22132
| 2:51 | 4.6953 | -0.22147
| 2:51 | 4.6956 | -0.22161
| 2:51 | 4.6958 | -0.22175
| 2:51 | 4.6961 | -0.22189
| 2:51 | 4.6964 | -0.22203
| 2:51 | 4.6967 | -0.22217
| 2:51 | 4.6969 | -0.22231
| 2:51 | 4.6972 | -0.22245
| 2:51 | 4.6975 | -0.22259
| 2:51 | 4.6978 | -0.22273
| 2:51 | 4.6981 | -0.22287
| 2:51 | 4.6983 | -0.22301
| 2:51 | 4.6986 | -0.22315
| 2:51 | 4.6989 | -0.22329
| 2:51 | 4.6992 | -0.22343
| 2:51 | 4.6994 | -0.22357
| 2:51 | 4.6997 | -0.22371
| 2:51 | 4.7 | -0.22385
| 2:51 | 4.7003 | -0.22399
| 2:51 | 4.7006 | -0.22413
| 2:51 | 4.7008 | -0.22427
| 2:51 | 4.7011 | -0.22441
| 2:51 | 4.7014 | -0.22455
| 2:51 | 4.7017 | -0.22469
| 2:51 | 4.7019 | -0.22482
| 2:51 | 4.7022 | -0.22496
| 2:51 | 4.7025 | -0.2251
| 2:51 | 4.7028 | -0.22524
| 2:51 | 4.7031 | -0.22538
| 2:51 | 4.7033 | -0.22552
| 2:51 | 4.7036 | -0.22566
| 2:51 | 4.7039 | -0.2258
| 2:51 | 4.7042 | -0.22594
| 2:51 | 4.7044 | -0.22608
| 2:51 | 4.7047 | -0.22622
| 2:51 | 4.705 | -0.22636
| 2:51 | 4.7053 | -0.2265
| 2:51 | 4.7056 | -0.22664
| 2:51 | 4.7058 | -0.22678
| 2:51 | 4.7061 | -0.22692
| 2:51 | 4.7064 | -0.22706
| 2:51 | 4.7067 | -0.22719
| 2:51 | 4.7069 | -0.22734
| 2:51 | 4.7072 | -0.22748
| 2:51 | 4.7075 | -0.22762
| 2:51 | 4.7078 | -0.22776
| 2:51 | 4.7081 | -0.2279
| 2:51 | 4.7083 | -0.22804
| 2:51 | 4.7086 | -0.22818
| 2:51 | 4.7089 | -0.22832
| 2:51 | 4.7092 | -0.22846
| 2:51 | 4.7094 | -0.2286
| 2:51 | 4.7097 | -0.22875
| 2:51 | 4.71 | -0.22889
| 2:51 | 4.7103 | -0.22903
| 2:51 | 4.7106 | -0.22917
| 2:51 | 4.7108 | -0.22931
| 2:51 | 4.7111 | -0.22946
| 2:51 | 4.7114 | -0.2296
| 2:52 | 4.7117 | -0.22974
| 2:52 | 4.7119 | -0.22989
| 2:52 | 4.7122 | -0.23004
| 2:52 | 4.7125 | -0.23019
| 2:52 | 4.7128 | -0.23034
| 2:52 | 4.7131 | -0.23049
| 2:52 | 4.7133 | -0.23064
| 2:52 | 4.7136 | -0.2308
| 2:52 | 4.7139 | -0.23096
| 2:52 | 4.7142 | -0.23111
| 2:52 | 4.7144 | -0.23127
| 2:52 | 4.7147 | -0.23144
| 2:52 | 4.715 | -0.2316
| 2:52 | 4.7153 | -0.23176
| 2:52 | 4.7156 | -0.23193
| 2:52 | 4.7158 | -0.23211
| 2:52 | 4.7161 | -0.23228
| 2:52 | 4.7164 | -0.23246
| 2:52 | 4.7167 | -0.23264
| 2:52 | 4.7169 | -0.23281
| 2:52 | 4.7172 | -0.23298
| 2:52 | 4.7175 | -0.23315
| 2:52 | 4.7178 | -0.23332
| 2:52 | 4.7181 | -0.2335
| 2:52 | 4.7183 | -0.23367
| 2:52 | 4.7186 | -0.23384
| 2:52 | 4.7189 | -0.23401
| 2:52 | 4.7192 | -0.23418
| 2:52 | 4.7194 | -0.23435
| 2:52 | 4.7197 | -0.23452
| 2:52 | 4.72 | -0.23469
| 2:52 | 4.7203 | -0.23485
| 2:52 | 4.7206 | -0.23502
| 2:52 | 4.7208 | -0.23518
| 2:52 | 4.7211 | -0.23535
| 2:52 | 4.7214 | -0.23551
| 2:52 | 4.7217 | -0.23567
| 2:52 | 4.7219 | -0.23584
| 2:52 | 4.7222 | -0.236
| 2:52 | 4.7225 | -0.23616
| 2:52 | 4.7228 | -0.23632
| 2:52 | 4.7231 | -0.23647
| 2:52 | 4.7233 | -0.23663
| 2:52 | 4.7236 | -0.23678
| 2:52 | 4.7239 | -0.23693
| 2:52 | 4.7242 | -0.23708
| 2:52 | 4.7244 | -0.23723
| 2:52 | 4.7247 | -0.23738
| 2:52 | 4.725 | -0.23753
| 2:52 | 4.7253 | -0.23768
| 2:52 | 4.7256 | -0.23783
| 2:52 | 4.7258 | -0.23798
| 2:52 | 4.7261 | -0.23813
| 2:52 | 4.7264 | -0.23827
| 2:52 | 4.7267 | -0.23842
| 2:52 | 4.7269 | -0.23857
| 2:52 | 4.7272 | -0.23871
| 2:52 | 4.7275 | -0.23886
| 2:52 | 4.7278 | -0.239
| 2:52 | 4.7281 | -0.23915
| 2:52 | 4.7283 | -0.23929
| 2:53 | 4.7286 | -0.23944
| 2:53 | 4.7289 | -0.23958
| 2:53 | 4.7292 | -0.23972
| 2:53 | 4.7294 | -0.23936
| 2:53 | 4.7297 | -0.23899
| 2:53 | 4.73 | -0.23863
| 2:53 | 4.7303 | -0.23827
| 2:53 | 4.7306 | -0.23792
| 2:53 | 4.7308 | -0.23756
| 2:53 | 4.7311 | -0.23721
| 2:53 | 4.7314 | -0.23686
| 2:53 | 4.7317 | -0.23651
| 2:53 | 4.7319 | -0.23616
| 2:53 | 4.7322 | -0.23581
| 2:53 | 4.7325 | -0.23547
| 2:53 | 4.7328 | -0.23511
| 2:53 | 4.7331 | -0.23476
| 2:53 | 4.7333 | -0.23439
| 2:53 | 4.7336 | -0.23402
| 2:53 | 4.7339 | -0.23365
| 2:53 | 4.7342 | -0.23328
| 2:53 | 4.7344 | -0.23291
| 2:53 | 4.7347 | -0.23253
| 2:53 | 4.735 | -0.23215
| 2:53 | 4.7353 | -0.23177
| 2:53 | 4.7356 | -0.23142
| 2:53 | 4.7358 | -0.23109
| 2:53 | 4.7361 | -0.23075
| 2:53 | 4.7364 | -0.23039
| 2:53 | 4.7367 | -0.23002
| 2:53 | 4.7369 | -0.22965
| 2:53 | 4.7372 | -0.22928
| 2:53 | 4.7375 | -0.22892
| 2:53 | 4.7378 | -0.22857
| 2:53 | 4.7381 | -0.22823
| 2:53 | 4.7383 | -0.22791
| 2:53 | 4.7386 | -0.22759
| 2:53 | 4.7389 | -0.22728
| 2:53 | 4.7392 | -0.22698
| 2:53 | 4.7394 | -0.22669
| 2:53 | 4.7397 | -0.22641
| 2:53 | 4.74 | -0.22614
| 2:53 | 4.7403 | -0.22587
| 2:53 | 4.7406 | -0.22559
| 2:53 | 4.7408 | -0.22532
| 2:53 | 4.7411 | -0.22504
| 2:53 | 4.7414 | -0.22475
| 2:53 | 4.7417 | -0.22445
| 2:53 | 4.7419 | -0.22414
| 2:53 | 4.7422 | -0.22383
| 2:53 | 4.7425 | -0.22351
| 2:53 | 4.7428 | -0.22319
| 2:53 | 4.7431 | -0.22286
| 2:53 | 4.7433 | -0.22252
| 2:53 | 4.7436 | -0.22219
| 2:53 | 4.7439 | -0.22185
| 2:53 | 4.7442 | -0.22151
| 2:53 | 4.7444 | -0.22115
| 2:53 | 4.7447 | -0.22079
| 2:54 | 4.745 | -0.22042
| 2:54 | 4.7453 | -0.22004
| 2:54 | 4.7456 | -0.21966
| 2:54 | 4.7458 | -0.21927
| 2:54 | 4.7461 | -0.21889
| 2:54 | 4.7464 | -0.21853
| 2:54 | 4.7467 | -0.21817
| 2:54 | 4.7469 | -0.21782
| 2:54 | 4.7472 | -0.21746
| 2:54 | 4.7475 | -0.21711
| 2:54 | 4.7478 | -0.21677
| 2:54 | 4.7481 | -0.21642
| 2:54 | 4.7483 | -0.21608
| 2:54 | 4.7486 | -0.21575
| 2:54 | 4.7489 | -0.21541
| 2:54 | 4.7492 | -0.21508
| 2:54 | 4.7494 | -0.21475
| 2:54 | 4.7497 | -0.21442
| 2:54 | 4.75 | -0.21409
| 2:54 | 4.7503 | -0.21375
| 2:54 | 4.7506 | -0.21342
| 2:54 | 4.7508 | -0.21308
| 2:54 | 4.7511 | -0.21275
| 2:54 | 4.7514 | -0.21241
| 2:54 | 4.7517 | -0.21207
| 2:54 | 4.7519 | -0.21173
| 2:54 | 4.7522 | -0.21137
| 2:54 | 4.7525 | -0.211
| 2:54 | 4.7528 | -0.21062
| 2:54 | 4.7531 | -0.21024
| 2:54 | 4.7533 | -0.20984
| 2:54 | 4.7536 | -0.20945
| 2:54 | 4.7539 | -0.20905
| 2:54 | 4.7542 | -0.20865
| 2:54 | 4.7544 | -0.20825
| 2:54 | 4.7547 | -0.20784
| 2:54 | 4.755 | -0.20744
| 2:54 | 4.7553 | -0.20705
| 2:54 | 4.7556 | -0.20667
| 2:54 | 4.7558 | -0.20629
| 2:54 | 4.7561 | -0.20593
| 2:54 | 4.7564 | -0.20557
| 2:54 | 4.7567 | -0.20522
| 2:54 | 4.7569 | -0.20487
| 2:54 | 4.7572 | -0.20453
| 2:54 | 4.7575 | -0.20418
| 2:54 | 4.7578 | -0.20384
| 2:54 | 4.7581 | -0.20351
| 2:54 | 4.7583 | -0.20317
| 2:54 | 4.7586 | -0.20283
| 2:54 | 4.7589 | -0.2025
| 2:54 | 4.7592 | -0.20217
| 2:54 | 4.7594 | -0.20184
| 2:54 | 4.7597 | -0.2015
| 2:54 | 4.76 | -0.20117
| 2:54 | 4.7603 | -0.20083
| 2:54 | 4.7606 | -0.20049
| 2:54 | 4.7608 | -0.20014
| 2:54 | 4.7611 | -0.19979
| 2:54 | 4.7614 | -0.19945
| 2:54 | 4.7617 | -0.19911
| 2:55 | 4.7619 | -0.19878
| 2:55 | 4.7622 | -0.19844
| 2:55 | 4.7625 | -0.19811
| 2:55 | 4.7628 | -0.19779
| 2:55 | 4.7631 | -0.19746
| 2:55 | 4.7633 | -0.19713
| 2:55 | 4.7636 | -0.1968
| 2:55 | 4.7639 | -0.19645
| 2:55 | 4.7642 | -0.1961
| 2:55 | 4.7644 | -0.19575
| 2:55 | 4.7647 | -0.19539
| 2:55 | 4.765 | -0.19502
| 2:55 | 4.7653 | -0.19464
| 2:55 | 4.7656 | -0.19426
| 2:55 | 4.7658 | -0.19387
| 2:55 | 4.7661 | -0.19348
| 2:55 | 4.7664 | -0.19307
| 2:55 | 4.7667 | -0.19266
| 2:55 | 4.7669 | -0.19225
| 2:55 | 4.7672 | -0.19184
| 2:55 | 4.7675 | -0.19143
| 2:55 | 4.7678 | -0.19101
| 2:55 | 4.7681 | -0.19059
| 2:55 | 4.7683 | -0.19016
| 2:55 | 4.7686 | -0.18973
| 2:55 | 4.7689 | -0.18929
| 2:55 | 4.7692 | -0.18885
| 2:55 | 4.7694 | -0.18841
| 2:55 | 4.7697 | -0.18795
| 2:55 | 4.77 | -0.18748
| 2:55 | 4.7703 | -0.187
| 2:55 | 4.7706 | -0.18653
| 2:55 | 4.7708 | -0.18605
| 2:55 | 4.7711 | -0.18557
| 2:55 | 4.7714 | -0.18509
| 2:55 | 4.7717 | -0.18462
| 2:55 | 4.7719 | -0.18414
| 2:55 | 4.7722 | -0.18365
| 2:55 | 4.7725 | -0.18317
| 2:55 | 4.7728 | -0.18269
| 2:55 | 4.7731 | -0.18221
| 2:55 | 4.7733 | -0.18172
| 2:55 | 4.7736 | -0.18124
| 2:55 | 4.7739 | -0.18075
| 2:55 | 4.7742 | -0.18027
| 2:55 | 4.7744 | -0.17977
| 2:55 | 4.7747 | -0.17927
| 2:55 | 4.775 | -0.17875
| 2:55 | 4.7753 | -0.17823
| 2:55 | 4.7756 | -0.17771
| 2:55 | 4.7758 | -0.17718
| 2:55 | 4.7761 | -0.17666
| 2:55 | 4.7764 | -0.17614
| 2:55 | 4.7767 | -0.17561
| 2:55 | 4.7769 | -0.17509
| 2:55 | 4.7772 | -0.17456
| 2:55 | 4.7775 | -0.17403
| 2:55 | 4.7778 | -0.1735
| 2:55 | 4.7781 | -0.17297
| 2:56 | 4.7783 | -0.17243
| 2:56 | 4.7786 | -0.17189
| 2:56 | 4.7789 | -0.17135
| 2:56 | 4.7792 | -0.17081
| 2:56 | 4.7794 | -0.17026
| 2:56 | 4.7797 | -0.16972
| 2:56 | 4.78 | -0.16917
| 2:56 | 4.7803 | -0.16863
| 2:56 | 4.7806 | -0.16808
| 2:56 | 4.7808 | -0.16753
| 2:56 | 4.7811 | -0.16698
| 2:56 | 4.7814 | -0.16644
| 2:56 | 4.7817 | -0.16589
| 2:56 | 4.7819 | -0.16534
| 2:56 | 4.7822 | -0.16479
| 2:56 | 4.7825 | -0.16424
| 2:56 | 4.7828 | -0.16369
| 2:56 | 4.7831 | -0.16312
| 2:56 | 4.7833 | -0.16255
| 2:56 | 4.7836 | -0.16198
| 2:56 | 4.7839 | -0.1614
| 2:56 | 4.7842 | -0.16082
| 2:56 | 4.7844 | -0.16024
| 2:56 | 4.7847 | -0.15966
| 2:56 | 4.785 | -0.15909
| 2:56 | 4.7853 | -0.15851
| 2:56 | 4.7856 | -0.15794
| 2:56 | 4.7858 | -0.15737
| 2:56 | 4.7861 | -0.1568
| 2:56 | 4.7864 | -0.15623
| 2:56 | 4.7867 | -0.15566
| 2:56 | 4.7869 | -0.15509
| 2:56 | 4.7872 | -0.15452
| 2:56 | 4.7875 | -0.15395
| 2:56 | 4.7878 | -0.15338
| 2:56 | 4.7881 | -0.15281
| 2:56 | 4.7883 | -0.15224
| 2:56 | 4.7886 | -0.15166
| 2:56 | 4.7889 | -0.15109
| 2:56 | 4.7892 | -0.15051
| 2:56 | 4.7894 | -0.14993
| 2:56 | 4.7897 | -0.14935
| 2:56 | 4.79 | -0.14877
| 2:56 | 4.7903 | -0.14819
| 2:56 | 4.7906 | -0.14761
| 2:56 | 4.7908 | -0.14703
| 2:56 | 4.7911 | -0.14645
| 2:56 | 4.7914 | -0.14586
| 2:56 | 4.7917 | -0.14527
| 2:56 | 4.7919 | -0.14469
| 2:56 | 4.7922 | -0.1441
| 2:56 | 4.7925 | -0.14351
| 2:56 | 4.7928 | -0.14293
| 2:56 | 4.7931 | -0.14235
| 2:56 | 4.7933 | -0.14179
| 2:56 | 4.7936 | -0.14124
| 2:56 | 4.7939 | -0.14069
| 2:56 | 4.7942 | -0.14014
| 2:56 | 4.7944 | -0.1396
| 2:56 | 4.7947 | -0.13905
| 2:56 | 4.795 | -0.13851
| 2:57 | 4.7953 | -0.13797
| 2:57 | 4.7956 | -0.13744
| 2:57 | 4.7958 | -0.13692
| 2:57 | 4.7961 | -0.1364
| 2:57 | 4.7964 | -0.13589
| 2:57 | 4.7967 | -0.13538
| 2:57 | 4.7969 | -0.13487
| 2:57 | 4.7972 | -0.13437
| 2:57 | 4.7975 | -0.13387
| 2:57 | 4.7978 | -0.13336
| 2:57 | 4.7981 | -0.13286
| 2:57 | 4.7983 | -0.13237
| 2:57 | 4.7986 | -0.13187
| 2:57 | 4.7989 | -0.13138
| 2:57 | 4.7992 | -0.13089
| 2:57 | 4.7994 | -0.13039
| 2:57 | 4.7997 | -0.12988
| 2:57 | 4.8 | -0.12937
| 2:57 | 4.8003 | -0.12886
| 2:57 | 4.8006 | -0.12834
| 2:57 | 4.8008 | -0.12782
| 2:57 | 4.8011 | -0.1273
| 2:57 | 4.8014 | -0.12678
| 2:57 | 4.8017 | -0.12625
| 2:57 | 4.8019 | -0.12573
| 2:57 | 4.8022 | -0.1252
| 2:57 | 4.8025 | -0.12467
| 2:57 | 4.8028 | -0.12414
| 2:57 | 4.8031 | -0.12362
| 2:57 | 4.8033 | -0.12309
| 2:57 | 4.8036 | -0.12258
| 2:57 | 4.8039 | -0.12207
| 2:57 | 4.8042 | -0.12157
| 2:57 | 4.8044 | -0.12107
| 2:57 | 4.8047 | -0.12058
| 2:57 | 4.805 | -0.12008
| 2:57 | 4.8053 | -0.11959
| 2:57 | 4.8056 | -0.11908
| 2:57 | 4.8058 | -0.11858
| 2:57 | 4.8061 | -0.11807
| 2:57 | 4.8064 | -0.11756
| 2:57 | 4.8067 | -0.11705
| 2:57 | 4.8069 | -0.11653
| 2:57 | 4.8072 | -0.11602
| 2:57 | 4.8075 | -0.11551
| 2:57 | 4.8078 | -0.11501
| 2:57 | 4.8081 | -0.11451
| 2:57 | 4.8083 | -0.11403
| 2:57 | 4.8086 | -0.11354
| 2:57 | 4.8089 | -0.11304
| 2:57 | 4.8092 | -0.11255
| 2:57 | 4.8094 | -0.11205
| 2:57 | 4.8097 | -0.11155
| 2:57 | 4.81 | -0.11104
| 2:57 | 4.8103 | -0.11053
| 2:57 | 4.8106 | -0.11002
| 2:57 | 4.8108 | -0.10951
| 2:57 | 4.8111 | -0.109
| 2:57 | 4.8114 | -0.10848
| 2:58 | 4.8117 | -0.10796
| 2:58 | 4.8119 | -0.10744
| 2:58 | 4.8122 | -0.10689
| 2:58 | 4.8125 | -0.10633
| 2:58 | 4.8128 | -0.10577
| 2:58 | 4.8131 | -0.10521
| 2:58 | 4.8133 | -0.10465
| 2:58 | 4.8136 | -0.10409
| 2:58 | 4.8139 | -0.10353
| 2:58 | 4.8142 | -0.10298
| 2:58 | 4.8144 | -0.10243
| 2:58 | 4.8147 | -0.10188
| 2:58 | 4.815 | -0.10134
| 2:58 | 4.8153 | -0.10079
| 2:58 | 4.8156 | -0.10025
| 2:58 | 4.8158 | -0.099716
| 2:58 | 4.8161 | -0.099178
| 2:58 | 4.8164 | -0.098639
| 2:58 | 4.8167 | -0.0981
| 2:58 | 4.8169 | -0.09756
| 2:58 | 4.8172 | -0.097017
| 2:58 | 4.8175 | -0.096474
| 2:58 | 4.8178 | -0.095931
| 2:58 | 4.8181 | -0.095386
| 2:58 | 4.8183 | -0.094841
| 2:58 | 4.8186 | -0.094296
| 2:58 | 4.8189 | -0.09375
| 2:58 | 4.8192 | -0.093203
| 2:58 | 4.8194 | -0.092656
| 2:58 | 4.8197 | -0.092108
| 2:58 | 4.82 | -0.09156
| 2:58 | 4.8203 | -0.091011
| 2:58 | 4.8206 | -0.090459
| 2:58 | 4.8208 | -0.089907
| 2:58 | 4.8211 | -0.089354
| 2:58 | 4.8214 | -0.08879
| 2:58 | 4.8217 | -0.088227
| 2:58 | 4.8219 | -0.087665
| 2:58 | 4.8222 | -0.087103
| 2:58 | 4.8225 | -0.086542
| 2:58 | 4.8228 | -0.085982
| 2:58 | 4.8231 | -0.085423
| 2:58 | 4.8233 | -0.084864
| 2:58 | 4.8236 | -0.084305
| 2:58 | 4.8239 | -0.083749
| 2:58 | 4.8242 | -0.0832
| 2:58 | 4.8244 | -0.082653
| 2:58 | 4.8247 | -0.082108
| 2:58 | 4.825 | -0.081566
| 2:58 | 4.8253 | -0.081026
| 2:58 | 4.8256 | -0.080488
| 2:58 | 4.8258 | -0.079952
| 2:58 | 4.8261 | -0.079416
| 2:58 | 4.8264 | -0.078877
| 2:58 | 4.8267 | -0.078336
| 2:58 | 4.8269 | -0.077793
| 2:58 | 4.8272 | -0.077248
| 2:58 | 4.8275 | -0.0767
| 2:58 | 4.8278 | -0.076151
| 2:58 | 4.8281 | -0.075602
| 2:58 | 4.8283 | -0.075057
| 2:59 | 4.8286 | -0.074514
| 2:59 | 4.8289 | -0.073974
| 2:59 | 4.8292 | -0.073437
| 2:59 | 4.8294 | -0.072902
| 2:59 | 4.8297 | -0.072366
| 2:59 | 4.83 | -0.071831
| 2:59 | 4.8303 | -0.071295
| 2:59 | 4.8306 | -0.070758
| 2:59 | 4.8308 | -0.070221
| 2:59 | 4.8311 | -0.069684
| 2:59 | 4.8314 | -0.069146
| 2:59 | 4.8317 | -0.068608
| 2:59 | 4.8319 | -0.06807
| 2:59 | 4.8322 | -0.067531
| 2:59 | 4.8325 | -0.066993
| 2:59 | 4.8328 | -0.066454
| 2:59 | 4.8331 | -0.065913
| 2:59 | 4.8333 | -0.065352
| 2:59 | 4.8336 | -0.06478
| 2:59 | 4.8339 | -0.064203
| 2:59 | 4.8342 | -0.063628
| 2:59 | 4.8344 | -0.063058
| 2:59 | 4.8347 | -0.062497
| 2:59 | 4.835 | -0.061934
| 2:59 | 4.8353 | -0.061371
| 2:59 | 4.8356 | -0.060805
| 2:59 | 4.8358 | -0.060237
| 2:59 | 4.8361 | -0.059669
| 2:59 | 4.8364 | -0.0591
| 2:59 | 4.8367 | -0.05853
| 2:59 | 4.8369 | -0.057959
| 2:59 | 4.8372 | -0.057388
| 2:59 | 4.8375 | -0.056815
| 2:59 | 4.8378 | -0.056242
| 2:59 | 4.8381 | -0.055667
| 2:59 | 4.8383 | -0.055088
| 2:59 | 4.8386 | -0.054504
| 2:59 | 4.8389 | -0.053915
| 2:59 | 4.8392 | -0.053322
| 2:59 | 4.8394 | -0.052724
| 2:59 | 4.8397 | -0.052121
| 2:59 | 4.84 | -0.051513
| 2:59 | 4.8403 | -0.050905
| 2:59 | 4.8406 | -0.050307
| 2:59 | 4.8408 | -0.049728
| 2:59 | 4.8411 | -0.049169
| 2:59 | 4.8414 | -0.048613
| 2:59 | 4.8417 | -0.048061
| 2:59 | 4.8419 | -0.047511
| 2:59 | 4.8422 | -0.046965
| 2:59 | 4.8425 | -0.046418
| 2:59 | 4.8428 | -0.04587
| 2:59 | 4.8431 | -0.045319
| 2:59 | 4.8433 | -0.044766
| 2:59 | 4.8436 | -0.044211
| 2:59 | 4.8439 | -0.043653
| 2:59 | 4.8442 | -0.043092
| 2:59 | 4.8444 | -0.042528
| 2:59 | 4.8447 | -0.041961
| 3:00 | 4.845 | -0.041393
| 3:00 | 4.8453 | -0.040822
| 3:00 | 4.8456 | -0.040242
| 3:00 | 4.8458 | -0.039655
| 3:00 | 4.8461 | -0.039063
| 3:00 | 4.8464 | -0.038465
| 3:00 | 4.8467 | -0.037865
| 3:00 | 4.8469 | -0.037264
| 3:00 | 4.8472 | -0.036663
| 3:00 | 4.8475 | -0.03606
| 3:00 | 4.8478 | -0.035456
| 3:00 | 4.8481 | -0.034852
| 3:00 | 4.8483 | -0.034247
| 3:00 | 4.8486 | -0.033641
| 3:00 | 4.8489 | -0.033035
| 3:00 | 4.8492 | -0.032425
| 3:00 | 4.8494 | -0.031808
| 3:00 | 4.8497 | -0.031191
| 3:00 | 4.85 | -0.030577
| 3:00 | 4.8503 | -0.029965
| 3:00 | 4.8506 | -0.029355
| 3:00 | 4.8508 | -0.028747
| 3:00 | 4.8511 | -0.028142
| 3:00 | 4.8514 | -0.027542
| 3:00 | 4.8517 | -0.026938
| 3:00 | 4.8519 | -0.02633
| 3:00 | 4.8522 | -0.025717
| 3:00 | 4.8525 | -0.025099
| 3:00 | 4.8528 | -0.024483
| 3:00 | 4.8531 | -0.023868
| 3:00 | 4.8533 | -0.023257
| 3:00 | 4.8536 | -0.022647
| 3:00 | 4.8539 | -0.02204
| 3:00 | 4.8542 | -0.021439
| 3:00 | 4.8544 | -0.020842
| 3:00 | 4.8547 | -0.020247
| 3:00 | 4.855 | -0.019649
| 3:00 | 4.8553 | -0.019047
| 3:00 | 4.8556 | -0.018443
| 3:00 | 4.8558 | -0.017835
| 3:00 | 4.8561 | -0.017224
| 3:00 | 4.8564 | -0.01661
| 3:00 | 4.8567 | -0.015993
| 3:00 | 4.8569 | -0.015371
| 3:00 | 4.8572 | -0.014742
| 3:00 | 4.8575 | -0.014106
| 3:00 | 4.8578 | -0.013461
| 3:00 | 4.8581 | -0.012807
| 3:00 | 4.8583 | -0.012153
| 3:00 | 4.8586 | -0.011499
| 3:00 | 4.8589 | -0.010845
| 3:00 | 4.8592 | -0.010192
| 3:00 | 4.8594 | -0.0095397
| 3:00 | 4.8597 | -0.0088882
| 3:00 | 4.86 | -0.0082374
| 3:00 | 4.8603 | -0.0075875
| 3:00 | 4.8606 | -0.0069384
| 3:00 | 4.8608 | -0.0062902
| 3:00 | 4.8611 | -0.0056427
| 3:00 | 4.8614 | -0.0049961
| 3:00 | 4.8617 | -0.0043503
| 3:01 | 4.8619 | -0.0037039
| 3:01 | 4.8622 | -0.0030575
| 3:01 | 4.8625 | -0.0024142
| 3:01 | 4.8628 | -0.0017786
| 3:01 | 4.8631 | -0.001149
| 3:01 | 4.8633 | -0.00052142
| 3:01 | 4.8636 | 0.00010409
| 3:01 | 4.8639 | 0.00072755
| 3:01 | 4.8642 | 0.0013489
| 3:01 | 4.8644 | 0.0019683
| 3:01 | 4.8647 | 0.0025856
| 3:01 | 4.865 | 0.0032008
| 3:01 | 4.8653 | 0.003814
| 3:01 | 4.8656 | 0.0044251
| 3:01 | 4.8658 | 0.0050356
| 3:01 | 4.8661 | 0.0056349
| 3:01 | 4.8664 | 0.0062271
| 3:01 | 4.8667 | 0.0068224
| 3:01 | 4.8669 | 0.007421
| 3:01 | 4.8672 | 0.0080228
| 3:01 | 4.8675 | 0.0086279
| 3:01 | 4.8678 | 0.0092361
| 3:01 | 4.8681 | 0.0098449
| 3:01 | 4.8683 | 0.010454
| 3:01 | 4.8686 | 0.011065
| 3:01 | 4.8689 | 0.011675
| 3:01 | 4.8692 | 0.012287
| 3:01 | 4.8694 | 0.012899
| 3:01 | 4.8697 | 0.013512
| 3:01 | 4.87 | 0.014125
| 3:01 | 4.8703 | 0.014739
| 3:01 | 4.8706 | 0.015356
| 3:01 | 4.8708 | 0.01598
| 3:01 | 4.8711 | 0.01661
| 3:01 | 4.8714 | 0.017239
| 3:01 | 4.8717 | 0.017866
| 3:01 | 4.8719 | 0.018492
| 3:01 | 4.8722 | 0.019117
| 3:01 | 4.8725 | 0.019741
| 3:01 | 4.8728 | 0.020363
| 3:01 | 4.8731 | 0.020984
| 3:01 | 4.8733 | 0.021604
| 3:01 | 4.8736 | 0.022222
| 3:01 | 4.8739 | 0.022839
| 3:01 | 4.8742 | 0.023455
| 3:01 | 4.8744 | 0.024071
| 3:01 | 4.8747 | 0.024688
| 3:01 | 4.875 | 0.025306
| 3:01 | 4.8753 | 0.025925
| 3:01 | 4.8756 | 0.026546
| 3:01 | 4.8758 | 0.027168
| 3:01 | 4.8761 | 0.027791
| 3:01 | 4.8764 | 0.028416
| 3:01 | 4.8767 | 0.029042
| 3:01 | 4.8769 | 0.029674
| 3:01 | 4.8772 | 0.03031
| 3:01 | 4.8775 | 0.03095
| 3:01 | 4.8778 | 0.031592
| 3:01 | 4.8781 | 0.032238
| 3:02 | 4.8783 | 0.03289
| 3:02 | 4.8786 | 0.033542
| 3:02 | 4.8789 | 0.034193
| 3:02 | 4.8792 | 0.034842
| 3:02 | 4.8794 | 0.035486
| 3:02 | 4.8797 | 0.036124
| 3:02 | 4.88 | 0.036762
| 3:02 | 4.8803 | 0.037402
| 3:02 | 4.8806 | 0.038042
| 3:02 | 4.8808 | 0.038683
| 3:02 | 4.8811 | 0.039325
| 3:02 | 4.8814 | 0.039968
| 3:02 | 4.8817 | 0.040611
| 3:02 | 4.8819 | 0.041255
| 3:02 | 4.8822 | 0.041901
| 3:02 | 4.8825 | 0.042546
| 3:02 | 4.8828 | 0.043193
| 3:02 | 4.8831 | 0.043841
| 3:02 | 4.8833 | 0.044489
| 3:02 | 4.8836 | 0.04514
| 3:02 | 4.8839 | 0.045793
| 3:02 | 4.8842 | 0.046446
| 3:02 | 4.8844 | 0.047099
| 3:02 | 4.8847 | 0.047754
| 3:02 | 4.885 | 0.048409
| 3:02 | 4.8853 | 0.049065
| 3:02 | 4.8856 | 0.049722
| 3:02 | 4.8858 | 0.050379
| 3:02 | 4.8861 | 0.051036
| 3:02 | 4.8864 | 0.051691
| 3:02 | 4.8867 | 0.052346
| 3:02 | 4.8869 | 0.053
| 3:02 | 4.8872 | 0.053653
| 3:02 | 4.8875 | 0.054305
| 3:02 | 4.8878 | 0.054957
| 3:02 | 4.8881 | 0.055607
| 3:02 | 4.8883 | 0.056256
| 3:02 | 4.8886 | 0.056901
| 3:02 | 4.8889 | 0.057544
| 3:02 | 4.8892 | 0.058184
| 3:02 | 4.8894 | 0.058822
| 3:02 | 4.8897 | 0.059457
| 3:02 | 4.89 | 0.060089
| 3:02 | 4.8903 | 0.060719
| 3:02 | 4.8906 | 0.061349
| 3:02 | 4.8908 | 0.061978
| 3:02 | 4.8911 | 0.062607
| 3:02 | 4.8914 | 0.063234
| 3:02 | 4.8917 | 0.063861
| 3:02 | 4.8919 | 0.064488
| 3:02 | 4.8922 | 0.065116
| 3:02 | 4.8925 | 0.065743
| 3:02 | 4.8928 | 0.066369
| 3:02 | 4.8931 | 0.066994
| 3:02 | 4.8933 | 0.067619
| 3:02 | 4.8936 | 0.068243
| 3:02 | 4.8939 | 0.068866
| 3:02 | 4.8942 | 0.069488
| 3:02 | 4.8944 | 0.070104
| 3:02 | 4.8947 | 0.07072
| 3:02 | 4.895 | 0.071336
| 3:03 | 4.8953 | 0.071952
| 3:03 | 4.8956 | 0.072568
| 3:03 | 4.8958 | 0.073185
| 3:03 | 4.8961 | 0.073801
| 3:03 | 4.8964 | 0.074418
| 3:03 | 4.8967 | 0.075035
| 3:03 | 4.8969 | 0.075652
| 3:03 | 4.8972 | 0.076269
| 3:03 | 4.8975 | 0.076886
| 3:03 | 4.8978 | 0.077503
| 3:03 | 4.8981 | 0.07812
| 3:03 | 4.8983 | 0.078738
| 3:03 | 4.8986 | 0.079356
| 3:03 | 4.8989 | 0.079973
| 3:03 | 4.8992 | 0.080591
| 3:03 | 4.8994 | 0.081209
| 3:03 | 4.8997 | 0.081827
| 3:03 | 4.9 | 0.082445
| 3:03 | 4.9003 | 0.083064
| 3:03 | 4.9006 | 0.083682
| 3:03 | 4.9008 | 0.084284
| 3:03 | 4.9011 | 0.084888
| 3:03 | 4.9014 | 0.085496
| 3:03 | 4.9017 | 0.086117
| 3:03 | 4.9019 | 0.086745
| 3:03 | 4.9022 | 0.087375
| 3:03 | 4.9025 | 0.088007
| 3:03 | 4.9028 | 0.088642
| 3:03 | 4.9031 | 0.08928
| 3:03 | 4.9033 | 0.08992
| 3:03 | 4.9036 | 0.090563
| 3:03 | 4.9039 | 0.091212
| 3:03 | 4.9042 | 0.091868
| 3:03 | 4.9044 | 0.092529
| 3:03 | 4.9047 | 0.09319
| 3:03 | 4.905 | 0.093849
| 3:03 | 4.9053 | 0.094504
| 3:03 | 4.9056 | 0.095155
| 3:03 | 4.9058 | 0.095804
| 3:03 | 4.9061 | 0.096449
| 3:03 | 4.9064 | 0.097091
| 3:03 | 4.9067 | 0.09773
| 3:03 | 4.9069 | 0.098367
| 3:03 | 4.9072 | 0.099006
| 3:03 | 4.9075 | 0.099643
| 3:03 | 4.9078 | 0.10028
| 3:03 | 4.9081 | 0.10091
| 3:03 | 4.9083 | 0.10155
| 3:03 | 4.9086 | 0.10218
| 3:03 | 4.9089 | 0.10282
| 3:03 | 4.9092 | 0.10345
| 3:03 | 4.9094 | 0.10409
| 3:03 | 4.9097 | 0.10472
| 3:03 | 4.91 | 0.10535
| 3:03 | 4.9103 | 0.10598
| 3:03 | 4.9106 | 0.10662
| 3:03 | 4.9108 | 0.10725
| 3:03 | 4.9111 | 0.10788
| 3:03 | 4.9114 | 0.1085
| 3:04 | 4.9117 | 0.10913
| 3:04 | 4.9119 | 0.10976
| 3:04 | 4.9122 | 0.11039
| 3:04 | 4.9125 | 0.11103
| 3:04 | 4.9128 | 0.11167
| 3:04 | 4.9131 | 0.11231
| 3:04 | 4.9133 | 0.11296
| 3:04 | 4.9136 | 0.11359
| 3:04 | 4.9139 | 0.11423
| 3:04 | 4.9142 | 0.11486
| 3:04 | 4.9144 | 0.11549
| 3:04 | 4.9147 | 0.11611
| 3:04 | 4.915 | 0.11674
| 3:04 | 4.9153 | 0.11736
| 3:04 | 4.9156 | 0.11797
| 3:04 | 4.9158 | 0.11859
| 3:04 | 4.9161 | 0.1192
| 3:04 | 4.9164 | 0.11981
| 3:04 | 4.9167 | 0.12043
| 3:04 | 4.9169 | 0.12105
| 3:04 | 4.9172 | 0.12167
| 3:04 | 4.9175 | 0.12229
| 3:04 | 4.9178 | 0.12291
| 3:04 | 4.9181 | 0.12353
| 3:04 | 4.9183 | 0.12415
| 3:04 | 4.9186 | 0.12478
| 3:04 | 4.9189 | 0.1254
| 3:04 | 4.9192 | 0.12603
| 3:04 | 4.9194 | 0.12666
| 3:04 | 4.9197 | 0.12728
| 3:04 | 4.92 | 0.1279
| 3:04 | 4.9203 | 0.12851
| 3:04 | 4.9206 | 0.12912
| 3:04 | 4.9208 | 0.12973
| 3:04 | 4.9211 | 0.13033
| 3:04 | 4.9214 | 0.13093
| 3:04 | 4.9217 | 0.13152
| 3:04 | 4.9219 | 0.13211
| 3:04 | 4.9222 | 0.1327
| 3:04 | 4.9225 | 0.13328
| 3:04 | 4.9228 | 0.13386
| 3:04 | 4.9231 | 0.13444
| 3:04 | 4.9233 | 0.13501
| 3:04 | 4.9236 | 0.13559
| 3:04 | 4.9239 | 0.13616
| 3:04 | 4.9242 | 0.13674
| 3:04 | 4.9244 | 0.13732
| 3:04 | 4.9247 | 0.1379
| 3:04 | 4.925 | 0.13849
| 3:04 | 4.9253 | 0.13908
| 3:04 | 4.9256 | 0.13968
| 3:04 | 4.9258 | 0.1403
| 3:04 | 4.9261 | 0.14091
| 3:04 | 4.9264 | 0.14151
| 3:04 | 4.9267 | 0.14212
| 3:04 | 4.9269 | 0.14273
| 3:04 | 4.9272 | 0.14334
| 3:04 | 4.9275 | 0.14397
| 3:04 | 4.9278 | 0.14459
| 3:04 | 4.9281 | 0.14522
| 3:04 | 4.9283 | 0.14585
| 3:05 | 4.9286 | 0.14649
| 3:05 | 4.9289 | 0.14714
| 3:05 | 4.9292 | 0.1478
| 3:05 | 4.9294 | 0.14847
| 3:05 | 4.9297 | 0.14913
| 3:05 | 4.93 | 0.1498
| 3:05 | 4.9303 | 0.15046
| 3:05 | 4.9306 | 0.15113
| 3:05 | 4.9308 | 0.15179
| 3:05 | 4.9311 | 0.15245
| 3:05 | 4.9314 | 0.15312
| 3:05 | 4.9317 | 0.15378
| 3:05 | 4.9319 | 0.15444
| 3:05 | 4.9322 | 0.1551
| 3:05 | 4.9325 | 0.15576
| 3:05 | 4.9328 | 0.15643
| 3:05 | 4.9331 | 0.15709
| 3:05 | 4.9333 | 0.15775
| 3:05 | 4.9336 | 0.15841
| 3:05 | 4.9339 | 0.15906
| 3:05 | 4.9342 | 0.15971
| 3:05 | 4.9344 | 0.16036
| 3:05 | 4.9347 | 0.16101
| 3:05 | 4.935 | 0.16166
| 3:05 | 4.9353 | 0.16231
| 3:05 | 4.9356 | 0.16296
| 3:05 | 4.9358 | 0.16362
| 3:05 | 4.9361 | 0.16427
| 3:05 | 4.9364 | 0.16492
| 3:05 | 4.9367 | 0.16558
| 3:05 | 4.9369 | 0.16623
| 3:05 | 4.9372 | 0.16691
| 3:05 | 4.9375 | 0.1676
| 3:05 | 4.9378 | 0.1683
| 3:05 | 4.9381 | 0.16899
| 3:05 | 4.9383 | 0.16969
| 3:05 | 4.9386 | 0.17038
| 3:05 | 4.9389 | 0.17107
| 3:05 | 4.9392 | 0.17175
| 3:05 | 4.9394 | 0.17243
| 3:05 | 4.9397 | 0.1731
| 3:05 | 4.94 | 0.17377
| 3:05 | 4.9403 | 0.17444
| 3:05 | 4.9406 | 0.1751
| 3:05 | 4.9408 | 0.17576
| 3:05 | 4.9411 | 0.17641
| 3:05 | 4.9414 | 0.17704
| 3:05 | 4.9417 | 0.17767
| 3:05 | 4.9419 | 0.17828
| 3:05 | 4.9422 | 0.17889
| 3:05 | 4.9425 | 0.1795
| 3:05 | 4.9428 | 0.18011
| 3:05 | 4.9431 | 0.18072
| 3:05 | 4.9433 | 0.18133
| 3:05 | 4.9436 | 0.18193
| 3:05 | 4.9439 | 0.18253
| 3:05 | 4.9442 | 0.18311
| 3:05 | 4.9444 | 0.1837
| 3:05 | 4.9447 | 0.18428
| 3:05 | 4.945 | 0.18487
| 3:06 | 4.9453 | 0.18545
| 3:06 | 4.9456 | 0.18603
| 3:06 | 4.9458 | 0.18661
| 3:06 | 4.9461 | 0.18718
| 3:06 | 4.9464 | 0.18774
| 3:06 | 4.9467 | 0.18831
| 3:06 | 4.9469 | 0.18888
| 3:06 | 4.9472 | 0.18945
| 3:06 | 4.9475 | 0.19003
| 3:06 | 4.9478 | 0.19061
| 3:06 | 4.9481 | 0.19119
| 3:06 | 4.9483 | 0.19178
| 3:06 | 4.9486 | 0.19236
| 3:06 | 4.9489 | 0.19296
| 3:06 | 4.9492 | 0.19355
| 3:06 | 4.9494 | 0.19414
| 3:06 | 4.9497 | 0.19473
| 3:06 | 4.95 | 0.1953
| 3:06 | 4.9503 | 0.19586
| 3:06 | 4.9506 | 0.19642
| 3:06 | 4.9508 | 0.19696
| 3:06 | 4.9511 | 0.1975
| 3:06 | 4.9514 | 0.19802
| 3:06 | 4.9517 | 0.19854
| 3:06 | 4.9519 | 0.19906
| 3:06 | 4.9522 | 0.19956
| 3:06 | 4.9525 | 0.20006
| 3:06 | 4.9528 | 0.20057
| 3:06 | 4.9531 | 0.20106
| 3:06 | 4.9533 | 0.20156
| 3:06 | 4.9536 | 0.20206
| 3:06 | 4.9539 | 0.20256
| 3:06 | 4.9542 | 0.20306
| 3:06 | 4.9544 | 0.20356
| 3:06 | 4.9547 | 0.20406
| 3:06 | 4.955 | 0.20455
| 3:06 | 4.9553 | 0.20505
| 3:06 | 4.9556 | 0.20555
| 3:06 | 4.9558 | 0.20605
| 3:06 | 4.9561 | 0.20654
| 3:06 | 4.9564 | 0.20704
| 3:06 | 4.9567 | 0.20754
| 3:06 | 4.9569 | 0.20803
| 3:06 | 4.9572 | 0.20853
| 3:06 | 4.9575 | 0.20902
| 3:06 | 4.9578 | 0.20952
| 3:06 | 4.9581 | 0.21001
| 3:06 | 4.9583 | 0.2105
| 3:06 | 4.9586 | 0.211
| 3:06 | 4.9589 | 0.21149
| 3:06 | 4.9592 | 0.21198
| 3:06 | 4.9594 | 0.21247
| 3:06 | 4.9597 | 0.21296
| 3:06 | 4.96 | 0.21345
| 3:06 | 4.9603 | 0.21395
| 3:06 | 4.9606 | 0.21444
| 3:06 | 4.9608 | 0.21495
| 3:06 | 4.9611 | 0.21545
| 3:06 | 4.9614 | 0.21596
| 3:07 | 4.9617 | 0.21648
| 3:07 | 4.9619 | 0.21701
| 3:07 | 4.9622 | 0.21754
| 3:07 | 4.9625 | 0.21808
| 3:07 | 4.9628 | 0.21863
| 3:07 | 4.9631 | 0.21918
| 3:07 | 4.9633 | 0.21974
| 3:07 | 4.9636 | 0.2203
| 3:07 | 4.9639 | 0.22087
| 3:07 | 4.9642 | 0.22144
| 3:07 | 4.9644 | 0.22202
| 3:07 | 4.9647 | 0.2226
| 3:07 | 4.965 | 0.22319
| 3:07 | 4.9653 | 0.22378
| 3:07 | 4.9656 | 0.22437
| 3:07 | 4.9658 | 0.22497
| 3:07 | 4.9661 | 0.22557
| 3:07 | 4.9664 | 0.22618
| 3:07 | 4.9667 | 0.22678
| 3:07 | 4.9669 | 0.22739
| 3:07 | 4.9672 | 0.22801
| 3:07 | 4.9675 | 0.22863
| 3:07 | 4.9678 | 0.22925
| 3:07 | 4.9681 | 0.22986
| 3:07 | 4.9683 | 0.23046
| 3:07 | 4.9686 | 0.23106
| 3:07 | 4.9689 | 0.23164
| 3:07 | 4.9692 | 0.23221
| 3:07 | 4.9694 | 0.23276
| 3:07 | 4.9697 | 0.2333
| 3:07 | 4.97 | 0.23383
| 3:07 | 4.9703 | 0.23435
| 3:07 | 4.9706 | 0.23486
| 3:07 | 4.9708 | 0.23536
| 3:07 | 4.9711 | 0.23584
| 3:07 | 4.9714 | 0.23633
| 3:07 | 4.9717 | 0.23681
| 3:07 | 4.9719 | 0.23729
| 3:07 | 4.9722 | 0.23777
| 3:07 | 4.9725 | 0.23826
| 3:07 | 4.9728 | 0.23874
| 3:07 | 4.9731 | 0.23923
| 3:07 | 4.9733 | 0.23972
| 3:07 | 4.9736 | 0.2402
| 3:07 | 4.9739 | 0.24069
| 3:07 | 4.9742 | 0.24118
| 3:07 | 4.9744 | 0.24167
| 3:07 | 4.9747 | 0.24216
| 3:07 | 4.975 | 0.24265
| 3:07 | 4.9753 | 0.24315
| 3:07 | 4.9756 | 0.24366
| 3:07 | 4.9758 | 0.24419
| 3:07 | 4.9761 | 0.24472
| 3:07 | 4.9764 | 0.24527
| 3:07 | 4.9767 | 0.24583
| 3:07 | 4.9769 | 0.2464
| 3:07 | 4.9772 | 0.24696
| 3:07 | 4.9775 | 0.24753
| 3:07 | 4.9778 | 0.2481
| 3:07 | 4.9781 | 0.24866
| 3:08 | 4.9783 | 0.24923
| 3:08 | 4.9786 | 0.2498
| 3:08 | 4.9789 | 0.25036
| 3:08 | 4.9792 | 0.25093
| 3:08 | 4.9794 | 0.25099
| 3:08 | 4.9797 | 0.25106
| 3:08 | 4.98 | 0.25112
| 3:08 | 4.9803 | 0.25119
| 3:08 | 4.9806 | 0.25126
| 3:08 | 4.9808 | 0.25133
| 3:08 | 4.9811 | 0.25141
| 3:08 | 4.9814 | 0.25148
| 3:08 | 4.9817 | 0.25156
| 3:08 | 4.9819 | 0.25164
| 3:08 | 4.9822 | 0.25172
| 3:08 | 4.9825 | 0.25181
| 3:08 | 4.9828 | 0.25189
| 3:08 | 4.9831 | 0.25196
| 3:08 | 4.9833 | 0.25202
| 3:08 | 4.9836 | 0.25209
| 3:08 | 4.9839 | 0.25217
| 3:08 | 4.9842 | 0.25225
| 3:08 | 4.9844 | 0.25235
| 3:08 | 4.9847 | 0.25245
| 3:08 | 4.985 | 0.25256
| 3:08 | 4.9853 | 0.25267
| 3:08 | 4.9856 | 0.2528
| 3:08 | 4.9858 | 0.25295
| 3:08 | 4.9861 | 0.25309
| 3:08 | 4.9864 | 0.25322
| 3:08 | 4.9867 | 0.25332
| 3:08 | 4.9869 | 0.25343
| 3:08 | 4.9872 | 0.25354
| 3:08 | 4.9875 | 0.25365
| 3:08 | 4.9878 | 0.2538
| 3:08 | 4.9881 | 0.25397
| 3:08 | 4.9883 | 0.25415
| 3:08 | 4.9886 | 0.25434
| 3:08 | 4.9889 | 0.25454
| 3:08 | 4.9892 | 0.25476
| 3:08 | 4.9894 | 0.25498
| 3:08 | 4.9897 | 0.25522
| 3:08 | 4.99 | 0.25548
| 3:08 | 4.9903 | 0.25573
| 3:08 | 4.9906 | 0.25598
| 3:08 | 4.9908 | 0.25623
| 3:08 | 4.9911 | 0.25647
| 3:08 | 4.9914 | 0.25669
| 3:08 | 4.9917 | 0.25692
| 3:08 | 4.9919 | 0.25714
| 3:08 | 4.9922 | 0.25736
| 3:08 | 4.9925 | 0.25759
| 3:08 | 4.9928 | 0.25781
| 3:08 | 4.9931 | 0.25803
| 3:08 | 4.9933 | 0.25826
| 3:08 | 4.9936 | 0.25849
| 3:08 | 4.9939 | 0.25872
| 3:08 | 4.9942 | 0.25894
| 3:08 | 4.9944 | 0.25915
| 3:08 | 4.9947 | 0.25934
| 3:08 | 4.995 | 0.25952
| 3:09 | 4.9953 | 0.25968
| 3:09 | 4.9956 | 0.25982
| 3:09 | 4.9958 | 0.25997
| 3:09 | 4.9961 | 0.26012
| 3:09 | 4.9964 | 0.26029
| 3:09 | 4.9967 | 0.26047
| 3:09 | 4.9969 | 0.26065
| 3:09 | 4.9972 | 0.26084
| 3:09 | 4.9975 | 0.26103
| 3:09 | 4.9978 | 0.26122
| 3:09 | 4.9981 | 0.26142
| 3:09 | 4.9983 | 0.26163
| 3:09 | 4.9986 | 0.26184
| 3:09 | 4.9989 | 0.26205
| 3:09 | 4.9992 | 0.26227
| 3:09 | 4.9994 | 0.26249
| 3:09 | 4.9997 | 0.26271
| 3:09 | 5 | 0.26293
| 3:09 | 5.0003 | 0.26315
| 3:09 | 5.0006 | 0.26337
| 3:09 | 5.0008 | 0.26359
| 3:09 | 5.0011 | 0.26382
| 3:09 | 5.0014 | 0.26404
| 3:09 | 5.0017 | 0.26427
| 3:09 | 5.0019 | 0.26449
| 3:09 | 5.0022 | 0.2647
| 3:09 | 5.0025 | 0.26489
| 3:09 | 5.0028 | 0.26507
| 3:09 | 5.0031 | 0.26524
| 3:09 | 5.0033 | 0.2654
| 3:09 | 5.0036 | 0.26556
| 3:09 | 5.0039 | 0.26572
| 3:09 | 5.0042 | 0.26586
| 3:09 | 5.0044 | 0.26599
| 3:09 | 5.0047 | 0.26612
| 3:09 | 5.005 | 0.26626
| 3:09 | 5.0053 | 0.2664
| 3:09 | 5.0056 | 0.26656
| 3:09 | 5.0058 | 0.26672
| 3:09 | 5.0061 | 0.26689
| 3:09 | 5.0064 | 0.26707
| 3:09 | 5.0067 | 0.26727
| 3:09 | 5.0069 | 0.26746
| 3:09 | 5.0072 | 0.26767
| 3:09 | 5.0075 | 0.26787
| 3:09 | 5.0078 | 0.26808
| 3:09 | 5.0081 | 0.26828
| 3:09 | 5.0083 | 0.2685
| 3:09 | 5.0086 | 0.26872
| 3:09 | 5.0089 | 0.26894
| 3:09 | 5.0092 | 0.26917
| 3:09 | 5.0094 | 0.26939
| 3:09 | 5.0097 | 0.26961
| 3:09 | 5.01 | 0.26983
| 3:09 | 5.0103 | 0.27004
| 3:09 | 5.0106 | 0.27026
| 3:09 | 5.0108 | 0.27045
| 3:09 | 5.0111 | 0.27065
| 3:09 | 5.0114 | 0.27084
| 3:10 | 5.0117 | 0.27104
| 3:10 | 5.0119 | 0.27125
| 3:10 | 5.0122 | 0.27145
| 3:10 | 5.0125 | 0.27164
| 3:10 | 5.0128 | 0.27183
| 3:10 | 5.0131 | 0.27203
| 3:10 | 5.0133 | 0.27222
| 3:10 | 5.0136 | 0.27241
| 3:10 | 5.0139 | 0.27261
| 3:10 | 5.0142 | 0.27279
| 3:10 | 5.0144 | 0.27298
| 3:10 | 5.0147 | 0.27317
| 3:10 | 5.015 | 0.27335
| 3:10 | 5.0153 | 0.27353
| 3:10 | 5.0156 | 0.27371
| 3:10 | 5.0158 | 0.27388
| 3:10 | 5.0161 | 0.27403
| 3:10 | 5.0164 | 0.27416
| 3:10 | 5.0167 | 0.27428
| 3:10 | 5.0169 | 0.2744
| 3:10 | 5.0172 | 0.27452
| 3:10 | 5.0175 | 0.27465
| 3:10 | 5.0178 | 0.27478
| 3:10 | 5.0181 | 0.2749
| 3:10 | 5.0183 | 0.27502
| 3:10 | 5.0186 | 0.27513
| 3:10 | 5.0189 | 0.27523
| 3:10 | 5.0192 | 0.27533
| 3:10 | 5.0194 | 0.27542
| 3:10 | 5.0197 | 0.27549
| 3:10 | 5.02 | 0.27555
| 3:10 | 5.0203 | 0.27562
| 3:10 | 5.0206 | 0.27569
| 3:10 | 5.0208 | 0.27575
| 3:10 | 5.0211 | 0.2758
| 3:10 | 5.0214 | 0.27582
| 3:10 | 5.0217 | 0.27585
| 3:10 | 5.0219 | 0.27586
| 3:10 | 5.0222 | 0.27587
| 3:10 | 5.0225 | 0.27587
| 3:10 | 5.0228 | 0.27586
| 3:10 | 5.0231 | 0.27585
| 3:10 | 5.0233 | 0.27583
| 3:10 | 5.0236 | 0.2758
| 3:10 | 5.0239 | 0.27576
| 3:10 | 5.0242 | 0.27572
| 3:10 | 5.0244 | 0.27568
| 3:10 | 5.0247 | 0.27562
| 3:10 | 5.025 | 0.27555
| 3:10 | 5.0253 | 0.27549
| 3:10 | 5.0256 | 0.27543
| 3:10 | 5.0258 | 0.27539
| 3:10 | 5.0261 | 0.27536
| 3:10 | 5.0264 | 0.27534
| 3:10 | 5.0267 | 0.27533
| 3:10 | 5.0269 | 0.27534
| 3:10 | 5.0272 | 0.27535
| 3:10 | 5.0275 | 0.27538
| 3:10 | 5.0278 | 0.2754
| 3:10 | 5.0281 | 0.27542
| 3:10 | 5.0283 | 0.27544
| 3:11 | 5.0286 | 0.27545
| 3:11 | 5.0289 | 0.27545
| 3:11 | 5.0292 | 0.27545
| 3:11 | 5.0294 | 0.27544
| 3:11 | 5.0297 | 0.27543
| 3:11 | 5.03 | 0.27542
| 3:11 | 5.0303 | 0.2754
| 3:11 | 5.0306 | 0.27539
| 3:11 | 5.0308 | 0.27537
| 3:11 | 5.0311 | 0.27535
| 3:11 | 5.0314 | 0.27534
| 3:11 | 5.0317 | 0.27532
| 3:11 | 5.0319 | 0.27529
| 3:11 | 5.0322 | 0.27527
| 3:11 | 5.0325 | 0.27525
| 3:11 | 5.0328 | 0.27522
| 3:11 | 5.0331 | 0.27518
| 3:11 | 5.0333 | 0.27514
| 3:11 | 5.0336 | 0.27509
| 3:11 | 5.0339 | 0.27504
| 3:11 | 5.0342 | 0.27498
| 3:11 | 5.0344 | 0.27492
| 3:11 | 5.0347 | 0.27487
| 3:11 | 5.035 | 0.27481
| 3:11 | 5.0353 | 0.27476
| 3:11 | 5.0356 | 0.2747
| 3:11 | 5.0358 | 0.27465
| 3:11 | 5.0361 | 0.2746
| 3:11 | 5.0364 | 0.27453
| 3:11 | 5.0367 | 0.27445
| 3:11 | 5.0369 | 0.27437
| 3:11 | 5.0372 | 0.2743
| 3:11 | 5.0375 | 0.27422
| 3:11 | 5.0378 | 0.27414
| 3:11 | 5.0381 | 0.27406
| 3:11 | 5.0383 | 0.27398
| 3:11 | 5.0386 | 0.27391
| 3:11 | 5.0389 | 0.27383
| 3:11 | 5.0392 | 0.27376
| 3:11 | 5.0394 | 0.27369
| 3:11 | 5.0397 | 0.27362
| 3:11 | 5.04 | 0.27355
| 3:11 | 5.0403 | 0.27348
| 3:11 | 5.0406 | 0.27341
| 3:11 | 5.0408 | 0.27335
| 3:11 | 5.0411 | 0.27328
| 3:11 | 5.0414 | 0.27322
| 3:11 | 5.0417 | 0.27317
| 3:11 | 5.0419 | 0.27311
| 3:11 | 5.0422 | 0.27305
| 3:11 | 5.0425 | 0.27298
| 3:11 | 5.0428 | 0.27291
| 3:11 | 5.0431 | 0.27284
| 3:11 | 5.0433 | 0.2728
| 3:11 | 5.0436 | 0.27275
| 3:11 | 5.0439 | 0.27272
| 3:11 | 5.0442 | 0.27268
| 3:11 | 5.0444 | 0.27265
| 3:11 | 5.0447 | 0.27262
| 3:12 | 5.045 | 0.27259
| 3:12 | 5.0453 | 0.27257
| 3:12 | 5.0456 | 0.27258
| 3:12 | 5.0458 | 0.27261
| 3:12 | 5.0461 | 0.27269
| 3:12 | 5.0464 | 0.27278
| 3:12 | 5.0467 | 0.27287
| 3:12 | 5.0469 | 0.27297
| 3:12 | 5.0472 | 0.27306
| 3:12 | 5.0475 | 0.27316
| 3:12 | 5.0478 | 0.27326
| 3:12 | 5.0481 | 0.27336
| 3:12 | 5.0483 | 0.27345
| 3:12 | 5.0486 | 0.27355
| 3:12 | 5.0489 | 0.27365
| 3:12 | 5.0492 | 0.27375
| 3:12 | 5.0494 | 0.27385
| 3:12 | 5.0497 | 0.27393
| 3:12 | 5.05 | 0.27401
| 3:12 | 5.0503 | 0.27409
| 3:12 | 5.0506 | 0.27416
| 3:12 | 5.0508 | 0.27423
| 3:12 | 5.0511 | 0.27427
| 3:12 | 5.0514 | 0.27431
| 3:12 | 5.0517 | 0.27434
| 3:12 | 5.0519 | 0.27437
| 3:12 | 5.0522 | 0.27439
| 3:12 | 5.0525 | 0.27441
| 3:12 | 5.0528 | 0.27443
| 3:12 | 5.0531 | 0.27444
| 3:12 | 5.0533 | 0.27446
| 3:12 | 5.0536 | 0.27448
| 3:12 | 5.0539 | 0.2745
| 3:12 | 5.0542 | 0.27453
| 3:12 | 5.0544 | 0.27457
| 3:12 | 5.0547 | 0.27462
| 3:12 | 5.055 | 0.27466
| 3:12 | 5.0553 | 0.27471
| 3:12 | 5.0556 | 0.27475
| 3:12 | 5.0558 | 0.27481
| 3:12 | 5.0561 | 0.27486
| 3:12 | 5.0564 | 0.27492
| 3:12 | 5.0567 | 0.27498
| 3:12 | 5.0569 | 0.27505
| 3:12 | 5.0572 | 0.27512
| 3:12 | 5.0575 | 0.27521
| 3:12 | 5.0578 | 0.2753
| 3:12 | 5.0581 | 0.27539
| 3:12 | 5.0583 | 0.2755
| 3:12 | 5.0586 | 0.27559
| 3:12 | 5.0589 | 0.27568
| 3:12 | 5.0592 | 0.27576
| 3:12 | 5.0594 | 0.27584
| 3:12 | 5.0597 | 0.27591
| 3:12 | 5.06 | 0.27596
| 3:12 | 5.0603 | 0.27601
| 3:12 | 5.0606 | 0.27603
| 3:12 | 5.0608 | 0.27605
| 3:12 | 5.0611 | 0.27606
| 3:12 | 5.0614 | 0.2761
| 3:12 | 5.0617 | 0.27615
| 3:13 | 5.0619 | 0.2762
| 3:13 | 5.0622 | 0.27623
| 3:13 | 5.0625 | 0.27625
| 3:13 | 5.0628 | 0.27626
| 3:13 | 5.0631 | 0.27627
| 3:13 | 5.0633 | 0.27628
| 3:13 | 5.0636 | 0.2763
| 3:13 | 5.0639 | 0.27631
| 3:13 | 5.0642 | 0.27634
| 3:13 | 5.0644 | 0.27636
| 3:13 | 5.0647 | 0.27638
| 3:13 | 5.065 | 0.27641
| 3:13 | 5.0653 | 0.27644
| 3:13 | 5.0656 | 0.27648
| 3:13 | 5.0658 | 0.27651
| 3:13 | 5.0661 | 0.27652
| 3:13 | 5.0664 | 0.27653
| 3:13 | 5.0667 | 0.27655
| 3:13 | 5.0669 | 0.27658
| 3:13 | 5.0672 | 0.27661
| 3:13 | 5.0675 | 0.27665
| 3:13 | 5.0678 | 0.27669
| 3:13 | 5.0681 | 0.27676
| 3:13 | 5.0683 | 0.27684
| 3:13 | 5.0686 | 0.27691
| 3:13 | 5.0689 | 0.27698
| 3:13 | 5.0692 | 0.27703
| 3:13 | 5.0694 | 0.27705
| 3:13 | 5.0697 | 0.27707
| 3:13 | 5.07 | 0.27708
| 3:13 | 5.0703 | 0.27709
| 3:13 | 5.0706 | 0.2771
| 3:13 | 5.0708 | 0.2771
| 3:13 | 5.0711 | 0.27709
| 3:13 | 5.0714 | 0.27706
| 3:13 | 5.0717 | 0.27704
| 3:13 | 5.0719 | 0.27702
| 3:13 | 5.0722 | 0.27701
| 3:13 | 5.0725 | 0.27701
| 3:13 | 5.0728 | 0.27702
| 3:13 | 5.0731 | 0.27702
| 3:13 | 5.0733 | 0.27704
| 3:13 | 5.0736 | 0.27706
| 3:13 | 5.0739 | 0.27709
| 3:13 | 5.0742 | 0.27714
| 3:13 | 5.0744 | 0.2772
| 3:13 | 5.0747 | 0.27727
| 3:13 | 5.075 | 0.27735
| 3:13 | 5.0753 | 0.27742
| 3:13 | 5.0756 | 0.27751
| 3:13 | 5.0758 | 0.27759
| 3:13 | 5.0761 | 0.27768
| 3:13 | 5.0764 | 0.27777
| 3:13 | 5.0767 | 0.27785
| 3:13 | 5.0769 | 0.27794
| 3:13 | 5.0772 | 0.27802
| 3:13 | 5.0775 | 0.2781
| 3:13 | 5.0778 | 0.27816
| 3:13 | 5.0781 | 0.27822
| 3:14 | 5.0783 | 0.27829
| 3:14 | 5.0786 | 0.27836
| 3:14 | 5.0789 | 0.27843
| 3:14 | 5.0792 | 0.27851
| 3:14 | 5.0794 | 0.27858
| 3:14 | 5.0797 | 0.27866
| 3:14 | 5.08 | 0.27873
| 3:14 | 5.0803 | 0.2788
| 3:14 | 5.0806 | 0.27887
| 3:14 | 5.0808 | 0.27893
| 3:14 | 5.0811 | 0.27899
| 3:14 | 5.0814 | 0.27904
| 3:14 | 5.0817 | 0.2791
| 3:14 | 5.0819 | 0.27914
| 3:14 | 5.0822 | 0.27919
| 3:14 | 5.0825 | 0.27923
| 3:14 | 5.0828 | 0.27928
| 3:14 | 5.0831 | 0.27934
| 3:14 | 5.0833 | 0.27938
| 3:14 | 5.0836 | 0.27941
| 3:14 | 5.0839 | 0.27944
| 3:14 | 5.0842 | 0.27946
| 3:14 | 5.0844 | 0.27949
| 3:14 | 5.0847 | 0.27952
| 3:14 | 5.085 | 0.27956
| 3:14 | 5.0853 | 0.27959
| 3:14 | 5.0856 | 0.27962
| 3:14 | 5.0858 | 0.27965
| 3:14 | 5.0861 | 0.27967
| 3:14 | 5.0864 | 0.27969
| 3:14 | 5.0867 | 0.2797
| 3:14 | 5.0869 | 0.2797
| 3:14 | 5.0872 | 0.2797
| 3:14 | 5.0875 | 0.27968
| 3:14 | 5.0878 | 0.27965
| 3:14 | 5.0881 | 0.27961
| 3:14 | 5.0883 | 0.27956
| 3:14 | 5.0886 | 0.27951
| 3:14 | 5.0889 | 0.27944
| 3:14 | 5.0892 | 0.27936
| 3:14 | 5.0894 | 0.27927
| 3:14 | 5.0897 | 0.27917
| 3:14 | 5.09 | 0.27907
| 3:14 | 5.0903 | 0.27896
| 3:14 | 5.0906 | 0.27885
| 3:14 | 5.0908 | 0.27874
| 3:14 | 5.0911 | 0.27865
| 3:14 | 5.0914 | 0.27856
| 3:14 | 5.0917 | 0.27846
| 3:14 | 5.0919 | 0.27836
| 3:14 | 5.0922 | 0.27827
| 3:14 | 5.0925 | 0.27817
| 3:14 | 5.0928 | 0.27806
| 3:14 | 5.0931 | 0.27795
| 3:14 | 5.0933 | 0.27782
| 3:14 | 5.0936 | 0.27769
| 3:14 | 5.0939 | 0.27755
| 3:14 | 5.0942 | 0.27741
| 3:14 | 5.0944 | 0.27728
| 3:14 | 5.0947 | 0.27714
| 3:14 | 5.095 | 0.277
| 3:15 | 5.0953 | 0.27686
| 3:15 | 5.0956 | 0.27671
| 3:15 | 5.0958 | 0.27656
| 3:15 | 5.0961 | 0.27641
| 3:15 | 5.0964 | 0.27626
| 3:15 | 5.0967 | 0.27611
| 3:15 | 5.0969 | 0.27596
| 3:15 | 5.0972 | 0.27582
| 3:15 | 5.0975 | 0.27568
| 3:15 | 5.0978 | 0.27554
| 3:15 | 5.0981 | 0.27541
| 3:15 | 5.0983 | 0.27528
| 3:15 | 5.0986 | 0.27515
| 3:15 | 5.0989 | 0.27503
| 3:15 | 5.0992 | 0.27491
| 3:15 | 5.0994 | 0.27479
| 3:15 | 5.0997 | 0.27467
| 3:15 | 5.1 | 0.27456
| 3:15 | 5.1003 | 0.27445
| 3:15 | 5.1006 | 0.27435
| 3:15 | 5.1008 | 0.27422
| 3:15 | 5.1011 | 0.27409
| 3:15 | 5.1014 | 0.27395
| 3:15 | 5.1017 | 0.2738
| 3:15 | 5.1019 | 0.27363
| 3:15 | 5.1022 | 0.27344
| 3:15 | 5.1025 | 0.27323
| 3:15 | 5.1028 | 0.27302
| 3:15 | 5.1031 | 0.27282
| 3:15 | 5.1033 | 0.27263
| 3:15 | 5.1036 | 0.27244
| 3:15 | 5.1039 | 0.27226
| 3:15 | 5.1042 | 0.27207
| 3:15 | 5.1044 | 0.27189
| 3:15 | 5.1047 | 0.27171
| 3:15 | 5.105 | 0.27153
| 3:15 | 5.1053 | 0.27134
| 3:15 | 5.1056 | 0.27114
| 3:15 | 5.1058 | 0.27094
| 3:15 | 5.1061 | 0.27073
| 3:15 | 5.1064 | 0.27052
| 3:15 | 5.1067 | 0.2703
| 3:15 | 5.1069 | 0.27009
| 3:15 | 5.1072 | 0.2699
| 3:15 | 5.1075 | 0.26972
| 3:15 | 5.1078 | 0.26953
| 3:15 | 5.1081 | 0.26936
| 3:15 | 5.1083 | 0.26921
| 3:15 | 5.1086 | 0.26906
| 3:15 | 5.1089 | 0.26892
| 3:15 | 5.1092 | 0.26879
| 3:15 | 5.1094 | 0.26866
| 3:15 | 5.1097 | 0.26853
| 3:15 | 5.11 | 0.26839
| 3:15 | 5.1103 | 0.26826
| 3:15 | 5.1106 | 0.26813
| 3:15 | 5.1108 | 0.26799
| 3:15 | 5.1111 | 0.26786
| 3:15 | 5.1114 | 0.26773
| 3:15 | 5.1117 | 0.26759
| 3:16 | 5.1119 | 0.26746
| 3:16 | 5.1122 | 0.26731
| 3:16 | 5.1125 | 0.26716
| 3:16 | 5.1128 | 0.26701
| 3:16 | 5.1131 | 0.26685
| 3:16 | 5.1133 | 0.2667
| 3:16 | 5.1136 | 0.26654
| 3:16 | 5.1139 | 0.26637
| 3:16 | 5.1142 | 0.26621
| 3:16 | 5.1144 | 0.26604
| 3:16 | 5.1147 | 0.26587
| 3:16 | 5.115 | 0.26569
| 3:16 | 5.1153 | 0.26551
| 3:16 | 5.1156 | 0.26533
| 3:16 | 5.1158 | 0.26515
| 3:16 | 5.1161 | 0.26498
| 3:16 | 5.1164 | 0.26482
| 3:16 | 5.1167 | 0.26466
| 3:16 | 5.1169 | 0.2645
| 3:16 | 5.1172 | 0.26435
| 3:16 | 5.1175 | 0.2642
| 3:16 | 5.1178 | 0.26405
| 3:16 | 5.1181 | 0.2639
| 3:16 | 5.1183 | 0.26377
| 3:16 | 5.1186 | 0.26365
| 3:16 | 5.1189 | 0.26353
| 3:16 | 5.1192 | 0.26342
| 3:16 | 5.1194 | 0.26332
| 3:16 | 5.1197 | 0.26324
| 3:16 | 5.12 | 0.26316
| 3:16 | 5.1203 | 0.26308
| 3:16 | 5.1206 | 0.263
| 3:16 | 5.1208 | 0.26291
| 3:16 | 5.1211 | 0.26282
| 3:16 | 5.1214 | 0.26273
| 3:16 | 5.1217 | 0.26264
| 3:16 | 5.1219 | 0.26254
| 3:16 | 5.1222 | 0.26244
| 3:16 | 5.1225 | 0.26234
| 3:16 | 5.1228 | 0.26224
| 3:16 | 5.1231 | 0.26213
| 3:16 | 5.1233 | 0.26202
| 3:16 | 5.1236 | 0.26191
| 3:16 | 5.1239 | 0.2618
| 3:16 | 5.1242 | 0.2617
| 3:16 | 5.1244 | 0.2616
| 3:16 | 5.1247 | 0.26151
| 3:16 | 5.125 | 0.26142
| 3:16 | 5.1253 | 0.26132
| 3:16 | 5.1256 | 0.26122
| 3:16 | 5.1258 | 0.26112
| 3:16 | 5.1261 | 0.26102
| 3:16 | 5.1264 | 0.26092
| 3:16 | 5.1267 | 0.26081
| 3:16 | 5.1269 | 0.2607
| 3:16 | 5.1272 | 0.26058
| 3:16 | 5.1275 | 0.26046
| 3:16 | 5.1278 | 0.26033
| 3:16 | 5.1281 | 0.2602
| 3:16 | 5.1283 | 0.26007
| 3:17 | 5.1286 | 0.25993
| 3:17 | 5.1289 | 0.2598
| 3:17 | 5.1292 | 0.25966
| 3:17 | 5.1294 | 0.25952
| 3:17 | 5.1297 | 0.25939
| 3:17 | 5.13 | 0.25925
| 3:17 | 5.1303 | 0.2591
| 3:17 | 5.1306 | 0.25896
| 3:17 | 5.1308 | 0.25881
| 3:17 | 5.1311 | 0.25866
| 3:17 | 5.1314 | 0.2585
| 3:17 | 5.1317 | 0.25835
| 3:17 | 5.1319 | 0.25819
| 3:17 | 5.1322 | 0.25802
| 3:17 | 5.1325 | 0.25786
| 3:17 | 5.1328 | 0.2577
| 3:17 | 5.1331 | 0.25754
| 3:17 | 5.1333 | 0.25738
| 3:17 | 5.1336 | 0.25723
| 3:17 | 5.1339 | 0.25709
| 3:17 | 5.1342 | 0.25694
| 3:17 | 5.1344 | 0.2568
| 3:17 | 5.1347 | 0.25666
| 3:17 | 5.135 | 0.25653
| 3:17 | 5.1353 | 0.25641
| 3:17 | 5.1356 | 0.25629
| 3:17 | 5.1358 | 0.25618
| 3:17 | 5.1361 | 0.25607
| 3:17 | 5.1364 | 0.25596
| 3:17 | 5.1367 | 0.25587
| 3:17 | 5.1369 | 0.25579
| 3:17 | 5.1372 | 0.25572
| 3:17 | 5.1375 | 0.25566
| 3:17 | 5.1378 | 0.25561
| 3:17 | 5.1381 | 0.25555
| 3:17 | 5.1383 | 0.2555
| 3:17 | 5.1386 | 0.25546
| 3:17 | 5.1389 | 0.25542
| 3:17 | 5.1392 | 0.25538
| 3:17 | 5.1394 | 0.25535
| 3:17 | 5.1397 | 0.25532
| 3:17 | 5.14 | 0.2553
| 3:17 | 5.1403 | 0.25528
| 3:17 | 5.1406 | 0.25525
| 3:17 | 5.1408 | 0.25522
| 3:17 | 5.1411 | 0.25518
| 3:17 | 5.1414 | 0.25515
| 3:17 | 5.1417 | 0.25512
| 3:17 | 5.1419 | 0.25509
| 3:17 | 5.1422 | 0.25506
| 3:17 | 5.1425 | 0.25503
| 3:17 | 5.1428 | 0.255
| 3:17 | 5.1431 | 0.25495
| 3:17 | 5.1433 | 0.25489
| 3:17 | 5.1436 | 0.25483
| 3:17 | 5.1439 | 0.25476
| 3:17 | 5.1442 | 0.25469
| 3:17 | 5.1444 | 0.25463
| 3:17 | 5.1447 | 0.25456
| 3:18 | 5.145 | 0.2545
| 3:18 | 5.1453 | 0.25442
| 3:18 | 5.1456 | 0.25434
| 3:18 | 5.1458 | 0.25426
| 3:18 | 5.1461 | 0.25419
| 3:18 | 5.1464 | 0.25411
| 3:18 | 5.1467 | 0.25403
| 3:18 | 5.1469 | 0.25396
| 3:18 | 5.1472 | 0.25388
| 3:18 | 5.1475 | 0.2538
| 3:18 | 5.1478 | 0.25373
| 3:18 | 5.1481 | 0.25365
| 3:18 | 5.1483 | 0.25357
| 3:18 | 5.1486 | 0.2535
| 3:18 | 5.1489 | 0.25342
| 3:18 | 5.1492 | 0.25334
| 3:18 | 5.1494 | 0.25327
| 3:18 | 5.1497 | 0.25319
| 3:18 | 5.15 | 0.25313
| 3:18 | 5.1503 | 0.25309
| 3:18 | 5.1506 | 0.25306
| 3:18 | 5.1508 | 0.25305
| 3:18 | 5.1511 | 0.25304
| 3:18 | 5.1514 | 0.25303
| 3:18 | 5.1517 | 0.253
| 3:18 | 5.1519 | 0.25296
| 3:18 | 5.1522 | 0.25292
| 3:18 | 5.1525 | 0.25287
| 3:18 | 5.1528 | 0.25281
| 3:18 | 5.1531 | 0.25276
| 3:18 | 5.1533 | 0.25269
| 3:18 | 5.1536 | 0.25262
| 3:18 | 5.1539 | 0.25253
| 3:18 | 5.1542 | 0.25242
| 3:18 | 5.1544 | 0.25229
| 3:18 | 5.1547 | 0.25216
| 3:18 | 5.155 | 0.25202
| 3:18 | 5.1553 | 0.25189
| 3:18 | 5.1556 | 0.25175
| 3:18 | 5.1558 | 0.25161
| 3:18 | 5.1561 | 0.25148
| 3:18 | 5.1564 | 0.25134
| 3:18 | 5.1567 | 0.25121
| 3:18 | 5.1569 | 0.25107
| 3:18 | 5.1572 | 0.25094
| 3:18 | 5.1575 | 0.25082
| 3:18 | 5.1578 | 0.25069
| 3:18 | 5.1581 | 0.25058
| 3:18 | 5.1583 | 0.25045
| 3:18 | 5.1586 | 0.25033
| 3:18 | 5.1589 | 0.25019
| 3:18 | 5.1592 | 0.25006
| 3:18 | 5.1594 | 0.24993
| 3:18 | 5.1597 | 0.24979
| 3:18 | 5.16 | 0.24966
| 3:18 | 5.1603 | 0.24952
| 3:18 | 5.1606 | 0.24937
| 3:18 | 5.1608 | 0.24923
| 3:18 | 5.1611 | 0.24909
| 3:18 | 5.1614 | 0.24896
| 3:18 | 5.1617 | 0.24882
| 3:19 | 5.1619 | 0.2487
| 3:19 | 5.1622 | 0.24857
| 3:19 | 5.1625 | 0.24845
| 3:19 | 5.1628 | 0.24833
| 3:19 | 5.1631 | 0.2482
| 3:19 | 5.1633 | 0.24807
| 3:19 | 5.1636 | 0.24794
| 3:19 | 5.1639 | 0.2478
| 3:19 | 5.1642 | 0.24766
| 3:19 | 5.1644 | 0.24751
| 3:19 | 5.1647 | 0.24736
| 3:19 | 5.165 | 0.24721
| 3:19 | 5.1653 | 0.24704
| 3:19 | 5.1656 | 0.24688
| 3:19 | 5.1658 | 0.24671
| 3:19 | 5.1661 | 0.24653
| 3:19 | 5.1664 | 0.24635
| 3:19 | 5.1667 | 0.24613
| 3:19 | 5.1669 | 0.2459
| 3:19 | 5.1672 | 0.24566
| 3:19 | 5.1675 | 0.24542
| 3:19 | 5.1678 | 0.24518
| 3:19 | 5.1681 | 0.24494
| 3:19 | 5.1683 | 0.24471
| 3:19 | 5.1686 | 0.24447
| 3:19 | 5.1689 | 0.24423
| 3:19 | 5.1692 | 0.24399
| 3:19 | 5.1694 | 0.24375
| 3:19 | 5.1697 | 0.24352
| 3:19 | 5.17 | 0.2433
| 3:19 | 5.1703 | 0.24309
| 3:19 | 5.1706 | 0.24289
| 3:19 | 5.1708 | 0.24269
| 3:19 | 5.1711 | 0.24251
| 3:19 | 5.1714 | 0.24233
| 3:19 | 5.1717 | 0.24216
| 3:19 | 5.1719 | 0.242
| 3:19 | 5.1722 | 0.24185
| 3:19 | 5.1725 | 0.2417
| 3:19 | 5.1728 | 0.24155
| 3:19 | 5.1731 | 0.24141
| 3:19 | 5.1733 | 0.24128
| 3:19 | 5.1736 | 0.24115
| 3:19 | 5.1739 | 0.24102
| 3:19 | 5.1742 | 0.24089
| 3:19 | 5.1744 | 0.24076
| 3:19 | 5.1747 | 0.24064
| 3:19 | 5.175 | 0.24051
| 3:19 | 5.1753 | 0.24036
| 3:19 | 5.1756 | 0.24019
| 3:19 | 5.1758 | 0.24001
| 3:19 | 5.1761 | 0.23983
| 3:19 | 5.1764 | 0.23966
| 3:19 | 5.1767 | 0.23948
| 3:19 | 5.1769 | 0.2393
| 3:19 | 5.1772 | 0.23911
| 3:19 | 5.1775 | 0.23891
| 3:19 | 5.1778 | 0.2387
| 3:19 | 5.1781 | 0.23849
| 3:20 | 5.1783 | 0.23828
| 3:20 | 5.1786 | 0.23806
| 3:20 | 5.1789 | 0.23784
| 3:20 | 5.1792 | 0.2376
| 3:20 | 5.1794 | 0.23737
| 3:20 | 5.1797 | 0.23713
| 3:20 | 5.18 | 0.23689
| 3:20 | 5.1803 | 0.23665
| 3:20 | 5.1806 | 0.23641
| 3:20 | 5.1808 | 0.23617
| 3:20 | 5.1811 | 0.23593
| 3:20 | 5.1814 | 0.23568
| 3:20 | 5.1817 | 0.23544
| 3:20 | 5.1819 | 0.2352
| 3:20 | 5.1822 | 0.23495
| 3:20 | 5.1825 | 0.23471
| 3:20 | 5.1828 | 0.23447
| 3:20 | 5.1831 | 0.23424
| 3:20 | 5.1833 | 0.23402
| 3:20 | 5.1836 | 0.23381
| 3:20 | 5.1839 | 0.23361
| 3:20 | 5.1842 | 0.23342
| 3:20 | 5.1844 | 0.23323
| 3:20 | 5.1847 | 0.23304
| 3:20 | 5.185 | 0.23284
| 3:20 | 5.1853 | 0.23264
| 3:20 | 5.1856 | 0.23244
| 3:20 | 5.1858 | 0.23224
| 3:20 | 5.1861 | 0.23203
| 3:20 | 5.1864 | 0.23181
| 3:20 | 5.1867 | 0.2316
| 3:20 | 5.1869 | 0.23139
| 3:20 | 5.1872 | 0.23116
| 3:20 | 5.1875 | 0.23091
| 3:20 | 5.1878 | 0.23067
| 3:20 | 5.1881 | 0.23042
| 3:20 | 5.1883 | 0.23018
| 3:20 | 5.1886 | 0.22994
| 3:20 | 5.1889 | 0.22971
| 3:20 | 5.1892 | 0.22949
| 3:20 | 5.1894 | 0.22927
| 3:20 | 5.1897 | 0.22906
| 3:20 | 5.19 | 0.22885
| 3:20 | 5.1903 | 0.22865
| 3:20 | 5.1906 | 0.22845
| 3:20 | 5.1908 | 0.22826
| 3:20 | 5.1911 | 0.22807
| 3:20 | 5.1914 | 0.22789
| 3:20 | 5.1917 | 0.22772
| 3:20 | 5.1919 | 0.22756
| 3:20 | 5.1922 | 0.2274
| 3:20 | 5.1925 | 0.22722
| 3:20 | 5.1928 | 0.22704
| 3:20 | 5.1931 | 0.22686
| 3:20 | 5.1933 | 0.22667
| 3:20 | 5.1936 | 0.22649
| 3:20 | 5.1939 | 0.22631
| 3:20 | 5.1942 | 0.22614
| 3:20 | 5.1944 | 0.22597
| 3:20 | 5.1947 | 0.2258
| 3:20 | 5.195 | 0.22563
| 3:21 | 5.1953 | 0.22546
| 3:21 | 5.1956 | 0.22529
| 3:21 | 5.1958 | 0.22512
| 3:21 | 5.1961 | 0.22496
| 3:21 | 5.1964 | 0.2248
| 3:21 | 5.1967 | 0.22464
| 3:21 | 5.1969 | 0.22448
| 3:21 | 5.1972 | 0.22433
| 3:21 | 5.1975 | 0.22418
| 3:21 | 5.1978 | 0.22403
| 3:21 | 5.1981 | 0.22388
| 3:21 | 5.1983 | 0.22374
| 3:21 | 5.1986 | 0.2236
| 3:21 | 5.1989 | 0.22346
| 3:21 | 5.1992 | 0.22333
| 3:21 | 5.1994 | 0.22319
| 3:21 | 5.1997 | 0.22307
| 3:21 | 5.2 | 0.22296
| 3:21 | 5.2003 | 0.22286
| 3:21 | 5.2006 | 0.22278
| 3:21 | 5.2008 | 0.22272
| 3:21 | 5.2011 | 0.22268
| 3:21 | 5.2014 | 0.22267
| 3:21 | 5.2017 | 0.22268
| 3:21 | 5.2019 | 0.22271
| 3:21 | 5.2022 | 0.22276
| 3:21 | 5.2025 | 0.22281
| 3:21 | 5.2028 | 0.22286
| 3:21 | 5.2031 | 0.22291
| 3:21 | 5.2033 | 0.22296
| 3:21 | 5.2036 | 0.223
| 3:21 | 5.2039 | 0.22304
| 3:21 | 5.2042 | 0.22308
| 3:21 | 5.2044 | 0.22311
| 3:21 | 5.2047 | 0.22313
| 3:21 | 5.205 | 0.22315
| 3:21 | 5.2053 | 0.22316
| 3:21 | 5.2056 | 0.22317
| 3:21 | 5.2058 | 0.22317
| 3:21 | 5.2061 | 0.22317
| 3:21 | 5.2064 | 0.22317
| 3:21 | 5.2067 | 0.22316
| 3:21 | 5.2069 | 0.22314
| 3:21 | 5.2072 | 0.22311
| 3:21 | 5.2075 | 0.22309
| 3:21 | 5.2078 | 0.22305
| 3:21 | 5.2081 | 0.22302
| 3:21 | 5.2083 | 0.22298
| 3:21 | 5.2086 | 0.22294
| 3:21 | 5.2089 | 0.2229
| 3:21 | 5.2092 | 0.22285
| 3:21 | 5.2094 | 0.22282
| 3:21 | 5.2097 | 0.22279
| 3:21 | 5.21 | 0.22275
| 3:21 | 5.2103 | 0.22272
| 3:21 | 5.2106 | 0.22268
| 3:21 | 5.2108 | 0.22264
| 3:21 | 5.2111 | 0.22259
| 3:21 | 5.2114 | 0.22254
| 3:22 | 5.2117 | 0.22247
| 3:22 | 5.2119 | 0.2224
| 3:22 | 5.2122 | 0.22231
| 3:22 | 5.2125 | 0.22221
| 3:22 | 5.2128 | 0.22211
| 3:22 | 5.2131 | 0.222
| 3:22 | 5.2133 | 0.22188
| 3:22 | 5.2136 | 0.22175
| 3:22 | 5.2139 | 0.22161
| 3:22 | 5.2142 | 0.22145
| 3:22 | 5.2144 | 0.22129
| 3:22 | 5.2147 | 0.22112
| 3:22 | 5.215 | 0.22094
| 3:22 | 5.2153 | 0.22074
| 3:22 | 5.2156 | 0.22054
| 3:22 | 5.2158 | 0.22033
| 3:22 | 5.2161 | 0.22012
| 3:22 | 5.2164 | 0.21992
| 3:22 | 5.2167 | 0.21971
| 3:22 | 5.2169 | 0.21951
| 3:22 | 5.2172 | 0.2193
| 3:22 | 5.2175 | 0.21912
| 3:22 | 5.2178 | 0.21895
| 3:22 | 5.2181 | 0.2188
| 3:22 | 5.2183 | 0.21865
| 3:22 | 5.2186 | 0.21851
| 3:22 | 5.2189 | 0.21837
| 3:22 | 5.2192 | 0.21824
| 3:22 | 5.2194 | 0.21812
| 3:22 | 5.2197 | 0.21802
| 3:22 | 5.22 | 0.21793
| 3:22 | 5.2203 | 0.21785
| 3:22 | 5.2206 | 0.21778
| 3:22 | 5.2208 | 0.21773
| 3:22 | 5.2211 | 0.21769
| 3:22 | 5.2214 | 0.21766
| 3:22 | 5.2217 | 0.21764
| 3:22 | 5.2219 | 0.21761
| 3:22 | 5.2222 | 0.2176
| 3:22 | 5.2225 | 0.21759
| 3:22 | 5.2228 | 0.21759
| 3:22 | 5.2231 | 0.21759
| 3:22 | 5.2233 | 0.2176
| 3:22 | 5.2236 | 0.21761
| 3:22 | 5.2239 | 0.21758
| 3:22 | 5.2242 | 0.21756
| 3:22 | 5.2244 | 0.21754
| 3:22 | 5.2247 | 0.21753
| 3:22 | 5.225 | 0.21752
| 3:22 | 5.2253 | 0.21748
| 3:22 | 5.2256 | 0.21742
| 3:22 | 5.2258 | 0.21736
| 3:22 | 5.2261 | 0.21728
| 3:22 | 5.2264 | 0.21719
| 3:22 | 5.2267 | 0.21709
| 3:22 | 5.2269 | 0.21699
| 3:22 | 5.2272 | 0.2169
| 3:22 | 5.2275 | 0.2168
| 3:22 | 5.2278 | 0.21672
| 3:22 | 5.2281 | 0.21665
| 3:22 | 5.2283 | 0.21658
| 3:23 | 5.2286 | 0.2165
| 3:23 | 5.2289 | 0.21642
| 3:23 | 5.2292 | 0.21634
| 3:23 | 5.2294 | 0.21625
| 3:23 | 5.2297 | 0.21614
| 3:23 | 5.23 | 0.21603
| 3:23 | 5.2303 | 0.2159
| 3:23 | 5.2306 | 0.21576
| 3:23 | 5.2308 | 0.2156
| 3:23 | 5.2311 | 0.21543
| 3:23 | 5.2314 | 0.21525
| 3:23 | 5.2317 | 0.21505
| 3:23 | 5.2319 | 0.21484
| 3:23 | 5.2322 | 0.21462
| 3:23 | 5.2325 | 0.21439
| 3:23 | 5.2328 | 0.21416
| 3:23 | 5.2331 | 0.21393
| 3:23 | 5.2333 | 0.21371
| 3:23 | 5.2336 | 0.21349
| 3:23 | 5.2339 | 0.21327
| 3:23 | 5.2342 | 0.21307
| 3:23 | 5.2344 | 0.21286
| 3:23 | 5.2347 | 0.21266
| 3:23 | 5.235 | 0.21248
| 3:23 | 5.2353 | 0.2123
| 3:23 | 5.2356 | 0.21213
| 3:23 | 5.2358 | 0.21196
| 3:23 | 5.2361 | 0.21179
| 3:23 | 5.2364 | 0.21162
| 3:23 | 5.2367 | 0.21145
| 3:23 | 5.2369 | 0.2113
| 3:23 | 5.2372 | 0.21114
| 3:23 | 5.2375 | 0.21099
| 3:23 | 5.2378 | 0.21083
| 3:23 | 5.2381 | 0.21066
| 3:23 | 5.2383 | 0.2105
| 3:23 | 5.2386 | 0.21035
| 3:23 | 5.2389 | 0.2102
| 3:23 | 5.2392 | 0.21005
| 3:23 | 5.2394 | 0.20991
| 3:23 | 5.2397 | 0.20977
| 3:23 | 5.24 | 0.20963
| 3:23 | 5.2403 | 0.2095
| 3:23 | 5.2406 | 0.20937
| 3:23 | 5.2408 | 0.20925
| 3:23 | 5.2411 | 0.20913
| 3:23 | 5.2414 | 0.20903
| 3:23 | 5.2417 | 0.20893
| 3:23 | 5.2419 | 0.20883
| 3:23 | 5.2422 | 0.20872
| 3:23 | 5.2425 | 0.2086
| 3:23 | 5.2428 | 0.20848
| 3:23 | 5.2431 | 0.20834
| 3:23 | 5.2433 | 0.20819
| 3:23 | 5.2436 | 0.20803
| 3:23 | 5.2439 | 0.20787
| 3:23 | 5.2442 | 0.20771
| 3:23 | 5.2444 | 0.20755
| 3:23 | 5.2447 | 0.20738
| 3:24 | 5.245 | 0.20721
| 3:24 | 5.2453 | 0.20705
| 3:24 | 5.2456 | 0.20689
| 3:24 | 5.2458 | 0.20672
| 3:24 | 5.2461 | 0.20653
| 3:24 | 5.2464 | 0.20632
| 3:24 | 5.2467 | 0.20612
| 3:24 | 5.2469 | 0.20591
| 3:24 | 5.2472 | 0.20569
| 3:24 | 5.2475 | 0.20548
| 3:24 | 5.2478 | 0.20525
| 3:24 | 5.2481 | 0.20503
| 3:24 | 5.2483 | 0.2048
| 3:24 | 5.2486 | 0.20456
| 3:24 | 5.2489 | 0.20432
| 3:24 | 5.2492 | 0.20408
| 3:24 | 5.2494 | 0.20383
| 3:24 | 5.2497 | 0.20358
| 3:24 | 5.25 | 0.20332
| 3:24 | 5.2503 | 0.20305
| 3:24 | 5.2506 | 0.20275
| 3:24 | 5.2508 | 0.20243
| 3:24 | 5.2511 | 0.20208
| 3:24 | 5.2514 | 0.20172
| 3:24 | 5.2517 | 0.20136
| 3:24 | 5.2519 | 0.201
| 3:24 | 5.2522 | 0.20065
| 3:24 | 5.2525 | 0.2003
| 3:24 | 5.2528 | 0.19995
| 3:24 | 5.2531 | 0.1996
| 3:24 | 5.2533 | 0.19926
| 3:24 | 5.2536 | 0.19894
| 3:24 | 5.2539 | 0.19865
| 3:24 | 5.2542 | 0.19837
| 3:24 | 5.2544 | 0.1981
| 3:24 | 5.2547 | 0.19784
| 3:24 | 5.255 | 0.19758
| 3:24 | 5.2553 | 0.19731
| 3:24 | 5.2556 | 0.19705
| 3:24 | 5.2558 | 0.19679
| 3:24 | 5.2561 | 0.19653
| 3:24 | 5.2564 | 0.19628
| 3:24 | 5.2567 | 0.19602
| 3:24 | 5.2569 | 0.19577
| 3:24 | 5.2572 | 0.19551
| 3:24 | 5.2575 | 0.19527
| 3:24 | 5.2578 | 0.19504
| 3:24 | 5.2581 | 0.19481
| 3:24 | 5.2583 | 0.19458
| 3:24 | 5.2586 | 0.19435
| 3:24 | 5.2589 | 0.19411
| 3:24 | 5.2592 | 0.19388
| 3:24 | 5.2594 | 0.19364
| 3:24 | 5.2597 | 0.19339
| 3:24 | 5.26 | 0.19313
| 3:24 | 5.2603 | 0.19287
| 3:24 | 5.2606 | 0.19261
| 3:24 | 5.2608 | 0.19234
| 3:24 | 5.2611 | 0.19207
| 3:24 | 5.2614 | 0.1918
| 3:24 | 5.2617 | 0.19154
| 3:25 | 5.2619 | 0.19127
| 3:25 | 5.2622 | 0.19101
| 3:25 | 5.2625 | 0.19077
| 3:25 | 5.2628 | 0.19053
| 3:25 | 5.2631 | 0.19028
| 3:25 | 5.2633 | 0.19003
| 3:25 | 5.2636 | 0.18977
| 3:25 | 5.2639 | 0.18951
| 3:25 | 5.2642 | 0.18924
| 3:25 | 5.2644 | 0.18896
| 3:25 | 5.2647 | 0.18867
| 3:25 | 5.265 | 0.18838
| 3:25 | 5.2653 | 0.18808
| 3:25 | 5.2656 | 0.18778
| 3:25 | 5.2658 | 0.18747
| 3:25 | 5.2661 | 0.18718
| 3:25 | 5.2664 | 0.1869
| 3:25 | 5.2667 | 0.18662
| 3:25 | 5.2669 | 0.18635
| 3:25 | 5.2672 | 0.18608
| 3:25 | 5.2675 | 0.1858
| 3:25 | 5.2678 | 0.18554
| 3:25 | 5.2681 | 0.18528
| 3:25 | 5.2683 | 0.18503
| 3:25 | 5.2686 | 0.18478
| 3:25 | 5.2689 | 0.18454
| 3:25 | 5.2692 | 0.1843
| 3:25 | 5.2694 | 0.18408
| 3:25 | 5.2697 | 0.18385
| 3:25 | 5.27 | 0.18361
| 3:25 | 5.2703 | 0.18338
| 3:25 | 5.2706 | 0.18315
| 3:25 | 5.2708 | 0.18292
| 3:25 | 5.2711 | 0.18272
| 3:25 | 5.2714 | 0.18253
| 3:25 | 5.2717 | 0.18236
| 3:25 | 5.2719 | 0.18221
| 3:25 | 5.2722 | 0.18207
| 3:25 | 5.2725 | 0.18196
| 3:25 | 5.2728 | 0.18186
| 3:25 | 5.2731 | 0.18177
| 3:25 | 5.2733 | 0.18171
| 3:25 | 5.2736 | 0.18166
| 3:25 | 5.2739 | 0.18163
| 3:25 | 5.2742 | 0.1816
| 3:25 | 5.2744 | 0.18157
| 3:25 | 5.2747 | 0.18153
| 3:25 | 5.275 | 0.18149
| 3:25 | 5.2753 | 0.18144
| 3:25 | 5.2756 | 0.18138
| 3:25 | 5.2758 | 0.18131
| 3:25 | 5.2761 | 0.18122
| 3:25 | 5.2764 | 0.18112
| 3:25 | 5.2767 | 0.18101
| 3:25 | 5.2769 | 0.18089
| 3:25 | 5.2772 | 0.18076
| 3:25 | 5.2775 | 0.18062
| 3:25 | 5.2778 | 0.18047
| 3:25 | 5.2781 | 0.18034
| 3:26 | 5.2783 | 0.1802
| 3:26 | 5.2786 | 0.18007
| 3:26 | 5.2789 | 0.17994
| 3:26 | 5.2792 | 0.17982
| 3:26 | 5.2794 | 0.17971
| 3:26 | 5.2797 | 0.1796
| 3:26 | 5.28 | 0.1795
| 3:26 | 5.2803 | 0.17941
| 3:26 | 5.2806 | 0.17932
| 3:26 | 5.2808 | 0.17922
| 3:26 | 5.2811 | 0.17913
| 3:26 | 5.2814 | 0.17905
| 3:26 | 5.2817 | 0.17896
| 3:26 | 5.2819 | 0.17887
| 3:26 | 5.2822 | 0.17879
| 3:26 | 5.2825 | 0.17871
| 3:26 | 5.2828 | 0.17862
| 3:26 | 5.2831 | 0.17854
| 3:26 | 5.2833 | 0.17847
| 3:26 | 5.2836 | 0.17839
| 3:26 | 5.2839 | 0.17831
| 3:26 | 5.2842 | 0.17825
| 3:26 | 5.2844 | 0.17819
| 3:26 | 5.2847 | 0.17814
| 3:26 | 5.285 | 0.17809
| 3:26 | 5.2853 | 0.17804
| 3:26 | 5.2856 | 0.178
| 3:26 | 5.2858 | 0.17795
| 3:26 | 5.2861 | 0.17789
| 3:26 | 5.2864 | 0.17785
| 3:26 | 5.2867 | 0.17781
| 3:26 | 5.2869 | 0.17777
| 3:26 | 5.2872 | 0.17772
| 3:26 | 5.2875 | 0.17766
| 3:26 | 5.2878 | 0.17759
| 3:26 | 5.2881 | 0.17752
| 3:26 | 5.2883 | 0.17744
| 3:26 | 5.2886 | 0.17736
| 3:26 | 5.2889 | 0.17728
| 3:26 | 5.2892 | 0.1772
| 3:26 | 5.2894 | 0.17711
| 3:26 | 5.2897 | 0.17702
| 3:26 | 5.29 | 0.17693
| 3:26 | 5.2903 | 0.17684
| 3:26 | 5.2906 | 0.17674
| 3:26 | 5.2908 | 0.17664
| 3:26 | 5.2911 | 0.17654
| 3:26 | 5.2914 | 0.17644
| 3:26 | 5.2917 | 0.17632
| 3:26 | 5.2919 | 0.17621
| 3:26 | 5.2922 | 0.1761
| 3:26 | 5.2925 | 0.17597
| 3:26 | 5.2928 | 0.17586
| 3:26 | 5.2931 | 0.17574
| 3:26 | 5.2933 | 0.17563
| 3:26 | 5.2936 | 0.17553
| 3:26 | 5.2939 | 0.17543
| 3:26 | 5.2942 | 0.17534
| 3:26 | 5.2944 | 0.17525
| 3:26 | 5.2947 | 0.17518
| 3:26 | 5.295 | 0.1751
| 3:27 | 5.2953 | 0.17503
| 3:27 | 5.2956 | 0.17495
| 3:27 | 5.2958 | 0.17486
| 3:27 | 5.2961 | 0.17474
| 3:27 | 5.2964 | 0.1746
| 3:27 | 5.2967 | 0.17446
| 3:27 | 5.2969 | 0.17432
| 3:27 | 5.2972 | 0.17418
| 3:27 | 5.2975 | 0.17404
| 3:27 | 5.2978 | 0.1739
| 3:27 | 5.2981 | 0.17376
| 3:27 | 5.2983 | 0.17362
| 3:27 | 5.2986 | 0.17348
| 3:27 | 5.2989 | 0.17334
| 3:27 | 5.2992 | 0.1732
| 3:27 | 5.2994 | 0.17306
| 3:27 | 5.2997 | 0.17291
| 3:27 | 5.3 | 0.17277
| 3:27 | 5.3003 | 0.17262
| 3:27 | 5.3006 | 0.17247
| 3:27 | 5.3008 | 0.17232
| 3:27 | 5.3011 | 0.17218
| 3:27 | 5.3014 | 0.17205
| 3:27 | 5.3017 | 0.17193
| 3:27 | 5.3019 | 0.1718
| 3:27 | 5.3022 | 0.17167
| 3:27 | 5.3025 | 0.17154
| 3:27 | 5.3028 | 0.17141
| 3:27 | 5.3031 | 0.17128
| 3:27 | 5.3033 | 0.17115
| 3:27 | 5.3036 | 0.17102
| 3:27 | 5.3039 | 0.17087
| 3:27 | 5.3042 | 0.1707
| 3:27 | 5.3044 | 0.17052
| 3:27 | 5.3047 | 0.17034
| 3:27 | 5.305 | 0.17016
| 3:27 | 5.3053 | 0.16998
| 3:27 | 5.3056 | 0.16979
| 3:27 | 5.3058 | 0.16959
| 3:27 | 5.3061 | 0.16939
| 3:27 | 5.3064 | 0.16918
| 3:27 | 5.3067 | 0.16897
| 3:27 | 5.3069 | 0.16877
| 3:27 | 5.3072 | 0.16857
| 3:27 | 5.3075 | 0.16837
| 3:27 | 5.3078 | 0.16817
| 3:27 | 5.3081 | 0.16798
| 3:27 | 5.3083 | 0.16779
| 3:27 | 5.3086 | 0.16759
| 3:27 | 5.3089 | 0.1674
| 3:27 | 5.3092 | 0.16721
| 3:27 | 5.3094 | 0.16702
| 3:27 | 5.3097 | 0.16683
| 3:27 | 5.31 | 0.16664
| 3:27 | 5.3103 | 0.16646
| 3:27 | 5.3106 | 0.1663
| 3:27 | 5.3108 | 0.16614
| 3:27 | 5.3111 | 0.16598
| 3:27 | 5.3114 | 0.1658
| 3:27 | 5.3117 | 0.16558
| 3:28 | 5.3119 | 0.16536
| 3:28 | 5.3122 | 0.16514
| 3:28 | 5.3125 | 0.16492
| 3:28 | 5.3128 | 0.1647
| 3:28 | 5.3131 | 0.16448
| 3:28 | 5.3133 | 0.16427
| 3:28 | 5.3136 | 0.16406
| 3:28 | 5.3139 | 0.16386
| 3:28 | 5.3142 | 0.16367
| 3:28 | 5.3144 | 0.16348
| 3:28 | 5.3147 | 0.1633
| 3:28 | 5.315 | 0.16313
| 3:28 | 5.3153 | 0.16296
| 3:28 | 5.3156 | 0.1628
| 3:28 | 5.3158 | 0.16266
| 3:28 | 5.3161 | 0.16253
| 3:28 | 5.3164 | 0.1624
| 3:28 | 5.3167 | 0.16226
| 3:28 | 5.3169 | 0.1621
| 3:28 | 5.3172 | 0.16194
| 3:28 | 5.3175 | 0.16177
| 3:28 | 5.3178 | 0.16159
| 3:28 | 5.3181 | 0.16139
| 3:28 | 5.3183 | 0.16116
| 3:28 | 5.3186 | 0.16094
| 3:28 | 5.3189 | 0.16072
| 3:28 | 5.3192 | 0.16051
| 3:28 | 5.3194 | 0.16033
| 3:28 | 5.3197 | 0.16015
| 3:28 | 5.32 | 0.15997
| 3:28 | 5.3203 | 0.15979
| 3:28 | 5.3206 | 0.15961
| 3:28 | 5.3208 | 0.15943
| 3:28 | 5.3211 | 0.15926
| 3:28 | 5.3214 | 0.1591
| 3:28 | 5.3217 | 0.15893
| 3:28 | 5.3219 | 0.15875
| 3:28 | 5.3222 | 0.15857
| 3:28 | 5.3225 | 0.15838
| 3:28 | 5.3228 | 0.15819
| 3:28 | 5.3231 | 0.15799
| 3:28 | 5.3233 | 0.15778
| 3:28 | 5.3236 | 0.15758
| 3:28 | 5.3239 | 0.15736
| 3:28 | 5.3242 | 0.15713
| 3:28 | 5.3244 | 0.15689
| 3:28 | 5.3247 | 0.15665
| 3:28 | 5.325 | 0.1564
| 3:28 | 5.3253 | 0.15616
| 3:28 | 5.3256 | 0.15591
| 3:28 | 5.3258 | 0.15566
| 3:28 | 5.3261 | 0.15542
| 3:28 | 5.3264 | 0.15516
| 3:28 | 5.3267 | 0.15491
| 3:28 | 5.3269 | 0.15465
| 3:28 | 5.3272 | 0.1544
| 3:28 | 5.3275 | 0.15415
| 3:28 | 5.3278 | 0.1539
| 3:28 | 5.3281 | 0.15366
| 3:29 | 5.3283 | 0.15342
| 3:29 | 5.3286 | 0.15318
| 3:29 | 5.3289 | 0.15294
| 3:29 | 5.3292 | 0.1527
| 3:29 | 5.3294 | 0.15245
| 3:29 | 5.3297 | 0.15221
| 3:29 | 5.33 | 0.15196
| 3:29 | 5.3303 | 0.15172
| 3:29 | 5.3306 | 0.15148
| 3:29 | 5.3308 | 0.15124
| 3:29 | 5.3311 | 0.151
| 3:29 | 5.3314 | 0.15076
| 3:29 | 5.3317 | 0.15052
| 3:29 | 5.3319 | 0.15029
| 3:29 | 5.3322 | 0.15005
| 3:29 | 5.3325 | 0.14981
| 3:29 | 5.3328 | 0.14956
| 3:29 | 5.3331 | 0.1493
| 3:29 | 5.3333 | 0.14904
| 3:29 | 5.3336 | 0.14878
| 3:29 | 5.3339 | 0.1485
| 3:29 | 5.3342 | 0.14822
| 3:29 | 5.3344 | 0.14794
| 3:29 | 5.3347 | 0.14765
| 3:29 | 5.335 | 0.14736
| 3:29 | 5.3353 | 0.14706
| 3:29 | 5.3356 | 0.14677
| 3:29 | 5.3358 | 0.14647
| 3:29 | 5.3361 | 0.14618
| 3:29 | 5.3364 | 0.14589
| 3:29 | 5.3367 | 0.1456
| 3:29 | 5.3369 | 0.14532
| 3:29 | 5.3372 | 0.14503
| 3:29 | 5.3375 | 0.14474
| 3:29 | 5.3378 | 0.14445
| 3:29 | 5.3381 | 0.14416
| 3:29 | 5.3383 | 0.14387
| 3:29 | 5.3386 | 0.14359
| 3:29 | 5.3389 | 0.14331
| 3:29 | 5.3392 | 0.14304
| 3:29 | 5.3394 | 0.14277
| 3:29 | 5.3397 | 0.1425
| 3:29 | 5.34 | 0.14224
| 3:29 | 5.3403 | 0.14198
| 3:29 | 5.3406 | 0.14173
| 3:29 | 5.3408 | 0.1415
| 3:29 | 5.3411 | 0.14127
| 3:29 | 5.3414 | 0.14104
| 3:29 | 5.3417 | 0.14082
| 3:29 | 5.3419 | 0.1406
| 3:29 | 5.3422 | 0.14038
| 3:29 | 5.3425 | 0.14017
| 3:29 | 5.3428 | 0.13995
| 3:29 | 5.3431 | 0.13975
| 3:29 | 5.3433 | 0.13955
| 3:29 | 5.3436 | 0.13935
| 3:29 | 5.3439 | 0.13916
| 3:29 | 5.3442 | 0.13896
| 3:29 | 5.3444 | 0.13876
| 3:29 | 5.3447 | 0.13856
| 3:30 | 5.345 | 0.13834
| 3:30 | 5.3453 | 0.13813
| 3:30 | 5.3456 | 0.1379
| 3:30 | 5.3458 | 0.13767
| 3:30 | 5.3461 | 0.13743
| 3:30 | 5.3464 | 0.13718
| 3:30 | 5.3467 | 0.13693
| 3:30 | 5.3469 | 0.13668
| 3:30 | 5.3472 | 0.13642
| 3:30 | 5.3475 | 0.13617
| 3:30 | 5.3478 | 0.13591
| 3:30 | 5.3481 | 0.13565
| 3:30 | 5.3483 | 0.13539
| 3:30 | 5.3486 | 0.13513
| 3:30 | 5.3489 | 0.13486
| 3:30 | 5.3492 | 0.1346
| 3:30 | 5.3494 | 0.13433
| 3:30 | 5.3497 | 0.13405
| 3:30 | 5.35 | 0.13377
| 3:30 | 5.3503 | 0.13348
| 3:30 | 5.3506 | 0.13319
| 3:30 | 5.3508 | 0.13292
| 3:30 | 5.3511 | 0.13266
| 3:30 | 5.3514 | 0.1324
| 3:30 | 5.3517 | 0.13216
| 3:30 | 5.3519 | 0.13192
| 3:30 | 5.3522 | 0.1317
| 3:30 | 5.3525 | 0.13148
| 3:30 | 5.3528 | 0.13125
| 3:30 | 5.3531 | 0.13101
| 3:30 | 5.3533 | 0.13077
| 3:30 | 5.3536 | 0.13053
| 3:30 | 5.3539 | 0.13028
| 3:30 | 5.3542 | 0.13004
| 3:30 | 5.3544 | 0.1298
| 3:30 | 5.3547 | 0.12956
| 3:30 | 5.355 | 0.12933
| 3:30 | 5.3553 | 0.1291
| 3:30 | 5.3556 | 0.12887
| 3:30 | 5.3558 | 0.12865
| 3:30 | 5.3561 | 0.12843
| 3:30 | 5.3564 | 0.12821
| 3:30 | 5.3567 | 0.12799
| 3:30 | 5.3569 | 0.12777
| 3:30 | 5.3572 | 0.12751
| 3:30 | 5.3575 | 0.12724
| 3:30 | 5.3578 | 0.12696
| 3:30 | 5.3581 | 0.12667
| 3:30 | 5.3583 | 0.12636
| 3:30 | 5.3586 | 0.12605
| 3:30 | 5.3589 | 0.12575
| 3:30 | 5.3592 | 0.12544
| 3:30 | 5.3594 | 0.12514
| 3:30 | 5.3597 | 0.12483
| 3:30 | 5.36 | 0.12452
| 3:30 | 5.3603 | 0.12422
| 3:30 | 5.3606 | 0.12391
| 3:30 | 5.3608 | 0.12361
| 3:30 | 5.3611 | 0.12331
| 3:30 | 5.3614 | 0.123
| 3:30 | 5.3617 | 0.1227
| 3:31 | 5.3619 | 0.1224
| 3:31 | 5.3622 | 0.12212
| 3:31 | 5.3625 | 0.12183
| 3:31 | 5.3628 | 0.12156
| 3:31 | 5.3631 | 0.12129
| 3:31 | 5.3633 | 0.12103
| 3:31 | 5.3636 | 0.12078
| 3:31 | 5.3639 | 0.12053
| 3:31 | 5.3642 | 0.12028
| 3:31 | 5.3644 | 0.12004
| 3:31 | 5.3647 | 0.1198
| 3:31 | 5.365 | 0.11957
| 3:31 | 5.3653 | 0.11934
| 3:31 | 5.3656 | 0.11912
| 3:31 | 5.3658 | 0.1189
| 3:31 | 5.3661 | 0.11867
| 3:31 | 5.3664 | 0.11845
| 3:31 | 5.3667 | 0.11822
| 3:31 | 5.3669 | 0.11798
| 3:31 | 5.3672 | 0.11774
| 3:31 | 5.3675 | 0.1175
| 3:31 | 5.3678 | 0.11724
| 3:31 | 5.3681 | 0.11698
| 3:31 | 5.3683 | 0.11672
| 3:31 | 5.3686 | 0.11643
| 3:31 | 5.3689 | 0.11614
| 3:31 | 5.3692 | 0.11584
| 3:31 | 5.3694 | 0.11553
| 3:31 | 5.3697 | 0.1152
| 3:31 | 5.37 | 0.11486
| 3:31 | 5.3703 | 0.11452
| 3:31 | 5.3706 | 0.11417
| 3:31 | 5.3708 | 0.11382
| 3:31 | 5.3711 | 0.11347
| 3:31 | 5.3714 | 0.11311
| 3:31 | 5.3717 | 0.11276
| 3:31 | 5.3719 | 0.11242
| 3:31 | 5.3722 | 0.11207
| 3:31 | 5.3725 | 0.11173
| 3:31 | 5.3728 | 0.1114
| 3:31 | 5.3731 | 0.11106
| 3:31 | 5.3733 | 0.11073
| 3:31 | 5.3736 | 0.1104
| 3:31 | 5.3739 | 0.11006
| 3:31 | 5.3742 | 0.10971
| 3:31 | 5.3744 | 0.10936
| 3:31 | 5.3747 | 0.109
| 3:31 | 5.375 | 0.10864
| 3:31 | 5.3753 | 0.10828
| 3:31 | 5.3756 | 0.10791
| 3:31 | 5.3758 | 0.10755
| 3:31 | 5.3761 | 0.10719
| 3:31 | 5.3764 | 0.10683
| 3:31 | 5.3767 | 0.10647
| 3:31 | 5.3769 | 0.10611
| 3:31 | 5.3772 | 0.10576
| 3:31 | 5.3775 | 0.10541
| 3:31 | 5.3778 | 0.10506
| 3:31 | 5.3781 | 0.10471
| 3:32 | 5.3783 | 0.10436
| 3:32 | 5.3786 | 0.10402
| 3:32 | 5.3789 | 0.10368
| 3:32 | 5.3792 | 0.10334
| 3:32 | 5.3794 | 0.103
| 3:32 | 5.3797 | 0.10268
| 3:32 | 5.38 | 0.10236
| 3:32 | 5.3803 | 0.10204
| 3:32 | 5.3806 | 0.10172
| 3:32 | 5.3808 | 0.1014
| 3:32 | 5.3811 | 0.10109
| 3:32 | 5.3814 | 0.10078
| 3:32 | 5.3817 | 0.10046
| 3:32 | 5.3819 | 0.10015
| 3:32 | 5.3822 | 0.099844
| 3:32 | 5.3825 | 0.099534
| 3:32 | 5.3828 | 0.099222
| 3:32 | 5.3831 | 0.098908
| 3:32 | 5.3833 | 0.098584
| 3:32 | 5.3836 | 0.098256
| 3:32 | 5.3839 | 0.097924
| 3:32 | 5.3842 | 0.097588
| 3:32 | 5.3844 | 0.097249
| 3:32 | 5.3847 | 0.096904
| 3:32 | 5.385 | 0.096549
| 3:32 | 5.3853 | 0.096184
| 3:32 | 5.3856 | 0.095814
| 3:32 | 5.3858 | 0.095442
| 3:32 | 5.3861 | 0.095067
| 3:32 | 5.3864 | 0.094681
| 3:32 | 5.3867 | 0.094292
| 3:32 | 5.3869 | 0.093883
| 3:32 | 5.3872 | 0.093464
| 3:32 | 5.3875 | 0.093037
| 3:32 | 5.3878 | 0.092608
| 3:32 | 5.3881 | 0.092176
| 3:32 | 5.3883 | 0.091743
| 3:32 | 5.3886 | 0.091306
| 3:32 | 5.3889 | 0.090868
| 3:32 | 5.3892 | 0.090427
| 3:32 | 5.3894 | 0.089984
| 3:32 | 5.3897 | 0.089539
| 3:32 | 5.39 | 0.089091
| 3:32 | 5.3903 | 0.088642
| 3:32 | 5.3906 | 0.088193
| 3:32 | 5.3908 | 0.08775
| 3:32 | 5.3911 | 0.087304
| 3:32 | 5.3914 | 0.086855
| 3:32 | 5.3917 | 0.086408
| 3:32 | 5.3919 | 0.085961
| 3:32 | 5.3922 | 0.085516
| 3:32 | 5.3925 | 0.085072
| 3:32 | 5.3928 | 0.084633
| 3:32 | 5.3931 | 0.084217
| 3:32 | 5.3933 | 0.08381
| 3:32 | 5.3936 | 0.083411
| 3:32 | 5.3939 | 0.083015
| 3:32 | 5.3942 | 0.082622
| 3:32 | 5.3944 | 0.082234
| 3:32 | 5.3947 | 0.081849
| 3:32 | 5.395 | 0.081469
| 3:33 | 5.3953 | 0.081099
| 3:33 | 5.3956 | 0.08073
| 3:33 | 5.3958 | 0.080363
| 3:33 | 5.3961 | 0.079997
| 3:33 | 5.3964 | 0.079633
| 3:33 | 5.3967 | 0.079271
| 3:33 | 5.3969 | 0.078911
| 3:33 | 5.3972 | 0.078552
| 3:33 | 5.3975 | 0.078195
| 3:33 | 5.3978 | 0.077839
| 3:33 | 5.3981 | 0.077485
| 3:33 | 5.3983 | 0.077133
| 3:33 | 5.3986 | 0.076782
| 3:33 | 5.3989 | 0.076433
| 3:33 | 5.3992 | 0.076085
| 3:33 | 5.3994 | 0.075738
| 3:33 | 5.3997 | 0.07539
| 3:33 | 5.4 | 0.075022
| 3:33 | 5.4003 | 0.074642
| 3:33 | 5.4006 | 0.074254
| 3:33 | 5.4008 | 0.07386
| 3:33 | 5.4011 | 0.073461
| 3:33 | 5.4014 | 0.073065
| 3:33 | 5.4017 | 0.072672
| 3:33 | 5.4019 | 0.072283
| 3:33 | 5.4022 | 0.071896
| 3:33 | 5.4025 | 0.071513
| 3:33 | 5.4028 | 0.071133
| 3:33 | 5.4031 | 0.07076
| 3:33 | 5.4033 | 0.07039
| 3:33 | 5.4036 | 0.070029
| 3:33 | 5.4039 | 0.069674
| 3:33 | 5.4042 | 0.069327
| 3:33 | 5.4044 | 0.068994
| 3:33 | 5.4047 | 0.068667
| 3:33 | 5.405 | 0.06834
| 3:33 | 5.4053 | 0.068012
| 3:33 | 5.4056 | 0.067684
| 3:33 | 5.4058 | 0.067356
| 3:33 | 5.4061 | 0.067027
| 3:33 | 5.4064 | 0.066698
| 3:33 | 5.4067 | 0.066369
| 3:33 | 5.4069 | 0.066033
| 3:33 | 5.4072 | 0.065688
| 3:33 | 5.4075 | 0.065334
| 3:33 | 5.4078 | 0.064976
| 3:33 | 5.4081 | 0.064612
| 3:33 | 5.4083 | 0.064253
| 3:33 | 5.4086 | 0.063898
| 3:33 | 5.4089 | 0.063547
| 3:33 | 5.4092 | 0.063197
| 3:33 | 5.4094 | 0.062847
| 3:33 | 5.4097 | 0.062498
| 3:33 | 5.41 | 0.062149
| 3:33 | 5.4103 | 0.061801
| 3:33 | 5.4106 | 0.06146
| 3:33 | 5.4108 | 0.061118
| 3:33 | 5.4111 | 0.060772
| 3:33 | 5.4114 | 0.060419
| 3:34 | 5.4117 | 0.06006
| 3:34 | 5.4119 | 0.059682
| 3:34 | 5.4122 | 0.059295
| 3:34 | 5.4125 | 0.058904
| 3:34 | 5.4128 | 0.058511
| 3:34 | 5.4131 | 0.058114
| 3:34 | 5.4133 | 0.057726
| 3:34 | 5.4136 | 0.057345
| 3:34 | 5.4139 | 0.056972
| 3:34 | 5.4142 | 0.056607
| 3:34 | 5.4144 | 0.056249
| 3:34 | 5.4147 | 0.0559
| 3:34 | 5.415 | 0.055559
| 3:34 | 5.4153 | 0.055225
| 3:34 | 5.4156 | 0.0549
| 3:34 | 5.4158 | 0.054582
| 3:34 | 5.4161 | 0.054272
| 3:34 | 5.4164 | 0.053971
| 3:34 | 5.4167 | 0.053701
| 3:34 | 5.4169 | 0.053439
| 3:34 | 5.4172 | 0.053184
| 3:34 | 5.4175 | 0.052932
| 3:34 | 5.4178 | 0.052679
| 3:34 | 5.4181 | 0.052425
| 3:34 | 5.4183 | 0.05217
| 3:34 | 5.4186 | 0.051913
| 3:34 | 5.4189 | 0.051656
| 3:34 | 5.4192 | 0.051397
| 3:34 | 5.4194 | 0.051137
| 3:34 | 5.4197 | 0.050876
| 3:34 | 5.42 | 0.050611
| 3:34 | 5.4203 | 0.050341
| 3:34 | 5.4206 | 0.050065
| 3:34 | 5.4208 | 0.049783
| 3:34 | 5.4211 | 0.049497
| 3:34 | 5.4214 | 0.049209
| 3:34 | 5.4217 | 0.048918
| 3:34 | 5.4219 | 0.048625
| 3:34 | 5.4222 | 0.04833
| 3:34 | 5.4225 | 0.048033
| 3:34 | 5.4228 | 0.047733
| 3:34 | 5.4231 | 0.047431
| 3:34 | 5.4233 | 0.047127
| 3:34 | 5.4236 | 0.046821
| 3:34 | 5.4239 | 0.046512
| 3:34 | 5.4242 | 0.046201
| 3:34 | 5.4244 | 0.045886
| 3:34 | 5.4247 | 0.045568
| 3:34 | 5.425 | 0.045253
| 3:34 | 5.4253 | 0.044947
| 3:34 | 5.4256 | 0.044652
| 3:34 | 5.4258 | 0.044358
| 3:34 | 5.4261 | 0.044063
| 3:34 | 5.4264 | 0.043766
| 3:34 | 5.4267 | 0.043468
| 3:34 | 5.4269 | 0.043168
| 3:34 | 5.4272 | 0.042867
| 3:34 | 5.4275 | 0.042565
| 3:34 | 5.4278 | 0.042276
| 3:34 | 5.4281 | 0.041986
| 3:34 | 5.4283 | 0.041697
| 3:35 | 5.4286 | 0.041408
| 3:35 | 5.4289 | 0.041124
| 3:35 | 5.4292 | 0.040835
| 3:35 | 5.4294 | 0.040547
| 3:35 | 5.4297 | 0.040262
| 3:35 | 5.43 | 0.039978
| 3:35 | 5.4303 | 0.039697
| 3:35 | 5.4306 | 0.039418
| 3:35 | 5.4308 | 0.039142
| 3:35 | 5.4311 | 0.038868
| 3:35 | 5.4314 | 0.038596
| 3:35 | 5.4317 | 0.038326
| 3:35 | 5.4319 | 0.038059
| 3:35 | 5.4322 | 0.037794
| 3:35 | 5.4325 | 0.037527
| 3:35 | 5.4328 | 0.037257
| 3:35 | 5.4331 | 0.036983
| 3:35 | 5.4333 | 0.036698
| 3:35 | 5.4336 | 0.036407
| 3:35 | 5.4339 | 0.036111
| 3:35 | 5.4342 | 0.035811
| 3:35 | 5.4344 | 0.035512
| 3:35 | 5.4347 | 0.035218
| 3:35 | 5.435 | 0.034927
| 3:35 | 5.4353 | 0.034641
| 3:35 | 5.4356 | 0.034359
| 3:35 | 5.4358 | 0.034081
| 3:35 | 5.4361 | 0.033818
| 3:35 | 5.4364 | 0.033565
| 3:35 | 5.4367 | 0.03332
| 3:35 | 5.4369 | 0.033075
| 3:35 | 5.4372 | 0.032828
| 3:35 | 5.4375 | 0.03258
| 3:35 | 5.4378 | 0.03233
| 3:35 | 5.4381 | 0.032079
| 3:35 | 5.4383 | 0.031827
| 3:35 | 5.4386 | 0.031576
| 3:35 | 5.4389 | 0.031325
| 3:35 | 5.4392 | 0.031074
| 3:35 | 5.4394 | 0.030824
| 3:35 | 5.4397 | 0.030574
| 3:35 | 5.44 | 0.030324
| 3:35 | 5.4403 | 0.030076
| 3:35 | 5.4406 | 0.029827
| 3:35 | 5.4408 | 0.029578
| 3:35 | 5.4411 | 0.029329
| 3:35 | 5.4414 | 0.029079
| 3:35 | 5.4417 | 0.028822
| 3:35 | 5.4419 | 0.028554
| 3:35 | 5.4422 | 0.028288
| 3:35 | 5.4425 | 0.028038
| 3:35 | 5.4428 | 0.027799
| 3:35 | 5.4431 | 0.027567
| 3:35 | 5.4433 | 0.027339
| 3:35 | 5.4436 | 0.027117
| 3:35 | 5.4439 | 0.026901
| 3:35 | 5.4442 | 0.026694
| 3:35 | 5.4444 | 0.026493
| 3:35 | 5.4447 | 0.026294
| 3:36 | 5.445 | 0.026096
| 3:36 | 5.4453 | 0.025899
| 3:36 | 5.4456 | 0.025704
| 3:36 | 5.4458 | 0.025509
| 3:36 | 5.4461 | 0.025316
| 3:36 | 5.4464 | 0.025124
| 3:36 | 5.4467 | 0.024932
| 3:36 | 5.4469 | 0.024738
| 3:36 | 5.4472 | 0.024543
| 3:36 | 5.4475 | 0.024346
| 3:36 | 5.4478 | 0.024149
| 3:36 | 5.4481 | 0.02395
| 3:36 | 5.4483 | 0.023749
| 3:36 | 5.4486 | 0.023548
| 3:36 | 5.4489 | 0.023345
| 3:36 | 5.4492 | 0.023142
| 3:36 | 5.4494 | 0.022945
| 3:36 | 5.4497 | 0.022763
| 3:36 | 5.45 | 0.022589
| 3:36 | 5.4503 | 0.022421
| 3:36 | 5.4506 | 0.022248
| 3:36 | 5.4508 | 0.022065
| 3:36 | 5.4511 | 0.021869
| 3:36 | 5.4514 | 0.021663
| 3:36 | 5.4517 | 0.021448
| 3:36 | 5.4519 | 0.021215
| 3:36 | 5.4522 | 0.020973
| 3:36 | 5.4525 | 0.02073
| 3:36 | 5.4528 | 0.020492
| 3:36 | 5.4531 | 0.020257
| 3:36 | 5.4533 | 0.020027
| 3:36 | 5.4536 | 0.0198
| 3:36 | 5.4539 | 0.019578
| 3:36 | 5.4542 | 0.01936
| 3:36 | 5.4544 | 0.019147
| 3:36 | 5.4547 | 0.018946
| 3:36 | 5.455 | 0.018752
| 3:36 | 5.4553 | 0.018563
| 3:36 | 5.4556 | 0.018382
| 3:36 | 5.4558 | 0.018207
| 3:36 | 5.4561 | 0.018038
| 3:36 | 5.4564 | 0.017876
| 3:36 | 5.4567 | 0.017719
| 3:36 | 5.4569 | 0.017568
| 3:36 | 5.4572 | 0.017417
| 3:36 | 5.4575 | 0.01727
| 3:36 | 5.4578 | 0.017128
| 3:36 | 5.4581 | 0.016991
| 3:36 | 5.4583 | 0.016859
| 3:36 | 5.4586 | 0.016739
| 3:36 | 5.4589 | 0.016636
| 3:36 | 5.4592 | 0.016532
| 3:36 | 5.4594 | 0.016425
| 3:36 | 5.4597 | 0.016309
| 3:36 | 5.46 | 0.016179
| 3:36 | 5.4603 | 0.016043
| 3:36 | 5.4606 | 0.015899
| 3:36 | 5.4608 | 0.015751
| 3:36 | 5.4611 | 0.015603
| 3:36 | 5.4614 | 0.015452
| 3:36 | 5.4617 | 0.015292
| 3:37 | 5.4619 | 0.015129
| 3:37 | 5.4622 | 0.014965
| 3:37 | 5.4625 | 0.014799
| 3:37 | 5.4628 | 0.014633
| 3:37 | 5.4631 | 0.014468
| 3:37 | 5.4633 | 0.014308
| 3:37 | 5.4636 | 0.014153
| 3:37 | 5.4639 | 0.014002
| 3:37 | 5.4642 | 0.013856
| 3:37 | 5.4644 | 0.013714
| 3:37 | 5.4647 | 0.013577
| 3:37 | 5.465 | 0.013445
| 3:37 | 5.4653 | 0.013318
| 3:37 | 5.4656 | 0.013195
| 3:37 | 5.4658 | 0.013073
| 3:37 | 5.4661 | 0.012942
| 3:37 | 5.4664 | 0.012799
| 3:37 | 5.4667 | 0.012651
| 3:37 | 5.4669 | 0.012501
| 3:37 | 5.4672 | 0.012363
| 3:37 | 5.4675 | 0.012219
| 3:37 | 5.4678 | 0.012068
| 3:37 | 5.4681 | 0.01191
| 3:37 | 5.4683 | 0.01176
| 3:37 | 5.4686 | 0.011625
| 3:37 | 5.4689 | 0.011501
| 3:37 | 5.4692 | 0.011385
| 3:37 | 5.4694 | 0.011269
| 3:37 | 5.4697 | 0.011154
| 3:37 | 5.47 | 0.01104
| 3:37 | 5.4703 | 0.010926
| 3:37 | 5.4706 | 0.010823
| 3:37 | 5.4708 | 0.010736
| 3:37 | 5.4711 | 0.010664
| 3:37 | 5.4714 | 0.010592
| 3:37 | 5.4717 | 0.010517
| 3:37 | 5.4719 | 0.010439
| 3:37 | 5.4722 | 0.010358
| 3:37 | 5.4725 | 0.010274
| 3:37 | 5.4728 | 0.010188
| 3:37 | 5.4731 | 0.010098
| 3:37 | 5.4733 | 0.010006
| 3:37 | 5.4736 | 0.0099121
| 3:37 | 5.4739 | 0.0098453
| 3:37 | 5.4742 | 0.0097612
| 3:37 | 5.4744 | 0.009659
| 3:37 | 5.4747 | 0.0095478
| 3:37 | 5.475 | 0.0094434
| 3:37 | 5.4753 | 0.0093679
| 3:37 | 5.4756 | 0.0093148
| 3:37 | 5.4758 | 0.0092692
| 3:37 | 5.4761 | 0.0092217
| 3:37 | 5.4764 | 0.0091722
| 3:37 | 5.4767 | 0.0091209
| 3:37 | 5.4769 | 0.0090676
| 3:37 | 5.4772 | 0.0090124
| 3:37 | 5.4775 | 0.0089731
| 3:37 | 5.4778 | 0.0089211
| 3:37 | 5.4781 | 0.0088669
| 3:38 | 5.4783 | 0.0088146
| 3:38 | 5.4786 | 0.0087642
| 3:38 | 5.4789 | 0.0087152
| 3:38 | 5.4792 | 0.0086567
| 3:38 | 5.4794 | 0.0085941
| 3:38 | 5.4797 | 0.0085361
| 3:38 | 5.48 | 0.0084919
| 3:38 | 5.4803 | 0.0084614
| 3:38 | 5.4806 | 0.0084445
| 3:38 | 5.4808 | 0.0084414
| 3:38 | 5.4811 | 0.008452
| 3:38 | 5.4814 | 0.0084763
| 3:38 | 5.4817 | 0.0085143
| 3:38 | 5.4819 | 0.008566
| 3:38 | 5.4822 | 0.0086314
| 3:38 | 5.4825 | 0.0087046
| 3:38 | 5.4828 | 0.0087772
| 3:38 | 5.4831 | 0.0088491
| 3:38 | 5.4833 | 0.0089203
| 3:38 | 5.4836 | 0.0089903
| 3:38 | 5.4839 | 0.0090717
| 3:38 | 5.4842 | 0.009137
| 3:38 | 5.4844 | 0.0092116
| 3:38 | 5.4847 | 0.0092662
| 3:38 | 5.485 | 0.0093095
| 3:38 | 5.4853 | 0.0093725
| 3:38 | 5.4856 | 0.009455
| 3:38 | 5.4858 | 0.0095431
| 3:38 | 5.4861 | 0.0096275
| 3:38 | 5.4864 | 0.0097081
| 3:38 | 5.4867 | 0.0097851
| 3:38 | 5.4869 | 0.0098583
| 3:38 | 5.4872 | 0.0099144
| 3:38 | 5.4875 | 0.0099508
| 3:38 | 5.4878 | 0.009964
| 3:38 | 5.4881 | 0.0099594
| 3:38 | 5.4883 | 0.0099385
| 3:38 | 5.4886 | 0.0099013
| 3:38 | 5.4889 | 0.0098477
| 3:38 | 5.4892 | 0.0097779
| 3:38 | 5.4894 | 0.0096918
| 3:38 | 5.4897 | 0.0095893
| 3:38 | 5.49 | 0.0094706
| 3:38 | 5.4903 | 0.0093555
| 3:38 | 5.4906 | 0.0092545
| 3:38 | 5.4908 | 0.0091496
| 3:38 | 5.4911 | 0.0090354
| 3:38 | 5.4914 | 0.0089044
| 3:38 | 5.4917 | 0.0087549
| 3:38 | 5.4919 | 0.0086028
| 3:38 | 5.4922 | 0.0084519
| 3:38 | 5.4925 | 0.0083022
| 3:38 | 5.4928 | 0.0081539
| 3:38 | 5.4931 | 0.0080127
| 3:38 | 5.4933 | 0.0078723
| 3:38 | 5.4936 | 0.0077321
| 3:38 | 5.4939 | 0.0075965
| 3:38 | 5.4942 | 0.0074654
| 3:38 | 5.4944 | 0.007339
| 3:38 | 5.4947 | 0.0072215
| 3:38 | 5.495 | 0.0071207
| 3:39 | 5.4953 | 0.0070266
| 3:39 | 5.4956 | 0.0069434
| 3:39 | 5.4958 | 0.0068842
| 3:39 | 5.4961 | 0.0068413
| 3:39 | 5.4964 | 0.0068087
| 3:39 | 5.4967 | 0.0067799
| 3:39 | 5.4969 | 0.0067547
| 3:39 | 5.4972 | 0.0067332
| 3:39 | 5.4975 | 0.0067154
| 3:39 | 5.4978 | 0.0067012
| 3:39 | 5.4981 | 0.0066908
| 3:39 | 5.4983 | 0.006684
| 3:39 | 5.4986 | 0.0066808
| 3:39 | 5.4989 | 0.0066814
| 3:39 | 5.4992 | 0.0066856
| 3:39 | 5.4994 | 0.0066935
| 3:39 | 5.4997 | 0.006705
| 3:39 | 5.5 | 0.0067208
| 3:39 | 5.5003 | 0.0067642
| 3:39 | 5.5006 | 0.0068397
| 3:39 | 5.5008 | 0.0069466
| 3:39 | 5.5011 | 0.0070832
| 3:39 | 5.5014 | 0.0072345
| 3:39 | 5.5017 | 0.0074021
| 3:39 | 5.5019 | 0.0075793
| 3:39 | 5.5022 | 0.0077623
| 3:39 | 5.5025 | 0.0079439
| 3:39 | 5.5028 | 0.0081241
| 3:39 | 5.5031 | 0.0083028
| 3:39 | 5.5033 | 0.0084802
| 3:39 | 5.5036 | 0.0086328
| 3:39 | 5.5039 | 0.0087603
| 3:39 | 5.5042 | 0.0088857
| 3:39 | 5.5044 | 0.009009
| 3:39 | 5.5047 | 0.0091301
| 3:39 | 5.505 | 0.009249
| 3:39 | 5.5053 | 0.0093658
| 3:39 | 5.5056 | 0.0094805
| 3:39 | 5.5058 | 0.009593
| 3:39 | 5.5061 | 0.0097033
| 3:39 | 5.5064 | 0.0098115
| 3:39 | 5.5067 | 0.0099175
| 3:39 | 5.5069 | 0.010009
| 3:39 | 5.5072 | 0.010074
| 3:39 | 5.5075 | 0.010096
| 3:39 | 5.5078 | 0.010068
| 3:39 | 5.5081 | 0.010005
| 3:39 | 5.5083 | 0.0099398
| 3:39 | 5.5086 | 0.009878
| 3:39 | 5.5089 | 0.0098195
| 3:39 | 5.5092 | 0.0097644
| 3:39 | 5.5094 | 0.0097164
| 3:39 | 5.5097 | 0.0096791
| 3:39 | 5.51 | 0.0096494
| 3:39 | 5.5103 | 0.0096274
| 3:39 | 5.5106 | 0.0096255
| 3:39 | 5.5108 | 0.0096377
| 3:39 | 5.5111 | 0.0096603
| 3:39 | 5.5114 | 0.0096813
| 3:40 | 5.5117 | 0.0096988
| 3:40 | 5.5119 | 0.0097128
| 3:40 | 5.5122 | 0.0097192
| 3:40 | 5.5125 | 0.0097252
| 3:40 | 5.5128 | 0.009731
| 3:40 | 5.5131 | 0.0097387
| 3:40 | 5.5133 | 0.0097559
| 3:40 | 5.5136 | 0.0097833
| 3:40 | 5.5139 | 0.0098211
| 3:40 | 5.5142 | 0.0098692
| 3:40 | 5.5144 | 0.0099276
| 3:40 | 5.5147 | 0.0099963
| 3:40 | 5.515 | 0.010075
| 3:40 | 5.5153 | 0.010165
| 3:40 | 5.5156 | 0.010264
| 3:40 | 5.5158 | 0.010372
| 3:40 | 5.5161 | 0.01048
| 3:40 | 5.5164 | 0.010586
| 3:40 | 5.5167 | 0.010691
| 3:40 | 5.5169 | 0.010795
| 3:40 | 5.5172 | 0.010889
| 3:40 | 5.5175 | 0.010972
| 3:40 | 5.5178 | 0.011049
| 3:40 | 5.5181 | 0.011114
| 3:40 | 5.5183 | 0.011169
| 3:40 | 5.5186 | 0.011216
| 3:40 | 5.5189 | 0.011233
| 3:40 | 5.5192 | 0.011238
| 3:40 | 5.5194 | 0.011238
| 3:40 | 5.5197 | 0.011234
| 3:40 | 5.52 | 0.011225
| 3:40 | 5.5203 | 0.011196
| 3:40 | 5.5206 | 0.011148
| 3:40 | 5.5208 | 0.011096
| 3:40 | 5.5211 | 0.01104
| 3:40 | 5.5214 | 0.010978
| 3:40 | 5.5217 | 0.01091
| 3:40 | 5.5219 | 0.010835
| 3:40 | 5.5222 | 0.010754
| 3:40 | 5.5225 | 0.010667
| 3:40 | 5.5228 | 0.010574
| 3:40 | 5.5231 | 0.010475
| 3:40 | 5.5233 | 0.010369
| 3:40 | 5.5236 | 0.010253
| 3:40 | 5.5239 | 0.010127
| 3:40 | 5.5242 | 0.0099649
| 3:40 | 5.5244 | 0.0097982
| 3:40 | 5.5247 | 0.0096059
| 3:40 | 5.525 | 0.0093992
| 3:40 | 5.5253 | 0.0091994
| 3:40 | 5.5256 | 0.009014
| 3:40 | 5.5258 | 0.0088402
| 3:40 | 5.5261 | 0.0086957
| 3:40 | 5.5264 | 0.0085843
| 3:40 | 5.5267 | 0.0084987
| 3:40 | 5.5269 | 0.0084281
| 3:40 | 5.5272 | 0.0083595
| 3:40 | 5.5275 | 0.0082929
| 3:40 | 5.5278 | 0.0082282
| 3:40 | 5.5281 | 0.0081661
| 3:41 | 5.5283 | 0.0081128
| 3:41 | 5.5286 | 0.008054
| 3:41 | 5.5289 | 0.0079897
| 3:41 | 5.5292 | 0.0079063
| 3:41 | 5.5294 | 0.007813
| 3:41 | 5.5297 | 0.0076924
| 3:41 | 5.53 | 0.0075654
| 3:41 | 5.5303 | 0.00744
| 3:41 | 5.5306 | 0.0073162
| 3:41 | 5.5308 | 0.007194
| 3:41 | 5.5311 | 0.0070734
| 3:41 | 5.5314 | 0.0069544
| 3:41 | 5.5317 | 0.006837
| 3:41 | 5.5319 | 0.0067213
| 3:41 | 5.5322 | 0.0066066
| 3:41 | 5.5325 | 0.0064863
| 3:41 | 5.5328 | 0.0063602
| 3:41 | 5.5331 | 0.0062285
| 3:41 | 5.5333 | 0.0060953
| 3:41 | 5.5336 | 0.0059641
| 3:41 | 5.5339 | 0.0058348
| 3:41 | 5.5342 | 0.0056965
| 3:41 | 5.5344 | 0.0055652
| 3:41 | 5.5347 | 0.0054345
| 3:41 | 5.535 | 0.0053045
| 3:41 | 5.5353 | 0.0051752
| 3:41 | 5.5356 | 0.0050464
| 3:41 | 5.5358 | 0.0049268
| 3:41 | 5.5361 | 0.0048174
| 3:41 | 5.5364 | 0.0047275
| 3:41 | 5.5367 | 0.0046487
| 3:41 | 5.5369 | 0.0045805
| 3:41 | 5.5372 | 0.0045247
| 3:41 | 5.5375 | 0.0044759
| 3:41 | 5.5378 | 0.0044328
| 3:41 | 5.5381 | 0.0043878
| 3:41 | 5.5383 | 0.0043427
| 3:41 | 5.5386 | 0.004302
| 3:41 | 5.5389 | 0.0042654
| 3:41 | 5.5392 | 0.0042331
| 3:41 | 5.5394 | 0.004205
| 3:41 | 5.5397 | 0.0041811
| 3:41 | 5.54 | 0.0041615
| 3:41 | 5.5403 | 0.0041461
| 3:41 | 5.5406 | 0.0041301
| 3:41 | 5.5408 | 0.0041125
| 3:41 | 5.5411 | 0.0040933
| 3:41 | 5.5414 | 0.0040724
| 3:41 | 5.5417 | 0.0040498
| 3:41 | 5.5419 | 0.0040256
| 3:41 | 5.5422 | 0.0040071
| 3:41 | 5.5425 | 0.003997
| 3:41 | 5.5428 | 0.0039991
| 3:41 | 5.5431 | 0.004007
| 3:41 | 5.5433 | 0.0040196
| 3:41 | 5.5436 | 0.0040338
| 3:41 | 5.5439 | 0.0040497
| 3:41 | 5.5442 | 0.0040622
| 3:41 | 5.5444 | 0.0040775
| 3:41 | 5.5447 | 0.0040988
| 3:42 | 5.545 | 0.0041208
| 3:42 | 5.5453 | 0.0041437
| 3:42 | 5.5456 | 0.0041575
| 3:42 | 5.5458 | 0.0041555
| 3:42 | 5.5461 | 0.0041492
| 3:42 | 5.5464 | 0.0041405
| 3:42 | 5.5467 | 0.0041251
| 3:42 | 5.5469 | 0.0041012
| 3:42 | 5.5472 | 0.004069
| 3:42 | 5.5475 | 0.0040285
| 3:42 | 5.5478 | 0.0039796
| 3:42 | 5.5481 | 0.0039223
| 3:42 | 5.5483 | 0.0038567
| 3:42 | 5.5486 | 0.0037827
| 3:42 | 5.5489 | 0.0037004
| 3:42 | 5.5492 | 0.0036175
| 3:42 | 5.5494 | 0.0035375
| 3:42 | 5.5497 | 0.003476
| 3:42 | 5.55 | 0.0034365
| 3:42 | 5.5503 | 0.0034049
| 3:42 | 5.5506 | 0.0033813
| 3:42 | 5.5508 | 0.0033658
| 3:42 | 5.5511 | 0.00336
| 3:42 | 5.5514 | 0.0033702
| 3:42 | 5.5517 | 0.0033895
| 3:42 | 5.5519 | 0.0034093
| 3:42 | 5.5522 | 0.0034294
| 3:42 | 5.5525 | 0.0034493
| 3:42 | 5.5528 | 0.0034662
| 3:42 | 5.5531 | 0.00348
| 3:42 | 5.5533 | 0.003492
| 3:42 | 5.5536 | 0.0035055
| 3:42 | 5.5539 | 0.003535
| 3:42 | 5.5542 | 0.0035887
| 3:42 | 5.5544 | 0.0036496
| 3:42 | 5.5547 | 0.0037101
| 3:42 | 5.555 | 0.0037701
| 3:42 | 5.5553 | 0.0038297
| 3:42 | 5.5556 | 0.0038889
| 3:42 | 5.5558 | 0.0039476
| 3:42 | 5.5561 | 0.0040059
| 3:42 | 5.5564 | 0.0040637
| 3:42 | 5.5567 | 0.0041211
| 3:42 | 5.5569 | 0.004164
| 3:42 | 5.5572 | 0.0042131
| 3:42 | 5.5575 | 0.0042668
| 3:42 | 5.5578 | 0.0043298
| 3:42 | 5.5581 | 0.0044048
| 3:42 | 5.5583 | 0.0044876
| 3:42 | 5.5586 | 0.0045711
| 3:42 | 5.5589 | 0.0046552
| 3:42 | 5.5592 | 0.0047399
| 3:42 | 5.5594 | 0.0048282
| 3:42 | 5.5597 | 0.0049199
| 3:42 | 5.56 | 0.0050122
| 3:42 | 5.5603 | 0.0051052
| 3:42 | 5.5606 | 0.0051898
| 3:42 | 5.5608 | 0.0052581
| 3:42 | 5.5611 | 0.0053162
| 3:42 | 5.5614 | 0.0053726
| 3:42 | 5.5617 | 0.0054353
| 3:43 | 5.5619 | 0.0055015
| 3:43 | 5.5622 | 0.0055713
| 3:43 | 5.5625 | 0.0056447
| 3:43 | 5.5628 | 0.0057215
| 3:43 | 5.5631 | 0.0058015
| 3:43 | 5.5633 | 0.0058781
| 3:43 | 5.5636 | 0.0059495
| 3:43 | 5.5639 | 0.0060157
| 3:43 | 5.5642 | 0.0060767
| 3:43 | 5.5644 | 0.0061323
| 3:43 | 5.5647 | 0.0061828
| 3:43 | 5.565 | 0.006228
| 3:43 | 5.5653 | 0.006268
| 3:43 | 5.5656 | 0.0063028
| 3:43 | 5.5658 | 0.0063323
| 3:43 | 5.5661 | 0.0063602
| 3:43 | 5.5664 | 0.0063838
| 3:43 | 5.5667 | 0.0064033
| 3:43 | 5.5669 | 0.0064227
| 3:43 | 5.5672 | 0.0064431
| 3:43 | 5.5675 | 0.0064645
| 3:43 | 5.5678 | 0.0064888
| 3:43 | 5.5681 | 0.0065183
| 3:43 | 5.5683 | 0.0065497
| 3:43 | 5.5686 | 0.0065831
| 3:43 | 5.5689 | 0.0066185
| 3:43 | 5.5692 | 0.0066503
| 3:43 | 5.5694 | 0.006677
| 3:43 | 5.5697 | 0.0066986
| 3:43 | 5.57 | 0.0067162
| 3:43 | 5.5703 | 0.0067333
| 3:43 | 5.5706 | 0.0067537
| 3:43 | 5.5708 | 0.0067644
| 3:43 | 5.5711 | 0.0067742
| 3:43 | 5.5714 | 0.0067832
| 3:43 | 5.5717 | 0.0067914
| 3:43 | 5.5719 | 0.0067987
| 3:43 | 5.5722 | 0.0068053
| 3:43 | 5.5725 | 0.006811
| 3:43 | 5.5728 | 0.0068158
| 3:43 | 5.5731 | 0.0068199
| 3:43 | 5.5733 | 0.0068231
| 3:43 | 5.5736 | 0.0068254
| 3:43 | 5.5739 | 0.0068243
| 3:43 | 5.5742 | 0.0068192
| 3:43 | 5.5744 | 0.0068135
| 3:43 | 5.5747 | 0.0068073
| 3:43 | 5.575 | 0.0068006
| 3:43 | 5.5753 | 0.0067931
| 3:43 | 5.5756 | 0.006778
| 3:43 | 5.5758 | 0.0067626
| 3:43 | 5.5761 | 0.006742
| 3:43 | 5.5764 | 0.0067176
| 3:43 | 5.5767 | 0.0066967
| 3:43 | 5.5769 | 0.0066793
| 3:43 | 5.5772 | 0.0066655
| 3:43 | 5.5775 | 0.0066553
| 3:43 | 5.5778 | 0.0066659
| 3:43 | 5.5781 | 0.0066823
| 3:44 | 5.5783 | 0.0067044
| 3:44 | 5.5786 | 0.0067309
| 3:44 | 5.5789 | 0.0067603
| 3:44 | 5.5792 | 0.0067924
| 3:44 | 5.5794 | 0.0068273
| 3:44 | 5.5797 | 0.0068676
| 3:44 | 5.58 | 0.0069181
| 3:44 | 5.5803 | 0.0069788
| 3:44 | 5.5806 | 0.0070496
| 3:44 | 5.5808 | 0.0071306
| 3:44 | 5.5811 | 0.0072217
| 3:44 | 5.5814 | 0.0073229
| 3:44 | 5.5817 | 0.0074344
| 3:44 | 5.5819 | 0.0075559
| 3:44 | 5.5822 | 0.0076876
| 3:44 | 5.5825 | 0.0078359
| 3:44 | 5.5828 | 0.0080113
| 3:44 | 5.5831 | 0.0082143
| 3:44 | 5.5833 | 0.008425
| 3:44 | 5.5836 | 0.0086407
| 3:44 | 5.5839 | 0.0088667
| 3:44 | 5.5842 | 0.009109
| 3:44 | 5.5844 | 0.0093706
| 3:44 | 5.5847 | 0.0096514
| 3:44 | 5.585 | 0.00994
| 3:44 | 5.5853 | 0.010232
| 3:44 | 5.5856 | 0.010526
| 3:44 | 5.5858 | 0.010824
| 3:44 | 5.5861 | 0.011124
| 3:44 | 5.5864 | 0.011427
| 3:44 | 5.5867 | 0.011734
| 3:44 | 5.5869 | 0.012043
| 3:44 | 5.5872 | 0.012367
| 3:44 | 5.5875 | 0.012701
| 3:44 | 5.5878 | 0.013054
| 3:44 | 5.5881 | 0.01342
| 3:44 | 5.5883 | 0.01379
| 3:44 | 5.5886 | 0.014164
| 3:44 | 5.5889 | 0.014542
| 3:44 | 5.5892 | 0.014923
| 3:44 | 5.5894 | 0.015309
| 3:44 | 5.5897 | 0.015698
| 3:44 | 5.59 | 0.016091
| 3:44 | 5.5903 | 0.016487
| 3:44 | 5.5906 | 0.016888
| 3:44 | 5.5908 | 0.017295
| 3:44 | 5.5911 | 0.017708
| 3:44 | 5.5914 | 0.018121
| 3:44 | 5.5917 | 0.018535
| 3:44 | 5.5919 | 0.018949
| 3:44 | 5.5922 | 0.019363
| 3:44 | 5.5925 | 0.019778
| 3:44 | 5.5928 | 0.020182
| 3:44 | 5.5931 | 0.02059
| 3:44 | 5.5933 | 0.021001
| 3:44 | 5.5936 | 0.021415
| 3:44 | 5.5939 | 0.021832
| 3:44 | 5.5942 | 0.022253
| 3:44 | 5.5944 | 0.022678
| 3:44 | 5.5947 | 0.02311
| 3:44 | 5.595 | 0.023544
| 3:45 | 5.5953 | 0.023982
| 3:45 | 5.5956 | 0.024423
| 3:45 | 5.5958 | 0.024867
| 3:45 | 5.5961 | 0.025315
| 3:45 | 5.5964 | 0.025765
| 3:45 | 5.5967 | 0.026214
| 3:45 | 5.5969 | 0.026658
| 3:45 | 5.5972 | 0.0271
| 3:45 | 5.5975 | 0.027538
| 3:45 | 5.5978 | 0.027973
| 3:45 | 5.5981 | 0.028404
| 3:45 | 5.5983 | 0.028833
| 3:45 | 5.5986 | 0.029257
| 3:45 | 5.5989 | 0.029679
| 3:45 | 5.5992 | 0.030097
| 3:45 | 5.5994 | 0.030516
| 3:45 | 5.5997 | 0.030926
| 3:45 | 5.6 | 0.031329
| 3:45 | 5.6003 | 0.031731
| 3:45 | 5.6006 | 0.032131
| 3:45 | 5.6008 | 0.032526
| 3:45 | 5.6011 | 0.03291
| 3:45 | 5.6014 | 0.033284
| 3:45 | 5.6017 | 0.03366
| 3:45 | 5.6019 | 0.034038
| 3:45 | 5.6022 | 0.034419
| 3:45 | 5.6025 | 0.034805
| 3:45 | 5.6028 | 0.035195
| 3:45 | 5.6031 | 0.035591
| 3:45 | 5.6033 | 0.035978
| 3:45 | 5.6036 | 0.036345
| 3:45 | 5.6039 | 0.036684
| 3:45 | 5.6042 | 0.036999
| 3:45 | 5.6044 | 0.037305
| 3:45 | 5.6047 | 0.037606
| 3:45 | 5.605 | 0.037907
| 3:45 | 5.6053 | 0.038208
| 3:45 | 5.6056 | 0.03851
| 3:45 | 5.6058 | 0.038811
| 3:45 | 5.6061 | 0.039113
| 3:45 | 5.6064 | 0.039415
| 3:45 | 5.6067 | 0.039716
| 3:45 | 5.6069 | 0.040018
| 3:45 | 5.6072 | 0.04032
| 3:45 | 5.6075 | 0.040638
| 3:45 | 5.6078 | 0.04097
| 3:45 | 5.6081 | 0.041303
| 3:45 | 5.6083 | 0.04163
| 3:45 | 5.6086 | 0.041946
| 3:45 | 5.6089 | 0.042253
| 3:45 | 5.6092 | 0.042547
| 3:45 | 5.6094 | 0.042811
| 3:45 | 5.6097 | 0.043035
| 3:45 | 5.61 | 0.043259
| 3:45 | 5.6103 | 0.043545
| 3:45 | 5.6106 | 0.043907
| 3:45 | 5.6108 | 0.044324
| 3:45 | 5.6111 | 0.044772
| 3:45 | 5.6114 | 0.045238
| 3:46 | 5.6117 | 0.045711
| 3:46 | 5.6119 | 0.046184
| 3:46 | 5.6122 | 0.046656
| 3:46 | 5.6125 | 0.047128
| 3:46 | 5.6128 | 0.0476
| 3:46 | 5.6131 | 0.048072
| 3:46 | 5.6133 | 0.048547
| 3:46 | 5.6136 | 0.049024
| 3:46 | 5.6139 | 0.049504
| 3:46 | 5.6142 | 0.049986
| 3:46 | 5.6144 | 0.050471
| 3:46 | 5.6147 | 0.050959
| 3:46 | 5.615 | 0.051449
| 3:46 | 5.6153 | 0.051942
| 3:46 | 5.6156 | 0.052438
| 3:46 | 5.6158 | 0.052936
| 3:46 | 5.6161 | 0.053433
| 3:46 | 5.6164 | 0.053931
| 3:46 | 5.6167 | 0.054429
| 3:46 | 5.6169 | 0.054927
| 3:46 | 5.6172 | 0.055425
| 3:46 | 5.6175 | 0.055923
| 3:46 | 5.6178 | 0.056421
| 3:46 | 5.6181 | 0.056919
| 3:46 | 5.6183 | 0.057418
| 3:46 | 5.6186 | 0.057916
| 3:46 | 5.6189 | 0.058415
| 3:46 | 5.6192 | 0.058913
| 3:46 | 5.6194 | 0.059413
| 3:46 | 5.6197 | 0.059914
| 3:46 | 5.62 | 0.060409
| 3:46 | 5.6203 | 0.060908
| 3:46 | 5.6206 | 0.06141
| 3:46 | 5.6208 | 0.061914
| 3:46 | 5.6211 | 0.062419
| 3:46 | 5.6214 | 0.062925
| 3:46 | 5.6217 | 0.063431
| 3:46 | 5.6219 | 0.063938
| 3:46 | 5.6222 | 0.064445
| 3:46 | 5.6225 | 0.064954
| 3:46 | 5.6228 | 0.065463
| 3:46 | 5.6231 | 0.065972
| 3:46 | 5.6233 | 0.066483
| 3:46 | 5.6236 | 0.066994
| 3:46 | 5.6239 | 0.06751
| 3:46 | 5.6242 | 0.068029
| 3:46 | 5.6244 | 0.068549
| 3:46 | 5.6247 | 0.069072
| 3:46 | 5.625 | 0.069596
| 3:46 | 5.6253 | 0.070123
| 3:46 | 5.6256 | 0.070652
| 3:46 | 5.6258 | 0.071179
| 3:46 | 5.6261 | 0.071705
| 3:46 | 5.6264 | 0.072229
| 3:46 | 5.6267 | 0.072752
| 3:46 | 5.6269 | 0.073274
| 3:46 | 5.6272 | 0.073794
| 3:46 | 5.6275 | 0.074311
| 3:46 | 5.6278 | 0.074818
| 3:46 | 5.6281 | 0.075315
| 3:46 | 5.6283 | 0.075804
| 3:47 | 5.6286 | 0.076284
| 3:47 | 5.6289 | 0.076759
| 3:47 | 5.6292 | 0.077229
| 3:47 | 5.6294 | 0.077694
| 3:47 | 5.6297 | 0.078154
| 3:47 | 5.63 | 0.078609
| 3:47 | 5.6303 | 0.079061
| 3:47 | 5.6306 | 0.07951
| 3:47 | 5.6308 | 0.079956
| 3:47 | 5.6311 | 0.080398
| 3:47 | 5.6314 | 0.080837
| 3:47 | 5.6317 | 0.081273
| 3:47 | 5.6319 | 0.081705
| 3:47 | 5.6322 | 0.082133
| 3:47 | 5.6325 | 0.082562
| 3:47 | 5.6328 | 0.082997
| 3:47 | 5.6331 | 0.08344
| 3:47 | 5.6333 | 0.083891
| 3:47 | 5.6336 | 0.08435
| 3:47 | 5.6339 | 0.084814
| 3:47 | 5.6342 | 0.085276
| 3:47 | 5.6344 | 0.085737
| 3:47 | 5.6347 | 0.086197
| 3:47 | 5.635 | 0.086656
| 3:47 | 5.6353 | 0.087113
| 3:47 | 5.6356 | 0.087554
| 3:47 | 5.6358 | 0.087959
| 3:47 | 5.6361 | 0.088317
| 3:47 | 5.6364 | 0.088653
| 3:47 | 5.6367 | 0.088961
| 3:47 | 5.6369 | 0.089276
| 3:47 | 5.6372 | 0.089598
| 3:47 | 5.6375 | 0.089932
| 3:47 | 5.6378 | 0.090278
| 3:47 | 5.6381 | 0.090634
| 3:47 | 5.6383 | 0.091
| 3:47 | 5.6386 | 0.091375
| 3:47 | 5.6389 | 0.091759
| 3:47 | 5.6392 | 0.092152
| 3:47 | 5.6394 | 0.092555
| 3:47 | 5.6397 | 0.092968
| 3:47 | 5.64 | 0.093389
| 3:47 | 5.6403 | 0.093839
| 3:47 | 5.6406 | 0.094311
| 3:47 | 5.6408 | 0.094795
| 3:47 | 5.6411 | 0.095291
| 3:47 | 5.6414 | 0.095796
| 3:47 | 5.6417 | 0.096303
| 3:47 | 5.6419 | 0.096814
| 3:47 | 5.6422 | 0.097343
| 3:47 | 5.6425 | 0.097878
| 3:47 | 5.6428 | 0.098413
| 3:47 | 5.6431 | 0.09895
| 3:47 | 5.6433 | 0.099486
| 3:47 | 5.6436 | 0.10002
| 3:47 | 5.6439 | 0.10056
| 3:47 | 5.6442 | 0.1011
| 3:47 | 5.6444 | 0.10164
| 3:47 | 5.6447 | 0.10218
| 3:48 | 5.645 | 0.10272
| 3:48 | 5.6453 | 0.10326
| 3:48 | 5.6456 | 0.1038
| 3:48 | 5.6458 | 0.10434
| 3:48 | 5.6461 | 0.10488
| 3:48 | 5.6464 | 0.10543
| 3:48 | 5.6467 | 0.10597
| 3:48 | 5.6469 | 0.10651
| 3:48 | 5.6472 | 0.10705
| 3:48 | 5.6475 | 0.10759
| 3:48 | 5.6478 | 0.10812
| 3:48 | 5.6481 | 0.10866
| 3:48 | 5.6483 | 0.1092
| 3:48 | 5.6486 | 0.10974
| 3:48 | 5.6489 | 0.11027
| 3:48 | 5.6492 | 0.11081
| 3:48 | 5.6494 | 0.11134
| 3:48 | 5.6497 | 0.11187
| 3:48 | 5.65 | 0.1124
| 3:48 | 5.6503 | 0.11293
| 3:48 | 5.6506 | 0.11345
| 3:48 | 5.6508 | 0.11398
| 3:48 | 5.6511 | 0.1145
| 3:48 | 5.6514 | 0.11502
| 3:48 | 5.6517 | 0.11554
| 3:48 | 5.6519 | 0.11606
| 3:48 | 5.6522 | 0.11658
| 3:48 | 5.6525 | 0.11709
| 3:48 | 5.6528 | 0.11761
| 3:48 | 5.6531 | 0.11812
| 3:48 | 5.6533 | 0.11862
| 3:48 | 5.6536 | 0.11913
| 3:48 | 5.6539 | 0.11964
| 3:48 | 5.6542 | 0.12015
| 3:48 | 5.6544 | 0.12065
| 3:48 | 5.6547 | 0.12116
| 3:48 | 5.655 | 0.12167
| 3:48 | 5.6553 | 0.12218
| 3:48 | 5.6556 | 0.1227
| 3:48 | 5.6558 | 0.12321
| 3:48 | 5.6561 | 0.12373
| 3:48 | 5.6564 | 0.12424
| 3:48 | 5.6567 | 0.12476
| 3:48 | 5.6569 | 0.12529
| 3:48 | 5.6572 | 0.1258
| 3:48 | 5.6575 | 0.12632
| 3:48 | 5.6578 | 0.12684
| 3:48 | 5.6581 | 0.12737
| 3:48 | 5.6583 | 0.12789
| 3:48 | 5.6586 | 0.12841
| 3:48 | 5.6589 | 0.12893
| 3:48 | 5.6592 | 0.12945
| 3:48 | 5.6594 | 0.12998
| 3:48 | 5.6597 | 0.1305
| 3:48 | 5.66 | 0.13102
| 3:48 | 5.6603 | 0.13153
| 3:48 | 5.6606 | 0.13203
| 3:48 | 5.6608 | 0.13252
| 3:48 | 5.6611 | 0.133
| 3:48 | 5.6614 | 0.13347
| 3:48 | 5.6617 | 0.13393
| 3:49 | 5.6619 | 0.1344
| 3:49 | 5.6622 | 0.1349
| 3:49 | 5.6625 | 0.1354
| 3:49 | 5.6628 | 0.13591
| 3:49 | 5.6631 | 0.13641
| 3:49 | 5.6633 | 0.13692
| 3:49 | 5.6636 | 0.13743
| 3:49 | 5.6639 | 0.13793
| 3:49 | 5.6642 | 0.13844
| 3:49 | 5.6644 | 0.13893
| 3:49 | 5.6647 | 0.13943
| 3:49 | 5.665 | 0.13992
| 3:49 | 5.6653 | 0.14042
| 3:49 | 5.6656 | 0.1409
| 3:49 | 5.6658 | 0.14139
| 3:49 | 5.6661 | 0.1419
| 3:49 | 5.6664 | 0.1424
| 3:49 | 5.6667 | 0.14289
| 3:49 | 5.6669 | 0.14338
| 3:49 | 5.6672 | 0.14387
| 3:49 | 5.6675 | 0.14436
| 3:49 | 5.6678 | 0.14485
| 3:49 | 5.6681 | 0.14535
| 3:49 | 5.6683 | 0.14586
| 3:49 | 5.6686 | 0.14636
| 3:49 | 5.6689 | 0.14687
| 3:49 | 5.6692 | 0.14739
| 3:49 | 5.6694 | 0.1479
| 3:49 | 5.6697 | 0.14841
| 3:49 | 5.67 | 0.14893
| 3:49 | 5.6703 | 0.14944
| 3:49 | 5.6706 | 0.14996
| 3:49 | 5.6708 | 0.15048
| 3:49 | 5.6711 | 0.151
| 3:49 | 5.6714 | 0.15152
| 3:49 | 5.6717 | 0.15203
| 3:49 | 5.6719 | 0.15255
| 3:49 | 5.6722 | 0.15306
| 3:49 | 5.6725 | 0.15357
| 3:49 | 5.6728 | 0.15407
| 3:49 | 5.6731 | 0.15457
| 3:49 | 5.6733 | 0.15507
| 3:49 | 5.6736 | 0.15557
| 3:49 | 5.6739 | 0.15606
| 3:49 | 5.6742 | 0.15655
| 3:49 | 5.6744 | 0.15703
| 3:49 | 5.6747 | 0.15752
| 3:49 | 5.675 | 0.158
| 3:49 | 5.6753 | 0.15848
| 3:49 | 5.6756 | 0.15897
| 3:49 | 5.6758 | 0.15945
| 3:49 | 5.6761 | 0.15994
| 3:49 | 5.6764 | 0.16043
| 3:49 | 5.6767 | 0.16093
| 3:49 | 5.6769 | 0.16143
| 3:49 | 5.6772 | 0.16194
| 3:49 | 5.6775 | 0.16245
| 3:49 | 5.6778 | 0.16297
| 3:49 | 5.6781 | 0.1635
| 3:49 | 5.6783 | 0.16403
| 3:50 | 5.6786 | 0.16457
| 3:50 | 5.6789 | 0.16509
| 3:50 | 5.6792 | 0.16562
| 3:50 | 5.6794 | 0.16614
| 3:50 | 5.6797 | 0.16667
| 3:50 | 5.68 | 0.16719
| 3:50 | 5.6803 | 0.16771
| 3:50 | 5.6806 | 0.16824
| 3:50 | 5.6808 | 0.16876
| 3:50 | 5.6811 | 0.16929
| 3:50 | 5.6814 | 0.16981
| 3:50 | 5.6817 | 0.17033
| 3:50 | 5.6819 | 0.17086
| 3:50 | 5.6822 | 0.17138
| 3:50 | 5.6825 | 0.1719
| 3:50 | 5.6828 | 0.17243
| 3:50 | 5.6831 | 0.17295
| 3:50 | 5.6833 | 0.17347
| 3:50 | 5.6836 | 0.174
| 3:50 | 5.6839 | 0.17452
| 3:50 | 5.6842 | 0.17504
| 3:50 | 5.6844 | 0.17557
| 3:50 | 5.6847 | 0.17609
| 3:50 | 5.685 | 0.17661
| 3:50 | 5.6853 | 0.17713
| 3:50 | 5.6856 | 0.17764
| 3:50 | 5.6858 | 0.17816
| 3:50 | 5.6861 | 0.17867
| 3:50 | 5.6864 | 0.17917
| 3:50 | 5.6867 | 0.17966
| 3:50 | 5.6869 | 0.18016
| 3:50 | 5.6872 | 0.18065
| 3:50 | 5.6875 | 0.18114
| 3:50 | 5.6878 | 0.18164
| 3:50 | 5.6881 | 0.18213
| 3:50 | 5.6883 | 0.18263
| 3:50 | 5.6886 | 0.18312
| 3:50 | 5.6889 | 0.18362
| 3:50 | 5.6892 | 0.18411
| 3:50 | 5.6894 | 0.18461
| 3:50 | 5.6897 | 0.18511
| 3:50 | 5.69 | 0.1856
| 3:50 | 5.6903 | 0.18609
| 3:50 | 5.6906 | 0.18658
| 3:50 | 5.6908 | 0.18708
| 3:50 | 5.6911 | 0.18757
| 3:50 | 5.6914 | 0.18806
| 3:50 | 5.6917 | 0.18856
| 3:50 | 5.6919 | 0.18907
| 3:50 | 5.6922 | 0.18959
| 3:50 | 5.6925 | 0.1901
| 3:50 | 5.6928 | 0.1906
| 3:50 | 5.6931 | 0.19111
| 3:50 | 5.6933 | 0.1916
| 3:50 | 5.6936 | 0.1921
| 3:50 | 5.6939 | 0.19259
| 3:50 | 5.6942 | 0.19307
| 3:50 | 5.6944 | 0.19354
| 3:50 | 5.6947 | 0.19402
| 3:50 | 5.695 | 0.19449
| 3:51 | 5.6953 | 0.19496
| 3:51 | 5.6956 | 0.19544
| 3:51 | 5.6958 | 0.19591
| 3:51 | 5.6961 | 0.19638
| 3:51 | 5.6964 | 0.19685
| 3:51 | 5.6967 | 0.19732
| 3:51 | 5.6969 | 0.19779
| 3:51 | 5.6972 | 0.19824
| 3:51 | 5.6975 | 0.1987
| 3:51 | 5.6978 | 0.19915
| 3:51 | 5.6981 | 0.19959
| 3:51 | 5.6983 | 0.20003
| 3:51 | 5.6986 | 0.20046
| 3:51 | 5.6989 | 0.20089
| 3:51 | 5.6992 | 0.20131
| 3:51 | 5.6994 | 0.20173
| 3:51 | 5.6997 | 0.20213
| 3:51 | 5.7 | 0.20252
| 3:51 | 5.7003 | 0.20291
| 3:51 | 5.7006 | 0.20329
| 3:51 | 5.7008 | 0.20367
| 3:51 | 5.7011 | 0.20405
| 3:51 | 5.7014 | 0.20442
| 3:51 | 5.7017 | 0.20479
| 3:51 | 5.7019 | 0.20517
| 3:51 | 5.7022 | 0.20554
| 3:51 | 5.7025 | 0.20591
| 3:51 | 5.7028 | 0.20628
| 3:51 | 5.7031 | 0.20666
| 3:51 | 5.7033 | 0.20703
| 3:51 | 5.7036 | 0.2074
| 3:51 | 5.7039 | 0.20777
| 3:51 | 5.7042 | 0.20814
| 3:51 | 5.7044 | 0.20852
| 3:51 | 5.7047 | 0.20889
| 3:51 | 5.705 | 0.20926
| 3:51 | 5.7053 | 0.20963
| 3:51 | 5.7056 | 0.20999
| 3:51 | 5.7058 | 0.21036
| 3:51 | 5.7061 | 0.21073
| 3:51 | 5.7064 | 0.21109
| 3:51 | 5.7067 | 0.21146
| 3:51 | 5.7069 | 0.21183
| 3:51 | 5.7072 | 0.21222
| 3:51 | 5.7075 | 0.2126
| 3:51 | 5.7078 | 0.21298
| 3:51 | 5.7081 | 0.21336
| 3:51 | 5.7083 | 0.21373
| 3:51 | 5.7086 | 0.21411
| 3:51 | 5.7089 | 0.21447
| 3:51 | 5.7092 | 0.21483
| 3:51 | 5.7094 | 0.21519
| 3:51 | 5.7097 | 0.21556
| 3:51 | 5.71 | 0.21594
| 3:51 | 5.7103 | 0.21632
| 3:51 | 5.7106 | 0.21672
| 3:51 | 5.7108 | 0.21712
| 3:51 | 5.7111 | 0.21752
| 3:51 | 5.7114 | 0.21793
| 3:52 | 5.7117 | 0.21835
| 3:52 | 5.7119 | 0.21878
| 3:52 | 5.7122 | 0.21922
| 3:52 | 5.7125 | 0.21966
| 3:52 | 5.7128 | 0.2201
| 3:52 | 5.7131 | 0.22054
| 3:52 | 5.7133 | 0.22098
| 3:52 | 5.7136 | 0.22142
| 3:52 | 5.7139 | 0.22186
| 3:52 | 5.7142 | 0.22231
| 3:52 | 5.7144 | 0.22275
| 3:52 | 5.7147 | 0.2232
| 3:52 | 5.715 | 0.22365
| 3:52 | 5.7153 | 0.22409
| 3:52 | 5.7156 | 0.22454
| 3:52 | 5.7158 | 0.22499
| 3:52 | 5.7161 | 0.22545
| 3:52 | 5.7164 | 0.22591
| 3:52 | 5.7167 | 0.22638
| 3:52 | 5.7169 | 0.22684
| 3:52 | 5.7172 | 0.22728
| 3:52 | 5.7175 | 0.2277
| 3:52 | 5.7178 | 0.22812
| 3:52 | 5.7181 | 0.22853
| 3:52 | 5.7183 | 0.22894
| 3:52 | 5.7186 | 0.22934
| 3:52 | 5.7189 | 0.22974
| 3:52 | 5.7192 | 0.23014
| 3:52 | 5.7194 | 0.23053
| 3:52 | 5.7197 | 0.23092
| 3:52 | 5.72 | 0.23131
| 3:52 | 5.7203 | 0.2317
| 3:52 | 5.7206 | 0.23208
| 3:52 | 5.7208 | 0.23243
| 3:52 | 5.7211 | 0.23278
| 3:52 | 5.7214 | 0.23311
| 3:52 | 5.7217 | 0.23345
| 3:52 | 5.7219 | 0.23378
| 3:52 | 5.7222 | 0.23411
| 3:52 | 5.7225 | 0.23443
| 3:52 | 5.7228 | 0.23475
| 3:52 | 5.7231 | 0.23507
| 3:52 | 5.7233 | 0.23538
| 3:52 | 5.7236 | 0.2357
| 3:52 | 5.7239 | 0.23601
| 3:52 | 5.7242 | 0.23635
| 3:52 | 5.7244 | 0.2367
| 3:52 | 5.7247 | 0.23705
| 3:52 | 5.725 | 0.23739
| 3:52 | 5.7253 | 0.23771
| 3:52 | 5.7256 | 0.23803
| 3:52 | 5.7258 | 0.23833
| 3:52 | 5.7261 | 0.23863
| 3:52 | 5.7264 | 0.23893
| 3:52 | 5.7267 | 0.23924
| 3:52 | 5.7269 | 0.23954
| 3:52 | 5.7272 | 0.23984
| 3:52 | 5.7275 | 0.24013
| 3:52 | 5.7278 | 0.2404
| 3:52 | 5.7281 | 0.24065
| 3:52 | 5.7283 | 0.24088
| 3:53 | 5.7286 | 0.24109
| 3:53 | 5.7289 | 0.24128
| 3:53 | 5.7292 | 0.24147
| 3:53 | 5.7294 | 0.24168
| 3:53 | 5.7297 | 0.24135
| 3:53 | 5.73 | 0.24102
| 3:53 | 5.7303 | 0.24069
| 3:53 | 5.7306 | 0.24036
| 3:53 | 5.7308 | 0.24003
| 3:53 | 5.7311 | 0.2397
| 3:53 | 5.7314 | 0.23937
| 3:53 | 5.7317 | 0.23903
| 3:53 | 5.7319 | 0.2387
| 3:53 | 5.7322 | 0.23837
| 3:53 | 5.7325 | 0.23804
| 3:53 | 5.7328 | 0.2377
| 3:53 | 5.7331 | 0.23737
| 3:53 | 5.7333 | 0.23703
| 3:53 | 5.7336 | 0.23669
| 3:53 | 5.7339 | 0.23632
| 3:53 | 5.7342 | 0.23594
| 3:53 | 5.7344 | 0.23555
| 3:53 | 5.7347 | 0.23515
| 3:53 | 5.735 | 0.23474
| 3:53 | 5.7353 | 0.23431
| 3:53 | 5.7356 | 0.23386
| 3:53 | 5.7358 | 0.2334
| 3:53 | 5.7361 | 0.23294
| 3:53 | 5.7364 | 0.23249
| 3:53 | 5.7367 | 0.23204
| 3:53 | 5.7369 | 0.2316
| 3:53 | 5.7372 | 0.23117
| 3:53 | 5.7375 | 0.23075
| 3:53 | 5.7378 | 0.23035
| 3:53 | 5.7381 | 0.22996
| 3:53 | 5.7383 | 0.22958
| 3:53 | 5.7386 | 0.22921
| 3:53 | 5.7389 | 0.22885
| 3:53 | 5.7392 | 0.2285
| 3:53 | 5.7394 | 0.22816
| 3:53 | 5.7397 | 0.22783
| 3:53 | 5.74 | 0.22751
| 3:53 | 5.7403 | 0.22719
| 3:53 | 5.7406 | 0.22684
| 3:53 | 5.7408 | 0.2265
| 3:53 | 5.7411 | 0.22617
| 3:53 | 5.7414 | 0.22584
| 3:53 | 5.7417 | 0.22552
| 3:53 | 5.7419 | 0.22519
| 3:53 | 5.7422 | 0.22487
| 3:53 | 5.7425 | 0.22455
| 3:53 | 5.7428 | 0.22424
| 3:53 | 5.7431 | 0.22392
| 3:53 | 5.7433 | 0.22361
| 3:53 | 5.7436 | 0.2233
| 3:53 | 5.7439 | 0.22299
| 3:53 | 5.7442 | 0.22268
| 3:53 | 5.7444 | 0.22237
| 3:53 | 5.7447 | 0.22205
| 3:54 | 5.745 | 0.22174
| 3:54 | 5.7453 | 0.22142
| 3:54 | 5.7456 | 0.22109
| 3:54 | 5.7458 | 0.22075
| 3:54 | 5.7461 | 0.22041
| 3:54 | 5.7464 | 0.22006
| 3:54 | 5.7467 | 0.21972
| 3:54 | 5.7469 | 0.21937
| 3:54 | 5.7472 | 0.21903
| 3:54 | 5.7475 | 0.21868
| 3:54 | 5.7478 | 0.21833
| 3:54 | 5.7481 | 0.21799
| 3:54 | 5.7483 | 0.21764
| 3:54 | 5.7486 | 0.21729
| 3:54 | 5.7489 | 0.21694
| 3:54 | 5.7492 | 0.21659
| 3:54 | 5.7494 | 0.21624
| 3:54 | 5.7497 | 0.21589
| 3:54 | 5.75 | 0.21554
| 3:54 | 5.7503 | 0.21517
| 3:54 | 5.7506 | 0.2148
| 3:54 | 5.7508 | 0.21442
| 3:54 | 5.7511 | 0.21404
| 3:54 | 5.7514 | 0.21365
| 3:54 | 5.7517 | 0.21325
| 3:54 | 5.7519 | 0.21283
| 3:54 | 5.7522 | 0.21241
| 3:54 | 5.7525 | 0.21198
| 3:54 | 5.7528 | 0.21155
| 3:54 | 5.7531 | 0.21113
| 3:54 | 5.7533 | 0.2107
| 3:54 | 5.7536 | 0.21028
| 3:54 | 5.7539 | 0.20985
| 3:54 | 5.7542 | 0.20943
| 3:54 | 5.7544 | 0.209
| 3:54 | 5.7547 | 0.20857
| 3:54 | 5.755 | 0.20815
| 3:54 | 5.7553 | 0.20772
| 3:54 | 5.7556 | 0.2073
| 3:54 | 5.7558 | 0.20687
| 3:54 | 5.7561 | 0.20644
| 3:54 | 5.7564 | 0.20601
| 3:54 | 5.7567 | 0.20559
| 3:54 | 5.7569 | 0.20517
| 3:54 | 5.7572 | 0.20478
| 3:54 | 5.7575 | 0.20441
| 3:54 | 5.7578 | 0.20409
| 3:54 | 5.7581 | 0.20379
| 3:54 | 5.7583 | 0.20349
| 3:54 | 5.7586 | 0.20319
| 3:54 | 5.7589 | 0.20288
| 3:54 | 5.7592 | 0.20258
| 3:54 | 5.7594 | 0.20227
| 3:54 | 5.7597 | 0.20196
| 3:54 | 5.76 | 0.20165
| 3:54 | 5.7603 | 0.20133
| 3:54 | 5.7606 | 0.201
| 3:54 | 5.7608 | 0.20066
| 3:54 | 5.7611 | 0.20032
| 3:54 | 5.7614 | 0.19998
| 3:54 | 5.7617 | 0.19965
| 3:55 | 5.7619 | 0.19931
| 3:55 | 5.7622 | 0.19898
| 3:55 | 5.7625 | 0.19866
| 3:55 | 5.7628 | 0.19833
| 3:55 | 5.7631 | 0.198
| 3:55 | 5.7633 | 0.19766
| 3:55 | 5.7636 | 0.19732
| 3:55 | 5.7639 | 0.19696
| 3:55 | 5.7642 | 0.1966
| 3:55 | 5.7644 | 0.19623
| 3:55 | 5.7647 | 0.19586
| 3:55 | 5.765 | 0.19547
| 3:55 | 5.7653 | 0.19508
| 3:55 | 5.7656 | 0.19468
| 3:55 | 5.7658 | 0.19427
| 3:55 | 5.7661 | 0.19387
| 3:55 | 5.7664 | 0.19347
| 3:55 | 5.7667 | 0.19306
| 3:55 | 5.7669 | 0.19266
| 3:55 | 5.7672 | 0.19226
| 3:55 | 5.7675 | 0.19186
| 3:55 | 5.7678 | 0.19147
| 3:55 | 5.7681 | 0.19107
| 3:55 | 5.7683 | 0.19068
| 3:55 | 5.7686 | 0.1903
| 3:55 | 5.7689 | 0.18994
| 3:55 | 5.7692 | 0.1896
| 3:55 | 5.7694 | 0.18925
| 3:55 | 5.7697 | 0.18891
| 3:55 | 5.77 | 0.18857
| 3:55 | 5.7703 | 0.18826
| 3:55 | 5.7706 | 0.18795
| 3:55 | 5.7708 | 0.18765
| 3:55 | 5.7711 | 0.18736
| 3:55 | 5.7714 | 0.18706
| 3:55 | 5.7717 | 0.18676
| 3:55 | 5.7719 | 0.18645
| 3:55 | 5.7722 | 0.18614
| 3:55 | 5.7725 | 0.18583
| 3:55 | 5.7728 | 0.18551
| 3:55 | 5.7731 | 0.18518
| 3:55 | 5.7733 | 0.18486
| 3:55 | 5.7736 | 0.18453
| 3:55 | 5.7739 | 0.1842
| 3:55 | 5.7742 | 0.18392
| 3:55 | 5.7744 | 0.18363
| 3:55 | 5.7747 | 0.18338
| 3:55 | 5.775 | 0.18314
| 3:55 | 5.7753 | 0.1829
| 3:55 | 5.7756 | 0.18265
| 3:55 | 5.7758 | 0.18239
| 3:55 | 5.7761 | 0.18209
| 3:55 | 5.7764 | 0.18176
| 3:55 | 5.7767 | 0.18141
| 3:55 | 5.7769 | 0.18104
| 3:55 | 5.7772 | 0.18066
| 3:55 | 5.7775 | 0.18029
| 3:55 | 5.7778 | 0.17991
| 3:55 | 5.7781 | 0.17952
| 3:56 | 5.7783 | 0.17913
| 3:56 | 5.7786 | 0.17874
| 3:56 | 5.7789 | 0.17836
| 3:56 | 5.7792 | 0.17799
| 3:56 | 5.7794 | 0.17763
| 3:56 | 5.7797 | 0.17729
| 3:56 | 5.78 | 0.17695
| 3:56 | 5.7803 | 0.17661
| 3:56 | 5.7806 | 0.17626
| 3:56 | 5.7808 | 0.17591
| 3:56 | 5.7811 | 0.17556
| 3:56 | 5.7814 | 0.17521
| 3:56 | 5.7817 | 0.17486
| 3:56 | 5.7819 | 0.1745
| 3:56 | 5.7822 | 0.17414
| 3:56 | 5.7825 | 0.17379
| 3:56 | 5.7828 | 0.17344
| 3:56 | 5.7831 | 0.1731
| 3:56 | 5.7833 | 0.17276
| 3:56 | 5.7836 | 0.17241
| 3:56 | 5.7839 | 0.17207
| 3:56 | 5.7842 | 0.17172
| 3:56 | 5.7844 | 0.17136
| 3:56 | 5.7847 | 0.17099
| 3:56 | 5.785 | 0.17062
| 3:56 | 5.7853 | 0.17025
| 3:56 | 5.7856 | 0.16988
| 3:56 | 5.7858 | 0.1695
| 3:56 | 5.7861 | 0.16912
| 3:56 | 5.7864 | 0.16873
| 3:56 | 5.7867 | 0.16833
| 3:56 | 5.7869 | 0.16792
| 3:56 | 5.7872 | 0.16751
| 3:56 | 5.7875 | 0.1671
| 3:56 | 5.7878 | 0.1667
| 3:56 | 5.7881 | 0.1663
| 3:56 | 5.7883 | 0.1659
| 3:56 | 5.7886 | 0.16549
| 3:56 | 5.7889 | 0.16509
| 3:56 | 5.7892 | 0.16468
| 3:56 | 5.7894 | 0.16426
| 3:56 | 5.7897 | 0.16384
| 3:56 | 5.79 | 0.16342
| 3:56 | 5.7903 | 0.163
| 3:56 | 5.7906 | 0.16258
| 3:56 | 5.7908 | 0.16215
| 3:56 | 5.7911 | 0.16173
| 3:56 | 5.7914 | 0.16132
| 3:56 | 5.7917 | 0.1609
| 3:56 | 5.7919 | 0.16049
| 3:56 | 5.7922 | 0.16008
| 3:56 | 5.7925 | 0.15967
| 3:56 | 5.7928 | 0.15926
| 3:56 | 5.7931 | 0.15884
| 3:56 | 5.7933 | 0.15841
| 3:56 | 5.7936 | 0.15798
| 3:56 | 5.7939 | 0.15754
| 3:56 | 5.7942 | 0.15709
| 3:56 | 5.7944 | 0.15663
| 3:56 | 5.7947 | 0.15616
| 3:56 | 5.795 | 0.15569
| 3:57 | 5.7953 | 0.15521
| 3:57 | 5.7956 | 0.15473
| 3:57 | 5.7958 | 0.15426
| 3:57 | 5.7961 | 0.15379
| 3:57 | 5.7964 | 0.15332
| 3:57 | 5.7967 | 0.15287
| 3:57 | 5.7969 | 0.15242
| 3:57 | 5.7972 | 0.15199
| 3:57 | 5.7975 | 0.15156
| 3:57 | 5.7978 | 0.15115
| 3:57 | 5.7981 | 0.15075
| 3:57 | 5.7983 | 0.15036
| 3:57 | 5.7986 | 0.14998
| 3:57 | 5.7989 | 0.14961
| 3:57 | 5.7992 | 0.14924
| 3:57 | 5.7994 | 0.14887
| 3:57 | 5.7997 | 0.14849
| 3:57 | 5.8 | 0.14809
| 3:57 | 5.8003 | 0.14769
| 3:57 | 5.8006 | 0.14728
| 3:57 | 5.8008 | 0.14687
| 3:57 | 5.8011 | 0.14645
| 3:57 | 5.8014 | 0.14602
| 3:57 | 5.8017 | 0.14558
| 3:57 | 5.8019 | 0.14515
| 3:57 | 5.8022 | 0.14472
| 3:57 | 5.8025 | 0.1443
| 3:57 | 5.8028 | 0.14388
| 3:57 | 5.8031 | 0.14347
| 3:57 | 5.8033 | 0.14307
| 3:57 | 5.8036 | 0.14268
| 3:57 | 5.8039 | 0.14229
| 3:57 | 5.8042 | 0.1419
| 3:57 | 5.8044 | 0.14151
| 3:57 | 5.8047 | 0.14113
| 3:57 | 5.805 | 0.14074
| 3:57 | 5.8053 | 0.14036
| 3:57 | 5.8056 | 0.13998
| 3:57 | 5.8058 | 0.1396
| 3:57 | 5.8061 | 0.13923
| 3:57 | 5.8064 | 0.13886
| 3:57 | 5.8067 | 0.13849
| 3:57 | 5.8069 | 0.13812
| 3:57 | 5.8072 | 0.13774
| 3:57 | 5.8075 | 0.13736
| 3:57 | 5.8078 | 0.13697
| 3:57 | 5.8081 | 0.13656
| 3:57 | 5.8083 | 0.13616
| 3:57 | 5.8086 | 0.13577
| 3:57 | 5.8089 | 0.13537
| 3:57 | 5.8092 | 0.13499
| 3:57 | 5.8094 | 0.1346
| 3:57 | 5.8097 | 0.13423
| 3:57 | 5.81 | 0.13385
| 3:57 | 5.8103 | 0.13349
| 3:57 | 5.8106 | 0.13314
| 3:57 | 5.8108 | 0.13282
| 3:57 | 5.8111 | 0.1325
| 3:57 | 5.8114 | 0.13221
| 3:58 | 5.8117 | 0.13191
| 3:58 | 5.8119 | 0.13161
| 3:58 | 5.8122 | 0.13131
| 3:58 | 5.8125 | 0.13102
| 3:58 | 5.8128 | 0.13072
| 3:58 | 5.8131 | 0.13042
| 3:58 | 5.8133 | 0.13012
| 3:58 | 5.8136 | 0.12983
| 3:58 | 5.8139 | 0.12953
| 3:58 | 5.8142 | 0.12924
| 3:58 | 5.8144 | 0.12896
| 3:58 | 5.8147 | 0.12868
| 3:58 | 5.815 | 0.12841
| 3:58 | 5.8153 | 0.12815
| 3:58 | 5.8156 | 0.12788
| 3:58 | 5.8158 | 0.12763
| 3:58 | 5.8161 | 0.12738
| 3:58 | 5.8164 | 0.12715
| 3:58 | 5.8167 | 0.12693
| 3:58 | 5.8169 | 0.12672
| 3:58 | 5.8172 | 0.12651
| 3:58 | 5.8175 | 0.12631
| 3:58 | 5.8178 | 0.12612
| 3:58 | 5.8181 | 0.12593
| 3:58 | 5.8183 | 0.12573
| 3:58 | 5.8186 | 0.12553
| 3:58 | 5.8189 | 0.12533
| 3:58 | 5.8192 | 0.12512
| 3:58 | 5.8194 | 0.12491
| 3:58 | 5.8197 | 0.12471
| 3:58 | 5.82 | 0.1245
| 3:58 | 5.8203 | 0.12428
| 3:58 | 5.8206 | 0.12406
| 3:58 | 5.8208 | 0.12385
| 3:58 | 5.8211 | 0.12363
| 3:58 | 5.8214 | 0.1234
| 3:58 | 5.8217 | 0.12317
| 3:58 | 5.8219 | 0.12294
| 3:58 | 5.8222 | 0.1227
| 3:58 | 5.8225 | 0.12246
| 3:58 | 5.8228 | 0.12222
| 3:58 | 5.8231 | 0.12197
| 3:58 | 5.8233 | 0.12171
| 3:58 | 5.8236 | 0.12146
| 3:58 | 5.8239 | 0.1212
| 3:58 | 5.8242 | 0.12095
| 3:58 | 5.8244 | 0.1207
| 3:58 | 5.8247 | 0.12044
| 3:58 | 5.825 | 0.12019
| 3:58 | 5.8253 | 0.11994
| 3:58 | 5.8256 | 0.11969
| 3:58 | 5.8258 | 0.11944
| 3:58 | 5.8261 | 0.1192
| 3:58 | 5.8264 | 0.11896
| 3:58 | 5.8267 | 0.11872
| 3:58 | 5.8269 | 0.11848
| 3:58 | 5.8272 | 0.11823
| 3:58 | 5.8275 | 0.11798
| 3:58 | 5.8278 | 0.1177
| 3:58 | 5.8281 | 0.11743
| 3:58 | 5.8283 | 0.11714
| 3:59 | 5.8286 | 0.11685
| 3:59 | 5.8289 | 0.11656
| 3:59 | 5.8292 | 0.11626
| 3:59 | 5.8294 | 0.11596
| 3:59 | 5.8297 | 0.11566
| 3:59 | 5.83 | 0.11535
| 3:59 | 5.8303 | 0.11502
| 3:59 | 5.8306 | 0.11469
| 3:59 | 5.8308 | 0.11436
| 3:59 | 5.8311 | 0.11401
| 3:59 | 5.8314 | 0.11365
| 3:59 | 5.8317 | 0.11329
| 3:59 | 5.8319 | 0.11292
| 3:59 | 5.8322 | 0.11254
| 3:59 | 5.8325 | 0.11215
| 3:59 | 5.8328 | 0.11173
| 3:59 | 5.8331 | 0.11129
| 3:59 | 5.8333 | 0.11084
| 3:59 | 5.8336 | 0.11039
| 3:59 | 5.8339 | 0.10994
| 3:59 | 5.8342 | 0.10948
| 3:59 | 5.8344 | 0.10901
| 3:59 | 5.8347 | 0.10852
| 3:59 | 5.835 | 0.10803
| 3:59 | 5.8353 | 0.10754
| 3:59 | 5.8356 | 0.10706
| 3:59 | 5.8358 | 0.10657
| 3:59 | 5.8361 | 0.10609
| 3:59 | 5.8364 | 0.1056
| 3:59 | 5.8367 | 0.10512
| 3:59 | 5.8369 | 0.10464
| 3:59 | 5.8372 | 0.10416
| 3:59 | 5.8375 | 0.10368
| 3:59 | 5.8378 | 0.1032
| 3:59 | 5.8381 | 0.10272
| 3:59 | 5.8383 | 0.10223
| 3:59 | 5.8386 | 0.10175
| 3:59 | 5.8389 | 0.10127
| 3:59 | 5.8392 | 0.10079
| 3:59 | 5.8394 | 0.10031
| 3:59 | 5.8397 | 0.099823
| 3:59 | 5.84 | 0.099341
| 3:59 | 5.8403 | 0.09886
| 3:59 | 5.8406 | 0.09838
| 3:59 | 5.8408 | 0.097897
| 3:59 | 5.8411 | 0.09741
| 3:59 | 5.8414 | 0.096926
| 3:59 | 5.8417 | 0.096446
| 3:59 | 5.8419 | 0.095967
| 3:59 | 5.8422 | 0.09549
| 3:59 | 5.8425 | 0.095012
| 3:59 | 5.8428 | 0.094544
| 3:59 | 5.8431 | 0.094073
| 3:59 | 5.8433 | 0.093599
| 3:59 | 5.8436 | 0.093123
| 3:59 | 5.8439 | 0.092643
| 3:59 | 5.8442 | 0.092155
| 3:59 | 5.8444 | 0.091664
| 3:59 | 5.8447 | 0.091167
| 4:00 | 5.845 | 0.090668
| 4:00 | 5.8453 | 0.090168
| 4:00 | 5.8456 | 0.089664
| 4:00 | 5.8458 | 0.08916
| 4:00 | 5.8461 | 0.088653
| 4:00 | 5.8464 | 0.088148
| 4:00 | 5.8467 | 0.087644
| 4:00 | 5.8469 | 0.087143
| 4:00 | 5.8472 | 0.086646
| 4:00 | 5.8475 | 0.086151
| 4:00 | 5.8478 | 0.08566
| 4:00 | 5.8481 | 0.085172
| 4:00 | 5.8483 | 0.084687
| 4:00 | 5.8486 | 0.084205
| 4:00 | 5.8489 | 0.083726
| 4:00 | 5.8492 | 0.083252
| 4:00 | 5.8494 | 0.082785
| 4:00 | 5.8497 | 0.08234
| 4:00 | 5.85 | 0.081909
| 4:00 | 5.8503 | 0.081497
| 4:00 | 5.8506 | 0.081092
| 4:00 | 5.8508 | 0.080713
| 4:00 | 5.8511 | 0.08035
| 4:00 | 5.8514 | 0.080016
| 4:00 | 5.8517 | 0.079692
| 4:00 | 5.8519 | 0.079381
| 4:00 | 5.8522 | 0.079081
| 4:00 | 5.8525 | 0.078799
| 4:00 | 5.8528 | 0.078531
| 4:00 | 5.8531 | 0.078269
| 4:00 | 5.8533 | 0.078023
| 4:00 | 5.8536 | 0.077798
| 4:00 | 5.8539 | 0.077603
| 4:00 | 5.8542 | 0.077437
| 4:00 | 5.8544 | 0.07728
| 4:00 | 5.8547 | 0.077129
| 4:00 | 5.855 | 0.076978
| 4:00 | 5.8553 | 0.076828
| 4:00 | 5.8556 | 0.076679
| 4:00 | 5.8558 | 0.076531
| 4:00 | 5.8561 | 0.076385
| 4:00 | 5.8564 | 0.076239
| 4:00 | 5.8567 | 0.076094
| 4:00 | 5.8569 | 0.07595
| 4:00 | 5.8572 | 0.075806
| 4:00 | 5.8575 | 0.075648
| 4:00 | 5.8578 | 0.075475
| 4:00 | 5.8581 | 0.075302
| 4:00 | 5.8583 | 0.075128
| 4:00 | 5.8586 | 0.074954
| 4:00 | 5.8589 | 0.074779
| 4:00 | 5.8592 | 0.074615
| 4:00 | 5.8594 | 0.07448
| 4:00 | 5.8597 | 0.074382
| 4:00 | 5.86 | 0.074283
| 4:00 | 5.8603 | 0.074121
| 4:00 | 5.8606 | 0.073878
| 4:00 | 5.8608 | 0.073576
| 4:00 | 5.8611 | 0.073238
| 4:00 | 5.8614 | 0.072876
| 4:00 | 5.8617 | 0.072504
| 4:01 | 5.8619 | 0.072128
| 4:01 | 5.8622 | 0.071746
| 4:01 | 5.8625 | 0.071357
| 4:01 | 5.8628 | 0.070964
| 4:01 | 5.8631 | 0.070568
| 4:01 | 5.8633 | 0.070166
| 4:01 | 5.8636 | 0.069759
| 4:01 | 5.8639 | 0.069347
| 4:01 | 5.8642 | 0.068929
| 4:01 | 5.8644 | 0.068506
| 4:01 | 5.8647 | 0.068077
| 4:01 | 5.865 | 0.067644
| 4:01 | 5.8653 | 0.067204
| 4:01 | 5.8656 | 0.06676
| 4:01 | 5.8658 | 0.066312
| 4:01 | 5.8661 | 0.065865
| 4:01 | 5.8664 | 0.065417
| 4:01 | 5.8667 | 0.064968
| 4:01 | 5.8669 | 0.06452
| 4:01 | 5.8672 | 0.064069
| 4:01 | 5.8675 | 0.06362
| 4:01 | 5.8678 | 0.06317
| 4:01 | 5.8681 | 0.062721
| 4:01 | 5.8683 | 0.062272
| 4:01 | 5.8686 | 0.061826
| 4:01 | 5.8689 | 0.061381
| 4:01 | 5.8692 | 0.060941
| 4:01 | 5.8694 | 0.060502
| 4:01 | 5.8697 | 0.06007
| 4:01 | 5.87 | 0.05965
| 4:01 | 5.8703 | 0.059231
| 4:01 | 5.8706 | 0.058816
| 4:01 | 5.8708 | 0.058403
| 4:01 | 5.8711 | 0.057994
| 4:01 | 5.8714 | 0.057584
| 4:01 | 5.8717 | 0.057171
| 4:01 | 5.8719 | 0.056757
| 4:01 | 5.8722 | 0.056341
| 4:01 | 5.8725 | 0.055923
| 4:01 | 5.8728 | 0.055503
| 4:01 | 5.8731 | 0.055081
| 4:01 | 5.8733 | 0.054657
| 4:01 | 5.8736 | 0.054231
| 4:01 | 5.8739 | 0.053803
| 4:01 | 5.8742 | 0.053366
| 4:01 | 5.8744 | 0.052927
| 4:01 | 5.8747 | 0.052484
| 4:01 | 5.875 | 0.052038
| 4:01 | 5.8753 | 0.051589
| 4:01 | 5.8756 | 0.051138
| 4:01 | 5.8758 | 0.050685
| 4:01 | 5.8761 | 0.050228
| 4:01 | 5.8764 | 0.049769
| 4:01 | 5.8767 | 0.049311
| 4:01 | 5.8769 | 0.048852
| 4:01 | 5.8772 | 0.048392
| 4:01 | 5.8775 | 0.047935
| 4:01 | 5.8778 | 0.047486
| 4:01 | 5.8781 | 0.047046
| 4:01 | 5.8783 | 0.046615
| 4:02 | 5.8786 | 0.046194
| 4:02 | 5.8789 | 0.045782
| 4:02 | 5.8792 | 0.045375
| 4:02 | 5.8794 | 0.044975
| 4:02 | 5.8797 | 0.044583
| 4:02 | 5.88 | 0.044199
| 4:02 | 5.8803 | 0.043828
| 4:02 | 5.8806 | 0.043468
| 4:02 | 5.8808 | 0.043121
| 4:02 | 5.8811 | 0.042785
| 4:02 | 5.8814 | 0.042462
| 4:02 | 5.8817 | 0.04215
| 4:02 | 5.8819 | 0.041851
| 4:02 | 5.8822 | 0.041563
| 4:02 | 5.8825 | 0.041288
| 4:02 | 5.8828 | 0.041026
| 4:02 | 5.8831 | 0.040766
| 4:02 | 5.8833 | 0.040506
| 4:02 | 5.8836 | 0.040254
| 4:02 | 5.8839 | 0.040007
| 4:02 | 5.8842 | 0.039774
| 4:02 | 5.8844 | 0.039551
| 4:02 | 5.8847 | 0.039348
| 4:02 | 5.885 | 0.039156
| 4:02 | 5.8853 | 0.038979
| 4:02 | 5.8856 | 0.038826
| 4:02 | 5.8858 | 0.038727
| 4:02 | 5.8861 | 0.038682
| 4:02 | 5.8864 | 0.038678
| 4:02 | 5.8867 | 0.038712
| 4:02 | 5.8869 | 0.038748
| 4:02 | 5.8872 | 0.038785
| 4:02 | 5.8875 | 0.038824
| 4:02 | 5.8878 | 0.038855
| 4:02 | 5.8881 | 0.038885
| 4:02 | 5.8883 | 0.038908
| 4:02 | 5.8886 | 0.038922
| 4:02 | 5.8889 | 0.038925
| 4:02 | 5.8892 | 0.038918
| 4:02 | 5.8894 | 0.038902
| 4:02 | 5.8897 | 0.038875
| 4:02 | 5.89 | 0.038839
| 4:02 | 5.8903 | 0.038773
| 4:02 | 5.8906 | 0.038676
| 4:02 | 5.8908 | 0.038567
| 4:02 | 5.8911 | 0.038441
| 4:02 | 5.8914 | 0.038303
| 4:02 | 5.8917 | 0.038158
| 4:02 | 5.8919 | 0.038
| 4:02 | 5.8922 | 0.03782
| 4:02 | 5.8925 | 0.037628
| 4:02 | 5.8928 | 0.03743
| 4:02 | 5.8931 | 0.037231
| 4:02 | 5.8933 | 0.037029
| 4:02 | 5.8936 | 0.036827
| 4:02 | 5.8939 | 0.036624
| 4:02 | 5.8942 | 0.036419
| 4:02 | 5.8944 | 0.036215
| 4:02 | 5.8947 | 0.036011
| 4:03 | 5.895 | 0.035807
| 4:03 | 5.8953 | 0.035603
| 4:03 | 5.8956 | 0.035401
| 4:03 | 5.8958 | 0.035197
| 4:03 | 5.8961 | 0.034992
| 4:03 | 5.8964 | 0.034785
| 4:03 | 5.8967 | 0.034575
| 4:03 | 5.8969 | 0.034363
| 4:03 | 5.8972 | 0.034149
| 4:03 | 5.8975 | 0.033933
| 4:03 | 5.8978 | 0.033714
| 4:03 | 5.8981 | 0.033494
| 4:03 | 5.8983 | 0.033271
| 4:03 | 5.8986 | 0.033046
| 4:03 | 5.8989 | 0.032819
| 4:03 | 5.8992 | 0.032593
| 4:03 | 5.8994 | 0.032367
| 4:03 | 5.8997 | 0.032139
| 4:03 | 5.9 | 0.031912
| 4:03 | 5.9003 | 0.031684
| 4:03 | 5.9006 | 0.031456
| 4:03 | 5.9008 | 0.031228
| 4:03 | 5.9011 | 0.030999
| 4:03 | 5.9014 | 0.030771
| 4:03 | 5.9017 | 0.030542
| 4:03 | 5.9019 | 0.030312
| 4:03 | 5.9022 | 0.030083
| 4:03 | 5.9025 | 0.029855
| 4:03 | 5.9028 | 0.029627
| 4:03 | 5.9031 | 0.029401
| 4:03 | 5.9033 | 0.029176
| 4:03 | 5.9036 | 0.028956
| 4:03 | 5.9039 | 0.02874
| 4:03 | 5.9042 | 0.028529
| 4:03 | 5.9044 | 0.028329
| 4:03 | 5.9047 | 0.028133
| 4:03 | 5.905 | 0.027944
| 4:03 | 5.9053 | 0.027764
| 4:03 | 5.9056 | 0.027592
| 4:03 | 5.9058 | 0.027428
| 4:03 | 5.9061 | 0.027273
| 4:03 | 5.9064 | 0.027127
| 4:03 | 5.9067 | 0.026989
| 4:03 | 5.9069 | 0.026859
| 4:03 | 5.9072 | 0.026752
| 4:03 | 5.9075 | 0.026651
| 4:03 | 5.9078 | 0.026556
| 4:03 | 5.9081 | 0.026468
| 4:03 | 5.9083 | 0.026382
| 4:03 | 5.9086 | 0.026302
| 4:03 | 5.9089 | 0.026228
| 4:03 | 5.9092 | 0.026157
| 4:03 | 5.9094 | 0.026097
| 4:03 | 5.9097 | 0.026042
| 4:03 | 5.91 | 0.025995
| 4:03 | 5.9103 | 0.025969
| 4:03 | 5.9106 | 0.025955
| 4:03 | 5.9108 | 0.025957
| 4:03 | 5.9111 | 0.025971
| 4:03 | 5.9114 | 0.026013
| 4:04 | 5.9117 | 0.02607
| 4:04 | 5.9119 | 0.02612
| 4:04 | 5.9122 | 0.026157
| 4:04 | 5.9125 | 0.026192
| 4:04 | 5.9128 | 0.026228
| 4:04 | 5.9131 | 0.026263
| 4:04 | 5.9133 | 0.0263
| 4:04 | 5.9136 | 0.026341
| 4:04 | 5.9139 | 0.026384
| 4:04 | 5.9142 | 0.026429
| 4:04 | 5.9144 | 0.026478
| 4:04 | 5.9147 | 0.026529
| 4:04 | 5.915 | 0.026583
| 4:04 | 5.9153 | 0.02664
| 4:04 | 5.9156 | 0.026699
| 4:04 | 5.9158 | 0.02676
| 4:04 | 5.9161 | 0.026802
| 4:04 | 5.9164 | 0.026852
| 4:04 | 5.9167 | 0.026909
| 4:04 | 5.9169 | 0.026973
| 4:04 | 5.9172 | 0.027035
| 4:04 | 5.9175 | 0.027096
| 4:04 | 5.9178 | 0.027156
| 4:04 | 5.9181 | 0.027213
| 4:04 | 5.9183 | 0.027261
| 4:04 | 5.9186 | 0.027304
| 4:04 | 5.9189 | 0.027345
| 4:04 | 5.9192 | 0.027382
| 4:04 | 5.9194 | 0.027417
| 4:04 | 5.9197 | 0.027446
| 4:04 | 5.92 | 0.027471
| 4:04 | 5.9203 | 0.027486
| 4:04 | 5.9206 | 0.027493
| 4:04 | 5.9208 | 0.027492
| 4:04 | 5.9211 | 0.027481
| 4:04 | 5.9214 | 0.027459
| 4:04 | 5.9217 | 0.027425
| 4:04 | 5.9219 | 0.027386
| 4:04 | 5.9222 | 0.027341
| 4:04 | 5.9225 | 0.027291
| 4:04 | 5.9228 | 0.027235
| 4:04 | 5.9231 | 0.027174
| 4:04 | 5.9233 | 0.027107
| 4:04 | 5.9236 | 0.027035
| 4:04 | 5.9239 | 0.026962
| 4:04 | 5.9242 | 0.026885
| 4:04 | 5.9244 | 0.026806
| 4:04 | 5.9247 | 0.026725
| 4:04 | 5.925 | 0.026641
| 4:04 | 5.9253 | 0.026553
| 4:04 | 5.9256 | 0.026456
| 4:04 | 5.9258 | 0.02635
| 4:04 | 5.9261 | 0.026239
| 4:04 | 5.9264 | 0.026116
| 4:04 | 5.9267 | 0.02599
| 4:04 | 5.9269 | 0.025846
| 4:04 | 5.9272 | 0.0257
| 4:04 | 5.9275 | 0.025527
| 4:04 | 5.9278 | 0.025339
| 4:04 | 5.9281 | 0.025135
| 4:04 | 5.9283 | 0.024914
| 4:05 | 5.9286 | 0.02468
| 4:05 | 5.9289 | 0.024431
| 4:05 | 5.9292 | 0.024146
| 4:05 | 5.9294 | 0.023853
| 4:05 | 5.9297 | 0.023542
| 4:05 | 5.93 | 0.023223
| 4:05 | 5.9303 | 0.022894
| 4:05 | 5.9306 | 0.022557
| 4:05 | 5.9308 | 0.022211
| 4:05 | 5.9311 | 0.021856
| 4:05 | 5.9314 | 0.021492
| 4:05 | 5.9317 | 0.021119
| 4:05 | 5.9319 | 0.020737
| 4:05 | 5.9322 | 0.020354
| 4:05 | 5.9325 | 0.01997
| 4:05 | 5.9328 | 0.019586
| 4:05 | 5.9331 | 0.019204
| 4:05 | 5.9333 | 0.018826
| 4:05 | 5.9336 | 0.018457
| 4:05 | 5.9339 | 0.018089
| 4:05 | 5.9342 | 0.017735
| 4:05 | 5.9344 | 0.017387
| 4:05 | 5.9347 | 0.017062
| 4:05 | 5.935 | 0.016746
| 4:05 | 5.9353 | 0.016448
| 4:05 | 5.9356 | 0.016177
| 4:05 | 5.9358 | 0.015937
| 4:05 | 5.9361 | 0.015731
| 4:05 | 5.9364 | 0.015536
| 4:05 | 5.9367 | 0.015362
| 4:05 | 5.9369 | 0.01521
| 4:05 | 5.9372 | 0.015075
| 4:05 | 5.9375 | 0.014966
| 4:05 | 5.9378 | 0.014867
| 4:05 | 5.9381 | 0.01478
| 4:05 | 5.9383 | 0.014696
| 4:05 | 5.9386 | 0.014621
| 4:05 | 5.9389 | 0.014556
| 4:05 | 5.9392 | 0.014501
| 4:05 | 5.9394 | 0.014455
| 4:05 | 5.9397 | 0.01442
| 4:05 | 5.94 | 0.014394
| 4:05 | 5.9403 | 0.014382
| 4:05 | 5.9406 | 0.014379
| 4:05 | 5.9408 | 0.014384
| 4:05 | 5.9411 | 0.01439
| 4:05 | 5.9414 | 0.014397
| 4:05 | 5.9417 | 0.014402
| 4:05 | 5.9419 | 0.014409
| 4:05 | 5.9422 | 0.014416
| 4:05 | 5.9425 | 0.014421
| 4:05 | 5.9428 | 0.01442
| 4:05 | 5.9431 | 0.014414
| 4:05 | 5.9433 | 0.014398
| 4:05 | 5.9436 | 0.014375
| 4:05 | 5.9439 | 0.014337
| 4:05 | 5.9442 | 0.014292
| 4:05 | 5.9444 | 0.014241
| 4:05 | 5.9447 | 0.014176
| 4:06 | 5.945 | 0.014105
| 4:06 | 5.9453 | 0.014028
| 4:06 | 5.9456 | 0.013937
| 4:06 | 5.9458 | 0.013841
| 4:06 | 5.9461 | 0.013742
| 4:06 | 5.9464 | 0.013634
| 4:06 | 5.9467 | 0.013514
| 4:06 | 5.9469 | 0.013385
| 4:06 | 5.9472 | 0.013244
| 4:06 | 5.9475 | 0.013093
| 4:06 | 5.9478 | 0.012932
| 4:06 | 5.9481 | 0.01276
| 4:06 | 5.9483 | 0.012578
| 4:06 | 5.9486 | 0.012385
| 4:06 | 5.9489 | 0.012181
| 4:06 | 5.9492 | 0.011965
| 4:06 | 5.9494 | 0.011733
| 4:06 | 5.9497 | 0.011496
| 4:06 | 5.95 | 0.011253
| 4:06 | 5.9503 | 0.01101
| 4:06 | 5.9506 | 0.010763
| 4:06 | 5.9508 | 0.010518
| 4:06 | 5.9511 | 0.010275
| 4:06 | 5.9514 | 0.010043
| 4:06 | 5.9517 | 0.009824
| 4:06 | 5.9519 | 0.0096151
| 4:06 | 5.9522 | 0.009422
| 4:06 | 5.9525 | 0.0092389
| 4:06 | 5.9528 | 0.0090731
| 4:06 | 5.9531 | 0.0089166
| 4:06 | 5.9533 | 0.0087731
| 4:06 | 5.9536 | 0.0086394
| 4:06 | 5.9539 | 0.0085158
| 4:06 | 5.9542 | 0.0084088
| 4:06 | 5.9544 | 0.0083076
| 4:06 | 5.9547 | 0.0082166
| 4:06 | 5.955 | 0.0081319
| 4:06 | 5.9553 | 0.0080537
| 4:06 | 5.9556 | 0.007982
| 4:06 | 5.9558 | 0.0079167
| 4:06 | 5.9561 | 0.0078579
| 4:06 | 5.9564 | 0.0078055
| 4:06 | 5.9567 | 0.0077596
| 4:06 | 5.9569 | 0.0077202
| 4:06 | 5.9572 | 0.0076835
| 4:06 | 5.9575 | 0.0076493
| 4:06 | 5.9578 | 0.0076117
| 4:06 | 5.9581 | 0.0075721
| 4:06 | 5.9583 | 0.007528
| 4:06 | 5.9586 | 0.0074803
| 4:06 | 5.9589 | 0.0074285
| 4:06 | 5.9592 | 0.0073721
| 4:06 | 5.9594 | 0.0073149
| 4:06 | 5.9597 | 0.0072551
| 4:06 | 5.96 | 0.0071937
| 4:06 | 5.9603 | 0.007131
| 4:06 | 5.9606 | 0.0070655
| 4:06 | 5.9608 | 0.006999
| 4:06 | 5.9611 | 0.0069361
| 4:06 | 5.9614 | 0.0068776
| 4:06 | 5.9617 | 0.0068268
| 4:07 | 5.9619 | 0.0067789
| 4:07 | 5.9622 | 0.0067413
| 4:07 | 5.9625 | 0.0067054
| 4:07 | 5.9628 | 0.0066779
| 4:07 | 5.9631 | 0.0066528
| 4:07 | 5.9633 | 0.0066267
| 4:07 | 5.9636 | 0.0065986
| 4:07 | 5.9639 | 0.0065685
| 4:07 | 5.9642 | 0.0065364
| 4:07 | 5.9644 | 0.0065023
| 4:07 | 5.9647 | 0.0064661
| 4:07 | 5.965 | 0.0064279
| 4:07 | 5.9653 | 0.0063877
| 4:07 | 5.9656 | 0.006345
| 4:07 | 5.9658 | 0.0062989
| 4:07 | 5.9661 | 0.00625
| 4:07 | 5.9664 | 0.0061921
| 4:07 | 5.9667 | 0.0061287
| 4:07 | 5.9669 | 0.0060641
| 4:07 | 5.9672 | 0.0059967
| 4:07 | 5.9675 | 0.0059265
| 4:07 | 5.9678 | 0.0058477
| 4:07 | 5.9681 | 0.0057653
| 4:07 | 5.9683 | 0.0056764
| 4:07 | 5.9686 | 0.0055878
| 4:07 | 5.9689 | 0.0054993
| 4:07 | 5.9692 | 0.005411
| 4:07 | 5.9694 | 0.0053225
| 4:07 | 5.9697 | 0.0052324
| 4:07 | 5.97 | 0.0051425
| 4:07 | 5.9703 | 0.0050524
| 4:07 | 5.9706 | 0.0049606
| 4:07 | 5.9708 | 0.004869
| 4:07 | 5.9711 | 0.004779
| 4:07 | 5.9714 | 0.0046906
| 4:07 | 5.9717 | 0.0046046
| 4:07 | 5.9719 | 0.0045226
| 4:07 | 5.9722 | 0.0044446
| 4:07 | 5.9725 | 0.0043706
| 4:07 | 5.9728 | 0.0043007
| 4:07 | 5.9731 | 0.0042349
| 4:07 | 5.9733 | 0.004173
| 4:07 | 5.9736 | 0.0041153
| 4:07 | 5.9739 | 0.0040633
| 4:07 | 5.9742 | 0.0040229
| 4:07 | 5.9744 | 0.0039854
| 4:07 | 5.9747 | 0.0039532
| 4:07 | 5.975 | 0.0039289
| 4:07 | 5.9753 | 0.0039103
| 4:07 | 5.9756 | 0.0038965
| 4:07 | 5.9758 | 0.0038869
| 4:07 | 5.9761 | 0.0038834
| 4:07 | 5.9764 | 0.00388
| 4:07 | 5.9767 | 0.0038833
| 4:07 | 5.9769 | 0.0038903
| 4:07 | 5.9772 | 0.0039065
| 4:07 | 5.9775 | 0.0039272
| 4:07 | 5.9778 | 0.0039665
| 4:07 | 5.9781 | 0.0040201
| 4:08 | 5.9783 | 0.0040916
| 4:08 | 5.9786 | 0.0041932
| 4:08 | 5.9789 | 0.0043265
| 4:08 | 5.9792 | 0.0044688
| 4:08 | 5.9794 | 0.0046149
| 4:08 | 5.9797 | 0.0053016
| 4:08 | 5.98 | 0.0059883
| 4:08 | 5.9803 | 0.0066757
| 4:08 | 5.9806 | 0.0073636
| 4:08 | 5.9808 | 0.008052
| 4:08 | 5.9811 | 0.008741
| 4:08 | 5.9814 | 0.0094305
| 4:08 | 5.9817 | 0.010121
| 4:08 | 5.9819 | 0.010811
| 4:08 | 5.9822 | 0.011502
| 4:08 | 5.9825 | 0.012194
| 4:08 | 5.9828 | 0.012886
| 4:08 | 5.9831 | 0.013577
| 4:08 | 5.9833 | 0.014267
| 4:08 | 5.9836 | 0.014954
| 4:08 | 5.9839 | 0.01563
| 4:08 | 5.9842 | 0.016307
| 4:08 | 5.9844 | 0.016985
| 4:08 | 5.9847 | 0.017664
| 4:08 | 5.985 | 0.018345
| 4:08 | 5.9853 | 0.019023
| 4:08 | 5.9856 | 0.019702
| 4:08 | 5.9858 | 0.020375
| 4:08 | 5.9861 | 0.021045
| 4:08 | 5.9864 | 0.021715
| 4:08 | 5.9867 | 0.022384
| 4:08 | 5.9869 | 0.02305
| 4:08 | 5.9872 | 0.023709
| 4:08 | 5.9875 | 0.024363
| 4:08 | 5.9878 | 0.025009
| 4:08 | 5.9881 | 0.025655
| 4:08 | 5.9883 | 0.026299
| 4:08 | 5.9886 | 0.026941
| 4:08 | 5.9889 | 0.027581
| 4:08 | 5.9892 | 0.028218
| 4:08 | 5.9894 | 0.028854
| 4:08 | 5.9897 | 0.029488
| 4:08 | 5.99 | 0.03012
| 4:08 | 5.9903 | 0.03075
| 4:08 | 5.9906 | 0.031381
| 4:08 | 5.9908 | 0.032013
| 4:08 | 5.9911 | 0.032642
| 4:08 | 5.9914 | 0.033266
| 4:08 | 5.9917 | 0.033884
| 4:08 | 5.9919 | 0.034499
| 4:08 | 5.9922 | 0.035114
| 4:08 | 5.9925 | 0.035732
| 4:08 | 5.9928 | 0.036352
| 4:08 | 5.9931 | 0.036972
| 4:08 | 5.9933 | 0.037594
| 4:08 | 5.9936 | 0.038218
| 4:08 | 5.9939 | 0.038841
| 4:08 | 5.9942 | 0.039463
| 4:08 | 5.9944 | 0.040088
| 4:08 | 5.9947 | 0.040716
| 4:08 | 5.995 | 0.041343
| 4:09 | 5.9953 | 0.041968
| 4:09 | 5.9956 | 0.042588
| 4:09 | 5.9958 | 0.043213
| 4:09 | 5.9961 | 0.043841
| 4:09 | 5.9964 | 0.044476
| 4:09 | 5.9967 | 0.045112
| 4:09 | 5.9969 | 0.045749
| 4:09 | 5.9972 | 0.046386
| 4:09 | 5.9975 | 0.047023
| 4:09 | 5.9978 | 0.047661
| 4:09 | 5.9981 | 0.0483
| 4:09 | 5.9983 | 0.048939
| 4:09 | 5.9986 | 0.049579
| 4:09 | 5.9989 | 0.050219
| 4:09 | 5.9992 | 0.050854
| 4:09 | 5.9994 | 0.051484
| 4:09 | 5.9997 | 0.052111
| 4:09 | 6 | 0.052736
| 4:09 | 6.0003 | 0.053365
| 4:09 | 6.0006 | 0.053995
| 4:09 | 6.0008 | 0.054625
| 4:09 | 6.0011 | 0.055255
| 4:09 | 6.0014 | 0.055885
| 4:09 | 6.0017 | 0.056511
| 4:09 | 6.0019 | 0.057137
| 4:09 | 6.0022 | 0.057766
| 4:09 | 6.0025 | 0.058396
| 4:09 | 6.0028 | 0.059023
| 4:09 | 6.0031 | 0.059644
| 4:09 | 6.0033 | 0.06026
| 4:09 | 6.0036 | 0.060875
| 4:09 | 6.0039 | 0.061492
| 4:09 | 6.0042 | 0.062114
| 4:09 | 6.0044 | 0.062734
| 4:09 | 6.0047 | 0.063353
| 4:09 | 6.005 | 0.063974
| 4:09 | 6.0053 | 0.064593
| 4:09 | 6.0056 | 0.065211
| 4:09 | 6.0058 | 0.065827
| 4:09 | 6.0061 | 0.066442
| 4:09 | 6.0064 | 0.067056
| 4:09 | 6.0067 | 0.067668
| 4:09 | 6.0069 | 0.068279
| 4:09 | 6.0072 | 0.068884
| 4:09 | 6.0075 | 0.069491
| 4:09 | 6.0078 | 0.070104
| 4:09 | 6.0081 | 0.07072
| 4:09 | 6.0083 | 0.071338
| 4:09 | 6.0086 | 0.071956
| 4:09 | 6.0089 | 0.072579
| 4:09 | 6.0092 | 0.073204
| 4:09 | 6.0094 | 0.073826
| 4:09 | 6.0097 | 0.074448
| 4:09 | 6.01 | 0.075071
| 4:09 | 6.0103 | 0.075696
| 4:09 | 6.0106 | 0.076321
| 4:09 | 6.0108 | 0.07694
| 4:09 | 6.0111 | 0.077556
| 4:09 | 6.0114 | 0.078168
| 4:10 | 6.0117 | 0.078782
| 4:10 | 6.0119 | 0.079401
| 4:10 | 6.0122 | 0.080019
| 4:10 | 6.0125 | 0.080638
| 4:10 | 6.0128 | 0.081258
| 4:10 | 6.0131 | 0.081879
| 4:10 | 6.0133 | 0.082502
| 4:10 | 6.0136 | 0.083126
| 4:10 | 6.0139 | 0.08375
| 4:10 | 6.0142 | 0.084375
| 4:10 | 6.0144 | 0.085
| 4:10 | 6.0147 | 0.085625
| 4:10 | 6.015 | 0.08625
| 4:10 | 6.0153 | 0.086876
| 4:10 | 6.0156 | 0.087502
| 4:10 | 6.0158 | 0.088128
| 4:10 | 6.0161 | 0.088754
| 4:10 | 6.0164 | 0.089382
| 4:10 | 6.0167 | 0.090011
| 4:10 | 6.0169 | 0.090646
| 4:10 | 6.0172 | 0.091277
| 4:10 | 6.0175 | 0.091908
| 4:10 | 6.0178 | 0.09254
| 4:10 | 6.0181 | 0.093178
| 4:10 | 6.0183 | 0.093814
| 4:10 | 6.0186 | 0.094445
| 4:10 | 6.0189 | 0.095074
| 4:10 | 6.0192 | 0.095698
| 4:10 | 6.0194 | 0.096328
| 4:10 | 6.0197 | 0.096964
| 4:10 | 6.02 | 0.097599
| 4:10 | 6.0203 | 0.098235
| 4:10 | 6.0206 | 0.098872
| 4:10 | 6.0208 | 0.099512
| 4:10 | 6.0211 | 0.10015
| 4:10 | 6.0214 | 0.10079
| 4:10 | 6.0217 | 0.10143
| 4:10 | 6.0219 | 0.10207
| 4:10 | 6.0222 | 0.10271
| 4:10 | 6.0225 | 0.10335
| 4:10 | 6.0228 | 0.10399
| 4:10 | 6.0231 | 0.10463
| 4:10 | 6.0233 | 0.10527
| 4:10 | 6.0236 | 0.1059
| 4:10 | 6.0239 | 0.10654
| 4:10 | 6.0242 | 0.10718
| 4:10 | 6.0244 | 0.10782
| 4:10 | 6.0247 | 0.10847
| 4:10 | 6.025 | 0.10911
| 4:10 | 6.0253 | 0.10975
| 4:10 | 6.0256 | 0.11039
| 4:10 | 6.0258 | 0.11103
| 4:10 | 6.0261 | 0.11167
| 4:10 | 6.0264 | 0.11231
| 4:10 | 6.0267 | 0.11294
| 4:10 | 6.0269 | 0.11356
| 4:10 | 6.0272 | 0.11419
| 4:10 | 6.0275 | 0.11483
| 4:10 | 6.0278 | 0.11547
| 4:10 | 6.0281 | 0.11611
| 4:10 | 6.0283 | 0.11675
| 4:11 | 6.0286 | 0.11739
| 4:11 | 6.0289 | 0.11803
| 4:11 | 6.0292 | 0.11867
| 4:11 | 6.0294 | 0.11931
| 4:11 | 6.0297 | 0.11996
| 4:11 | 6.03 | 0.1206
| 4:11 | 6.0303 | 0.12125
| 4:11 | 6.0306 | 0.1219
| 4:11 | 6.0308 | 0.12254
| 4:11 | 6.0311 | 0.12319
| 4:11 | 6.0314 | 0.12384
| 4:11 | 6.0317 | 0.12448
| 4:11 | 6.0319 | 0.12513
| 4:11 | 6.0322 | 0.12578
| 4:11 | 6.0325 | 0.12642
| 4:11 | 6.0328 | 0.12706
| 4:11 | 6.0331 | 0.1277
| 4:11 | 6.0333 | 0.12834
| 4:11 | 6.0336 | 0.12899
| 4:11 | 6.0339 | 0.12963
| 4:11 | 6.0342 | 0.13027
| 4:11 | 6.0344 | 0.1309
| 4:11 | 6.0347 | 0.13153
| 4:11 | 6.035 | 0.13216
| 4:11 | 6.0353 | 0.13279
| 4:11 | 6.0356 | 0.13343
| 4:11 | 6.0358 | 0.13407
| 4:11 | 6.0361 | 0.13471
| 4:11 | 6.0364 | 0.13535
| 4:11 | 6.0367 | 0.136
| 4:11 | 6.0369 | 0.13664
| 4:11 | 6.0372 | 0.13728
| 4:11 | 6.0375 | 0.13792
| 4:11 | 6.0378 | 0.13856
| 4:11 | 6.0381 | 0.1392
| 4:11 | 6.0383 | 0.13984
| 4:11 | 6.0386 | 0.14048
| 4:11 | 6.0389 | 0.14112
| 4:11 | 6.0392 | 0.14177
| 4:11 | 6.0394 | 0.14241
| 4:11 | 6.0397 | 0.14305
| 4:11 | 6.04 | 0.1437
| 4:11 | 6.0403 | 0.14435
| 4:11 | 6.0406 | 0.14498
| 4:11 | 6.0408 | 0.14562
| 4:11 | 6.0411 | 0.14626
| 4:11 | 6.0414 | 0.1469
| 4:11 | 6.0417 | 0.14754
| 4:11 | 6.0419 | 0.14818
| 4:11 | 6.0422 | 0.14881
| 4:11 | 6.0425 | 0.14943
| 4:11 | 6.0428 | 0.15006
| 4:11 | 6.0431 | 0.15069
| 4:11 | 6.0433 | 0.15133
| 4:11 | 6.0436 | 0.15196
| 4:11 | 6.0439 | 0.1526
| 4:11 | 6.0442 | 0.15324
| 4:11 | 6.0444 | 0.15387
| 4:11 | 6.0447 | 0.15451
| 4:12 | 6.045 | 0.15515
| 4:12 | 6.0453 | 0.15578
| 4:12 | 6.0456 | 0.15642
| 4:12 | 6.0458 | 0.15704
| 4:12 | 6.0461 | 0.15766
| 4:12 | 6.0464 | 0.15827
| 4:12 | 6.0467 | 0.15889
| 4:12 | 6.0469 | 0.15951
| 4:12 | 6.0472 | 0.16013
| 4:12 | 6.0475 | 0.16075
| 4:12 | 6.0478 | 0.16137
| 4:12 | 6.0481 | 0.16199
| 4:12 | 6.0483 | 0.16261
| 4:12 | 6.0486 | 0.16323
| 4:12 | 6.0489 | 0.16385
| 4:12 | 6.0492 | 0.16448
| 4:12 | 6.0494 | 0.1651
| 4:12 | 6.0497 | 0.16572
| 4:12 | 6.05 | 0.16634
| 4:12 | 6.0503 | 0.16694
| 4:12 | 6.0506 | 0.16755
| 4:12 | 6.0508 | 0.16817
| 4:12 | 6.0511 | 0.16879
| 4:12 | 6.0514 | 0.16942
| 4:12 | 6.0517 | 0.17004
| 4:12 | 6.0519 | 0.17067
| 4:12 | 6.0522 | 0.17129
| 4:12 | 6.0525 | 0.17191
| 4:12 | 6.0528 | 0.17254
| 4:12 | 6.0531 | 0.17316
| 4:12 | 6.0533 | 0.17378
| 4:12 | 6.0536 | 0.17439
| 4:12 | 6.0539 | 0.17499
| 4:12 | 6.0542 | 0.17559
| 4:12 | 6.0544 | 0.17619
| 4:12 | 6.0547 | 0.1768
| 4:12 | 6.055 | 0.17741
| 4:12 | 6.0553 | 0.17801
| 4:12 | 6.0556 | 0.17861
| 4:12 | 6.0558 | 0.17921
| 4:12 | 6.0561 | 0.1798
| 4:12 | 6.0564 | 0.18039
| 4:12 | 6.0567 | 0.18098
| 4:12 | 6.0569 | 0.18157
| 4:12 | 6.0572 | 0.18215
| 4:12 | 6.0575 | 0.18272
| 4:12 | 6.0578 | 0.18328
| 4:12 | 6.0581 | 0.18384
| 4:12 | 6.0583 | 0.18439
| 4:12 | 6.0586 | 0.18494
| 4:12 | 6.0589 | 0.18549
| 4:12 | 6.0592 | 0.18604
| 4:12 | 6.0594 | 0.18659
| 4:12 | 6.0597 | 0.18714
| 4:12 | 6.06 | 0.18768
| 4:12 | 6.0603 | 0.1882
| 4:12 | 6.0606 | 0.18873
| 4:12 | 6.0608 | 0.18925
| 4:12 | 6.0611 | 0.18976
| 4:12 | 6.0614 | 0.19026
| 4:12 | 6.0617 | 0.19075
| 4:13 | 6.0619 | 0.19123
| 4:13 | 6.0622 | 0.19171
| 4:13 | 6.0625 | 0.19218
| 4:13 | 6.0628 | 0.19265
| 4:13 | 6.0631 | 0.19311
| 4:13 | 6.0633 | 0.19356
| 4:13 | 6.0636 | 0.19399
| 4:13 | 6.0639 | 0.19441
| 4:13 | 6.0642 | 0.19481
| 4:13 | 6.0644 | 0.19519
| 4:13 | 6.0647 | 0.19555
| 4:13 | 6.065 | 0.1959
| 4:13 | 6.0653 | 0.19622
| 4:13 | 6.0656 | 0.19653
| 4:13 | 6.0658 | 0.19682
| 4:13 | 6.0661 | 0.19707
| 4:13 | 6.0664 | 0.19731
| 4:13 | 6.0667 | 0.19753
| 4:13 | 6.0669 | 0.1977
| 4:13 | 6.0672 | 0.19785
| 4:13 | 6.0675 | 0.19799
| 4:13 | 6.0678 | 0.19809
| 4:13 | 6.0681 | 0.19817
| 4:13 | 6.0683 | 0.19824
| 4:13 | 6.0686 | 0.1983
| 4:13 | 6.0689 | 0.19835
| 4:13 | 6.0692 | 0.1984
| 4:13 | 6.0694 | 0.19843
| 4:13 | 6.0697 | 0.19846
| 4:13 | 6.07 | 0.19849
| 4:13 | 6.0703 | 0.19852
| 4:13 | 6.0706 | 0.19854
| 4:13 | 6.0708 | 0.19856
| 4:13 | 6.0711 | 0.19858
| 4:13 | 6.0714 | 0.19861
| 4:13 | 6.0717 | 0.19863
| 4:13 | 6.0719 | 0.19866
| 4:13 | 6.0722 | 0.19868
| 4:13 | 6.0725 | 0.19871
| 4:13 | 6.0728 | 0.19873
| 4:13 | 6.0731 | 0.19876
| 4:13 | 6.0733 | 0.19879
| 4:13 | 6.0736 | 0.19882
| 4:13 | 6.0739 | 0.19885
| 4:13 | 6.0742 | 0.19889
| 4:13 | 6.0744 | 0.19893
| 4:13 | 6.0747 | 0.19898
| 4:13 | 6.075 | 0.19903
| 4:13 | 6.0753 | 0.19908
| 4:13 | 6.0756 | 0.19914
| 4:13 | 6.0758 | 0.1992
| 4:13 | 6.0761 | 0.19927
| 4:13 | 6.0764 | 0.19934
| 4:13 | 6.0767 | 0.19942
| 4:13 | 6.0769 | 0.19951
| 4:13 | 6.0772 | 0.1996
| 4:13 | 6.0775 | 0.1997
| 4:13 | 6.0778 | 0.1998
| 4:13 | 6.0781 | 0.19992
| 4:14 | 6.0783 | 0.20005
| 4:14 | 6.0786 | 0.20018
| 4:14 | 6.0789 | 0.20033
| 4:14 | 6.0792 | 0.20049
| 4:14 | 6.0794 | 0.20065
| 4:14 | 6.0797 | 0.20083
| 4:14 | 6.08 | 0.20102
| 4:14 | 6.0803 | 0.20121
| 4:14 | 6.0806 | 0.20142
| 4:14 | 6.0808 | 0.20163
| 4:14 | 6.0811 | 0.20186
| 4:14 | 6.0814 | 0.20209
| 4:14 | 6.0817 | 0.20233
| 4:14 | 6.0819 | 0.20259
| 4:14 | 6.0822 | 0.20285
| 4:14 | 6.0825 | 0.20311
| 4:14 | 6.0828 | 0.20339
| 4:14 | 6.0831 | 0.20367
| 4:14 | 6.0833 | 0.20395
| 4:14 | 6.0836 | 0.20424
| 4:14 | 6.0839 | 0.20453
| 4:14 | 6.0842 | 0.20482
| 4:14 | 6.0844 | 0.20512
| 4:14 | 6.0847 | 0.20541
| 4:14 | 6.085 | 0.2057
| 4:14 | 6.0853 | 0.20599
| 4:14 | 6.0856 | 0.20628
| 4:14 | 6.0858 | 0.20657
| 4:14 | 6.0861 | 0.20686
| 4:14 | 6.0864 | 0.20714
| 4:14 | 6.0867 | 0.20743
| 4:14 | 6.0869 | 0.20771
| 4:14 | 6.0872 | 0.20799
| 4:14 | 6.0875 | 0.20826
| 4:14 | 6.0878 | 0.20853
| 4:14 | 6.0881 | 0.2088
| 4:14 | 6.0883 | 0.20906
| 4:14 | 6.0886 | 0.20931
| 4:14 | 6.0889 | 0.20956
| 4:14 | 6.0892 | 0.20981
| 4:14 | 6.0894 | 0.21005
| 4:14 | 6.0897 | 0.21028
| 4:14 | 6.09 | 0.21051
| 4:14 | 6.0903 | 0.21074
| 4:14 | 6.0906 | 0.21096
| 4:14 | 6.0908 | 0.21117
| 4:14 | 6.0911 | 0.21138
| 4:14 | 6.0914 | 0.21159
| 4:14 | 6.0917 | 0.21179
| 4:14 | 6.0919 | 0.212
| 4:14 | 6.0922 | 0.21219
| 4:14 | 6.0925 | 0.21238
| 4:14 | 6.0928 | 0.21257
| 4:14 | 6.0931 | 0.21276
| 4:14 | 6.0933 | 0.21295
| 4:14 | 6.0936 | 0.21314
| 4:14 | 6.0939 | 0.21333
| 4:14 | 6.0942 | 0.21352
| 4:14 | 6.0944 | 0.21371
| 4:14 | 6.0947 | 0.21391
| 4:15 | 6.095 | 0.21409
| 4:15 | 6.0953 | 0.21428
| 4:15 | 6.0956 | 0.21447
| 4:15 | 6.0958 | 0.21465
| 4:15 | 6.0961 | 0.21483
| 4:15 | 6.0964 | 0.215
| 4:15 | 6.0967 | 0.21516
| 4:15 | 6.0969 | 0.21532
| 4:15 | 6.0972 | 0.21547
| 4:15 | 6.0975 | 0.21562
| 4:15 | 6.0978 | 0.21576
| 4:15 | 6.0981 | 0.21589
| 4:15 | 6.0983 | 0.21602
| 4:15 | 6.0986 | 0.21614
| 4:15 | 6.0989 | 0.21625
| 4:15 | 6.0992 | 0.21636
| 4:15 | 6.0994 | 0.21645
| 4:15 | 6.0997 | 0.21654
| 4:15 | 6.1 | 0.21661
| 4:15 | 6.1003 | 0.21666
| 4:15 | 6.1006 | 0.21671
| 4:15 | 6.1008 | 0.21673
| 4:15 | 6.1011 | 0.21675
| 4:15 | 6.1014 | 0.21675
| 4:15 | 6.1017 | 0.21673
| 4:15 | 6.1019 | 0.21671
| 4:15 | 6.1022 | 0.21667
| 4:15 | 6.1025 | 0.21662
| 4:15 | 6.1028 | 0.21655
| 4:15 | 6.1031 | 0.21648
| 4:15 | 6.1033 | 0.2164
| 4:15 | 6.1036 | 0.21631
| 4:15 | 6.1039 | 0.21622
| 4:15 | 6.1042 | 0.21612
| 4:15 | 6.1044 | 0.21602
| 4:15 | 6.1047 | 0.21591
| 4:15 | 6.105 | 0.2158
| 4:15 | 6.1053 | 0.21567
| 4:15 | 6.1056 | 0.21555
| 4:15 | 6.1058 | 0.21541
| 4:15 | 6.1061 | 0.21527
| 4:15 | 6.1064 | 0.21512
| 4:15 | 6.1067 | 0.21497
| 4:15 | 6.1069 | 0.21481
| 4:15 | 6.1072 | 0.21464
| 4:15 | 6.1075 | 0.21447
| 4:15 | 6.1078 | 0.21429
| 4:15 | 6.1081 | 0.2141
| 4:15 | 6.1083 | 0.2139
| 4:15 | 6.1086 | 0.2137
| 4:15 | 6.1089 | 0.2135
| 4:15 | 6.1092 | 0.21329
| 4:15 | 6.1094 | 0.21307
| 4:15 | 6.1097 | 0.21286
| 4:15 | 6.11 | 0.21264
| 4:15 | 6.1103 | 0.21242
| 4:15 | 6.1106 | 0.2122
| 4:15 | 6.1108 | 0.21199
| 4:15 | 6.1111 | 0.21177
| 4:15 | 6.1114 | 0.21155
| 4:16 | 6.1117 | 0.21134
| 4:16 | 6.1119 | 0.21113
| 4:16 | 6.1122 | 0.21092
| 4:16 | 6.1125 | 0.21072
| 4:16 | 6.1128 | 0.21052
| 4:16 | 6.1131 | 0.21032
| 4:16 | 6.1133 | 0.21012
| 4:16 | 6.1136 | 0.20993
| 4:16 | 6.1139 | 0.20974
| 4:16 | 6.1142 | 0.20955
| 4:16 | 6.1144 | 0.20936
| 4:16 | 6.1147 | 0.20917
| 4:16 | 6.115 | 0.20899
| 4:16 | 6.1153 | 0.20881
| 4:16 | 6.1156 | 0.20863
| 4:16 | 6.1158 | 0.20844
| 4:16 | 6.1161 | 0.20826
| 4:16 | 6.1164 | 0.20808
| 4:16 | 6.1167 | 0.2079
| 4:16 | 6.1169 | 0.20772
| 4:16 | 6.1172 | 0.20754
| 4:16 | 6.1175 | 0.20736
| 4:16 | 6.1178 | 0.20718
| 4:16 | 6.1181 | 0.207
| 4:16 | 6.1183 | 0.20682
| 4:16 | 6.1186 | 0.20663
| 4:16 | 6.1189 | 0.20645
| 4:16 | 6.1192 | 0.20626
| 4:16 | 6.1194 | 0.20607
| 4:16 | 6.1197 | 0.20587
| 4:16 | 6.12 | 0.20567
| 4:16 | 6.1203 | 0.20547
| 4:16 | 6.1206 | 0.20527
| 4:16 | 6.1208 | 0.20506
| 4:16 | 6.1211 | 0.20486
| 4:16 | 6.1214 | 0.20465
| 4:16 | 6.1217 | 0.20445
| 4:16 | 6.1219 | 0.20425
| 4:16 | 6.1222 | 0.20406
| 4:16 | 6.1225 | 0.20388
| 4:16 | 6.1228 | 0.20369
| 4:16 | 6.1231 | 0.20352
| 4:16 | 6.1233 | 0.20334
| 4:16 | 6.1236 | 0.20318
| 4:16 | 6.1239 | 0.20301
| 4:16 | 6.1242 | 0.20287
| 4:16 | 6.1244 | 0.20273
| 4:16 | 6.1247 | 0.20261
| 4:16 | 6.125 | 0.20249
| 4:16 | 6.1253 | 0.20238
| 4:16 | 6.1256 | 0.20229
| 4:16 | 6.1258 | 0.2022
| 4:16 | 6.1261 | 0.20213
| 4:16 | 6.1264 | 0.20206
| 4:16 | 6.1267 | 0.202
| 4:16 | 6.1269 | 0.20195
| 4:16 | 6.1272 | 0.20191
| 4:16 | 6.1275 | 0.20188
| 4:16 | 6.1278 | 0.20185
| 4:16 | 6.1281 | 0.20183
| 4:16 | 6.1283 | 0.20182
| 4:17 | 6.1286 | 0.20181
| 4:17 | 6.1289 | 0.2018
| 4:17 | 6.1292 | 0.2018
| 4:17 | 6.1294 | 0.20179
| 4:17 | 6.1297 | 0.20179
| 4:17 | 6.13 | 0.20179
| 4:17 | 6.1303 | 0.20178
| 4:17 | 6.1306 | 0.20177
| 4:17 | 6.1308 | 0.20175
| 4:17 | 6.1311 | 0.20173
| 4:17 | 6.1314 | 0.2017
| 4:17 | 6.1317 | 0.20166
| 4:17 | 6.1319 | 0.20162
| 4:17 | 6.1322 | 0.20157
| 4:17 | 6.1325 | 0.20152
| 4:17 | 6.1328 | 0.20144
| 4:17 | 6.1331 | 0.20135
| 4:17 | 6.1333 | 0.20126
| 4:17 | 6.1336 | 0.20114
| 4:17 | 6.1339 | 0.20101
| 4:17 | 6.1342 | 0.20086
| 4:17 | 6.1344 | 0.2007
| 4:17 | 6.1347 | 0.20051
| 4:17 | 6.135 | 0.20031
| 4:17 | 6.1353 | 0.20009
| 4:17 | 6.1356 | 0.19986
| 4:17 | 6.1358 | 0.19961
| 4:17 | 6.1361 | 0.19935
| 4:17 | 6.1364 | 0.19906
| 4:17 | 6.1367 | 0.19876
| 4:17 | 6.1369 | 0.19845
| 4:17 | 6.1372 | 0.19813
| 4:17 | 6.1375 | 0.19779
| 4:17 | 6.1378 | 0.19744
| 4:17 | 6.1381 | 0.19708
| 4:17 | 6.1383 | 0.19671
| 4:17 | 6.1386 | 0.19635
| 4:17 | 6.1389 | 0.19599
| 4:17 | 6.1392 | 0.19563
| 4:17 | 6.1394 | 0.19526
| 4:17 | 6.1397 | 0.1949
| 4:17 | 6.14 | 0.19454
| 4:17 | 6.1403 | 0.19419
| 4:17 | 6.1406 | 0.19384
| 4:17 | 6.1408 | 0.1935
| 4:17 | 6.1411 | 0.19317
| 4:17 | 6.1414 | 0.19285
| 4:17 | 6.1417 | 0.19252
| 4:17 | 6.1419 | 0.19221
| 4:17 | 6.1422 | 0.1919
| 4:17 | 6.1425 | 0.1916
| 4:17 | 6.1428 | 0.1913
| 4:17 | 6.1431 | 0.19101
| 4:17 | 6.1433 | 0.19071
| 4:17 | 6.1436 | 0.19042
| 4:17 | 6.1439 | 0.19012
| 4:17 | 6.1442 | 0.18983
| 4:17 | 6.1444 | 0.18954
| 4:17 | 6.1447 | 0.18925
| 4:18 | 6.145 | 0.18895
| 4:18 | 6.1453 | 0.18867
| 4:18 | 6.1456 | 0.18838
| 4:18 | 6.1458 | 0.18809
| 4:18 | 6.1461 | 0.18781
| 4:18 | 6.1464 | 0.18754
| 4:18 | 6.1467 | 0.18726
| 4:18 | 6.1469 | 0.18699
| 4:18 | 6.1472 | 0.18673
| 4:18 | 6.1475 | 0.18647
| 4:18 | 6.1478 | 0.18622
| 4:18 | 6.1481 | 0.18597
| 4:18 | 6.1483 | 0.18572
| 4:18 | 6.1486 | 0.18549
| 4:18 | 6.1489 | 0.18525
| 4:18 | 6.1492 | 0.18502
| 4:18 | 6.1494 | 0.1848
| 4:18 | 6.1497 | 0.18459
| 4:18 | 6.15 | 0.18438
| 4:18 | 6.1503 | 0.18418
| 4:18 | 6.1506 | 0.18398
| 4:18 | 6.1508 | 0.18379
| 4:18 | 6.1511 | 0.18361
| 4:18 | 6.1514 | 0.18343
| 4:18 | 6.1517 | 0.18327
| 4:18 | 6.1519 | 0.18311
| 4:18 | 6.1522 | 0.18295
| 4:18 | 6.1525 | 0.1828
| 4:18 | 6.1528 | 0.18265
| 4:18 | 6.1531 | 0.1825
| 4:18 | 6.1533 | 0.18236
| 4:18 | 6.1536 | 0.18221
| 4:18 | 6.1539 | 0.18207
| 4:18 | 6.1542 | 0.18192
| 4:18 | 6.1544 | 0.18176
| 4:18 | 6.1547 | 0.18161
| 4:18 | 6.155 | 0.18144
| 4:18 | 6.1553 | 0.18128
| 4:18 | 6.1556 | 0.1811
| 4:18 | 6.1558 | 0.18092
| 4:18 | 6.1561 | 0.18073
| 4:18 | 6.1564 | 0.18054
| 4:18 | 6.1567 | 0.18034
| 4:18 | 6.1569 | 0.18013
| 4:18 | 6.1572 | 0.17992
| 4:18 | 6.1575 | 0.1797
| 4:18 | 6.1578 | 0.17947
| 4:18 | 6.1581 | 0.17924
| 4:18 | 6.1583 | 0.17901
| 4:18 | 6.1586 | 0.17877
| 4:18 | 6.1589 | 0.17853
| 4:18 | 6.1592 | 0.17828
| 4:18 | 6.1594 | 0.17802
| 4:18 | 6.1597 | 0.17775
| 4:18 | 6.16 | 0.17747
| 4:18 | 6.1603 | 0.17718
| 4:18 | 6.1606 | 0.17688
| 4:18 | 6.1608 | 0.17658
| 4:18 | 6.1611 | 0.17627
| 4:18 | 6.1614 | 0.17596
| 4:18 | 6.1617 | 0.17564
| 4:19 | 6.1619 | 0.17531
| 4:19 | 6.1622 | 0.17499
| 4:19 | 6.1625 | 0.17465
| 4:19 | 6.1628 | 0.17432
| 4:19 | 6.1631 | 0.17399
| 4:19 | 6.1633 | 0.17365
| 4:19 | 6.1636 | 0.17331
| 4:19 | 6.1639 | 0.17299
| 4:19 | 6.1642 | 0.17266
| 4:19 | 6.1644 | 0.17234
| 4:19 | 6.1647 | 0.17202
| 4:19 | 6.165 | 0.17171
| 4:19 | 6.1653 | 0.1714
| 4:19 | 6.1656 | 0.17109
| 4:19 | 6.1658 | 0.1708
| 4:19 | 6.1661 | 0.17052
| 4:19 | 6.1664 | 0.17025
| 4:19 | 6.1667 | 0.16999
| 4:19 | 6.1669 | 0.16974
| 4:19 | 6.1672 | 0.16951
| 4:19 | 6.1675 | 0.16929
| 4:19 | 6.1678 | 0.16909
| 4:19 | 6.1681 | 0.16889
| 4:19 | 6.1683 | 0.1687
| 4:19 | 6.1686 | 0.16852
| 4:19 | 6.1689 | 0.16835
| 4:19 | 6.1692 | 0.16818
| 4:19 | 6.1694 | 0.16802
| 4:19 | 6.1697 | 0.16787
| 4:19 | 6.17 | 0.16773
| 4:19 | 6.1703 | 0.16759
| 4:19 | 6.1706 | 0.16745
| 4:19 | 6.1708 | 0.16731
| 4:19 | 6.1711 | 0.16719
| 4:19 | 6.1714 | 0.16706
| 4:19 | 6.1717 | 0.16694
| 4:19 | 6.1719 | 0.16681
| 4:19 | 6.1722 | 0.16667
| 4:19 | 6.1725 | 0.16654
| 4:19 | 6.1728 | 0.16639
| 4:19 | 6.1731 | 0.16625
| 4:19 | 6.1733 | 0.16609
| 4:19 | 6.1736 | 0.16593
| 4:19 | 6.1739 | 0.16575
| 4:19 | 6.1742 | 0.16553
| 4:19 | 6.1744 | 0.1653
| 4:19 | 6.1747 | 0.16505
| 4:19 | 6.175 | 0.16478
| 4:19 | 6.1753 | 0.16449
| 4:19 | 6.1756 | 0.16419
| 4:19 | 6.1758 | 0.16388
| 4:19 | 6.1761 | 0.16355
| 4:19 | 6.1764 | 0.16323
| 4:19 | 6.1767 | 0.16289
| 4:19 | 6.1769 | 0.16255
| 4:19 | 6.1772 | 0.1622
| 4:19 | 6.1775 | 0.16187
| 4:19 | 6.1778 | 0.16152
| 4:19 | 6.1781 | 0.16118
| 4:20 | 6.1783 | 0.16083
| 4:20 | 6.1786 | 0.16048
| 4:20 | 6.1789 | 0.16014
| 4:20 | 6.1792 | 0.15982
| 4:20 | 6.1794 | 0.15951
| 4:20 | 6.1797 | 0.15921
| 4:20 | 6.18 | 0.15891
| 4:20 | 6.1803 | 0.15861
| 4:20 | 6.1806 | 0.15832
| 4:20 | 6.1808 | 0.15804
| 4:20 | 6.1811 | 0.15775
| 4:20 | 6.1814 | 0.15747
| 4:20 | 6.1817 | 0.1572
| 4:20 | 6.1819 | 0.15693
| 4:20 | 6.1822 | 0.15666
| 4:20 | 6.1825 | 0.15638
| 4:20 | 6.1828 | 0.15611
| 4:20 | 6.1831 | 0.15583
| 4:20 | 6.1833 | 0.15554
| 4:20 | 6.1836 | 0.15525
| 4:20 | 6.1839 | 0.15495
| 4:20 | 6.1842 | 0.15464
| 4:20 | 6.1844 | 0.15432
| 4:20 | 6.1847 | 0.15398
| 4:20 | 6.185 | 0.15362
| 4:20 | 6.1853 | 0.15325
| 4:20 | 6.1856 | 0.15284
| 4:20 | 6.1858 | 0.15241
| 4:20 | 6.1861 | 0.15193
| 4:20 | 6.1864 | 0.15144
| 4:20 | 6.1867 | 0.15094
| 4:20 | 6.1869 | 0.1504
| 4:20 | 6.1872 | 0.14985
| 4:20 | 6.1875 | 0.14927
| 4:20 | 6.1878 | 0.14868
| 4:20 | 6.1881 | 0.14807
| 4:20 | 6.1883 | 0.14746
| 4:20 | 6.1886 | 0.14683
| 4:20 | 6.1889 | 0.14619
| 4:20 | 6.1892 | 0.14553
| 4:20 | 6.1894 | 0.14486
| 4:20 | 6.1897 | 0.14418
| 4:20 | 6.19 | 0.14349
| 4:20 | 6.1903 | 0.14278
| 4:20 | 6.1906 | 0.14206
| 4:20 | 6.1908 | 0.14134
| 4:20 | 6.1911 | 0.14061
| 4:20 | 6.1914 | 0.13989
| 4:20 | 6.1917 | 0.13916
| 4:20 | 6.1919 | 0.13844
| 4:20 | 6.1922 | 0.13772
| 4:20 | 6.1925 | 0.137
| 4:20 | 6.1928 | 0.13628
| 4:20 | 6.1931 | 0.13557
| 4:20 | 6.1933 | 0.13487
| 4:20 | 6.1936 | 0.13418
| 4:20 | 6.1939 | 0.1335
| 4:20 | 6.1942 | 0.13283
| 4:20 | 6.1944 | 0.13216
| 4:20 | 6.1947 | 0.13151
| 4:20 | 6.195 | 0.13086
| 4:21 | 6.1953 | 0.13023
| 4:21 | 6.1956 | 0.1296
| 4:21 | 6.1958 | 0.12898
| 4:21 | 6.1961 | 0.12837
| 4:21 | 6.1964 | 0.12776
| 4:21 | 6.1967 | 0.12717
| 4:21 | 6.1969 | 0.12658
| 4:21 | 6.1972 | 0.12601
| 4:21 | 6.1975 | 0.12546
| 4:21 | 6.1978 | 0.12491
| 4:21 | 6.1981 | 0.12437
| 4:21 | 6.1983 | 0.12385
| 4:21 | 6.1986 | 0.12334
| 4:21 | 6.1989 | 0.12284
| 4:21 | 6.1992 | 0.12235
| 4:21 | 6.1994 | 0.12188
| 4:21 | 6.1997 | 0.12142
| 4:21 | 6.2 | 0.12096
| 4:21 | 6.2003 | 0.12051
| 4:21 | 6.2006 | 0.12007
| 4:21 | 6.2008 | 0.11962
| 4:21 | 6.2011 | 0.11918
| 4:21 | 6.2014 | 0.11873
| 4:21 | 6.2017 | 0.11826
| 4:21 | 6.2019 | 0.11779
| 4:21 | 6.2022 | 0.11731
| 4:21 | 6.2025 | 0.11681
| 4:21 | 6.2028 | 0.1163
| 4:21 | 6.2031 | 0.11579
| 4:21 | 6.2033 | 0.11526
| 4:21 | 6.2036 | 0.11472
| 4:21 | 6.2039 | 0.11417
| 4:21 | 6.2042 | 0.11361
| 4:21 | 6.2044 | 0.11304
| 4:21 | 6.2047 | 0.11246
| 4:21 | 6.205 | 0.11187
| 4:21 | 6.2053 | 0.11128
| 4:21 | 6.2056 | 0.11068
| 4:21 | 6.2058 | 0.11007
| 4:21 | 6.2061 | 0.10946
| 4:21 | 6.2064 | 0.10884
| 4:21 | 6.2067 | 0.10821
| 4:21 | 6.2069 | 0.10757
| 4:21 | 6.2072 | 0.10694
| 4:21 | 6.2075 | 0.10629
| 4:21 | 6.2078 | 0.10565
| 4:21 | 6.2081 | 0.10501
| 4:21 | 6.2083 | 0.10436
| 4:21 | 6.2086 | 0.10372
| 4:21 | 6.2089 | 0.10308
| 4:21 | 6.2092 | 0.10244
| 4:21 | 6.2094 | 0.1018
| 4:21 | 6.2097 | 0.10116
| 4:21 | 6.21 | 0.10052
| 4:21 | 6.2103 | 0.099871
| 4:21 | 6.2106 | 0.099224
| 4:21 | 6.2108 | 0.098574
| 4:21 | 6.2111 | 0.097918
| 4:21 | 6.2114 | 0.097253
| 4:22 | 6.2117 | 0.096579
| 4:22 | 6.2119 | 0.095901
| 4:22 | 6.2122 | 0.095209
| 4:22 | 6.2125 | 0.094516
| 4:22 | 6.2128 | 0.093815
| 4:22 | 6.2131 | 0.093112
| 4:22 | 6.2133 | 0.092413
| 4:22 | 6.2136 | 0.091716
| 4:22 | 6.2139 | 0.091023
| 4:22 | 6.2142 | 0.090334
| 4:22 | 6.2144 | 0.089648
| 4:22 | 6.2147 | 0.088965
| 4:22 | 6.215 | 0.088286
| 4:22 | 6.2153 | 0.087611
| 4:22 | 6.2156 | 0.086939
| 4:22 | 6.2158 | 0.086271
| 4:22 | 6.2161 | 0.085605
| 4:22 | 6.2164 | 0.084947
| 4:22 | 6.2167 | 0.084294
| 4:22 | 6.2169 | 0.083641
| 4:22 | 6.2172 | 0.082988
| 4:22 | 6.2175 | 0.082334
| 4:22 | 6.2178 | 0.081686
| 4:22 | 6.2181 | 0.081037
| 4:22 | 6.2183 | 0.080394
| 4:22 | 6.2186 | 0.07975
| 4:22 | 6.2189 | 0.079103
| 4:22 | 6.2192 | 0.078454
| 4:22 | 6.2194 | 0.077804
| 4:22 | 6.2197 | 0.077154
| 4:22 | 6.22 | 0.076504
| 4:22 | 6.2203 | 0.075853
| 4:22 | 6.2206 | 0.0752
| 4:22 | 6.2208 | 0.074548
| 4:22 | 6.2211 | 0.073894
| 4:22 | 6.2214 | 0.073237
| 4:22 | 6.2217 | 0.072577
| 4:22 | 6.2219 | 0.071913
| 4:22 | 6.2222 | 0.071244
| 4:22 | 6.2225 | 0.070572
| 4:22 | 6.2228 | 0.069895
| 4:22 | 6.2231 | 0.069214
| 4:22 | 6.2233 | 0.068529
| 4:22 | 6.2236 | 0.06784
| 4:22 | 6.2239 | 0.067146
| 4:22 | 6.2242 | 0.06644
| 4:22 | 6.2244 | 0.065732
| 4:22 | 6.2247 | 0.06502
| 4:22 | 6.225 | 0.0643
| 4:22 | 6.2253 | 0.063575
| 4:22 | 6.2256 | 0.062846
| 4:22 | 6.2258 | 0.062114
| 4:22 | 6.2261 | 0.061377
| 4:22 | 6.2264 | 0.060639
| 4:22 | 6.2267 | 0.059896
| 4:22 | 6.2269 | 0.059148
| 4:22 | 6.2272 | 0.058391
| 4:22 | 6.2275 | 0.05763
| 4:22 | 6.2278 | 0.056862
| 4:22 | 6.2281 | 0.05609
| 4:22 | 6.2283 | 0.055312
| 4:23 | 6.2286 | 0.054532
| 4:23 | 6.2289 | 0.053751
| 4:23 | 6.2292 | 0.052962
| 4:23 | 6.2294 | 0.052171
| 4:23 | 6.2297 | 0.05138
| 4:23 | 6.23 | 0.050588
| 4:23 | 6.2303 | 0.049797
| 4:23 | 6.2306 | 0.049006
| 4:23 | 6.2308 | 0.048214
| 4:23 | 6.2311 | 0.047423
| 4:23 | 6.2314 | 0.046631
| 4:23 | 6.2317 | 0.045839
| 4:23 | 6.2319 | 0.045048
| 4:23 | 6.2322 | 0.044256
| 4:23 | 6.2325 | 0.043465
| 4:23 | 6.2328 | 0.042675
| 4:23 | 6.2331 | 0.041886
| 4:23 | 6.2333 | 0.041101
| 4:23 | 6.2336 | 0.04032
| 4:23 | 6.2339 | 0.03955
| 4:23 | 6.2342 | 0.038783
| 4:23 | 6.2344 | 0.038016
| 4:23 | 6.2347 | 0.037248
| 4:23 | 6.235 | 0.036481
| 4:23 | 6.2353 | 0.035718
| 4:23 | 6.2356 | 0.034956
| 4:23 | 6.2358 | 0.034201
| 4:23 | 6.2361 | 0.033452
| 4:23 | 6.2364 | 0.032704
| 4:23 | 6.2367 | 0.031956
| 4:23 | 6.2369 | 0.031212
| 4:23 | 6.2372 | 0.030477
| 4:23 | 6.2375 | 0.029747
| 4:23 | 6.2378 | 0.029026
| 4:23 | 6.2381 | 0.028307
| 4:23 | 6.2383 | 0.027592
| 4:23 | 6.2386 | 0.02688
| 4:23 | 6.2389 | 0.026171
| 4:23 | 6.2392 | 0.025467
| 4:23 | 6.2394 | 0.024765
| 4:23 | 6.2397 | 0.024068
| 4:23 | 6.24 | 0.023373
| 4:23 | 6.2403 | 0.022682
| 4:23 | 6.2406 | 0.021992
| 4:23 | 6.2408 | 0.021304
| 4:23 | 6.2411 | 0.020623
| 4:23 | 6.2414 | 0.01995
| 4:23 | 6.2417 | 0.019286
| 4:23 | 6.2419 | 0.018637
| 4:23 | 6.2422 | 0.017993
| 4:23 | 6.2425 | 0.017351
| 4:23 | 6.2428 | 0.016713
| 4:23 | 6.2431 | 0.016079
| 4:23 | 6.2433 | 0.015452
| 4:23 | 6.2436 | 0.014832
| 4:23 | 6.2439 | 0.014218
| 4:23 | 6.2442 | 0.013621
| 4:23 | 6.2444 | 0.013032
| 4:23 | 6.2447 | 0.012447
| 4:24 | 6.245 | 0.011881
| 4:24 | 6.2453 | 0.011329
| 4:24 | 6.2456 | 0.010788
| 4:24 | 6.2458 | 0.010258
| 4:24 | 6.2461 | 0.0097437
| 4:24 | 6.2464 | 0.0092343
| 4:24 | 6.2467 | 0.0087384
| 4:24 | 6.2469 | 0.0082515
| 4:24 | 6.2472 | 0.0077734
| 4:24 | 6.2475 | 0.0073041
| 4:24 | 6.2478 | 0.0068437
| 4:24 | 6.2481 | 0.0063922
| 4:24 | 6.2483 | 0.0059495
| 4:24 | 6.2486 | 0.0055156
| 4:24 | 6.2489 | 0.0050906
| 4:24 | 6.2492 | 0.0046805
| 4:24 | 6.2494 | 0.0042872
| 4:24 | 6.2497 | 0.0039
| 4:24 | 6.25 | 0.0035258
| 4:24 | 6.2503 | 0.0031562
| 4:24 | 6.2506 | 0.0027905
| 4:24 | 6.2508 | 0.0024291
| 4:24 | 6.2511 | 0.0020679
| 4:24 | 6.2514 | 0.0017106
| 4:24 | 6.2517 | 0.0013577
| 4:24 | 6.2519 | 0.0010048
| 4:24 | 6.2522 | 0.00065182
| 4:24 | 6.2525 | 0.00029757
| 4:24 | 6.2528 | -5.5754e-05
| 4:24 | 6.2531 | -0.00040444
| 4:24 | 6.2533 | -0.0007486
| 4:24 | 6.2536 | -0.0010974
| 4:24 | 6.2539 | -0.0014508
| 4:24 | 6.2542 | -0.001815
| 4:24 | 6.2544 | -0.0021864
| 4:24 | 6.2547 | -0.0025622
| 4:24 | 6.255 | -0.0029437
| 4:24 | 6.2553 | -0.0033285
| 4:24 | 6.2556 | -0.0037165
| 4:24 | 6.2558 | -0.0041079
| 4:24 | 6.2561 | -0.0045026
| 4:24 | 6.2564 | -0.0049007
| 4:24 | 6.2567 | -0.005302
| 4:24 | 6.2569 | -0.0057049
| 4:24 | 6.2572 | -0.0061055
| 4:24 | 6.2575 | -0.0065086
| 4:24 | 6.2578 | -0.0069236
| 4:24 | 6.2581 | -0.0073443
| 4:24 | 6.2583 | -0.0077673
| 4:24 | 6.2586 | -0.0081937
| 4:24 | 6.2589 | -0.008624
| 4:24 | 6.2592 | -0.0090583
| 4:24 | 6.2594 | -0.0094887
| 4:24 | 6.2597 | -0.0099207
| 4:24 | 6.26 | -0.010353
| 4:24 | 6.2603 | -0.010785
| 4:24 | 6.2606 | -0.011215
| 4:24 | 6.2608 | -0.011638
| 4:24 | 6.2611 | -0.012054
| 4:24 | 6.2614 | -0.012465
| 4:24 | 6.2617 | -0.01287
| 4:25 | 6.2619 | -0.013272
| 4:25 | 6.2622 | -0.01367
| 4:25 | 6.2625 | -0.014058
| 4:25 | 6.2628 | -0.01444
| 4:25 | 6.2631 | -0.014815
| 4:25 | 6.2633 | -0.015182
| 4:25 | 6.2636 | -0.015542
| 4:25 | 6.2639 | -0.015893
| 4:25 | 6.2642 | -0.016236
| 4:25 | 6.2644 | -0.01657
| 4:25 | 6.2647 | -0.016896
| 4:25 | 6.265 | -0.017214
| 4:25 | 6.2653 | -0.017523
| 4:25 | 6.2656 | -0.017824
| 4:25 | 6.2658 | -0.018117
| 4:25 | 6.2661 | -0.018398
| 4:25 | 6.2664 | -0.018673
| 4:25 | 6.2667 | -0.018944
| 4:25 | 6.2669 | -0.019217
| 4:25 | 6.2672 | -0.019473
| 4:25 | 6.2675 | -0.019723
| 4:25 | 6.2678 | -0.019962
| 4:25 | 6.2681 | -0.020197
| 4:25 | 6.2683 | -0.020426
| 4:25 | 6.2686 | -0.020636
| 4:25 | 6.2689 | -0.020833
| 4:25 | 6.2692 | -0.021017
| 4:25 | 6.2694 | -0.021196
| 4:25 | 6.2697 | -0.021372
| 4:25 | 6.27 | -0.021541
| 4:25 | 6.2703 | -0.021706
| 4:25 | 6.2706 | -0.021861
| 4:25 | 6.2708 | -0.022009
| 4:25 | 6.2711 | -0.022155
| 4:25 | 6.2714 | -0.022295
| 4:25 | 6.2717 | -0.022421
| 4:25 | 6.2719 | -0.022545
| 4:25 | 6.2722 | -0.022663
| 4:25 | 6.2725 | -0.022776
| 4:25 | 6.2728 | -0.022883
| 4:25 | 6.2731 | -0.022984
| 4:25 | 6.2733 | -0.02308
| 4:25 | 6.2736 | -0.02317
| 4:25 | 6.2739 | -0.023255
| 4:25 | 6.2742 | -0.023337
| 4:25 | 6.2744 | -0.023421
| 4:25 | 6.2747 | -0.023503
| 4:25 | 6.275 | -0.023582
| 4:25 | 6.2753 | -0.02366
| 4:25 | 6.2756 | -0.023741
| 4:25 | 6.2758 | -0.023829
| 4:25 | 6.2761 | -0.023916
| 4:25 | 6.2764 | -0.024005
| 4:25 | 6.2767 | -0.024091
| 4:25 | 6.2769 | -0.02418
| 4:25 | 6.2772 | -0.024275
| 4:25 | 6.2775 | -0.024381
| 4:25 | 6.2778 | -0.024499
| 4:25 | 6.2781 | -0.024619
| 4:26 | 6.2783 | -0.024747
| 4:26 | 6.2786 | -0.024885
| 4:26 | 6.2789 | -0.02503
| 4:26 | 6.2792 | -0.025177
| 4:26 | 6.2794 | -0.025327
| 4:26 | 6.2797 | -0.025485
| 4:26 | 6.28 | -0.025649
| 4:26 | 6.2803 | -0.025815
| 4:26 | 6.2806 | -0.025984
| 4:26 | 6.2808 | -0.026156
| 4:26 | 6.2811 | -0.02633
| 4:26 | 6.2814 | -0.026507
| 4:26 | 6.2817 | -0.026686
| 4:26 | 6.2819 | -0.026867
| 4:26 | 6.2822 | -0.027051
| 4:26 | 6.2825 | -0.027231
| 4:26 | 6.2828 | -0.027411
| 4:26 | 6.2831 | -0.027584
| 4:26 | 6.2833 | -0.027756
| 4:26 | 6.2836 | -0.027929
| 4:26 | 6.2839 | -0.028092
| 4:26 | 6.2842 | -0.028245
| 4:26 | 6.2844 | -0.028388
| 4:26 | 6.2847 | -0.028523
| 4:26 | 6.285 | -0.028655
| 4:26 | 6.2853 | -0.028788
| 4:26 | 6.2856 | -0.028921
| 4:26 | 6.2858 | -0.029049
| 4:26 | 6.2861 | -0.029174
| 4:26 | 6.2864 | -0.029299
| 4:26 | 6.2867 | -0.029419
| 4:26 | 6.2869 | -0.029534
| 4:26 | 6.2872 | -0.029646
| 4:26 | 6.2875 | -0.02976
| 4:26 | 6.2878 | -0.029866
| 4:26 | 6.2881 | -0.029972
| 4:26 | 6.2883 | -0.030078
| 4:26 | 6.2886 | -0.030186
| 4:26 | 6.2889 | -0.030294
| 4:26 | 6.2892 | -0.030404
| 4:26 | 6.2894 | -0.030516
| 4:26 | 6.2897 | -0.030628
| 4:26 | 6.29 | -0.030742
| 4:26 | 6.2903 | -0.030855
| 4:26 | 6.2906 | -0.030966
| 4:26 | 6.2908 | -0.031079
| 4:26 | 6.2911 | -0.031196
| 4:26 | 6.2914 | -0.031317
| 4:26 | 6.2917 | -0.031436
| 4:26 | 6.2919 | -0.031556
| 4:26 | 6.2922 | -0.031677
| 4:26 | 6.2925 | -0.031796
| 4:26 | 6.2928 | -0.031919
| 4:26 | 6.2931 | -0.032052
| 4:26 | 6.2933 | -0.032192
| 4:26 | 6.2936 | -0.032339
| 4:26 | 6.2939 | -0.032491
| 4:26 | 6.2942 | -0.032652
| 4:26 | 6.2944 | -0.032822
| 4:26 | 6.2947 | -0.032998
| 4:26 | 6.295 | -0.033181
| 4:27 | 6.2953 | -0.033373
| 4:27 | 6.2956 | -0.033566
| 4:27 | 6.2958 | -0.033757
| 4:27 | 6.2961 | -0.03395
| 4:27 | 6.2964 | -0.034144
| 4:27 | 6.2967 | -0.034343
| 4:27 | 6.2969 | -0.034548
| 4:27 | 6.2972 | -0.034758
| 4:27 | 6.2975 | -0.034973
| 4:27 | 6.2978 | -0.035194
| 4:27 | 6.2981 | -0.035421
| 4:27 | 6.2983 | -0.035652
| 4:27 | 6.2986 | -0.03589
| 4:27 | 6.2989 | -0.036131
| 4:27 | 6.2992 | -0.03638
| 4:27 | 6.2994 | -0.036627
| 4:27 | 6.2997 | -0.03687
| 4:27 | 6.3 | -0.03711
| 4:27 | 6.3003 | -0.037344
| 4:27 | 6.3006 | -0.037578
| 4:27 | 6.3008 | -0.037819
| 4:27 | 6.3011 | -0.038062
| 4:27 | 6.3014 | -0.038304
| 4:27 | 6.3017 | -0.038552
| 4:27 | 6.3019 | -0.038798
| 4:27 | 6.3022 | -0.039033
| 4:27 | 6.3025 | -0.039268
| 4:27 | 6.3028 | -0.039502
| 4:27 | 6.3031 | -0.039734
| 4:27 | 6.3033 | -0.039958
| 4:27 | 6.3036 | -0.040174
| 4:27 | 6.3039 | -0.040379
| 4:27 | 6.3042 | -0.040582
| 4:27 | 6.3044 | -0.040785
| 4:27 | 6.3047 | -0.040997
| 4:27 | 6.305 | -0.041213
| 4:27 | 6.3053 | -0.041434
| 4:27 | 6.3056 | -0.041659
| 4:27 | 6.3058 | -0.041889
| 4:27 | 6.3061 | -0.042124
| 4:27 | 6.3064 | -0.042362
| 4:27 | 6.3067 | -0.042606
| 4:27 | 6.3069 | -0.042856
| 4:27 | 6.3072 | -0.043118
| 4:27 | 6.3075 | -0.043381
| 4:27 | 6.3078 | -0.043639
| 4:27 | 6.3081 | -0.043902
| 4:27 | 6.3083 | -0.044175
| 4:27 | 6.3086 | -0.044459
| 4:27 | 6.3089 | -0.044754
| 4:27 | 6.3092 | -0.045052
| 4:27 | 6.3094 | -0.045359
| 4:27 | 6.3097 | -0.045666
| 4:27 | 6.31 | -0.045973
| 4:27 | 6.3103 | -0.046277
| 4:27 | 6.3106 | -0.046582
| 4:27 | 6.3108 | -0.046887
| 4:27 | 6.3111 | -0.047183
| 4:27 | 6.3114 | -0.047469
| 4:28 | 6.3117 | -0.047742
| 4:28 | 6.3119 | -0.048014
| 4:28 | 6.3122 | -0.048279
| 4:28 | 6.3125 | -0.048541
| 4:28 | 6.3128 | -0.048794
| 4:28 | 6.3131 | -0.049038
| 4:28 | 6.3133 | -0.049262
| 4:28 | 6.3136 | -0.049463
| 4:28 | 6.3139 | -0.049643
| 4:28 | 6.3142 | -0.049801
| 4:28 | 6.3144 | -0.049937
| 4:28 | 6.3147 | -0.050051
| 4:28 | 6.315 | -0.050143
| 4:28 | 6.3153 | -0.050213
| 4:28 | 6.3156 | -0.050266
| 4:28 | 6.3158 | -0.050284
| 4:28 | 6.3161 | -0.050268
| 4:28 | 6.3164 | -0.050236
| 4:28 | 6.3167 | -0.05018
| 4:28 | 6.3169 | -0.050075
| 4:28 | 6.3172 | -0.049939
| 4:28 | 6.3175 | -0.049775
| 4:28 | 6.3178 | -0.049574
| 4:28 | 6.3181 | -0.049342
| 4:28 | 6.3183 | -0.049085
| 4:28 | 6.3186 | -0.048802
| 4:28 | 6.3189 | -0.048493
| 4:28 | 6.3192 | -0.048161
| 4:28 | 6.3194 | -0.047796
| 4:28 | 6.3197 | -0.047418
| 4:28 | 6.32 | -0.047026
| 4:28 | 6.3203 | -0.04661
| 4:28 | 6.3206 | -0.046181
| 4:28 | 6.3208 | -0.04574
| 4:28 | 6.3211 | -0.045287
| 4:28 | 6.3214 | -0.044828
| 4:28 | 6.3217 | -0.044357
| 4:28 | 6.3219 | -0.04388
| 4:28 | 6.3222 | -0.043396
| 4:28 | 6.3225 | -0.042905
| 4:28 | 6.3228 | -0.042408
| 4:28 | 6.3231 | -0.041904
| 4:28 | 6.3233 | -0.041394
| 4:28 | 6.3236 | -0.04088
| 4:28 | 6.3239 | -0.040366
| 4:28 | 6.3242 | -0.039855
| 4:28 | 6.3244 | -0.039346
| 4:28 | 6.3247 | -0.038837
| 4:28 | 6.325 | -0.038328
| 4:28 | 6.3253 | -0.037823
| 4:28 | 6.3256 | -0.037323
| 4:28 | 6.3258 | -0.036827
| 4:28 | 6.3261 | -0.036336
| 4:28 | 6.3264 | -0.035853
| 4:28 | 6.3267 | -0.035374
| 4:28 | 6.3269 | -0.0349
| 4:28 | 6.3272 | -0.034434
| 4:28 | 6.3275 | -0.033976
| 4:28 | 6.3278 | -0.033525
| 4:28 | 6.3281 | -0.033089
| 4:28 | 6.3283 | -0.032661
| 4:29 | 6.3286 | -0.032238
| 4:29 | 6.3289 | -0.031829
| 4:29 | 6.3292 | -0.03143
| 4:29 | 6.3294 | -0.031036
| 4:29 | 6.3297 | -0.030656
| 4:29 | 6.33 | -0.030285
| 4:29 | 6.3303 | -0.029924
| 4:29 | 6.3306 | -0.029573
| 4:29 | 6.3308 | -0.029231
| 4:29 | 6.3311 | -0.028898
| 4:29 | 6.3314 | -0.028576
| 4:29 | 6.3317 | -0.028263
| 4:29 | 6.3319 | -0.027959
| 4:29 | 6.3322 | -0.027665
| 4:29 | 6.3325 | -0.027375
| 4:29 | 6.3328 | -0.027094
| 4:29 | 6.3331 | -0.026819
| 4:29 | 6.3333 | -0.026549
| 4:29 | 6.3336 | -0.02628
| 4:29 | 6.3339 | -0.026018
| 4:29 | 6.3342 | -0.025763
| 4:29 | 6.3344 | -0.025508
| 4:29 | 6.3347 | -0.025252
| 4:29 | 6.335 | -0.024996
| 4:29 | 6.3353 | -0.024742
| 4:29 | 6.3356 | -0.024491
| 4:29 | 6.3358 | -0.024244
| 4:29 | 6.3361 | -0.023997
| 4:29 | 6.3364 | -0.023749
| 4:29 | 6.3367 | -0.023503
| 4:29 | 6.3369 | -0.023258
| 4:29 | 6.3372 | -0.023009
| 4:29 | 6.3375 | -0.022756
| 4:29 | 6.3378 | -0.022505
| 4:29 | 6.3381 | -0.022252
| 4:29 | 6.3383 | -0.021997
| 4:29 | 6.3386 | -0.02174
| 4:29 | 6.3389 | -0.021481
| 4:29 | 6.3392 | -0.021219
| 4:29 | 6.3394 | -0.020956
| 4:29 | 6.3397 | -0.02069
| 4:29 | 6.34 | -0.020422
| 4:29 | 6.3403 | -0.020154
| 4:29 | 6.3406 | -0.019887
| 4:29 | 6.3408 | -0.019616
| 4:29 | 6.3411 | -0.019341
| 4:29 | 6.3414 | -0.019064
| 4:29 | 6.3417 | -0.018789
| 4:29 | 6.3419 | -0.018514
| 4:29 | 6.3422 | -0.018232
| 4:29 | 6.3425 | -0.017944
| 4:29 | 6.3428 | -0.017659
| 4:29 | 6.3431 | -0.017372
| 4:29 | 6.3433 | -0.017086
| 4:29 | 6.3436 | -0.0168
| 4:29 | 6.3439 | -0.016514
| 4:29 | 6.3442 | -0.016224
| 4:29 | 6.3444 | -0.015931
| 4:29 | 6.3447 | -0.015635
| 4:30 | 6.345 | -0.015332
| 4:30 | 6.3453 | -0.015024
| 4:30 | 6.3456 | -0.014717
| 4:30 | 6.3458 | -0.014401
| 4:30 | 6.3461 | -0.014079
| 4:30 | 6.3464 | -0.013748
| 4:30 | 6.3467 | -0.013413
| 4:30 | 6.3469 | -0.013074
| 4:30 | 6.3472 | -0.012732
| 4:30 | 6.3475 | -0.012387
| 4:30 | 6.3478 | -0.012037
| 4:30 | 6.3481 | -0.011684
| 4:30 | 6.3483 | -0.011327
| 4:30 | 6.3486 | -0.010967
| 4:30 | 6.3489 | -0.010602
| 4:30 | 6.3492 | -0.010233
| 4:30 | 6.3494 | -0.0098649
| 4:30 | 6.3497 | -0.0094939
| 4:30 | 6.35 | -0.0091162
| 4:30 | 6.3503 | -0.0087356
| 4:30 | 6.3506 | -0.0083535
| 4:30 | 6.3508 | -0.0079632
| 4:30 | 6.3511 | -0.0075773
| 4:30 | 6.3514 | -0.0071908
| 4:30 | 6.3517 | -0.0067995
| 4:30 | 6.3519 | -0.0064056
| 4:30 | 6.3522 | -0.0060094
| 4:30 | 6.3525 | -0.005614
| 4:30 | 6.3528 | -0.0052143
| 4:30 | 6.3531 | -0.0048126
| 4:30 | 6.3533 | -0.0044106
| 4:30 | 6.3536 | -0.0040065
| 4:30 | 6.3539 | -0.0036
| 4:30 | 6.3542 | -0.0031897
| 4:30 | 6.3544 | -0.002781
| 4:30 | 6.3547 | -0.002371
| 4:30 | 6.355 | -0.0019572
| 4:30 | 6.3553 | -0.0015395
| 4:30 | 6.3556 | -0.001118
| 4:30 | 6.3558 | -0.00069273
| 4:30 | 6.3561 | -0.00026359
| 4:30 | 6.3564 | 0.00016939
| 4:30 | 6.3567 | 0.00060621
| 4:30 | 6.3569 | 0.0010414
| 4:30 | 6.3572 | 0.0014822
| 4:30 | 6.3575 | 0.0019218
| 4:30 | 6.3578 | 0.0023698
| 4:30 | 6.3581 | 0.0028244
| 4:30 | 6.3583 | 0.0032803
| 4:30 | 6.3586 | 0.0037406
| 4:30 | 6.3589 | 0.004199
| 4:30 | 6.3592 | 0.0046609
| 4:30 | 6.3594 | 0.0051306
| 4:30 | 6.3597 | 0.0056066
| 4:30 | 6.36 | 0.0060834
| 4:30 | 6.3603 | 0.0065663
| 4:30 | 6.3606 | 0.0070502
| 4:30 | 6.3608 | 0.0075399
| 4:30 | 6.3611 | 0.0080304
| 4:30 | 6.3614 | 0.0085269
| 4:30 | 6.3617 | 0.0090246
| 4:31 | 6.3619 | 0.0095237
| 4:31 | 6.3622 | 0.010029
| 4:31 | 6.3625 | 0.010537
| 4:31 | 6.3628 | 0.011043
| 4:31 | 6.3631 | 0.011549
| 4:31 | 6.3633 | 0.012056
| 4:31 | 6.3636 | 0.012566
| 4:31 | 6.3639 | 0.013078
| 4:31 | 6.3642 | 0.013592
| 4:31 | 6.3644 | 0.014109
| 4:31 | 6.3647 | 0.014629
| 4:31 | 6.365 | 0.015151
| 4:31 | 6.3653 | 0.015675
| 4:31 | 6.3656 | 0.016202
| 4:31 | 6.3658 | 0.016732
| 4:31 | 6.3661 | 0.017266
| 4:31 | 6.3664 | 0.017801
| 4:31 | 6.3667 | 0.018336
| 4:31 | 6.3669 | 0.018868
| 4:31 | 6.3672 | 0.019402
| 4:31 | 6.3675 | 0.019936
| 4:31 | 6.3678 | 0.020476
| 4:31 | 6.3681 | 0.021017
| 4:31 | 6.3683 | 0.021561
| 4:31 | 6.3686 | 0.022107
| 4:31 | 6.3689 | 0.022653
| 4:31 | 6.3692 | 0.023199
| 4:31 | 6.3694 | 0.023747
| 4:31 | 6.3697 | 0.024298
| 4:31 | 6.37 | 0.02485
| 4:31 | 6.3703 | 0.025401
| 4:31 | 6.3706 | 0.025945
| 4:31 | 6.3708 | 0.026486
| 4:31 | 6.3711 | 0.027029
| 4:31 | 6.3714 | 0.027577
| 4:31 | 6.3717 | 0.028123
| 4:31 | 6.3719 | 0.028667
| 4:31 | 6.3722 | 0.029209
| 4:31 | 6.3725 | 0.029749
| 4:31 | 6.3728 | 0.030287
| 4:31 | 6.3731 | 0.030823
| 4:31 | 6.3733 | 0.031357
| 4:31 | 6.3736 | 0.031888
| 4:31 | 6.3739 | 0.032414
| 4:31 | 6.3742 | 0.03293
| 4:31 | 6.3744 | 0.033437
| 4:31 | 6.3747 | 0.033938
| 4:31 | 6.375 | 0.034432
| 4:31 | 6.3753 | 0.034923
| 4:31 | 6.3756 | 0.035404
| 4:31 | 6.3758 | 0.035882
| 4:31 | 6.3761 | 0.036352
| 4:31 | 6.3764 | 0.03682
| 4:31 | 6.3767 | 0.037276
| 4:31 | 6.3769 | 0.037722
| 4:31 | 6.3772 | 0.038157
| 4:31 | 6.3775 | 0.038588
| 4:31 | 6.3778 | 0.039013
| 4:31 | 6.3781 | 0.03943
| 4:32 | 6.3783 | 0.039836
| 4:32 | 6.3786 | 0.040231
| 4:32 | 6.3789 | 0.040622
| 4:32 | 6.3792 | 0.041009
| 4:32 | 6.3794 | 0.041395
| 4:32 | 6.3797 | 0.041777
| 4:32 | 6.38 | 0.042154
| 4:32 | 6.3803 | 0.042527
| 4:32 | 6.3806 | 0.042896
| 4:32 | 6.3808 | 0.043262
| 4:32 | 6.3811 | 0.043624
| 4:32 | 6.3814 | 0.043983
| 4:32 | 6.3817 | 0.044338
| 4:32 | 6.3819 | 0.044689
| 4:32 | 6.3822 | 0.045037
| 4:32 | 6.3825 | 0.045384
| 4:32 | 6.3828 | 0.045736
| 4:32 | 6.3831 | 0.04609
| 4:32 | 6.3833 | 0.046447
| 4:32 | 6.3836 | 0.046806
| 4:32 | 6.3839 | 0.047169
| 4:32 | 6.3842 | 0.047544
| 4:32 | 6.3844 | 0.047922
| 4:32 | 6.3847 | 0.048306
| 4:32 | 6.385 | 0.048692
| 4:32 | 6.3853 | 0.049082
| 4:32 | 6.3856 | 0.049476
| 4:32 | 6.3858 | 0.049871
| 4:32 | 6.3861 | 0.05027
| 4:32 | 6.3864 | 0.050672
| 4:32 | 6.3867 | 0.051077
| 4:32 | 6.3869 | 0.051488
| 4:32 | 6.3872 | 0.051908
| 4:32 | 6.3875 | 0.05233
| 4:32 | 6.3878 | 0.052759
| 4:32 | 6.3881 | 0.05319
| 4:32 | 6.3883 | 0.053621
| 4:32 | 6.3886 | 0.054051
| 4:32 | 6.3889 | 0.05448
| 4:32 | 6.3892 | 0.054909
| 4:32 | 6.3894 | 0.055336
| 4:32 | 6.3897 | 0.055763
| 4:32 | 6.39 | 0.056189
| 4:32 | 6.3903 | 0.056615
| 4:32 | 6.3906 | 0.057043
| 4:32 | 6.3908 | 0.057476
| 4:32 | 6.3911 | 0.057909
| 4:32 | 6.3914 | 0.058341
| 4:32 | 6.3917 | 0.058774
| 4:32 | 6.3919 | 0.059206
| 4:32 | 6.3922 | 0.059635
| 4:32 | 6.3925 | 0.060063
| 4:32 | 6.3928 | 0.06049
| 4:32 | 6.3931 | 0.060916
| 4:32 | 6.3933 | 0.06134
| 4:32 | 6.3936 | 0.06176
| 4:32 | 6.3939 | 0.062174
| 4:32 | 6.3942 | 0.062584
| 4:32 | 6.3944 | 0.062994
| 4:32 | 6.3947 | 0.063407
| 4:32 | 6.395 | 0.063817
| 4:33 | 6.3953 | 0.064221
| 4:33 | 6.3956 | 0.064622
| 4:33 | 6.3958 | 0.065023
| 4:33 | 6.3961 | 0.065416
| 4:33 | 6.3964 | 0.065807
| 4:33 | 6.3967 | 0.066195
| 4:33 | 6.3969 | 0.066578
| 4:33 | 6.3972 | 0.066957
| 4:33 | 6.3975 | 0.067332
| 4:33 | 6.3978 | 0.067702
| 4:33 | 6.3981 | 0.068068
| 4:33 | 6.3983 | 0.068429
| 4:33 | 6.3986 | 0.068786
| 4:33 | 6.3989 | 0.069138
| 4:33 | 6.3992 | 0.069486
| 4:33 | 6.3994 | 0.069828
| 4:33 | 6.3997 | 0.070166
| 4:33 | 6.4 | 0.0705
| 4:33 | 6.4003 | 0.07083
| 4:33 | 6.4006 | 0.071156
| 4:33 | 6.4008 | 0.071477
| 4:33 | 6.4011 | 0.071793
| 4:33 | 6.4014 | 0.072095
| 4:33 | 6.4017 | 0.072386
| 4:33 | 6.4019 | 0.072673
| 4:33 | 6.4022 | 0.072956
| 4:33 | 6.4025 | 0.073237
| 4:33 | 6.4028 | 0.073517
| 4:33 | 6.4031 | 0.073793
| 4:33 | 6.4033 | 0.074067
| 4:33 | 6.4036 | 0.074338
| 4:33 | 6.4039 | 0.074603
| 4:33 | 6.4042 | 0.074861
| 4:33 | 6.4044 | 0.075119
| 4:33 | 6.4047 | 0.075373
| 4:33 | 6.405 | 0.075621
| 4:33 | 6.4053 | 0.075863
| 4:33 | 6.4056 | 0.0761
| 4:33 | 6.4058 | 0.076331
| 4:33 | 6.4061 | 0.076557
| 4:33 | 6.4064 | 0.076777
| 4:33 | 6.4067 | 0.076991
| 4:33 | 6.4069 | 0.077201
| 4:33 | 6.4072 | 0.077408
| 4:33 | 6.4075 | 0.077607
| 4:33 | 6.4078 | 0.077803
| 4:33 | 6.4081 | 0.077991
| 4:33 | 6.4083 | 0.078178
| 4:33 | 6.4086 | 0.078359
| 4:33 | 6.4089 | 0.078531
| 4:33 | 6.4092 | 0.078701
| 4:33 | 6.4094 | 0.07886
| 4:33 | 6.4097 | 0.079022
| 4:33 | 6.41 | 0.079184
| 4:33 | 6.4103 | 0.079345
| 4:33 | 6.4106 | 0.079503
| 4:33 | 6.4108 | 0.079658
| 4:33 | 6.4111 | 0.079812
| 4:33 | 6.4114 | 0.079967
| 4:34 | 6.4117 | 0.080118
| 4:34 | 6.4119 | 0.08027
| 4:34 | 6.4122 | 0.080419
| 4:34 | 6.4125 | 0.080566
| 4:34 | 6.4128 | 0.08071
| 4:34 | 6.4131 | 0.080853
| 4:34 | 6.4133 | 0.080995
| 4:34 | 6.4136 | 0.081135
| 4:34 | 6.4139 | 0.081275
| 4:34 | 6.4142 | 0.081413
| 4:34 | 6.4144 | 0.08155
| 4:34 | 6.4147 | 0.081685
| 4:34 | 6.415 | 0.08182
| 4:34 | 6.4153 | 0.081953
| 4:34 | 6.4156 | 0.082085
| 4:34 | 6.4158 | 0.082204
| 4:34 | 6.4161 | 0.082316
| 4:34 | 6.4164 | 0.082422
| 4:34 | 6.4167 | 0.08252
| 4:34 | 6.4169 | 0.082615
| 4:34 | 6.4172 | 0.082682
| 4:34 | 6.4175 | 0.082744
| 4:34 | 6.4178 | 0.0828
| 4:34 | 6.4181 | 0.08285
| 4:34 | 6.4183 | 0.0829
| 4:34 | 6.4186 | 0.082946
| 4:34 | 6.4189 | 0.082989
| 4:34 | 6.4192 | 0.083035
| 4:34 | 6.4194 | 0.083084
| 4:34 | 6.4197 | 0.083126
| 4:34 | 6.42 | 0.08317
| 4:34 | 6.4203 | 0.083226
| 4:34 | 6.4206 | 0.083287
| 4:34 | 6.4208 | 0.08335
| 4:34 | 6.4211 | 0.083414
| 4:34 | 6.4214 | 0.083489
| 4:34 | 6.4217 | 0.083578
| 4:34 | 6.4219 | 0.083683
| 4:34 | 6.4222 | 0.083803
| 4:34 | 6.4225 | 0.083937
| 4:34 | 6.4228 | 0.084086
| 4:34 | 6.4231 | 0.084251
| 4:34 | 6.4233 | 0.084429
| 4:34 | 6.4236 | 0.084631
| 4:34 | 6.4239 | 0.084854
| 4:34 | 6.4242 | 0.085125
| 4:34 | 6.4244 | 0.085415
| 4:34 | 6.4247 | 0.085726
| 4:34 | 6.425 | 0.086054
| 4:34 | 6.4253 | 0.086402
| 4:34 | 6.4256 | 0.086771
| 4:34 | 6.4258 | 0.087164
| 4:34 | 6.4261 | 0.087583
| 4:34 | 6.4264 | 0.088009
| 4:34 | 6.4267 | 0.088451
| 4:34 | 6.4269 | 0.08891
| 4:34 | 6.4272 | 0.089382
| 4:34 | 6.4275 | 0.089858
| 4:34 | 6.4278 | 0.090351
| 4:34 | 6.4281 | 0.090853
| 4:34 | 6.4283 | 0.091369
| 4:35 | 6.4286 | 0.091891
| 4:35 | 6.4289 | 0.092417
| 4:35 | 6.4292 | 0.092952
| 4:35 | 6.4294 | 0.093489
| 4:35 | 6.4297 | 0.094042
| 4:35 | 6.43 | 0.094598
| 4:35 | 6.4303 | 0.09516
| 4:35 | 6.4306 | 0.095725
| 4:35 | 6.4308 | 0.096294
| 4:35 | 6.4311 | 0.096868
| 4:35 | 6.4314 | 0.097446
| 4:35 | 6.4317 | 0.098028
| 4:35 | 6.4319 | 0.098614
| 4:35 | 6.4322 | 0.099202
| 4:35 | 6.4325 | 0.099789
| 4:35 | 6.4328 | 0.10037
| 4:35 | 6.4331 | 0.10095
| 4:35 | 6.4333 | 0.10153
| 4:35 | 6.4336 | 0.10212
| 4:35 | 6.4339 | 0.10271
| 4:35 | 6.4342 | 0.1033
| 4:35 | 6.4344 | 0.10389
| 4:35 | 6.4347 | 0.10448
| 4:35 | 6.435 | 0.10508
| 4:35 | 6.4353 | 0.10567
| 4:35 | 6.4356 | 0.10627
| 4:35 | 6.4358 | 0.10687
| 4:35 | 6.4361 | 0.10746
| 4:35 | 6.4364 | 0.10806
| 4:35 | 6.4367 | 0.10865
| 4:35 | 6.4369 | 0.10924
| 4:35 | 6.4372 | 0.10984
| 4:35 | 6.4375 | 0.11044
| 4:35 | 6.4378 | 0.11105
| 4:35 | 6.4381 | 0.11165
| 4:35 | 6.4383 | 0.11226
| 4:35 | 6.4386 | 0.11287
| 4:35 | 6.4389 | 0.11348
| 4:35 | 6.4392 | 0.11409
| 4:35 | 6.4394 | 0.1147
| 4:35 | 6.4397 | 0.11531
| 4:35 | 6.44 | 0.11593
| 4:35 | 6.4403 | 0.11655
| 4:35 | 6.4406 | 0.11716
| 4:35 | 6.4408 | 0.11777
| 4:35 | 6.4411 | 0.11839
| 4:35 | 6.4414 | 0.11901
| 4:35 | 6.4417 | 0.11963
| 4:35 | 6.4419 | 0.12026
| 4:35 | 6.4422 | 0.12088
| 4:35 | 6.4425 | 0.12152
| 4:35 | 6.4428 | 0.12214
| 4:35 | 6.4431 | 0.12277
| 4:35 | 6.4433 | 0.1234
| 4:35 | 6.4436 | 0.12404
| 4:35 | 6.4439 | 0.12467
| 4:35 | 6.4442 | 0.1253
| 4:35 | 6.4444 | 0.12593
| 4:35 | 6.4447 | 0.12655
| 4:36 | 6.445 | 0.12718
| 4:36 | 6.4453 | 0.12782
| 4:36 | 6.4456 | 0.12845
| 4:36 | 6.4458 | 0.12908
| 4:36 | 6.4461 | 0.12972
| 4:36 | 6.4464 | 0.13036
| 4:36 | 6.4467 | 0.131
| 4:36 | 6.4469 | 0.13164
| 4:36 | 6.4472 | 0.13228
| 4:36 | 6.4475 | 0.13291
| 4:36 | 6.4478 | 0.13355
| 4:36 | 6.4481 | 0.13418
| 4:36 | 6.4483 | 0.13481
| 4:36 | 6.4486 | 0.13544
| 4:36 | 6.4489 | 0.13606
| 4:36 | 6.4492 | 0.13669
| 4:36 | 6.4494 | 0.13732
| 4:36 | 6.4497 | 0.13795
| 4:36 | 6.45 | 0.13857
| 4:36 | 6.4503 | 0.1392
| 4:36 | 6.4506 | 0.13982
| 4:36 | 6.4508 | 0.14043
| 4:36 | 6.4511 | 0.14105
| 4:36 | 6.4514 | 0.14166
| 4:36 | 6.4517 | 0.14227
| 4:36 | 6.4519 | 0.14287
| 4:36 | 6.4522 | 0.14347
| 4:36 | 6.4525 | 0.14406
| 4:36 | 6.4528 | 0.14465
| 4:36 | 6.4531 | 0.14525
| 4:36 | 6.4533 | 0.14584
| 4:36 | 6.4536 | 0.14643
| 4:36 | 6.4539 | 0.14703
| 4:36 | 6.4542 | 0.14762
| 4:36 | 6.4544 | 0.14822
| 4:36 | 6.4547 | 0.14881
| 4:36 | 6.455 | 0.1494
| 4:36 | 6.4553 | 0.14999
| 4:36 | 6.4556 | 0.15058
| 4:36 | 6.4558 | 0.15116
| 4:36 | 6.4561 | 0.15175
| 4:36 | 6.4564 | 0.15234
| 4:36 | 6.4567 | 0.15292
| 4:36 | 6.4569 | 0.15351
| 4:36 | 6.4572 | 0.15409
| 4:36 | 6.4575 | 0.15468
| 4:36 | 6.4578 | 0.15527
| 4:36 | 6.4581 | 0.15586
| 4:36 | 6.4583 | 0.15645
| 4:36 | 6.4586 | 0.15704
| 4:36 | 6.4589 | 0.15764
| 4:36 | 6.4592 | 0.15824
| 4:36 | 6.4594 | 0.15884
| 4:36 | 6.4597 | 0.15944
| 4:36 | 6.46 | 0.16003
| 4:36 | 6.4603 | 0.16063
| 4:36 | 6.4606 | 0.16124
| 4:36 | 6.4608 | 0.16185
| 4:36 | 6.4611 | 0.16246
| 4:36 | 6.4614 | 0.16307
| 4:36 | 6.4617 | 0.16369
| 4:37 | 6.4619 | 0.16431
| 4:37 | 6.4622 | 0.16492
| 4:37 | 6.4625 | 0.16554
| 4:37 | 6.4628 | 0.16616
| 4:37 | 6.4631 | 0.16678
| 4:37 | 6.4633 | 0.1674
| 4:37 | 6.4636 | 0.16802
| 4:37 | 6.4639 | 0.16864
| 4:37 | 6.4642 | 0.16925
| 4:37 | 6.4644 | 0.16987
| 4:37 | 6.4647 | 0.17048
| 4:37 | 6.465 | 0.1711
| 4:37 | 6.4653 | 0.17171
| 4:37 | 6.4656 | 0.17232
| 4:37 | 6.4658 | 0.17293
| 4:37 | 6.4661 | 0.17353
| 4:37 | 6.4664 | 0.17414
| 4:37 | 6.4667 | 0.17475
| 4:37 | 6.4669 | 0.17537
| 4:37 | 6.4672 | 0.17598
| 4:37 | 6.4675 | 0.1766
| 4:37 | 6.4678 | 0.17721
| 4:37 | 6.4681 | 0.17782
| 4:37 | 6.4683 | 0.17844
| 4:37 | 6.4686 | 0.17907
| 4:37 | 6.4689 | 0.17969
| 4:37 | 6.4692 | 0.18032
| 4:37 | 6.4694 | 0.18095
| 4:37 | 6.4697 | 0.18159
| 4:37 | 6.47 | 0.18222
| 4:37 | 6.4703 | 0.18285
| 4:37 | 6.4706 | 0.18349
| 4:37 | 6.4708 | 0.18412
| 4:37 | 6.4711 | 0.18476
| 4:37 | 6.4714 | 0.1854
| 4:37 | 6.4717 | 0.18604
| 4:37 | 6.4719 | 0.18667
| 4:37 | 6.4722 | 0.18731
| 4:37 | 6.4725 | 0.18795
| 4:37 | 6.4728 | 0.18859
| 4:37 | 6.4731 | 0.18923
| 4:37 | 6.4733 | 0.18988
| 4:37 | 6.4736 | 0.19052
| 4:37 | 6.4739 | 0.19116
| 4:37 | 6.4742 | 0.1918
| 4:37 | 6.4744 | 0.19244
| 4:37 | 6.4747 | 0.19308
| 4:37 | 6.475 | 0.19371
| 4:37 | 6.4753 | 0.19435
| 4:37 | 6.4756 | 0.19498
| 4:37 | 6.4758 | 0.19561
| 4:37 | 6.4761 | 0.19624
| 4:37 | 6.4764 | 0.19687
| 4:37 | 6.4767 | 0.19751
| 4:37 | 6.4769 | 0.19815
| 4:37 | 6.4772 | 0.19878
| 4:37 | 6.4775 | 0.19942
| 4:37 | 6.4778 | 0.20006
| 4:37 | 6.4781 | 0.20069
| 4:38 | 6.4783 | 0.20133
| 4:38 | 6.4786 | 0.20196
| 4:38 | 6.4789 | 0.2026
| 4:38 | 6.4792 | 0.20322
| 4:38 | 6.4794 | 0.20385
| 4:38 | 6.4797 | 0.20447
| 4:38 | 6.48 | 0.20509
| 4:38 | 6.4803 | 0.2057
| 4:38 | 6.4806 | 0.20632
| 4:38 | 6.4808 | 0.20694
| 4:38 | 6.4811 | 0.20755
| 4:38 | 6.4814 | 0.20817
| 4:38 | 6.4817 | 0.20878
| 4:38 | 6.4819 | 0.2094
| 4:38 | 6.4822 | 0.21001
| 4:38 | 6.4825 | 0.21062
| 4:38 | 6.4828 | 0.21122
| 4:38 | 6.4831 | 0.21182
| 4:38 | 6.4833 | 0.21241
| 4:38 | 6.4836 | 0.21299
| 4:38 | 6.4839 | 0.21358
| 4:38 | 6.4842 | 0.21417
| 4:38 | 6.4844 | 0.21476
| 4:38 | 6.4847 | 0.21535
| 4:38 | 6.485 | 0.21593
| 4:38 | 6.4853 | 0.21652
| 4:38 | 6.4856 | 0.2171
| 4:38 | 6.4858 | 0.21768
| 4:38 | 6.4861 | 0.21826
| 4:38 | 6.4864 | 0.21884
| 4:38 | 6.4867 | 0.21943
| 4:38 | 6.4869 | 0.22
| 4:38 | 6.4872 | 0.22058
| 4:38 | 6.4875 | 0.22115
| 4:38 | 6.4878 | 0.22172
| 4:38 | 6.4881 | 0.2223
| 4:38 | 6.4883 | 0.22288
| 4:38 | 6.4886 | 0.22346
| 4:38 | 6.4889 | 0.22404
| 4:38 | 6.4892 | 0.22463
| 4:38 | 6.4894 | 0.22521
| 4:38 | 6.4897 | 0.22579
| 4:38 | 6.49 | 0.22638
| 4:38 | 6.4903 | 0.22696
| 4:38 | 6.4906 | 0.22755
| 4:38 | 6.4908 | 0.22813
| 4:38 | 6.4911 | 0.2287
| 4:38 | 6.4914 | 0.22926
| 4:38 | 6.4917 | 0.22983
| 4:38 | 6.4919 | 0.23038
| 4:38 | 6.4922 | 0.23094
| 4:38 | 6.4925 | 0.23149
| 4:38 | 6.4928 | 0.23203
| 4:38 | 6.4931 | 0.23257
| 4:38 | 6.4933 | 0.2331
| 4:38 | 6.4936 | 0.23362
| 4:38 | 6.4939 | 0.23414
| 4:38 | 6.4942 | 0.23464
| 4:38 | 6.4944 | 0.23513
| 4:38 | 6.4947 | 0.23561
| 4:38 | 6.495 | 0.23607
| 4:39 | 6.4953 | 0.23652
| 4:39 | 6.4956 | 0.23696
| 4:39 | 6.4958 | 0.2374
| 4:39 | 6.4961 | 0.23781
| 4:39 | 6.4964 | 0.23822
| 4:39 | 6.4967 | 0.23862
| 4:39 | 6.4969 | 0.239
| 4:39 | 6.4972 | 0.23937
| 4:39 | 6.4975 | 0.23974
| 4:39 | 6.4978 | 0.24009
| 4:39 | 6.4981 | 0.24043
| 4:39 | 6.4983 | 0.24077
| 4:39 | 6.4986 | 0.24109
| 4:39 | 6.4989 | 0.24141
| 4:39 | 6.4992 | 0.24171
| 4:39 | 6.4994 | 0.242
| 4:39 | 6.4997 | 0.2423
| 4:39 | 6.5 | 0.24258
| 4:39 | 6.5003 | 0.24286
| 4:39 | 6.5006 | 0.24313
| 4:39 | 6.5008 | 0.2434
| 4:39 | 6.5011 | 0.24366
| 4:39 | 6.5014 | 0.24392
| 4:39 | 6.5017 | 0.24418
| 4:39 | 6.5019 | 0.24444
| 4:39 | 6.5022 | 0.2447
| 4:39 | 6.5025 | 0.24495
| 4:39 | 6.5028 | 0.24521
| 4:39 | 6.5031 | 0.24546
| 4:39 | 6.5033 | 0.24572
| 4:39 | 6.5036 | 0.24598
| 4:39 | 6.5039 | 0.24625
| 4:39 | 6.5042 | 0.24653
| 4:39 | 6.5044 | 0.24681
| 4:39 | 6.5047 | 0.2471
| 4:39 | 6.505 | 0.2474
| 4:39 | 6.5053 | 0.2477
| 4:39 | 6.5056 | 0.24801
| 4:39 | 6.5058 | 0.24832
| 4:39 | 6.5061 | 0.24863
| 4:39 | 6.5064 | 0.24894
| 4:39 | 6.5067 | 0.24926
| 4:39 | 6.5069 | 0.24957
| 4:39 | 6.5072 | 0.2499
| 4:39 | 6.5075 | 0.25024
| 4:39 | 6.5078 | 0.25058
| 4:39 | 6.5081 | 0.25092
| 4:39 | 6.5083 | 0.25127
| 4:39 | 6.5086 | 0.25163
| 4:39 | 6.5089 | 0.25198
| 4:39 | 6.5092 | 0.25233
| 4:39 | 6.5094 | 0.25269
| 4:39 | 6.5097 | 0.25304
| 4:39 | 6.51 | 0.2534
| 4:39 | 6.5103 | 0.25375
| 4:39 | 6.5106 | 0.2541
| 4:39 | 6.5108 | 0.25444
| 4:39 | 6.5111 | 0.25478
| 4:39 | 6.5114 | 0.25513
| 4:40 | 6.5117 | 0.25546
| 4:40 | 6.5119 | 0.2558
| 4:40 | 6.5122 | 0.25613
| 4:40 | 6.5125 | 0.25645
| 4:40 | 6.5128 | 0.25676
| 4:40 | 6.5131 | 0.25706
| 4:40 | 6.5133 | 0.25736
| 4:40 | 6.5136 | 0.25764
| 4:40 | 6.5139 | 0.25792
| 4:40 | 6.5142 | 0.25819
| 4:40 | 6.5144 | 0.25845
| 4:40 | 6.5147 | 0.25871
| 4:40 | 6.515 | 0.25895
| 4:40 | 6.5153 | 0.25919
| 4:40 | 6.5156 | 0.25941
| 4:40 | 6.5158 | 0.25963
| 4:40 | 6.5161 | 0.25984
| 4:40 | 6.5164 | 0.26004
| 4:40 | 6.5167 | 0.26023
| 4:40 | 6.5169 | 0.26042
| 4:40 | 6.5172 | 0.2606
| 4:40 | 6.5175 | 0.26077
| 4:40 | 6.5178 | 0.26093
| 4:40 | 6.5181 | 0.26108
| 4:40 | 6.5183 | 0.26122
| 4:40 | 6.5186 | 0.26134
| 4:40 | 6.5189 | 0.26145
| 4:40 | 6.5192 | 0.26156
| 4:40 | 6.5194 | 0.26166
| 4:40 | 6.5197 | 0.26175
| 4:40 | 6.52 | 0.26183
| 4:40 | 6.5203 | 0.26191
| 4:40 | 6.5206 | 0.26198
| 4:40 | 6.5208 | 0.26204
| 4:40 | 6.5211 | 0.26209
| 4:40 | 6.5214 | 0.26215
| 4:40 | 6.5217 | 0.26218
| 4:40 | 6.5219 | 0.26222
| 4:40 | 6.5222 | 0.26224
| 4:40 | 6.5225 | 0.26226
| 4:40 | 6.5228 | 0.26227
| 4:40 | 6.5231 | 0.26228
| 4:40 | 6.5233 | 0.26228
| 4:40 | 6.5236 | 0.26227
| 4:40 | 6.5239 | 0.26226
| 4:40 | 6.5242 | 0.26225
| 4:40 | 6.5244 | 0.26224
| 4:40 | 6.5247 | 0.26222
| 4:40 | 6.525 | 0.2622
| 4:40 | 6.5253 | 0.26218
| 4:40 | 6.5256 | 0.26216
| 4:40 | 6.5258 | 0.26215
| 4:40 | 6.5261 | 0.26213
| 4:40 | 6.5264 | 0.26212
| 4:40 | 6.5267 | 0.26211
| 4:40 | 6.5269 | 0.2621
| 4:40 | 6.5272 | 0.26211
| 4:40 | 6.5275 | 0.26212
| 4:40 | 6.5278 | 0.26214
| 4:40 | 6.5281 | 0.26216
| 4:40 | 6.5283 | 0.26219
| 4:41 | 6.5286 | 0.26223
| 4:41 | 6.5289 | 0.26227
| 4:41 | 6.5292 | 0.26232
| 4:41 | 6.5294 | 0.26237
| 4:41 | 6.5297 | 0.26243
| 4:41 | 6.53 | 0.26248
| 4:41 | 6.5303 | 0.26254
| 4:41 | 6.5306 | 0.2626
| 4:41 | 6.5308 | 0.26267
| 4:41 | 6.5311 | 0.26274
| 4:41 | 6.5314 | 0.26281
| 4:41 | 6.5317 | 0.26288
| 4:41 | 6.5319 | 0.26296
| 4:41 | 6.5322 | 0.26304
| 4:41 | 6.5325 | 0.26312
| 4:41 | 6.5328 | 0.26319
| 4:41 | 6.5331 | 0.26327
| 4:41 | 6.5333 | 0.26334
| 4:41 | 6.5336 | 0.26341
| 4:41 | 6.5339 | 0.26346
| 4:41 | 6.5342 | 0.26351
| 4:41 | 6.5344 | 0.26355
| 4:41 | 6.5347 | 0.26359
| 4:41 | 6.535 | 0.26363
| 4:41 | 6.5353 | 0.26367
| 4:41 | 6.5356 | 0.26371
| 4:41 | 6.5358 | 0.26374
| 4:41 | 6.5361 | 0.26376
| 4:41 | 6.5364 | 0.26378
| 4:41 | 6.5367 | 0.2638
| 4:41 | 6.5369 | 0.26381
| 4:41 | 6.5372 | 0.26382
| 4:41 | 6.5375 | 0.26383
| 4:41 | 6.5378 | 0.26383
| 4:41 | 6.5381 | 0.26382
| 4:41 | 6.5383 | 0.26382
| 4:41 | 6.5386 | 0.26382
| 4:41 | 6.5389 | 0.26382
| 4:41 | 6.5392 | 0.26382
| 4:41 | 6.5394 | 0.26382
| 4:41 | 6.5397 | 0.26383
| 4:41 | 6.54 | 0.26383
| 4:41 | 6.5403 | 0.26383
| 4:41 | 6.5406 | 0.26384
| 4:41 | 6.5408 | 0.26386
| 4:41 | 6.5411 | 0.26388
| 4:41 | 6.5414 | 0.26389
| 4:41 | 6.5417 | 0.2639
| 4:41 | 6.5419 | 0.26391
| 4:41 | 6.5422 | 0.26393
| 4:41 | 6.5425 | 0.26395
| 4:41 | 6.5428 | 0.26398
| 4:41 | 6.5431 | 0.26402
| 4:41 | 6.5433 | 0.26406
| 4:41 | 6.5436 | 0.26411
| 4:41 | 6.5439 | 0.26417
| 4:41 | 6.5442 | 0.26423
| 4:41 | 6.5444 | 0.2643
| 4:41 | 6.5447 | 0.26438
| 4:42 | 6.545 | 0.26446
| 4:42 | 6.5453 | 0.26454
| 4:42 | 6.5456 | 0.26463
| 4:42 | 6.5458 | 0.26472
| 4:42 | 6.5461 | 0.26482
| 4:42 | 6.5464 | 0.26493
| 4:42 | 6.5467 | 0.26504
| 4:42 | 6.5469 | 0.26516
| 4:42 | 6.5472 | 0.26528
| 4:42 | 6.5475 | 0.26541
| 4:42 | 6.5478 | 0.26554
| 4:42 | 6.5481 | 0.26568
| 4:42 | 6.5483 | 0.26582
| 4:42 | 6.5486 | 0.26596
| 4:42 | 6.5489 | 0.26611
| 4:42 | 6.5492 | 0.26626
| 4:42 | 6.5494 | 0.2664
| 4:42 | 6.5497 | 0.26654
| 4:42 | 6.55 | 0.26668
| 4:42 | 6.5503 | 0.26683
| 4:42 | 6.5506 | 0.26697
| 4:42 | 6.5508 | 0.26711
| 4:42 | 6.5511 | 0.26726
| 4:42 | 6.5514 | 0.2674
| 4:42 | 6.5517 | 0.26754
| 4:42 | 6.5519 | 0.26767
| 4:42 | 6.5522 | 0.2678
| 4:42 | 6.5525 | 0.26793
| 4:42 | 6.5528 | 0.26805
| 4:42 | 6.5531 | 0.26816
| 4:42 | 6.5533 | 0.26827
| 4:42 | 6.5536 | 0.26837
| 4:42 | 6.5539 | 0.26846
| 4:42 | 6.5542 | 0.26856
| 4:42 | 6.5544 | 0.26865
| 4:42 | 6.5547 | 0.26874
| 4:42 | 6.555 | 0.26884
| 4:42 | 6.5553 | 0.26893
| 4:42 | 6.5556 | 0.26902
| 4:42 | 6.5558 | 0.26912
| 4:42 | 6.5561 | 0.26922
| 4:42 | 6.5564 | 0.26931
| 4:42 | 6.5567 | 0.26941
| 4:42 | 6.5569 | 0.26951
| 4:42 | 6.5572 | 0.26962
| 4:42 | 6.5575 | 0.26973
| 4:42 | 6.5578 | 0.26984
| 4:42 | 6.5581 | 0.26996
| 4:42 | 6.5583 | 0.2701
| 4:42 | 6.5586 | 0.27023
| 4:42 | 6.5589 | 0.27038
| 4:42 | 6.5592 | 0.27052
| 4:42 | 6.5594 | 0.27067
| 4:42 | 6.5597 | 0.27082
| 4:42 | 6.56 | 0.27098
| 4:42 | 6.5603 | 0.27114
| 4:42 | 6.5606 | 0.27129
| 4:42 | 6.5608 | 0.27145
| 4:42 | 6.5611 | 0.2716
| 4:42 | 6.5614 | 0.27174
| 4:42 | 6.5617 | 0.27189
| 4:43 | 6.5619 | 0.27203
| 4:43 | 6.5622 | 0.27218
| 4:43 | 6.5625 | 0.27231
| 4:43 | 6.5628 | 0.27245
| 4:43 | 6.5631 | 0.27258
| 4:43 | 6.5633 | 0.2727
| 4:43 | 6.5636 | 0.27281
| 4:43 | 6.5639 | 0.2729
| 4:43 | 6.5642 | 0.27297
| 4:43 | 6.5644 | 0.27303
| 4:43 | 6.5647 | 0.27308
| 4:43 | 6.565 | 0.27311
| 4:43 | 6.5653 | 0.27313
| 4:43 | 6.5656 | 0.27313
| 4:43 | 6.5658 | 0.27311
| 4:43 | 6.5661 | 0.27308
| 4:43 | 6.5664 | 0.27304
| 4:43 | 6.5667 | 0.27299
| 4:43 | 6.5669 | 0.27291
| 4:43 | 6.5672 | 0.27282
| 4:43 | 6.5675 | 0.27272
| 4:43 | 6.5678 | 0.2726
| 4:43 | 6.5681 | 0.27247
| 4:43 | 6.5683 | 0.27233
| 4:43 | 6.5686 | 0.27217
| 4:43 | 6.5689 | 0.27199
| 4:43 | 6.5692 | 0.2718
| 4:43 | 6.5694 | 0.2716
| 4:43 | 6.5697 | 0.27139
| 4:43 | 6.57 | 0.27117
| 4:43 | 6.5703 | 0.27094
| 4:43 | 6.5706 | 0.2707
| 4:43 | 6.5708 | 0.27046
| 4:43 | 6.5711 | 0.2702
| 4:43 | 6.5714 | 0.26993
| 4:43 | 6.5717 | 0.26966
| 4:43 | 6.5719 | 0.26938
| 4:43 | 6.5722 | 0.26909
| 4:43 | 6.5725 | 0.26879
| 4:43 | 6.5728 | 0.26849
| 4:43 | 6.5731 | 0.26818
| 4:43 | 6.5733 | 0.26787
| 4:43 | 6.5736 | 0.26754
| 4:43 | 6.5739 | 0.26722
| 4:43 | 6.5742 | 0.26689
| 4:43 | 6.5744 | 0.26655
| 4:43 | 6.5747 | 0.26621
| 4:43 | 6.575 | 0.26586
| 4:43 | 6.5753 | 0.2655
| 4:43 | 6.5756 | 0.26514
| 4:43 | 6.5758 | 0.26478
| 4:43 | 6.5761 | 0.26441
| 4:43 | 6.5764 | 0.26405
| 4:43 | 6.5767 | 0.26367
| 4:43 | 6.5769 | 0.2633
| 4:43 | 6.5772 | 0.26293
| 4:43 | 6.5775 | 0.26256
| 4:43 | 6.5778 | 0.2622
| 4:43 | 6.5781 | 0.26184
| 4:44 | 6.5783 | 0.26148
| 4:44 | 6.5786 | 0.26113
| 4:44 | 6.5789 | 0.26078
| 4:44 | 6.5792 | 0.26043
| 4:44 | 6.5794 | 0.26009
| 4:44 | 6.5797 | 0.25975
| 4:44 | 6.58 | 0.25941
| 4:44 | 6.5803 | 0.25908
| 4:44 | 6.5806 | 0.25876
| 4:44 | 6.5808 | 0.25843
| 4:44 | 6.5811 | 0.25811
| 4:44 | 6.5814 | 0.25779
| 4:44 | 6.5817 | 0.25748
| 4:44 | 6.5819 | 0.25717
| 4:44 | 6.5822 | 0.25686
| 4:44 | 6.5825 | 0.25655
| 4:44 | 6.5828 | 0.25625
| 4:44 | 6.5831 | 0.25594
| 4:44 | 6.5833 | 0.25563
| 4:44 | 6.5836 | 0.25533
| 4:44 | 6.5839 | 0.25502
| 4:44 | 6.5842 | 0.25471
| 4:44 | 6.5844 | 0.25439
| 4:44 | 6.5847 | 0.25407
| 4:44 | 6.585 | 0.25376
| 4:44 | 6.5853 | 0.25344
| 4:44 | 6.5856 | 0.25312
| 4:44 | 6.5858 | 0.2528
| 4:44 | 6.5861 | 0.25248
| 4:44 | 6.5864 | 0.25214
| 4:44 | 6.5867 | 0.2518
| 4:44 | 6.5869 | 0.25146
| 4:44 | 6.5872 | 0.2511
| 4:44 | 6.5875 | 0.25074
| 4:44 | 6.5878 | 0.25037
| 4:44 | 6.5881 | 0.24999
| 4:44 | 6.5883 | 0.2496
| 4:44 | 6.5886 | 0.24921
| 4:44 | 6.5889 | 0.24882
| 4:44 | 6.5892 | 0.24842
| 4:44 | 6.5894 | 0.24802
| 4:44 | 6.5897 | 0.24762
| 4:44 | 6.59 | 0.24721
| 4:44 | 6.5903 | 0.2468
| 4:44 | 6.5906 | 0.24639
| 4:44 | 6.5908 | 0.24598
| 4:44 | 6.5911 | 0.24558
| 4:44 | 6.5914 | 0.24517
| 4:44 | 6.5917 | 0.24478
| 4:44 | 6.5919 | 0.24438
| 4:44 | 6.5922 | 0.244
| 4:44 | 6.5925 | 0.24362
| 4:44 | 6.5928 | 0.24325
| 4:44 | 6.5931 | 0.24289
| 4:44 | 6.5933 | 0.24254
| 4:44 | 6.5936 | 0.2422
| 4:44 | 6.5939 | 0.24186
| 4:44 | 6.5942 | 0.24153
| 4:44 | 6.5944 | 0.2412
| 4:44 | 6.5947 | 0.24088
| 4:44 | 6.595 | 0.24057
| 4:45 | 6.5953 | 0.24025
| 4:45 | 6.5956 | 0.23994
| 4:45 | 6.5958 | 0.23964
| 4:45 | 6.5961 | 0.23933
| 4:45 | 6.5964 | 0.23904
| 4:45 | 6.5967 | 0.23874
| 4:45 | 6.5969 | 0.23846
| 4:45 | 6.5972 | 0.23817
| 4:45 | 6.5975 | 0.2379
| 4:45 | 6.5978 | 0.23763
| 4:45 | 6.5981 | 0.23737
| 4:45 | 6.5983 | 0.23711
| 4:45 | 6.5986 | 0.23686
| 4:45 | 6.5989 | 0.23662
| 4:45 | 6.5992 | 0.23638
| 4:45 | 6.5994 | 0.23614
| 4:45 | 6.5997 | 0.23591
| 4:45 | 6.6 | 0.23569
| 4:45 | 6.6003 | 0.23546
| 4:45 | 6.6006 | 0.23525
| 4:45 | 6.6008 | 0.23503
| 4:45 | 6.6011 | 0.23483
| 4:45 | 6.6014 | 0.23463
| 4:45 | 6.6017 | 0.23444
| 4:45 | 6.6019 | 0.23424
| 4:45 | 6.6022 | 0.23404
| 4:45 | 6.6025 | 0.23385
| 4:45 | 6.6028 | 0.23366
| 4:45 | 6.6031 | 0.23347
| 4:45 | 6.6033 | 0.23328
| 4:45 | 6.6036 | 0.23309
| 4:45 | 6.6039 | 0.23291
| 4:45 | 6.6042 | 0.23274
| 4:45 | 6.6044 | 0.23257
| 4:45 | 6.6047 | 0.23242
| 4:45 | 6.605 | 0.23227
| 4:45 | 6.6053 | 0.23212
| 4:45 | 6.6056 | 0.23199
| 4:45 | 6.6058 | 0.23185
| 4:45 | 6.6061 | 0.23173
| 4:45 | 6.6064 | 0.23161
| 4:45 | 6.6067 | 0.23149
| 4:45 | 6.6069 | 0.23139
| 4:45 | 6.6072 | 0.23129
| 4:45 | 6.6075 | 0.23119
| 4:45 | 6.6078 | 0.2311
| 4:45 | 6.6081 | 0.23101
| 4:45 | 6.6083 | 0.23093
| 4:45 | 6.6086 | 0.23086
| 4:45 | 6.6089 | 0.2308
| 4:45 | 6.6092 | 0.23074
| 4:45 | 6.6094 | 0.23069
| 4:45 | 6.6097 | 0.23063
| 4:45 | 6.61 | 0.23058
| 4:45 | 6.6103 | 0.23052
| 4:45 | 6.6106 | 0.23048
| 4:45 | 6.6108 | 0.23043
| 4:45 | 6.6111 | 0.23037
| 4:45 | 6.6114 | 0.23032
| 4:46 | 6.6117 | 0.23028
| 4:46 | 6.6119 | 0.23023
| 4:46 | 6.6122 | 0.23019
| 4:46 | 6.6125 | 0.23015
| 4:46 | 6.6128 | 0.23011
| 4:46 | 6.6131 | 0.23008
| 4:46 | 6.6133 | 0.23004
| 4:46 | 6.6136 | 0.23001
| 4:46 | 6.6139 | 0.22997
| 4:46 | 6.6142 | 0.22993
| 4:46 | 6.6144 | 0.22989
| 4:46 | 6.6147 | 0.22984
| 4:46 | 6.615 | 0.2298
| 4:46 | 6.6153 | 0.22975
| 4:46 | 6.6156 | 0.2297
| 4:46 | 6.6158 | 0.22965
| 4:46 | 6.6161 | 0.2296
| 4:46 | 6.6164 | 0.22955
| 4:46 | 6.6167 | 0.2295
| 4:46 | 6.6169 | 0.22945
| 4:46 | 6.6172 | 0.2294
| 4:46 | 6.6175 | 0.22934
| 4:46 | 6.6178 | 0.22929
| 4:46 | 6.6181 | 0.22923
| 4:46 | 6.6183 | 0.22917
| 4:46 | 6.6186 | 0.2291
| 4:46 | 6.6189 | 0.22902
| 4:46 | 6.6192 | 0.22895
| 4:46 | 6.6194 | 0.22888
| 4:46 | 6.6197 | 0.2288
| 4:46 | 6.62 | 0.22873
| 4:46 | 6.6203 | 0.22865
| 4:46 | 6.6206 | 0.22858
| 4:46 | 6.6208 | 0.22851
| 4:46 | 6.6211 | 0.22843
| 4:46 | 6.6214 | 0.22834
| 4:46 | 6.6217 | 0.22826
| 4:46 | 6.6219 | 0.22817
| 4:46 | 6.6222 | 0.22808
| 4:46 | 6.6225 | 0.22799
| 4:46 | 6.6228 | 0.2279
| 4:46 | 6.6231 | 0.22781
| 4:46 | 6.6233 | 0.22771
| 4:46 | 6.6236 | 0.22762
| 4:46 | 6.6239 | 0.22753
| 4:46 | 6.6242 | 0.22744
| 4:46 | 6.6244 | 0.22735
| 4:46 | 6.6247 | 0.22726
| 4:46 | 6.625 | 0.22718
| 4:46 | 6.6253 | 0.22708
| 4:46 | 6.6256 | 0.22699
| 4:46 | 6.6258 | 0.2269
| 4:46 | 6.6261 | 0.22681
| 4:46 | 6.6264 | 0.22672
| 4:46 | 6.6267 | 0.22662
| 4:46 | 6.6269 | 0.22652
| 4:46 | 6.6272 | 0.22642
| 4:46 | 6.6275 | 0.22633
| 4:46 | 6.6278 | 0.22624
| 4:46 | 6.6281 | 0.22615
| 4:46 | 6.6283 | 0.22607
| 4:47 | 6.6286 | 0.22599
| 4:47 | 6.6289 | 0.22591
| 4:47 | 6.6292 | 0.22583
| 4:47 | 6.6294 | 0.22575
| 4:47 | 6.6297 | 0.22568
| 4:47 | 6.63 | 0.2256
| 4:47 | 6.6303 | 0.22553
| 4:47 | 6.6306 | 0.22546
| 4:47 | 6.6308 | 0.22539
| 4:47 | 6.6311 | 0.22532
| 4:47 | 6.6314 | 0.22526
| 4:47 | 6.6317 | 0.2252
| 4:47 | 6.6319 | 0.22514
| 4:47 | 6.6322 | 0.22508
| 4:47 | 6.6325 | 0.22502
| 4:47 | 6.6328 | 0.22496
| 4:47 | 6.6331 | 0.2249
| 4:47 | 6.6333 | 0.22484
| 4:47 | 6.6336 | 0.22478
| 4:47 | 6.6339 | 0.22472
| 4:47 | 6.6342 | 0.22465
| 4:47 | 6.6344 | 0.22458
| 4:47 | 6.6347 | 0.22451
| 4:47 | 6.635 | 0.22445
| 4:47 | 6.6353 | 0.22438
| 4:47 | 6.6356 | 0.22432
| 4:47 | 6.6358 | 0.22426
| 4:47 | 6.6361 | 0.22421
| 4:47 | 6.6364 | 0.22416
| 4:47 | 6.6367 | 0.2241
| 4:47 | 6.6369 | 0.22405
| 4:47 | 6.6372 | 0.22399
| 4:47 | 6.6375 | 0.22393
| 4:47 | 6.6378 | 0.22387
| 4:47 | 6.6381 | 0.22381
| 4:47 | 6.6383 | 0.22375
| 4:47 | 6.6386 | 0.22369
| 4:47 | 6.6389 | 0.22363
| 4:47 | 6.6392 | 0.22358
| 4:47 | 6.6394 | 0.22352
| 4:47 | 6.6397 | 0.22347
| 4:47 | 6.64 | 0.22342
| 4:47 | 6.6403 | 0.22337
| 4:47 | 6.6406 | 0.22332
| 4:47 | 6.6408 | 0.22326
| 4:47 | 6.6411 | 0.2232
| 4:47 | 6.6414 | 0.22314
| 4:47 | 6.6417 | 0.22308
| 4:47 | 6.6419 | 0.22302
| 4:47 | 6.6422 | 0.22296
| 4:47 | 6.6425 | 0.22289
| 4:47 | 6.6428 | 0.22283
| 4:47 | 6.6431 | 0.22277
| 4:47 | 6.6433 | 0.22271
| 4:47 | 6.6436 | 0.22265
| 4:47 | 6.6439 | 0.2226
| 4:47 | 6.6442 | 0.22255
| 4:47 | 6.6444 | 0.2225
| 4:47 | 6.6447 | 0.22244
| 4:48 | 6.645 | 0.22239
| 4:48 | 6.6453 | 0.22233
| 4:48 | 6.6456 | 0.22227
| 4:48 | 6.6458 | 0.22221
| 4:48 | 6.6461 | 0.22215
| 4:48 | 6.6464 | 0.22208
| 4:48 | 6.6467 | 0.22202
| 4:48 | 6.6469 | 0.22195
| 4:48 | 6.6472 | 0.22189
| 4:48 | 6.6475 | 0.22183
| 4:48 | 6.6478 | 0.22177
| 4:48 | 6.6481 | 0.22171
| 4:48 | 6.6483 | 0.22166
| 4:48 | 6.6486 | 0.2216
| 4:48 | 6.6489 | 0.22155
| 4:48 | 6.6492 | 0.22149
| 4:48 | 6.6494 | 0.22144
| 4:48 | 6.6497 | 0.22138
| 4:48 | 6.65 | 0.22131
| 4:48 | 6.6503 | 0.22125
| 4:48 | 6.6506 | 0.22119
| 4:48 | 6.6508 | 0.22113
| 4:48 | 6.6511 | 0.22107
| 4:48 | 6.6514 | 0.22102
| 4:48 | 6.6517 | 0.22097
| 4:48 | 6.6519 | 0.22092
| 4:48 | 6.6522 | 0.22087
| 4:48 | 6.6525 | 0.22082
| 4:48 | 6.6528 | 0.22077
| 4:48 | 6.6531 | 0.22072
| 4:48 | 6.6533 | 0.22066
| 4:48 | 6.6536 | 0.2206
| 4:48 | 6.6539 | 0.22055
| 4:48 | 6.6542 | 0.2205
| 4:48 | 6.6544 | 0.22045
| 4:48 | 6.6547 | 0.2204
| 4:48 | 6.655 | 0.22036
| 4:48 | 6.6553 | 0.22033
| 4:48 | 6.6556 | 0.22031
| 4:48 | 6.6558 | 0.22029
| 4:48 | 6.6561 | 0.22028
| 4:48 | 6.6564 | 0.22027
| 4:48 | 6.6567 | 0.22027
| 4:48 | 6.6569 | 0.22028
| 4:48 | 6.6572 | 0.22028
| 4:48 | 6.6575 | 0.22029
| 4:48 | 6.6578 | 0.22029
| 4:48 | 6.6581 | 0.22031
| 4:48 | 6.6583 | 0.22033
| 4:48 | 6.6586 | 0.22035
| 4:48 | 6.6589 | 0.22039
| 4:48 | 6.6592 | 0.22044
| 4:48 | 6.6594 | 0.22049
| 4:48 | 6.6597 | 0.22056
| 4:48 | 6.66 | 0.22062
| 4:48 | 6.6603 | 0.22068
| 4:48 | 6.6606 | 0.22075
| 4:48 | 6.6608 | 0.22083
| 4:48 | 6.6611 | 0.22091
| 4:48 | 6.6614 | 0.22099
| 4:48 | 6.6617 | 0.22107
| 4:49 | 6.6619 | 0.22115
| 4:49 | 6.6622 | 0.22123
| 4:49 | 6.6625 | 0.22132
| 4:49 | 6.6628 | 0.22142
| 4:49 | 6.6631 | 0.22151
| 4:49 | 6.6633 | 0.2216
| 4:49 | 6.6636 | 0.22169
| 4:49 | 6.6639 | 0.22178
| 4:49 | 6.6642 | 0.22186
| 4:49 | 6.6644 | 0.22194
| 4:49 | 6.6647 | 0.22202
| 4:49 | 6.665 | 0.22209
| 4:49 | 6.6653 | 0.22216
| 4:49 | 6.6656 | 0.22222
| 4:49 | 6.6658 | 0.22228
| 4:49 | 6.6661 | 0.22233
| 4:49 | 6.6664 | 0.22239
| 4:49 | 6.6667 | 0.22244
| 4:49 | 6.6669 | 0.22249
| 4:49 | 6.6672 | 0.22253
| 4:49 | 6.6675 | 0.22258
| 4:49 | 6.6678 | 0.22262
| 4:49 | 6.6681 | 0.22265
| 4:49 | 6.6683 | 0.22268
| 4:49 | 6.6686 | 0.2227
| 4:49 | 6.6689 | 0.22272
| 4:49 | 6.6692 | 0.22273
| 4:49 | 6.6694 | 0.22272
| 4:49 | 6.6697 | 0.22271
| 4:49 | 6.67 | 0.2227
| 4:49 | 6.6703 | 0.2227
| 4:49 | 6.6706 | 0.22268
| 4:49 | 6.6708 | 0.22267
| 4:49 | 6.6711 | 0.22266
| 4:49 | 6.6714 | 0.22266
| 4:49 | 6.6717 | 0.22264
| 4:49 | 6.6719 | 0.22263
| 4:49 | 6.6722 | 0.22261
| 4:49 | 6.6725 | 0.22259
| 4:49 | 6.6728 | 0.22256
| 4:49 | 6.6731 | 0.22253
| 4:49 | 6.6733 | 0.22249
| 4:49 | 6.6736 | 0.22246
| 4:49 | 6.6739 | 0.22242
| 4:49 | 6.6742 | 0.22238
| 4:49 | 6.6744 | 0.22235
| 4:49 | 6.6747 | 0.22232
| 4:49 | 6.675 | 0.2223
| 4:49 | 6.6753 | 0.22228
| 4:49 | 6.6756 | 0.22225
| 4:49 | 6.6758 | 0.22221
| 4:49 | 6.6761 | 0.22218
| 4:49 | 6.6764 | 0.22215
| 4:49 | 6.6767 | 0.22212
| 4:49 | 6.6769 | 0.22208
| 4:49 | 6.6772 | 0.22203
| 4:49 | 6.6775 | 0.22198
| 4:49 | 6.6778 | 0.22194
| 4:49 | 6.6781 | 0.2219
| 4:50 | 6.6783 | 0.22186
| 4:50 | 6.6786 | 0.22183
| 4:50 | 6.6789 | 0.2218
| 4:50 | 6.6792 | 0.22178
| 4:50 | 6.6794 | 0.22175
| 4:50 | 6.6797 | 0.22172
| 4:50 | 6.68 | 0.22168
| 4:50 | 6.6803 | 0.22165
| 4:50 | 6.6806 | 0.22161
| 4:50 | 6.6808 | 0.22158
| 4:50 | 6.6811 | 0.22154
| 4:50 | 6.6814 | 0.22151
| 4:50 | 6.6817 | 0.22147
| 4:50 | 6.6819 | 0.22144
| 4:50 | 6.6822 | 0.2214
| 4:50 | 6.6825 | 0.22137
| 4:50 | 6.6828 | 0.22134
| 4:50 | 6.6831 | 0.22132
| 4:50 | 6.6833 | 0.22129
| 4:50 | 6.6836 | 0.22126
| 4:50 | 6.6839 | 0.22123
| 4:50 | 6.6842 | 0.22121
| 4:50 | 6.6844 | 0.22118
| 4:50 | 6.6847 | 0.22114
| 4:50 | 6.685 | 0.2211
| 4:50 | 6.6853 | 0.22106
| 4:50 | 6.6856 | 0.22102
| 4:50 | 6.6858 | 0.22099
| 4:50 | 6.6861 | 0.22095
| 4:50 | 6.6864 | 0.22093
| 4:50 | 6.6867 | 0.22091
| 4:50 | 6.6869 | 0.22089
| 4:50 | 6.6872 | 0.22086
| 4:50 | 6.6875 | 0.22083
| 4:50 | 6.6878 | 0.22081
| 4:50 | 6.6881 | 0.22078
| 4:50 | 6.6883 | 0.22076
| 4:50 | 6.6886 | 0.22074
| 4:50 | 6.6889 | 0.22071
| 4:50 | 6.6892 | 0.22069
| 4:50 | 6.6894 | 0.22067
| 4:50 | 6.6897 | 0.22065
| 4:50 | 6.69 | 0.22062
| 4:50 | 6.6903 | 0.2206
| 4:50 | 6.6906 | 0.22058
| 4:50 | 6.6908 | 0.22057
| 4:50 | 6.6911 | 0.22055
| 4:50 | 6.6914 | 0.22052
| 4:50 | 6.6917 | 0.2205
| 4:50 | 6.6919 | 0.22048
| 4:50 | 6.6922 | 0.22046
| 4:50 | 6.6925 | 0.22043
| 4:50 | 6.6928 | 0.2204
| 4:50 | 6.6931 | 0.22036
| 4:50 | 6.6933 | 0.22033
| 4:50 | 6.6936 | 0.2203
| 4:50 | 6.6939 | 0.22028
| 4:50 | 6.6942 | 0.22026
| 4:50 | 6.6944 | 0.22024
| 4:50 | 6.6947 | 0.22023
| 4:50 | 6.695 | 0.22021
| 4:51 | 6.6953 | 0.22019
| 4:51 | 6.6956 | 0.22017
| 4:51 | 6.6958 | 0.22015
| 4:51 | 6.6961 | 0.22013
| 4:51 | 6.6964 | 0.2201
| 4:51 | 6.6967 | 0.22007
| 4:51 | 6.6969 | 0.22004
| 4:51 | 6.6972 | 0.22002
| 4:51 | 6.6975 | 0.21999
| 4:51 | 6.6978 | 0.21997
| 4:51 | 6.6981 | 0.21995
| 4:51 | 6.6983 | 0.21993
| 4:51 | 6.6986 | 0.21991
| 4:51 | 6.6989 | 0.21989
| 4:51 | 6.6992 | 0.21988
| 4:51 | 6.6994 | 0.21986
| 4:51 | 6.6997 | 0.21984
| 4:51 | 6.7 | 0.21981
| 4:51 | 6.7003 | 0.21979
| 4:51 | 6.7006 | 0.21975
| 4:51 | 6.7008 | 0.21972
| 4:51 | 6.7011 | 0.21969
| 4:51 | 6.7014 | 0.21966
| 4:51 | 6.7017 | 0.21964
| 4:51 | 6.7019 | 0.21962
| 4:51 | 6.7022 | 0.21961
| 4:51 | 6.7025 | 0.2196
| 4:51 | 6.7028 | 0.21958
| 4:51 | 6.7031 | 0.21956
| 4:51 | 6.7033 | 0.21954
| 4:51 | 6.7036 | 0.21952
| 4:51 | 6.7039 | 0.2195
| 4:51 | 6.7042 | 0.21948
| 4:51 | 6.7044 | 0.21945
| 4:51 | 6.7047 | 0.21942
| 4:51 | 6.705 | 0.21939
| 4:51 | 6.7053 | 0.21936
| 4:51 | 6.7056 | 0.21934
| 4:51 | 6.7058 | 0.21931
| 4:51 | 6.7061 | 0.21929
| 4:51 | 6.7064 | 0.21927
| 4:51 | 6.7067 | 0.21926
| 4:51 | 6.7069 | 0.21924
| 4:51 | 6.7072 | 0.21922
| 4:51 | 6.7075 | 0.21921
| 4:51 | 6.7078 | 0.2192
| 4:51 | 6.7081 | 0.21917
| 4:51 | 6.7083 | 0.21915
| 4:51 | 6.7086 | 0.21912
| 4:51 | 6.7089 | 0.2191
| 4:51 | 6.7092 | 0.21908
| 4:51 | 6.7094 | 0.21907
| 4:51 | 6.7097 | 0.21906
| 4:51 | 6.71 | 0.21905
| 4:51 | 6.7103 | 0.21905
| 4:51 | 6.7106 | 0.21905
| 4:51 | 6.7108 | 0.21903
| 4:51 | 6.7111 | 0.21902
| 4:51 | 6.7114 | 0.21901
| 4:52 | 6.7117 | 0.219
| 4:52 | 6.7119 | 0.21898
| 4:52 | 6.7122 | 0.21896
| 4:52 | 6.7125 | 0.21894
| 4:52 | 6.7128 | 0.21892
| 4:52 | 6.7131 | 0.2189
| 4:52 | 6.7133 | 0.21889
| 4:52 | 6.7136 | 0.21887
| 4:52 | 6.7139 | 0.21885
| 4:52 | 6.7142 | 0.21883
| 4:52 | 6.7144 | 0.21882
| 4:52 | 6.7147 | 0.2188
| 4:52 | 6.715 | 0.21878
| 4:52 | 6.7153 | 0.21877
| 4:52 | 6.7156 | 0.21875
| 4:52 | 6.7158 | 0.21874
| 4:52 | 6.7161 | 0.21872
| 4:52 | 6.7164 | 0.2187
| 4:52 | 6.7167 | 0.21868
| 4:52 | 6.7169 | 0.21867
| 4:52 | 6.7172 | 0.21866
| 4:52 | 6.7175 | 0.21865
| 4:52 | 6.7178 | 0.21864
| 4:52 | 6.7181 | 0.21864
| 4:52 | 6.7183 | 0.21864
| 4:52 | 6.7186 | 0.21863
| 4:52 | 6.7189 | 0.21863
| 4:52 | 6.7192 | 0.21862
| 4:52 | 6.7194 | 0.21861
| 4:52 | 6.7197 | 0.21859
| 4:52 | 6.72 | 0.21858
| 4:52 | 6.7203 | 0.21856
| 4:52 | 6.7206 | 0.21855
| 4:52 | 6.7208 | 0.21854
| 4:52 | 6.7211 | 0.21853
| 4:52 | 6.7214 | 0.21852
| 4:52 | 6.7217 | 0.21851
| 4:52 | 6.7219 | 0.21851
| 4:52 | 6.7222 | 0.2185
| 4:52 | 6.7225 | 0.2185
| 4:52 | 6.7228 | 0.21849
| 4:52 | 6.7231 | 0.21848
| 4:52 | 6.7233 | 0.21848
| 4:52 | 6.7236 | 0.21847
| 4:52 | 6.7239 | 0.21845
| 4:52 | 6.7242 | 0.21844
| 4:52 | 6.7244 | 0.21843
| 4:52 | 6.7247 | 0.21842
| 4:52 | 6.725 | 0.21842
| 4:52 | 6.7253 | 0.21842
| 4:52 | 6.7256 | 0.21842
| 4:52 | 6.7258 | 0.21843
| 4:52 | 6.7261 | 0.21843
| 4:52 | 6.7264 | 0.21843
| 4:52 | 6.7267 | 0.21843
| 4:52 | 6.7269 | 0.21843
| 4:52 | 6.7272 | 0.21843
| 4:52 | 6.7275 | 0.21842
| 4:52 | 6.7278 | 0.21842
| 4:52 | 6.7281 | 0.21841
| 4:52 | 6.7283 | 0.2184
| 4:53 | 6.7286 | 0.2184
| 4:53 | 6.7289 | 0.2184
| 4:53 | 6.7292 | 0.21841
| 4:53 | 6.7294 | 0.21842
| 4:53 | 6.7297 | 0.21845
| 4:53 | 6.73 | 0.21816
| 4:53 | 6.7303 | 0.21792
| 4:53 | 6.7306 | 0.21769
| 4:53 | 6.7308 | 0.21749
| 4:53 | 6.7311 | 0.21731
| 4:53 | 6.7314 | 0.21716
| 4:53 | 6.7317 | 0.21703
| 4:53 | 6.7319 | 0.21692
| 4:53 | 6.7322 | 0.21684
| 4:53 | 6.7325 | 0.21679
| 4:53 | 6.7328 | 0.21677
| 4:53 | 6.7331 | 0.21677
| 4:53 | 6.7333 | 0.21679
| 4:53 | 6.7336 | 0.21683
| 4:53 | 6.7339 | 0.21686
| 4:53 | 6.7342 | 0.21689
| 4:53 | 6.7344 | 0.21693
| 4:53 | 6.7347 | 0.21696
| 4:53 | 6.735 | 0.21699
| 4:53 | 6.7353 | 0.21702
| 4:53 | 6.7356 | 0.21704
| 4:53 | 6.7358 | 0.21707
| 4:53 | 6.7361 | 0.2171
| 4:53 | 6.7364 | 0.21712
| 4:53 | 6.7367 | 0.21714
| 4:53 | 6.7369 | 0.21716
| 4:53 | 6.7372 | 0.21718
| 4:53 | 6.7375 | 0.2172
| 4:53 | 6.7378 | 0.21722
| 4:53 | 6.7381 | 0.21723
| 4:53 | 6.7383 | 0.21724
| 4:53 | 6.7386 | 0.21724
| 4:53 | 6.7389 | 0.21725
| 4:53 | 6.7392 | 0.21725
| 4:53 | 6.7394 | 0.21725
| 4:53 | 6.7397 | 0.21724
| 4:53 | 6.74 | 0.21724
| 4:53 | 6.7403 | 0.21723
| 4:53 | 6.7406 | 0.21723
| 4:53 | 6.7408 | 0.21722
| 4:53 | 6.7411 | 0.21722
| 4:53 | 6.7414 | 0.21723
| 4:53 | 6.7417 | 0.21722
| 4:53 | 6.7419 | 0.21722
| 4:53 | 6.7422 | 0.21722
| 4:53 | 6.7425 | 0.21721
| 4:53 | 6.7428 | 0.21721
| 4:53 | 6.7431 | 0.21722
| 4:53 | 6.7433 | 0.21723
| 4:53 | 6.7436 | 0.21724
| 4:53 | 6.7439 | 0.21726
| 4:53 | 6.7442 | 0.21727
| 4:53 | 6.7444 | 0.21729
| 4:53 | 6.7447 | 0.21732
| 4:54 | 6.745 | 0.21734
| 4:54 | 6.7453 | 0.21737
| 4:54 | 6.7456 | 0.21739
| 4:54 | 6.7458 | 0.21741
| 4:54 | 6.7461 | 0.21743
| 4:54 | 6.7464 | 0.21744
| 4:54 | 6.7467 | 0.21746
| 4:54 | 6.7469 | 0.21747
| 4:54 | 6.7472 | 0.21748
| 4:54 | 6.7475 | 0.21747
| 4:54 | 6.7478 | 0.21745
| 4:54 | 6.7481 | 0.21741
| 4:54 | 6.7483 | 0.21736
| 4:54 | 6.7486 | 0.2173
| 4:54 | 6.7489 | 0.21722
| 4:54 | 6.7492 | 0.21713
| 4:54 | 6.7494 | 0.21703
| 4:54 | 6.7497 | 0.2169
| 4:54 | 6.75 | 0.21675
| 4:54 | 6.7503 | 0.21658
| 4:54 | 6.7506 | 0.21639
| 4:54 | 6.7508 | 0.21617
| 4:54 | 6.7511 | 0.21594
| 4:54 | 6.7514 | 0.21567
| 4:54 | 6.7517 | 0.21538
| 4:54 | 6.7519 | 0.21506
| 4:54 | 6.7522 | 0.21473
| 4:54 | 6.7525 | 0.21439
| 4:54 | 6.7528 | 0.21402
| 4:54 | 6.7531 | 0.21365
| 4:54 | 6.7533 | 0.21326
| 4:54 | 6.7536 | 0.21284
| 4:54 | 6.7539 | 0.21238
| 4:54 | 6.7542 | 0.21189
| 4:54 | 6.7544 | 0.2114
| 4:54 | 6.7547 | 0.21087
| 4:54 | 6.755 | 0.21031
| 4:54 | 6.7553 | 0.20973
| 4:54 | 6.7556 | 0.20916
| 4:54 | 6.7558 | 0.20858
| 4:54 | 6.7561 | 0.20799
| 4:54 | 6.7564 | 0.20741
| 4:54 | 6.7567 | 0.20682
| 4:54 | 6.7569 | 0.20623
| 4:54 | 6.7572 | 0.20563
| 4:54 | 6.7575 | 0.20503
| 4:54 | 6.7578 | 0.20442
| 4:54 | 6.7581 | 0.20381
| 4:54 | 6.7583 | 0.20319
| 4:54 | 6.7586 | 0.20258
| 4:54 | 6.7589 | 0.20196
| 4:54 | 6.7592 | 0.20135
| 4:54 | 6.7594 | 0.20073
| 4:54 | 6.7597 | 0.20012
| 4:54 | 6.76 | 0.1995
| 4:54 | 6.7603 | 0.19889
| 4:54 | 6.7606 | 0.19828
| 4:54 | 6.7608 | 0.19766
| 4:54 | 6.7611 | 0.19705
| 4:54 | 6.7614 | 0.19643
| 4:54 | 6.7617 | 0.19581
| 4:55 | 6.7619 | 0.19519
| 4:55 | 6.7622 | 0.19457
| 4:55 | 6.7625 | 0.19395
| 4:55 | 6.7628 | 0.19332
| 4:55 | 6.7631 | 0.1927
| 4:55 | 6.7633 | 0.19208
| 4:55 | 6.7636 | 0.19145
| 4:55 | 6.7639 | 0.19083
| 4:55 | 6.7642 | 0.1902
| 4:55 | 6.7644 | 0.18958
| 4:55 | 6.7647 | 0.18895
| 4:55 | 6.765 | 0.18832
| 4:55 | 6.7653 | 0.1877
| 4:55 | 6.7656 | 0.18707
| 4:55 | 6.7658 | 0.18645
| 4:55 | 6.7661 | 0.18582
| 4:55 | 6.7664 | 0.18519
| 4:55 | 6.7667 | 0.18456
| 4:55 | 6.7669 | 0.18393
| 4:55 | 6.7672 | 0.18331
| 4:55 | 6.7675 | 0.18268
| 4:55 | 6.7678 | 0.18205
| 4:55 | 6.7681 | 0.18142
| 4:55 | 6.7683 | 0.1808
| 4:55 | 6.7686 | 0.18017
| 4:55 | 6.7689 | 0.17955
| 4:55 | 6.7692 | 0.17893
| 4:55 | 6.7694 | 0.1783
| 4:55 | 6.7697 | 0.17767
| 4:55 | 6.77 | 0.17704
| 4:55 | 6.7703 | 0.17641
| 4:55 | 6.7706 | 0.17578
| 4:55 | 6.7708 | 0.17516
| 4:55 | 6.7711 | 0.17453
| 4:55 | 6.7714 | 0.17389
| 4:55 | 6.7717 | 0.17326
| 4:55 | 6.7719 | 0.17263
| 4:55 | 6.7722 | 0.172
| 4:55 | 6.7725 | 0.17137
| 4:55 | 6.7728 | 0.17074
| 4:55 | 6.7731 | 0.17012
| 4:55 | 6.7733 | 0.16949
| 4:55 | 6.7736 | 0.16886
| 4:55 | 6.7739 | 0.16823
| 4:55 | 6.7742 | 0.1676
| 4:55 | 6.7744 | 0.16697
| 4:55 | 6.7747 | 0.16634
| 4:55 | 6.775 | 0.16571
| 4:55 | 6.7753 | 0.16508
| 4:55 | 6.7756 | 0.16445
| 4:55 | 6.7758 | 0.16383
| 4:55 | 6.7761 | 0.16321
| 4:55 | 6.7764 | 0.16258
| 4:55 | 6.7767 | 0.16196
| 4:55 | 6.7769 | 0.16134
| 4:55 | 6.7772 | 0.16072
| 4:55 | 6.7775 | 0.16009
| 4:55 | 6.7778 | 0.15947
| 4:55 | 6.7781 | 0.15884
| 4:56 | 6.7783 | 0.15821
| 4:56 | 6.7786 | 0.15759
| 4:56 | 6.7789 | 0.15696
| 4:56 | 6.7792 | 0.15634
| 4:56 | 6.7794 | 0.15571
| 4:56 | 6.7797 | 0.15509
| 4:56 | 6.78 | 0.15447
| 4:56 | 6.7803 | 0.15385
| 4:56 | 6.7806 | 0.15323
| 4:56 | 6.7808 | 0.1526
| 4:56 | 6.7811 | 0.15198
| 4:56 | 6.7814 | 0.15136
| 4:56 | 6.7817 | 0.15073
| 4:56 | 6.7819 | 0.15011
| 4:56 | 6.7822 | 0.14948
| 4:56 | 6.7825 | 0.14886
| 4:56 | 6.7828 | 0.14824
| 4:56 | 6.7831 | 0.14762
| 4:56 | 6.7833 | 0.14699
| 4:56 | 6.7836 | 0.14637
| 4:56 | 6.7839 | 0.14576
| 4:56 | 6.7842 | 0.14515
| 4:56 | 6.7844 | 0.14454
| 4:56 | 6.7847 | 0.14392
| 4:56 | 6.785 | 0.1433
| 4:56 | 6.7853 | 0.14268
| 4:56 | 6.7856 | 0.14207
| 4:56 | 6.7858 | 0.14144
| 4:56 | 6.7861 | 0.14083
| 4:56 | 6.7864 | 0.14021
| 4:56 | 6.7867 | 0.13959
| 4:56 | 6.7869 | 0.13897
| 4:56 | 6.7872 | 0.13835
| 4:56 | 6.7875 | 0.13774
| 4:56 | 6.7878 | 0.13713
| 4:56 | 6.7881 | 0.13652
| 4:56 | 6.7883 | 0.13591
| 4:56 | 6.7886 | 0.1353
| 4:56 | 6.7889 | 0.13469
| 4:56 | 6.7892 | 0.13408
| 4:56 | 6.7894 | 0.13347
| 4:56 | 6.7897 | 0.13286
| 4:56 | 6.79 | 0.13224
| 4:56 | 6.7903 | 0.13163
| 4:56 | 6.7906 | 0.13101
| 4:56 | 6.7908 | 0.1304
| 4:56 | 6.7911 | 0.12978
| 4:56 | 6.7914 | 0.12916
| 4:56 | 6.7917 | 0.12855
| 4:56 | 6.7919 | 0.12795
| 4:56 | 6.7922 | 0.12734
| 4:56 | 6.7925 | 0.12673
| 4:56 | 6.7928 | 0.12612
| 4:56 | 6.7931 | 0.1255
| 4:56 | 6.7933 | 0.12489
| 4:56 | 6.7936 | 0.12427
| 4:56 | 6.7939 | 0.12365
| 4:56 | 6.7942 | 0.12303
| 4:56 | 6.7944 | 0.12242
| 4:56 | 6.7947 | 0.1218
| 4:56 | 6.795 | 0.12118
| 4:57 | 6.7953 | 0.12057
| 4:57 | 6.7956 | 0.11996
| 4:57 | 6.7958 | 0.11936
| 4:57 | 6.7961 | 0.11875
| 4:57 | 6.7964 | 0.11813
| 4:57 | 6.7967 | 0.11752
| 4:57 | 6.7969 | 0.11691
| 4:57 | 6.7972 | 0.11629
| 4:57 | 6.7975 | 0.11568
| 4:57 | 6.7978 | 0.11506
| 4:57 | 6.7981 | 0.11445
| 4:57 | 6.7983 | 0.11383
| 4:57 | 6.7986 | 0.11321
| 4:57 | 6.7989 | 0.1126
| 4:57 | 6.7992 | 0.11199
| 4:57 | 6.7994 | 0.11138
| 4:57 | 6.7997 | 0.11077
| 4:57 | 6.8 | 0.11016
| 4:57 | 6.8003 | 0.10955
| 4:57 | 6.8006 | 0.10894
| 4:57 | 6.8008 | 0.10833
| 4:57 | 6.8011 | 0.10772
| 4:57 | 6.8014 | 0.1071
| 4:57 | 6.8017 | 0.10649
| 4:57 | 6.8019 | 0.10588
| 4:57 | 6.8022 | 0.10527
| 4:57 | 6.8025 | 0.10466
| 4:57 | 6.8028 | 0.10405
| 4:57 | 6.8031 | 0.10345
| 4:57 | 6.8033 | 0.10286
| 4:57 | 6.8036 | 0.10226
| 4:57 | 6.8039 | 0.10167
| 4:57 | 6.8042 | 0.10108
| 4:57 | 6.8044 | 0.10049
| 4:57 | 6.8047 | 0.099898
| 4:57 | 6.805 | 0.099314
| 4:57 | 6.8053 | 0.098735
| 4:57 | 6.8056 | 0.098166
| 4:57 | 6.8058 | 0.097608
| 4:57 | 6.8061 | 0.097061
| 4:57 | 6.8064 | 0.096524
| 4:57 | 6.8067 | 0.095998
| 4:57 | 6.8069 | 0.095481
| 4:57 | 6.8072 | 0.09498
| 4:57 | 6.8075 | 0.094488
| 4:57 | 6.8078 | 0.094004
| 4:57 | 6.8081 | 0.093535
| 4:57 | 6.8083 | 0.093089
| 4:57 | 6.8086 | 0.09266
| 4:57 | 6.8089 | 0.092248
| 4:57 | 6.8092 | 0.09186
| 4:57 | 6.8094 | 0.091487
| 4:57 | 6.8097 | 0.091137
| 4:57 | 6.81 | 0.090808
| 4:57 | 6.8103 | 0.090489
| 4:57 | 6.8106 | 0.090191
| 4:57 | 6.8108 | 0.089904
| 4:57 | 6.8111 | 0.08963
| 4:57 | 6.8114 | 0.089363
| 4:58 | 6.8117 | 0.08909
| 4:58 | 6.8119 | 0.088813
| 4:58 | 6.8122 | 0.088534
| 4:58 | 6.8125 | 0.088255
| 4:58 | 6.8128 | 0.087974
| 4:58 | 6.8131 | 0.087692
| 4:58 | 6.8133 | 0.08741
| 4:58 | 6.8136 | 0.087122
| 4:58 | 6.8139 | 0.086828
| 4:58 | 6.8142 | 0.086529
| 4:58 | 6.8144 | 0.086224
| 4:58 | 6.8147 | 0.085914
| 4:58 | 6.815 | 0.085598
| 4:58 | 6.8153 | 0.085277
| 4:58 | 6.8156 | 0.08495
| 4:58 | 6.8158 | 0.084616
| 4:58 | 6.8161 | 0.084275
| 4:58 | 6.8164 | 0.083926
| 4:58 | 6.8167 | 0.083578
| 4:58 | 6.8169 | 0.083236
| 4:58 | 6.8172 | 0.082898
| 4:58 | 6.8175 | 0.082563
| 4:58 | 6.8178 | 0.08223
| 4:58 | 6.8181 | 0.081907
| 4:58 | 6.8183 | 0.081594
| 4:58 | 6.8186 | 0.081315
| 4:58 | 6.8189 | 0.081068
| 4:58 | 6.8192 | 0.080829
| 4:58 | 6.8194 | 0.080605
| 4:58 | 6.8197 | 0.080411
| 4:58 | 6.82 | 0.080271
| 4:58 | 6.8203 | 0.080162
| 4:58 | 6.8206 | 0.08008
| 4:58 | 6.8208 | 0.080023
| 4:58 | 6.8211 | 0.079988
| 4:58 | 6.8214 | 0.079991
| 4:58 | 6.8217 | 0.08001
| 4:58 | 6.8219 | 0.080043
| 4:58 | 6.8222 | 0.080092
| 4:58 | 6.8225 | 0.080158
| 4:58 | 6.8228 | 0.08024
| 4:58 | 6.8231 | 0.080339
| 4:58 | 6.8233 | 0.080454
| 4:58 | 6.8236 | 0.080586
| 4:58 | 6.8239 | 0.080734
| 4:58 | 6.8242 | 0.080893
| 4:58 | 6.8244 | 0.081058
| 4:58 | 6.8247 | 0.081233
| 4:58 | 6.825 | 0.081419
| 4:58 | 6.8253 | 0.08161
| 4:58 | 6.8256 | 0.081805
| 4:58 | 6.8258 | 0.082004
| 4:58 | 6.8261 | 0.082206
| 4:58 | 6.8264 | 0.08241
| 4:58 | 6.8267 | 0.082616
| 4:58 | 6.8269 | 0.082821
| 4:58 | 6.8272 | 0.083025
| 4:58 | 6.8275 | 0.083225
| 4:58 | 6.8278 | 0.083423
| 4:58 | 6.8281 | 0.083616
| 4:58 | 6.8283 | 0.083808
| 4:59 | 6.8286 | 0.083993
| 4:59 | 6.8289 | 0.084168
| 4:59 | 6.8292 | 0.084331
| 4:59 | 6.8294 | 0.08448
| 4:59 | 6.8297 | 0.084617
| 4:59 | 6.83 | 0.084736
| 4:59 | 6.8303 | 0.084855
| 4:59 | 6.8306 | 0.084974
| 4:59 | 6.8308 | 0.085093
| 4:59 | 6.8311 | 0.085212
| 4:59 | 6.8314 | 0.085332
| 4:59 | 6.8317 | 0.085452
| 4:59 | 6.8319 | 0.085573
| 4:59 | 6.8322 | 0.085693
| 4:59 | 6.8325 | 0.085814
| 4:59 | 6.8328 | 0.085936
| 4:59 | 6.8331 | 0.086062
| 4:59 | 6.8333 | 0.086185
| 4:59 | 6.8336 | 0.086304
| 4:59 | 6.8339 | 0.086423
| 4:59 | 6.8342 | 0.086538
| 4:59 | 6.8344 | 0.086649
| 4:59 | 6.8347 | 0.086749
| 4:59 | 6.835 | 0.086833
| 4:59 | 6.8353 | 0.086902
| 4:59 | 6.8356 | 0.086955
| 4:59 | 6.8358 | 0.087006
| 4:59 | 6.8361 | 0.087051
| 4:59 | 6.8364 | 0.087087
| 4:59 | 6.8367 | 0.087121
| 4:59 | 6.8369 | 0.087162
| 4:59 | 6.8372 | 0.087208
| 4:59 | 6.8375 | 0.087266
| 4:59 | 6.8378 | 0.087335
| 4:59 | 6.8381 | 0.087427
| 4:59 | 6.8383 | 0.087529
| 4:59 | 6.8386 | 0.087643
| 4:59 | 6.8389 | 0.087777
| 4:59 | 6.8392 | 0.087926
| 4:59 | 6.8394 | 0.08809
| 4:59 | 6.8397 | 0.088269
| 4:59 | 6.84 | 0.088463
| 4:59 | 6.8403 | 0.088669
| 4:59 | 6.8406 | 0.088886
| 4:59 | 6.8408 | 0.089115
| 4:59 | 6.8411 | 0.08935
| 4:59 | 6.8414 | 0.089581
| 4:59 | 6.8417 | 0.089805
| 4:59 | 6.8419 | 0.090026
| 4:59 | 6.8422 | 0.090229
| 4:59 | 6.8425 | 0.090407
| 4:59 | 6.8428 | 0.090559
| 4:59 | 6.8431 | 0.090694
| 4:59 | 6.8433 | 0.090808
| 4:59 | 6.8436 | 0.090905
| 4:59 | 6.8439 | 0.090983
| 4:59 | 6.8442 | 0.091048
| 4:59 | 6.8444 | 0.091106
| 4:59 | 6.8447 | 0.091152
| 5:00 | 6.845 | 0.091194
| 5:00 | 6.8453 | 0.091226
| 5:00 | 6.8456 | 0.091247
| 5:00 | 6.8458 | 0.09125
| 5:00 | 6.8461 | 0.091241
| 5:00 | 6.8464 | 0.091201
| 5:00 | 6.8467 | 0.091141
| 5:00 | 6.8469 | 0.091065
| 5:00 | 6.8472 | 0.090964
| 5:00 | 6.8475 | 0.09084
| 5:00 | 6.8478 | 0.090691
| 5:00 | 6.8481 | 0.090518
| 5:00 | 6.8483 | 0.090321
| 5:00 | 6.8486 | 0.0901
| 5:00 | 6.8489 | 0.089855
| 5:00 | 6.8492 | 0.089586
| 5:00 | 6.8494 | 0.089297
| 5:00 | 6.8497 | 0.088988
| 5:00 | 6.85 | 0.088676
| 5:00 | 6.8503 | 0.08836
| 5:00 | 6.8506 | 0.088038
| 5:00 | 6.8508 | 0.087715
| 5:00 | 6.8511 | 0.087388
| 5:00 | 6.8514 | 0.087057
| 5:00 | 6.8517 | 0.086727
| 5:00 | 6.8519 | 0.086396
| 5:00 | 6.8522 | 0.086063
| 5:00 | 6.8525 | 0.085727
| 5:00 | 6.8528 | 0.085392
| 5:00 | 6.8531 | 0.085058
| 5:00 | 6.8533 | 0.084724
| 5:00 | 6.8536 | 0.084391
| 5:00 | 6.8539 | 0.084054
| 5:00 | 6.8542 | 0.083729
| 5:00 | 6.8544 | 0.083404
| 5:00 | 6.8547 | 0.083077
| 5:00 | 6.855 | 0.082761
| 5:00 | 6.8553 | 0.082455
| 5:00 | 6.8556 | 0.082162
| 5:00 | 6.8558 | 0.08188
| 5:00 | 6.8561 | 0.081609
| 5:00 | 6.8564 | 0.08135
| 5:00 | 6.8567 | 0.081103
| 5:00 | 6.8569 | 0.080867
| 5:00 | 6.8572 | 0.080645
| 5:00 | 6.8575 | 0.08043
| 5:00 | 6.8578 | 0.080218
| 5:00 | 6.8581 | 0.080016
| 5:00 | 6.8583 | 0.079817
| 5:00 | 6.8586 | 0.079621
| 5:00 | 6.8589 | 0.079424
| 5:00 | 6.8592 | 0.079227
| 5:00 | 6.8594 | 0.079025
| 5:00 | 6.8597 | 0.078826
| 5:00 | 6.86 | 0.078627
| 5:00 | 6.8603 | 0.078426
| 5:00 | 6.8606 | 0.078222
| 5:00 | 6.8608 | 0.078023
| 5:00 | 6.8611 | 0.077828
| 5:00 | 6.8614 | 0.077635
| 5:00 | 6.8617 | 0.077442
| 5:01 | 6.8619 | 0.077257
| 5:01 | 6.8622 | 0.077084
| 5:01 | 6.8625 | 0.07692
| 5:01 | 6.8628 | 0.076761
| 5:01 | 6.8631 | 0.076622
| 5:01 | 6.8633 | 0.076494
| 5:01 | 6.8636 | 0.076371
| 5:01 | 6.8639 | 0.07625
| 5:01 | 6.8642 | 0.07613
| 5:01 | 6.8644 | 0.076011
| 5:01 | 6.8647 | 0.075894
| 5:01 | 6.865 | 0.075777
| 5:01 | 6.8653 | 0.075663
| 5:01 | 6.8656 | 0.075549
| 5:01 | 6.8658 | 0.075436
| 5:01 | 6.8661 | 0.075325
| 5:01 | 6.8664 | 0.075214
| 5:01 | 6.8667 | 0.075086
| 5:01 | 6.8669 | 0.074932
| 5:01 | 6.8672 | 0.07477
| 5:01 | 6.8675 | 0.074597
| 5:01 | 6.8678 | 0.074413
| 5:01 | 6.8681 | 0.074217
| 5:01 | 6.8683 | 0.074013
| 5:01 | 6.8686 | 0.073803
| 5:01 | 6.8689 | 0.073588
| 5:01 | 6.8692 | 0.073363
| 5:01 | 6.8694 | 0.073134
| 5:01 | 6.8697 | 0.072909
| 5:01 | 6.87 | 0.072686
| 5:01 | 6.8703 | 0.072464
| 5:01 | 6.8706 | 0.072243
| 5:01 | 6.8708 | 0.072027
| 5:01 | 6.8711 | 0.071815
| 5:01 | 6.8714 | 0.071606
| 5:01 | 6.8717 | 0.071398
| 5:01 | 6.8719 | 0.071203
| 5:01 | 6.8722 | 0.071014
| 5:01 | 6.8725 | 0.070831
| 5:01 | 6.8728 | 0.070655
| 5:01 | 6.8731 | 0.070485
| 5:01 | 6.8733 | 0.070321
| 5:01 | 6.8736 | 0.070162
| 5:01 | 6.8739 | 0.07001
| 5:01 | 6.8742 | 0.069861
| 5:01 | 6.8744 | 0.069716
| 5:01 | 6.8747 | 0.069574
| 5:01 | 6.875 | 0.069438
| 5:01 | 6.8753 | 0.06931
| 5:01 | 6.8756 | 0.069189
| 5:01 | 6.8758 | 0.06907
| 5:01 | 6.8761 | 0.068958
| 5:01 | 6.8764 | 0.068852
| 5:01 | 6.8767 | 0.068751
| 5:01 | 6.8769 | 0.068658
| 5:01 | 6.8772 | 0.068567
| 5:01 | 6.8775 | 0.068474
| 5:01 | 6.8778 | 0.068384
| 5:01 | 6.8781 | 0.068299
| 5:02 | 6.8783 | 0.068214
| 5:02 | 6.8786 | 0.068123
| 5:02 | 6.8789 | 0.06803
| 5:02 | 6.8792 | 0.067936
| 5:02 | 6.8794 | 0.067838
| 5:02 | 6.8797 | 0.067735
| 5:02 | 6.88 | 0.06763
| 5:02 | 6.8803 | 0.067525
| 5:02 | 6.8806 | 0.067425
| 5:02 | 6.8808 | 0.06733
| 5:02 | 6.8811 | 0.06724
| 5:02 | 6.8814 | 0.067155
| 5:02 | 6.8817 | 0.067075
| 5:02 | 6.8819 | 0.067
| 5:02 | 6.8822 | 0.06693
| 5:02 | 6.8825 | 0.066863
| 5:02 | 6.8828 | 0.066805
| 5:02 | 6.8831 | 0.066751
| 5:02 | 6.8833 | 0.066695
| 5:02 | 6.8836 | 0.066633
| 5:02 | 6.8839 | 0.066571
| 5:02 | 6.8842 | 0.06651
| 5:02 | 6.8844 | 0.066448
| 5:02 | 6.8847 | 0.066388
| 5:02 | 6.885 | 0.06632
| 5:02 | 6.8853 | 0.06623
| 5:02 | 6.8856 | 0.06611
| 5:02 | 6.8858 | 0.065956
| 5:02 | 6.8861 | 0.065796
| 5:02 | 6.8864 | 0.065604
| 5:02 | 6.8867 | 0.065383
| 5:02 | 6.8869 | 0.065137
| 5:02 | 6.8872 | 0.064864
| 5:02 | 6.8875 | 0.064568
| 5:02 | 6.8878 | 0.064246
| 5:02 | 6.8881 | 0.063924
| 5:02 | 6.8883 | 0.063546
| 5:02 | 6.8886 | 0.063162
| 5:02 | 6.8889 | 0.062757
| 5:02 | 6.8892 | 0.062329
| 5:02 | 6.8894 | 0.061881
| 5:02 | 6.8897 | 0.06141
| 5:02 | 6.89 | 0.060919
| 5:02 | 6.8903 | 0.060402
| 5:02 | 6.8906 | 0.059867
| 5:02 | 6.8908 | 0.059319
| 5:02 | 6.8911 | 0.058762
| 5:02 | 6.8914 | 0.058199
| 5:02 | 6.8917 | 0.057636
| 5:02 | 6.8919 | 0.057072
| 5:02 | 6.8922 | 0.056509
| 5:02 | 6.8925 | 0.055949
| 5:02 | 6.8928 | 0.055385
| 5:02 | 6.8931 | 0.054813
| 5:02 | 6.8933 | 0.054238
| 5:02 | 6.8936 | 0.053662
| 5:02 | 6.8939 | 0.053085
| 5:02 | 6.8942 | 0.052507
| 5:02 | 6.8944 | 0.051933
| 5:02 | 6.8947 | 0.051358
| 5:02 | 6.895 | 0.050782
| 5:03 | 6.8953 | 0.050205
| 5:03 | 6.8956 | 0.049632
| 5:03 | 6.8958 | 0.049061
| 5:03 | 6.8961 | 0.048494
| 5:03 | 6.8964 | 0.047928
| 5:03 | 6.8967 | 0.047362
| 5:03 | 6.8969 | 0.046796
| 5:03 | 6.8972 | 0.046231
| 5:03 | 6.8975 | 0.045669
| 5:03 | 6.8978 | 0.045108
| 5:03 | 6.8981 | 0.04455
| 5:03 | 6.8983 | 0.043993
| 5:03 | 6.8986 | 0.043438
| 5:03 | 6.8989 | 0.042885
| 5:03 | 6.8992 | 0.042334
| 5:03 | 6.8994 | 0.041786
| 5:03 | 6.8997 | 0.041245
| 5:03 | 6.9 | 0.040718
| 5:03 | 6.9003 | 0.040211
| 5:03 | 6.9006 | 0.039726
| 5:03 | 6.9008 | 0.039266
| 5:03 | 6.9011 | 0.038808
| 5:03 | 6.9014 | 0.038366
| 5:03 | 6.9017 | 0.037959
| 5:03 | 6.9019 | 0.037562
| 5:03 | 6.9022 | 0.037189
| 5:03 | 6.9025 | 0.03683
| 5:03 | 6.9028 | 0.036472
| 5:03 | 6.9031 | 0.036117
| 5:03 | 6.9033 | 0.035769
| 5:03 | 6.9036 | 0.035429
| 5:03 | 6.9039 | 0.035096
| 5:03 | 6.9042 | 0.034766
| 5:03 | 6.9044 | 0.03444
| 5:03 | 6.9047 | 0.034113
| 5:03 | 6.905 | 0.033797
| 5:03 | 6.9053 | 0.033481
| 5:03 | 6.9056 | 0.033174
| 5:03 | 6.9058 | 0.032875
| 5:03 | 6.9061 | 0.032586
| 5:03 | 6.9064 | 0.032305
| 5:03 | 6.9067 | 0.032033
| 5:03 | 6.9069 | 0.031769
| 5:03 | 6.9072 | 0.031522
| 5:03 | 6.9075 | 0.031287
| 5:03 | 6.9078 | 0.031063
| 5:03 | 6.9081 | 0.030843
| 5:03 | 6.9083 | 0.030621
| 5:03 | 6.9086 | 0.030392
| 5:03 | 6.9089 | 0.030158
| 5:03 | 6.9092 | 0.029909
| 5:03 | 6.9094 | 0.029651
| 5:03 | 6.9097 | 0.029376
| 5:03 | 6.91 | 0.029101
| 5:03 | 6.9103 | 0.028819
| 5:03 | 6.9106 | 0.028511
| 5:03 | 6.9108 | 0.028189
| 5:03 | 6.9111 | 0.027866
| 5:03 | 6.9114 | 0.027539
| 5:04 | 6.9117 | 0.027216
| 5:04 | 6.9119 | 0.026894
| 5:04 | 6.9122 | 0.026572
| 5:04 | 6.9125 | 0.026247
| 5:04 | 6.9128 | 0.02592
| 5:04 | 6.9131 | 0.025592
| 5:04 | 6.9133 | 0.025265
| 5:04 | 6.9136 | 0.024951
| 5:04 | 6.9139 | 0.024648
| 5:04 | 6.9142 | 0.024358
| 5:04 | 6.9144 | 0.02408
| 5:04 | 6.9147 | 0.023814
| 5:04 | 6.915 | 0.023561
| 5:04 | 6.9153 | 0.023319
| 5:04 | 6.9156 | 0.023091
| 5:04 | 6.9158 | 0.022878
| 5:04 | 6.9161 | 0.022674
| 5:04 | 6.9164 | 0.022478
| 5:04 | 6.9167 | 0.022293
| 5:04 | 6.9169 | 0.022119
| 5:04 | 6.9172 | 0.021951
| 5:04 | 6.9175 | 0.021786
| 5:04 | 6.9178 | 0.021629
| 5:04 | 6.9181 | 0.021475
| 5:04 | 6.9183 | 0.021317
| 5:04 | 6.9186 | 0.021154
| 5:04 | 6.9189 | 0.020991
| 5:04 | 6.9192 | 0.020817
| 5:04 | 6.9194 | 0.020643
| 5:04 | 6.9197 | 0.020454
| 5:04 | 6.92 | 0.020246
| 5:04 | 6.9203 | 0.020013
| 5:04 | 6.9206 | 0.019777
| 5:04 | 6.9208 | 0.019502
| 5:04 | 6.9211 | 0.019205
| 5:04 | 6.9214 | 0.018904
| 5:04 | 6.9217 | 0.018571
| 5:04 | 6.9219 | 0.018239
| 5:04 | 6.9222 | 0.017892
| 5:04 | 6.9225 | 0.017532
| 5:04 | 6.9228 | 0.017157
| 5:04 | 6.9231 | 0.016768
| 5:04 | 6.9233 | 0.016365
| 5:04 | 6.9236 | 0.015946
| 5:04 | 6.9239 | 0.015512
| 5:04 | 6.9242 | 0.015063
| 5:04 | 6.9244 | 0.014608
| 5:04 | 6.9247 | 0.014149
| 5:04 | 6.925 | 0.013682
| 5:04 | 6.9253 | 0.013206
| 5:04 | 6.9256 | 0.012735
| 5:04 | 6.9258 | 0.012261
| 5:04 | 6.9261 | 0.01178
| 5:04 | 6.9264 | 0.011293
| 5:04 | 6.9267 | 0.010798
| 5:04 | 6.9269 | 0.010305
| 5:04 | 6.9272 | 0.0098161
| 5:04 | 6.9275 | 0.0093255
| 5:04 | 6.9278 | 0.008832
| 5:04 | 6.9281 | 0.0083318
| 5:04 | 6.9283 | 0.0078278
| 5:05 | 6.9286 | 0.0073219
| 5:05 | 6.9289 | 0.0068126
| 5:05 | 6.9292 | 0.0062995
| 5:05 | 6.9294 | 0.0057863
| 5:05 | 6.9297 | 0.0052792
| 5:05 | 6.93 | 0.0047732
| 5:05 | 6.9303 | 0.0042705
| 5:05 | 6.9306 | 0.0037735
| 5:05 | 6.9308 | 0.0032823
| 5:05 | 6.9311 | 0.0027968
| 5:05 | 6.9314 | 0.0023171
| 5:05 | 6.9317 | 0.0018432
| 5:05 | 6.9319 | 0.001375
| 5:05 | 6.9322 | 0.00091254
| 5:05 | 6.9325 | 0.00045533
| 5:05 | 6.9328 | 5.2325e-07
| 5:05 | 6.9331 | -0.00044784
| 5:05 | 6.9333 | -0.0008799
| 5:05 | 6.9336 | -0.0013066
| 5:05 | 6.9339 | -0.001726
| 5:05 | 6.9342 | -0.0021332
| 5:05 | 6.9344 | -0.0025293
| 5:05 | 6.9347 | -0.0029169
| 5:05 | 6.935 | -0.0032826
| 5:05 | 6.9353 | -0.0036381
| 5:05 | 6.9356 | -0.0039849
| 5:05 | 6.9358 | -0.0043332
| 5:05 | 6.9361 | -0.0046756
| 5:05 | 6.9364 | -0.005012
| 5:05 | 6.9367 | -0.0053357
| 5:05 | 6.9369 | -0.005659
| 5:05 | 6.9372 | -0.0059726
| 5:05 | 6.9375 | -0.0062697
| 5:05 | 6.9378 | -0.0065673
| 5:05 | 6.9381 | -0.0068495
| 5:05 | 6.9383 | -0.0071333
| 5:05 | 6.9386 | -0.0074131
| 5:05 | 6.9389 | -0.0076888
| 5:05 | 6.9392 | -0.0079605
| 5:05 | 6.9394 | -0.0082281
| 5:05 | 6.9397 | -0.0084917
| 5:05 | 6.94 | -0.0087512
| 5:05 | 6.9403 | -0.009007
| 5:05 | 6.9406 | -0.0092601
| 5:05 | 6.9408 | -0.009513
| 5:05 | 6.9411 | -0.0097517
| 5:05 | 6.9414 | -0.0099772
| 5:05 | 6.9417 | -0.010205
| 5:05 | 6.9419 | -0.010421
| 5:05 | 6.9422 | -0.010627
| 5:05 | 6.9425 | -0.010828
| 5:05 | 6.9428 | -0.011004
| 5:05 | 6.9431 | -0.01117
| 5:05 | 6.9433 | -0.011323
| 5:05 | 6.9436 | -0.011473
| 5:05 | 6.9439 | -0.011616
| 5:05 | 6.9442 | -0.01175
| 5:05 | 6.9444 | -0.011878
| 5:05 | 6.9447 | -0.012003
| 5:06 | 6.945 | -0.012099
| 5:06 | 6.9453 | -0.012188
| 5:06 | 6.9456 | -0.012275
| 5:06 | 6.9458 | -0.012354
| 5:06 | 6.9461 | -0.012428
| 5:06 | 6.9464 | -0.012486
| 5:06 | 6.9467 | -0.012539
| 5:06 | 6.9469 | -0.012587
| 5:06 | 6.9472 | -0.012633
| 5:06 | 6.9475 | -0.01268
| 5:06 | 6.9478 | -0.012726
| 5:06 | 6.9481 | -0.012772
| 5:06 | 6.9483 | -0.012818
| 5:06 | 6.9486 | -0.012864
| 5:06 | 6.9489 | -0.01291
| 5:06 | 6.9492 | -0.012955
| 5:06 | 6.9494 | -0.013002
| 5:06 | 6.9497 | -0.013051
| 5:06 | 6.95 | -0.013098
| 5:06 | 6.9503 | -0.013145
| 5:06 | 6.9506 | -0.013187
| 5:06 | 6.9508 | -0.013231
| 5:06 | 6.9511 | -0.013283
| 5:06 | 6.9514 | -0.013342
| 5:06 | 6.9517 | -0.013404
| 5:06 | 6.9519 | -0.013466
| 5:06 | 6.9522 | -0.013531
| 5:06 | 6.9525 | -0.013598
| 5:06 | 6.9528 | -0.013662
| 5:06 | 6.9531 | -0.013725
| 5:06 | 6.9533 | -0.013791
| 5:06 | 6.9536 | -0.013859
| 5:06 | 6.9539 | -0.013927
| 5:06 | 6.9542 | -0.013991
| 5:06 | 6.9544 | -0.014054
| 5:06 | 6.9547 | -0.014112
| 5:06 | 6.955 | -0.014171
| 5:06 | 6.9553 | -0.014231
| 5:06 | 6.9556 | -0.014293
| 5:06 | 6.9558 | -0.014357
| 5:06 | 6.9561 | -0.014423
| 5:06 | 6.9564 | -0.01449
| 5:06 | 6.9567 | -0.014559
| 5:06 | 6.9569 | -0.01463
| 5:06 | 6.9572 | -0.014702
| 5:06 | 6.9575 | -0.014778
| 5:06 | 6.9578 | -0.014852
| 5:06 | 6.9581 | -0.01492
| 5:06 | 6.9583 | -0.014987
| 5:06 | 6.9586 | -0.015058
| 5:06 | 6.9589 | -0.015138
| 5:06 | 6.9592 | -0.015234
| 5:06 | 6.9594 | -0.015347
| 5:06 | 6.9597 | -0.015486
| 5:06 | 6.96 | -0.015634
| 5:06 | 6.9603 | -0.015799
| 5:06 | 6.9606 | -0.015985
| 5:06 | 6.9608 | -0.016176
| 5:06 | 6.9611 | -0.016376
| 5:06 | 6.9614 | -0.016595
| 5:06 | 6.9617 | -0.01682
| 5:07 | 6.9619 | -0.017044
| 5:07 | 6.9622 | -0.017267
| 5:07 | 6.9625 | -0.01749
| 5:07 | 6.9628 | -0.017718
| 5:07 | 6.9631 | -0.017953
| 5:07 | 6.9633 | -0.018189
| 5:07 | 6.9636 | -0.018427
| 5:07 | 6.9639 | -0.018667
| 5:07 | 6.9642 | -0.018914
| 5:07 | 6.9644 | -0.019171
| 5:07 | 6.9647 | -0.019437
| 5:07 | 6.965 | -0.019713
| 5:07 | 6.9653 | -0.019998
| 5:07 | 6.9656 | -0.020293
| 5:07 | 6.9658 | -0.020595
| 5:07 | 6.9661 | -0.020903
| 5:07 | 6.9664 | -0.021217
| 5:07 | 6.9667 | -0.021542
| 5:07 | 6.9669 | -0.021883
| 5:07 | 6.9672 | -0.022233
| 5:07 | 6.9675 | -0.022583
| 5:07 | 6.9678 | -0.022931
| 5:07 | 6.9681 | -0.023277
| 5:07 | 6.9683 | -0.023622
| 5:07 | 6.9686 | -0.023959
| 5:07 | 6.9689 | -0.024294
| 5:07 | 6.9692 | -0.024626
| 5:07 | 6.9694 | -0.024944
| 5:07 | 6.9697 | -0.025242
| 5:07 | 6.97 | -0.025514
| 5:07 | 6.9703 | -0.025781
| 5:07 | 6.9706 | -0.026033
| 5:07 | 6.9708 | -0.02628
| 5:07 | 6.9711 | -0.026511
| 5:07 | 6.9714 | -0.026718
| 5:07 | 6.9717 | -0.026919
| 5:07 | 6.9719 | -0.027102
| 5:07 | 6.9722 | -0.027273
| 5:07 | 6.9725 | -0.027433
| 5:07 | 6.9728 | -0.027582
| 5:07 | 6.9731 | -0.027719
| 5:07 | 6.9733 | -0.027844
| 5:07 | 6.9736 | -0.027956
| 5:07 | 6.9739 | -0.028052
| 5:07 | 6.9742 | -0.028145
| 5:07 | 6.9744 | -0.028237
| 5:07 | 6.9747 | -0.028335
| 5:07 | 6.975 | -0.028431
| 5:07 | 6.9753 | -0.028525
| 5:07 | 6.9756 | -0.028617
| 5:07 | 6.9758 | -0.028713
| 5:07 | 6.9761 | -0.028804
| 5:07 | 6.9764 | -0.028898
| 5:07 | 6.9767 | -0.028995
| 5:07 | 6.9769 | -0.029096
| 5:07 | 6.9772 | -0.029193
| 5:07 | 6.9775 | -0.029289
| 5:07 | 6.9778 | -0.029381
| 5:07 | 6.9781 | -0.029472
| 5:08 | 6.9783 | -0.029573
| 5:08 | 6.9786 | -0.029679
| 5:08 | 6.9789 | -0.029783
| 5:08 | 6.9792 | -0.029888
| 5:08 | 6.9794 | -0.029992
| 5:08 | 6.9797 | -0.0301
| 5:08 | 6.98 | -0.0299
| 5:08 | 6.9803 | -0.029738
| 5:08 | 6.9806 | -0.029598
| 5:08 | 6.9808 | -0.029484
| 5:08 | 6.9811 | -0.029397
| 5:08 | 6.9814 | -0.029336
| 5:08 | 6.9817 | -0.029303
| 5:08 | 6.9819 | -0.029296
| 5:08 | 6.9822 | -0.029315
| 5:08 | 6.9825 | -0.029361
| 5:08 | 6.9828 | -0.029434
| 5:08 | 6.9831 | -0.029534
| 5:08 | 6.9833 | -0.029654
| 5:08 | 6.9836 | -0.029782
| 5:08 | 6.9839 | -0.029919
| 5:08 | 6.9842 | -0.030066
| 5:08 | 6.9844 | -0.030215
| 5:08 | 6.9847 | -0.030366
| 5:08 | 6.985 | -0.03052
| 5:08 | 6.9853 | -0.030675
| 5:08 | 6.9856 | -0.030832
| 5:08 | 6.9858 | -0.030986
| 5:08 | 6.9861 | -0.031138
| 5:08 | 6.9864 | -0.031287
| 5:08 | 6.9867 | -0.031434
| 5:08 | 6.9869 | -0.031578
| 5:08 | 6.9872 | -0.03172
| 5:08 | 6.9875 | -0.031859
| 5:08 | 6.9878 | -0.031996
| 5:08 | 6.9881 | -0.03213
| 5:08 | 6.9883 | -0.032263
| 5:08 | 6.9886 | -0.032393
| 5:08 | 6.9889 | -0.03252
| 5:08 | 6.9892 | -0.032645
| 5:08 | 6.9894 | -0.032767
| 5:08 | 6.9897 | -0.032887
| 5:08 | 6.99 | -0.033003
| 5:08 | 6.9903 | -0.033117
| 5:08 | 6.9906 | -0.033228
| 5:08 | 6.9908 | -0.033336
| 5:08 | 6.9911 | -0.033442
| 5:08 | 6.9914 | -0.033535
| 5:08 | 6.9917 | -0.03363
| 5:08 | 6.9919 | -0.033726
| 5:08 | 6.9922 | -0.033823
| 5:08 | 6.9925 | -0.033921
| 5:08 | 6.9928 | -0.03403
| 5:08 | 6.9931 | -0.034143
| 5:08 | 6.9933 | -0.03426
| 5:08 | 6.9936 | -0.034382
| 5:08 | 6.9939 | -0.034508
| 5:08 | 6.9942 | -0.034635
| 5:08 | 6.9944 | -0.034763
| 5:08 | 6.9947 | -0.034892
| 5:08 | 6.995 | -0.03502
| 5:09 | 6.9953 | -0.03515
| 5:09 | 6.9956 | -0.035279
| 5:09 | 6.9958 | -0.03541
| 5:09 | 6.9961 | -0.03554
| 5:09 | 6.9964 | -0.035671
| 5:09 | 6.9967 | -0.035803
| 5:09 | 6.9969 | -0.035936
| 5:09 | 6.9972 | -0.036062
| 5:09 | 6.9975 | -0.036176
| 5:09 | 6.9978 | -0.036278
| 5:09 | 6.9981 | -0.03637
| 5:09 | 6.9983 | -0.03645
| 5:09 | 6.9986 | -0.036519
| 5:09 | 6.9989 | -0.036577
| 5:09 | 6.9992 | -0.036624
| 5:09 | 6.9994 | -0.036659
| 5:09 | 6.9997 | -0.036685
| 5:09 | 7 | -0.03671
| 5:09 | 7.0003 | -0.03672
| 5:09 | 7.0006 | -0.036714
| 5:09 | 7.0008 | -0.036704
| 5:09 | 7.0011 | -0.036699
| 5:09 | 7.0014 | -0.036677
| 5:09 | 7.0017 | -0.036648
| 5:09 | 7.0019 | -0.036615
| 5:09 | 7.0022 | -0.036579
| 5:09 | 7.0025 | -0.036564
| 5:09 | 7.0028 | -0.03655
| 5:09 | 7.0031 | -0.036529
| 5:09 | 7.0033 | -0.03651
| 5:09 | 7.0036 | -0.036489
| 5:09 | 7.0039 | -0.03642
| 5:09 | 7.0042 | -0.036325
| 5:09 | 7.0044 | -0.036224
| 5:09 | 7.0047 | -0.036093
| 5:09 | 7.005 | -0.035932
| 5:09 | 7.0053 | -0.035728
| 5:09 | 7.0056 | -0.035506
| 5:09 | 7.0058 | -0.035265
| 5:09 | 7.0061 | -0.035006
| 5:09 | 7.0064 | -0.034728
| 5:09 | 7.0067 | -0.034431
| 5:09 | 7.0069 | -0.034115
| 5:09 | 7.0072 | -0.033781
| 5:09 | 7.0075 | -0.033443
| 5:09 | 7.0078 | -0.033059
| 5:09 | 7.0081 | -0.032663
| 5:09 | 7.0083 | -0.032253
| 5:09 | 7.0086 | -0.031831
| 5:09 | 7.0089 | -0.031396
| 5:09 | 7.0092 | -0.030937
| 5:09 | 7.0094 | -0.030467
| 5:09 | 7.0097 | -0.029984
| 5:09 | 7.01 | -0.02949
| 5:09 | 7.0103 | -0.028979
| 5:09 | 7.0106 | -0.028463
| 5:09 | 7.0108 | -0.027941
| 5:09 | 7.0111 | -0.027414
| 5:09 | 7.0114 | -0.026884
| 5:10 | 7.0117 | -0.026354
| 5:10 | 7.0119 | -0.025823
| 5:10 | 7.0122 | -0.025292
| 5:10 | 7.0125 | -0.024761
| 5:10 | 7.0128 | -0.02423
| 5:10 | 7.0131 | -0.023699
| 5:10 | 7.0133 | -0.023168
| 5:10 | 7.0136 | -0.022638
| 5:10 | 7.0139 | -0.022108
| 5:10 | 7.0142 | -0.021577
| 5:10 | 7.0144 | -0.021047
| 5:10 | 7.0147 | -0.020518
| 5:10 | 7.015 | -0.019988
| 5:10 | 7.0153 | -0.019458
| 5:10 | 7.0156 | -0.018929
| 5:10 | 7.0158 | -0.0184
| 5:10 | 7.0161 | -0.017871
| 5:10 | 7.0164 | -0.017342
| 5:10 | 7.0167 | -0.016813
| 5:10 | 7.0169 | -0.016284
| 5:10 | 7.0172 | -0.015756
| 5:10 | 7.0175 | -0.015228
| 5:10 | 7.0178 | -0.014699
| 5:10 | 7.0181 | -0.014171
| 5:10 | 7.0183 | -0.013644
| 5:10 | 7.0186 | -0.013116
| 5:10 | 7.0189 | -0.012588
| 5:10 | 7.0192 | -0.012061
| 5:10 | 7.0194 | -0.011534
| 5:10 | 7.0197 | -0.011011
| 5:10 | 7.02 | -0.010497
| 5:10 | 7.0203 | -0.0099918
| 5:10 | 7.0206 | -0.0094961
| 5:10 | 7.0208 | -0.0090007
| 5:10 | 7.0211 | -0.0085049
| 5:10 | 7.0214 | -0.0080088
| 5:10 | 7.0217 | -0.0075123
| 5:10 | 7.0219 | -0.0070155
| 5:10 | 7.0222 | -0.0065159
| 5:10 | 7.0225 | -0.0060134
| 5:10 | 7.0228 | -0.0055079
| 5:10 | 7.0231 | -0.0049995
| 5:10 | 7.0233 | -0.0044882
| 5:10 | 7.0236 | -0.0039739
| 5:10 | 7.0239 | -0.0034567
| 5:10 | 7.0242 | -0.0029365
| 5:10 | 7.0244 | -0.0024134
| 5:10 | 7.0247 | -0.0018874
| 5:10 | 7.025 | -0.0013584
| 5:10 | 7.0253 | -0.00082705
| 5:10 | 7.0256 | -0.00029667
| 5:10 | 7.0258 | 0.00023239
| 5:10 | 7.0261 | 0.00076011
| 5:10 | 7.0264 | 0.0012865
| 5:10 | 7.0267 | 0.0018116
| 5:10 | 7.0269 | 0.0023353
| 5:10 | 7.0272 | 0.0028577
| 5:10 | 7.0275 | 0.0033705
| 5:10 | 7.0278 | 0.0038768
| 5:10 | 7.0281 | 0.0043697
| 5:10 | 7.0283 | 0.0048557
| 5:11 | 7.0286 | 0.0053372
| 5:11 | 7.0289 | 0.005809
| 5:11 | 7.0292 | 0.0062667
| 5:11 | 7.0294 | 0.0067161
| 5:11 | 7.0297 | 0.0071604
| 5:11 | 7.03 | 0.0075994
| 5:11 | 7.0303 | 0.0080361
| 5:11 | 7.0306 | 0.0084752
| 5:11 | 7.0308 | 0.0089169
| 5:11 | 7.0311 | 0.009361
| 5:11 | 7.0314 | 0.0098076
| 5:11 | 7.0317 | 0.010257
| 5:11 | 7.0319 | 0.010708
| 5:11 | 7.0322 | 0.011162
| 5:11 | 7.0325 | 0.011619
| 5:11 | 7.0328 | 0.012078
| 5:11 | 7.0331 | 0.012539
| 5:11 | 7.0333 | 0.013007
| 5:11 | 7.0336 | 0.013488
| 5:11 | 7.0339 | 0.013977
| 5:11 | 7.0342 | 0.014472
| 5:11 | 7.0344 | 0.014975
| 5:11 | 7.0347 | 0.015485
| 5:11 | 7.035 | 0.016001
| 5:11 | 7.0353 | 0.016521
| 5:11 | 7.0356 | 0.017041
| 5:11 | 7.0358 | 0.017564
| 5:11 | 7.0361 | 0.018088
| 5:11 | 7.0364 | 0.018613
| 5:11 | 7.0367 | 0.01914
| 5:11 | 7.0369 | 0.019672
| 5:11 | 7.0372 | 0.020207
| 5:11 | 7.0375 | 0.020741
| 5:11 | 7.0378 | 0.021275
| 5:11 | 7.0381 | 0.021808
| 5:11 | 7.0383 | 0.022342
| 5:11 | 7.0386 | 0.022875
| 5:11 | 7.0389 | 0.023407
| 5:11 | 7.0392 | 0.02394
| 5:11 | 7.0394 | 0.024472
| 5:11 | 7.0397 | 0.025003
| 5:11 | 7.04 | 0.025535
| 5:11 | 7.0403 | 0.026066
| 5:11 | 7.0406 | 0.026597
| 5:11 | 7.0408 | 0.027128
| 5:11 | 7.0411 | 0.027658
| 5:11 | 7.0414 | 0.028188
| 5:11 | 7.0417 | 0.028718
| 5:11 | 7.0419 | 0.029247
| 5:11 | 7.0422 | 0.029776
| 5:11 | 7.0425 | 0.030305
| 5:11 | 7.0428 | 0.030833
| 5:11 | 7.0431 | 0.031362
| 5:11 | 7.0433 | 0.03189
| 5:11 | 7.0436 | 0.032417
| 5:11 | 7.0439 | 0.032944
| 5:11 | 7.0442 | 0.033472
| 5:11 | 7.0444 | 0.033998
| 5:11 | 7.0447 | 0.034525
| 5:12 | 7.045 | 0.035051
| 5:12 | 7.0453 | 0.035577
| 5:12 | 7.0456 | 0.036102
| 5:12 | 7.0458 | 0.036627
| 5:12 | 7.0461 | 0.037152
| 5:12 | 7.0464 | 0.037677
| 5:12 | 7.0467 | 0.038201
| 5:12 | 7.0469 | 0.038726
| 5:12 | 7.0472 | 0.039249
| 5:12 | 7.0475 | 0.039773
| 5:12 | 7.0478 | 0.040296
| 5:12 | 7.0481 | 0.040819
| 5:12 | 7.0483 | 0.041342
| 5:12 | 7.0486 | 0.041864
| 5:12 | 7.0489 | 0.042386
| 5:12 | 7.0492 | 0.042908
| 5:12 | 7.0494 | 0.043429
| 5:12 | 7.0497 | 0.04395
| 5:12 | 7.05 | 0.044471
| 5:12 | 7.0503 | 0.044992
| 5:12 | 7.0506 | 0.045512
| 5:12 | 7.0508 | 0.046032
| 5:12 | 7.0511 | 0.046552
| 5:12 | 7.0514 | 0.047072
| 5:12 | 7.0517 | 0.047586
| 5:12 | 7.0519 | 0.048099
| 5:12 | 7.0522 | 0.048611
| 5:12 | 7.0525 | 0.049122
| 5:12 | 7.0528 | 0.049632
| 5:12 | 7.0531 | 0.050142
| 5:12 | 7.0533 | 0.05065
| 5:12 | 7.0536 | 0.051158
| 5:12 | 7.0539 | 0.051664
| 5:12 | 7.0542 | 0.05217
| 5:12 | 7.0544 | 0.052674
| 5:12 | 7.0547 | 0.053178
| 5:12 | 7.055 | 0.05368
| 5:12 | 7.0553 | 0.054182
| 5:12 | 7.0556 | 0.054677
| 5:12 | 7.0558 | 0.055166
| 5:12 | 7.0561 | 0.055647
| 5:12 | 7.0564 | 0.056121
| 5:12 | 7.0567 | 0.056588
| 5:12 | 7.0569 | 0.057048
| 5:12 | 7.0572 | 0.057501
| 5:12 | 7.0575 | 0.057948
| 5:12 | 7.0578 | 0.058386
| 5:12 | 7.0581 | 0.058809
| 5:12 | 7.0583 | 0.059211
| 5:12 | 7.0586 | 0.059594
| 5:12 | 7.0589 | 0.059961
| 5:12 | 7.0592 | 0.060306
| 5:12 | 7.0594 | 0.060636
| 5:12 | 7.0597 | 0.060944
| 5:12 | 7.06 | 0.061232
| 5:12 | 7.0603 | 0.061505
| 5:12 | 7.0606 | 0.061762
| 5:12 | 7.0608 | 0.062007
| 5:12 | 7.0611 | 0.062244
| 5:12 | 7.0614 | 0.062477
| 5:12 | 7.0617 | 0.06271
| 5:13 | 7.0619 | 0.062945
| 5:13 | 7.0622 | 0.063181
| 5:13 | 7.0625 | 0.063418
| 5:13 | 7.0628 | 0.063656
| 5:13 | 7.0631 | 0.063895
| 5:13 | 7.0633 | 0.064139
| 5:13 | 7.0636 | 0.064393
| 5:13 | 7.0639 | 0.064657
| 5:13 | 7.0642 | 0.064931
| 5:13 | 7.0644 | 0.065216
| 5:13 | 7.0647 | 0.065512
| 5:13 | 7.065 | 0.065818
| 5:13 | 7.0653 | 0.066134
| 5:13 | 7.0656 | 0.06646
| 5:13 | 7.0658 | 0.066798
| 5:13 | 7.0661 | 0.067145
| 5:13 | 7.0664 | 0.067503
| 5:13 | 7.0667 | 0.067862
| 5:13 | 7.0669 | 0.068221
| 5:13 | 7.0672 | 0.068579
| 5:13 | 7.0675 | 0.068936
| 5:13 | 7.0678 | 0.069293
| 5:13 | 7.0681 | 0.069643
| 5:13 | 7.0683 | 0.069989
| 5:13 | 7.0686 | 0.07031
| 5:13 | 7.0689 | 0.070608
| 5:13 | 7.0692 | 0.070902
| 5:13 | 7.0694 | 0.071178
| 5:13 | 7.0697 | 0.07143
| 5:13 | 7.07 | 0.071632
| 5:13 | 7.0703 | 0.071806
| 5:13 | 7.0706 | 0.071954
| 5:13 | 7.0708 | 0.072081
| 5:13 | 7.0711 | 0.072196
| 5:13 | 7.0714 | 0.072273
| 5:13 | 7.0717 | 0.072338
| 5:13 | 7.0719 | 0.072395
| 5:13 | 7.0722 | 0.072439
| 5:13 | 7.0725 | 0.072471
| 5:13 | 7.0728 | 0.072492
| 5:13 | 7.0731 | 0.072501
| 5:13 | 7.0733 | 0.072497
| 5:13 | 7.0736 | 0.072482
| 5:13 | 7.0739 | 0.072455
| 5:13 | 7.0742 | 0.072418
| 5:13 | 7.0744 | 0.072378
| 5:13 | 7.0747 | 0.072333
| 5:13 | 7.075 | 0.072285
| 5:13 | 7.0753 | 0.072232
| 5:13 | 7.0756 | 0.072177
| 5:13 | 7.0758 | 0.072123
| 5:13 | 7.0761 | 0.072069
| 5:13 | 7.0764 | 0.072016
| 5:13 | 7.0767 | 0.071964
| 5:13 | 7.0769 | 0.071913
| 5:13 | 7.0772 | 0.071862
| 5:13 | 7.0775 | 0.071812
| 5:13 | 7.0778 | 0.071763
| 5:13 | 7.0781 | 0.071715
| 5:14 | 7.0783 | 0.071668
| 5:14 | 7.0786 | 0.071621
| 5:14 | 7.0789 | 0.071582
| 5:14 | 7.0792 | 0.071554
| 5:14 | 7.0794 | 0.071537
| 5:14 | 7.0797 | 0.071531
| 5:14 | 7.08 | 0.071539
| 5:14 | 7.0803 | 0.071545
| 5:14 | 7.0806 | 0.071549
| 5:14 | 7.0808 | 0.071551
| 5:14 | 7.0811 | 0.071552
| 5:14 | 7.0814 | 0.071551
| 5:14 | 7.0817 | 0.071549
| 5:14 | 7.0819 | 0.071545
| 5:14 | 7.0822 | 0.071539
| 5:14 | 7.0825 | 0.071531
| 5:14 | 7.0828 | 0.071522
| 5:14 | 7.0831 | 0.071511
| 5:14 | 7.0833 | 0.071504
| 5:14 | 7.0836 | 0.071502
| 5:14 | 7.0839 | 0.071506
| 5:14 | 7.0842 | 0.071516
| 5:14 | 7.0844 | 0.071533
| 5:14 | 7.0847 | 0.071563
| 5:14 | 7.085 | 0.071609
| 5:14 | 7.0853 | 0.071672
| 5:14 | 7.0856 | 0.071752
| 5:14 | 7.0858 | 0.07184
| 5:14 | 7.0861 | 0.071934
| 5:14 | 7.0864 | 0.072037
| 5:14 | 7.0867 | 0.07215
| 5:14 | 7.0869 | 0.072265
| 5:14 | 7.0872 | 0.07238
| 5:14 | 7.0875 | 0.072497
| 5:14 | 7.0878 | 0.072615
| 5:14 | 7.0881 | 0.072721
| 5:14 | 7.0883 | 0.072824
| 5:14 | 7.0886 | 0.072918
| 5:14 | 7.0889 | 0.072993
| 5:14 | 7.0892 | 0.073055
| 5:14 | 7.0894 | 0.073103
| 5:14 | 7.0897 | 0.073139
| 5:14 | 7.09 | 0.073161
| 5:14 | 7.0903 | 0.073169
| 5:14 | 7.0906 | 0.073165
| 5:14 | 7.0908 | 0.073147
| 5:14 | 7.0911 | 0.073122
| 5:14 | 7.0914 | 0.073102
| 5:14 | 7.0917 | 0.073086
| 5:14 | 7.0919 | 0.073079
| 5:14 | 7.0922 | 0.073081
| 5:14 | 7.0925 | 0.073098
| 5:14 | 7.0928 | 0.073132
| 5:14 | 7.0931 | 0.073175
| 5:14 | 7.0933 | 0.07323
| 5:14 | 7.0936 | 0.073293
| 5:14 | 7.0939 | 0.073368
| 5:14 | 7.0942 | 0.073445
| 5:14 | 7.0944 | 0.073525
| 5:14 | 7.0947 | 0.073607
| 5:14 | 7.095 | 0.073691
| 5:15 | 7.0953 | 0.073783
| 5:15 | 7.0956 | 0.073881
| 5:15 | 7.0958 | 0.073994
| 5:15 | 7.0961 | 0.074116
| 5:15 | 7.0964 | 0.074261
| 5:15 | 7.0967 | 0.074426
| 5:15 | 7.0969 | 0.074602
| 5:15 | 7.0972 | 0.074796
| 5:15 | 7.0975 | 0.075008
| 5:15 | 7.0978 | 0.075238
| 5:15 | 7.0981 | 0.075486
| 5:15 | 7.0983 | 0.075753
| 5:15 | 7.0986 | 0.076037
| 5:15 | 7.0989 | 0.076339
| 5:15 | 7.0992 | 0.07666
| 5:15 | 7.0994 | 0.076998
| 5:15 | 7.0997 | 0.077354
| 5:15 | 7.1 | 0.077708
| 5:15 | 7.1003 | 0.078062
| 5:15 | 7.1006 | 0.078415
| 5:15 | 7.1008 | 0.078767
| 5:15 | 7.1011 | 0.079118
| 5:15 | 7.1014 | 0.079469
| 5:15 | 7.1017 | 0.079818
| 5:15 | 7.1019 | 0.080166
| 5:15 | 7.1022 | 0.080514
| 5:15 | 7.1025 | 0.08086
| 5:15 | 7.1028 | 0.081206
| 5:15 | 7.1031 | 0.081551
| 5:15 | 7.1033 | 0.081895
| 5:15 | 7.1036 | 0.082236
| 5:15 | 7.1039 | 0.082572
| 5:15 | 7.1042 | 0.082891
| 5:15 | 7.1044 | 0.083207
| 5:15 | 7.1047 | 0.083519
| 5:15 | 7.105 | 0.083814
| 5:15 | 7.1053 | 0.084094
| 5:15 | 7.1056 | 0.084357
| 5:15 | 7.1058 | 0.084605
| 5:15 | 7.1061 | 0.084836
| 5:15 | 7.1064 | 0.085051
| 5:15 | 7.1067 | 0.08525
| 5:15 | 7.1069 | 0.085433
| 5:15 | 7.1072 | 0.085599
| 5:15 | 7.1075 | 0.085759
| 5:15 | 7.1078 | 0.085913
| 5:15 | 7.1081 | 0.08605
| 5:15 | 7.1083 | 0.086179
| 5:15 | 7.1086 | 0.086303
| 5:15 | 7.1089 | 0.086425
| 5:15 | 7.1092 | 0.086546
| 5:15 | 7.1094 | 0.086666
| 5:15 | 7.1097 | 0.086784
| 5:15 | 7.11 | 0.086901
| 5:15 | 7.1103 | 0.087017
| 5:15 | 7.1106 | 0.087131
| 5:15 | 7.1108 | 0.087245
| 5:15 | 7.1111 | 0.087356
| 5:15 | 7.1114 | 0.087467
| 5:16 | 7.1117 | 0.087572
| 5:16 | 7.1119 | 0.087664
| 5:16 | 7.1122 | 0.087746
| 5:16 | 7.1125 | 0.087818
| 5:16 | 7.1128 | 0.087881
| 5:16 | 7.1131 | 0.087923
| 5:16 | 7.1133 | 0.087955
| 5:16 | 7.1136 | 0.087982
| 5:16 | 7.1139 | 0.088007
| 5:16 | 7.1142 | 0.088032
| 5:16 | 7.1144 | 0.088056
| 5:16 | 7.1147 | 0.088079
| 5:16 | 7.115 | 0.088102
| 5:16 | 7.1153 | 0.088123
| 5:16 | 7.1156 | 0.088143
| 5:16 | 7.1158 | 0.088163
| 5:16 | 7.1161 | 0.088181
| 5:16 | 7.1164 | 0.088199
| 5:16 | 7.1167 | 0.088233
| 5:16 | 7.1169 | 0.088293
| 5:16 | 7.1172 | 0.088362
| 5:16 | 7.1175 | 0.088434
| 5:16 | 7.1178 | 0.088519
| 5:16 | 7.1181 | 0.088616
| 5:16 | 7.1183 | 0.088725
| 5:16 | 7.1186 | 0.088846
| 5:16 | 7.1189 | 0.08898
| 5:16 | 7.1192 | 0.089128
| 5:16 | 7.1194 | 0.089278
| 5:16 | 7.1197 | 0.089426
| 5:16 | 7.12 | 0.089572
| 5:16 | 7.1203 | 0.089716
| 5:16 | 7.1206 | 0.089857
| 5:16 | 7.1208 | 0.089996
| 5:16 | 7.1211 | 0.090131
| 5:16 | 7.1214 | 0.09026
| 5:16 | 7.1217 | 0.090388
| 5:16 | 7.1219 | 0.090504
| 5:16 | 7.1222 | 0.090615
| 5:16 | 7.1225 | 0.09072
| 5:16 | 7.1228 | 0.09082
| 5:16 | 7.1231 | 0.090915
| 5:16 | 7.1233 | 0.091003
| 5:16 | 7.1236 | 0.091087
| 5:16 | 7.1239 | 0.091165
| 5:16 | 7.1242 | 0.091238
| 5:16 | 7.1244 | 0.091308
| 5:16 | 7.1247 | 0.091373
| 5:16 | 7.125 | 0.091434
| 5:16 | 7.1253 | 0.091488
| 5:16 | 7.1256 | 0.091534
| 5:16 | 7.1258 | 0.091575
| 5:16 | 7.1261 | 0.091612
| 5:16 | 7.1264 | 0.091645
| 5:16 | 7.1267 | 0.091674
| 5:16 | 7.1269 | 0.091699
| 5:16 | 7.1272 | 0.091719
| 5:16 | 7.1275 | 0.091735
| 5:16 | 7.1278 | 0.091747
| 5:16 | 7.1281 | 0.091755
| 5:16 | 7.1283 | 0.091761
| 5:17 | 7.1286 | 0.091767
| 5:17 | 7.1289 | 0.091775
| 5:17 | 7.1292 | 0.091784
| 5:17 | 7.1294 | 0.091794
| 5:17 | 7.1297 | 0.091805
| 5:17 | 7.13 | 0.091817
| 5:17 | 7.1303 | 0.091827
| 5:17 | 7.1306 | 0.091831
| 5:17 | 7.1308 | 0.091829
| 5:17 | 7.1311 | 0.09182
| 5:17 | 7.1314 | 0.091805
| 5:17 | 7.1317 | 0.091783
| 5:17 | 7.1319 | 0.091755
| 5:17 | 7.1322 | 0.091721
| 5:17 | 7.1325 | 0.09168
| 5:17 | 7.1328 | 0.091633
| 5:17 | 7.1331 | 0.091582
| 5:17 | 7.1333 | 0.091533
| 5:17 | 7.1336 | 0.091486
| 5:17 | 7.1339 | 0.091442
| 5:17 | 7.1342 | 0.091399
| 5:17 | 7.1344 | 0.091358
| 5:17 | 7.1347 | 0.091319
| 5:17 | 7.135 | 0.091288
| 5:17 | 7.1353 | 0.091274
| 5:17 | 7.1356 | 0.091287
| 5:17 | 7.1358 | 0.091334
| 5:17 | 7.1361 | 0.091387
| 5:17 | 7.1364 | 0.09147
| 5:17 | 7.1367 | 0.091582
| 5:17 | 7.1369 | 0.091721
| 5:17 | 7.1372 | 0.091884
| 5:17 | 7.1375 | 0.092072
| 5:17 | 7.1378 | 0.092286
| 5:17 | 7.1381 | 0.0925
| 5:17 | 7.1383 | 0.092769
| 5:17 | 7.1386 | 0.093044
| 5:17 | 7.1389 | 0.093341
| 5:17 | 7.1392 | 0.09366
| 5:17 | 7.1394 | 0.093999
| 5:17 | 7.1397 | 0.094361
| 5:17 | 7.14 | 0.094743
| 5:17 | 7.1403 | 0.095147
| 5:17 | 7.1406 | 0.095573
| 5:17 | 7.1408 | 0.09601
| 5:17 | 7.1411 | 0.096458
| 5:17 | 7.1414 | 0.096909
| 5:17 | 7.1417 | 0.097362
| 5:17 | 7.1419 | 0.097816
| 5:17 | 7.1422 | 0.098273
| 5:17 | 7.1425 | 0.098731
| 5:17 | 7.1428 | 0.099192
| 5:17 | 7.1431 | 0.099654
| 5:17 | 7.1433 | 0.10012
| 5:17 | 7.1436 | 0.10058
| 5:17 | 7.1439 | 0.10104
| 5:17 | 7.1442 | 0.10151
| 5:17 | 7.1444 | 0.10197
| 5:17 | 7.1447 | 0.10243
| 5:18 | 7.145 | 0.10289
| 5:18 | 7.1453 | 0.10336
| 5:18 | 7.1456 | 0.10382
| 5:18 | 7.1458 | 0.10429
| 5:18 | 7.1461 | 0.10476
| 5:18 | 7.1464 | 0.10524
| 5:18 | 7.1467 | 0.10572
| 5:18 | 7.1469 | 0.1062
| 5:18 | 7.1472 | 0.10667
| 5:18 | 7.1475 | 0.10714
| 5:18 | 7.1478 | 0.10761
| 5:18 | 7.1481 | 0.10807
| 5:18 | 7.1483 | 0.10853
| 5:18 | 7.1486 | 0.10898
| 5:18 | 7.1489 | 0.10944
| 5:18 | 7.1492 | 0.10989
| 5:18 | 7.1494 | 0.11033
| 5:18 | 7.1497 | 0.11077
| 5:18 | 7.15 | 0.1112
| 5:18 | 7.1503 | 0.11162
| 5:18 | 7.1506 | 0.112
| 5:18 | 7.1508 | 0.11236
| 5:18 | 7.1511 | 0.11272
| 5:18 | 7.1514 | 0.11306
| 5:18 | 7.1517 | 0.11336
| 5:18 | 7.1519 | 0.11365
| 5:18 | 7.1522 | 0.11391
| 5:18 | 7.1525 | 0.11416
| 5:18 | 7.1528 | 0.11441
| 5:18 | 7.1531 | 0.11465
| 5:18 | 7.1533 | 0.1149
| 5:18 | 7.1536 | 0.11514
| 5:18 | 7.1539 | 0.11538
| 5:18 | 7.1542 | 0.11562
| 5:18 | 7.1544 | 0.11586
| 5:18 | 7.1547 | 0.11609
| 5:18 | 7.155 | 0.11631
| 5:18 | 7.1553 | 0.11652
| 5:18 | 7.1556 | 0.11673
| 5:18 | 7.1558 | 0.11693
| 5:18 | 7.1561 | 0.11711
| 5:18 | 7.1564 | 0.11729
| 5:18 | 7.1567 | 0.11746
| 5:18 | 7.1569 | 0.11761
| 5:18 | 7.1572 | 0.11776
| 5:18 | 7.1575 | 0.11789
| 5:18 | 7.1578 | 0.11802
| 5:18 | 7.1581 | 0.11814
| 5:18 | 7.1583 | 0.11826
| 5:18 | 7.1586 | 0.11839
| 5:18 | 7.1589 | 0.11852
| 5:18 | 7.1592 | 0.11866
| 5:18 | 7.1594 | 0.11881
| 5:18 | 7.1597 | 0.11897
| 5:18 | 7.16 | 0.11914
| 5:18 | 7.1603 | 0.1193
| 5:18 | 7.1606 | 0.11949
| 5:18 | 7.1608 | 0.1197
| 5:18 | 7.1611 | 0.11991
| 5:18 | 7.1614 | 0.12013
| 5:18 | 7.1617 | 0.12035
| 5:19 | 7.1619 | 0.12057
| 5:19 | 7.1622 | 0.1208
| 5:19 | 7.1625 | 0.12103
| 5:19 | 7.1628 | 0.12125
| 5:19 | 7.1631 | 0.12148
| 5:19 | 7.1633 | 0.1217
| 5:19 | 7.1636 | 0.12191
| 5:19 | 7.1639 | 0.12211
| 5:19 | 7.1642 | 0.1223
| 5:19 | 7.1644 | 0.12247
| 5:19 | 7.1647 | 0.12264
| 5:19 | 7.165 | 0.12279
| 5:19 | 7.1653 | 0.12293
| 5:19 | 7.1656 | 0.12305
| 5:19 | 7.1658 | 0.12317
| 5:19 | 7.1661 | 0.12327
| 5:19 | 7.1664 | 0.12336
| 5:19 | 7.1667 | 0.12344
| 5:19 | 7.1669 | 0.12351
| 5:19 | 7.1672 | 0.12356
| 5:19 | 7.1675 | 0.12362
| 5:19 | 7.1678 | 0.12367
| 5:19 | 7.1681 | 0.1237
| 5:19 | 7.1683 | 0.12374
| 5:19 | 7.1686 | 0.12379
| 5:19 | 7.1689 | 0.12384
| 5:19 | 7.1692 | 0.1239
| 5:19 | 7.1694 | 0.12398
| 5:19 | 7.1697 | 0.12407
| 5:19 | 7.17 | 0.12419
| 5:19 | 7.1703 | 0.12432
| 5:19 | 7.1706 | 0.12445
| 5:19 | 7.1708 | 0.12462
| 5:19 | 7.1711 | 0.12481
| 5:19 | 7.1714 | 0.125
| 5:19 | 7.1717 | 0.12523
| 5:19 | 7.1719 | 0.12546
| 5:19 | 7.1722 | 0.1257
| 5:19 | 7.1725 | 0.12596
| 5:19 | 7.1728 | 0.12623
| 5:19 | 7.1731 | 0.12652
| 5:19 | 7.1733 | 0.12682
| 5:19 | 7.1736 | 0.12714
| 5:19 | 7.1739 | 0.12748
| 5:19 | 7.1742 | 0.12782
| 5:19 | 7.1744 | 0.12817
| 5:19 | 7.1747 | 0.12852
| 5:19 | 7.175 | 0.12887
| 5:19 | 7.1753 | 0.12923
| 5:19 | 7.1756 | 0.12959
| 5:19 | 7.1758 | 0.12994
| 5:19 | 7.1761 | 0.13031
| 5:19 | 7.1764 | 0.13067
| 5:19 | 7.1767 | 0.13106
| 5:19 | 7.1769 | 0.13144
| 5:19 | 7.1772 | 0.13183
| 5:19 | 7.1775 | 0.13222
| 5:19 | 7.1778 | 0.13262
| 5:19 | 7.1781 | 0.13302
| 5:20 | 7.1783 | 0.13341
| 5:20 | 7.1786 | 0.13381
| 5:20 | 7.1789 | 0.13421
| 5:20 | 7.1792 | 0.13461
| 5:20 | 7.1794 | 0.13501
| 5:20 | 7.1797 | 0.1354
| 5:20 | 7.18 | 0.13578
| 5:20 | 7.1803 | 0.13615
| 5:20 | 7.1806 | 0.13653
| 5:20 | 7.1808 | 0.1369
| 5:20 | 7.1811 | 0.13726
| 5:20 | 7.1814 | 0.13763
| 5:20 | 7.1817 | 0.13799
| 5:20 | 7.1819 | 0.13835
| 5:20 | 7.1822 | 0.1387
| 5:20 | 7.1825 | 0.13905
| 5:20 | 7.1828 | 0.1394
| 5:20 | 7.1831 | 0.13974
| 5:20 | 7.1833 | 0.14006
| 5:20 | 7.1836 | 0.14037
| 5:20 | 7.1839 | 0.14066
| 5:20 | 7.1842 | 0.14094
| 5:20 | 7.1844 | 0.14121
| 5:20 | 7.1847 | 0.14148
| 5:20 | 7.185 | 0.14174
| 5:20 | 7.1853 | 0.142
| 5:20 | 7.1856 | 0.14224
| 5:20 | 7.1858 | 0.14248
| 5:20 | 7.1861 | 0.14271
| 5:20 | 7.1864 | 0.14293
| 5:20 | 7.1867 | 0.14314
| 5:20 | 7.1869 | 0.14334
| 5:20 | 7.1872 | 0.14354
| 5:20 | 7.1875 | 0.14371
| 5:20 | 7.1878 | 0.14388
| 5:20 | 7.1881 | 0.14404
| 5:20 | 7.1883 | 0.14419
| 5:20 | 7.1886 | 0.14434
| 5:20 | 7.1889 | 0.1445
| 5:20 | 7.1892 | 0.14464
| 5:20 | 7.1894 | 0.14479
| 5:20 | 7.1897 | 0.14494
| 5:20 | 7.19 | 0.14508
| 5:20 | 7.1903 | 0.14522
| 5:20 | 7.1906 | 0.14536
| 5:20 | 7.1908 | 0.1455
| 5:20 | 7.1911 | 0.14562
| 5:20 | 7.1914 | 0.14572
| 5:20 | 7.1917 | 0.14582
| 5:20 | 7.1919 | 0.1459
| 5:20 | 7.1922 | 0.14597
| 5:20 | 7.1925 | 0.14605
| 5:20 | 7.1928 | 0.14611
| 5:20 | 7.1931 | 0.14617
| 5:20 | 7.1933 | 0.14621
| 5:20 | 7.1936 | 0.14625
| 5:20 | 7.1939 | 0.14628
| 5:20 | 7.1942 | 0.14629
| 5:20 | 7.1944 | 0.1463
| 5:20 | 7.1947 | 0.1463
| 5:20 | 7.195 | 0.14627
| 5:21 | 7.1953 | 0.14623
| 5:21 | 7.1956 | 0.14618
| 5:21 | 7.1958 | 0.14612
| 5:21 | 7.1961 | 0.14606
| 5:21 | 7.1964 | 0.14598
| 5:21 | 7.1967 | 0.14591
| 5:21 | 7.1969 | 0.14582
| 5:21 | 7.1972 | 0.14574
| 5:21 | 7.1975 | 0.14565
| 5:21 | 7.1978 | 0.14557
| 5:21 | 7.1981 | 0.14548
| 5:21 | 7.1983 | 0.1454
| 5:21 | 7.1986 | 0.14532
| 5:21 | 7.1989 | 0.14523
| 5:21 | 7.1992 | 0.14515
| 5:21 | 7.1994 | 0.14507
| 5:21 | 7.1997 | 0.14498
| 5:21 | 7.2 | 0.1449
| 5:21 | 7.2003 | 0.14483
| 5:21 | 7.2006 | 0.14475
| 5:21 | 7.2008 | 0.14469
| 5:21 | 7.2011 | 0.14463
| 5:21 | 7.2014 | 0.14457
| 5:21 | 7.2017 | 0.1445
| 5:21 | 7.2019 | 0.14444
| 5:21 | 7.2022 | 0.14438
| 5:21 | 7.2025 | 0.14431
| 5:21 | 7.2028 | 0.14424
| 5:21 | 7.2031 | 0.14417
| 5:21 | 7.2033 | 0.1441
| 5:21 | 7.2036 | 0.14403
| 5:21 | 7.2039 | 0.14396
| 5:21 | 7.2042 | 0.1439
| 5:21 | 7.2044 | 0.14384
| 5:21 | 7.2047 | 0.14379
| 5:21 | 7.205 | 0.14374
| 5:21 | 7.2053 | 0.14368
| 5:21 | 7.2056 | 0.14362
| 5:21 | 7.2058 | 0.14356
| 5:21 | 7.2061 | 0.14351
| 5:21 | 7.2064 | 0.14344
| 5:21 | 7.2067 | 0.14338
| 5:21 | 7.2069 | 0.14332
| 5:21 | 7.2072 | 0.14325
| 5:21 | 7.2075 | 0.14319
| 5:21 | 7.2078 | 0.14313
| 5:21 | 7.2081 | 0.14307
| 5:21 | 7.2083 | 0.14302
| 5:21 | 7.2086 | 0.14298
| 5:21 | 7.2089 | 0.14295
| 5:21 | 7.2092 | 0.14292
| 5:21 | 7.2094 | 0.14292
| 5:21 | 7.2097 | 0.14293
| 5:21 | 7.21 | 0.14296
| 5:21 | 7.2103 | 0.143
| 5:21 | 7.2106 | 0.14306
| 5:21 | 7.2108 | 0.14313
| 5:21 | 7.2111 | 0.1432
| 5:21 | 7.2114 | 0.1433
| 5:22 | 7.2117 | 0.1434
| 5:22 | 7.2119 | 0.1435
| 5:22 | 7.2122 | 0.14361
| 5:22 | 7.2125 | 0.14372
| 5:22 | 7.2128 | 0.14383
| 5:22 | 7.2131 | 0.14394
| 5:22 | 7.2133 | 0.14406
| 5:22 | 7.2136 | 0.14417
| 5:22 | 7.2139 | 0.14428
| 5:22 | 7.2142 | 0.14441
| 5:22 | 7.2144 | 0.14454
| 5:22 | 7.2147 | 0.14468
| 5:22 | 7.215 | 0.14483
| 5:22 | 7.2153 | 0.14499
| 5:22 | 7.2156 | 0.14515
| 5:22 | 7.2158 | 0.14533
| 5:22 | 7.2161 | 0.14551
| 5:22 | 7.2164 | 0.14571
| 5:22 | 7.2167 | 0.14591
| 5:22 | 7.2169 | 0.14613
| 5:22 | 7.2172 | 0.14635
| 5:22 | 7.2175 | 0.14657
| 5:22 | 7.2178 | 0.14679
| 5:22 | 7.2181 | 0.147
| 5:22 | 7.2183 | 0.14721
| 5:22 | 7.2186 | 0.14741
| 5:22 | 7.2189 | 0.14761
| 5:22 | 7.2192 | 0.1478
| 5:22 | 7.2194 | 0.14799
| 5:22 | 7.2197 | 0.14816
| 5:22 | 7.22 | 0.14831
| 5:22 | 7.2203 | 0.14846
| 5:22 | 7.2206 | 0.1486
| 5:22 | 7.2208 | 0.14873
| 5:22 | 7.2211 | 0.14884
| 5:22 | 7.2214 | 0.14893
| 5:22 | 7.2217 | 0.149
| 5:22 | 7.2219 | 0.14906
| 5:22 | 7.2222 | 0.14911
| 5:22 | 7.2225 | 0.14914
| 5:22 | 7.2228 | 0.14916
| 5:22 | 7.2231 | 0.14917
| 5:22 | 7.2233 | 0.14917
| 5:22 | 7.2236 | 0.14915
| 5:22 | 7.2239 | 0.14913
| 5:22 | 7.2242 | 0.1491
| 5:22 | 7.2244 | 0.14907
| 5:22 | 7.2247 | 0.14903
| 5:22 | 7.225 | 0.14899
| 5:22 | 7.2253 | 0.14895
| 5:22 | 7.2256 | 0.14891
| 5:22 | 7.2258 | 0.14886
| 5:22 | 7.2261 | 0.14881
| 5:22 | 7.2264 | 0.14877
| 5:22 | 7.2267 | 0.14872
| 5:22 | 7.2269 | 0.14868
| 5:22 | 7.2272 | 0.14863
| 5:22 | 7.2275 | 0.14859
| 5:22 | 7.2278 | 0.14855
| 5:22 | 7.2281 | 0.14851
| 5:22 | 7.2283 | 0.14848
| 5:23 | 7.2286 | 0.14844
| 5:23 | 7.2289 | 0.1484
| 5:23 | 7.2292 | 0.14837
| 5:23 | 7.2294 | 0.14833
| 5:23 | 7.2297 | 0.14829
| 5:23 | 7.23 | 0.14824
| 5:23 | 7.2303 | 0.1482
| 5:23 | 7.2306 | 0.14816
| 5:23 | 7.2308 | 0.14813
| 5:23 | 7.2311 | 0.14809
| 5:23 | 7.2314 | 0.14806
| 5:23 | 7.2317 | 0.14803
| 5:23 | 7.2319 | 0.148
| 5:23 | 7.2322 | 0.14798
| 5:23 | 7.2325 | 0.14796
| 5:23 | 7.2328 | 0.14794
| 5:23 | 7.2331 | 0.14792
| 5:23 | 7.2333 | 0.14791
| 5:23 | 7.2336 | 0.1479
| 5:23 | 7.2339 | 0.14789
| 5:23 | 7.2342 | 0.14789
| 5:23 | 7.2344 | 0.1479
| 5:23 | 7.2347 | 0.1479
| 5:23 | 7.235 | 0.14792
| 5:23 | 7.2353 | 0.14793
| 5:23 | 7.2356 | 0.14795
| 5:23 | 7.2358 | 0.14796
| 5:23 | 7.2361 | 0.14797
| 5:23 | 7.2364 | 0.14798
| 5:23 | 7.2367 | 0.14799
| 5:23 | 7.2369 | 0.148
| 5:23 | 7.2372 | 0.14801
| 5:23 | 7.2375 | 0.14801
| 5:23 | 7.2378 | 0.14802
| 5:23 | 7.2381 | 0.14802
| 5:23 | 7.2383 | 0.14802
| 5:23 | 7.2386 | 0.14802
| 5:23 | 7.2389 | 0.14801
| 5:23 | 7.2392 | 0.14801
| 5:23 | 7.2394 | 0.14799
| 5:23 | 7.2397 | 0.14798
| 5:23 | 7.24 | 0.14796
| 5:23 | 7.2403 | 0.14794
| 5:23 | 7.2406 | 0.14791
| 5:23 | 7.2408 | 0.14788
| 5:23 | 7.2411 | 0.14785
| 5:23 | 7.2414 | 0.14781
| 5:23 | 7.2417 | 0.14776
| 5:23 | 7.2419 | 0.14772
| 5:23 | 7.2422 | 0.14767
| 5:23 | 7.2425 | 0.14763
| 5:23 | 7.2428 | 0.14759
| 5:23 | 7.2431 | 0.14755
| 5:23 | 7.2433 | 0.1475
| 5:23 | 7.2436 | 0.14746
| 5:23 | 7.2439 | 0.14742
| 5:23 | 7.2442 | 0.14738
| 5:23 | 7.2444 | 0.14734
| 5:23 | 7.2447 | 0.1473
| 5:24 | 7.245 | 0.14726
| 5:24 | 7.2453 | 0.14722
| 5:24 | 7.2456 | 0.14719
| 5:24 | 7.2458 | 0.14715
| 5:24 | 7.2461 | 0.14711
| 5:24 | 7.2464 | 0.14707
| 5:24 | 7.2467 | 0.14704
| 5:24 | 7.2469 | 0.147
| 5:24 | 7.2472 | 0.14697
| 5:24 | 7.2475 | 0.14694
| 5:24 | 7.2478 | 0.14691
| 5:24 | 7.2481 | 0.14689
| 5:24 | 7.2483 | 0.14687
| 5:24 | 7.2486 | 0.14685
| 5:24 | 7.2489 | 0.14684
| 5:24 | 7.2492 | 0.14683
| 5:24 | 7.2494 | 0.14682
| 5:24 | 7.2497 | 0.14681
| 5:24 | 7.25 | 0.14683
| 5:24 | 7.2503 | 0.14685
| 5:24 | 7.2506 | 0.14688
| 5:24 | 7.2508 | 0.14693
| 5:24 | 7.2511 | 0.14699
| 5:24 | 7.2514 | 0.14708
| 5:24 | 7.2517 | 0.14719
| 5:24 | 7.2519 | 0.1473
| 5:24 | 7.2522 | 0.14744
| 5:24 | 7.2525 | 0.14761
| 5:24 | 7.2528 | 0.14781
| 5:24 | 7.2531 | 0.14801
| 5:24 | 7.2533 | 0.14823
| 5:24 | 7.2536 | 0.14847
| 5:24 | 7.2539 | 0.1487
| 5:24 | 7.2542 | 0.14894
| 5:24 | 7.2544 | 0.14917
| 5:24 | 7.2547 | 0.14941
| 5:24 | 7.255 | 0.14964
| 5:24 | 7.2553 | 0.14986
| 5:24 | 7.2556 | 0.15005
| 5:24 | 7.2558 | 0.15024
| 5:24 | 7.2561 | 0.15041
| 5:24 | 7.2564 | 0.15056
| 5:24 | 7.2567 | 0.1507
| 5:24 | 7.2569 | 0.15082
| 5:24 | 7.2572 | 0.15093
| 5:24 | 7.2575 | 0.15104
| 5:24 | 7.2578 | 0.15111
| 5:24 | 7.2581 | 0.15117
| 5:24 | 7.2583 | 0.15121
| 5:24 | 7.2586 | 0.15124
| 5:24 | 7.2589 | 0.15126
| 5:24 | 7.2592 | 0.15126
| 5:24 | 7.2594 | 0.15124
| 5:24 | 7.2597 | 0.15122
| 5:24 | 7.26 | 0.15118
| 5:24 | 7.2603 | 0.15113
| 5:24 | 7.2606 | 0.15107
| 5:24 | 7.2608 | 0.15101
| 5:24 | 7.2611 | 0.15094
| 5:24 | 7.2614 | 0.15088
| 5:24 | 7.2617 | 0.15081
| 5:25 | 7.2619 | 0.15074
| 5:25 | 7.2622 | 0.15067
| 5:25 | 7.2625 | 0.15061
| 5:25 | 7.2628 | 0.15054
| 5:25 | 7.2631 | 0.15048
| 5:25 | 7.2633 | 0.15041
| 5:25 | 7.2636 | 0.15035
| 5:25 | 7.2639 | 0.15029
| 5:25 | 7.2642 | 0.15022
| 5:25 | 7.2644 | 0.15016
| 5:25 | 7.2647 | 0.1501
| 5:25 | 7.265 | 0.15004
| 5:25 | 7.2653 | 0.14997
| 5:25 | 7.2656 | 0.14991
| 5:25 | 7.2658 | 0.14985
| 5:25 | 7.2661 | 0.14979
| 5:25 | 7.2664 | 0.14973
| 5:25 | 7.2667 | 0.14967
| 5:25 | 7.2669 | 0.14961
| 5:25 | 7.2672 | 0.14956
| 5:25 | 7.2675 | 0.1495
| 5:25 | 7.2678 | 0.14944
| 5:25 | 7.2681 | 0.14938
| 5:25 | 7.2683 | 0.14933
| 5:25 | 7.2686 | 0.14927
| 5:25 | 7.2689 | 0.14922
| 5:25 | 7.2692 | 0.14916
| 5:25 | 7.2694 | 0.14911
| 5:25 | 7.2697 | 0.14906
| 5:25 | 7.27 | 0.14901
| 5:25 | 7.2703 | 0.14898
| 5:25 | 7.2706 | 0.14896
| 5:25 | 7.2708 | 0.14894
| 5:25 | 7.2711 | 0.14892
| 5:25 | 7.2714 | 0.1489
| 5:25 | 7.2717 | 0.14888
| 5:25 | 7.2719 | 0.14885
| 5:25 | 7.2722 | 0.14883
| 5:25 | 7.2725 | 0.1488
| 5:25 | 7.2728 | 0.14877
| 5:25 | 7.2731 | 0.14874
| 5:25 | 7.2733 | 0.14871
| 5:25 | 7.2736 | 0.14867
| 5:25 | 7.2739 | 0.14863
| 5:25 | 7.2742 | 0.14859
| 5:25 | 7.2744 | 0.14854
| 5:25 | 7.2747 | 0.14849
| 5:25 | 7.275 | 0.14844
| 5:25 | 7.2753 | 0.14839
| 5:25 | 7.2756 | 0.14834
| 5:25 | 7.2758 | 0.14829
| 5:25 | 7.2761 | 0.14824
| 5:25 | 7.2764 | 0.14819
| 5:25 | 7.2767 | 0.14814
| 5:25 | 7.2769 | 0.14809
| 5:25 | 7.2772 | 0.14805
| 5:25 | 7.2775 | 0.14801
| 5:25 | 7.2778 | 0.14798
| 5:25 | 7.2781 | 0.14797
| 5:26 | 7.2783 | 0.14796
| 5:26 | 7.2786 | 0.14795
| 5:26 | 7.2789 | 0.14795
| 5:26 | 7.2792 | 0.14797
| 5:26 | 7.2794 | 0.148
| 5:26 | 7.2797 | 0.14803
| 5:26 | 7.28 | 0.14806
| 5:26 | 7.2803 | 0.1481
| 5:26 | 7.2806 | 0.14814
| 5:26 | 7.2808 | 0.14817
| 5:26 | 7.2811 | 0.1482
| 5:26 | 7.2814 | 0.14823
| 5:26 | 7.2817 | 0.14825
| 5:26 | 7.2819 | 0.14827
| 5:26 | 7.2822 | 0.14829
| 5:26 | 7.2825 | 0.14831
| 5:26 | 7.2828 | 0.14832
| 5:26 | 7.2831 | 0.14834
| 5:26 | 7.2833 | 0.14834
| 5:26 | 7.2836 | 0.14833
| 5:26 | 7.2839 | 0.14832
| 5:26 | 7.2842 | 0.14829
| 5:26 | 7.2844 | 0.14826
| 5:26 | 7.2847 | 0.14822
| 5:26 | 7.285 | 0.14818
| 5:26 | 7.2853 | 0.14813
| 5:26 | 7.2856 | 0.14808
| 5:26 | 7.2858 | 0.14803
| 5:26 | 7.2861 | 0.14798
| 5:26 | 7.2864 | 0.14792
| 5:26 | 7.2867 | 0.14787
| 5:26 | 7.2869 | 0.1478
| 5:26 | 7.2872 | 0.14774
| 5:26 | 7.2875 | 0.14767
| 5:26 | 7.2878 | 0.14761
| 5:26 | 7.2881 | 0.14755
| 5:26 | 7.2883 | 0.14748
| 5:26 | 7.2886 | 0.14742
| 5:26 | 7.2889 | 0.14735
| 5:26 | 7.2892 | 0.14729
| 5:26 | 7.2894 | 0.14723
| 5:26 | 7.2897 | 0.14716
| 5:26 | 7.29 | 0.1471
| 5:26 | 7.2903 | 0.14704
| 5:26 | 7.2906 | 0.14697
| 5:26 | 7.2908 | 0.14691
| 5:26 | 7.2911 | 0.14685
| 5:26 | 7.2914 | 0.14679
| 5:26 | 7.2917 | 0.14672
| 5:26 | 7.2919 | 0.14666
| 5:26 | 7.2922 | 0.1466
| 5:26 | 7.2925 | 0.14654
| 5:26 | 7.2928 | 0.14647
| 5:26 | 7.2931 | 0.14641
| 5:26 | 7.2933 | 0.14635
| 5:26 | 7.2936 | 0.14629
| 5:26 | 7.2939 | 0.14623
| 5:26 | 7.2942 | 0.14617
| 5:26 | 7.2944 | 0.1461
| 5:26 | 7.2947 | 0.14604
| 5:26 | 7.295 | 0.14598
| 5:27 | 7.2953 | 0.14592
| 5:27 | 7.2956 | 0.14586
| 5:27 | 7.2958 | 0.1458
| 5:27 | 7.2961 | 0.14574
| 5:27 | 7.2964 | 0.14568
| 5:27 | 7.2967 | 0.14562
| 5:27 | 7.2969 | 0.14556
| 5:27 | 7.2972 | 0.1455
| 5:27 | 7.2975 | 0.14543
| 5:27 | 7.2978 | 0.14537
| 5:27 | 7.2981 | 0.14531
| 5:27 | 7.2983 | 0.14525
| 5:27 | 7.2986 | 0.14519
| 5:27 | 7.2989 | 0.14514
| 5:27 | 7.2992 | 0.14508
| 5:27 | 7.2994 | 0.14502
| 5:27 | 7.2997 | 0.14496
| 5:27 | 7.3 | 0.1449
| 5:27 | 7.3003 | 0.14484
| 5:27 | 7.3006 | 0.14478
| 5:27 | 7.3008 | 0.14472
| 5:27 | 7.3011 | 0.14466
| 5:27 | 7.3014 | 0.1446
| 5:27 | 7.3017 | 0.14455
| 5:27 | 7.3019 | 0.1445
| 5:27 | 7.3022 | 0.14444
| 5:27 | 7.3025 | 0.14439
| 5:27 | 7.3028 | 0.14434
| 5:27 | 7.3031 | 0.14429
| 5:27 | 7.3033 | 0.14423
| 5:27 | 7.3036 | 0.14418
| 5:27 | 7.3039 | 0.14413
| 5:27 | 7.3042 | 0.14407
| 5:27 | 7.3044 | 0.14402
| 5:27 | 7.3047 | 0.14396
| 5:27 | 7.305 | 0.14391
| 5:27 | 7.3053 | 0.14385
| 5:27 | 7.3056 | 0.1438
| 5:27 | 7.3058 | 0.14374
| 5:27 | 7.3061 | 0.14369
| 5:27 | 7.3064 | 0.14363
| 5:27 | 7.3067 | 0.14358
| 5:27 | 7.3069 | 0.14352
| 5:27 | 7.3072 | 0.14347
| 5:27 | 7.3075 | 0.14341
| 5:27 | 7.3078 | 0.14335
| 5:27 | 7.3081 | 0.1433
| 5:27 | 7.3083 | 0.14324
| 5:27 | 7.3086 | 0.14318
| 5:27 | 7.3089 | 0.14312
| 5:27 | 7.3092 | 0.14307
| 5:27 | 7.3094 | 0.14301
| 5:27 | 7.3097 | 0.14295
| 5:27 | 7.31 | 0.14289
| 5:27 | 7.3103 | 0.14283
| 5:27 | 7.3106 | 0.14278
| 5:27 | 7.3108 | 0.14272
| 5:27 | 7.3111 | 0.14266
| 5:27 | 7.3114 | 0.1426
| 5:28 | 7.3117 | 0.14254
| 5:28 | 7.3119 | 0.14248
| 5:28 | 7.3122 | 0.14242
| 5:28 | 7.3125 | 0.14236
| 5:28 | 7.3128 | 0.1423
| 5:28 | 7.3131 | 0.14224
| 5:28 | 7.3133 | 0.14218
| 5:28 | 7.3136 | 0.14212
| 5:28 | 7.3139 | 0.14206
| 5:28 | 7.3142 | 0.142
| 5:28 | 7.3144 | 0.14193
| 5:28 | 7.3147 | 0.14187
| 5:28 | 7.315 | 0.14181
| 5:28 | 7.3153 | 0.14175
| 5:28 | 7.3156 | 0.14169
| 5:28 | 7.3158 | 0.14162
| 5:28 | 7.3161 | 0.14156
| 5:28 | 7.3164 | 0.1415
| 5:28 | 7.3167 | 0.14143
| 5:28 | 7.3169 | 0.14137
| 5:28 | 7.3172 | 0.14131
| 5:28 | 7.3175 | 0.14124
| 5:28 | 7.3178 | 0.14118
| 5:28 | 7.3181 | 0.14112
| 5:28 | 7.3183 | 0.14105
| 5:28 | 7.3186 | 0.14098
| 5:28 | 7.3189 | 0.14091
| 5:28 | 7.3192 | 0.14084
| 5:28 | 7.3194 | 0.14077
| 5:28 | 7.3197 | 0.1407
| 5:28 | 7.32 | 0.14063
| 5:28 | 7.3203 | 0.14056
| 5:28 | 7.3206 | 0.14049
| 5:28 | 7.3208 | 0.14043
| 5:28 | 7.3211 | 0.14036
| 5:28 | 7.3214 | 0.14029
| 5:28 | 7.3217 | 0.14022
| 5:28 | 7.3219 | 0.14016
| 5:28 | 7.3222 | 0.14009
| 5:28 | 7.3225 | 0.14003
| 5:28 | 7.3228 | 0.13996
| 5:28 | 7.3231 | 0.13989
| 5:28 | 7.3233 | 0.13983
| 5:28 | 7.3236 | 0.13977
| 5:28 | 7.3239 | 0.1397
| 5:28 | 7.3242 | 0.13964
| 5:28 | 7.3244 | 0.13957
| 5:28 | 7.3247 | 0.13951
| 5:28 | 7.325 | 0.13945
| 5:28 | 7.3253 | 0.13939
| 5:28 | 7.3256 | 0.13932
| 5:28 | 7.3258 | 0.13926
| 5:28 | 7.3261 | 0.1392
| 5:28 | 7.3264 | 0.13914
| 5:28 | 7.3267 | 0.13908
| 5:28 | 7.3269 | 0.13902
| 5:28 | 7.3272 | 0.13896
| 5:28 | 7.3275 | 0.1389
| 5:28 | 7.3278 | 0.13884
| 5:28 | 7.3281 | 0.13878
| 5:28 | 7.3283 | 0.13873
| 5:29 | 7.3286 | 0.13867
| 5:29 | 7.3289 | 0.13861
| 5:29 | 7.3292 | 0.13855
| 5:29 | 7.3294 | 0.13849
| 5:29 | 7.3297 | 0.13843
| 5:29 | 7.33 | 0.13837
| 5:29 | 7.3303 | 0.1383
| 5:29 | 7.3306 | 0.13824
| 5:29 | 7.3308 | 0.13818
| 5:29 | 7.3311 | 0.13811
| 5:29 | 7.3314 | 0.13805
| 5:29 | 7.3317 | 0.13798
| 5:29 | 7.3319 | 0.13791
| 5:29 | 7.3322 | 0.13784
| 5:29 | 7.3325 | 0.13777
| 5:29 | 7.3328 | 0.1377
| 5:29 | 7.3331 | 0.13763
| 5:29 | 7.3333 | 0.13756
| 5:29 | 7.3336 | 0.13749
| 5:29 | 7.3339 | 0.13742
| 5:29 | 7.3342 | 0.13734
| 5:29 | 7.3344 | 0.13727
| 5:29 | 7.3347 | 0.13719
| 5:29 | 7.335 | 0.13712
| 5:29 | 7.3353 | 0.13705
| 5:29 | 7.3356 | 0.13698
| 5:29 | 7.3358 | 0.13692
| 5:29 | 7.3361 | 0.13685
| 5:29 | 7.3364 | 0.13679
| 5:29 | 7.3367 | 0.13673
| 5:29 | 7.3369 | 0.13667
| 5:29 | 7.3372 | 0.1366
| 5:29 | 7.3375 | 0.13654
| 5:29 | 7.3378 | 0.13647
| 5:29 | 7.3381 | 0.1364
| 5:29 | 7.3383 | 0.13633
| 5:29 | 7.3386 | 0.13626
| 5:29 | 7.3389 | 0.13619
| 5:29 | 7.3392 | 0.13612
| 5:29 | 7.3394 | 0.13605
| 5:29 | 7.3397 | 0.13599
| 5:29 | 7.34 | 0.13593
| 5:29 | 7.3403 | 0.13587
| 5:29 | 7.3406 | 0.13581
| 5:29 | 7.3408 | 0.13576
| 5:29 | 7.3411 | 0.1357
| 5:29 | 7.3414 | 0.13565
| 5:29 | 7.3417 | 0.13558
| 5:29 | 7.3419 | 0.13551
| 5:29 | 7.3422 | 0.13545
| 5:29 | 7.3425 | 0.13538
| 5:29 | 7.3428 | 0.13531
| 5:29 | 7.3431 | 0.13525
| 5:29 | 7.3433 | 0.13518
| 5:29 | 7.3436 | 0.13512
| 5:29 | 7.3439 | 0.13506
| 5:29 | 7.3442 | 0.13501
| 5:29 | 7.3444 | 0.13495
| 5:29 | 7.3447 | 0.1349
| 5:30 | 7.345 | 0.13484
| 5:30 | 7.3453 | 0.13479
| 5:30 | 7.3456 | 0.13473
| 5:30 | 7.3458 | 0.13468
| 5:30 | 7.3461 | 0.13463
| 5:30 | 7.3464 | 0.13457
| 5:30 | 7.3467 | 0.13452
| 5:30 | 7.3469 | 0.13446
| 5:30 | 7.3472 | 0.13441
| 5:30 | 7.3475 | 0.13436
| 5:30 | 7.3478 | 0.1343
| 5:30 | 7.3481 | 0.13425
| 5:30 | 7.3483 | 0.13419
| 5:30 | 7.3486 | 0.13414
| 5:30 | 7.3489 | 0.13409
| 5:30 | 7.3492 | 0.13403
| 5:30 | 7.3494 | 0.13398
| 5:30 | 7.3497 | 0.13392
| 5:30 | 7.35 | 0.13387
| 5:30 | 7.3503 | 0.13382
| 5:30 | 7.3506 | 0.13376
| 5:30 | 7.3508 | 0.13371
| 5:30 | 7.3511 | 0.13365
| 5:30 | 7.3514 | 0.1336
| 5:30 | 7.3517 | 0.13355
| 5:30 | 7.3519 | 0.13349
| 5:30 | 7.3522 | 0.13344
| 5:30 | 7.3525 | 0.13339
| 5:30 | 7.3528 | 0.13333
| 5:30 | 7.3531 | 0.13328
| 5:30 | 7.3533 | 0.13323
| 5:30 | 7.3536 | 0.13317
| 5:30 | 7.3539 | 0.13312
| 5:30 | 7.3542 | 0.13307
| 5:30 | 7.3544 | 0.13301
| 5:30 | 7.3547 | 0.13296
| 5:30 | 7.355 | 0.13291
| 5:30 | 7.3553 | 0.13285
| 5:30 | 7.3556 | 0.1328
| 5:30 | 7.3558 | 0.13275
| 5:30 | 7.3561 | 0.13269
| 5:30 | 7.3564 | 0.13264
| 5:30 | 7.3567 | 0.13259
| 5:30 | 7.3569 | 0.13253
| 5:30 | 7.3572 | 0.13248
| 5:30 | 7.3575 | 0.13243
| 5:30 | 7.3578 | 0.13238
| 5:30 | 7.3581 | 0.13232
| 5:30 | 7.3583 | 0.13227
| 5:30 | 7.3586 | 0.13222
| 5:30 | 7.3589 | 0.13216
| 5:30 | 7.3592 | 0.13211
| 5:30 | 7.3594 | 0.13206
| 5:30 | 7.3597 | 0.13201
| 5:30 | 7.36 | 0.13195
| 5:30 | 7.3603 | 0.1319
| 5:30 | 7.3606 | 0.13185
| 5:30 | 7.3608 | 0.1318
| 5:30 | 7.3611 | 0.13174
| 5:30 | 7.3614 | 0.13169
| 5:30 | 7.3617 | 0.13164
| 5:31 | 7.3619 | 0.13159
| 5:31 | 7.3622 | 0.13153
| 5:31 | 7.3625 | 0.13148
| 5:31 | 7.3628 | 0.13143
| 5:31 | 7.3631 | 0.13138
| 5:31 | 7.3633 | 0.13133
| 5:31 | 7.3636 | 0.13127
| 5:31 | 7.3639 | 0.13122
| 5:31 | 7.3642 | 0.13117
| 5:31 | 7.3644 | 0.13112
| 5:31 | 7.3647 | 0.13107
| 5:31 | 7.365 | 0.13101
| 5:31 | 7.3653 | 0.13096
| 5:31 | 7.3656 | 0.13091
| 5:31 | 7.3658 | 0.13086
| 5:31 | 7.3661 | 0.13081
| 5:31 | 7.3664 | 0.13076
| 5:31 | 7.3667 | 0.1307
| 5:31 | 7.3669 | 0.13065
| 5:31 | 7.3672 | 0.13061
| 5:31 | 7.3675 | 0.13058
| 5:31 | 7.3678 | 0.13054
| 5:31 | 7.3681 | 0.13051
| 5:31 | 7.3683 | 0.13049
| 5:31 | 7.3686 | 0.13046
| 5:31 | 7.3689 | 0.13043
| 5:31 | 7.3692 | 0.13039
| 5:31 | 7.3694 | 0.13035
| 5:31 | 7.3697 | 0.1303
| 5:31 | 7.37 | 0.13026
| 5:31 | 7.3703 | 0.13021
| 5:31 | 7.3706 | 0.13016
| 5:31 | 7.3708 | 0.13011
| 5:31 | 7.3711 | 0.13006
| 5:31 | 7.3714 | 0.13002
| 5:31 | 7.3717 | 0.12998
| 5:31 | 7.3719 | 0.12994
| 5:31 | 7.3722 | 0.1299
| 5:31 | 7.3725 | 0.12986
| 5:31 | 7.3728 | 0.12983
| 5:31 | 7.3731 | 0.12979
| 5:31 | 7.3733 | 0.12975
| 5:31 | 7.3736 | 0.12972
| 5:31 | 7.3739 | 0.12968
| 5:31 | 7.3742 | 0.12965
| 5:31 | 7.3744 | 0.12961
| 5:31 | 7.3747 | 0.12958
| 5:31 | 7.375 | 0.12955
| 5:31 | 7.3753 | 0.12951
| 5:31 | 7.3756 | 0.12948
| 5:31 | 7.3758 | 0.12945
| 5:31 | 7.3761 | 0.12943
| 5:31 | 7.3764 | 0.1294
| 5:31 | 7.3767 | 0.12938
| 5:31 | 7.3769 | 0.12936
| 5:31 | 7.3772 | 0.12933
| 5:31 | 7.3775 | 0.1293
| 5:31 | 7.3778 | 0.12927
| 5:31 | 7.3781 | 0.12924
| 5:32 | 7.3783 | 0.1292
| 5:32 | 7.3786 | 0.12916
| 5:32 | 7.3789 | 0.12913
| 5:32 | 7.3792 | 0.1291
| 5:32 | 7.3794 | 0.12907
| 5:32 | 7.3797 | 0.12904
| 5:32 | 7.38 | 0.12902
| 5:32 | 7.3803 | 0.129
| 5:32 | 7.3806 | 0.12898
| 5:32 | 7.3808 | 0.12896
| 5:32 | 7.3811 | 0.12894
| 5:32 | 7.3814 | 0.12891
| 5:32 | 7.3817 | 0.12889
| 5:32 | 7.3819 | 0.12887
| 5:32 | 7.3822 | 0.12885
| 5:32 | 7.3825 | 0.12883
| 5:32 | 7.3828 | 0.1288
| 5:32 | 7.3831 | 0.12878
| 5:32 | 7.3833 | 0.12875
| 5:32 | 7.3836 | 0.12873
| 5:32 | 7.3839 | 0.12871
| 5:32 | 7.3842 | 0.12868
| 5:32 | 7.3844 | 0.12865
| 5:32 | 7.3847 | 0.12863
| 5:32 | 7.385 | 0.1286
| 5:32 | 7.3853 | 0.12858
| 5:32 | 7.3856 | 0.12855
| 5:32 | 7.3858 | 0.12851
| 5:32 | 7.3861 | 0.12848
| 5:32 | 7.3864 | 0.12844
| 5:32 | 7.3867 | 0.12841
| 5:32 | 7.3869 | 0.12838
| 5:32 | 7.3872 | 0.12836
| 5:32 | 7.3875 | 0.12834
| 5:32 | 7.3878 | 0.12832
| 5:32 | 7.3881 | 0.1283
| 5:32 | 7.3883 | 0.12829
| 5:32 | 7.3886 | 0.12827
| 5:32 | 7.3889 | 0.12826
| 5:32 | 7.3892 | 0.12824
| 5:32 | 7.3894 | 0.12822
| 5:32 | 7.3897 | 0.12821
| 5:32 | 7.39 | 0.12819
| 5:32 | 7.3903 | 0.12817
| 5:32 | 7.3906 | 0.12816
| 5:32 | 7.3908 | 0.12814
| 5:32 | 7.3911 | 0.12812
| 5:32 | 7.3914 | 0.1281
| 5:32 | 7.3917 | 0.12808
| 5:32 | 7.3919 | 0.12806
| 5:32 | 7.3922 | 0.12804
| 5:32 | 7.3925 | 0.12803
| 5:32 | 7.3928 | 0.12801
| 5:32 | 7.3931 | 0.12799
| 5:32 | 7.3933 | 0.12797
| 5:32 | 7.3936 | 0.12795
| 5:32 | 7.3939 | 0.12791
| 5:32 | 7.3942 | 0.12788
| 5:32 | 7.3944 | 0.12786
| 5:32 | 7.3947 | 0.12783
| 5:32 | 7.395 | 0.12781
| 5:33 | 7.3953 | 0.12779
| 5:33 | 7.3956 | 0.12777
| 5:33 | 7.3958 | 0.12775
| 5:33 | 7.3961 | 0.12773
| 5:33 | 7.3964 | 0.1277
| 5:33 | 7.3967 | 0.12767
| 5:33 | 7.3969 | 0.12765
| 5:33 | 7.3972 | 0.12762
| 5:33 | 7.3975 | 0.12759
| 5:33 | 7.3978 | 0.12756
| 5:33 | 7.3981 | 0.12753
| 5:33 | 7.3983 | 0.1275
| 5:33 | 7.3986 | 0.12748
| 5:33 | 7.3989 | 0.12745
| 5:33 | 7.3992 | 0.12742
| 5:33 | 7.3994 | 0.12739
| 5:33 | 7.3997 | 0.12737
| 5:33 | 7.4 | 0.12734
| 5:33 | 7.4003 | 0.12731
| 5:33 | 7.4006 | 0.12729
| 5:33 | 7.4008 | 0.12726
| 5:33 | 7.4011 | 0.12723
| 5:33 | 7.4014 | 0.12721
| 5:33 | 7.4017 | 0.12718
| 5:33 | 7.4019 | 0.12715
| 5:33 | 7.4022 | 0.12713
| 5:33 | 7.4025 | 0.12711
| 5:33 | 7.4028 | 0.12709
| 5:33 | 7.4031 | 0.12707
| 5:33 | 7.4033 | 0.12704
| 5:33 | 7.4036 | 0.12701
| 5:33 | 7.4039 | 0.12698
| 5:33 | 7.4042 | 0.12695
| 5:33 | 7.4044 | 0.12691
| 5:33 | 7.4047 | 0.12688
| 5:33 | 7.405 | 0.12684
| 5:33 | 7.4053 | 0.1268
| 5:33 | 7.4056 | 0.12675
| 5:33 | 7.4058 | 0.12671
| 5:33 | 7.4061 | 0.12667
| 5:33 | 7.4064 | 0.12664
| 5:33 | 7.4067 | 0.1266
| 5:33 | 7.4069 | 0.12657
| 5:33 | 7.4072 | 0.12654
| 5:33 | 7.4075 | 0.12651
| 5:33 | 7.4078 | 0.12648
| 5:33 | 7.4081 | 0.12646
| 5:33 | 7.4083 | 0.12644
| 5:33 | 7.4086 | 0.12642
| 5:33 | 7.4089 | 0.12639
| 5:33 | 7.4092 | 0.12637
| 5:33 | 7.4094 | 0.12633
| 5:33 | 7.4097 | 0.1263
| 5:33 | 7.41 | 0.12628
| 5:33 | 7.4103 | 0.12626
| 5:33 | 7.4106 | 0.12625
| 5:33 | 7.4108 | 0.12623
| 5:33 | 7.4111 | 0.12622
| 5:33 | 7.4114 | 0.12621
| 5:34 | 7.4117 | 0.1262
| 5:34 | 7.4119 | 0.12618
| 5:34 | 7.4122 | 0.12615
| 5:34 | 7.4125 | 0.12613
| 5:34 | 7.4128 | 0.1261
| 5:34 | 7.4131 | 0.12607
| 5:34 | 7.4133 | 0.12603
| 5:34 | 7.4136 | 0.12599
| 5:34 | 7.4139 | 0.12596
| 5:34 | 7.4142 | 0.12592
| 5:34 | 7.4144 | 0.12589
| 5:34 | 7.4147 | 0.12585
| 5:34 | 7.415 | 0.12582
| 5:34 | 7.4153 | 0.12579
| 5:34 | 7.4156 | 0.12576
| 5:34 | 7.4158 | 0.12573
| 5:34 | 7.4161 | 0.12571
| 5:34 | 7.4164 | 0.12568
| 5:34 | 7.4167 | 0.12565
| 5:34 | 7.4169 | 0.12563
| 5:34 | 7.4172 | 0.12561
| 5:34 | 7.4175 | 0.12559
| 5:34 | 7.4178 | 0.12557
| 5:34 | 7.4181 | 0.12555
| 5:34 | 7.4183 | 0.12554
| 5:34 | 7.4186 | 0.12554
| 5:34 | 7.4189 | 0.12553
| 5:34 | 7.4192 | 0.12552
| 5:34 | 7.4194 | 0.12551
| 5:34 | 7.4197 | 0.12549
| 5:34 | 7.42 | 0.12547
| 5:34 | 7.4203 | 0.12545
| 5:34 | 7.4206 | 0.12543
| 5:34 | 7.4208 | 0.1254
| 5:34 | 7.4211 | 0.12536
| 5:34 | 7.4214 | 0.12534
| 5:34 | 7.4217 | 0.12531
| 5:34 | 7.4219 | 0.12529
| 5:34 | 7.4222 | 0.12527
| 5:34 | 7.4225 | 0.12525
| 5:34 | 7.4228 | 0.12524
| 5:34 | 7.4231 | 0.12522
| 5:34 | 7.4233 | 0.12521
| 5:34 | 7.4236 | 0.1252
| 5:34 | 7.4239 | 0.12519
| 5:34 | 7.4242 | 0.12518
| 5:34 | 7.4244 | 0.12516
| 5:34 | 7.4247 | 0.12515
| 5:34 | 7.425 | 0.12513
| 5:34 | 7.4253 | 0.1251
| 5:34 | 7.4256 | 0.12508
| 5:34 | 7.4258 | 0.12507
| 5:34 | 7.4261 | 0.12506
| 5:34 | 7.4264 | 0.12506
| 5:34 | 7.4267 | 0.12505
| 5:34 | 7.4269 | 0.12504
| 5:34 | 7.4272 | 0.12503
| 5:34 | 7.4275 | 0.12501
| 5:34 | 7.4278 | 0.125
| 5:34 | 7.4281 | 0.12497
| 5:34 | 7.4283 | 0.12495
| 5:35 | 7.4286 | 0.12493
| 5:35 | 7.4289 | 0.1249
| 5:35 | 7.4292 | 0.12488
| 5:35 | 7.4294 | 0.12486
| 5:35 | 7.4297 | 0.12485
| 5:35 | 7.43 | 0.12486
| 5:35 | 7.4303 | 0.12486
| 5:35 | 7.4306 | 0.12487
| 5:35 | 7.4308 | 0.12487
| 5:35 | 7.4311 | 0.12486
| 5:35 | 7.4314 | 0.12486
| 5:35 | 7.4317 | 0.12485
| 5:35 | 7.4319 | 0.12484
| 5:35 | 7.4322 | 0.12482
| 5:35 | 7.4325 | 0.1248
| 5:35 | 7.4328 | 0.12478
| 5:35 | 7.4331 | 0.12476
| 5:35 | 7.4333 | 0.12474
| 5:35 | 7.4336 | 0.12474
| 5:35 | 7.4339 | 0.12473
| 5:35 | 7.4342 | 0.12472
| 5:35 | 7.4344 | 0.12471
| 5:35 | 7.4347 | 0.1247
| 5:35 | 7.435 | 0.12468
| 5:35 | 7.4353 | 0.12465
| 5:35 | 7.4356 | 0.12463
| 5:35 | 7.4358 | 0.1246
| 5:35 | 7.4361 | 0.12458
| 5:35 | 7.4364 | 0.12456
| 5:35 | 7.4367 | 0.12453
| 5:35 | 7.4369 | 0.12451
| 5:35 | 7.4372 | 0.1245
| 5:35 | 7.4375 | 0.1245
| 5:35 | 7.4378 | 0.1245
| 5:35 | 7.4381 | 0.1245
| 5:35 | 7.4383 | 0.1245
| 5:35 | 7.4386 | 0.1245
| 5:35 | 7.4389 | 0.12449
| 5:35 | 7.4392 | 0.12448
| 5:35 | 7.4394 | 0.12447
| 5:35 | 7.4397 | 0.12445
| 5:35 | 7.44 | 0.12443
| 5:35 | 7.4403 | 0.1244
| 5:35 | 7.4406 | 0.12437
| 5:35 | 7.4408 | 0.12435
| 5:35 | 7.4411 | 0.12433
| 5:35 | 7.4414 | 0.12432
| 5:35 | 7.4417 | 0.12432
| 5:35 | 7.4419 | 0.12433
| 5:35 | 7.4422 | 0.12434
| 5:35 | 7.4425 | 0.12434
| 5:35 | 7.4428 | 0.12434
| 5:35 | 7.4431 | 0.12433
| 5:35 | 7.4433 | 0.12432
| 5:35 | 7.4436 | 0.1243
| 5:35 | 7.4439 | 0.12429
| 5:35 | 7.4442 | 0.12427
| 5:35 | 7.4444 | 0.12425
| 5:35 | 7.4447 | 0.12424
| 5:36 | 7.445 | 0.12423
| 5:36 | 7.4453 | 0.12423
| 5:36 | 7.4456 | 0.12423
| 5:36 | 7.4458 | 0.12425
| 5:36 | 7.4461 | 0.12426
| 5:36 | 7.4464 | 0.12427
| 5:36 | 7.4467 | 0.12428
| 5:36 | 7.4469 | 0.12429
| 5:36 | 7.4472 | 0.1243
| 5:36 | 7.4475 | 0.1243
| 5:36 | 7.4478 | 0.12431
| 5:36 | 7.4481 | 0.12432
| 5:36 | 7.4483 | 0.12432
| 5:36 | 7.4486 | 0.12432
| 5:36 | 7.4489 | 0.12433
| 5:36 | 7.4492 | 0.12433
| 5:36 | 7.4494 | 0.12433
| 5:36 | 7.4497 | 0.12433
| 5:36 | 7.45 | 0.12433
| 5:36 | 7.4503 | 0.12433
| 5:36 | 7.4506 | 0.12432
| 5:36 | 7.4508 | 0.12432
| 5:36 | 7.4511 | 0.12431
| 5:36 | 7.4514 | 0.1243
| 5:36 | 7.4517 | 0.12429
| 5:36 | 7.4519 | 0.12428
| 5:36 | 7.4522 | 0.12427
| 5:36 | 7.4525 | 0.12427
| 5:36 | 7.4528 | 0.12427
| 5:36 | 7.4531 | 0.12427
| 5:36 | 7.4533 | 0.12428
| 5:36 | 7.4536 | 0.12429
| 5:36 | 7.4539 | 0.1243
| 5:36 | 7.4542 | 0.1243
| 5:36 | 7.4544 | 0.1243
| 5:36 | 7.4547 | 0.1243
| 5:36 | 7.455 | 0.12429
| 5:36 | 7.4553 | 0.12429
| 5:36 | 7.4556 | 0.12429
| 5:36 | 7.4558 | 0.12429
| 5:36 | 7.4561 | 0.12429
| 5:36 | 7.4564 | 0.1243
| 5:36 | 7.4567 | 0.1243
| 5:36 | 7.4569 | 0.12431
| 5:36 | 7.4572 | 0.12432
| 5:36 | 7.4575 | 0.12433
| 5:36 | 7.4578 | 0.12433
| 5:36 | 7.4581 | 0.12433
| 5:36 | 7.4583 | 0.12432
| 5:36 | 7.4586 | 0.12431
| 5:36 | 7.4589 | 0.1243
| 5:36 | 7.4592 | 0.12429
| 5:36 | 7.4594 | 0.12428
| 5:36 | 7.4597 | 0.12426
| 5:36 | 7.46 | 0.12424
| 5:36 | 7.4603 | 0.12423
| 5:36 | 7.4606 | 0.12422
| 5:36 | 7.4608 | 0.12421
| 5:36 | 7.4611 | 0.1242
| 5:36 | 7.4614 | 0.1242
| 5:36 | 7.4617 | 0.12419
| 5:37 | 7.4619 | 0.12419
| 5:37 | 7.4622 | 0.12418
| 5:37 | 7.4625 | 0.12418
| 5:37 | 7.4628 | 0.12417
| 5:37 | 7.4631 | 0.12416
| 5:37 | 7.4633 | 0.12415
| 5:37 | 7.4636 | 0.12414
| 5:37 | 7.4639 | 0.12412
| 5:37 | 7.4642 | 0.12411
| 5:37 | 7.4644 | 0.12409
| 5:37 | 7.4647 | 0.12408
| 5:37 | 7.465 | 0.12407
| 5:37 | 7.4653 | 0.12406
| 5:37 | 7.4656 | 0.12405
| 5:37 | 7.4658 | 0.12404
| 5:37 | 7.4661 | 0.12403
| 5:37 | 7.4664 | 0.12404
| 5:37 | 7.4667 | 0.12404
| 5:37 | 7.4669 | 0.12403
| 5:37 | 7.4672 | 0.12403
| 5:37 | 7.4675 | 0.12403
| 5:37 | 7.4678 | 0.12401
| 5:37 | 7.4681 | 0.124
| 5:37 | 7.4683 | 0.12399
| 5:37 | 7.4686 | 0.12399
| 5:37 | 7.4689 | 0.12399
| 5:37 | 7.4692 | 0.12399
| 5:37 | 7.4694 | 0.124
| 5:37 | 7.4697 | 0.124
| 5:37 | 7.47 | 0.124
| 5:37 | 7.4703 | 0.12399
| 5:37 | 7.4706 | 0.12398
| 5:37 | 7.4708 | 0.12396
| 5:37 | 7.4711 | 0.12394
| 5:37 | 7.4714 | 0.12392
| 5:37 | 7.4717 | 0.12389
| 5:37 | 7.4719 | 0.12387
| 5:37 | 7.4722 | 0.12385
| 5:37 | 7.4725 | 0.12384
| 5:37 | 7.4728 | 0.12382
| 5:37 | 7.4731 | 0.12381
| 5:37 | 7.4733 | 0.12379
| 5:37 | 7.4736 | 0.12378
| 5:37 | 7.4739 | 0.12377
| 5:37 | 7.4742 | 0.12377
| 5:37 | 7.4744 | 0.12377
| 5:37 | 7.4747 | 0.12377
| 5:37 | 7.475 | 0.12376
| 5:37 | 7.4753 | 0.12375
| 5:37 | 7.4756 | 0.12373
| 5:37 | 7.4758 | 0.12372
| 5:37 | 7.4761 | 0.12371
| 5:37 | 7.4764 | 0.12371
| 5:37 | 7.4767 | 0.1237
| 5:37 | 7.4769 | 0.1237
| 5:37 | 7.4772 | 0.1237
| 5:37 | 7.4775 | 0.12371
| 5:37 | 7.4778 | 0.12371
| 5:37 | 7.4781 | 0.12371
| 5:38 | 7.4783 | 0.12371
| 5:38 | 7.4786 | 0.12371
| 5:38 | 7.4789 | 0.12371
| 5:38 | 7.4792 | 0.12369
| 5:38 | 7.4794 | 0.12368
| 5:38 | 7.4797 | 0.12367
| 5:38 | 7.48 | 0.12365
| 5:38 | 7.4803 | 0.12364
| 5:38 | 7.4806 | 0.12363
| 5:38 | 7.4808 | 0.12362
| 5:38 | 7.4811 | 0.12361
| 5:38 | 7.4814 | 0.1236
| 5:38 | 7.4817 | 0.12359
| 5:38 | 7.4819 | 0.12358
| 5:38 | 7.4822 | 0.12357
| 5:38 | 7.4825 | 0.12356
| 5:38 | 7.4828 | 0.12355
| 5:38 | 7.4831 | 0.12355
| 5:38 | 7.4833 | 0.12354
| 5:38 | 7.4836 | 0.12353
| 5:38 | 7.4839 | 0.12353
| 5:38 | 7.4842 | 0.12352
| 5:38 | 7.4844 | 0.12352
| 5:38 | 7.4847 | 0.12351
| 5:38 | 7.485 | 0.12352
| 5:38 | 7.4853 | 0.12353
| 5:38 | 7.4856 | 0.12353
| 5:38 | 7.4858 | 0.12353
| 5:38 | 7.4861 | 0.12353
| 5:38 | 7.4864 | 0.12353
| 5:38 | 7.4867 | 0.12353
| 5:38 | 7.4869 | 0.12352
| 5:38 | 7.4872 | 0.12351
| 5:38 | 7.4875 | 0.12349
| 5:38 | 7.4878 | 0.12348
| 5:38 | 7.4881 | 0.12348
| 5:38 | 7.4883 | 0.12348
| 5:38 | 7.4886 | 0.12348
| 5:38 | 7.4889 | 0.12349
| 5:38 | 7.4892 | 0.12349
| 5:38 | 7.4894 | 0.12349
| 5:38 | 7.4897 | 0.12349
| 5:38 | 7.49 | 0.12349
| 5:38 | 7.4903 | 0.12348
| 5:38 | 7.4906 | 0.12348
| 5:38 | 7.4908 | 0.12347
| 5:38 | 7.4911 | 0.12346
| 5:38 | 7.4914 | 0.12346
| 5:38 | 7.4917 | 0.12345
| 5:38 | 7.4919 | 0.12345
| 5:38 | 7.4922 | 0.12344
| 5:38 | 7.4925 | 0.12345
| 5:38 | 7.4928 | 0.12345
| 5:38 | 7.4931 | 0.12346
| 5:38 | 7.4933 | 0.12346
| 5:38 | 7.4936 | 0.12346
| 5:38 | 7.4939 | 0.12345
| 5:38 | 7.4942 | 0.12345
| 5:38 | 7.4944 | 0.12344
| 5:38 | 7.4947 | 0.12343
| 5:38 | 7.495 | 0.12341
| 5:39 | 7.4953 | 0.1234
| 5:39 | 7.4956 | 0.1234
| 5:39 | 7.4958 | 0.12339
| 5:39 | 7.4961 | 0.12339
| 5:39 | 7.4964 | 0.12339
| 5:39 | 7.4967 | 0.12339
| 5:39 | 7.4969 | 0.12339
| 5:39 | 7.4972 | 0.1234
| 5:39 | 7.4975 | 0.1234
| 5:39 | 7.4978 | 0.1234
| 5:39 | 7.4981 | 0.1234
| 5:39 | 7.4983 | 0.1234
| 5:39 | 7.4986 | 0.1234
| 5:39 | 7.4989 | 0.1234
| 5:39 | 7.4992 | 0.1234
| 5:39 | 7.4994 | 0.1234
| 5:39 | 7.4997 | 0.1234
| 5:39 | 7.5 | 0.1234
| 5:39 | 7.5003 | 0.1234
| 5:39 | 7.5006 | 0.12339
| 5:39 | 7.5008 | 0.12339
| 5:39 | 7.5011 | 0.12339
| 5:39 | 7.5014 | 0.12338
| 5:39 | 7.5017 | 0.12338
| 5:39 | 7.5019 | 0.12338
| 5:39 | 7.5022 | 0.12337
| 5:39 | 7.5025 | 0.12336
| 5:39 | 7.5028 | 0.12335
| 5:39 | 7.5031 | 0.12334
| 5:39 | 7.5033 | 0.12333
| 5:39 | 7.5036 | 0.12333
| 5:39 | 7.5039 | 0.12333
| 5:39 | 7.5042 | 0.12333
| 5:39 | 7.5044 | 0.12333
| 5:39 | 7.5047 | 0.12333
| 5:39 | 7.505 | 0.12334
| 5:39 | 7.5053 | 0.12334
| 5:39 | 7.5056 | 0.12334
| 5:39 | 7.5058 | 0.12334
| 5:39 | 7.5061 | 0.12334
| 5:39 | 7.5064 | 0.12334
| 5:39 | 7.5067 | 0.12335
| 5:39 | 7.5069 | 0.12335
| 5:39 | 7.5072 | 0.12335
| 5:39 | 7.5075 | 0.12335
| 5:39 | 7.5078 | 0.12335
| 5:39 | 7.5081 | 0.12335
| 5:39 | 7.5083 | 0.12335
| 5:39 | 7.5086 | 0.12335
| 5:39 | 7.5089 | 0.12335
| 5:39 | 7.5092 | 0.12335
| 5:39 | 7.5094 | 0.12335
| 5:39 | 7.5097 | 0.12335
| 5:39 | 7.51 | 0.12334
| 5:39 | 7.5103 | 0.12334
| 5:39 | 7.5106 | 0.12333
| 5:39 | 7.5108 | 0.12333
| 5:39 | 7.5111 | 0.12333
| 5:39 | 7.5114 | 0.12332
| 5:40 | 7.5117 | 0.12332
| 5:40 | 7.5119 | 0.12332
| 5:40 | 7.5122 | 0.12332
| 5:40 | 7.5125 | 0.12332
| 5:40 | 7.5128 | 0.12332
| 5:40 | 7.5131 | 0.12331
| 5:40 | 7.5133 | 0.12331
| 5:40 | 7.5136 | 0.12331
| 5:40 | 7.5139 | 0.12331
| 5:40 | 7.5142 | 0.12331
| 5:40 | 7.5144 | 0.12332
| 5:40 | 7.5147 | 0.12332
| 5:40 | 7.515 | 0.12332
| 5:40 | 7.5153 | 0.12332
| 5:40 | 7.5156 | 0.12332
| 5:40 | 7.5158 | 0.12332
| 5:40 | 7.5161 | 0.12333
| 5:40 | 7.5164 | 0.12333
| 5:40 | 7.5167 | 0.12333
| 5:40 | 7.5169 | 0.12334
| 5:40 | 7.5172 | 0.12334
| 5:40 | 7.5175 | 0.12334
| 5:40 | 7.5178 | 0.12335
| 5:40 | 7.5181 | 0.12335
| 5:40 | 7.5183 | 0.12336
| 5:40 | 7.5186 | 0.12336
| 5:40 | 7.5189 | 0.12337
| 5:40 | 7.5192 | 0.12338
| 5:40 | 7.5194 | 0.12338
| 5:40 | 7.5197 | 0.12339
| 5:40 | 7.52 | 0.1234
| 5:40 | 7.5203 | 0.1234
| 5:40 | 7.5206 | 0.12341
| 5:40 | 7.5208 | 0.12342
| 5:40 | 7.5211 | 0.12343
| 5:40 | 7.5214 | 0.12343
| 5:40 | 7.5217 | 0.12344
| 5:40 | 7.5219 | 0.12345
| 5:40 | 7.5222 | 0.12346
| 5:40 | 7.5225 | 0.12347
| 5:40 | 7.5228 | 0.12348
| 5:40 | 7.5231 | 0.12349
| 5:40 | 7.5233 | 0.1235
| 5:40 | 7.5236 | 0.12351
| 5:40 | 7.5239 | 0.12352
| 5:40 | 7.5242 | 0.12354
| 5:40 | 7.5244 | 0.12355
| 5:40 | 7.5247 | 0.12356
| 5:40 | 7.525 | 0.12357
| 5:40 | 7.5253 | 0.12358
| 5:40 | 7.5256 | 0.1236
| 5:40 | 7.5258 | 0.12361
| 5:40 | 7.5261 | 0.12362
| 5:40 | 7.5264 | 0.12364
| 5:40 | 7.5267 | 0.12365
| 5:40 | 7.5269 | 0.12367
| 5:40 | 7.5272 | 0.12368
| 5:40 | 7.5275 | 0.1237
| 5:40 | 7.5278 | 0.12371
| 5:40 | 7.5281 | 0.12373
| 5:40 | 7.5283 | 0.12374
| 5:41 | 7.5286 | 0.12376
| 5:41 | 7.5289 | 0.12377
| 5:41 | 7.5292 | 0.12378
| 5:41 | 7.5294 | 0.12379
| 5:41 | 7.5297 | 0.12379
| 5:41 | 7.53 | 0.12378
| 5:41 | 7.5303 | 0.12378
| 5:41 | 7.5306 | 0.12377
| 5:41 | 7.5308 | 0.12377
| 5:41 | 7.5311 | 0.12376
| 5:41 | 7.5314 | 0.12376
| 5:41 | 7.5317 | 0.12376
| 5:41 | 7.5319 | 0.12376
| 5:41 | 7.5322 | 0.12376
| 5:41 | 7.5325 | 0.12376
| 5:41 | 7.5328 | 0.12376
| 5:41 | 7.5331 | 0.12377
| 5:41 | 7.5333 | 0.12377
| 5:41 | 7.5336 | 0.12377
| 5:41 | 7.5339 | 0.12378
| 5:41 | 7.5342 | 0.12379
| 5:41 | 7.5344 | 0.12379
| 5:41 | 7.5347 | 0.1238
| 5:41 | 7.535 | 0.12381
| 5:41 | 7.5353 | 0.12382
| 5:41 | 7.5356 | 0.12384
| 5:41 | 7.5358 | 0.12385
| 5:41 | 7.5361 | 0.12387
| 5:41 | 7.5364 | 0.12388
| 5:41 | 7.5367 | 0.12389
| 5:41 | 7.5369 | 0.1239
| 5:41 | 7.5372 | 0.1239
| 5:41 | 7.5375 | 0.12391
| 5:41 | 7.5378 | 0.12391
| 5:41 | 7.5381 | 0.12391
| 5:41 | 7.5383 | 0.12391
| 5:41 | 7.5386 | 0.12392
| 5:41 | 7.5389 | 0.12393
| 5:41 | 7.5392 | 0.12394
| 5:41 | 7.5394 | 0.12395
| 5:41 | 7.5397 | 0.12397
| 5:41 | 7.54 | 0.12398
| 5:41 | 7.5403 | 0.124
| 5:41 | 7.5406 | 0.12402
| 5:41 | 7.5408 | 0.12404
| 5:41 | 7.5411 | 0.12406
| 5:41 | 7.5414 | 0.12408
| 5:41 | 7.5417 | 0.12408
| 5:41 | 7.5419 | 0.12408
| 5:41 | 7.5422 | 0.12409
| 5:41 | 7.5425 | 0.12409
| 5:41 | 7.5428 | 0.12411
| 5:41 | 7.5431 | 0.12413
| 5:41 | 7.5433 | 0.12415
| 5:41 | 7.5436 | 0.12416
| 5:41 | 7.5439 | 0.12418
| 5:41 | 7.5442 | 0.1242
| 5:41 | 7.5444 | 0.12421
| 5:41 | 7.5447 | 0.12423
| 5:42 | 7.545 | 0.12424
| 5:42 | 7.5453 | 0.12425
| 5:42 | 7.5456 | 0.12425
| 5:42 | 7.5458 | 0.12425
| 5:42 | 7.5461 | 0.12426
| 5:42 | 7.5464 | 0.12426
| 5:42 | 7.5467 | 0.12426
| 5:42 | 7.5469 | 0.12427
| 5:42 | 7.5472 | 0.12428
| 5:42 | 7.5475 | 0.12428
| 5:42 | 7.5478 | 0.12429
| 5:42 | 7.5481 | 0.1243
| 5:42 | 7.5483 | 0.12431
| 5:42 | 7.5486 | 0.12432
| 5:42 | 7.5489 | 0.12433
| 5:42 | 7.5492 | 0.12434
| 5:42 | 7.5494 | 0.12435
| 5:42 | 7.5497 | 0.12437
| 5:42 | 7.55 | 0.12438
| 5:42 | 7.5503 | 0.12439
| 5:42 | 7.5506 | 0.12441
| 5:42 | 7.5508 | 0.12443
| 5:42 | 7.5511 | 0.12446
| 5:42 | 7.5514 | 0.12448
| 5:42 | 7.5517 | 0.1245
| 5:42 | 7.5519 | 0.12452
| 5:42 | 7.5522 | 0.12454
| 5:42 | 7.5525 | 0.12455
| 5:42 | 7.5528 | 0.12457
| 5:42 | 7.5531 | 0.12458
| 5:42 | 7.5533 | 0.12458
| 5:42 | 7.5536 | 0.12459
| 5:42 | 7.5539 | 0.1246
| 5:42 | 7.5542 | 0.12462
| 5:42 | 7.5544 | 0.12463
| 5:42 | 7.5547 | 0.12465
| 5:42 | 7.555 | 0.12468
| 5:42 | 7.5553 | 0.1247
| 5:42 | 7.5556 | 0.12473
| 5:42 | 7.5558 | 0.12474
| 5:42 | 7.5561 | 0.12476
| 5:42 | 7.5564 | 0.12477
| 5:42 | 7.5567 | 0.12478
| 5:42 | 7.5569 | 0.12479
| 5:42 | 7.5572 | 0.12479
| 5:42 | 7.5575 | 0.1248
| 5:42 | 7.5578 | 0.12481
| 5:42 | 7.5581 | 0.12482
| 5:42 | 7.5583 | 0.12484
| 5:42 | 7.5586 | 0.12486
| 5:42 | 7.5589 | 0.12489
| 5:42 | 7.5592 | 0.12491
| 5:42 | 7.5594 | 0.12494
| 5:42 | 7.5597 | 0.12496
| 5:42 | 7.56 | 0.12499
| 5:42 | 7.5603 | 0.12501
| 5:42 | 7.5606 | 0.12503
| 5:42 | 7.5608 | 0.12504
| 5:42 | 7.5611 | 0.12505
| 5:42 | 7.5614 | 0.12506
| 5:42 | 7.5617 | 0.12507
| 5:43 | 7.5619 | 0.12509
| 5:43 | 7.5622 | 0.12511
| 5:43 | 7.5625 | 0.12514
| 5:43 | 7.5628 | 0.12517
| 5:43 | 7.5631 | 0.1252
| 5:43 | 7.5633 | 0.12522
| 5:43 | 7.5636 | 0.12525
| 5:43 | 7.5639 | 0.12528
| 5:43 | 7.5642 | 0.12531
| 5:43 | 7.5644 | 0.12533
| 5:43 | 7.5647 | 0.12536
| 5:43 | 7.565 | 0.12539
| 5:43 | 7.5653 | 0.12541
| 5:43 | 7.5656 | 0.12544
| 5:43 | 7.5658 | 0.12546
| 5:43 | 7.5661 | 0.12549
| 5:43 | 7.5664 | 0.12552
| 5:43 | 7.5667 | 0.12554
| 5:43 | 7.5669 | 0.12557
| 5:43 | 7.5672 | 0.12559
| 5:43 | 7.5675 | 0.12561
| 5:43 | 7.5678 | 0.12564
| 5:43 | 7.5681 | 0.12566
| 5:43 | 7.5683 | 0.12569
| 5:43 | 7.5686 | 0.1257
| 5:43 | 7.5689 | 0.12571
| 5:43 | 7.5692 | 0.12573
| 5:43 | 7.5694 | 0.12575
| 5:43 | 7.5697 | 0.12577
| 5:43 | 7.57 | 0.12579
| 5:43 | 7.5703 | 0.12582
| 5:43 | 7.5706 | 0.12585
| 5:43 | 7.5708 | 0.12588
| 5:43 | 7.5711 | 0.12591
| 5:43 | 7.5714 | 0.12593
| 5:43 | 7.5717 | 0.12596
| 5:43 | 7.5719 | 0.12599
| 5:43 | 7.5722 | 0.12602
| 5:43 | 7.5725 | 0.12605
| 5:43 | 7.5728 | 0.12607
| 5:43 | 7.5731 | 0.1261
| 5:43 | 7.5733 | 0.12613
| 5:43 | 7.5736 | 0.12615
| 5:43 | 7.5739 | 0.12618
| 5:43 | 7.5742 | 0.12621
| 5:43 | 7.5744 | 0.12623
| 5:43 | 7.5747 | 0.12626
| 5:43 | 7.575 | 0.12628
| 5:43 | 7.5753 | 0.1263
| 5:43 | 7.5756 | 0.12633
| 5:43 | 7.5758 | 0.12635
| 5:43 | 7.5761 | 0.12637
| 5:43 | 7.5764 | 0.12639
| 5:43 | 7.5767 | 0.1264
| 5:43 | 7.5769 | 0.12641
| 5:43 | 7.5772 | 0.12643
| 5:43 | 7.5775 | 0.12644
| 5:43 | 7.5778 | 0.12646
| 5:43 | 7.5781 | 0.12647
| 5:44 | 7.5783 | 0.12649
| 5:44 | 7.5786 | 0.1265
| 5:44 | 7.5789 | 0.12652
| 5:44 | 7.5792 | 0.12654
| 5:44 | 7.5794 | 0.12655
| 5:44 | 7.5797 | 0.12657
| 5:44 | 7.58 | 0.12659
| 5:44 | 7.5803 | 0.12661
| 5:44 | 7.5806 | 0.12663
| 5:44 | 7.5808 | 0.12665
| 5:44 | 7.5811 | 0.12667
| 5:44 | 7.5814 | 0.12669
| 5:44 | 7.5817 | 0.12672
| 5:44 | 7.5819 | 0.12674
| 5:44 | 7.5822 | 0.12676
| 5:44 | 7.5825 | 0.12679
| 5:44 | 7.5828 | 0.12681
| 5:44 | 7.5831 | 0.12684
| 5:44 | 7.5833 | 0.12687
| 5:44 | 7.5836 | 0.1269
| 5:44 | 7.5839 | 0.12693
| 5:44 | 7.5842 | 0.12695
| 5:44 | 7.5844 | 0.12696
| 5:44 | 7.5847 | 0.12698
| 5:44 | 7.585 | 0.127
| 5:44 | 7.5853 | 0.12702
| 5:44 | 7.5856 | 0.12705
| 5:44 | 7.5858 | 0.12708
| 5:44 | 7.5861 | 0.12711
| 5:44 | 7.5864 | 0.12714
| 5:44 | 7.5867 | 0.12718
| 5:44 | 7.5869 | 0.12721
| 5:44 | 7.5872 | 0.12724
| 5:44 | 7.5875 | 0.12726
| 5:44 | 7.5878 | 0.12729
| 5:44 | 7.5881 | 0.12731
| 5:44 | 7.5883 | 0.12733
| 5:44 | 7.5886 | 0.12735
| 5:44 | 7.5889 | 0.12738
| 5:44 | 7.5892 | 0.12741
| 5:44 | 7.5894 | 0.12744
| 5:44 | 7.5897 | 0.12747
| 5:44 | 7.59 | 0.1275
| 5:44 | 7.5903 | 0.12753
| 5:44 | 7.5906 | 0.12757
| 5:44 | 7.5908 | 0.1276
| 5:44 | 7.5911 | 0.12764
| 5:44 | 7.5914 | 0.12767
| 5:44 | 7.5917 | 0.1277
| 5:44 | 7.5919 | 0.12772
| 5:44 | 7.5922 | 0.12773
| 5:44 | 7.5925 | 0.12775
| 5:44 | 7.5928 | 0.12777
| 5:44 | 7.5931 | 0.12779
| 5:44 | 7.5933 | 0.12782
| 5:44 | 7.5936 | 0.12784
| 5:44 | 7.5939 | 0.12787
| 5:44 | 7.5942 | 0.12791
| 5:44 | 7.5944 | 0.12794
| 5:44 | 7.5947 | 0.12798
| 5:44 | 7.595 | 0.12801
| 5:45 | 7.5953 | 0.12804
| 5:45 | 7.5956 | 0.12806
| 5:45 | 7.5958 | 0.12808
| 5:45 | 7.5961 | 0.1281
| 5:45 | 7.5964 | 0.12812
| 5:45 | 7.5967 | 0.12813
| 5:45 | 7.5969 | 0.12815
| 5:45 | 7.5972 | 0.12817
| 5:45 | 7.5975 | 0.12819
| 5:45 | 7.5978 | 0.12821
| 5:45 | 7.5981 | 0.12823
| 5:45 | 7.5983 | 0.12826
| 5:45 | 7.5986 | 0.12828
| 5:45 | 7.5989 | 0.1283
| 5:45 | 7.5992 | 0.12833
| 5:45 | 7.5994 | 0.12835
| 5:45 | 7.5997 | 0.12838
| 5:45 | 7.6 | 0.1284
| 5:45 | 7.6003 | 0.12843
| 5:45 | 7.6006 | 0.12846
| 5:45 | 7.6008 | 0.12848
| 5:45 | 7.6011 | 0.12851
| 5:45 | 7.6014 | 0.12855
| 5:45 | 7.6017 | 0.12858
| 5:45 | 7.6019 | 0.12862
| 5:45 | 7.6022 | 0.12865
| 5:45 | 7.6025 | 0.12869
| 5:45 | 7.6028 | 0.12872
| 5:45 | 7.6031 | 0.12875
| 5:45 | 7.6033 | 0.12878
| 5:45 | 7.6036 | 0.1288
| 5:45 | 7.6039 | 0.12882
| 5:45 | 7.6042 | 0.12884
| 5:45 | 7.6044 | 0.12886
| 5:45 | 7.6047 | 0.12889
| 5:45 | 7.605 | 0.12892
| 5:45 | 7.6053 | 0.12896
| 5:45 | 7.6056 | 0.129
| 5:45 | 7.6058 | 0.12903
| 5:45 | 7.6061 | 0.12907
| 5:45 | 7.6064 | 0.1291
| 5:45 | 7.6067 | 0.12913
| 5:45 | 7.6069 | 0.12916
| 5:45 | 7.6072 | 0.12919
| 5:45 | 7.6075 | 0.12921
| 5:45 | 7.6078 | 0.12923
| 5:45 | 7.6081 | 0.12925
| 5:45 | 7.6083 | 0.12928
| 5:45 | 7.6086 | 0.1293
| 5:45 | 7.6089 | 0.12933
| 5:45 | 7.6092 | 0.12936
| 5:45 | 7.6094 | 0.1294
| 5:45 | 7.6097 | 0.12944
| 5:45 | 7.61 | 0.12947
| 5:45 | 7.6103 | 0.12951
| 5:45 | 7.6106 | 0.12954
| 5:45 | 7.6108 | 0.12957
| 5:45 | 7.6111 | 0.1296
| 5:45 | 7.6114 | 0.12963
| 5:46 | 7.6117 | 0.12964
| 5:46 | 7.6119 | 0.12966
| 5:46 | 7.6122 | 0.12969
| 5:46 | 7.6125 | 0.12971
| 5:46 | 7.6128 | 0.12974
| 5:46 | 7.6131 | 0.12977
| 5:46 | 7.6133 | 0.1298
| 5:46 | 7.6136 | 0.12984
| 5:46 | 7.6139 | 0.12988
| 5:46 | 7.6142 | 0.12993
| 5:46 | 7.6144 | 0.12996
| 5:46 | 7.6147 | 0.13
| 5:46 | 7.615 | 0.13004
| 5:46 | 7.6153 | 0.13008
| 5:46 | 7.6156 | 0.13012
| 5:46 | 7.6158 | 0.13015
| 5:46 | 7.6161 | 0.13019
| 5:46 | 7.6164 | 0.13023
| 5:46 | 7.6167 | 0.13026
| 5:46 | 7.6169 | 0.13029
| 5:46 | 7.6172 | 0.13032
| 5:46 | 7.6175 | 0.13035
| 5:46 | 7.6178 | 0.13037
| 5:46 | 7.6181 | 0.13038
| 5:46 | 7.6183 | 0.13039
| 5:46 | 7.6186 | 0.1304
| 5:46 | 7.6189 | 0.13041
| 5:46 | 7.6192 | 0.13042
| 5:46 | 7.6194 | 0.13042
| 5:46 | 7.6197 | 0.13043
| 5:46 | 7.62 | 0.13045
| 5:46 | 7.6203 | 0.13047
| 5:46 | 7.6206 | 0.1305
| 5:46 | 7.6208 | 0.13054
| 5:46 | 7.6211 | 0.13058
| 5:46 | 7.6214 | 0.13062
| 5:46 | 7.6217 | 0.13066
| 5:46 | 7.6219 | 0.13069
| 5:46 | 7.6222 | 0.13073
| 5:46 | 7.6225 | 0.13076
| 5:46 | 7.6228 | 0.1308
| 5:46 | 7.6231 | 0.13083
| 5:46 | 7.6233 | 0.13086
| 5:46 | 7.6236 | 0.13089
| 5:46 | 7.6239 | 0.13092
| 5:46 | 7.6242 | 0.13095
| 5:46 | 7.6244 | 0.13098
| 5:46 | 7.6247 | 0.13101
| 5:46 | 7.625 | 0.13103
| 5:46 | 7.6253 | 0.13106
| 5:46 | 7.6256 | 0.13108
| 5:46 | 7.6258 | 0.1311
| 5:46 | 7.6261 | 0.13112
| 5:46 | 7.6264 | 0.13113
| 5:46 | 7.6267 | 0.13114
| 5:46 | 7.6269 | 0.13115
| 5:46 | 7.6272 | 0.13116
| 5:46 | 7.6275 | 0.13117
| 5:46 | 7.6278 | 0.13118
| 5:46 | 7.6281 | 0.13121
| 5:46 | 7.6283 | 0.13124
| 5:47 | 7.6286 | 0.13127
| 5:47 | 7.6289 | 0.13131
| 5:47 | 7.6292 | 0.13134
| 5:47 | 7.6294 | 0.13137
| 5:47 | 7.6297 | 0.1314
| 5:47 | 7.63 | 0.13142
| 5:47 | 7.6303 | 0.13144
| 5:47 | 7.6306 | 0.13146
| 5:47 | 7.6308 | 0.13148
| 5:47 | 7.6311 | 0.1315
| 5:47 | 7.6314 | 0.13151
| 5:47 | 7.6317 | 0.13153
| 5:47 | 7.6319 | 0.13155
| 5:47 | 7.6322 | 0.13157
| 5:47 | 7.6325 | 0.13159
| 5:47 | 7.6328 | 0.13161
| 5:47 | 7.6331 | 0.13162
| 5:47 | 7.6333 | 0.13164
| 5:47 | 7.6336 | 0.13166
| 5:47 | 7.6339 | 0.13168
| 5:47 | 7.6342 | 0.1317
| 5:47 | 7.6344 | 0.13171
| 5:47 | 7.6347 | 0.13172
| 5:47 | 7.635 | 0.13173
| 5:47 | 7.6353 | 0.13175
| 5:47 | 7.6356 | 0.13176
| 5:47 | 7.6358 | 0.13179
| 5:47 | 7.6361 | 0.13182
| 5:47 | 7.6364 | 0.13186
| 5:47 | 7.6367 | 0.13189
| 5:47 | 7.6369 | 0.13192
| 5:47 | 7.6372 | 0.13195
| 5:47 | 7.6375 | 0.13197
| 5:47 | 7.6378 | 0.13198
| 5:47 | 7.6381 | 0.13199
| 5:47 | 7.6383 | 0.13201
| 5:47 | 7.6386 | 0.13201
| 5:47 | 7.6389 | 0.13201
| 5:47 | 7.6392 | 0.13201
| 5:47 | 7.6394 | 0.13201
| 5:47 | 7.6397 | 0.13202
| 5:47 | 7.64 | 0.13202
| 5:47 | 7.6403 | 0.13203
| 5:47 | 7.6406 | 0.13204
| 5:47 | 7.6408 | 0.13206
| 5:47 | 7.6411 | 0.13207
| 5:47 | 7.6414 | 0.13209
| 5:47 | 7.6417 | 0.13212
| 5:47 | 7.6419 | 0.13214
| 5:47 | 7.6422 | 0.13216
| 5:47 | 7.6425 | 0.13216
| 5:47 | 7.6428 | 0.13217
| 5:47 | 7.6431 | 0.13218
| 5:47 | 7.6433 | 0.13219
| 5:47 | 7.6436 | 0.1322
| 5:47 | 7.6439 | 0.13223
| 5:47 | 7.6442 | 0.13227
| 5:47 | 7.6444 | 0.1323
| 5:47 | 7.6447 | 0.13233
| 5:48 | 7.645 | 0.13235
| 5:48 | 7.6453 | 0.13237
| 5:48 | 7.6456 | 0.13239
| 5:48 | 7.6458 | 0.1324
| 5:48 | 7.6461 | 0.13241
| 5:48 | 7.6464 | 0.13241
| 5:48 | 7.6467 | 0.13242
| 5:48 | 7.6469 | 0.13243
| 5:48 | 7.6472 | 0.13244
| 5:48 | 7.6475 | 0.13245
| 5:48 | 7.6478 | 0.13246
| 5:48 | 7.6481 | 0.13248
| 5:48 | 7.6483 | 0.13249
| 5:48 | 7.6486 | 0.13251
| 5:48 | 7.6489 | 0.13253
| 5:48 | 7.6492 | 0.13256
| 5:48 | 7.6494 | 0.13258
| 5:48 | 7.6497 | 0.13261
| 5:48 | 7.65 | 0.13263
| 5:48 | 7.6503 | 0.13264
| 5:48 | 7.6506 | 0.13264
| 5:48 | 7.6508 | 0.13265
| 5:48 | 7.6511 | 0.13265
| 5:48 | 7.6514 | 0.13266
| 5:48 | 7.6517 | 0.13268
| 5:48 | 7.6519 | 0.1327
| 5:48 | 7.6522 | 0.13272
| 5:48 | 7.6525 | 0.13275
| 5:48 | 7.6528 | 0.13277
| 5:48 | 7.6531 | 0.13279
| 5:48 | 7.6533 | 0.13282
| 5:48 | 7.6536 | 0.13284
| 5:48 | 7.6539 | 0.13286
| 5:48 | 7.6542 | 0.13288
| 5:48 | 7.6544 | 0.13289
| 5:48 | 7.6547 | 0.1329
| 5:48 | 7.655 | 0.13292
| 5:48 | 7.6553 | 0.13295
| 5:48 | 7.6556 | 0.13299
| 5:48 | 7.6558 | 0.13302
| 5:48 | 7.6561 | 0.13305
| 5:48 | 7.6564 | 0.13309
| 5:48 | 7.6567 | 0.13312
| 5:48 | 7.6569 | 0.13315
| 5:48 | 7.6572 | 0.13319
| 5:48 | 7.6575 | 0.13321
| 5:48 | 7.6578 | 0.13324
| 5:48 | 7.6581 | 0.13323
| 5:48 | 7.6583 | 0.13324
| 5:48 | 7.6586 | 0.13325
| 5:48 | 7.6589 | 0.13326
| 5:48 | 7.6592 | 0.13328
| 5:48 | 7.6594 | 0.13331
| 5:48 | 7.6597 | 0.13335
| 5:48 | 7.66 | 0.13339
| 5:48 | 7.6603 | 0.13342
| 5:48 | 7.6606 | 0.13344
| 5:48 | 7.6608 | 0.13346
| 5:48 | 7.6611 | 0.13348
| 5:48 | 7.6614 | 0.13349
| 5:48 | 7.6617 | 0.13351
| 5:49 | 7.6619 | 0.13352
| 5:49 | 7.6622 | 0.13352
| 5:49 | 7.6625 | 0.13353
| 5:49 | 7.6628 | 0.13354
| 5:49 | 7.6631 | 0.13355
| 5:49 | 7.6633 | 0.13357
| 5:49 | 7.6636 | 0.13359
| 5:49 | 7.6639 | 0.13361
| 5:49 | 7.6642 | 0.13363
| 5:49 | 7.6644 | 0.13365
| 5:49 | 7.6647 | 0.13368
| 5:49 | 7.665 | 0.1337
| 5:49 | 7.6653 | 0.13372
| 5:49 | 7.6656 | 0.13374
| 5:49 | 7.6658 | 0.13376
| 5:49 | 7.6661 | 0.13378
| 5:49 | 7.6664 | 0.1338
| 5:49 | 7.6667 | 0.13383
| 5:49 | 7.6669 | 0.13385
| 5:49 | 7.6672 | 0.13387
| 5:49 | 7.6675 | 0.1339
| 5:49 | 7.6678 | 0.13393
| 5:49 | 7.6681 | 0.13396
| 5:49 | 7.6683 | 0.13398
| 5:49 | 7.6686 | 0.134
| 5:49 | 7.6689 | 0.13401
| 5:49 | 7.6692 | 0.13402
| 5:49 | 7.6694 | 0.13404
| 5:49 | 7.6697 | 0.13405
| 5:49 | 7.67 | 0.13405
| 5:49 | 7.6703 | 0.13406
| 5:49 | 7.6706 | 0.13407
| 5:49 | 7.6708 | 0.1341
| 5:49 | 7.6711 | 0.13412
| 5:49 | 7.6714 | 0.13416
| 5:49 | 7.6717 | 0.13418
| 5:49 | 7.6719 | 0.1342
| 5:49 | 7.6722 | 0.13422
| 5:49 | 7.6725 | 0.13423
| 5:49 | 7.6728 | 0.13424
| 5:49 | 7.6731 | 0.13425
| 5:49 | 7.6733 | 0.13425
| 5:49 | 7.6736 | 0.13425
| 5:49 | 7.6739 | 0.13425
| 5:49 | 7.6742 | 0.13426
| 5:49 | 7.6744 | 0.13428
| 5:49 | 7.6747 | 0.1343
| 5:49 | 7.675 | 0.13432
| 5:49 | 7.6753 | 0.13435
| 5:49 | 7.6756 | 0.13438
| 5:49 | 7.6758 | 0.13441
| 5:49 | 7.6761 | 0.13443
| 5:49 | 7.6764 | 0.13444
| 5:49 | 7.6767 | 0.13445
| 5:49 | 7.6769 | 0.13447
| 5:49 | 7.6772 | 0.13449
| 5:49 | 7.6775 | 0.1345
| 5:49 | 7.6778 | 0.13451
| 5:49 | 7.6781 | 0.13452
| 5:50 | 7.6783 | 0.13454
| 5:50 | 7.6786 | 0.13456
| 5:50 | 7.6789 | 0.13459
| 5:50 | 7.6792 | 0.13462
| 5:50 | 7.6794 | 0.13464
| 5:50 | 7.6797 | 0.13466
| 5:50 | 7.68 | 0.13468
| 5:50 | 7.6803 | 0.13469
| 5:50 | 7.6806 | 0.1347
| 5:50 | 7.6808 | 0.13471
| 5:50 | 7.6811 | 0.13472
| 5:50 | 7.6814 | 0.13473
| 5:50 | 7.6817 | 0.13474
| 5:50 | 7.6819 | 0.13475
| 5:50 | 7.6822 | 0.13477
| 5:50 | 7.6825 | 0.13478
| 5:50 | 7.6828 | 0.13479
| 5:50 | 7.6831 | 0.1348
| 5:50 | 7.6833 | 0.13482
| 5:50 | 7.6836 | 0.13483
| 5:50 | 7.6839 | 0.13484
| 5:50 | 7.6842 | 0.13485
| 5:50 | 7.6844 | 0.13487
| 5:50 | 7.6847 | 0.13488
| 5:50 | 7.685 | 0.13489
| 5:50 | 7.6853 | 0.13491
| 5:50 | 7.6856 | 0.13493
| 5:50 | 7.6858 | 0.13495
| 5:50 | 7.6861 | 0.13498
| 5:50 | 7.6864 | 0.13501
| 5:50 | 7.6867 | 0.13504
| 5:50 | 7.6869 | 0.13507
| 5:50 | 7.6872 | 0.1351
| 5:50 | 7.6875 | 0.13512
| 5:50 | 7.6878 | 0.13513
| 5:50 | 7.6881 | 0.13514
| 5:50 | 7.6883 | 0.13515
| 5:50 | 7.6886 | 0.13517
| 5:50 | 7.6889 | 0.13518
| 5:50 | 7.6892 | 0.1352
| 5:50 | 7.6894 | 0.13521
| 5:50 | 7.6897 | 0.13523
| 5:50 | 7.69 | 0.13525
| 5:50 | 7.6903 | 0.13527
| 5:50 | 7.6906 | 0.1353
| 5:50 | 7.6908 | 0.13532
| 5:50 | 7.6911 | 0.13534
| 5:50 | 7.6914 | 0.13535
| 5:50 | 7.6917 | 0.13537
| 5:50 | 7.6919 | 0.13537
| 5:50 | 7.6922 | 0.13537
| 5:50 | 7.6925 | 0.13537
| 5:50 | 7.6928 | 0.13537
| 5:50 | 7.6931 | 0.13537
| 5:50 | 7.6933 | 0.13538
| 5:50 | 7.6936 | 0.13539
| 5:50 | 7.6939 | 0.1354
| 5:50 | 7.6942 | 0.13543
| 5:50 | 7.6944 | 0.13546
| 5:50 | 7.6947 | 0.13549
| 5:50 | 7.695 | 0.13551
| 5:51 | 7.6953 | 0.13554
| 5:51 | 7.6956 | 0.13556
| 5:51 | 7.6958 | 0.13557
| 5:51 | 7.6961 | 0.13558
| 5:51 | 7.6964 | 0.1356
| 5:51 | 7.6967 | 0.13561
| 5:51 | 7.6969 | 0.13563
| 5:51 | 7.6972 | 0.13564
| 5:51 | 7.6975 | 0.13566
| 5:51 | 7.6978 | 0.13567
| 5:51 | 7.6981 | 0.13569
| 5:51 | 7.6983 | 0.1357
| 5:51 | 7.6986 | 0.13572
| 5:51 | 7.6989 | 0.13574
| 5:51 | 7.6992 | 0.13575
| 5:51 | 7.6994 | 0.13577
| 5:51 | 7.6997 | 0.13579
| 5:51 | 7.7 | 0.1358
| 5:51 | 7.7003 | 0.13582
| 5:51 | 7.7006 | 0.13584
| 5:51 | 7.7008 | 0.13585
| 5:51 | 7.7011 | 0.13585
| 5:51 | 7.7014 | 0.13587
| 5:51 | 7.7017 | 0.13588
| 5:51 | 7.7019 | 0.1359
| 5:51 | 7.7022 | 0.13593
| 5:51 | 7.7025 | 0.13596
| 5:51 | 7.7028 | 0.136
| 5:51 | 7.7031 | 0.13603
| 5:51 | 7.7033 | 0.13605
| 5:51 | 7.7036 | 0.13607
| 5:51 | 7.7039 | 0.13608
| 5:51 | 7.7042 | 0.1361
| 5:51 | 7.7044 | 0.13611
| 5:51 | 7.7047 | 0.13613
| 5:51 | 7.705 | 0.13613
| 5:51 | 7.7053 | 0.13614
| 5:51 | 7.7056 | 0.13615
| 5:51 | 7.7058 | 0.13616
| 5:51 | 7.7061 | 0.13618
| 5:51 | 7.7064 | 0.1362
| 5:51 | 7.7067 | 0.13622
| 5:51 | 7.7069 | 0.13624
| 5:51 | 7.7072 | 0.13627
| 5:51 | 7.7075 | 0.1363
| 5:51 | 7.7078 | 0.13632
| 5:51 | 7.7081 | 0.13634
| 5:51 | 7.7083 | 0.13636
| 5:51 | 7.7086 | 0.13637
| 5:51 | 7.7089 | 0.13638
| 5:51 | 7.7092 | 0.13639
| 5:51 | 7.7094 | 0.13641
| 5:51 | 7.7097 | 0.13643
| 5:51 | 7.71 | 0.13646
| 5:51 | 7.7103 | 0.13648
| 5:51 | 7.7106 | 0.1365
| 5:51 | 7.7108 | 0.13652
| 5:51 | 7.7111 | 0.13653
| 5:51 | 7.7114 | 0.13654
| 5:52 | 7.7117 | 0.13655
| 5:52 | 7.7119 | 0.13655
| 5:52 | 7.7122 | 0.13656
| 5:52 | 7.7125 | 0.13656
| 5:52 | 7.7128 | 0.13657
| 5:52 | 7.7131 | 0.13659
| 5:52 | 7.7133 | 0.13661
| 5:52 | 7.7136 | 0.13664
| 5:52 | 7.7139 | 0.13668
| 5:52 | 7.7142 | 0.13671
| 5:52 | 7.7144 | 0.13674
| 5:52 | 7.7147 | 0.13677
| 5:52 | 7.715 | 0.1368
| 5:52 | 7.7153 | 0.13684
| 5:52 | 7.7156 | 0.13687
| 5:52 | 7.7158 | 0.1369
| 5:52 | 7.7161 | 0.13693
| 5:52 | 7.7164 | 0.13696
| 5:52 | 7.7167 | 0.13698
| 5:52 | 7.7169 | 0.13701
| 5:52 | 7.7172 | 0.13705
| 5:52 | 7.7175 | 0.13708
| 5:52 | 7.7178 | 0.13713
| 5:52 | 7.7181 | 0.13717
| 5:52 | 7.7183 | 0.13722
| 5:52 | 7.7186 | 0.13726
| 5:52 | 7.7189 | 0.1373
| 5:52 | 7.7192 | 0.13733
| 5:52 | 7.7194 | 0.13735
| 5:52 | 7.7197 | 0.13737
| 5:52 | 7.72 | 0.13739
| 5:52 | 7.7203 | 0.1374
| 5:52 | 7.7206 | 0.13742
| 5:52 | 7.7208 | 0.13745
| 5:52 | 7.7211 | 0.13748
| 5:52 | 7.7214 | 0.13753
| 5:52 | 7.7217 | 0.13757
| 5:52 | 7.7219 | 0.13761
| 5:52 | 7.7222 | 0.13765
| 5:52 | 7.7225 | 0.13769
| 5:52 | 7.7228 | 0.13773
| 5:52 | 7.7231 | 0.13776
| 5:52 | 7.7233 | 0.1378
| 5:52 | 7.7236 | 0.13784
| 5:52 | 7.7239 | 0.13788
| 5:52 | 7.7242 | 0.13791
| 5:52 | 7.7244 | 0.13795
| 5:52 | 7.7247 | 0.13799
| 5:52 | 7.725 | 0.13803
| 5:52 | 7.7253 | 0.13808
| 5:52 | 7.7256 | 0.13813
| 5:52 | 7.7258 | 0.13819
| 5:52 | 7.7261 | 0.13824
| 5:52 | 7.7264 | 0.13829
| 5:52 | 7.7267 | 0.13833
| 5:52 | 7.7269 | 0.13838
| 5:52 | 7.7272 | 0.13842
| 5:52 | 7.7275 | 0.13845
| 5:52 | 7.7278 | 0.13847
| 5:52 | 7.7281 | 0.13849
| 5:52 | 7.7283 | 0.13852
| 5:53 | 7.7286 | 0.13854
| 5:53 | 7.7289 | 0.13858
| 5:53 | 7.7292 | 0.13862
| 5:53 | 7.7294 | 0.13867
| 5:53 | 7.7297 | 0.13872
| 5:53 | 7.73 | 0.13878
| 5:53 | 7.7303 | 0.13841
| 5:53 | 7.7306 | 0.13805
| 5:53 | 7.7308 | 0.13768
| 5:53 | 7.7311 | 0.13731
| 5:53 | 7.7314 | 0.13694
| 5:53 | 7.7317 | 0.13658
| 5:53 | 7.7319 | 0.13621
| 5:53 | 7.7322 | 0.13584
| 5:53 | 7.7325 | 0.13547
| 5:53 | 7.7328 | 0.13511
| 5:53 | 7.7331 | 0.13474
| 5:53 | 7.7333 | 0.13437
| 5:53 | 7.7336 | 0.134
| 5:53 | 7.7339 | 0.13363
| 5:53 | 7.7342 | 0.13327
| 5:53 | 7.7344 | 0.1329
| 5:53 | 7.7347 | 0.13253
| 5:53 | 7.735 | 0.13215
| 5:53 | 7.7353 | 0.13177
| 5:53 | 7.7356 | 0.1314
| 5:53 | 7.7358 | 0.13103
| 5:53 | 7.7361 | 0.13065
| 5:53 | 7.7364 | 0.13028
| 5:53 | 7.7367 | 0.12992
| 5:53 | 7.7369 | 0.12955
| 5:53 | 7.7372 | 0.1292
| 5:53 | 7.7375 | 0.12884
| 5:53 | 7.7378 | 0.12848
| 5:53 | 7.7381 | 0.12812
| 5:53 | 7.7383 | 0.12776
| 5:53 | 7.7386 | 0.12738
| 5:53 | 7.7389 | 0.12701
| 5:53 | 7.7392 | 0.12664
| 5:53 | 7.7394 | 0.12627
| 5:53 | 7.7397 | 0.12591
| 5:53 | 7.74 | 0.12554
| 5:53 | 7.7403 | 0.12518
| 5:53 | 7.7406 | 0.12483
| 5:53 | 7.7408 | 0.12447
| 5:53 | 7.7411 | 0.12411
| 5:53 | 7.7414 | 0.12375
| 5:53 | 7.7417 | 0.1234
| 5:53 | 7.7419 | 0.12304
| 5:53 | 7.7422 | 0.12268
| 5:53 | 7.7425 | 0.12231
| 5:53 | 7.7428 | 0.12194
| 5:53 | 7.7431 | 0.12158
| 5:53 | 7.7433 | 0.12121
| 5:53 | 7.7436 | 0.12085
| 5:53 | 7.7439 | 0.1205
| 5:53 | 7.7442 | 0.12014
| 5:53 | 7.7444 | 0.11979
| 5:53 | 7.7447 | 0.11944
| 5:54 | 7.745 | 0.1191
| 5:54 | 7.7453 | 0.11875
| 5:54 | 7.7456 | 0.1184
| 5:54 | 7.7458 | 0.11805
| 5:54 | 7.7461 | 0.11769
| 5:54 | 7.7464 | 0.11733
| 5:54 | 7.7467 | 0.11697
| 5:54 | 7.7469 | 0.11661
| 5:54 | 7.7472 | 0.11625
| 5:54 | 7.7475 | 0.1159
| 5:54 | 7.7478 | 0.11554
| 5:54 | 7.7481 | 0.11518
| 5:54 | 7.7483 | 0.11483
| 5:54 | 7.7486 | 0.11447
| 5:54 | 7.7489 | 0.11412
| 5:54 | 7.7492 | 0.11376
| 5:54 | 7.7494 | 0.11341
| 5:54 | 7.7497 | 0.11306
| 5:54 | 7.75 | 0.11271
| 5:54 | 7.7503 | 0.11236
| 5:54 | 7.7506 | 0.11201
| 5:54 | 7.7508 | 0.11166
| 5:54 | 7.7511 | 0.11131
| 5:54 | 7.7514 | 0.11096
| 5:54 | 7.7517 | 0.11062
| 5:54 | 7.7519 | 0.11027
| 5:54 | 7.7522 | 0.10993
| 5:54 | 7.7525 | 0.10959
| 5:54 | 7.7528 | 0.10925
| 5:54 | 7.7531 | 0.10891
| 5:54 | 7.7533 | 0.10857
| 5:54 | 7.7536 | 0.10822
| 5:54 | 7.7539 | 0.10788
| 5:54 | 7.7542 | 0.10753
| 5:54 | 7.7544 | 0.10718
| 5:54 | 7.7547 | 0.10683
| 5:54 | 7.755 | 0.10649
| 5:54 | 7.7553 | 0.10614
| 5:54 | 7.7556 | 0.10579
| 5:54 | 7.7558 | 0.10544
| 5:54 | 7.7561 | 0.1051
| 5:54 | 7.7564 | 0.10475
| 5:54 | 7.7567 | 0.10441
| 5:54 | 7.7569 | 0.10406
| 5:54 | 7.7572 | 0.10372
| 5:54 | 7.7575 | 0.10338
| 5:54 | 7.7578 | 0.10303
| 5:54 | 7.7581 | 0.10269
| 5:54 | 7.7583 | 0.10235
| 5:54 | 7.7586 | 0.10201
| 5:54 | 7.7589 | 0.10167
| 5:54 | 7.7592 | 0.10133
| 5:54 | 7.7594 | 0.10099
| 5:54 | 7.7597 | 0.10065
| 5:54 | 7.76 | 0.10031
| 5:54 | 7.7603 | 0.099972
| 5:54 | 7.7606 | 0.099643
| 5:54 | 7.7608 | 0.099308
| 5:54 | 7.7611 | 0.098973
| 5:54 | 7.7614 | 0.098639
| 5:54 | 7.7617 | 0.098305
| 5:55 | 7.7619 | 0.097972
| 5:55 | 7.7622 | 0.09764
| 5:55 | 7.7625 | 0.097308
| 5:55 | 7.7628 | 0.096977
| 5:55 | 7.7631 | 0.096646
| 5:55 | 7.7633 | 0.096316
| 5:55 | 7.7636 | 0.095987
| 5:55 | 7.7639 | 0.095658
| 5:55 | 7.7642 | 0.095329
| 5:55 | 7.7644 | 0.095001
| 5:55 | 7.7647 | 0.094674
| 5:55 | 7.765 | 0.094348
| 5:55 | 7.7653 | 0.094022
| 5:55 | 7.7656 | 0.093696
| 5:55 | 7.7658 | 0.093371
| 5:55 | 7.7661 | 0.093047
| 5:55 | 7.7664 | 0.092723
| 5:55 | 7.7667 | 0.092399
| 5:55 | 7.7669 | 0.092075
| 5:55 | 7.7672 | 0.091752
| 5:55 | 7.7675 | 0.091429
| 5:55 | 7.7678 | 0.091106
| 5:55 | 7.7681 | 0.090784
| 5:55 | 7.7683 | 0.090462
| 5:55 | 7.7686 | 0.09014
| 5:55 | 7.7689 | 0.089819
| 5:55 | 7.7692 | 0.089498
| 5:55 | 7.7694 | 0.089177
| 5:55 | 7.7697 | 0.088856
| 5:55 | 7.77 | 0.088536
| 5:55 | 7.7703 | 0.088216
| 5:55 | 7.7706 | 0.087897
| 5:55 | 7.7708 | 0.087577
| 5:55 | 7.7711 | 0.087258
| 5:55 | 7.7714 | 0.08694
| 5:55 | 7.7717 | 0.086621
| 5:55 | 7.7719 | 0.086303
| 5:55 | 7.7722 | 0.085986
| 5:55 | 7.7725 | 0.085668
| 5:55 | 7.7728 | 0.085351
| 5:55 | 7.7731 | 0.085034
| 5:55 | 7.7733 | 0.084718
| 5:55 | 7.7736 | 0.084401
| 5:55 | 7.7739 | 0.084085
| 5:55 | 7.7742 | 0.08377
| 5:55 | 7.7744 | 0.08346
| 5:55 | 7.7747 | 0.083155
| 5:55 | 7.775 | 0.082854
| 5:55 | 7.7753 | 0.082559
| 5:55 | 7.7756 | 0.082268
| 5:55 | 7.7758 | 0.081983
| 5:55 | 7.7761 | 0.081702
| 5:55 | 7.7764 | 0.081426
| 5:55 | 7.7767 | 0.081156
| 5:55 | 7.7769 | 0.08089
| 5:55 | 7.7772 | 0.080629
| 5:55 | 7.7775 | 0.080372
| 5:55 | 7.7778 | 0.080118
| 5:55 | 7.7781 | 0.079868
| 5:56 | 7.7783 | 0.079622
| 5:56 | 7.7786 | 0.079378
| 5:56 | 7.7789 | 0.079141
| 5:56 | 7.7792 | 0.078911
| 5:56 | 7.7794 | 0.078687
| 5:56 | 7.7797 | 0.07847
| 5:56 | 7.78 | 0.07826
| 5:56 | 7.7803 | 0.078052
| 5:56 | 7.7806 | 0.077844
| 5:56 | 7.7808 | 0.077637
| 5:56 | 7.7811 | 0.077432
| 5:56 | 7.7814 | 0.077227
| 5:56 | 7.7817 | 0.077023
| 5:56 | 7.7819 | 0.076821
| 5:56 | 7.7822 | 0.076619
| 5:56 | 7.7825 | 0.076418
| 5:56 | 7.7828 | 0.076219
| 5:56 | 7.7831 | 0.07602
| 5:56 | 7.7833 | 0.075822
| 5:56 | 7.7836 | 0.075626
| 5:56 | 7.7839 | 0.07543
| 5:56 | 7.7842 | 0.075235
| 5:56 | 7.7844 | 0.075042
| 5:56 | 7.7847 | 0.074849
| 5:56 | 7.785 | 0.074657
| 5:56 | 7.7853 | 0.074459
| 5:56 | 7.7856 | 0.074263
| 5:56 | 7.7858 | 0.074071
| 5:56 | 7.7861 | 0.073882
| 5:56 | 7.7864 | 0.073696
| 5:56 | 7.7867 | 0.073513
| 5:56 | 7.7869 | 0.073333
| 5:56 | 7.7872 | 0.073157
| 5:56 | 7.7875 | 0.072987
| 5:56 | 7.7878 | 0.072824
| 5:56 | 7.7881 | 0.072662
| 5:56 | 7.7883 | 0.072501
| 5:56 | 7.7886 | 0.072341
| 5:56 | 7.7889 | 0.07218
| 5:56 | 7.7892 | 0.07202
| 5:56 | 7.7894 | 0.071859
| 5:56 | 7.7897 | 0.071699
| 5:56 | 7.79 | 0.071539
| 5:56 | 7.7903 | 0.071378
| 5:56 | 7.7906 | 0.071218
| 5:56 | 7.7908 | 0.071057
| 5:56 | 7.7911 | 0.070902
| 5:56 | 7.7914 | 0.070753
| 5:56 | 7.7917 | 0.070618
| 5:56 | 7.7919 | 0.070487
| 5:56 | 7.7922 | 0.070354
| 5:56 | 7.7925 | 0.07022
| 5:56 | 7.7928 | 0.070084
| 5:56 | 7.7931 | 0.069941
| 5:56 | 7.7933 | 0.069801
| 5:56 | 7.7936 | 0.069664
| 5:56 | 7.7939 | 0.06953
| 5:56 | 7.7942 | 0.069398
| 5:56 | 7.7944 | 0.06927
| 5:56 | 7.7947 | 0.069145
| 5:56 | 7.795 | 0.069023
| 5:57 | 7.7953 | 0.068907
| 5:57 | 7.7956 | 0.0688
| 5:57 | 7.7958 | 0.068694
| 5:57 | 7.7961 | 0.068589
| 5:57 | 7.7964 | 0.068485
| 5:57 | 7.7967 | 0.068383
| 5:57 | 7.7969 | 0.068282
| 5:57 | 7.7972 | 0.068181
| 5:57 | 7.7975 | 0.068082
| 5:57 | 7.7978 | 0.067983
| 5:57 | 7.7981 | 0.067885
| 5:57 | 7.7983 | 0.067787
| 5:57 | 7.7986 | 0.067691
| 5:57 | 7.7989 | 0.067595
| 5:57 | 7.7992 | 0.0675
| 5:57 | 7.7994 | 0.067406
| 5:57 | 7.7997 | 0.067313
| 5:57 | 7.8 | 0.06722
| 5:57 | 7.8003 | 0.067128
| 5:57 | 7.8006 | 0.067037
| 5:57 | 7.8008 | 0.066939
| 5:57 | 7.8011 | 0.066846
| 5:57 | 7.8014 | 0.066758
| 5:57 | 7.8017 | 0.066673
| 5:57 | 7.8019 | 0.066594
| 5:57 | 7.8022 | 0.066518
| 5:57 | 7.8025 | 0.066447
| 5:57 | 7.8028 | 0.066377
| 5:57 | 7.8031 | 0.066321
| 5:57 | 7.8033 | 0.066263
| 5:57 | 7.8036 | 0.066205
| 5:57 | 7.8039 | 0.066146
| 5:57 | 7.8042 | 0.066087
| 5:57 | 7.8044 | 0.066027
| 5:57 | 7.8047 | 0.065965
| 5:57 | 7.805 | 0.065899
| 5:57 | 7.8053 | 0.065833
| 5:57 | 7.8056 | 0.065771
| 5:57 | 7.8058 | 0.065714
| 5:57 | 7.8061 | 0.065662
| 5:57 | 7.8064 | 0.065614
| 5:57 | 7.8067 | 0.065571
| 5:57 | 7.8069 | 0.065533
| 5:57 | 7.8072 | 0.065499
| 5:57 | 7.8075 | 0.065463
| 5:57 | 7.8078 | 0.065426
| 5:57 | 7.8081 | 0.065387
| 5:57 | 7.8083 | 0.065347
| 5:57 | 7.8086 | 0.065303
| 5:57 | 7.8089 | 0.065253
| 5:57 | 7.8092 | 0.065205
| 5:57 | 7.8094 | 0.065161
| 5:57 | 7.8097 | 0.065119
| 5:57 | 7.81 | 0.065079
| 5:57 | 7.8103 | 0.06504
| 5:57 | 7.8106 | 0.065002
| 5:57 | 7.8108 | 0.064975
| 5:57 | 7.8111 | 0.064945
| 5:57 | 7.8114 | 0.064912
| 5:58 | 7.8117 | 0.064877
| 5:58 | 7.8119 | 0.06484
| 5:58 | 7.8122 | 0.064799
| 5:58 | 7.8125 | 0.064749
| 5:58 | 7.8128 | 0.064698
| 5:58 | 7.8131 | 0.064647
| 5:58 | 7.8133 | 0.064595
| 5:58 | 7.8136 | 0.064543
| 5:58 | 7.8139 | 0.064491
| 5:58 | 7.8142 | 0.064439
| 5:58 | 7.8144 | 0.064386
| 5:58 | 7.8147 | 0.064334
| 5:58 | 7.815 | 0.064281
| 5:58 | 7.8153 | 0.064227
| 5:58 | 7.8156 | 0.064174
| 5:58 | 7.8158 | 0.06412
| 5:58 | 7.8161 | 0.064066
| 5:58 | 7.8164 | 0.064011
| 5:58 | 7.8167 | 0.063957
| 5:58 | 7.8169 | 0.063902
| 5:58 | 7.8172 | 0.063847
| 5:58 | 7.8175 | 0.063792
| 5:58 | 7.8178 | 0.063736
| 5:58 | 7.8181 | 0.06368
| 5:58 | 7.8183 | 0.063623
| 5:58 | 7.8186 | 0.063574
| 5:58 | 7.8189 | 0.063522
| 5:58 | 7.8192 | 0.063467
| 5:58 | 7.8194 | 0.063409
| 5:58 | 7.8197 | 0.063348
| 5:58 | 7.82 | 0.063284
| 5:58 | 7.8203 | 0.06321
| 5:58 | 7.8206 | 0.063133
| 5:58 | 7.8208 | 0.063055
| 5:58 | 7.8211 | 0.062975
| 5:58 | 7.8214 | 0.062895
| 5:58 | 7.8217 | 0.062813
| 5:58 | 7.8219 | 0.06273
| 5:58 | 7.8222 | 0.062645
| 5:58 | 7.8225 | 0.06256
| 5:58 | 7.8228 | 0.062473
| 5:58 | 7.8231 | 0.062385
| 5:58 | 7.8233 | 0.062295
| 5:58 | 7.8236 | 0.062205
| 5:58 | 7.8239 | 0.062113
| 5:58 | 7.8242 | 0.06202
| 5:58 | 7.8244 | 0.061927
| 5:58 | 7.8247 | 0.061832
| 5:58 | 7.825 | 0.061737
| 5:58 | 7.8253 | 0.061641
| 5:58 | 7.8256 | 0.061545
| 5:58 | 7.8258 | 0.061448
| 5:58 | 7.8261 | 0.06135
| 5:58 | 7.8264 | 0.061262
| 5:58 | 7.8267 | 0.061173
| 5:58 | 7.8269 | 0.061082
| 5:58 | 7.8272 | 0.060989
| 5:58 | 7.8275 | 0.060895
| 5:58 | 7.8278 | 0.060799
| 5:58 | 7.8281 | 0.060702
| 5:58 | 7.8283 | 0.060603
| 5:59 | 7.8286 | 0.060503
| 5:59 | 7.8289 | 0.060402
| 5:59 | 7.8292 | 0.0603
| 5:59 | 7.8294 | 0.060197
| 5:59 | 7.8297 | 0.060092
| 5:59 | 7.83 | 0.059987
| 5:59 | 7.8303 | 0.05988
| 5:59 | 7.8306 | 0.059772
| 5:59 | 7.8308 | 0.059662
| 5:59 | 7.8311 | 0.059552
| 5:59 | 7.8314 | 0.05944
| 5:59 | 7.8317 | 0.059328
| 5:59 | 7.8319 | 0.059214
| 5:59 | 7.8322 | 0.059098
| 5:59 | 7.8325 | 0.058982
| 5:59 | 7.8328 | 0.058864
| 5:59 | 7.8331 | 0.058746
| 5:59 | 7.8333 | 0.05862
| 5:59 | 7.8336 | 0.05849
| 5:59 | 7.8339 | 0.058366
| 5:59 | 7.8342 | 0.058252
| 5:59 | 7.8344 | 0.058139
| 5:59 | 7.8347 | 0.058022
| 5:59 | 7.835 | 0.057901
| 5:59 | 7.8353 | 0.057777
| 5:59 | 7.8356 | 0.057648
| 5:59 | 7.8358 | 0.057509
| 5:59 | 7.8361 | 0.057367
| 5:59 | 7.8364 | 0.057225
| 5:59 | 7.8367 | 0.057081
| 5:59 | 7.8369 | 0.056938
| 5:59 | 7.8372 | 0.056796
| 5:59 | 7.8375 | 0.056656
| 5:59 | 7.8378 | 0.056517
| 5:59 | 7.8381 | 0.056387
| 5:59 | 7.8383 | 0.056253
| 5:59 | 7.8386 | 0.056116
| 5:59 | 7.8389 | 0.055977
| 5:59 | 7.8392 | 0.055836
| 5:59 | 7.8394 | 0.055694
| 5:59 | 7.8397 | 0.055551
| 5:59 | 7.84 | 0.055406
| 5:59 | 7.8403 | 0.05526
| 5:59 | 7.8406 | 0.055112
| 5:59 | 7.8408 | 0.054964
| 5:59 | 7.8411 | 0.054818
| 5:59 | 7.8414 | 0.054675
| 5:59 | 7.8417 | 0.054535
| 5:59 | 7.8419 | 0.054404
| 5:59 | 7.8422 | 0.054278
| 5:59 | 7.8425 | 0.054151
| 5:59 | 7.8428 | 0.054023
| 5:59 | 7.8431 | 0.053893
| 5:59 | 7.8433 | 0.053762
| 5:59 | 7.8436 | 0.05363
| 5:59 | 7.8439 | 0.053494
| 5:59 | 7.8442 | 0.053351
| 5:59 | 7.8444 | 0.053211
| 5:59 | 7.8447 | 0.053073
| 6:00 | 7.845 | 0.052937
| 6:00 | 7.8453 | 0.052804
| 6:00 | 7.8456 | 0.052674
| 6:00 | 7.8458 | 0.052553
| 6:00 | 7.8461 | 0.052434
| 6:00 | 7.8464 | 0.052316
| 6:00 | 7.8467 | 0.052197
| 6:00 | 7.8469 | 0.052078
| 6:00 | 7.8472 | 0.05196
| 6:00 | 7.8475 | 0.051841
| 6:00 | 7.8478 | 0.051722
| 6:00 | 7.8481 | 0.051603
| 6:00 | 7.8483 | 0.051484
| 6:00 | 7.8486 | 0.051364
| 6:00 | 7.8489 | 0.051245
| 6:00 | 7.8492 | 0.051125
| 6:00 | 7.8494 | 0.051006
| 6:00 | 7.8497 | 0.050886
| 6:00 | 7.85 | 0.050766
| 6:00 | 7.8503 | 0.050647
| 6:00 | 7.8506 | 0.050527
| 6:00 | 7.8508 | 0.050407
| 6:00 | 7.8511 | 0.050286
| 6:00 | 7.8514 | 0.050162
| 6:00 | 7.8517 | 0.050034
| 6:00 | 7.8519 | 0.049909
| 6:00 | 7.8522 | 0.049785
| 6:00 | 7.8525 | 0.049663
| 6:00 | 7.8528 | 0.049543
| 6:00 | 7.8531 | 0.049424
| 6:00 | 7.8533 | 0.049308
| 6:00 | 7.8536 | 0.049201
| 6:00 | 7.8539 | 0.049096
| 6:00 | 7.8542 | 0.048988
| 6:00 | 7.8544 | 0.048878
| 6:00 | 7.8547 | 0.048765
| 6:00 | 7.855 | 0.048649
| 6:00 | 7.8553 | 0.048522
| 6:00 | 7.8556 | 0.048397
| 6:00 | 7.8558 | 0.048272
| 6:00 | 7.8561 | 0.048149
| 6:00 | 7.8564 | 0.048028
| 6:00 | 7.8567 | 0.047907
| 6:00 | 7.8569 | 0.047788
| 6:00 | 7.8572 | 0.04767
| 6:00 | 7.8575 | 0.047563
| 6:00 | 7.8578 | 0.047455
| 6:00 | 7.8581 | 0.047344
| 6:00 | 7.8583 | 0.047232
| 6:00 | 7.8586 | 0.047117
| 6:00 | 7.8589 | 0.047
| 6:00 | 7.8592 | 0.046881
| 6:00 | 7.8594 | 0.046752
| 6:00 | 7.8597 | 0.046624
| 6:00 | 7.86 | 0.046497
| 6:00 | 7.8603 | 0.046371
| 6:00 | 7.8606 | 0.046247
| 6:00 | 7.8608 | 0.046124
| 6:00 | 7.8611 | 0.046003
| 6:00 | 7.8614 | 0.045888
| 6:00 | 7.8617 | 0.045779
| 6:01 | 7.8619 | 0.045668
| 6:01 | 7.8622 | 0.045554
| 6:01 | 7.8625 | 0.045438
| 6:01 | 7.8628 | 0.04532
| 6:01 | 7.8631 | 0.045198
| 6:01 | 7.8633 | 0.045071
| 6:01 | 7.8636 | 0.044937
| 6:01 | 7.8639 | 0.044804
| 6:01 | 7.8642 | 0.044671
| 6:01 | 7.8644 | 0.044539
| 6:01 | 7.8647 | 0.044407
| 6:01 | 7.865 | 0.044275
| 6:01 | 7.8653 | 0.044144
| 6:01 | 7.8656 | 0.044013
| 6:01 | 7.8658 | 0.043883
| 6:01 | 7.8661 | 0.043753
| 6:01 | 7.8664 | 0.043623
| 6:01 | 7.8667 | 0.043494
| 6:01 | 7.8669 | 0.043366
| 6:01 | 7.8672 | 0.043237
| 6:01 | 7.8675 | 0.04311
| 6:01 | 7.8678 | 0.042982
| 6:01 | 7.8681 | 0.042855
| 6:01 | 7.8683 | 0.042729
| 6:01 | 7.8686 | 0.042603
| 6:01 | 7.8689 | 0.042477
| 6:01 | 7.8692 | 0.042361
| 6:01 | 7.8694 | 0.042244
| 6:01 | 7.8697 | 0.042124
| 6:01 | 7.87 | 0.042001
| 6:01 | 7.8703 | 0.041877
| 6:01 | 7.8706 | 0.04175
| 6:01 | 7.8708 | 0.041612
| 6:01 | 7.8711 | 0.041474
| 6:01 | 7.8714 | 0.041337
| 6:01 | 7.8717 | 0.041199
| 6:01 | 7.8719 | 0.041062
| 6:01 | 7.8722 | 0.040926
| 6:01 | 7.8725 | 0.04079
| 6:01 | 7.8728 | 0.040654
| 6:01 | 7.8731 | 0.040518
| 6:01 | 7.8733 | 0.040383
| 6:01 | 7.8736 | 0.040247
| 6:01 | 7.8739 | 0.040113
| 6:01 | 7.8742 | 0.039978
| 6:01 | 7.8744 | 0.039844
| 6:01 | 7.8747 | 0.03971
| 6:01 | 7.875 | 0.039575
| 6:01 | 7.8753 | 0.039439
| 6:01 | 7.8756 | 0.039303
| 6:01 | 7.8758 | 0.039165
| 6:01 | 7.8761 | 0.039028
| 6:01 | 7.8764 | 0.038889
| 6:01 | 7.8767 | 0.038755
| 6:01 | 7.8769 | 0.038627
| 6:01 | 7.8772 | 0.038495
| 6:01 | 7.8775 | 0.038359
| 6:01 | 7.8778 | 0.03822
| 6:01 | 7.8781 | 0.038077
| 6:02 | 7.8783 | 0.037931
| 6:02 | 7.8786 | 0.037777
| 6:02 | 7.8789 | 0.03762
| 6:02 | 7.8792 | 0.037464
| 6:02 | 7.8794 | 0.037308
| 6:02 | 7.8797 | 0.037152
| 6:02 | 7.88 | 0.036995
| 6:02 | 7.8803 | 0.036839
| 6:02 | 7.8806 | 0.036683
| 6:02 | 7.8808 | 0.036526
| 6:02 | 7.8811 | 0.03637
| 6:02 | 7.8814 | 0.036213
| 6:02 | 7.8817 | 0.036056
| 6:02 | 7.8819 | 0.0359
| 6:02 | 7.8822 | 0.035743
| 6:02 | 7.8825 | 0.035587
| 6:02 | 7.8828 | 0.03543
| 6:02 | 7.8831 | 0.035273
| 6:02 | 7.8833 | 0.035116
| 6:02 | 7.8836 | 0.03496
| 6:02 | 7.8839 | 0.034803
| 6:02 | 7.8842 | 0.034646
| 6:02 | 7.8844 | 0.034489
| 6:02 | 7.8847 | 0.034342
| 6:02 | 7.885 | 0.034193
| 6:02 | 7.8853 | 0.03404
| 6:02 | 7.8856 | 0.033886
| 6:02 | 7.8858 | 0.033728
| 6:02 | 7.8861 | 0.033568
| 6:02 | 7.8864 | 0.033396
| 6:02 | 7.8867 | 0.033224
| 6:02 | 7.8869 | 0.033054
| 6:02 | 7.8872 | 0.032884
| 6:02 | 7.8875 | 0.032715
| 6:02 | 7.8878 | 0.032547
| 6:02 | 7.8881 | 0.032379
| 6:02 | 7.8883 | 0.032212
| 6:02 | 7.8886 | 0.032053
| 6:02 | 7.8889 | 0.031898
| 6:02 | 7.8892 | 0.031741
| 6:02 | 7.8894 | 0.031582
| 6:02 | 7.8897 | 0.031421
| 6:02 | 7.89 | 0.031257
| 6:02 | 7.8903 | 0.031091
| 6:02 | 7.8906 | 0.030924
| 6:02 | 7.8908 | 0.030754
| 6:02 | 7.8911 | 0.030582
| 6:02 | 7.8914 | 0.0304
| 6:02 | 7.8917 | 0.030218
| 6:02 | 7.8919 | 0.030039
| 6:02 | 7.8922 | 0.029863
| 6:02 | 7.8925 | 0.029702
| 6:02 | 7.8928 | 0.029538
| 6:02 | 7.8931 | 0.029373
| 6:02 | 7.8933 | 0.029206
| 6:02 | 7.8936 | 0.029037
| 6:02 | 7.8939 | 0.028867
| 6:02 | 7.8942 | 0.028688
| 6:02 | 7.8944 | 0.028507
| 6:02 | 7.8947 | 0.028328
| 6:02 | 7.895 | 0.028151
| 6:03 | 7.8953 | 0.027976
| 6:03 | 7.8956 | 0.027802
| 6:03 | 7.8958 | 0.02763
| 6:03 | 7.8961 | 0.02746
| 6:03 | 7.8964 | 0.027297
| 6:03 | 7.8967 | 0.027134
| 6:03 | 7.8969 | 0.026967
| 6:03 | 7.8972 | 0.026798
| 6:03 | 7.8975 | 0.026626
| 6:03 | 7.8978 | 0.026451
| 6:03 | 7.8981 | 0.026274
| 6:03 | 7.8983 | 0.026094
| 6:03 | 7.8986 | 0.025912
| 6:03 | 7.8989 | 0.025726
| 6:03 | 7.8992 | 0.025539
| 6:03 | 7.8994 | 0.025348
| 6:03 | 7.8997 | 0.025156
| 6:03 | 7.9 | 0.024969
| 6:03 | 7.9003 | 0.024785
| 6:03 | 7.9006 | 0.024612
| 6:03 | 7.9008 | 0.024438
| 6:03 | 7.9011 | 0.024261
| 6:03 | 7.9014 | 0.024079
| 6:03 | 7.9017 | 0.023893
| 6:03 | 7.9019 | 0.023699
| 6:03 | 7.9022 | 0.023498
| 6:03 | 7.9025 | 0.023297
| 6:03 | 7.9028 | 0.023097
| 6:03 | 7.9031 | 0.022896
| 6:03 | 7.9033 | 0.022695
| 6:03 | 7.9036 | 0.022494
| 6:03 | 7.9039 | 0.022293
| 6:03 | 7.9042 | 0.022094
| 6:03 | 7.9044 | 0.021904
| 6:03 | 7.9047 | 0.021708
| 6:03 | 7.905 | 0.021504
| 6:03 | 7.9053 | 0.021297
| 6:03 | 7.9056 | 0.021087
| 6:03 | 7.9058 | 0.020875
| 6:03 | 7.9061 | 0.02066
| 6:03 | 7.9064 | 0.020442
| 6:03 | 7.9067 | 0.020221
| 6:03 | 7.9069 | 0.019998
| 6:03 | 7.9072 | 0.019774
| 6:03 | 7.9075 | 0.019552
| 6:03 | 7.9078 | 0.019334
| 6:03 | 7.9081 | 0.019129
| 6:03 | 7.9083 | 0.01892
| 6:03 | 7.9086 | 0.018707
| 6:03 | 7.9089 | 0.018491
| 6:03 | 7.9092 | 0.018272
| 6:03 | 7.9094 | 0.018048
| 6:03 | 7.9097 | 0.017812
| 6:03 | 7.91 | 0.017576
| 6:03 | 7.9103 | 0.01734
| 6:03 | 7.9106 | 0.017105
| 6:03 | 7.9108 | 0.016869
| 6:03 | 7.9111 | 0.016634
| 6:03 | 7.9114 | 0.016399
| 6:04 | 7.9117 | 0.016164
| 6:04 | 7.9119 | 0.015934
| 6:04 | 7.9122 | 0.015711
| 6:04 | 7.9125 | 0.015485
| 6:04 | 7.9128 | 0.015258
| 6:04 | 7.9131 | 0.01503
| 6:04 | 7.9133 | 0.014799
| 6:04 | 7.9136 | 0.014566
| 6:04 | 7.9139 | 0.014335
| 6:04 | 7.9142 | 0.014106
| 6:04 | 7.9144 | 0.01388
| 6:04 | 7.9147 | 0.013657
| 6:04 | 7.915 | 0.013437
| 6:04 | 7.9153 | 0.013219
| 6:04 | 7.9156 | 0.013003
| 6:04 | 7.9158 | 0.01279
| 6:04 | 7.9161 | 0.012578
| 6:04 | 7.9164 | 0.012364
| 6:04 | 7.9167 | 0.012149
| 6:04 | 7.9169 | 0.011933
| 6:04 | 7.9172 | 0.011716
| 6:04 | 7.9175 | 0.011488
| 6:04 | 7.9178 | 0.01126
| 6:04 | 7.9181 | 0.011033
| 6:04 | 7.9183 | 0.010806
| 6:04 | 7.9186 | 0.010579
| 6:04 | 7.9189 | 0.010352
| 6:04 | 7.9192 | 0.010125
| 6:04 | 7.9194 | 0.009898
| 6:04 | 7.9197 | 0.0096742
| 6:04 | 7.92 | 0.0094569
| 6:04 | 7.9203 | 0.0092352
| 6:04 | 7.9206 | 0.0090092
| 6:04 | 7.9208 | 0.0087787
| 6:04 | 7.9211 | 0.0085429
| 6:04 | 7.9214 | 0.0082966
| 6:04 | 7.9217 | 0.0080548
| 6:04 | 7.9219 | 0.0078152
| 6:04 | 7.9222 | 0.0075761
| 6:04 | 7.9225 | 0.0073377
| 6:04 | 7.9228 | 0.0070999
| 6:04 | 7.9231 | 0.0068628
| 6:04 | 7.9233 | 0.0066263
| 6:04 | 7.9236 | 0.0063904
| 6:04 | 7.9239 | 0.006154
| 6:04 | 7.9242 | 0.0059084
| 6:04 | 7.9244 | 0.0056545
| 6:04 | 7.9247 | 0.0053992
| 6:04 | 7.925 | 0.0051424
| 6:04 | 7.9253 | 0.0048841
| 6:04 | 7.9256 | 0.0046245
| 6:04 | 7.9258 | 0.0043633
| 6:04 | 7.9261 | 0.0041008
| 6:04 | 7.9264 | 0.0038367
| 6:04 | 7.9267 | 0.0035713
| 6:04 | 7.9269 | 0.0033043
| 6:04 | 7.9272 | 0.003036
| 6:04 | 7.9275 | 0.0027686
| 6:04 | 7.9278 | 0.0025107
| 6:04 | 7.9281 | 0.0022473
| 6:04 | 7.9283 | 0.0019786
| 6:05 | 7.9286 | 0.0017046
| 6:05 | 7.9289 | 0.0014279
| 6:05 | 7.9292 | 0.0011503
| 6:05 | 7.9294 | 0.00087191
| 6:05 | 7.9297 | 0.00059271
| 6:05 | 7.93 | 0.00031269
| 6:05 | 7.9303 | 3.1852e-05
| 6:05 | 7.9306 | -0.00024981
| 6:05 | 7.9308 | -0.00053229
| 6:05 | 7.9311 | -0.00081559
| 6:05 | 7.9314 | -0.0010997
| 6:05 | 7.9317 | -0.0013847
| 6:05 | 7.9319 | -0.0016704
| 6:05 | 7.9322 | -0.001957
| 6:05 | 7.9325 | -0.0022444
| 6:05 | 7.9328 | -0.0025327
| 6:05 | 7.9331 | -0.0028218
| 6:05 | 7.9333 | -0.0031116
| 6:05 | 7.9336 | -0.0034024
| 6:05 | 7.9339 | -0.0036939
| 6:05 | 7.9342 | -0.0039863
| 6:05 | 7.9344 | -0.0042795
| 6:05 | 7.9347 | -0.0045735
| 6:05 | 7.935 | -0.0048683
| 6:05 | 7.9353 | -0.005164
| 6:05 | 7.9356 | -0.0054636
| 6:05 | 7.9358 | -0.0057698
| 6:05 | 7.9361 | -0.0060827
| 6:05 | 7.9364 | -0.0063991
| 6:05 | 7.9367 | -0.0067164
| 6:05 | 7.9369 | -0.0070345
| 6:05 | 7.9372 | -0.0073518
| 6:05 | 7.9375 | -0.0076674
| 6:05 | 7.9378 | -0.0079813
| 6:05 | 7.9381 | -0.0082935
| 6:05 | 7.9383 | -0.008604
| 6:05 | 7.9386 | -0.0089128
| 6:05 | 7.9389 | -0.0092199
| 6:05 | 7.9392 | -0.0095253
| 6:05 | 7.9394 | -0.0098289
| 6:05 | 7.9397 | -0.010131
| 6:05 | 7.94 | -0.010431
| 6:05 | 7.9403 | -0.01073
| 6:05 | 7.9406 | -0.011027
| 6:05 | 7.9408 | -0.011322
| 6:05 | 7.9411 | -0.011615
| 6:05 | 7.9414 | -0.011907
| 6:05 | 7.9417 | -0.012197
| 6:05 | 7.9419 | -0.012485
| 6:05 | 7.9422 | -0.012772
| 6:05 | 7.9425 | -0.013057
| 6:05 | 7.9428 | -0.01334
| 6:05 | 7.9431 | -0.013621
| 6:05 | 7.9433 | -0.013903
| 6:05 | 7.9436 | -0.014187
| 6:05 | 7.9439 | -0.014474
| 6:05 | 7.9442 | -0.014762
| 6:05 | 7.9444 | -0.015054
| 6:05 | 7.9447 | -0.015344
| 6:06 | 7.945 | -0.015633
| 6:06 | 7.9453 | -0.01592
| 6:06 | 7.9456 | -0.016207
| 6:06 | 7.9458 | -0.016492
| 6:06 | 7.9461 | -0.016777
| 6:06 | 7.9464 | -0.01706
| 6:06 | 7.9467 | -0.017341
| 6:06 | 7.9469 | -0.017622
| 6:06 | 7.9472 | -0.017901
| 6:06 | 7.9475 | -0.01818
| 6:06 | 7.9478 | -0.018457
| 6:06 | 7.9481 | -0.018733
| 6:06 | 7.9483 | -0.019008
| 6:06 | 7.9486 | -0.019281
| 6:06 | 7.9489 | -0.019554
| 6:06 | 7.9492 | -0.019825
| 6:06 | 7.9494 | -0.020095
| 6:06 | 7.9497 | -0.020364
| 6:06 | 7.95 | -0.020631
| 6:06 | 7.9503 | -0.020898
| 6:06 | 7.9506 | -0.02117
| 6:06 | 7.9508 | -0.021433
| 6:06 | 7.9511 | -0.021702
| 6:06 | 7.9514 | -0.021977
| 6:06 | 7.9517 | -0.022256
| 6:06 | 7.9519 | -0.022541
| 6:06 | 7.9522 | -0.022829
| 6:06 | 7.9525 | -0.023131
| 6:06 | 7.9528 | -0.023436
| 6:06 | 7.9531 | -0.023741
| 6:06 | 7.9533 | -0.024046
| 6:06 | 7.9536 | -0.024347
| 6:06 | 7.9539 | -0.024645
| 6:06 | 7.9542 | -0.024941
| 6:06 | 7.9544 | -0.025233
| 6:06 | 7.9547 | -0.025522
| 6:06 | 7.955 | -0.025798
| 6:06 | 7.9553 | -0.026077
| 6:06 | 7.9556 | -0.02636
| 6:06 | 7.9558 | -0.026646
| 6:06 | 7.9561 | -0.026932
| 6:06 | 7.9564 | -0.027221
| 6:06 | 7.9567 | -0.027511
| 6:06 | 7.9569 | -0.027803
| 6:06 | 7.9572 | -0.028096
| 6:06 | 7.9575 | -0.028391
| 6:06 | 7.9578 | -0.028683
| 6:06 | 7.9581 | -0.028972
| 6:06 | 7.9583 | -0.029257
| 6:06 | 7.9586 | -0.02953
| 6:06 | 7.9589 | -0.029804
| 6:06 | 7.9592 | -0.030081
| 6:06 | 7.9594 | -0.030362
| 6:06 | 7.9597 | -0.030647
| 6:06 | 7.96 | -0.03093
| 6:06 | 7.9603 | -0.031213
| 6:06 | 7.9606 | -0.031493
| 6:06 | 7.9608 | -0.031772
| 6:06 | 7.9611 | -0.032049
| 6:06 | 7.9614 | -0.032325
| 6:06 | 7.9617 | -0.032599
| 6:07 | 7.9619 | -0.032871
| 6:07 | 7.9622 | -0.033142
| 6:07 | 7.9625 | -0.033411
| 6:07 | 7.9628 | -0.033682
| 6:07 | 7.9631 | -0.033961
| 6:07 | 7.9633 | -0.034244
| 6:07 | 7.9636 | -0.034529
| 6:07 | 7.9639 | -0.034814
| 6:07 | 7.9642 | -0.035099
| 6:07 | 7.9644 | -0.035386
| 6:07 | 7.9647 | -0.035673
| 6:07 | 7.965 | -0.03596
| 6:07 | 7.9653 | -0.036249
| 6:07 | 7.9656 | -0.036538
| 6:07 | 7.9658 | -0.036828
| 6:07 | 7.9661 | -0.037118
| 6:07 | 7.9664 | -0.037409
| 6:07 | 7.9667 | -0.037701
| 6:07 | 7.9669 | -0.037993
| 6:07 | 7.9672 | -0.038287
| 6:07 | 7.9675 | -0.03858
| 6:07 | 7.9678 | -0.038875
| 6:07 | 7.9681 | -0.03917
| 6:07 | 7.9683 | -0.039466
| 6:07 | 7.9686 | -0.039761
| 6:07 | 7.9689 | -0.040053
| 6:07 | 7.9692 | -0.040343
| 6:07 | 7.9694 | -0.040629
| 6:07 | 7.9697 | -0.040914
| 6:07 | 7.97 | -0.041191
| 6:07 | 7.9703 | -0.041464
| 6:07 | 7.9706 | -0.041743
| 6:07 | 7.9708 | -0.042028
| 6:07 | 7.9711 | -0.042316
| 6:07 | 7.9714 | -0.042606
| 6:07 | 7.9717 | -0.042897
| 6:07 | 7.9719 | -0.04319
| 6:07 | 7.9722 | -0.043484
| 6:07 | 7.9725 | -0.04378
| 6:07 | 7.9728 | -0.044076
| 6:07 | 7.9731 | -0.044374
| 6:07 | 7.9733 | -0.044674
| 6:07 | 7.9736 | -0.044975
| 6:07 | 7.9739 | -0.045277
| 6:07 | 7.9742 | -0.045581
| 6:07 | 7.9744 | -0.045886
| 6:07 | 7.9747 | -0.046192
| 6:07 | 7.975 | -0.046501
| 6:07 | 7.9753 | -0.046812
| 6:07 | 7.9756 | -0.047125
| 6:07 | 7.9758 | -0.047439
| 6:07 | 7.9761 | -0.047756
| 6:07 | 7.9764 | -0.048074
| 6:07 | 7.9767 | -0.048395
| 6:07 | 7.9769 | -0.048717
| 6:07 | 7.9772 | -0.049038
| 6:07 | 7.9775 | -0.049353
| 6:07 | 7.9778 | -0.049663
| 6:07 | 7.9781 | -0.049967
| 6:08 | 7.9783 | -0.050273
| 6:08 | 7.9786 | -0.050583
| 6:08 | 7.9789 | -0.050897
| 6:08 | 7.9792 | -0.051215
| 6:08 | 7.9794 | -0.051536
| 6:08 | 7.9797 | -0.051869
| 6:08 | 7.98 | -0.052204
| 6:08 | 7.9803 | -0.052117
| 6:08 | 7.9806 | -0.052031
| 6:08 | 7.9808 | -0.051947
| 6:08 | 7.9811 | -0.051864
| 6:08 | 7.9814 | -0.051783
| 6:08 | 7.9817 | -0.051704
| 6:08 | 7.9819 | -0.051625
| 6:08 | 7.9822 | -0.051549
| 6:08 | 7.9825 | -0.051474
| 6:08 | 7.9828 | -0.0514
| 6:08 | 7.9831 | -0.051328
| 6:08 | 7.9833 | -0.051258
| 6:08 | 7.9836 | -0.051189
| 6:08 | 7.9839 | -0.051121
| 6:08 | 7.9842 | -0.051055
| 6:08 | 7.9844 | -0.050991
| 6:08 | 7.9847 | -0.050928
| 6:08 | 7.985 | -0.050866
| 6:08 | 7.9853 | -0.050807
| 6:08 | 7.9856 | -0.050748
| 6:08 | 7.9858 | -0.050691
| 6:08 | 7.9861 | -0.050636
| 6:08 | 7.9864 | -0.050582
| 6:08 | 7.9867 | -0.05053
| 6:08 | 7.9869 | -0.050479
| 6:08 | 7.9872 | -0.05043
| 6:08 | 7.9875 | -0.050382
| 6:08 | 7.9878 | -0.050336
| 6:08 | 7.9881 | -0.050291
| 6:08 | 7.9883 | -0.050248
| 6:08 | 7.9886 | -0.050206
| 6:08 | 7.9889 | -0.050166
| 6:08 | 7.9892 | -0.050128
| 6:08 | 7.9894 | -0.050091
| 6:08 | 7.9897 | -0.050056
| 6:08 | 7.99 | -0.050023
| 6:08 | 7.9903 | -0.049992
| 6:08 | 7.9906 | -0.049962
| 6:08 | 7.9908 | -0.049934
| 6:08 | 7.9911 | -0.049907
| 6:08 | 7.9914 | -0.04988
| 6:08 | 7.9917 | -0.049854
| 6:08 | 7.9919 | -0.049827
| 6:08 | 7.9922 | -0.049801
| 6:08 | 7.9925 | -0.049775
| 6:08 | 7.9928 | -0.049749
| 6:08 | 7.9931 | -0.049724
| 6:08 | 7.9933 | -0.049699
| 6:08 | 7.9936 | -0.049674
| 6:08 | 7.9939 | -0.049649
| 6:08 | 7.9942 | -0.049625
| 6:08 | 7.9944 | -0.049601
| 6:08 | 7.9947 | -0.049577
| 6:08 | 7.995 | -0.049553
| 6:09 | 7.9953 | -0.04953
| 6:09 | 7.9956 | -0.049507
| 6:09 | 7.9958 | -0.049484
| 6:09 | 7.9961 | -0.049461
| 6:09 | 7.9964 | -0.049439
| 6:09 | 7.9967 | -0.049417
| 6:09 | 7.9969 | -0.049395
| 6:09 | 7.9972 | -0.049373
| 6:09 | 7.9975 | -0.049352
| 6:09 | 7.9978 | -0.049331
| 6:09 | 7.9981 | -0.04931
| 6:09 | 7.9983 | -0.04929
| 6:09 | 7.9986 | -0.049269
| 6:09 | 7.9989 | -0.049249
| 6:09 | 7.9992 | -0.049229
| 6:09 | 7.9994 | -0.04921
| 6:09 | 7.9997 | -0.049191
| 6:09 | 8 | -0.049172
| 6:09 | 8.0003 | -0.049153
| 6:09 | 8.0006 | -0.049134
| 6:09 | 8.0008 | -0.049116
| 6:09 | 8.0011 | -0.049098
| 6:09 | 8.0014 | -0.04908
| 6:09 | 8.0017 | -0.049062
| 6:09 | 8.0019 | -0.049045
| 6:09 | 8.0022 | -0.049028
| 6:09 | 8.0025 | -0.049011
| 6:09 | 8.0028 | -0.048994
| 6:09 | 8.0031 | -0.048978
| 6:09 | 8.0033 | -0.048962
| 6:09 | 8.0036 | -0.048946
| 6:09 | 8.0039 | -0.04893
| 6:09 | 8.0042 | -0.048915
| 6:09 | 8.0044 | -0.048899
| 6:09 | 8.0047 | -0.048884
| 6:09 | 8.005 | -0.04887
| 6:09 | 8.0053 | -0.048855
| 6:09 | 8.0056 | -0.048841
| 6:09 | 8.0058 | -0.048827
| 6:09 | 8.0061 | -0.048813
| 6:09 | 8.0064 | -0.0488
| 6:09 | 8.0067 | -0.048786
| 6:09 | 8.0069 | -0.048773
| 6:09 | 8.0072 | -0.04876
| 6:09 | 8.0075 | -0.048748
| 6:09 | 8.0078 | -0.048735
| 6:09 | 8.0081 | -0.048723
| 6:09 | 8.0083 | -0.048711
| 6:09 | 8.0086 | -0.0487
| 6:09 | 8.0089 | -0.048688
| 6:09 | 8.0092 | -0.048677
| 6:09 | 8.0094 | -0.048666
| 6:09 | 8.0097 | -0.048656
| 6:09 | 8.01 | -0.048645
| 6:09 | 8.0103 | -0.048635
| 6:09 | 8.0106 | -0.048625
| 6:09 | 8.0108 | -0.048616
| 6:09 | 8.0111 | -0.048606
| 6:09 | 8.0114 | -0.048598
| 6:09 | 8.0117 | -0.048591
| 6:10 | 8.0119 | -0.048585
| 6:10 | 8.0122 | -0.048581
| 6:10 | 8.0125 | -0.048577
| 6:10 | 8.0128 | -0.048575
| 6:10 | 8.0131 | -0.048574
| 6:10 | 8.0133 | -0.048575
| 6:10 | 8.0136 | -0.048576
| 6:10 | 8.0139 | -0.048579
| 6:10 | 8.0142 | -0.048584
| 6:10 | 8.0144 | -0.048589
| 6:10 | 8.0147 | -0.048596
| 6:10 | 8.015 | -0.048604
| 6:10 | 8.0153 | -0.048613
| 6:10 | 8.0156 | -0.048624
| 6:10 | 8.0158 | -0.048636
| 6:10 | 8.0161 | -0.048649
| 6:10 | 8.0164 | -0.048663
| 6:10 | 8.0167 | -0.048678
| 6:10 | 8.0169 | -0.048694
| 6:10 | 8.0172 | -0.048711
| 6:10 | 8.0175 | -0.048729
| 6:10 | 8.0178 | -0.048748
| 6:10 | 8.0181 | -0.048768
| 6:10 | 8.0183 | -0.048789
| 6:10 | 8.0186 | -0.048811
| 6:10 | 8.0189 | -0.048834
| 6:10 | 8.0192 | -0.048858
| 6:10 | 8.0194 | -0.048883
| 6:10 | 8.0197 | -0.048909
| 6:10 | 8.02 | -0.048937
| 6:10 | 8.0203 | -0.048965
| 6:10 | 8.0206 | -0.048994
| 6:10 | 8.0208 | -0.049024
| 6:10 | 8.0211 | -0.049055
| 6:10 | 8.0214 | -0.049087
| 6:10 | 8.0217 | -0.049121
| 6:10 | 8.0219 | -0.049155
| 6:10 | 8.0222 | -0.04919
| 6:10 | 8.0225 | -0.049226
| 6:10 | 8.0228 | -0.049264
| 6:10 | 8.0231 | -0.049302
| 6:10 | 8.0233 | -0.049341
| 6:10 | 8.0236 | -0.049381
| 6:10 | 8.0239 | -0.049423
| 6:10 | 8.0242 | -0.049465
| 6:10 | 8.0244 | -0.049514
| 6:10 | 8.0247 | -0.049568
| 6:10 | 8.025 | -0.049627
| 6:10 | 8.0253 | -0.049691
| 6:10 | 8.0256 | -0.049761
| 6:10 | 8.0258 | -0.049836
| 6:10 | 8.0261 | -0.049917
| 6:10 | 8.0264 | -0.050003
| 6:10 | 8.0267 | -0.050094
| 6:10 | 8.0269 | -0.05019
| 6:10 | 8.0272 | -0.050292
| 6:10 | 8.0275 | -0.050398
| 6:10 | 8.0278 | -0.050509
| 6:10 | 8.0281 | -0.050622
| 6:10 | 8.0283 | -0.05074
| 6:11 | 8.0286 | -0.050862
| 6:11 | 8.0289 | -0.050987
| 6:11 | 8.0292 | -0.051115
| 6:11 | 8.0294 | -0.051245
| 6:11 | 8.0297 | -0.051377
| 6:11 | 8.03 | -0.05151
| 6:11 | 8.0303 | -0.051646
| 6:11 | 8.0306 | -0.051783
| 6:11 | 8.0308 | -0.051923
| 6:11 | 8.0311 | -0.052064
| 6:11 | 8.0314 | -0.052207
| 6:11 | 8.0317 | -0.052352
| 6:11 | 8.0319 | -0.052499
| 6:11 | 8.0322 | -0.052647
| 6:11 | 8.0325 | -0.052798
| 6:11 | 8.0328 | -0.05295
| 6:11 | 8.0331 | -0.053104
| 6:11 | 8.0333 | -0.05326
| 6:11 | 8.0336 | -0.053418
| 6:11 | 8.0339 | -0.053578
| 6:11 | 8.0342 | -0.05374
| 6:11 | 8.0344 | -0.053903
| 6:11 | 8.0347 | -0.054069
| 6:11 | 8.035 | -0.054236
| 6:11 | 8.0353 | -0.054405
| 6:11 | 8.0356 | -0.054576
| 6:11 | 8.0358 | -0.054749
| 6:11 | 8.0361 | -0.054924
| 6:11 | 8.0364 | -0.0551
| 6:11 | 8.0367 | -0.055279
| 6:11 | 8.0369 | -0.055459
| 6:11 | 8.0372 | -0.055642
| 6:11 | 8.0375 | -0.055828
| 6:11 | 8.0378 | -0.056017
| 6:11 | 8.0381 | -0.056209
| 6:11 | 8.0383 | -0.056405
| 6:11 | 8.0386 | -0.056603
| 6:11 | 8.0389 | -0.056803
| 6:11 | 8.0392 | -0.057006
| 6:11 | 8.0394 | -0.05721
| 6:11 | 8.0397 | -0.057417
| 6:11 | 8.04 | -0.057625
| 6:11 | 8.0403 | -0.057836
| 6:11 | 8.0406 | -0.058048
| 6:11 | 8.0408 | -0.058263
| 6:11 | 8.0411 | -0.05848
| 6:11 | 8.0414 | -0.058699
| 6:11 | 8.0417 | -0.058919
| 6:11 | 8.0419 | -0.059142
| 6:11 | 8.0422 | -0.059367
| 6:11 | 8.0425 | -0.059594
| 6:11 | 8.0428 | -0.059823
| 6:11 | 8.0431 | -0.060054
| 6:11 | 8.0433 | -0.060287
| 6:11 | 8.0436 | -0.060522
| 6:11 | 8.0439 | -0.060759
| 6:11 | 8.0442 | -0.060998
| 6:11 | 8.0444 | -0.061239
| 6:11 | 8.0447 | -0.061482
| 6:12 | 8.045 | -0.061727
| 6:12 | 8.0453 | -0.061974
| 6:12 | 8.0456 | -0.062223
| 6:12 | 8.0458 | -0.062473
| 6:12 | 8.0461 | -0.062726
| 6:12 | 8.0464 | -0.062981
| 6:12 | 8.0467 | -0.063238
| 6:12 | 8.0469 | -0.063497
| 6:12 | 8.0472 | -0.063758
| 6:12 | 8.0475 | -0.06402
| 6:12 | 8.0478 | -0.064284
| 6:12 | 8.0481 | -0.064549
| 6:12 | 8.0483 | -0.064816
| 6:12 | 8.0486 | -0.065085
| 6:12 | 8.0489 | -0.065356
| 6:12 | 8.0492 | -0.065628
| 6:12 | 8.0494 | -0.065901
| 6:12 | 8.0497 | -0.066175
| 6:12 | 8.05 | -0.066449
| 6:12 | 8.0503 | -0.066725
| 6:12 | 8.0506 | -0.067001
| 6:12 | 8.0508 | -0.067279
| 6:12 | 8.0511 | -0.067559
| 6:12 | 8.0514 | -0.067842
| 6:12 | 8.0517 | -0.068128
| 6:12 | 8.0519 | -0.068416
| 6:12 | 8.0522 | -0.068706
| 6:12 | 8.0525 | -0.068998
| 6:12 | 8.0528 | -0.069291
| 6:12 | 8.0531 | -0.069585
| 6:12 | 8.0533 | -0.069879
| 6:12 | 8.0536 | -0.070174
| 6:12 | 8.0539 | -0.070469
| 6:12 | 8.0542 | -0.070765
| 6:12 | 8.0544 | -0.071062
| 6:12 | 8.0547 | -0.071359
| 6:12 | 8.055 | -0.071657
| 6:12 | 8.0553 | -0.071956
| 6:12 | 8.0556 | -0.072255
| 6:12 | 8.0558 | -0.072555
| 6:12 | 8.0561 | -0.072856
| 6:12 | 8.0564 | -0.073157
| 6:12 | 8.0567 | -0.073458
| 6:12 | 8.0569 | -0.073761
| 6:12 | 8.0572 | -0.074064
| 6:12 | 8.0575 | -0.074368
| 6:12 | 8.0578 | -0.074672
| 6:12 | 8.0581 | -0.074977
| 6:12 | 8.0583 | -0.075282
| 6:12 | 8.0586 | -0.075589
| 6:12 | 8.0589 | -0.075896
| 6:12 | 8.0592 | -0.076203
| 6:12 | 8.0594 | -0.076511
| 6:12 | 8.0597 | -0.07682
| 6:12 | 8.06 | -0.077129
| 6:12 | 8.0603 | -0.077436
| 6:12 | 8.0606 | -0.077742
| 6:12 | 8.0608 | -0.078047
| 6:12 | 8.0611 | -0.078351
| 6:12 | 8.0614 | -0.078653
| 6:13 | 8.0617 | -0.078954
| 6:13 | 8.0619 | -0.079254
| 6:13 | 8.0622 | -0.079553
| 6:13 | 8.0625 | -0.07985
| 6:13 | 8.0628 | -0.080146
| 6:13 | 8.0631 | -0.08044
| 6:13 | 8.0633 | -0.080734
| 6:13 | 8.0636 | -0.081026
| 6:13 | 8.0639 | -0.081316
| 6:13 | 8.0642 | -0.081605
| 6:13 | 8.0644 | -0.081891
| 6:13 | 8.0647 | -0.082176
| 6:13 | 8.065 | -0.082459
| 6:13 | 8.0653 | -0.082739
| 6:13 | 8.0656 | -0.083018
| 6:13 | 8.0658 | -0.083295
| 6:13 | 8.0661 | -0.08357
| 6:13 | 8.0664 | -0.083844
| 6:13 | 8.0667 | -0.084116
| 6:13 | 8.0669 | -0.084388
| 6:13 | 8.0672 | -0.084658
| 6:13 | 8.0675 | -0.084927
| 6:13 | 8.0678 | -0.085195
| 6:13 | 8.0681 | -0.085462
| 6:13 | 8.0683 | -0.085726
| 6:13 | 8.0686 | -0.085988
| 6:13 | 8.0689 | -0.086248
| 6:13 | 8.0692 | -0.086506
| 6:13 | 8.0694 | -0.086761
| 6:13 | 8.0697 | -0.087014
| 6:13 | 8.07 | -0.087265
| 6:13 | 8.0703 | -0.087514
| 6:13 | 8.0706 | -0.08776
| 6:13 | 8.0708 | -0.088004
| 6:13 | 8.0711 | -0.088246
| 6:13 | 8.0714 | -0.088486
| 6:13 | 8.0717 | -0.088723
| 6:13 | 8.0719 | -0.088958
| 6:13 | 8.0722 | -0.089191
| 6:13 | 8.0725 | -0.089422
| 6:13 | 8.0728 | -0.08965
| 6:13 | 8.0731 | -0.089876
| 6:13 | 8.0733 | -0.0901
| 6:13 | 8.0736 | -0.090321
| 6:13 | 8.0739 | -0.090541
| 6:13 | 8.0742 | -0.090758
| 6:13 | 8.0744 | -0.090973
| 6:13 | 8.0747 | -0.091187
| 6:13 | 8.075 | -0.091399
| 6:13 | 8.0753 | -0.09161
| 6:13 | 8.0756 | -0.091818
| 6:13 | 8.0758 | -0.092025
| 6:13 | 8.0761 | -0.092231
| 6:13 | 8.0764 | -0.092434
| 6:13 | 8.0767 | -0.092636
| 6:13 | 8.0769 | -0.092836
| 6:13 | 8.0772 | -0.093035
| 6:13 | 8.0775 | -0.093231
| 6:13 | 8.0778 | -0.093426
| 6:13 | 8.0781 | -0.09362
| 6:14 | 8.0783 | -0.093813
| 6:14 | 8.0786 | -0.094005
| 6:14 | 8.0789 | -0.094197
| 6:14 | 8.0792 | -0.094388
| 6:14 | 8.0794 | -0.094579
| 6:14 | 8.0797 | -0.094769
| 6:14 | 8.08 | -0.094958
| 6:14 | 8.0803 | -0.095147
| 6:14 | 8.0806 | -0.095335
| 6:14 | 8.0808 | -0.095523
| 6:14 | 8.0811 | -0.09571
| 6:14 | 8.0814 | -0.095896
| 6:14 | 8.0817 | -0.096082
| 6:14 | 8.0819 | -0.096267
| 6:14 | 8.0822 | -0.096452
| 6:14 | 8.0825 | -0.096636
| 6:14 | 8.0828 | -0.096819
| 6:14 | 8.0831 | -0.097002
| 6:14 | 8.0833 | -0.097184
| 6:14 | 8.0836 | -0.097365
| 6:14 | 8.0839 | -0.097546
| 6:14 | 8.0842 | -0.097727
| 6:14 | 8.0844 | -0.097906
| 6:14 | 8.0847 | -0.098085
| 6:14 | 8.085 | -0.098261
| 6:14 | 8.0853 | -0.098435
| 6:14 | 8.0856 | -0.098608
| 6:14 | 8.0858 | -0.098779
| 6:14 | 8.0861 | -0.098948
| 6:14 | 8.0864 | -0.099115
| 6:14 | 8.0867 | -0.09928
| 6:14 | 8.0869 | -0.099444
| 6:14 | 8.0872 | -0.099609
| 6:14 | 8.0875 | -0.099774
| 6:14 | 8.0878 | -0.099939
| 6:14 | 8.0881 | -0.1001
| 6:14 | 8.0883 | -0.10027
| 6:14 | 8.0886 | -0.10043
| 6:14 | 8.0889 | -0.1006
| 6:14 | 8.0892 | -0.10076
| 6:14 | 8.0894 | -0.10093
| 6:14 | 8.0897 | -0.10109
| 6:14 | 8.09 | -0.10126
| 6:14 | 8.0903 | -0.10142
| 6:14 | 8.0906 | -0.10159
| 6:14 | 8.0908 | -0.10176
| 6:14 | 8.0911 | -0.10192
| 6:14 | 8.0914 | -0.10209
| 6:14 | 8.0917 | -0.10226
| 6:14 | 8.0919 | -0.10242
| 6:14 | 8.0922 | -0.10259
| 6:14 | 8.0925 | -0.10276
| 6:14 | 8.0928 | -0.10293
| 6:14 | 8.0931 | -0.1031
| 6:14 | 8.0933 | -0.10327
| 6:14 | 8.0936 | -0.10344
| 6:14 | 8.0939 | -0.10361
| 6:14 | 8.0942 | -0.10379
| 6:14 | 8.0944 | -0.10396
| 6:14 | 8.0947 | -0.10413
| 6:14 | 8.095 | -0.10431
| 6:15 | 8.0953 | -0.10448
| 6:15 | 8.0956 | -0.10466
| 6:15 | 8.0958 | -0.10483
| 6:15 | 8.0961 | -0.10501
| 6:15 | 8.0964 | -0.10519
| 6:15 | 8.0967 | -0.10537
| 6:15 | 8.0969 | -0.10555
| 6:15 | 8.0972 | -0.10573
| 6:15 | 8.0975 | -0.10591
| 6:15 | 8.0978 | -0.10609
| 6:15 | 8.0981 | -0.10627
| 6:15 | 8.0983 | -0.10645
| 6:15 | 8.0986 | -0.10663
| 6:15 | 8.0989 | -0.10682
| 6:15 | 8.0992 | -0.107
| 6:15 | 8.0994 | -0.10718
| 6:15 | 8.0997 | -0.10737
| 6:15 | 8.1 | -0.10755
| 6:15 | 8.1003 | -0.10774
| 6:15 | 8.1006 | -0.10792
| 6:15 | 8.1008 | -0.1081
| 6:15 | 8.1011 | -0.10828
| 6:15 | 8.1014 | -0.10846
| 6:15 | 8.1017 | -0.10864
| 6:15 | 8.1019 | -0.10882
| 6:15 | 8.1022 | -0.109
| 6:15 | 8.1025 | -0.10917
| 6:15 | 8.1028 | -0.10935
| 6:15 | 8.1031 | -0.10953
| 6:15 | 8.1033 | -0.1097
| 6:15 | 8.1036 | -0.10988
| 6:15 | 8.1039 | -0.11005
| 6:15 | 8.1042 | -0.11022
| 6:15 | 8.1044 | -0.11039
| 6:15 | 8.1047 | -0.11056
| 6:15 | 8.105 | -0.11072
| 6:15 | 8.1053 | -0.11089
| 6:15 | 8.1056 | -0.11105
| 6:15 | 8.1058 | -0.11121
| 6:15 | 8.1061 | -0.11137
| 6:15 | 8.1064 | -0.11153
| 6:15 | 8.1067 | -0.11169
| 6:15 | 8.1069 | -0.11185
| 6:15 | 8.1072 | -0.112
| 6:15 | 8.1075 | -0.11215
| 6:15 | 8.1078 | -0.11231
| 6:15 | 8.1081 | -0.11246
| 6:15 | 8.1083 | -0.1126
| 6:15 | 8.1086 | -0.11275
| 6:15 | 8.1089 | -0.1129
| 6:15 | 8.1092 | -0.11304
| 6:15 | 8.1094 | -0.11318
| 6:15 | 8.1097 | -0.11333
| 6:15 | 8.11 | -0.11347
| 6:15 | 8.1103 | -0.1136
| 6:15 | 8.1106 | -0.11374
| 6:15 | 8.1108 | -0.11388
| 6:15 | 8.1111 | -0.11401
| 6:15 | 8.1114 | -0.11414
| 6:16 | 8.1117 | -0.11427
| 6:16 | 8.1119 | -0.1144
| 6:16 | 8.1122 | -0.11453
| 6:16 | 8.1125 | -0.11465
| 6:16 | 8.1128 | -0.11477
| 6:16 | 8.1131 | -0.11489
| 6:16 | 8.1133 | -0.115
| 6:16 | 8.1136 | -0.11511
| 6:16 | 8.1139 | -0.11522
| 6:16 | 8.1142 | -0.11533
| 6:16 | 8.1144 | -0.11543
| 6:16 | 8.1147 | -0.11553
| 6:16 | 8.115 | -0.11563
| 6:16 | 8.1153 | -0.11573
| 6:16 | 8.1156 | -0.11582
| 6:16 | 8.1158 | -0.11591
| 6:16 | 8.1161 | -0.116
| 6:16 | 8.1164 | -0.11608
| 6:16 | 8.1167 | -0.11617
| 6:16 | 8.1169 | -0.11625
| 6:16 | 8.1172 | -0.11633
| 6:16 | 8.1175 | -0.11642
| 6:16 | 8.1178 | -0.11649
| 6:16 | 8.1181 | -0.11656
| 6:16 | 8.1183 | -0.11663
| 6:16 | 8.1186 | -0.11669
| 6:16 | 8.1189 | -0.11675
| 6:16 | 8.1192 | -0.1168
| 6:16 | 8.1194 | -0.11685
| 6:16 | 8.1197 | -0.11689
| 6:16 | 8.12 | -0.11693
| 6:16 | 8.1203 | -0.11696
| 6:16 | 8.1206 | -0.11699
| 6:16 | 8.1208 | -0.11701
| 6:16 | 8.1211 | -0.11703
| 6:16 | 8.1214 | -0.11704
| 6:16 | 8.1217 | -0.11705
| 6:16 | 8.1219 | -0.11705
| 6:16 | 8.1222 | -0.11705
| 6:16 | 8.1225 | -0.11704
| 6:16 | 8.1228 | -0.11703
| 6:16 | 8.1231 | -0.11702
| 6:16 | 8.1233 | -0.11699
| 6:16 | 8.1236 | -0.11697
| 6:16 | 8.1239 | -0.11694
| 6:16 | 8.1242 | -0.1169
| 6:16 | 8.1244 | -0.11686
| 6:16 | 8.1247 | -0.11681
| 6:16 | 8.125 | -0.11676
| 6:16 | 8.1253 | -0.1167
| 6:16 | 8.1256 | -0.11664
| 6:16 | 8.1258 | -0.11657
| 6:16 | 8.1261 | -0.11649
| 6:16 | 8.1264 | -0.11641
| 6:16 | 8.1267 | -0.11632
| 6:16 | 8.1269 | -0.11623
| 6:16 | 8.1272 | -0.11613
| 6:16 | 8.1275 | -0.11602
| 6:16 | 8.1278 | -0.11591
| 6:16 | 8.1281 | -0.11579
| 6:16 | 8.1283 | -0.11567
| 6:17 | 8.1286 | -0.11554
| 6:17 | 8.1289 | -0.11541
| 6:17 | 8.1292 | -0.11527
| 6:17 | 8.1294 | -0.11512
| 6:17 | 8.1297 | -0.11497
| 6:17 | 8.13 | -0.11482
| 6:17 | 8.1303 | -0.11465
| 6:17 | 8.1306 | -0.11449
| 6:17 | 8.1308 | -0.11432
| 6:17 | 8.1311 | -0.11414
| 6:17 | 8.1314 | -0.11396
| 6:17 | 8.1317 | -0.11377
| 6:17 | 8.1319 | -0.11358
| 6:17 | 8.1322 | -0.11338
| 6:17 | 8.1325 | -0.11317
| 6:17 | 8.1328 | -0.11296
| 6:17 | 8.1331 | -0.11276
| 6:17 | 8.1333 | -0.11255
| 6:17 | 8.1336 | -0.11233
| 6:17 | 8.1339 | -0.11212
| 6:17 | 8.1342 | -0.11191
| 6:17 | 8.1344 | -0.1117
| 6:17 | 8.1347 | -0.11148
| 6:17 | 8.135 | -0.11126
| 6:17 | 8.1353 | -0.11105
| 6:17 | 8.1356 | -0.11083
| 6:17 | 8.1358 | -0.11061
| 6:17 | 8.1361 | -0.11039
| 6:17 | 8.1364 | -0.11017
| 6:17 | 8.1367 | -0.10995
| 6:17 | 8.1369 | -0.10973
| 6:17 | 8.1372 | -0.10951
| 6:17 | 8.1375 | -0.10928
| 6:17 | 8.1378 | -0.10906
| 6:17 | 8.1381 | -0.10884
| 6:17 | 8.1383 | -0.10862
| 6:17 | 8.1386 | -0.1084
| 6:17 | 8.1389 | -0.10818
| 6:17 | 8.1392 | -0.10797
| 6:17 | 8.1394 | -0.10775
| 6:17 | 8.1397 | -0.10753
| 6:17 | 8.14 | -0.10732
| 6:17 | 8.1403 | -0.1071
| 6:17 | 8.1406 | -0.10688
| 6:17 | 8.1408 | -0.10667
| 6:17 | 8.1411 | -0.10645
| 6:17 | 8.1414 | -0.10624
| 6:17 | 8.1417 | -0.10603
| 6:17 | 8.1419 | -0.10581
| 6:17 | 8.1422 | -0.1056
| 6:17 | 8.1425 | -0.10539
| 6:17 | 8.1428 | -0.10518
| 6:17 | 8.1431 | -0.10498
| 6:17 | 8.1433 | -0.10477
| 6:17 | 8.1436 | -0.10456
| 6:17 | 8.1439 | -0.10436
| 6:17 | 8.1442 | -0.10416
| 6:17 | 8.1444 | -0.10396
| 6:17 | 8.1447 | -0.10376
| 6:18 | 8.145 | -0.10356
| 6:18 | 8.1453 | -0.10337
| 6:18 | 8.1456 | -0.10317
| 6:18 | 8.1458 | -0.10298
| 6:18 | 8.1461 | -0.10279
| 6:18 | 8.1464 | -0.1026
| 6:18 | 8.1467 | -0.10241
| 6:18 | 8.1469 | -0.10222
| 6:18 | 8.1472 | -0.10204
| 6:18 | 8.1475 | -0.10185
| 6:18 | 8.1478 | -0.10166
| 6:18 | 8.1481 | -0.10148
| 6:18 | 8.1483 | -0.10129
| 6:18 | 8.1486 | -0.10111
| 6:18 | 8.1489 | -0.10092
| 6:18 | 8.1492 | -0.10073
| 6:18 | 8.1494 | -0.10055
| 6:18 | 8.1497 | -0.10036
| 6:18 | 8.15 | -0.10017
| 6:18 | 8.1503 | -0.099988
| 6:18 | 8.1506 | -0.099801
| 6:18 | 8.1508 | -0.099613
| 6:18 | 8.1511 | -0.099425
| 6:18 | 8.1514 | -0.099237
| 6:18 | 8.1517 | -0.099048
| 6:18 | 8.1519 | -0.098858
| 6:18 | 8.1522 | -0.098668
| 6:18 | 8.1525 | -0.098477
| 6:18 | 8.1528 | -0.098286
| 6:18 | 8.1531 | -0.098094
| 6:18 | 8.1533 | -0.097902
| 6:18 | 8.1536 | -0.09771
| 6:18 | 8.1539 | -0.097516
| 6:18 | 8.1542 | -0.097323
| 6:18 | 8.1544 | -0.097128
| 6:18 | 8.1547 | -0.096934
| 6:18 | 8.155 | -0.096742
| 6:18 | 8.1553 | -0.096555
| 6:18 | 8.1556 | -0.096371
| 6:18 | 8.1558 | -0.096188
| 6:18 | 8.1561 | -0.096005
| 6:18 | 8.1564 | -0.095823
| 6:18 | 8.1567 | -0.09564
| 6:18 | 8.1569 | -0.095459
| 6:18 | 8.1572 | -0.095277
| 6:18 | 8.1575 | -0.095096
| 6:18 | 8.1578 | -0.094916
| 6:18 | 8.1581 | -0.094736
| 6:18 | 8.1583 | -0.094556
| 6:18 | 8.1586 | -0.094377
| 6:18 | 8.1589 | -0.094198
| 6:18 | 8.1592 | -0.094019
| 6:18 | 8.1594 | -0.093841
| 6:18 | 8.1597 | -0.093663
| 6:18 | 8.16 | -0.093486
| 6:18 | 8.1603 | -0.093309
| 6:18 | 8.1606 | -0.093133
| 6:18 | 8.1608 | -0.092957
| 6:18 | 8.1611 | -0.092781
| 6:18 | 8.1614 | -0.092606
| 6:18 | 8.1617 | -0.092431
| 6:19 | 8.1619 | -0.092256
| 6:19 | 8.1622 | -0.092082
| 6:19 | 8.1625 | -0.091909
| 6:19 | 8.1628 | -0.091735
| 6:19 | 8.1631 | -0.091563
| 6:19 | 8.1633 | -0.09139
| 6:19 | 8.1636 | -0.091218
| 6:19 | 8.1639 | -0.09105
| 6:19 | 8.1642 | -0.090887
| 6:19 | 8.1644 | -0.090728
| 6:19 | 8.1647 | -0.090575
| 6:19 | 8.165 | -0.090426
| 6:19 | 8.1653 | -0.090283
| 6:19 | 8.1656 | -0.090144
| 6:19 | 8.1658 | -0.09001
| 6:19 | 8.1661 | -0.089879
| 6:19 | 8.1664 | -0.089749
| 6:19 | 8.1667 | -0.08962
| 6:19 | 8.1669 | -0.089492
| 6:19 | 8.1672 | -0.089365
| 6:19 | 8.1675 | -0.08924
| 6:19 | 8.1678 | -0.089116
| 6:19 | 8.1681 | -0.088993
| 6:19 | 8.1683 | -0.08887
| 6:19 | 8.1686 | -0.088746
| 6:19 | 8.1689 | -0.088626
| 6:19 | 8.1692 | -0.088508
| 6:19 | 8.1694 | -0.088395
| 6:19 | 8.1697 | -0.08829
| 6:19 | 8.17 | -0.088192
| 6:19 | 8.1703 | -0.088098
| 6:19 | 8.1706 | -0.088004
| 6:19 | 8.1708 | -0.087912
| 6:19 | 8.1711 | -0.08782
| 6:19 | 8.1714 | -0.087729
| 6:19 | 8.1717 | -0.087638
| 6:19 | 8.1719 | -0.087548
| 6:19 | 8.1722 | -0.087459
| 6:19 | 8.1725 | -0.087371
| 6:19 | 8.1728 | -0.087283
| 6:19 | 8.1731 | -0.087197
| 6:19 | 8.1733 | -0.087111
| 6:19 | 8.1736 | -0.087025
| 6:19 | 8.1739 | -0.086941
| 6:19 | 8.1742 | -0.086857
| 6:19 | 8.1744 | -0.086771
| 6:19 | 8.1747 | -0.086682
| 6:19 | 8.175 | -0.086592
| 6:19 | 8.1753 | -0.086499
| 6:19 | 8.1756 | -0.086403
| 6:19 | 8.1758 | -0.086306
| 6:19 | 8.1761 | -0.086206
| 6:19 | 8.1764 | -0.086104
| 6:19 | 8.1767 | -0.086
| 6:19 | 8.1769 | -0.085893
| 6:19 | 8.1772 | -0.085784
| 6:19 | 8.1775 | -0.085673
| 6:19 | 8.1778 | -0.08556
| 6:19 | 8.1781 | -0.085444
| 6:20 | 8.1783 | -0.085326
| 6:20 | 8.1786 | -0.085206
| 6:20 | 8.1789 | -0.085084
| 6:20 | 8.1792 | -0.084959
| 6:20 | 8.1794 | -0.084832
| 6:20 | 8.1797 | -0.084703
| 6:20 | 8.18 | -0.084571
| 6:20 | 8.1803 | -0.084437
| 6:20 | 8.1806 | -0.084301
| 6:20 | 8.1808 | -0.084163
| 6:20 | 8.1811 | -0.084022
| 6:20 | 8.1814 | -0.083879
| 6:20 | 8.1817 | -0.083734
| 6:20 | 8.1819 | -0.083586
| 6:20 | 8.1822 | -0.083436
| 6:20 | 8.1825 | -0.083284
| 6:20 | 8.1828 | -0.08313
| 6:20 | 8.1831 | -0.082973
| 6:20 | 8.1833 | -0.082815
| 6:20 | 8.1836 | -0.082653
| 6:20 | 8.1839 | -0.08249
| 6:20 | 8.1842 | -0.082324
| 6:20 | 8.1844 | -0.082156
| 6:20 | 8.1847 | -0.081986
| 6:20 | 8.185 | -0.081813
| 6:20 | 8.1853 | -0.081639
| 6:20 | 8.1856 | -0.081462
| 6:20 | 8.1858 | -0.081282
| 6:20 | 8.1861 | -0.081101
| 6:20 | 8.1864 | -0.080917
| 6:20 | 8.1867 | -0.080731
| 6:20 | 8.1869 | -0.080543
| 6:20 | 8.1872 | -0.080358
| 6:20 | 8.1875 | -0.080175
| 6:20 | 8.1878 | -0.079995
| 6:20 | 8.1881 | -0.079818
| 6:20 | 8.1883 | -0.079643
| 6:20 | 8.1886 | -0.079472
| 6:20 | 8.1889 | -0.079304
| 6:20 | 8.1892 | -0.079141
| 6:20 | 8.1894 | -0.078983
| 6:20 | 8.1897 | -0.078831
| 6:20 | 8.19 | -0.078683
| 6:20 | 8.1903 | -0.078541
| 6:20 | 8.1906 | -0.078404
| 6:20 | 8.1908 | -0.078272
| 6:20 | 8.1911 | -0.078146
| 6:20 | 8.1914 | -0.078024
| 6:20 | 8.1917 | -0.077908
| 6:20 | 8.1919 | -0.077797
| 6:20 | 8.1922 | -0.077692
| 6:20 | 8.1925 | -0.077593
| 6:20 | 8.1928 | -0.077498
| 6:20 | 8.1931 | -0.077407
| 6:20 | 8.1933 | -0.077319
| 6:20 | 8.1936 | -0.077235
| 6:20 | 8.1939 | -0.077153
| 6:20 | 8.1942 | -0.077076
| 6:20 | 8.1944 | -0.077002
| 6:20 | 8.1947 | -0.076931
| 6:20 | 8.195 | -0.076864
| 6:21 | 8.1953 | -0.0768
| 6:21 | 8.1956 | -0.076739
| 6:21 | 8.1958 | -0.076682
| 6:21 | 8.1961 | -0.076628
| 6:21 | 8.1964 | -0.076578
| 6:21 | 8.1967 | -0.076531
| 6:21 | 8.1969 | -0.076488
| 6:21 | 8.1972 | -0.076448
| 6:21 | 8.1975 | -0.076411
| 6:21 | 8.1978 | -0.076378
| 6:21 | 8.1981 | -0.076348
| 6:21 | 8.1983 | -0.076321
| 6:21 | 8.1986 | -0.076298
| 6:21 | 8.1989 | -0.076279
| 6:21 | 8.1992 | -0.076262
| 6:21 | 8.1994 | -0.07625
| 6:21 | 8.1997 | -0.07624
| 6:21 | 8.2 | -0.076234
| 6:21 | 8.2003 | -0.076231
| 6:21 | 8.2006 | -0.076226
| 6:21 | 8.2008 | -0.076219
| 6:21 | 8.2011 | -0.076209
| 6:21 | 8.2014 | -0.076199
| 6:21 | 8.2017 | -0.076189
| 6:21 | 8.2019 | -0.076178
| 6:21 | 8.2022 | -0.076168
| 6:21 | 8.2025 | -0.076158
| 6:21 | 8.2028 | -0.076148
| 6:21 | 8.2031 | -0.076138
| 6:21 | 8.2033 | -0.07613
| 6:21 | 8.2036 | -0.076126
| 6:21 | 8.2039 | -0.076126
| 6:21 | 8.2042 | -0.07613
| 6:21 | 8.2044 | -0.076138
| 6:21 | 8.2047 | -0.07615
| 6:21 | 8.205 | -0.076165
| 6:21 | 8.2053 | -0.076185
| 6:21 | 8.2056 | -0.076208
| 6:21 | 8.2058 | -0.076233
| 6:21 | 8.2061 | -0.076261
| 6:21 | 8.2064 | -0.076291
| 6:21 | 8.2067 | -0.076324
| 6:21 | 8.2069 | -0.076359
| 6:21 | 8.2072 | -0.076397
| 6:21 | 8.2075 | -0.076437
| 6:21 | 8.2078 | -0.076478
| 6:21 | 8.2081 | -0.07652
| 6:21 | 8.2083 | -0.076562
| 6:21 | 8.2086 | -0.076605
| 6:21 | 8.2089 | -0.076648
| 6:21 | 8.2092 | -0.076693
| 6:21 | 8.2094 | -0.076737
| 6:21 | 8.2097 | -0.076783
| 6:21 | 8.21 | -0.076829
| 6:21 | 8.2103 | -0.076875
| 6:21 | 8.2106 | -0.076922
| 6:21 | 8.2108 | -0.07697
| 6:21 | 8.2111 | -0.077018
| 6:21 | 8.2114 | -0.077067
| 6:22 | 8.2117 | -0.077117
| 6:22 | 8.2119 | -0.077166
| 6:22 | 8.2122 | -0.077211
| 6:22 | 8.2125 | -0.077253
| 6:22 | 8.2128 | -0.077291
| 6:22 | 8.2131 | -0.077326
| 6:22 | 8.2133 | -0.077357
| 6:22 | 8.2136 | -0.077385
| 6:22 | 8.2139 | -0.07741
| 6:22 | 8.2142 | -0.07743
| 6:22 | 8.2144 | -0.077448
| 6:22 | 8.2147 | -0.077461
| 6:22 | 8.215 | -0.077472
| 6:22 | 8.2153 | -0.077478
| 6:22 | 8.2156 | -0.077481
| 6:22 | 8.2158 | -0.077481
| 6:22 | 8.2161 | -0.077477
| 6:22 | 8.2164 | -0.07747
| 6:22 | 8.2167 | -0.077459
| 6:22 | 8.2169 | -0.077445
| 6:22 | 8.2172 | -0.077427
| 6:22 | 8.2175 | -0.077405
| 6:22 | 8.2178 | -0.077381
| 6:22 | 8.2181 | -0.077352
| 6:22 | 8.2183 | -0.07732
| 6:22 | 8.2186 | -0.077285
| 6:22 | 8.2189 | -0.077246
| 6:22 | 8.2192 | -0.077203
| 6:22 | 8.2194 | -0.077157
| 6:22 | 8.2197 | -0.077107
| 6:22 | 8.22 | -0.077053
| 6:22 | 8.2203 | -0.076994
| 6:22 | 8.2206 | -0.076932
| 6:22 | 8.2208 | -0.076864
| 6:22 | 8.2211 | -0.076793
| 6:22 | 8.2214 | -0.076717
| 6:22 | 8.2217 | -0.076637
| 6:22 | 8.2219 | -0.076552
| 6:22 | 8.2222 | -0.076463
| 6:22 | 8.2225 | -0.07637
| 6:22 | 8.2228 | -0.076273
| 6:22 | 8.2231 | -0.076171
| 6:22 | 8.2233 | -0.076065
| 6:22 | 8.2236 | -0.075955
| 6:22 | 8.2239 | -0.07584
| 6:22 | 8.2242 | -0.075721
| 6:22 | 8.2244 | -0.075597
| 6:22 | 8.2247 | -0.075469
| 6:22 | 8.225 | -0.075336
| 6:22 | 8.2253 | -0.075198
| 6:22 | 8.2256 | -0.075055
| 6:22 | 8.2258 | -0.074908
| 6:22 | 8.2261 | -0.074755
| 6:22 | 8.2264 | -0.074598
| 6:22 | 8.2267 | -0.074436
| 6:22 | 8.2269 | -0.07427
| 6:22 | 8.2272 | -0.074099
| 6:22 | 8.2275 | -0.073924
| 6:22 | 8.2278 | -0.073744
| 6:22 | 8.2281 | -0.073559
| 6:22 | 8.2283 | -0.07337
| 6:23 | 8.2286 | -0.073177
| 6:23 | 8.2289 | -0.072979
| 6:23 | 8.2292 | -0.072779
| 6:23 | 8.2294 | -0.072579
| 6:23 | 8.2297 | -0.072379
| 6:23 | 8.23 | -0.072178
| 6:23 | 8.2303 | -0.071977
| 6:23 | 8.2306 | -0.071775
| 6:23 | 8.2308 | -0.071573
| 6:23 | 8.2311 | -0.07137
| 6:23 | 8.2314 | -0.071167
| 6:23 | 8.2317 | -0.070964
| 6:23 | 8.2319 | -0.07076
| 6:23 | 8.2322 | -0.070556
| 6:23 | 8.2325 | -0.070351
| 6:23 | 8.2328 | -0.070146
| 6:23 | 8.2331 | -0.069941
| 6:23 | 8.2333 | -0.069735
| 6:23 | 8.2336 | -0.069528
| 6:23 | 8.2339 | -0.069321
| 6:23 | 8.2342 | -0.069114
| 6:23 | 8.2344 | -0.068906
| 6:23 | 8.2347 | -0.068698
| 6:23 | 8.235 | -0.06849
| 6:23 | 8.2353 | -0.068281
| 6:23 | 8.2356 | -0.068071
| 6:23 | 8.2358 | -0.067861
| 6:23 | 8.2361 | -0.067651
| 6:23 | 8.2364 | -0.06744
| 6:23 | 8.2367 | -0.067229
| 6:23 | 8.2369 | -0.067018
| 6:23 | 8.2372 | -0.066806
| 6:23 | 8.2375 | -0.066593
| 6:23 | 8.2378 | -0.06638
| 6:23 | 8.2381 | -0.066167
| 6:23 | 8.2383 | -0.065953
| 6:23 | 8.2386 | -0.065739
| 6:23 | 8.2389 | -0.065525
| 6:23 | 8.2392 | -0.065309
| 6:23 | 8.2394 | -0.065093
| 6:23 | 8.2397 | -0.064877
| 6:23 | 8.24 | -0.064659
| 6:23 | 8.2403 | -0.064441
| 6:23 | 8.2406 | -0.064222
| 6:23 | 8.2408 | -0.064003
| 6:23 | 8.2411 | -0.063784
| 6:23 | 8.2414 | -0.063566
| 6:23 | 8.2417 | -0.063349
| 6:23 | 8.2419 | -0.063132
| 6:23 | 8.2422 | -0.062916
| 6:23 | 8.2425 | -0.062702
| 6:23 | 8.2428 | -0.062488
| 6:23 | 8.2431 | -0.062274
| 6:23 | 8.2433 | -0.062062
| 6:23 | 8.2436 | -0.061851
| 6:23 | 8.2439 | -0.06164
| 6:23 | 8.2442 | -0.06143
| 6:23 | 8.2444 | -0.061221
| 6:23 | 8.2447 | -0.061012
| 6:24 | 8.245 | -0.060803
| 6:24 | 8.2453 | -0.060593
| 6:24 | 8.2456 | -0.060383
| 6:24 | 8.2458 | -0.060172
| 6:24 | 8.2461 | -0.059961
| 6:24 | 8.2464 | -0.05975
| 6:24 | 8.2467 | -0.059539
| 6:24 | 8.2469 | -0.059327
| 6:24 | 8.2472 | -0.059114
| 6:24 | 8.2475 | -0.0589
| 6:24 | 8.2478 | -0.058685
| 6:24 | 8.2481 | -0.058467
| 6:24 | 8.2483 | -0.058247
| 6:24 | 8.2486 | -0.058026
| 6:24 | 8.2489 | -0.057802
| 6:24 | 8.2492 | -0.057576
| 6:24 | 8.2494 | -0.057349
| 6:24 | 8.2497 | -0.057119
| 6:24 | 8.25 | -0.056888
| 6:24 | 8.2503 | -0.056654
| 6:24 | 8.2506 | -0.056419
| 6:24 | 8.2508 | -0.056181
| 6:24 | 8.2511 | -0.055941
| 6:24 | 8.2514 | -0.0557
| 6:24 | 8.2517 | -0.055457
| 6:24 | 8.2519 | -0.055211
| 6:24 | 8.2522 | -0.054964
| 6:24 | 8.2525 | -0.054714
| 6:24 | 8.2528 | -0.054463
| 6:24 | 8.2531 | -0.054209
| 6:24 | 8.2533 | -0.053954
| 6:24 | 8.2536 | -0.053697
| 6:24 | 8.2539 | -0.053437
| 6:24 | 8.2542 | -0.053176
| 6:24 | 8.2544 | -0.052913
| 6:24 | 8.2547 | -0.052647
| 6:24 | 8.255 | -0.05238
| 6:24 | 8.2553 | -0.052111
| 6:24 | 8.2556 | -0.05184
| 6:24 | 8.2558 | -0.051567
| 6:24 | 8.2561 | -0.051291
| 6:24 | 8.2564 | -0.051014
| 6:24 | 8.2567 | -0.050735
| 6:24 | 8.2569 | -0.050454
| 6:24 | 8.2572 | -0.050171
| 6:24 | 8.2575 | -0.049886
| 6:24 | 8.2578 | -0.049599
| 6:24 | 8.2581 | -0.04931
| 6:24 | 8.2583 | -0.049019
| 6:24 | 8.2586 | -0.048726
| 6:24 | 8.2589 | -0.048431
| 6:24 | 8.2592 | -0.048134
| 6:24 | 8.2594 | -0.047836
| 6:24 | 8.2597 | -0.047535
| 6:24 | 8.26 | -0.047232
| 6:24 | 8.2603 | -0.046927
| 6:24 | 8.2606 | -0.04662
| 6:24 | 8.2608 | -0.046312
| 6:24 | 8.2611 | -0.046001
| 6:24 | 8.2614 | -0.04569
| 6:24 | 8.2617 | -0.04538
| 6:25 | 8.2619 | -0.045071
| 6:25 | 8.2622 | -0.044762
| 6:25 | 8.2625 | -0.044454
| 6:25 | 8.2628 | -0.044147
| 6:25 | 8.2631 | -0.04384
| 6:25 | 8.2633 | -0.043534
| 6:25 | 8.2636 | -0.043229
| 6:25 | 8.2639 | -0.042924
| 6:25 | 8.2642 | -0.042619
| 6:25 | 8.2644 | -0.042312
| 6:25 | 8.2647 | -0.042004
| 6:25 | 8.265 | -0.041695
| 6:25 | 8.2653 | -0.041384
| 6:25 | 8.2656 | -0.041072
| 6:25 | 8.2658 | -0.040758
| 6:25 | 8.2661 | -0.040443
| 6:25 | 8.2664 | -0.040127
| 6:25 | 8.2667 | -0.039809
| 6:25 | 8.2669 | -0.039489
| 6:25 | 8.2672 | -0.039169
| 6:25 | 8.2675 | -0.038846
| 6:25 | 8.2678 | -0.038523
| 6:25 | 8.2681 | -0.038198
| 6:25 | 8.2683 | -0.037871
| 6:25 | 8.2686 | -0.037544
| 6:25 | 8.2689 | -0.037214
| 6:25 | 8.2692 | -0.036884
| 6:25 | 8.2694 | -0.036551
| 6:25 | 8.2697 | -0.036218
| 6:25 | 8.27 | -0.035883
| 6:25 | 8.2703 | -0.035546
| 6:25 | 8.2706 | -0.035208
| 6:25 | 8.2708 | -0.034869
| 6:25 | 8.2711 | -0.034528
| 6:25 | 8.2714 | -0.034186
| 6:25 | 8.2717 | -0.033842
| 6:25 | 8.2719 | -0.033497
| 6:25 | 8.2722 | -0.033151
| 6:25 | 8.2725 | -0.032803
| 6:25 | 8.2728 | -0.032453
| 6:25 | 8.2731 | -0.032103
| 6:25 | 8.2733 | -0.03175
| 6:25 | 8.2736 | -0.031396
| 6:25 | 8.2739 | -0.031041
| 6:25 | 8.2742 | -0.030685
| 6:25 | 8.2744 | -0.030327
| 6:25 | 8.2747 | -0.029967
| 6:25 | 8.275 | -0.029607
| 6:25 | 8.2753 | -0.029245
| 6:25 | 8.2756 | -0.028882
| 6:25 | 8.2758 | -0.028518
| 6:25 | 8.2761 | -0.028153
| 6:25 | 8.2764 | -0.027787
| 6:25 | 8.2767 | -0.027419
| 6:25 | 8.2769 | -0.027051
| 6:25 | 8.2772 | -0.026681
| 6:25 | 8.2775 | -0.02631
| 6:25 | 8.2778 | -0.025938
| 6:25 | 8.2781 | -0.025566
| 6:26 | 8.2783 | -0.025194
| 6:26 | 8.2786 | -0.024822
| 6:26 | 8.2789 | -0.024451
| 6:26 | 8.2792 | -0.024081
| 6:26 | 8.2794 | -0.023711
| 6:26 | 8.2797 | -0.023341
| 6:26 | 8.28 | -0.022973
| 6:26 | 8.2803 | -0.022604
| 6:26 | 8.2806 | -0.022236
| 6:26 | 8.2808 | -0.021869
| 6:26 | 8.2811 | -0.021503
| 6:26 | 8.2814 | -0.021139
| 6:26 | 8.2817 | -0.020776
| 6:26 | 8.2819 | -0.020414
| 6:26 | 8.2822 | -0.020054
| 6:26 | 8.2825 | -0.019695
| 6:26 | 8.2828 | -0.019337
| 6:26 | 8.2831 | -0.018981
| 6:26 | 8.2833 | -0.018627
| 6:26 | 8.2836 | -0.018273
| 6:26 | 8.2839 | -0.017921
| 6:26 | 8.2842 | -0.017571
| 6:26 | 8.2844 | -0.017222
| 6:26 | 8.2847 | -0.016874
| 6:26 | 8.285 | -0.016528
| 6:26 | 8.2853 | -0.016183
| 6:26 | 8.2856 | -0.015839
| 6:26 | 8.2858 | -0.015497
| 6:26 | 8.2861 | -0.015156
| 6:26 | 8.2864 | -0.014816
| 6:26 | 8.2867 | -0.014478
| 6:26 | 8.2869 | -0.014142
| 6:26 | 8.2872 | -0.013806
| 6:26 | 8.2875 | -0.013473
| 6:26 | 8.2878 | -0.01314
| 6:26 | 8.2881 | -0.012809
| 6:26 | 8.2883 | -0.012479
| 6:26 | 8.2886 | -0.012151
| 6:26 | 8.2889 | -0.011824
| 6:26 | 8.2892 | -0.011498
| 6:26 | 8.2894 | -0.011174
| 6:26 | 8.2897 | -0.010851
| 6:26 | 8.29 | -0.01053
| 6:26 | 8.2903 | -0.01021
| 6:26 | 8.2906 | -0.0098912
| 6:26 | 8.2908 | -0.009574
| 6:26 | 8.2911 | -0.0092582
| 6:26 | 8.2914 | -0.0089437
| 6:26 | 8.2917 | -0.0086307
| 6:26 | 8.2919 | -0.008319
| 6:26 | 8.2922 | -0.0080088
| 6:26 | 8.2925 | -0.0076999
| 6:26 | 8.2928 | -0.0073924
| 6:26 | 8.2931 | -0.0070863
| 6:26 | 8.2933 | -0.0067817
| 6:26 | 8.2936 | -0.0064784
| 6:26 | 8.2939 | -0.0061765
| 6:26 | 8.2942 | -0.005876
| 6:26 | 8.2944 | -0.0055768
| 6:26 | 8.2947 | -0.0052788
| 6:26 | 8.295 | -0.0049811
| 6:27 | 8.2953 | -0.0046837
| 6:27 | 8.2956 | -0.0043866
| 6:27 | 8.2958 | -0.0040899
| 6:27 | 8.2961 | -0.0037935
| 6:27 | 8.2964 | -0.0034974
| 6:27 | 8.2967 | -0.0032017
| 6:27 | 8.2969 | -0.0029063
| 6:27 | 8.2972 | -0.0026117
| 6:27 | 8.2975 | -0.0023188
| 6:27 | 8.2978 | -0.0020276
| 6:27 | 8.2981 | -0.0017382
| 6:27 | 8.2983 | -0.0014505
| 6:27 | 8.2986 | -0.0011645
| 6:27 | 8.2989 | -0.00088028
| 6:27 | 8.2992 | -0.0005978
| 6:27 | 8.2994 | -0.00031759
| 6:27 | 8.2997 | -3.9977e-05
| 6:27 | 8.3 | 0.00023504
| 6:27 | 8.3003 | 0.00050746
| 6:27 | 8.3006 | 0.00077728
| 6:27 | 8.3008 | 0.0010445
| 6:27 | 8.3011 | 0.0013091
| 6:27 | 8.3014 | 0.0015712
| 6:27 | 8.3017 | 0.0018306
| 6:27 | 8.3019 | 0.0020874
| 6:27 | 8.3022 | 0.0023417
| 6:27 | 8.3025 | 0.0025933
| 6:27 | 8.3028 | 0.0028423
| 6:27 | 8.3031 | 0.0030888
| 6:27 | 8.3033 | 0.0033326
| 6:27 | 8.3036 | 0.0035738
| 6:27 | 8.3039 | 0.0038125
| 6:27 | 8.3042 | 0.0040485
| 6:27 | 8.3044 | 0.004282
| 6:27 | 8.3047 | 0.0045129
| 6:27 | 8.305 | 0.0047411
| 6:27 | 8.3053 | 0.0049668
| 6:27 | 8.3056 | 0.0051899
| 6:27 | 8.3058 | 0.0054103
| 6:27 | 8.3061 | 0.0056282
| 6:27 | 8.3064 | 0.0058435
| 6:27 | 8.3067 | 0.0060562
| 6:27 | 8.3069 | 0.0062662
| 6:27 | 8.3072 | 0.0064737
| 6:27 | 8.3075 | 0.0066786
| 6:27 | 8.3078 | 0.0068809
| 6:27 | 8.3081 | 0.0070805
| 6:27 | 8.3083 | 0.0072776
| 6:27 | 8.3086 | 0.0074721
| 6:27 | 8.3089 | 0.0076639
| 6:27 | 8.3092 | 0.0078532
| 6:27 | 8.3094 | 0.0080399
| 6:27 | 8.3097 | 0.008224
| 6:27 | 8.31 | 0.0084054
| 6:27 | 8.3103 | 0.0085843
| 6:27 | 8.3106 | 0.0087606
| 6:27 | 8.3108 | 0.0089343
| 6:27 | 8.3111 | 0.0091053
| 6:27 | 8.3114 | 0.0092713
| 6:28 | 8.3117 | 0.0094312
| 6:28 | 8.3119 | 0.0095849
| 6:28 | 8.3122 | 0.0097325
| 6:28 | 8.3125 | 0.009874
| 6:28 | 8.3128 | 0.010009
| 6:28 | 8.3131 | 0.010139
| 6:28 | 8.3133 | 0.010265
| 6:28 | 8.3136 | 0.01039
| 6:28 | 8.3139 | 0.010513
| 6:28 | 8.3142 | 0.010634
| 6:28 | 8.3144 | 0.010752
| 6:28 | 8.3147 | 0.010868
| 6:28 | 8.315 | 0.010982
| 6:28 | 8.3153 | 0.011093
| 6:28 | 8.3156 | 0.011202
| 6:28 | 8.3158 | 0.011309
| 6:28 | 8.3161 | 0.011412
| 6:28 | 8.3164 | 0.011513
| 6:28 | 8.3167 | 0.01161
| 6:28 | 8.3169 | 0.011703
| 6:28 | 8.3172 | 0.011794
| 6:28 | 8.3175 | 0.011881
| 6:28 | 8.3178 | 0.011964
| 6:28 | 8.3181 | 0.012045
| 6:28 | 8.3183 | 0.012122
| 6:28 | 8.3186 | 0.012196
| 6:28 | 8.3189 | 0.012266
| 6:28 | 8.3192 | 0.012333
| 6:28 | 8.3194 | 0.012397
| 6:28 | 8.3197 | 0.012458
| 6:28 | 8.32 | 0.012515
| 6:28 | 8.3203 | 0.01257
| 6:28 | 8.3206 | 0.01262
| 6:28 | 8.3208 | 0.012668
| 6:28 | 8.3211 | 0.012712
| 6:28 | 8.3214 | 0.012753
| 6:28 | 8.3217 | 0.012791
| 6:28 | 8.3219 | 0.012825
| 6:28 | 8.3222 | 0.012856
| 6:28 | 8.3225 | 0.012884
| 6:28 | 8.3228 | 0.012909
| 6:28 | 8.3231 | 0.01293
| 6:28 | 8.3233 | 0.012948
| 6:28 | 8.3236 | 0.012962
| 6:28 | 8.3239 | 0.012974
| 6:28 | 8.3242 | 0.012982
| 6:28 | 8.3244 | 0.012987
| 6:28 | 8.3247 | 0.012988
| 6:28 | 8.325 | 0.012986
| 6:28 | 8.3253 | 0.012981
| 6:28 | 8.3256 | 0.012973
| 6:28 | 8.3258 | 0.012961
| 6:28 | 8.3261 | 0.012947
| 6:28 | 8.3264 | 0.012928
| 6:28 | 8.3267 | 0.012907
| 6:28 | 8.3269 | 0.012882
| 6:28 | 8.3272 | 0.012854
| 6:28 | 8.3275 | 0.012823
| 6:28 | 8.3278 | 0.012782
| 6:28 | 8.3281 | 0.012728
| 6:28 | 8.3283 | 0.012661
| 6:29 | 8.3286 | 0.012582
| 6:29 | 8.3289 | 0.012492
| 6:29 | 8.3292 | 0.012394
| 6:29 | 8.3294 | 0.012289
| 6:29 | 8.3297 | 0.012177
| 6:29 | 8.33 | 0.01206
| 6:29 | 8.3303 | 0.011937
| 6:29 | 8.3306 | 0.01181
| 6:29 | 8.3308 | 0.011681
| 6:29 | 8.3311 | 0.011549
| 6:29 | 8.3314 | 0.011415
| 6:29 | 8.3317 | 0.011279
| 6:29 | 8.3319 | 0.01114
| 6:29 | 8.3322 | 0.010999
| 6:29 | 8.3325 | 0.010855
| 6:29 | 8.3328 | 0.010711
| 6:29 | 8.3331 | 0.010566
| 6:29 | 8.3333 | 0.010421
| 6:29 | 8.3336 | 0.010276
| 6:29 | 8.3339 | 0.010131
| 6:29 | 8.3342 | 0.0099865
| 6:29 | 8.3344 | 0.0098414
| 6:29 | 8.3347 | 0.0096962
| 6:29 | 8.335 | 0.0095509
| 6:29 | 8.3353 | 0.0094056
| 6:29 | 8.3356 | 0.0092601
| 6:29 | 8.3358 | 0.0091145
| 6:29 | 8.3361 | 0.0089689
| 6:29 | 8.3364 | 0.0088231
| 6:29 | 8.3367 | 0.0086773
| 6:29 | 8.3369 | 0.0085313
| 6:29 | 8.3372 | 0.0083853
| 6:29 | 8.3375 | 0.0082392
| 6:29 | 8.3378 | 0.0080929
| 6:29 | 8.3381 | 0.0079466
| 6:29 | 8.3383 | 0.0078003
| 6:29 | 8.3386 | 0.0076538
| 6:29 | 8.3389 | 0.0075072
| 6:29 | 8.3392 | 0.0073606
| 6:29 | 8.3394 | 0.0072139
| 6:29 | 8.3397 | 0.0070671
| 6:29 | 8.34 | 0.0069202
| 6:29 | 8.3403 | 0.0067733
| 6:29 | 8.3406 | 0.0066262
| 6:29 | 8.3408 | 0.0064791
| 6:29 | 8.3411 | 0.0063319
| 6:29 | 8.3414 | 0.0061846
| 6:29 | 8.3417 | 0.0060372
| 6:29 | 8.3419 | 0.0058898
| 6:29 | 8.3422 | 0.0057423
| 6:29 | 8.3425 | 0.0055947
| 6:29 | 8.3428 | 0.005447
| 6:29 | 8.3431 | 0.0052993
| 6:29 | 8.3433 | 0.0051514
| 6:29 | 8.3436 | 0.0050035
| 6:29 | 8.3439 | 0.0048555
| 6:29 | 8.3442 | 0.0047075
| 6:29 | 8.3444 | 0.0045593
| 6:29 | 8.3447 | 0.0044111
| 6:30 | 8.345 | 0.0042628
| 6:30 | 8.3453 | 0.0041145
| 6:30 | 8.3456 | 0.003966
| 6:30 | 8.3458 | 0.0038175
| 6:30 | 8.3461 | 0.0036689
| 6:30 | 8.3464 | 0.0035203
| 6:30 | 8.3467 | 0.0033716
| 6:30 | 8.3469 | 0.0032227
| 6:30 | 8.3472 | 0.0030739
| 6:30 | 8.3475 | 0.0029249
| 6:30 | 8.3478 | 0.0027759
| 6:30 | 8.3481 | 0.0026268
| 6:30 | 8.3483 | 0.0024777
| 6:30 | 8.3486 | 0.0023284
| 6:30 | 8.3489 | 0.0021791
| 6:30 | 8.3492 | 0.0020298
| 6:30 | 8.3494 | 0.0018802
| 6:30 | 8.3497 | 0.00173
| 6:30 | 8.35 | 0.0015781
| 6:30 | 8.3503 | 0.0014246
| 6:30 | 8.3506 | 0.0012694
| 6:30 | 8.3508 | 0.0011126
| 6:30 | 8.3511 | 0.00095413
| 6:30 | 8.3514 | 0.00079402
| 6:30 | 8.3517 | 0.00063227
| 6:30 | 8.3519 | 0.00046886
| 6:30 | 8.3522 | 0.00030381
| 6:30 | 8.3525 | 0.00013711
| 6:30 | 8.3528 | -3.1234e-05
| 6:30 | 8.3531 | -0.00020123
| 6:30 | 8.3533 | -0.00037286
| 6:30 | 8.3536 | -0.00054615
| 6:30 | 8.3539 | -0.00072108
| 6:30 | 8.3542 | -0.00089766
| 6:30 | 8.3544 | -0.0010759
| 6:30 | 8.3547 | -0.0012558
| 6:30 | 8.355 | -0.0014373
| 6:30 | 8.3553 | -0.0016204
| 6:30 | 8.3556 | -0.0018052
| 6:30 | 8.3558 | -0.0019917
| 6:30 | 8.3561 | -0.0021798
| 6:30 | 8.3564 | -0.0023695
| 6:30 | 8.3567 | -0.0025609
| 6:30 | 8.3569 | -0.0027539
| 6:30 | 8.3572 | -0.0029486
| 6:30 | 8.3575 | -0.0031449
| 6:30 | 8.3578 | -0.0033429
| 6:30 | 8.3581 | -0.0035425
| 6:30 | 8.3583 | -0.0037438
| 6:30 | 8.3586 | -0.0039467
| 6:30 | 8.3589 | -0.0041512
| 6:30 | 8.3592 | -0.0043574
| 6:30 | 8.3594 | -0.0045652
| 6:30 | 8.3597 | -0.0047747
| 6:30 | 8.36 | -0.0049858
| 6:30 | 8.3603 | -0.0051985
| 6:30 | 8.3606 | -0.0054129
| 6:30 | 8.3608 | -0.0056289
| 6:30 | 8.3611 | -0.0058461
| 6:30 | 8.3614 | -0.0060639
| 6:30 | 8.3617 | -0.0062826
| 6:31 | 8.3619 | -0.0065032
| 6:31 | 8.3622 | -0.0067256
| 6:31 | 8.3625 | -0.0069498
| 6:31 | 8.3628 | -0.0071758
| 6:31 | 8.3631 | -0.0074037
| 6:31 | 8.3633 | -0.0076334
| 6:31 | 8.3636 | -0.0078649
| 6:31 | 8.3639 | -0.0080982
| 6:31 | 8.3642 | -0.0083334
| 6:31 | 8.3644 | -0.0085704
| 6:31 | 8.3647 | -0.0088092
| 6:31 | 8.365 | -0.0090498
| 6:31 | 8.3653 | -0.0092922
| 6:31 | 8.3656 | -0.0095365
| 6:31 | 8.3658 | -0.0097826
| 6:31 | 8.3661 | -0.01003
| 6:31 | 8.3664 | -0.010278
| 6:31 | 8.3667 | -0.010527
| 6:31 | 8.3669 | -0.010776
| 6:31 | 8.3672 | -0.011026
| 6:31 | 8.3675 | -0.011276
| 6:31 | 8.3678 | -0.011529
| 6:31 | 8.3681 | -0.011787
| 6:31 | 8.3683 | -0.012049
| 6:31 | 8.3686 | -0.012314
| 6:31 | 8.3689 | -0.012584
| 6:31 | 8.3692 | -0.012858
| 6:31 | 8.3694 | -0.013135
| 6:31 | 8.3697 | -0.013417
| 6:31 | 8.37 | -0.013703
| 6:31 | 8.3703 | -0.013993
| 6:31 | 8.3706 | -0.014287
| 6:31 | 8.3708 | -0.014585
| 6:31 | 8.3711 | -0.014887
| 6:31 | 8.3714 | -0.015193
| 6:31 | 8.3717 | -0.015504
| 6:31 | 8.3719 | -0.015818
| 6:31 | 8.3722 | -0.016136
| 6:31 | 8.3725 | -0.016458
| 6:31 | 8.3728 | -0.016785
| 6:31 | 8.3731 | -0.017115
| 6:31 | 8.3733 | -0.01745
| 6:31 | 8.3736 | -0.017788
| 6:31 | 8.3739 | -0.018131
| 6:31 | 8.3742 | -0.018477
| 6:31 | 8.3744 | -0.018828
| 6:31 | 8.3747 | -0.019183
| 6:31 | 8.375 | -0.019542
| 6:31 | 8.3753 | -0.019904
| 6:31 | 8.3756 | -0.020271
| 6:31 | 8.3758 | -0.020642
| 6:31 | 8.3761 | -0.021017
| 6:31 | 8.3764 | -0.021396
| 6:31 | 8.3767 | -0.021779
| 6:31 | 8.3769 | -0.022166
| 6:31 | 8.3772 | -0.022558
| 6:31 | 8.3775 | -0.022953
| 6:31 | 8.3778 | -0.023352
| 6:31 | 8.3781 | -0.023756
| 6:31 | 8.3783 | -0.024163
| 6:32 | 8.3786 | -0.024575
| 6:32 | 8.3789 | -0.02499
| 6:32 | 8.3792 | -0.02541
| 6:32 | 8.3794 | -0.025834
| 6:32 | 8.3797 | -0.026261
| 6:32 | 8.38 | -0.026693
| 6:32 | 8.3803 | -0.027129
| 6:32 | 8.3806 | -0.027568
| 6:32 | 8.3808 | -0.028009
| 6:32 | 8.3811 | -0.028452
| 6:32 | 8.3814 | -0.028897
| 6:32 | 8.3817 | -0.029344
| 6:32 | 8.3819 | -0.029792
| 6:32 | 8.3822 | -0.030243
| 6:32 | 8.3825 | -0.030695
| 6:32 | 8.3828 | -0.031149
| 6:32 | 8.3831 | -0.031603
| 6:32 | 8.3833 | -0.032056
| 6:32 | 8.3836 | -0.03251
| 6:32 | 8.3839 | -0.032963
| 6:32 | 8.3842 | -0.033415
| 6:32 | 8.3844 | -0.033868
| 6:32 | 8.3847 | -0.03432
| 6:32 | 8.385 | -0.034771
| 6:32 | 8.3853 | -0.035223
| 6:32 | 8.3856 | -0.035674
| 6:32 | 8.3858 | -0.036125
| 6:32 | 8.3861 | -0.036575
| 6:32 | 8.3864 | -0.037026
| 6:32 | 8.3867 | -0.037478
| 6:32 | 8.3869 | -0.037931
| 6:32 | 8.3872 | -0.038383
| 6:32 | 8.3875 | -0.038835
| 6:32 | 8.3878 | -0.039287
| 6:32 | 8.3881 | -0.039738
| 6:32 | 8.3883 | -0.040188
| 6:32 | 8.3886 | -0.040638
| 6:32 | 8.3889 | -0.041088
| 6:32 | 8.3892 | -0.041537
| 6:32 | 8.3894 | -0.041985
| 6:32 | 8.3897 | -0.042433
| 6:32 | 8.39 | -0.042881
| 6:32 | 8.3903 | -0.043328
| 6:32 | 8.3906 | -0.043774
| 6:32 | 8.3908 | -0.04422
| 6:32 | 8.3911 | -0.044666
| 6:32 | 8.3914 | -0.045111
| 6:32 | 8.3917 | -0.045555
| 6:32 | 8.3919 | -0.045999
| 6:32 | 8.3922 | -0.046442
| 6:32 | 8.3925 | -0.046885
| 6:32 | 8.3928 | -0.047328
| 6:32 | 8.3931 | -0.04777
| 6:32 | 8.3933 | -0.048211
| 6:32 | 8.3936 | -0.048652
| 6:32 | 8.3939 | -0.049093
| 6:32 | 8.3942 | -0.049533
| 6:32 | 8.3944 | -0.049972
| 6:32 | 8.3947 | -0.050411
| 6:32 | 8.395 | -0.05085
| 6:33 | 8.3953 | -0.051288
| 6:33 | 8.3956 | -0.051725
| 6:33 | 8.3958 | -0.052162
| 6:33 | 8.3961 | -0.052599
| 6:33 | 8.3964 | -0.053035
| 6:33 | 8.3967 | -0.05347
| 6:33 | 8.3969 | -0.053905
| 6:33 | 8.3972 | -0.05434
| 6:33 | 8.3975 | -0.054774
| 6:33 | 8.3978 | -0.055207
| 6:33 | 8.3981 | -0.05564
| 6:33 | 8.3983 | -0.056073
| 6:33 | 8.3986 | -0.056505
| 6:33 | 8.3989 | -0.056937
| 6:33 | 8.3992 | -0.057368
| 6:33 | 8.3994 | -0.057798
| 6:33 | 8.3997 | -0.058228
| 6:33 | 8.4 | -0.058658
| 6:33 | 8.4003 | -0.059087
| 6:33 | 8.4006 | -0.059517
| 6:33 | 8.4008 | -0.059946
| 6:33 | 8.4011 | -0.060376
| 6:33 | 8.4014 | -0.060806
| 6:33 | 8.4017 | -0.061235
| 6:33 | 8.4019 | -0.061665
| 6:33 | 8.4022 | -0.062094
| 6:33 | 8.4025 | -0.062524
| 6:33 | 8.4028 | -0.062954
| 6:33 | 8.4031 | -0.063384
| 6:33 | 8.4033 | -0.063813
| 6:33 | 8.4036 | -0.064241
| 6:33 | 8.4039 | -0.064668
| 6:33 | 8.4042 | -0.065095
| 6:33 | 8.4044 | -0.06552
| 6:33 | 8.4047 | -0.065945
| 6:33 | 8.405 | -0.066365
| 6:33 | 8.4053 | -0.066778
| 6:33 | 8.4056 | -0.067187
| 6:33 | 8.4058 | -0.067595
| 6:33 | 8.4061 | -0.068
| 6:33 | 8.4064 | -0.068404
| 6:33 | 8.4067 | -0.068806
| 6:33 | 8.4069 | -0.069206
| 6:33 | 8.4072 | -0.069604
| 6:33 | 8.4075 | -0.070001
| 6:33 | 8.4078 | -0.070395
| 6:33 | 8.4081 | -0.070788
| 6:33 | 8.4083 | -0.071179
| 6:33 | 8.4086 | -0.071568
| 6:33 | 8.4089 | -0.071955
| 6:33 | 8.4092 | -0.072341
| 6:33 | 8.4094 | -0.072725
| 6:33 | 8.4097 | -0.073106
| 6:33 | 8.41 | -0.073486
| 6:33 | 8.4103 | -0.073864
| 6:33 | 8.4106 | -0.074241
| 6:33 | 8.4108 | -0.074615
| 6:33 | 8.4111 | -0.074988
| 6:33 | 8.4114 | -0.075359
| 6:33 | 8.4117 | -0.075728
| 6:34 | 8.4119 | -0.076095
| 6:34 | 8.4122 | -0.07646
| 6:34 | 8.4125 | -0.076824
| 6:34 | 8.4128 | -0.077185
| 6:34 | 8.4131 | -0.077545
| 6:34 | 8.4133 | -0.077903
| 6:34 | 8.4136 | -0.078259
| 6:34 | 8.4139 | -0.078614
| 6:34 | 8.4142 | -0.078966
| 6:34 | 8.4144 | -0.079317
| 6:34 | 8.4147 | -0.079666
| 6:34 | 8.415 | -0.080013
| 6:34 | 8.4153 | -0.080358
| 6:34 | 8.4156 | -0.080702
| 6:34 | 8.4158 | -0.081043
| 6:34 | 8.4161 | -0.081383
| 6:34 | 8.4164 | -0.081721
| 6:34 | 8.4167 | -0.082057
| 6:34 | 8.4169 | -0.082392
| 6:34 | 8.4172 | -0.082724
| 6:34 | 8.4175 | -0.083055
| 6:34 | 8.4178 | -0.083384
| 6:34 | 8.4181 | -0.083711
| 6:34 | 8.4183 | -0.084036
| 6:34 | 8.4186 | -0.08436
| 6:34 | 8.4189 | -0.084679
| 6:34 | 8.4192 | -0.084993
| 6:34 | 8.4194 | -0.085301
| 6:34 | 8.4197 | -0.085601
| 6:34 | 8.42 | -0.08589
| 6:34 | 8.4203 | -0.086172
| 6:34 | 8.4206 | -0.08645
| 6:34 | 8.4208 | -0.086724
| 6:34 | 8.4211 | -0.086994
| 6:34 | 8.4214 | -0.08726
| 6:34 | 8.4217 | -0.087523
| 6:34 | 8.4219 | -0.087781
| 6:34 | 8.4222 | -0.088036
| 6:34 | 8.4225 | -0.088288
| 6:34 | 8.4228 | -0.088537
| 6:34 | 8.4231 | -0.088783
| 6:34 | 8.4233 | -0.089027
| 6:34 | 8.4236 | -0.089268
| 6:34 | 8.4239 | -0.089507
| 6:34 | 8.4242 | -0.089743
| 6:34 | 8.4244 | -0.089979
| 6:34 | 8.4247 | -0.090216
| 6:34 | 8.425 | -0.090453
| 6:34 | 8.4253 | -0.09069
| 6:34 | 8.4256 | -0.090928
| 6:34 | 8.4258 | -0.091166
| 6:34 | 8.4261 | -0.091405
| 6:34 | 8.4264 | -0.091644
| 6:34 | 8.4267 | -0.091883
| 6:34 | 8.4269 | -0.092122
| 6:34 | 8.4272 | -0.092363
| 6:34 | 8.4275 | -0.092603
| 6:34 | 8.4278 | -0.092844
| 6:34 | 8.4281 | -0.093085
| 6:35 | 8.4283 | -0.093326
| 6:35 | 8.4286 | -0.093568
| 6:35 | 8.4289 | -0.09381
| 6:35 | 8.4292 | -0.094053
| 6:35 | 8.4294 | -0.094296
| 6:35 | 8.4297 | -0.094539
| 6:35 | 8.43 | -0.094783
| 6:35 | 8.4303 | -0.095027
| 6:35 | 8.4306 | -0.095272
| 6:35 | 8.4308 | -0.095516
| 6:35 | 8.4311 | -0.095762
| 6:35 | 8.4314 | -0.096007
| 6:35 | 8.4317 | -0.096253
| 6:35 | 8.4319 | -0.0965
| 6:35 | 8.4322 | -0.096746
| 6:35 | 8.4325 | -0.096993
| 6:35 | 8.4328 | -0.097241
| 6:35 | 8.4331 | -0.097489
| 6:35 | 8.4333 | -0.097737
| 6:35 | 8.4336 | -0.097985
| 6:35 | 8.4339 | -0.098234
| 6:35 | 8.4342 | -0.098483
| 6:35 | 8.4344 | -0.098733
| 6:35 | 8.4347 | -0.098983
| 6:35 | 8.435 | -0.099233
| 6:35 | 8.4353 | -0.099484
| 6:35 | 8.4356 | -0.099735
| 6:35 | 8.4358 | -0.099986
| 6:35 | 8.4361 | -0.10024
| 6:35 | 8.4364 | -0.10049
| 6:35 | 8.4367 | -0.10075
| 6:35 | 8.4369 | -0.101
| 6:35 | 8.4372 | -0.10126
| 6:35 | 8.4375 | -0.10151
| 6:35 | 8.4378 | -0.10176
| 6:35 | 8.4381 | -0.10201
| 6:35 | 8.4383 | -0.10226
| 6:35 | 8.4386 | -0.10251
| 6:35 | 8.4389 | -0.10276
| 6:35 | 8.4392 | -0.103
| 6:35 | 8.4394 | -0.10324
| 6:35 | 8.4397 | -0.10347
| 6:35 | 8.44 | -0.1037
| 6:35 | 8.4403 | -0.10393
| 6:35 | 8.4406 | -0.10416
| 6:35 | 8.4408 | -0.10438
| 6:35 | 8.4411 | -0.10459
| 6:35 | 8.4414 | -0.10481
| 6:35 | 8.4417 | -0.10502
| 6:35 | 8.4419 | -0.10522
| 6:35 | 8.4422 | -0.10542
| 6:35 | 8.4425 | -0.10562
| 6:35 | 8.4428 | -0.10581
| 6:35 | 8.4431 | -0.10601
| 6:35 | 8.4433 | -0.1062
| 6:35 | 8.4436 | -0.10638
| 6:35 | 8.4439 | -0.10657
| 6:35 | 8.4442 | -0.10675
| 6:35 | 8.4444 | -0.10694
| 6:35 | 8.4447 | -0.10712
| 6:36 | 8.445 | -0.1073
| 6:36 | 8.4453 | -0.10747
| 6:36 | 8.4456 | -0.10765
| 6:36 | 8.4458 | -0.10782
| 6:36 | 8.4461 | -0.10799
| 6:36 | 8.4464 | -0.10816
| 6:36 | 8.4467 | -0.10833
| 6:36 | 8.4469 | -0.1085
| 6:36 | 8.4472 | -0.10866
| 6:36 | 8.4475 | -0.10882
| 6:36 | 8.4478 | -0.10898
| 6:36 | 8.4481 | -0.10914
| 6:36 | 8.4483 | -0.1093
| 6:36 | 8.4486 | -0.10945
| 6:36 | 8.4489 | -0.1096
| 6:36 | 8.4492 | -0.10975
| 6:36 | 8.4494 | -0.1099
| 6:36 | 8.4497 | -0.11005
| 6:36 | 8.45 | -0.11019
| 6:36 | 8.4503 | -0.11034
| 6:36 | 8.4506 | -0.11048
| 6:36 | 8.4508 | -0.11062
| 6:36 | 8.4511 | -0.11075
| 6:36 | 8.4514 | -0.11089
| 6:36 | 8.4517 | -0.11102
| 6:36 | 8.4519 | -0.11115
| 6:36 | 8.4522 | -0.11128
| 6:36 | 8.4525 | -0.11141
| 6:36 | 8.4528 | -0.11154
| 6:36 | 8.4531 | -0.11166
| 6:36 | 8.4533 | -0.11178
| 6:36 | 8.4536 | -0.1119
| 6:36 | 8.4539 | -0.11201
| 6:36 | 8.4542 | -0.11213
| 6:36 | 8.4544 | -0.11224
| 6:36 | 8.4547 | -0.11234
| 6:36 | 8.455 | -0.11245
| 6:36 | 8.4553 | -0.11255
| 6:36 | 8.4556 | -0.11265
| 6:36 | 8.4558 | -0.11275
| 6:36 | 8.4561 | -0.11284
| 6:36 | 8.4564 | -0.11293
| 6:36 | 8.4567 | -0.11302
| 6:36 | 8.4569 | -0.1131
| 6:36 | 8.4572 | -0.11319
| 6:36 | 8.4575 | -0.11327
| 6:36 | 8.4578 | -0.11334
| 6:36 | 8.4581 | -0.11341
| 6:36 | 8.4583 | -0.11348
| 6:36 | 8.4586 | -0.11355
| 6:36 | 8.4589 | -0.11361
| 6:36 | 8.4592 | -0.11367
| 6:36 | 8.4594 | -0.11372
| 6:36 | 8.4597 | -0.11377
| 6:36 | 8.46 | -0.11382
| 6:36 | 8.4603 | -0.11386
| 6:36 | 8.4606 | -0.1139
| 6:36 | 8.4608 | -0.11394
| 6:36 | 8.4611 | -0.11397
| 6:36 | 8.4614 | -0.114
| 6:37 | 8.4617 | -0.11402
| 6:37 | 8.4619 | -0.11405
| 6:37 | 8.4622 | -0.11407
| 6:37 | 8.4625 | -0.11409
| 6:37 | 8.4628 | -0.11412
| 6:37 | 8.4631 | -0.11414
| 6:37 | 8.4633 | -0.11417
| 6:37 | 8.4636 | -0.1142
| 6:37 | 8.4639 | -0.11422
| 6:37 | 8.4642 | -0.11425
| 6:37 | 8.4644 | -0.11428
| 6:37 | 8.4647 | -0.11431
| 6:37 | 8.465 | -0.11434
| 6:37 | 8.4653 | -0.11437
| 6:37 | 8.4656 | -0.1144
| 6:37 | 8.4658 | -0.11443
| 6:37 | 8.4661 | -0.11446
| 6:37 | 8.4664 | -0.11449
| 6:37 | 8.4667 | -0.11452
| 6:37 | 8.4669 | -0.11455
| 6:37 | 8.4672 | -0.11459
| 6:37 | 8.4675 | -0.11462
| 6:37 | 8.4678 | -0.11466
| 6:37 | 8.4681 | -0.11469
| 6:37 | 8.4683 | -0.11473
| 6:37 | 8.4686 | -0.11476
| 6:37 | 8.4689 | -0.1148
| 6:37 | 8.4692 | -0.11484
| 6:37 | 8.4694 | -0.11487
| 6:37 | 8.4697 | -0.11491
| 6:37 | 8.47 | -0.11494
| 6:37 | 8.4703 | -0.11497
| 6:37 | 8.4706 | -0.115
| 6:37 | 8.4708 | -0.11503
| 6:37 | 8.4711 | -0.11505
| 6:37 | 8.4714 | -0.11508
| 6:37 | 8.4717 | -0.11509
| 6:37 | 8.4719 | -0.11511
| 6:37 | 8.4722 | -0.11512
| 6:37 | 8.4725 | -0.11512
| 6:37 | 8.4728 | -0.11513
| 6:37 | 8.4731 | -0.11513
| 6:37 | 8.4733 | -0.11513
| 6:37 | 8.4736 | -0.11513
| 6:37 | 8.4739 | -0.11513
| 6:37 | 8.4742 | -0.11513
| 6:37 | 8.4744 | -0.11513
| 6:37 | 8.4747 | -0.11514
| 6:37 | 8.475 | -0.11516
| 6:37 | 8.4753 | -0.11518
| 6:37 | 8.4756 | -0.11521
| 6:37 | 8.4758 | -0.11525
| 6:37 | 8.4761 | -0.11529
| 6:37 | 8.4764 | -0.11534
| 6:37 | 8.4767 | -0.11539
| 6:37 | 8.4769 | -0.11545
| 6:37 | 8.4772 | -0.11552
| 6:37 | 8.4775 | -0.11559
| 6:37 | 8.4778 | -0.11567
| 6:37 | 8.4781 | -0.11575
| 6:38 | 8.4783 | -0.11584
| 6:38 | 8.4786 | -0.11594
| 6:38 | 8.4789 | -0.11604
| 6:38 | 8.4792 | -0.11615
| 6:38 | 8.4794 | -0.11625
| 6:38 | 8.4797 | -0.11636
| 6:38 | 8.48 | -0.11647
| 6:38 | 8.4803 | -0.11658
| 6:38 | 8.4806 | -0.1167
| 6:38 | 8.4808 | -0.11681
| 6:38 | 8.4811 | -0.11693
| 6:38 | 8.4814 | -0.11705
| 6:38 | 8.4817 | -0.11717
| 6:38 | 8.4819 | -0.11729
| 6:38 | 8.4822 | -0.11742
| 6:38 | 8.4825 | -0.11755
| 6:38 | 8.4828 | -0.11767
| 6:38 | 8.4831 | -0.11781
| 6:38 | 8.4833 | -0.11794
| 6:38 | 8.4836 | -0.11807
| 6:38 | 8.4839 | -0.11821
| 6:38 | 8.4842 | -0.11835
| 6:38 | 8.4844 | -0.11849
| 6:38 | 8.4847 | -0.11863
| 6:38 | 8.485 | -0.11877
| 6:38 | 8.4853 | -0.11892
| 6:38 | 8.4856 | -0.11906
| 6:38 | 8.4858 | -0.11921
| 6:38 | 8.4861 | -0.11936
| 6:38 | 8.4864 | -0.11952
| 6:38 | 8.4867 | -0.11967
| 6:38 | 8.4869 | -0.11983
| 6:38 | 8.4872 | -0.11998
| 6:38 | 8.4875 | -0.12014
| 6:38 | 8.4878 | -0.1203
| 6:38 | 8.4881 | -0.12046
| 6:38 | 8.4883 | -0.12061
| 6:38 | 8.4886 | -0.12077
| 6:38 | 8.4889 | -0.12093
| 6:38 | 8.4892 | -0.12108
| 6:38 | 8.4894 | -0.12124
| 6:38 | 8.4897 | -0.1214
| 6:38 | 8.49 | -0.12156
| 6:38 | 8.4903 | -0.12171
| 6:38 | 8.4906 | -0.12187
| 6:38 | 8.4908 | -0.12203
| 6:38 | 8.4911 | -0.12219
| 6:38 | 8.4914 | -0.12235
| 6:38 | 8.4917 | -0.1225
| 6:38 | 8.4919 | -0.12266
| 6:38 | 8.4922 | -0.12282
| 6:38 | 8.4925 | -0.12298
| 6:38 | 8.4928 | -0.12315
| 6:38 | 8.4931 | -0.12331
| 6:38 | 8.4933 | -0.12347
| 6:38 | 8.4936 | -0.12363
| 6:38 | 8.4939 | -0.1238
| 6:38 | 8.4942 | -0.12396
| 6:38 | 8.4944 | -0.12412
| 6:38 | 8.4947 | -0.12429
| 6:38 | 8.495 | -0.12446
| 6:39 | 8.4953 | -0.12463
| 6:39 | 8.4956 | -0.1248
| 6:39 | 8.4958 | -0.12497
| 6:39 | 8.4961 | -0.12514
| 6:39 | 8.4964 | -0.12532
| 6:39 | 8.4967 | -0.1255
| 6:39 | 8.4969 | -0.12568
| 6:39 | 8.4972 | -0.12586
| 6:39 | 8.4975 | -0.12604
| 6:39 | 8.4978 | -0.12623
| 6:39 | 8.4981 | -0.12642
| 6:39 | 8.4983 | -0.12661
| 6:39 | 8.4986 | -0.12681
| 6:39 | 8.4989 | -0.12701
| 6:39 | 8.4992 | -0.12722
| 6:39 | 8.4994 | -0.12742
| 6:39 | 8.4997 | -0.12763
| 6:39 | 8.5 | -0.12785
| 6:39 | 8.5003 | -0.12806
| 6:39 | 8.5006 | -0.12828
| 6:39 | 8.5008 | -0.12851
| 6:39 | 8.5011 | -0.12874
| 6:39 | 8.5014 | -0.12897
| 6:39 | 8.5017 | -0.1292
| 6:39 | 8.5019 | -0.12944
| 6:39 | 8.5022 | -0.12968
| 6:39 | 8.5025 | -0.12992
| 6:39 | 8.5028 | -0.13017
| 6:39 | 8.5031 | -0.13042
| 6:39 | 8.5033 | -0.13067
| 6:39 | 8.5036 | -0.13093
| 6:39 | 8.5039 | -0.13119
| 6:39 | 8.5042 | -0.13145
| 6:39 | 8.5044 | -0.13172
| 6:39 | 8.5047 | -0.13199
| 6:39 | 8.505 | -0.13227
| 6:39 | 8.5053 | -0.13254
| 6:39 | 8.5056 | -0.13282
| 6:39 | 8.5058 | -0.13311
| 6:39 | 8.5061 | -0.13339
| 6:39 | 8.5064 | -0.13368
| 6:39 | 8.5067 | -0.13398
| 6:39 | 8.5069 | -0.13427
| 6:39 | 8.5072 | -0.13457
| 6:39 | 8.5075 | -0.13487
| 6:39 | 8.5078 | -0.13518
| 6:39 | 8.5081 | -0.13549
| 6:39 | 8.5083 | -0.1358
| 6:39 | 8.5086 | -0.13612
| 6:39 | 8.5089 | -0.13644
| 6:39 | 8.5092 | -0.13676
| 6:39 | 8.5094 | -0.13708
| 6:39 | 8.5097 | -0.13741
| 6:39 | 8.51 | -0.13774
| 6:39 | 8.5103 | -0.13808
| 6:39 | 8.5106 | -0.13841
| 6:39 | 8.5108 | -0.13875
| 6:39 | 8.5111 | -0.1391
| 6:39 | 8.5114 | -0.13944
| 6:40 | 8.5117 | -0.13979
| 6:40 | 8.5119 | -0.14013
| 6:40 | 8.5122 | -0.14048
| 6:40 | 8.5125 | -0.14082
| 6:40 | 8.5128 | -0.14117
| 6:40 | 8.5131 | -0.14151
| 6:40 | 8.5133 | -0.14186
| 6:40 | 8.5136 | -0.14221
| 6:40 | 8.5139 | -0.14255
| 6:40 | 8.5142 | -0.1429
| 6:40 | 8.5144 | -0.14325
| 6:40 | 8.5147 | -0.1436
| 6:40 | 8.515 | -0.14395
| 6:40 | 8.5153 | -0.1443
| 6:40 | 8.5156 | -0.14466
| 6:40 | 8.5158 | -0.14502
| 6:40 | 8.5161 | -0.14538
| 6:40 | 8.5164 | -0.14575
| 6:40 | 8.5167 | -0.14611
| 6:40 | 8.5169 | -0.14648
| 6:40 | 8.5172 | -0.14685
| 6:40 | 8.5175 | -0.14722
| 6:40 | 8.5178 | -0.14759
| 6:40 | 8.5181 | -0.14797
| 6:40 | 8.5183 | -0.14835
| 6:40 | 8.5186 | -0.14873
| 6:40 | 8.5189 | -0.14911
| 6:40 | 8.5192 | -0.1495
| 6:40 | 8.5194 | -0.14988
| 6:40 | 8.5197 | -0.15027
| 6:40 | 8.52 | -0.15066
| 6:40 | 8.5203 | -0.15105
| 6:40 | 8.5206 | -0.15144
| 6:40 | 8.5208 | -0.15183
| 6:40 | 8.5211 | -0.15223
| 6:40 | 8.5214 | -0.15262
| 6:40 | 8.5217 | -0.15302
| 6:40 | 8.5219 | -0.15341
| 6:40 | 8.5222 | -0.15381
| 6:40 | 8.5225 | -0.1542
| 6:40 | 8.5228 | -0.1546
| 6:40 | 8.5231 | -0.155
| 6:40 | 8.5233 | -0.1554
| 6:40 | 8.5236 | -0.1558
| 6:40 | 8.5239 | -0.1562
| 6:40 | 8.5242 | -0.15661
| 6:40 | 8.5244 | -0.15701
| 6:40 | 8.5247 | -0.15741
| 6:40 | 8.525 | -0.15782
| 6:40 | 8.5253 | -0.15823
| 6:40 | 8.5256 | -0.15863
| 6:40 | 8.5258 | -0.15904
| 6:40 | 8.5261 | -0.15945
| 6:40 | 8.5264 | -0.15986
| 6:40 | 8.5267 | -0.16027
| 6:40 | 8.5269 | -0.16068
| 6:40 | 8.5272 | -0.16109
| 6:40 | 8.5275 | -0.1615
| 6:40 | 8.5278 | -0.16192
| 6:40 | 8.5281 | -0.16233
| 6:40 | 8.5283 | -0.16275
| 6:41 | 8.5286 | -0.16316
| 6:41 | 8.5289 | -0.16357
| 6:41 | 8.5292 | -0.16398
| 6:41 | 8.5294 | -0.16439
| 6:41 | 8.5297 | -0.1648
| 6:41 | 8.53 | -0.16521
| 6:41 | 8.5303 | -0.16562
| 6:41 | 8.5306 | -0.16602
| 6:41 | 8.5308 | -0.16643
| 6:41 | 8.5311 | -0.16684
| 6:41 | 8.5314 | -0.16724
| 6:41 | 8.5317 | -0.16764
| 6:41 | 8.5319 | -0.16804
| 6:41 | 8.5322 | -0.16844
| 6:41 | 8.5325 | -0.16883
| 6:41 | 8.5328 | -0.16923
| 6:41 | 8.5331 | -0.16962
| 6:41 | 8.5333 | -0.17001
| 6:41 | 8.5336 | -0.1704
| 6:41 | 8.5339 | -0.17079
| 6:41 | 8.5342 | -0.17118
| 6:41 | 8.5344 | -0.17156
| 6:41 | 8.5347 | -0.17194
| 6:41 | 8.535 | -0.17233
| 6:41 | 8.5353 | -0.1727
| 6:41 | 8.5356 | -0.17308
| 6:41 | 8.5358 | -0.17346
| 6:41 | 8.5361 | -0.17383
| 6:41 | 8.5364 | -0.17421
| 6:41 | 8.5367 | -0.17458
| 6:41 | 8.5369 | -0.17495
| 6:41 | 8.5372 | -0.17532
| 6:41 | 8.5375 | -0.17568
| 6:41 | 8.5378 | -0.17605
| 6:41 | 8.5381 | -0.17641
| 6:41 | 8.5383 | -0.17677
| 6:41 | 8.5386 | -0.17713
| 6:41 | 8.5389 | -0.17749
| 6:41 | 8.5392 | -0.17785
| 6:41 | 8.5394 | -0.1782
| 6:41 | 8.5397 | -0.17856
| 6:41 | 8.54 | -0.17891
| 6:41 | 8.5403 | -0.17926
| 6:41 | 8.5406 | -0.17961
| 6:41 | 8.5408 | -0.17996
| 6:41 | 8.5411 | -0.1803
| 6:41 | 8.5414 | -0.18064
| 6:41 | 8.5417 | -0.18099
| 6:41 | 8.5419 | -0.18133
| 6:41 | 8.5422 | -0.18167
| 6:41 | 8.5425 | -0.182
| 6:41 | 8.5428 | -0.18234
| 6:41 | 8.5431 | -0.18267
| 6:41 | 8.5433 | -0.183
| 6:41 | 8.5436 | -0.18333
| 6:41 | 8.5439 | -0.18366
| 6:41 | 8.5442 | -0.18399
| 6:41 | 8.5444 | -0.18432
| 6:41 | 8.5447 | -0.18464
| 6:42 | 8.545 | -0.18496
| 6:42 | 8.5453 | -0.18529
| 6:42 | 8.5456 | -0.18561
| 6:42 | 8.5458 | -0.18593
| 6:42 | 8.5461 | -0.18625
| 6:42 | 8.5464 | -0.18657
| 6:42 | 8.5467 | -0.18689
| 6:42 | 8.5469 | -0.18721
| 6:42 | 8.5472 | -0.18753
| 6:42 | 8.5475 | -0.18785
| 6:42 | 8.5478 | -0.18816
| 6:42 | 8.5481 | -0.18847
| 6:42 | 8.5483 | -0.18878
| 6:42 | 8.5486 | -0.18909
| 6:42 | 8.5489 | -0.1894
| 6:42 | 8.5492 | -0.1897
| 6:42 | 8.5494 | -0.19001
| 6:42 | 8.5497 | -0.19031
| 6:42 | 8.55 | -0.19061
| 6:42 | 8.5503 | -0.1909
| 6:42 | 8.5506 | -0.1912
| 6:42 | 8.5508 | -0.19149
| 6:42 | 8.5511 | -0.19178
| 6:42 | 8.5514 | -0.19207
| 6:42 | 8.5517 | -0.19236
| 6:42 | 8.5519 | -0.19264
| 6:42 | 8.5522 | -0.19292
| 6:42 | 8.5525 | -0.1932
| 6:42 | 8.5528 | -0.19348
| 6:42 | 8.5531 | -0.19376
| 6:42 | 8.5533 | -0.19403
| 6:42 | 8.5536 | -0.19431
| 6:42 | 8.5539 | -0.19458
| 6:42 | 8.5542 | -0.19485
| 6:42 | 8.5544 | -0.19511
| 6:42 | 8.5547 | -0.19538
| 6:42 | 8.555 | -0.19564
| 6:42 | 8.5553 | -0.1959
| 6:42 | 8.5556 | -0.19616
| 6:42 | 8.5558 | -0.19641
| 6:42 | 8.5561 | -0.19667
| 6:42 | 8.5564 | -0.19691
| 6:42 | 8.5567 | -0.19716
| 6:42 | 8.5569 | -0.1974
| 6:42 | 8.5572 | -0.19764
| 6:42 | 8.5575 | -0.19787
| 6:42 | 8.5578 | -0.1981
| 6:42 | 8.5581 | -0.19833
| 6:42 | 8.5583 | -0.19856
| 6:42 | 8.5586 | -0.19879
| 6:42 | 8.5589 | -0.19901
| 6:42 | 8.5592 | -0.19923
| 6:42 | 8.5594 | -0.19945
| 6:42 | 8.5597 | -0.19967
| 6:42 | 8.56 | -0.19988
| 6:42 | 8.5603 | -0.2001
| 6:42 | 8.5606 | -0.20031
| 6:42 | 8.5608 | -0.20052
| 6:42 | 8.5611 | -0.20072
| 6:42 | 8.5614 | -0.20092
| 6:42 | 8.5617 | -0.20112
| 6:43 | 8.5619 | -0.20131
| 6:43 | 8.5622 | -0.2015
| 6:43 | 8.5625 | -0.20168
| 6:43 | 8.5628 | -0.20185
| 6:43 | 8.5631 | -0.20202
| 6:43 | 8.5633 | -0.20218
| 6:43 | 8.5636 | -0.20235
| 6:43 | 8.5639 | -0.20251
| 6:43 | 8.5642 | -0.20267
| 6:43 | 8.5644 | -0.20283
| 6:43 | 8.5647 | -0.20299
| 6:43 | 8.565 | -0.20315
| 6:43 | 8.5653 | -0.20331
| 6:43 | 8.5656 | -0.20347
| 6:43 | 8.5658 | -0.20362
| 6:43 | 8.5661 | -0.20378
| 6:43 | 8.5664 | -0.20393
| 6:43 | 8.5667 | -0.20407
| 6:43 | 8.5669 | -0.20422
| 6:43 | 8.5672 | -0.20436
| 6:43 | 8.5675 | -0.2045
| 6:43 | 8.5678 | -0.20463
| 6:43 | 8.5681 | -0.20477
| 6:43 | 8.5683 | -0.20489
| 6:43 | 8.5686 | -0.20502
| 6:43 | 8.5689 | -0.20515
| 6:43 | 8.5692 | -0.20527
| 6:43 | 8.5694 | -0.20538
| 6:43 | 8.5697 | -0.2055
| 6:43 | 8.57 | -0.20561
| 6:43 | 8.5703 | -0.20572
| 6:43 | 8.5706 | -0.20583
| 6:43 | 8.5708 | -0.20593
| 6:43 | 8.5711 | -0.20603
| 6:43 | 8.5714 | -0.20613
| 6:43 | 8.5717 | -0.20622
| 6:43 | 8.5719 | -0.20632
| 6:43 | 8.5722 | -0.2064
| 6:43 | 8.5725 | -0.20649
| 6:43 | 8.5728 | -0.20657
| 6:43 | 8.5731 | -0.20665
| 6:43 | 8.5733 | -0.20673
| 6:43 | 8.5736 | -0.20681
| 6:43 | 8.5739 | -0.20688
| 6:43 | 8.5742 | -0.20695
| 6:43 | 8.5744 | -0.20701
| 6:43 | 8.5747 | -0.20707
| 6:43 | 8.575 | -0.20713
| 6:43 | 8.5753 | -0.20719
| 6:43 | 8.5756 | -0.20724
| 6:43 | 8.5758 | -0.2073
| 6:43 | 8.5761 | -0.20734
| 6:43 | 8.5764 | -0.20739
| 6:43 | 8.5767 | -0.20743
| 6:43 | 8.5769 | -0.20747
| 6:43 | 8.5772 | -0.20751
| 6:43 | 8.5775 | -0.20754
| 6:43 | 8.5778 | -0.20757
| 6:43 | 8.5781 | -0.20758
| 6:44 | 8.5783 | -0.20758
| 6:44 | 8.5786 | -0.20757
| 6:44 | 8.5789 | -0.20755
| 6:44 | 8.5792 | -0.20752
| 6:44 | 8.5794 | -0.20748
| 6:44 | 8.5797 | -0.20744
| 6:44 | 8.58 | -0.20739
| 6:44 | 8.5803 | -0.20733
| 6:44 | 8.5806 | -0.20727
| 6:44 | 8.5808 | -0.20721
| 6:44 | 8.5811 | -0.20715
| 6:44 | 8.5814 | -0.20708
| 6:44 | 8.5817 | -0.20701
| 6:44 | 8.5819 | -0.20694
| 6:44 | 8.5822 | -0.20687
| 6:44 | 8.5825 | -0.20679
| 6:44 | 8.5828 | -0.20672
| 6:44 | 8.5831 | -0.20664
| 6:44 | 8.5833 | -0.20657
| 6:44 | 8.5836 | -0.20649
| 6:44 | 8.5839 | -0.20641
| 6:44 | 8.5842 | -0.20634
| 6:44 | 8.5844 | -0.20626
| 6:44 | 8.5847 | -0.20619
| 6:44 | 8.585 | -0.20611
| 6:44 | 8.5853 | -0.20603
| 6:44 | 8.5856 | -0.20596
| 6:44 | 8.5858 | -0.20588
| 6:44 | 8.5861 | -0.20581
| 6:44 | 8.5864 | -0.20573
| 6:44 | 8.5867 | -0.20565
| 6:44 | 8.5869 | -0.20558
| 6:44 | 8.5872 | -0.2055
| 6:44 | 8.5875 | -0.20543
| 6:44 | 8.5878 | -0.20535
| 6:44 | 8.5881 | -0.20527
| 6:44 | 8.5883 | -0.2052
| 6:44 | 8.5886 | -0.20512
| 6:44 | 8.5889 | -0.20505
| 6:44 | 8.5892 | -0.20497
| 6:44 | 8.5894 | -0.20489
| 6:44 | 8.5897 | -0.20482
| 6:44 | 8.59 | -0.20474
| 6:44 | 8.5903 | -0.20467
| 6:44 | 8.5906 | -0.20459
| 6:44 | 8.5908 | -0.20452
| 6:44 | 8.5911 | -0.20444
| 6:44 | 8.5914 | -0.20437
| 6:44 | 8.5917 | -0.20429
| 6:44 | 8.5919 | -0.20421
| 6:44 | 8.5922 | -0.20414
| 6:44 | 8.5925 | -0.20406
| 6:44 | 8.5928 | -0.20399
| 6:44 | 8.5931 | -0.20391
| 6:44 | 8.5933 | -0.20384
| 6:44 | 8.5936 | -0.20376
| 6:44 | 8.5939 | -0.20369
| 6:44 | 8.5942 | -0.20361
| 6:44 | 8.5944 | -0.20354
| 6:44 | 8.5947 | -0.20346
| 6:44 | 8.595 | -0.20339
| 6:45 | 8.5953 | -0.20331
| 6:45 | 8.5956 | -0.20324
| 6:45 | 8.5958 | -0.20316
| 6:45 | 8.5961 | -0.20309
| 6:45 | 8.5964 | -0.20301
| 6:45 | 8.5967 | -0.20294
| 6:45 | 8.5969 | -0.20286
| 6:45 | 8.5972 | -0.20279
| 6:45 | 8.5975 | -0.20271
| 6:45 | 8.5978 | -0.20264
| 6:45 | 8.5981 | -0.20256
| 6:45 | 8.5983 | -0.20249
| 6:45 | 8.5986 | -0.20241
| 6:45 | 8.5989 | -0.20234
| 6:45 | 8.5992 | -0.20226
| 6:45 | 8.5994 | -0.20219
| 6:45 | 8.5997 | -0.20211
| 6:45 | 8.6 | -0.20203
| 6:45 | 8.6003 | -0.20195
| 6:45 | 8.6006 | -0.20187
| 6:45 | 8.6008 | -0.20179
| 6:45 | 8.6011 | -0.20171
| 6:45 | 8.6014 | -0.20162
| 6:45 | 8.6017 | -0.20153
| 6:45 | 8.6019 | -0.20145
| 6:45 | 8.6022 | -0.20136
| 6:45 | 8.6025 | -0.20126
| 6:45 | 8.6028 | -0.20117
| 6:45 | 8.6031 | -0.20107
| 6:45 | 8.6033 | -0.20098
| 6:45 | 8.6036 | -0.20088
| 6:45 | 8.6039 | -0.20078
| 6:45 | 8.6042 | -0.20068
| 6:45 | 8.6044 | -0.20057
| 6:45 | 8.6047 | -0.20047
| 6:45 | 8.605 | -0.20036
| 6:45 | 8.6053 | -0.20025
| 6:45 | 8.6056 | -0.20015
| 6:45 | 8.6058 | -0.20003
| 6:45 | 8.6061 | -0.19992
| 6:45 | 8.6064 | -0.19981
| 6:45 | 8.6067 | -0.19969
| 6:45 | 8.6069 | -0.19957
| 6:45 | 8.6072 | -0.19945
| 6:45 | 8.6075 | -0.19933
| 6:45 | 8.6078 | -0.19921
| 6:45 | 8.6081 | -0.19908
| 6:45 | 8.6083 | -0.19896
| 6:45 | 8.6086 | -0.19883
| 6:45 | 8.6089 | -0.1987
| 6:45 | 8.6092 | -0.19857
| 6:45 | 8.6094 | -0.19844
| 6:45 | 8.6097 | -0.19831
| 6:45 | 8.61 | -0.19817
| 6:45 | 8.6103 | -0.19803
| 6:45 | 8.6106 | -0.19789
| 6:45 | 8.6108 | -0.19775
| 6:45 | 8.6111 | -0.19761
| 6:45 | 8.6114 | -0.19747
| 6:46 | 8.6117 | -0.19733
| 6:46 | 8.6119 | -0.19718
| 6:46 | 8.6122 | -0.19703
| 6:46 | 8.6125 | -0.19689
| 6:46 | 8.6128 | -0.19674
| 6:46 | 8.6131 | -0.19659
| 6:46 | 8.6133 | -0.19643
| 6:46 | 8.6136 | -0.19628
| 6:46 | 8.6139 | -0.19612
| 6:46 | 8.6142 | -0.19597
| 6:46 | 8.6144 | -0.19581
| 6:46 | 8.6147 | -0.19565
| 6:46 | 8.615 | -0.19548
| 6:46 | 8.6153 | -0.19532
| 6:46 | 8.6156 | -0.19515
| 6:46 | 8.6158 | -0.19499
| 6:46 | 8.6161 | -0.19482
| 6:46 | 8.6164 | -0.19465
| 6:46 | 8.6167 | -0.19449
| 6:46 | 8.6169 | -0.19432
| 6:46 | 8.6172 | -0.19415
| 6:46 | 8.6175 | -0.19399
| 6:46 | 8.6178 | -0.19382
| 6:46 | 8.6181 | -0.19366
| 6:46 | 8.6183 | -0.19349
| 6:46 | 8.6186 | -0.19333
| 6:46 | 8.6189 | -0.19317
| 6:46 | 8.6192 | -0.193
| 6:46 | 8.6194 | -0.19284
| 6:46 | 8.6197 | -0.19268
| 6:46 | 8.62 | -0.19251
| 6:46 | 8.6203 | -0.19235
| 6:46 | 8.6206 | -0.19219
| 6:46 | 8.6208 | -0.19203
| 6:46 | 8.6211 | -0.19187
| 6:46 | 8.6214 | -0.19171
| 6:46 | 8.6217 | -0.19155
| 6:46 | 8.6219 | -0.19139
| 6:46 | 8.6222 | -0.19123
| 6:46 | 8.6225 | -0.19107
| 6:46 | 8.6228 | -0.19092
| 6:46 | 8.6231 | -0.19076
| 6:46 | 8.6233 | -0.1906
| 6:46 | 8.6236 | -0.19044
| 6:46 | 8.6239 | -0.19029
| 6:46 | 8.6242 | -0.19013
| 6:46 | 8.6244 | -0.18998
| 6:46 | 8.6247 | -0.18982
| 6:46 | 8.625 | -0.18967
| 6:46 | 8.6253 | -0.18951
| 6:46 | 8.6256 | -0.18936
| 6:46 | 8.6258 | -0.1892
| 6:46 | 8.6261 | -0.18905
| 6:46 | 8.6264 | -0.1889
| 6:46 | 8.6267 | -0.18875
| 6:46 | 8.6269 | -0.18859
| 6:46 | 8.6272 | -0.18844
| 6:46 | 8.6275 | -0.18829
| 6:46 | 8.6278 | -0.18814
| 6:46 | 8.6281 | -0.18799
| 6:46 | 8.6283 | -0.18784
| 6:47 | 8.6286 | -0.18769
| 6:47 | 8.6289 | -0.18754
| 6:47 | 8.6292 | -0.18739
| 6:47 | 8.6294 | -0.18724
| 6:47 | 8.6297 | -0.1871
| 6:47 | 8.63 | -0.18695
| 6:47 | 8.6303 | -0.1868
| 6:47 | 8.6306 | -0.18665
| 6:47 | 8.6308 | -0.18651
| 6:47 | 8.6311 | -0.18637
| 6:47 | 8.6314 | -0.18623
| 6:47 | 8.6317 | -0.1861
| 6:47 | 8.6319 | -0.18596
| 6:47 | 8.6322 | -0.18583
| 6:47 | 8.6325 | -0.1857
| 6:47 | 8.6328 | -0.18558
| 6:47 | 8.6331 | -0.18545
| 6:47 | 8.6333 | -0.18533
| 6:47 | 8.6336 | -0.1852
| 6:47 | 8.6339 | -0.18508
| 6:47 | 8.6342 | -0.18495
| 6:47 | 8.6344 | -0.18482
| 6:47 | 8.6347 | -0.18469
| 6:47 | 8.635 | -0.18456
| 6:47 | 8.6353 | -0.18443
| 6:47 | 8.6356 | -0.1843
| 6:47 | 8.6358 | -0.18417
| 6:47 | 8.6361 | -0.18403
| 6:47 | 8.6364 | -0.1839
| 6:47 | 8.6367 | -0.18376
| 6:47 | 8.6369 | -0.18362
| 6:47 | 8.6372 | -0.18347
| 6:47 | 8.6375 | -0.18333
| 6:47 | 8.6378 | -0.18318
| 6:47 | 8.6381 | -0.18303
| 6:47 | 8.6383 | -0.18287
| 6:47 | 8.6386 | -0.18272
| 6:47 | 8.6389 | -0.18256
| 6:47 | 8.6392 | -0.1824
| 6:47 | 8.6394 | -0.18223
| 6:47 | 8.6397 | -0.18207
| 6:47 | 8.64 | -0.1819
| 6:47 | 8.6403 | -0.18173
| 6:47 | 8.6406 | -0.18155
| 6:47 | 8.6408 | -0.18138
| 6:47 | 8.6411 | -0.1812
| 6:47 | 8.6414 | -0.18102
| 6:47 | 8.6417 | -0.18084
| 6:47 | 8.6419 | -0.18065
| 6:47 | 8.6422 | -0.18046
| 6:47 | 8.6425 | -0.18027
| 6:47 | 8.6428 | -0.18008
| 6:47 | 8.6431 | -0.17988
| 6:47 | 8.6433 | -0.17969
| 6:47 | 8.6436 | -0.17949
| 6:47 | 8.6439 | -0.17928
| 6:47 | 8.6442 | -0.17908
| 6:47 | 8.6444 | -0.17887
| 6:47 | 8.6447 | -0.17866
| 6:48 | 8.645 | -0.17845
| 6:48 | 8.6453 | -0.17823
| 6:48 | 8.6456 | -0.17801
| 6:48 | 8.6458 | -0.17779
| 6:48 | 8.6461 | -0.17757
| 6:48 | 8.6464 | -0.17735
| 6:48 | 8.6467 | -0.17712
| 6:48 | 8.6469 | -0.17689
| 6:48 | 8.6472 | -0.17666
| 6:48 | 8.6475 | -0.17642
| 6:48 | 8.6478 | -0.17618
| 6:48 | 8.6481 | -0.17594
| 6:48 | 8.6483 | -0.1757
| 6:48 | 8.6486 | -0.17546
| 6:48 | 8.6489 | -0.17521
| 6:48 | 8.6492 | -0.17496
| 6:48 | 8.6494 | -0.17471
| 6:48 | 8.6497 | -0.17446
| 6:48 | 8.65 | -0.17421
| 6:48 | 8.6503 | -0.17397
| 6:48 | 8.6506 | -0.17373
| 6:48 | 8.6508 | -0.17349
| 6:48 | 8.6511 | -0.17325
| 6:48 | 8.6514 | -0.17302
| 6:48 | 8.6517 | -0.17279
| 6:48 | 8.6519 | -0.17256
| 6:48 | 8.6522 | -0.17233
| 6:48 | 8.6525 | -0.17211
| 6:48 | 8.6528 | -0.17188
| 6:48 | 8.6531 | -0.17166
| 6:48 | 8.6533 | -0.17144
| 6:48 | 8.6536 | -0.17122
| 6:48 | 8.6539 | -0.171
| 6:48 | 8.6542 | -0.17078
| 6:48 | 8.6544 | -0.17057
| 6:48 | 8.6547 | -0.17035
| 6:48 | 8.655 | -0.17014
| 6:48 | 8.6553 | -0.16994
| 6:48 | 8.6556 | -0.16973
| 6:48 | 8.6558 | -0.16952
| 6:48 | 8.6561 | -0.16932
| 6:48 | 8.6564 | -0.16912
| 6:48 | 8.6567 | -0.16892
| 6:48 | 8.6569 | -0.16872
| 6:48 | 8.6572 | -0.16852
| 6:48 | 8.6575 | -0.16833
| 6:48 | 8.6578 | -0.16814
| 6:48 | 8.6581 | -0.16794
| 6:48 | 8.6583 | -0.16775
| 6:48 | 8.6586 | -0.16756
| 6:48 | 8.6589 | -0.16738
| 6:48 | 8.6592 | -0.16719
| 6:48 | 8.6594 | -0.16701
| 6:48 | 8.6597 | -0.16683
| 6:48 | 8.66 | -0.16664
| 6:48 | 8.6603 | -0.16647
| 6:48 | 8.6606 | -0.16629
| 6:48 | 8.6608 | -0.16611
| 6:48 | 8.6611 | -0.16594
| 6:48 | 8.6614 | -0.16577
| 6:48 | 8.6617 | -0.16559
| 6:49 | 8.6619 | -0.16543
| 6:49 | 8.6622 | -0.16526
| 6:49 | 8.6625 | -0.16509
| 6:49 | 8.6628 | -0.16493
| 6:49 | 8.6631 | -0.16476
| 6:49 | 8.6633 | -0.1646
| 6:49 | 8.6636 | -0.16444
| 6:49 | 8.6639 | -0.16429
| 6:49 | 8.6642 | -0.16413
| 6:49 | 8.6644 | -0.16397
| 6:49 | 8.6647 | -0.16382
| 6:49 | 8.665 | -0.16367
| 6:49 | 8.6653 | -0.16352
| 6:49 | 8.6656 | -0.16337
| 6:49 | 8.6658 | -0.16322
| 6:49 | 8.6661 | -0.16308
| 6:49 | 8.6664 | -0.16294
| 6:49 | 8.6667 | -0.16279
| 6:49 | 8.6669 | -0.16265
| 6:49 | 8.6672 | -0.16252
| 6:49 | 8.6675 | -0.16238
| 6:49 | 8.6678 | -0.16224
| 6:49 | 8.6681 | -0.16211
| 6:49 | 8.6683 | -0.16198
| 6:49 | 8.6686 | -0.16184
| 6:49 | 8.6689 | -0.16171
| 6:49 | 8.6692 | -0.16157
| 6:49 | 8.6694 | -0.16144
| 6:49 | 8.6697 | -0.1613
| 6:49 | 8.67 | -0.16116
| 6:49 | 8.6703 | -0.16103
| 6:49 | 8.6706 | -0.16089
| 6:49 | 8.6708 | -0.16076
| 6:49 | 8.6711 | -0.16063
| 6:49 | 8.6714 | -0.1605
| 6:49 | 8.6717 | -0.16036
| 6:49 | 8.6719 | -0.16023
| 6:49 | 8.6722 | -0.1601
| 6:49 | 8.6725 | -0.15997
| 6:49 | 8.6728 | -0.15985
| 6:49 | 8.6731 | -0.15972
| 6:49 | 8.6733 | -0.15959
| 6:49 | 8.6736 | -0.15946
| 6:49 | 8.6739 | -0.15933
| 6:49 | 8.6742 | -0.15921
| 6:49 | 8.6744 | -0.15908
| 6:49 | 8.6747 | -0.15895
| 6:49 | 8.675 | -0.15883
| 6:49 | 8.6753 | -0.1587
| 6:49 | 8.6756 | -0.15858
| 6:49 | 8.6758 | -0.15845
| 6:49 | 8.6761 | -0.15832
| 6:49 | 8.6764 | -0.1582
| 6:49 | 8.6767 | -0.15808
| 6:49 | 8.6769 | -0.15795
| 6:49 | 8.6772 | -0.15783
| 6:49 | 8.6775 | -0.1577
| 6:49 | 8.6778 | -0.15758
| 6:49 | 8.6781 | -0.15746
| 6:50 | 8.6783 | -0.15733
| 6:50 | 8.6786 | -0.15721
| 6:50 | 8.6789 | -0.15709
| 6:50 | 8.6792 | -0.15697
| 6:50 | 8.6794 | -0.15685
| 6:50 | 8.6797 | -0.15672
| 6:50 | 8.68 | -0.1566
| 6:50 | 8.6803 | -0.15648
| 6:50 | 8.6806 | -0.15636
| 6:50 | 8.6808 | -0.15624
| 6:50 | 8.6811 | -0.15612
| 6:50 | 8.6814 | -0.156
| 6:50 | 8.6817 | -0.15588
| 6:50 | 8.6819 | -0.15576
| 6:50 | 8.6822 | -0.15564
| 6:50 | 8.6825 | -0.15552
| 6:50 | 8.6828 | -0.15541
| 6:50 | 8.6831 | -0.15529
| 6:50 | 8.6833 | -0.15517
| 6:50 | 8.6836 | -0.15505
| 6:50 | 8.6839 | -0.15494
| 6:50 | 8.6842 | -0.15482
| 6:50 | 8.6844 | -0.1547
| 6:50 | 8.6847 | -0.15459
| 6:50 | 8.685 | -0.15447
| 6:50 | 8.6853 | -0.15435
| 6:50 | 8.6856 | -0.15424
| 6:50 | 8.6858 | -0.15413
| 6:50 | 8.6861 | -0.15401
| 6:50 | 8.6864 | -0.1539
| 6:50 | 8.6867 | -0.15379
| 6:50 | 8.6869 | -0.15368
| 6:50 | 8.6872 | -0.15357
| 6:50 | 8.6875 | -0.15346
| 6:50 | 8.6878 | -0.15335
| 6:50 | 8.6881 | -0.15324
| 6:50 | 8.6883 | -0.15314
| 6:50 | 8.6886 | -0.15303
| 6:50 | 8.6889 | -0.15293
| 6:50 | 8.6892 | -0.15283
| 6:50 | 8.6894 | -0.15273
| 6:50 | 8.6897 | -0.15264
| 6:50 | 8.69 | -0.15254
| 6:50 | 8.6903 | -0.15246
| 6:50 | 8.6906 | -0.15237
| 6:50 | 8.6908 | -0.15229
| 6:50 | 8.6911 | -0.15221
| 6:50 | 8.6914 | -0.15213
| 6:50 | 8.6917 | -0.15205
| 6:50 | 8.6919 | -0.15197
| 6:50 | 8.6922 | -0.15189
| 6:50 | 8.6925 | -0.15182
| 6:50 | 8.6928 | -0.15174
| 6:50 | 8.6931 | -0.15167
| 6:50 | 8.6933 | -0.15159
| 6:50 | 8.6936 | -0.15152
| 6:50 | 8.6939 | -0.15145
| 6:50 | 8.6942 | -0.15138
| 6:50 | 8.6944 | -0.15131
| 6:50 | 8.6947 | -0.15124
| 6:50 | 8.695 | -0.15117
| 6:51 | 8.6953 | -0.15111
| 6:51 | 8.6956 | -0.15104
| 6:51 | 8.6958 | -0.15098
| 6:51 | 8.6961 | -0.15091
| 6:51 | 8.6964 | -0.15085
| 6:51 | 8.6967 | -0.15079
| 6:51 | 8.6969 | -0.15073
| 6:51 | 8.6972 | -0.15067
| 6:51 | 8.6975 | -0.15061
| 6:51 | 8.6978 | -0.15055
| 6:51 | 8.6981 | -0.15049
| 6:51 | 8.6983 | -0.15044
| 6:51 | 8.6986 | -0.15038
| 6:51 | 8.6989 | -0.15033
| 6:51 | 8.6992 | -0.15028
| 6:51 | 8.6994 | -0.15023
| 6:51 | 8.6997 | -0.15017
| 6:51 | 8.7 | -0.15012
| 6:51 | 8.7003 | -0.15007
| 6:51 | 8.7006 | -0.15003
| 6:51 | 8.7008 | -0.14998
| 6:51 | 8.7011 | -0.14993
| 6:51 | 8.7014 | -0.14989
| 6:51 | 8.7017 | -0.14984
| 6:51 | 8.7019 | -0.1498
| 6:51 | 8.7022 | -0.14976
| 6:51 | 8.7025 | -0.14972
| 6:51 | 8.7028 | -0.14968
| 6:51 | 8.7031 | -0.14963
| 6:51 | 8.7033 | -0.14959
| 6:51 | 8.7036 | -0.14955
| 6:51 | 8.7039 | -0.14951
| 6:51 | 8.7042 | -0.14948
| 6:51 | 8.7044 | -0.14944
| 6:51 | 8.7047 | -0.1494
| 6:51 | 8.705 | -0.14936
| 6:51 | 8.7053 | -0.14933
| 6:51 | 8.7056 | -0.14929
| 6:51 | 8.7058 | -0.14926
| 6:51 | 8.7061 | -0.14922
| 6:51 | 8.7064 | -0.14919
| 6:51 | 8.7067 | -0.14916
| 6:51 | 8.7069 | -0.14913
| 6:51 | 8.7072 | -0.14909
| 6:51 | 8.7075 | -0.14906
| 6:51 | 8.7078 | -0.14904
| 6:51 | 8.7081 | -0.14901
| 6:51 | 8.7083 | -0.14899
| 6:51 | 8.7086 | -0.14898
| 6:51 | 8.7089 | -0.14896
| 6:51 | 8.7092 | -0.14896
| 6:51 | 8.7094 | -0.14895
| 6:51 | 8.7097 | -0.14895
| 6:51 | 8.71 | -0.14895
| 6:51 | 8.7103 | -0.14895
| 6:51 | 8.7106 | -0.14896
| 6:51 | 8.7108 | -0.14897
| 6:51 | 8.7111 | -0.14898
| 6:51 | 8.7114 | -0.149
| 6:52 | 8.7117 | -0.14902
| 6:52 | 8.7119 | -0.14905
| 6:52 | 8.7122 | -0.14907
| 6:52 | 8.7125 | -0.1491
| 6:52 | 8.7128 | -0.14914
| 6:52 | 8.7131 | -0.14918
| 6:52 | 8.7133 | -0.14922
| 6:52 | 8.7136 | -0.14926
| 6:52 | 8.7139 | -0.14931
| 6:52 | 8.7142 | -0.14936
| 6:52 | 8.7144 | -0.14942
| 6:52 | 8.7147 | -0.14948
| 6:52 | 8.715 | -0.14954
| 6:52 | 8.7153 | -0.1496
| 6:52 | 8.7156 | -0.14967
| 6:52 | 8.7158 | -0.14974
| 6:52 | 8.7161 | -0.14982
| 6:52 | 8.7164 | -0.1499
| 6:52 | 8.7167 | -0.14998
| 6:52 | 8.7169 | -0.15006
| 6:52 | 8.7172 | -0.15015
| 6:52 | 8.7175 | -0.15024
| 6:52 | 8.7178 | -0.15034
| 6:52 | 8.7181 | -0.15044
| 6:52 | 8.7183 | -0.15054
| 6:52 | 8.7186 | -0.15065
| 6:52 | 8.7189 | -0.15076
| 6:52 | 8.7192 | -0.15087
| 6:52 | 8.7194 | -0.15098
| 6:52 | 8.7197 | -0.15111
| 6:52 | 8.72 | -0.15123
| 6:52 | 8.7203 | -0.15137
| 6:52 | 8.7206 | -0.15151
| 6:52 | 8.7208 | -0.15165
| 6:52 | 8.7211 | -0.15181
| 6:52 | 8.7214 | -0.15196
| 6:52 | 8.7217 | -0.15213
| 6:52 | 8.7219 | -0.15231
| 6:52 | 8.7222 | -0.15249
| 6:52 | 8.7225 | -0.15268
| 6:52 | 8.7228 | -0.15288
| 6:52 | 8.7231 | -0.15308
| 6:52 | 8.7233 | -0.15328
| 6:52 | 8.7236 | -0.15349
| 6:52 | 8.7239 | -0.15371
| 6:52 | 8.7242 | -0.15394
| 6:52 | 8.7244 | -0.15416
| 6:52 | 8.7247 | -0.15437
| 6:52 | 8.725 | -0.15459
| 6:52 | 8.7253 | -0.1548
| 6:52 | 8.7256 | -0.15502
| 6:52 | 8.7258 | -0.15523
| 6:52 | 8.7261 | -0.15543
| 6:52 | 8.7264 | -0.15564
| 6:52 | 8.7267 | -0.15584
| 6:52 | 8.7269 | -0.15605
| 6:52 | 8.7272 | -0.15625
| 6:52 | 8.7275 | -0.15645
| 6:52 | 8.7278 | -0.15664
| 6:52 | 8.7281 | -0.15684
| 6:52 | 8.7283 | -0.15703
| 6:53 | 8.7286 | -0.15722
| 6:53 | 8.7289 | -0.15741
| 6:53 | 8.7292 | -0.15759
| 6:53 | 8.7294 | -0.15778
| 6:53 | 8.7297 | -0.15796
| 6:53 | 8.73 | -0.15814
| 6:53 | 8.7303 | -0.15832
| 6:53 | 8.7306 | -0.15833
| 6:53 | 8.7308 | -0.15834
| 6:53 | 8.7311 | -0.15834
| 6:53 | 8.7314 | -0.15834
| 6:53 | 8.7317 | -0.15834
| 6:53 | 8.7319 | -0.15834
| 6:53 | 8.7322 | -0.15834
| 6:53 | 8.7325 | -0.15833
| 6:53 | 8.7328 | -0.15832
| 6:53 | 8.7331 | -0.1583
| 6:53 | 8.7333 | -0.15828
| 6:53 | 8.7336 | -0.15826
| 6:53 | 8.7339 | -0.15824
| 6:53 | 8.7342 | -0.15822
| 6:53 | 8.7344 | -0.15819
| 6:53 | 8.7347 | -0.15816
| 6:53 | 8.735 | -0.15812
| 6:53 | 8.7353 | -0.15808
| 6:53 | 8.7356 | -0.15804
| 6:53 | 8.7358 | -0.158
| 6:53 | 8.7361 | -0.15795
| 6:53 | 8.7364 | -0.15791
| 6:53 | 8.7367 | -0.15785
| 6:53 | 8.7369 | -0.1578
| 6:53 | 8.7372 | -0.15774
| 6:53 | 8.7375 | -0.15769
| 6:53 | 8.7378 | -0.15763
| 6:53 | 8.7381 | -0.15757
| 6:53 | 8.7383 | -0.15751
| 6:53 | 8.7386 | -0.15745
| 6:53 | 8.7389 | -0.15738
| 6:53 | 8.7392 | -0.15732
| 6:53 | 8.7394 | -0.15725
| 6:53 | 8.7397 | -0.15719
| 6:53 | 8.74 | -0.15712
| 6:53 | 8.7403 | -0.15705
| 6:53 | 8.7406 | -0.15698
| 6:53 | 8.7408 | -0.15691
| 6:53 | 8.7411 | -0.15684
| 6:53 | 8.7414 | -0.15677
| 6:53 | 8.7417 | -0.15669
| 6:53 | 8.7419 | -0.15662
| 6:53 | 8.7422 | -0.15654
| 6:53 | 8.7425 | -0.15646
| 6:53 | 8.7428 | -0.15638
| 6:53 | 8.7431 | -0.15629
| 6:53 | 8.7433 | -0.15621
| 6:53 | 8.7436 | -0.15612
| 6:53 | 8.7439 | -0.15603
| 6:53 | 8.7442 | -0.15593
| 6:53 | 8.7444 | -0.15583
| 6:53 | 8.7447 | -0.15573
| 6:53 | 8.745 | -0.15563
| 6:54 | 8.7453 | -0.15552
| 6:54 | 8.7456 | -0.1554
| 6:54 | 8.7458 | -0.15529
| 6:54 | 8.7461 | -0.15517
| 6:54 | 8.7464 | -0.15505
| 6:54 | 8.7467 | -0.15492
| 6:54 | 8.7469 | -0.15479
| 6:54 | 8.7472 | -0.15466
| 6:54 | 8.7475 | -0.15451
| 6:54 | 8.7478 | -0.15437
| 6:54 | 8.7481 | -0.15422
| 6:54 | 8.7483 | -0.15407
| 6:54 | 8.7486 | -0.15391
| 6:54 | 8.7489 | -0.15376
| 6:54 | 8.7492 | -0.1536
| 6:54 | 8.7494 | -0.15344
| 6:54 | 8.7497 | -0.15327
| 6:54 | 8.75 | -0.15311
| 6:54 | 8.7503 | -0.15294
| 6:54 | 8.7506 | -0.15276
| 6:54 | 8.7508 | -0.15259
| 6:54 | 8.7511 | -0.15241
| 6:54 | 8.7514 | -0.15222
| 6:54 | 8.7517 | -0.15203
| 6:54 | 8.7519 | -0.15184
| 6:54 | 8.7522 | -0.15164
| 6:54 | 8.7525 | -0.15144
| 6:54 | 8.7528 | -0.15124
| 6:54 | 8.7531 | -0.15104
| 6:54 | 8.7533 | -0.15083
| 6:54 | 8.7536 | -0.15063
| 6:54 | 8.7539 | -0.15042
| 6:54 | 8.7542 | -0.1502
| 6:54 | 8.7544 | -0.14999
| 6:54 | 8.7547 | -0.14977
| 6:54 | 8.755 | -0.14956
| 6:54 | 8.7553 | -0.14933
| 6:54 | 8.7556 | -0.14911
| 6:54 | 8.7558 | -0.14887
| 6:54 | 8.7561 | -0.14862
| 6:54 | 8.7564 | -0.14837
| 6:54 | 8.7567 | -0.1481
| 6:54 | 8.7569 | -0.14783
| 6:54 | 8.7572 | -0.14754
| 6:54 | 8.7575 | -0.14725
| 6:54 | 8.7578 | -0.14695
| 6:54 | 8.7581 | -0.14664
| 6:54 | 8.7583 | -0.14631
| 6:54 | 8.7586 | -0.14599
| 6:54 | 8.7589 | -0.14566
| 6:54 | 8.7592 | -0.14531
| 6:54 | 8.7594 | -0.14497
| 6:54 | 8.7597 | -0.14463
| 6:54 | 8.76 | -0.14428
| 6:54 | 8.7603 | -0.14394
| 6:54 | 8.7606 | -0.14359
| 6:54 | 8.7608 | -0.14324
| 6:54 | 8.7611 | -0.14289
| 6:54 | 8.7614 | -0.14254
| 6:54 | 8.7617 | -0.14218
| 6:55 | 8.7619 | -0.14183
| 6:55 | 8.7622 | -0.14147
| 6:55 | 8.7625 | -0.1411
| 6:55 | 8.7628 | -0.14072
| 6:55 | 8.7631 | -0.14033
| 6:55 | 8.7633 | -0.13994
| 6:55 | 8.7636 | -0.13954
| 6:55 | 8.7639 | -0.13914
| 6:55 | 8.7642 | -0.13873
| 6:55 | 8.7644 | -0.13832
| 6:55 | 8.7647 | -0.13791
| 6:55 | 8.765 | -0.13749
| 6:55 | 8.7653 | -0.13707
| 6:55 | 8.7656 | -0.13664
| 6:55 | 8.7658 | -0.13621
| 6:55 | 8.7661 | -0.13577
| 6:55 | 8.7664 | -0.13533
| 6:55 | 8.7667 | -0.13488
| 6:55 | 8.7669 | -0.13443
| 6:55 | 8.7672 | -0.13398
| 6:55 | 8.7675 | -0.13353
| 6:55 | 8.7678 | -0.13308
| 6:55 | 8.7681 | -0.13263
| 6:55 | 8.7683 | -0.13218
| 6:55 | 8.7686 | -0.13173
| 6:55 | 8.7689 | -0.13128
| 6:55 | 8.7692 | -0.13083
| 6:55 | 8.7694 | -0.13038
| 6:55 | 8.7697 | -0.12993
| 6:55 | 8.77 | -0.12949
| 6:55 | 8.7703 | -0.12905
| 6:55 | 8.7706 | -0.12862
| 6:55 | 8.7708 | -0.12819
| 6:55 | 8.7711 | -0.12778
| 6:55 | 8.7714 | -0.12736
| 6:55 | 8.7717 | -0.12694
| 6:55 | 8.7719 | -0.12653
| 6:55 | 8.7722 | -0.12613
| 6:55 | 8.7725 | -0.12572
| 6:55 | 8.7728 | -0.12531
| 6:55 | 8.7731 | -0.1249
| 6:55 | 8.7733 | -0.12449
| 6:55 | 8.7736 | -0.12407
| 6:55 | 8.7739 | -0.12366
| 6:55 | 8.7742 | -0.12325
| 6:55 | 8.7744 | -0.12283
| 6:55 | 8.7747 | -0.12241
| 6:55 | 8.775 | -0.12199
| 6:55 | 8.7753 | -0.12157
| 6:55 | 8.7756 | -0.12115
| 6:55 | 8.7758 | -0.12073
| 6:55 | 8.7761 | -0.1203
| 6:55 | 8.7764 | -0.11988
| 6:55 | 8.7767 | -0.11945
| 6:55 | 8.7769 | -0.11902
| 6:55 | 8.7772 | -0.11859
| 6:55 | 8.7775 | -0.11816
| 6:55 | 8.7778 | -0.11772
| 6:55 | 8.7781 | -0.11728
| 6:55 | 8.7783 | -0.11682
| 6:56 | 8.7786 | -0.11636
| 6:56 | 8.7789 | -0.1159
| 6:56 | 8.7792 | -0.11544
| 6:56 | 8.7794 | -0.11496
| 6:56 | 8.7797 | -0.11447
| 6:56 | 8.78 | -0.11399
| 6:56 | 8.7803 | -0.1135
| 6:56 | 8.7806 | -0.11301
| 6:56 | 8.7808 | -0.11251
| 6:56 | 8.7811 | -0.11201
| 6:56 | 8.7814 | -0.1115
| 6:56 | 8.7817 | -0.11099
| 6:56 | 8.7819 | -0.11046
| 6:56 | 8.7822 | -0.10994
| 6:56 | 8.7825 | -0.1094
| 6:56 | 8.7828 | -0.10886
| 6:56 | 8.7831 | -0.10832
| 6:56 | 8.7833 | -0.10775
| 6:56 | 8.7836 | -0.10718
| 6:56 | 8.7839 | -0.10659
| 6:56 | 8.7842 | -0.106
| 6:56 | 8.7844 | -0.10539
| 6:56 | 8.7847 | -0.10478
| 6:56 | 8.785 | -0.10416
| 6:56 | 8.7853 | -0.10353
| 6:56 | 8.7856 | -0.1029
| 6:56 | 8.7858 | -0.10226
| 6:56 | 8.7861 | -0.10163
| 6:56 | 8.7864 | -0.10099
| 6:56 | 8.7867 | -0.10035
| 6:56 | 8.7869 | -0.099701
| 6:56 | 8.7872 | -0.099053
| 6:56 | 8.7875 | -0.098402
| 6:56 | 8.7878 | -0.097748
| 6:56 | 8.7881 | -0.097086
| 6:56 | 8.7883 | -0.096416
| 6:56 | 8.7886 | -0.095747
| 6:56 | 8.7889 | -0.095078
| 6:56 | 8.7892 | -0.094411
| 6:56 | 8.7894 | -0.093744
| 6:56 | 8.7897 | -0.093078
| 6:56 | 8.79 | -0.092412
| 6:56 | 8.7903 | -0.091747
| 6:56 | 8.7906 | -0.091083
| 6:56 | 8.7908 | -0.090419
| 6:56 | 8.7911 | -0.089756
| 6:56 | 8.7914 | -0.089094
| 6:56 | 8.7917 | -0.088433
| 6:56 | 8.7919 | -0.087772
| 6:56 | 8.7922 | -0.087112
| 6:56 | 8.7925 | -0.086452
| 6:56 | 8.7928 | -0.085793
| 6:56 | 8.7931 | -0.08514
| 6:56 | 8.7933 | -0.08449
| 6:56 | 8.7936 | -0.083844
| 6:56 | 8.7939 | -0.0832
| 6:56 | 8.7942 | -0.082559
| 6:56 | 8.7944 | -0.081921
| 6:56 | 8.7947 | -0.081293
| 6:57 | 8.795 | -0.080666
| 6:57 | 8.7953 | -0.080039
| 6:57 | 8.7956 | -0.079413
| 6:57 | 8.7958 | -0.078795
| 6:57 | 8.7961 | -0.078188
| 6:57 | 8.7964 | -0.077589
| 6:57 | 8.7967 | -0.076994
| 6:57 | 8.7969 | -0.076395
| 6:57 | 8.7972 | -0.075793
| 6:57 | 8.7975 | -0.075187
| 6:57 | 8.7978 | -0.074574
| 6:57 | 8.7981 | -0.073953
| 6:57 | 8.7983 | -0.073323
| 6:57 | 8.7986 | -0.072685
| 6:57 | 8.7989 | -0.072039
| 6:57 | 8.7992 | -0.071385
| 6:57 | 8.7994 | -0.070723
| 6:57 | 8.7997 | -0.070052
| 6:57 | 8.8 | -0.069374
| 6:57 | 8.8003 | -0.068688
| 6:57 | 8.8006 | -0.067998
| 6:57 | 8.8008 | -0.067306
| 6:57 | 8.8011 | -0.06661
| 6:57 | 8.8014 | -0.065911
| 6:57 | 8.8017 | -0.065212
| 6:57 | 8.8019 | -0.064514
| 6:57 | 8.8022 | -0.063817
| 6:57 | 8.8025 | -0.063121
| 6:57 | 8.8028 | -0.062426
| 6:57 | 8.8031 | -0.061732
| 6:57 | 8.8033 | -0.06104
| 6:57 | 8.8036 | -0.060349
| 6:57 | 8.8039 | -0.059659
| 6:57 | 8.8042 | -0.05897
| 6:57 | 8.8044 | -0.058282
| 6:57 | 8.8047 | -0.057604
| 6:57 | 8.805 | -0.056932
| 6:57 | 8.8053 | -0.056264
| 6:57 | 8.8056 | -0.055603
| 6:57 | 8.8058 | -0.054942
| 6:57 | 8.8061 | -0.054281
| 6:57 | 8.8064 | -0.053621
| 6:57 | 8.8067 | -0.052961
| 6:57 | 8.8069 | -0.052302
| 6:57 | 8.8072 | -0.051644
| 6:57 | 8.8075 | -0.050986
| 6:57 | 8.8078 | -0.050327
| 6:57 | 8.8081 | -0.049667
| 6:57 | 8.8083 | -0.049007
| 6:57 | 8.8086 | -0.048346
| 6:57 | 8.8089 | -0.047684
| 6:57 | 8.8092 | -0.047022
| 6:57 | 8.8094 | -0.046359
| 6:57 | 8.8097 | -0.045695
| 6:57 | 8.81 | -0.045031
| 6:57 | 8.8103 | -0.044369
| 6:57 | 8.8106 | -0.043708
| 6:57 | 8.8108 | -0.043048
| 6:57 | 8.8111 | -0.042389
| 6:57 | 8.8114 | -0.041731
| 6:58 | 8.8117 | -0.041074
| 6:58 | 8.8119 | -0.040418
| 6:58 | 8.8122 | -0.039767
| 6:58 | 8.8125 | -0.039124
| 6:58 | 8.8128 | -0.038486
| 6:58 | 8.8131 | -0.037852
| 6:58 | 8.8133 | -0.037224
| 6:58 | 8.8136 | -0.036603
| 6:58 | 8.8139 | -0.035999
| 6:58 | 8.8142 | -0.035398
| 6:58 | 8.8144 | -0.034796
| 6:58 | 8.8147 | -0.03419
| 6:58 | 8.815 | -0.033579
| 6:58 | 8.8153 | -0.032965
| 6:58 | 8.8156 | -0.032347
| 6:58 | 8.8158 | -0.031725
| 6:58 | 8.8161 | -0.031099
| 6:58 | 8.8164 | -0.030469
| 6:58 | 8.8167 | -0.029835
| 6:58 | 8.8169 | -0.029198
| 6:58 | 8.8172 | -0.028565
| 6:58 | 8.8175 | -0.027937
| 6:58 | 8.8178 | -0.027313
| 6:58 | 8.8181 | -0.026693
| 6:58 | 8.8183 | -0.026076
| 6:58 | 8.8186 | -0.025465
| 6:58 | 8.8189 | -0.024857
| 6:58 | 8.8192 | -0.024254
| 6:58 | 8.8194 | -0.023664
| 6:58 | 8.8197 | -0.023101
| 6:58 | 8.82 | -0.022574
| 6:58 | 8.8203 | -0.022073
| 6:58 | 8.8206 | -0.021592
| 6:58 | 8.8208 | -0.021111
| 6:58 | 8.8211 | -0.020629
| 6:58 | 8.8214 | -0.020128
| 6:58 | 8.8217 | -0.019615
| 6:58 | 8.8219 | -0.019086
| 6:58 | 8.8222 | -0.018542
| 6:58 | 8.8225 | -0.01799
| 6:58 | 8.8228 | -0.017431
| 6:58 | 8.8231 | -0.016864
| 6:58 | 8.8233 | -0.01629
| 6:58 | 8.8236 | -0.015709
| 6:58 | 8.8239 | -0.01512
| 6:58 | 8.8242 | -0.014523
| 6:58 | 8.8244 | -0.01392
| 6:58 | 8.8247 | -0.013309
| 6:58 | 8.825 | -0.012701
| 6:58 | 8.8253 | -0.012095
| 6:58 | 8.8256 | -0.011492
| 6:58 | 8.8258 | -0.010892
| 6:58 | 8.8261 | -0.010293
| 6:58 | 8.8264 | -0.0096975
| 6:58 | 8.8267 | -0.009104
| 6:58 | 8.8269 | -0.0085117
| 6:58 | 8.8272 | -0.0079203
| 6:58 | 8.8275 | -0.0073296
| 6:58 | 8.8278 | -0.0067397
| 6:58 | 8.8281 | -0.0061506
| 6:59 | 8.8283 | -0.0055622
| 6:59 | 8.8286 | -0.0049745
| 6:59 | 8.8289 | -0.0043876
| 6:59 | 8.8292 | -0.0038014
| 6:59 | 8.8294 | -0.003216
| 6:59 | 8.8297 | -0.0026313
| 6:59 | 8.83 | -0.0020474
| 6:59 | 8.8303 | -0.0014643
| 6:59 | 8.8306 | -0.00088187
| 6:59 | 8.8308 | -0.00032137
| 6:59 | 8.8311 | 0.00024068
| 6:59 | 8.8314 | 0.00080714
| 6:59 | 8.8317 | 0.001378
| 6:59 | 8.8319 | 0.0019533
| 6:59 | 8.8322 | 0.002533
| 6:59 | 8.8325 | 0.0031171
| 6:59 | 8.8328 | 0.0037056
| 6:59 | 8.8331 | 0.0042986
| 6:59 | 8.8333 | 0.0048959
| 6:59 | 8.8336 | 0.0054977
| 6:59 | 8.8339 | 0.0061022
| 6:59 | 8.8342 | 0.0067094
| 6:59 | 8.8344 | 0.0073191
| 6:59 | 8.8347 | 0.0079313
| 6:59 | 8.835 | 0.0085462
| 6:59 | 8.8353 | 0.0091637
| 6:59 | 8.8356 | 0.0097827
| 6:59 | 8.8358 | 0.010402
| 6:59 | 8.8361 | 0.011021
| 6:59 | 8.8364 | 0.01164
| 6:59 | 8.8367 | 0.012258
| 6:59 | 8.8369 | 0.012877
| 6:59 | 8.8372 | 0.013496
| 6:59 | 8.8375 | 0.014115
| 6:59 | 8.8378 | 0.014734
| 6:59 | 8.8381 | 0.015352
| 6:59 | 8.8383 | 0.015971
| 6:59 | 8.8386 | 0.01659
| 6:59 | 8.8389 | 0.017209
| 6:59 | 8.8392 | 0.017827
| 6:59 | 8.8394 | 0.018446
| 6:59 | 8.8397 | 0.019064
| 6:59 | 8.84 | 0.019683
| 6:59 | 8.8403 | 0.020302
| 6:59 | 8.8406 | 0.02092
| 6:59 | 8.8408 | 0.021539
| 6:59 | 8.8411 | 0.022157
| 6:59 | 8.8414 | 0.022776
| 6:59 | 8.8417 | 0.023394
| 6:59 | 8.8419 | 0.024013
| 6:59 | 8.8422 | 0.024631
| 6:59 | 8.8425 | 0.02525
| 6:59 | 8.8428 | 0.025868
| 6:59 | 8.8431 | 0.026487
| 6:59 | 8.8433 | 0.027105
| 6:59 | 8.8436 | 0.027723
| 6:59 | 8.8439 | 0.028342
| 6:59 | 8.8442 | 0.02896
| 6:59 | 8.8444 | 0.029578
| 6:59 | 8.8447 | 0.030197
| 7:00 | 8.845 | 0.030815
| 7:00 | 8.8453 | 0.031433
| 7:00 | 8.8456 | 0.032051
| 7:00 | 8.8458 | 0.03267
| 7:00 | 8.8461 | 0.033288
| 7:00 | 8.8464 | 0.033906
| 7:00 | 8.8467 | 0.034524
| 7:00 | 8.8469 | 0.035142
| 7:00 | 8.8472 | 0.03576
| 7:00 | 8.8475 | 0.036378
| 7:00 | 8.8478 | 0.036996
| 7:00 | 8.8481 | 0.037614
| 7:00 | 8.8483 | 0.038232
| 7:00 | 8.8486 | 0.03885
| 7:00 | 8.8489 | 0.039467
| 7:00 | 8.8492 | 0.040085
| 7:00 | 8.8494 | 0.040703
| 7:00 | 8.8497 | 0.04132
| 7:00 | 8.85 | 0.041935
| 7:00 | 8.8503 | 0.042549
| 7:00 | 8.8506 | 0.043161
| 7:00 | 8.8508 | 0.043772
| 7:00 | 8.8511 | 0.044381
| 7:00 | 8.8514 | 0.044989
| 7:00 | 8.8517 | 0.045596
| 7:00 | 8.8519 | 0.0462
| 7:00 | 8.8522 | 0.046804
| 7:00 | 8.8525 | 0.047406
| 7:00 | 8.8528 | 0.048006
| 7:00 | 8.8531 | 0.048605
| 7:00 | 8.8533 | 0.049203
| 7:00 | 8.8536 | 0.049799
| 7:00 | 8.8539 | 0.050393
| 7:00 | 8.8542 | 0.050987
| 7:00 | 8.8544 | 0.051578
| 7:00 | 8.8547 | 0.052167
| 7:00 | 8.855 | 0.052752
| 7:00 | 8.8553 | 0.053333
| 7:00 | 8.8556 | 0.05391
| 7:00 | 8.8558 | 0.054484
| 7:00 | 8.8561 | 0.055054
| 7:00 | 8.8564 | 0.05562
| 7:00 | 8.8567 | 0.056182
| 7:00 | 8.8569 | 0.056741
| 7:00 | 8.8572 | 0.057296
| 7:00 | 8.8575 | 0.057847
| 7:00 | 8.8578 | 0.058395
| 7:00 | 8.8581 | 0.05894
| 7:00 | 8.8583 | 0.059483
| 7:00 | 8.8586 | 0.060024
| 7:00 | 8.8589 | 0.060562
| 7:00 | 8.8592 | 0.061099
| 7:00 | 8.8594 | 0.061633
| 7:00 | 8.8597 | 0.062165
| 7:00 | 8.86 | 0.062694
| 7:00 | 8.8603 | 0.063222
| 7:00 | 8.8606 | 0.063747
| 7:00 | 8.8608 | 0.06427
| 7:00 | 8.8611 | 0.06479
| 7:00 | 8.8614 | 0.065309
| 7:00 | 8.8617 | 0.065825
| 7:01 | 8.8619 | 0.066337
| 7:01 | 8.8622 | 0.066847
| 7:01 | 8.8625 | 0.067353
| 7:01 | 8.8628 | 0.067855
| 7:01 | 8.8631 | 0.068347
| 7:01 | 8.8633 | 0.06883
| 7:01 | 8.8636 | 0.069306
| 7:01 | 8.8639 | 0.069777
| 7:01 | 8.8642 | 0.070242
| 7:01 | 8.8644 | 0.070701
| 7:01 | 8.8647 | 0.071154
| 7:01 | 8.865 | 0.071601
| 7:01 | 8.8653 | 0.072043
| 7:01 | 8.8656 | 0.072478
| 7:01 | 8.8658 | 0.072907
| 7:01 | 8.8661 | 0.073332
| 7:01 | 8.8664 | 0.073752
| 7:01 | 8.8667 | 0.074169
| 7:01 | 8.8669 | 0.074578
| 7:01 | 8.8672 | 0.074976
| 7:01 | 8.8675 | 0.075365
| 7:01 | 8.8678 | 0.075748
| 7:01 | 8.8681 | 0.076125
| 7:01 | 8.8683 | 0.076497
| 7:01 | 8.8686 | 0.076865
| 7:01 | 8.8689 | 0.07723
| 7:01 | 8.8692 | 0.077593
| 7:01 | 8.8694 | 0.077952
| 7:01 | 8.8697 | 0.078304
| 7:01 | 8.87 | 0.078651
| 7:01 | 8.8703 | 0.07899
| 7:01 | 8.8706 | 0.079324
| 7:01 | 8.8708 | 0.079654
| 7:01 | 8.8711 | 0.07998
| 7:01 | 8.8714 | 0.080302
| 7:01 | 8.8717 | 0.08062
| 7:01 | 8.8719 | 0.080934
| 7:01 | 8.8722 | 0.081244
| 7:01 | 8.8725 | 0.08155
| 7:01 | 8.8728 | 0.081856
| 7:01 | 8.8731 | 0.082161
| 7:01 | 8.8733 | 0.082464
| 7:01 | 8.8736 | 0.082767
| 7:01 | 8.8739 | 0.083068
| 7:01 | 8.8742 | 0.083368
| 7:01 | 8.8744 | 0.083667
| 7:01 | 8.8747 | 0.083959
| 7:01 | 8.875 | 0.084242
| 7:01 | 8.8753 | 0.084519
| 7:01 | 8.8756 | 0.08479
| 7:01 | 8.8758 | 0.085055
| 7:01 | 8.8761 | 0.085316
| 7:01 | 8.8764 | 0.085576
| 7:01 | 8.8767 | 0.085838
| 7:01 | 8.8769 | 0.0861
| 7:01 | 8.8772 | 0.086363
| 7:01 | 8.8775 | 0.086628
| 7:01 | 8.8778 | 0.086893
| 7:01 | 8.8781 | 0.087159
| 7:02 | 8.8783 | 0.087426
| 7:02 | 8.8786 | 0.087694
| 7:02 | 8.8789 | 0.087964
| 7:02 | 8.8792 | 0.088234
| 7:02 | 8.8794 | 0.08851
| 7:02 | 8.8797 | 0.088792
| 7:02 | 8.88 | 0.089085
| 7:02 | 8.8803 | 0.089382
| 7:02 | 8.8806 | 0.089679
| 7:02 | 8.8808 | 0.089976
| 7:02 | 8.8811 | 0.090273
| 7:02 | 8.8814 | 0.090571
| 7:02 | 8.8817 | 0.090868
| 7:02 | 8.8819 | 0.091167
| 7:02 | 8.8822 | 0.091465
| 7:02 | 8.8825 | 0.091764
| 7:02 | 8.8828 | 0.092063
| 7:02 | 8.8831 | 0.092363
| 7:02 | 8.8833 | 0.092662
| 7:02 | 8.8836 | 0.092962
| 7:02 | 8.8839 | 0.093263
| 7:02 | 8.8842 | 0.093562
| 7:02 | 8.8844 | 0.09386
| 7:02 | 8.8847 | 0.094158
| 7:02 | 8.885 | 0.094461
| 7:02 | 8.8853 | 0.09477
| 7:02 | 8.8856 | 0.095084
| 7:02 | 8.8858 | 0.095406
| 7:02 | 8.8861 | 0.095737
| 7:02 | 8.8864 | 0.096078
| 7:02 | 8.8867 | 0.096421
| 7:02 | 8.8869 | 0.09677
| 7:02 | 8.8872 | 0.097124
| 7:02 | 8.8875 | 0.097473
| 7:02 | 8.8878 | 0.097815
| 7:02 | 8.8881 | 0.098148
| 7:02 | 8.8883 | 0.098463
| 7:02 | 8.8886 | 0.098767
| 7:02 | 8.8889 | 0.099067
| 7:02 | 8.8892 | 0.099368
| 7:02 | 8.8894 | 0.099682
| 7:02 | 8.8897 | 0.10001
| 7:02 | 8.89 | 0.10035
| 7:02 | 8.8903 | 0.1007
| 7:02 | 8.8906 | 0.10106
| 7:02 | 8.8908 | 0.10144
| 7:02 | 8.8911 | 0.10183
| 7:02 | 8.8914 | 0.10223
| 7:02 | 8.8917 | 0.10262
| 7:02 | 8.8919 | 0.10301
| 7:02 | 8.8922 | 0.10339
| 7:02 | 8.8925 | 0.10377
| 7:02 | 8.8928 | 0.10415
| 7:02 | 8.8931 | 0.10453
| 7:02 | 8.8933 | 0.1049
| 7:02 | 8.8936 | 0.10527
| 7:02 | 8.8939 | 0.10564
| 7:02 | 8.8942 | 0.106
| 7:02 | 8.8944 | 0.10637
| 7:02 | 8.8947 | 0.10673
| 7:02 | 8.895 | 0.10708
| 7:03 | 8.8953 | 0.10743
| 7:03 | 8.8956 | 0.10778
| 7:03 | 8.8958 | 0.10813
| 7:03 | 8.8961 | 0.10847
| 7:03 | 8.8964 | 0.1088
| 7:03 | 8.8967 | 0.10912
| 7:03 | 8.8969 | 0.10943
| 7:03 | 8.8972 | 0.10972
| 7:03 | 8.8975 | 0.10999
| 7:03 | 8.8978 | 0.11026
| 7:03 | 8.8981 | 0.11052
| 7:03 | 8.8983 | 0.11076
| 7:03 | 8.8986 | 0.11101
| 7:03 | 8.8989 | 0.11124
| 7:03 | 8.8992 | 0.11146
| 7:03 | 8.8994 | 0.11168
| 7:03 | 8.8997 | 0.1119
| 7:03 | 8.9 | 0.11211
| 7:03 | 8.9003 | 0.11232
| 7:03 | 8.9006 | 0.11254
| 7:03 | 8.9008 | 0.11277
| 7:03 | 8.9011 | 0.11301
| 7:03 | 8.9014 | 0.11327
| 7:03 | 8.9017 | 0.11354
| 7:03 | 8.9019 | 0.11382
| 7:03 | 8.9022 | 0.11411
| 7:03 | 8.9025 | 0.11441
| 7:03 | 8.9028 | 0.11474
| 7:03 | 8.9031 | 0.11507
| 7:03 | 8.9033 | 0.11541
| 7:03 | 8.9036 | 0.11576
| 7:03 | 8.9039 | 0.11611
| 7:03 | 8.9042 | 0.11646
| 7:03 | 8.9044 | 0.11682
| 7:03 | 8.9047 | 0.11718
| 7:03 | 8.905 | 0.11754
| 7:03 | 8.9053 | 0.1179
| 7:03 | 8.9056 | 0.11827
| 7:03 | 8.9058 | 0.11864
| 7:03 | 8.9061 | 0.11901
| 7:03 | 8.9064 | 0.11938
| 7:03 | 8.9067 | 0.11975
| 7:03 | 8.9069 | 0.12013
| 7:03 | 8.9072 | 0.12051
| 7:03 | 8.9075 | 0.12089
| 7:03 | 8.9078 | 0.12127
| 7:03 | 8.9081 | 0.12166
| 7:03 | 8.9083 | 0.12205
| 7:03 | 8.9086 | 0.12244
| 7:03 | 8.9089 | 0.12284
| 7:03 | 8.9092 | 0.12323
| 7:03 | 8.9094 | 0.12362
| 7:03 | 8.9097 | 0.12402
| 7:03 | 8.91 | 0.12442
| 7:03 | 8.9103 | 0.12481
| 7:03 | 8.9106 | 0.12521
| 7:03 | 8.9108 | 0.12561
| 7:03 | 8.9111 | 0.12601
| 7:03 | 8.9114 | 0.12641
| 7:04 | 8.9117 | 0.12682
| 7:04 | 8.9119 | 0.12722
| 7:04 | 8.9122 | 0.12763
| 7:04 | 8.9125 | 0.12803
| 7:04 | 8.9128 | 0.12844
| 7:04 | 8.9131 | 0.12884
| 7:04 | 8.9133 | 0.12925
| 7:04 | 8.9136 | 0.12966
| 7:04 | 8.9139 | 0.13006
| 7:04 | 8.9142 | 0.13047
| 7:04 | 8.9144 | 0.13087
| 7:04 | 8.9147 | 0.13128
| 7:04 | 8.915 | 0.13169
| 7:04 | 8.9153 | 0.1321
| 7:04 | 8.9156 | 0.13251
| 7:04 | 8.9158 | 0.13292
| 7:04 | 8.9161 | 0.13334
| 7:04 | 8.9164 | 0.13375
| 7:04 | 8.9167 | 0.13417
| 7:04 | 8.9169 | 0.13458
| 7:04 | 8.9172 | 0.135
| 7:04 | 8.9175 | 0.13542
| 7:04 | 8.9178 | 0.13584
| 7:04 | 8.9181 | 0.13626
| 7:04 | 8.9183 | 0.13668
| 7:04 | 8.9186 | 0.1371
| 7:04 | 8.9189 | 0.13752
| 7:04 | 8.9192 | 0.13794
| 7:04 | 8.9194 | 0.13836
| 7:04 | 8.9197 | 0.13877
| 7:04 | 8.92 | 0.13919
| 7:04 | 8.9203 | 0.1396
| 7:04 | 8.9206 | 0.14002
| 7:04 | 8.9208 | 0.14043
| 7:04 | 8.9211 | 0.14084
| 7:04 | 8.9214 | 0.14125
| 7:04 | 8.9217 | 0.14165
| 7:04 | 8.9219 | 0.14206
| 7:04 | 8.9222 | 0.14246
| 7:04 | 8.9225 | 0.14287
| 7:04 | 8.9228 | 0.14327
| 7:04 | 8.9231 | 0.14367
| 7:04 | 8.9233 | 0.14407
| 7:04 | 8.9236 | 0.14446
| 7:04 | 8.9239 | 0.14486
| 7:04 | 8.9242 | 0.14525
| 7:04 | 8.9244 | 0.14564
| 7:04 | 8.9247 | 0.14603
| 7:04 | 8.925 | 0.14644
| 7:04 | 8.9253 | 0.14684
| 7:04 | 8.9256 | 0.14725
| 7:04 | 8.9258 | 0.14765
| 7:04 | 8.9261 | 0.14804
| 7:04 | 8.9264 | 0.14844
| 7:04 | 8.9267 | 0.14884
| 7:04 | 8.9269 | 0.14923
| 7:04 | 8.9272 | 0.14962
| 7:04 | 8.9275 | 0.15001
| 7:04 | 8.9278 | 0.1504
| 7:04 | 8.9281 | 0.15079
| 7:04 | 8.9283 | 0.15118
| 7:05 | 8.9286 | 0.15156
| 7:05 | 8.9289 | 0.15194
| 7:05 | 8.9292 | 0.15232
| 7:05 | 8.9294 | 0.1527
| 7:05 | 8.9297 | 0.15308
| 7:05 | 8.93 | 0.15345
| 7:05 | 8.9303 | 0.15382
| 7:05 | 8.9306 | 0.15418
| 7:05 | 8.9308 | 0.15454
| 7:05 | 8.9311 | 0.1549
| 7:05 | 8.9314 | 0.15527
| 7:05 | 8.9317 | 0.15564
| 7:05 | 8.9319 | 0.15602
| 7:05 | 8.9322 | 0.1564
| 7:05 | 8.9325 | 0.15679
| 7:05 | 8.9328 | 0.15719
| 7:05 | 8.9331 | 0.15759
| 7:05 | 8.9333 | 0.158
| 7:05 | 8.9336 | 0.1584
| 7:05 | 8.9339 | 0.15882
| 7:05 | 8.9342 | 0.15923
| 7:05 | 8.9344 | 0.15965
| 7:05 | 8.9347 | 0.16006
| 7:05 | 8.935 | 0.16048
| 7:05 | 8.9353 | 0.1609
| 7:05 | 8.9356 | 0.16132
| 7:05 | 8.9358 | 0.16174
| 7:05 | 8.9361 | 0.16216
| 7:05 | 8.9364 | 0.16258
| 7:05 | 8.9367 | 0.163
| 7:05 | 8.9369 | 0.16342
| 7:05 | 8.9372 | 0.16383
| 7:05 | 8.9375 | 0.16425
| 7:05 | 8.9378 | 0.16467
| 7:05 | 8.9381 | 0.16508
| 7:05 | 8.9383 | 0.1655
| 7:05 | 8.9386 | 0.16591
| 7:05 | 8.9389 | 0.16633
| 7:05 | 8.9392 | 0.16674
| 7:05 | 8.9394 | 0.16715
| 7:05 | 8.9397 | 0.16756
| 7:05 | 8.94 | 0.16796
| 7:05 | 8.9403 | 0.16836
| 7:05 | 8.9406 | 0.16876
| 7:05 | 8.9408 | 0.16915
| 7:05 | 8.9411 | 0.16954
| 7:05 | 8.9414 | 0.16993
| 7:05 | 8.9417 | 0.1703
| 7:05 | 8.9419 | 0.17067
| 7:05 | 8.9422 | 0.17104
| 7:05 | 8.9425 | 0.17141
| 7:05 | 8.9428 | 0.17178
| 7:05 | 8.9431 | 0.17215
| 7:05 | 8.9433 | 0.17251
| 7:05 | 8.9436 | 0.17288
| 7:05 | 8.9439 | 0.17324
| 7:05 | 8.9442 | 0.1736
| 7:05 | 8.9444 | 0.17396
| 7:05 | 8.9447 | 0.17432
| 7:06 | 8.945 | 0.17468
| 7:06 | 8.9453 | 0.17503
| 7:06 | 8.9456 | 0.17539
| 7:06 | 8.9458 | 0.17574
| 7:06 | 8.9461 | 0.17609
| 7:06 | 8.9464 | 0.17644
| 7:06 | 8.9467 | 0.17679
| 7:06 | 8.9469 | 0.17713
| 7:06 | 8.9472 | 0.17746
| 7:06 | 8.9475 | 0.17779
| 7:06 | 8.9478 | 0.17812
| 7:06 | 8.9481 | 0.17845
| 7:06 | 8.9483 | 0.17878
| 7:06 | 8.9486 | 0.17911
| 7:06 | 8.9489 | 0.17944
| 7:06 | 8.9492 | 0.17977
| 7:06 | 8.9494 | 0.18011
| 7:06 | 8.9497 | 0.18044
| 7:06 | 8.95 | 0.18077
| 7:06 | 8.9503 | 0.18111
| 7:06 | 8.9506 | 0.18144
| 7:06 | 8.9508 | 0.18177
| 7:06 | 8.9511 | 0.18211
| 7:06 | 8.9514 | 0.18244
| 7:06 | 8.9517 | 0.18278
| 7:06 | 8.9519 | 0.18312
| 7:06 | 8.9522 | 0.18346
| 7:06 | 8.9525 | 0.18381
| 7:06 | 8.9528 | 0.18415
| 7:06 | 8.9531 | 0.1845
| 7:06 | 8.9533 | 0.18485
| 7:06 | 8.9536 | 0.1852
| 7:06 | 8.9539 | 0.18555
| 7:06 | 8.9542 | 0.18591
| 7:06 | 8.9544 | 0.18628
| 7:06 | 8.9547 | 0.18665
| 7:06 | 8.955 | 0.18702
| 7:06 | 8.9553 | 0.1874
| 7:06 | 8.9556 | 0.18777
| 7:06 | 8.9558 | 0.18814
| 7:06 | 8.9561 | 0.1885
| 7:06 | 8.9564 | 0.18887
| 7:06 | 8.9567 | 0.18923
| 7:06 | 8.9569 | 0.18959
| 7:06 | 8.9572 | 0.18995
| 7:06 | 8.9575 | 0.1903
| 7:06 | 8.9578 | 0.19066
| 7:06 | 8.9581 | 0.19101
| 7:06 | 8.9583 | 0.19136
| 7:06 | 8.9586 | 0.19172
| 7:06 | 8.9589 | 0.19208
| 7:06 | 8.9592 | 0.19244
| 7:06 | 8.9594 | 0.1928
| 7:06 | 8.9597 | 0.19317
| 7:06 | 8.96 | 0.19354
| 7:06 | 8.9603 | 0.19392
| 7:06 | 8.9606 | 0.19429
| 7:06 | 8.9608 | 0.19467
| 7:06 | 8.9611 | 0.19505
| 7:06 | 8.9614 | 0.19544
| 7:06 | 8.9617 | 0.19582
| 7:07 | 8.9619 | 0.19621
| 7:07 | 8.9622 | 0.1966
| 7:07 | 8.9625 | 0.19699
| 7:07 | 8.9628 | 0.19738
| 7:07 | 8.9631 | 0.19777
| 7:07 | 8.9633 | 0.19816
| 7:07 | 8.9636 | 0.19855
| 7:07 | 8.9639 | 0.19894
| 7:07 | 8.9642 | 0.19934
| 7:07 | 8.9644 | 0.19973
| 7:07 | 8.9647 | 0.20013
| 7:07 | 8.965 | 0.20053
| 7:07 | 8.9653 | 0.20093
| 7:07 | 8.9656 | 0.20133
| 7:07 | 8.9658 | 0.20173
| 7:07 | 8.9661 | 0.20214
| 7:07 | 8.9664 | 0.20254
| 7:07 | 8.9667 | 0.20295
| 7:07 | 8.9669 | 0.20336
| 7:07 | 8.9672 | 0.20377
| 7:07 | 8.9675 | 0.20418
| 7:07 | 8.9678 | 0.20458
| 7:07 | 8.9681 | 0.20498
| 7:07 | 8.9683 | 0.20538
| 7:07 | 8.9686 | 0.20577
| 7:07 | 8.9689 | 0.20614
| 7:07 | 8.9692 | 0.20649
| 7:07 | 8.9694 | 0.20683
| 7:07 | 8.9697 | 0.20716
| 7:07 | 8.97 | 0.20749
| 7:07 | 8.9703 | 0.20781
| 7:07 | 8.9706 | 0.20814
| 7:07 | 8.9708 | 0.20846
| 7:07 | 8.9711 | 0.20877
| 7:07 | 8.9714 | 0.20904
| 7:07 | 8.9717 | 0.20931
| 7:07 | 8.9719 | 0.20956
| 7:07 | 8.9722 | 0.20981
| 7:07 | 8.9725 | 0.21007
| 7:07 | 8.9728 | 0.21033
| 7:07 | 8.9731 | 0.2106
| 7:07 | 8.9733 | 0.21087
| 7:07 | 8.9736 | 0.21114
| 7:07 | 8.9739 | 0.21143
| 7:07 | 8.9742 | 0.21171
| 7:07 | 8.9744 | 0.21201
| 7:07 | 8.9747 | 0.21228
| 7:07 | 8.975 | 0.21256
| 7:07 | 8.9753 | 0.21283
| 7:07 | 8.9756 | 0.21311
| 7:07 | 8.9758 | 0.21339
| 7:07 | 8.9761 | 0.21367
| 7:07 | 8.9764 | 0.21396
| 7:07 | 8.9767 | 0.21424
| 7:07 | 8.9769 | 0.21453
| 7:07 | 8.9772 | 0.21481
| 7:07 | 8.9775 | 0.2151
| 7:07 | 8.9778 | 0.21539
| 7:07 | 8.9781 | 0.21568
| 7:08 | 8.9783 | 0.21598
| 7:08 | 8.9786 | 0.21628
| 7:08 | 8.9789 | 0.21659
| 7:08 | 8.9792 | 0.2169
| 7:08 | 8.9794 | 0.21722
| 7:08 | 8.9797 | 0.21754
| 7:08 | 8.98 | 0.21787
| 7:08 | 8.9803 | 0.21819
| 7:08 | 8.9806 | 0.21835
| 7:08 | 8.9808 | 0.21852
| 7:08 | 8.9811 | 0.21868
| 7:08 | 8.9814 | 0.21885
| 7:08 | 8.9817 | 0.21902
| 7:08 | 8.9819 | 0.21919
| 7:08 | 8.9822 | 0.21936
| 7:08 | 8.9825 | 0.21953
| 7:08 | 8.9828 | 0.2197
| 7:08 | 8.9831 | 0.21988
| 7:08 | 8.9833 | 0.22005
| 7:08 | 8.9836 | 0.22023
| 7:08 | 8.9839 | 0.22041
| 7:08 | 8.9842 | 0.22059
| 7:08 | 8.9844 | 0.22078
| 7:08 | 8.9847 | 0.22098
| 7:08 | 8.985 | 0.22117
| 7:08 | 8.9853 | 0.22137
| 7:08 | 8.9856 | 0.22157
| 7:08 | 8.9858 | 0.22177
| 7:08 | 8.9861 | 0.22198
| 7:08 | 8.9864 | 0.2222
| 7:08 | 8.9867 | 0.22242
| 7:08 | 8.9869 | 0.22261
| 7:08 | 8.9872 | 0.22281
| 7:08 | 8.9875 | 0.22301
| 7:08 | 8.9878 | 0.22322
| 7:08 | 8.9881 | 0.22342
| 7:08 | 8.9883 | 0.22362
| 7:08 | 8.9886 | 0.22383
| 7:08 | 8.9889 | 0.22404
| 7:08 | 8.9892 | 0.22425
| 7:08 | 8.9894 | 0.22446
| 7:08 | 8.9897 | 0.22468
| 7:08 | 8.99 | 0.2249
| 7:08 | 8.9903 | 0.22513
| 7:08 | 8.9906 | 0.22536
| 7:08 | 8.9908 | 0.2256
| 7:08 | 8.9911 | 0.22584
| 7:08 | 8.9914 | 0.22608
| 7:08 | 8.9917 | 0.22633
| 7:08 | 8.9919 | 0.22657
| 7:08 | 8.9922 | 0.22682
| 7:08 | 8.9925 | 0.22707
| 7:08 | 8.9928 | 0.22731
| 7:08 | 8.9931 | 0.22756
| 7:08 | 8.9933 | 0.22782
| 7:08 | 8.9936 | 0.22808
| 7:08 | 8.9939 | 0.22834
| 7:08 | 8.9942 | 0.2286
| 7:08 | 8.9944 | 0.22886
| 7:08 | 8.9947 | 0.22911
| 7:08 | 8.995 | 0.22937
| 7:09 | 8.9953 | 0.22962
| 7:09 | 8.9956 | 0.22988
| 7:09 | 8.9958 | 0.23013
| 7:09 | 8.9961 | 0.23039
| 7:09 | 8.9964 | 0.23064
| 7:09 | 8.9967 | 0.23089
| 7:09 | 8.9969 | 0.23114
| 7:09 | 8.9972 | 0.2314
| 7:09 | 8.9975 | 0.23165
| 7:09 | 8.9978 | 0.23189
| 7:09 | 8.9981 | 0.23213
| 7:09 | 8.9983 | 0.23236
| 7:09 | 8.9986 | 0.23258
| 7:09 | 8.9989 | 0.2328
| 7:09 | 8.9992 | 0.233
| 7:09 | 8.9994 | 0.2332
| 7:09 | 8.9997 | 0.2334
| 7:09 | 9 | 0.23358
| 7:09 | 9.0003 | 0.23376
| 7:09 | 9.0006 | 0.23394
| 7:09 | 9.0008 | 0.23412
| 7:09 | 9.0011 | 0.23429
| 7:09 | 9.0014 | 0.23446
| 7:09 | 9.0017 | 0.23463
| 7:09 | 9.0019 | 0.2348
| 7:09 | 9.0022 | 0.23498
| 7:09 | 9.0025 | 0.23516
| 7:09 | 9.0028 | 0.23535
| 7:09 | 9.0031 | 0.23556
| 7:09 | 9.0033 | 0.23576
| 7:09 | 9.0036 | 0.23596
| 7:09 | 9.0039 | 0.23615
| 7:09 | 9.0042 | 0.23635
| 7:09 | 9.0044 | 0.23655
| 7:09 | 9.0047 | 0.23674
| 7:09 | 9.005 | 0.23693
| 7:09 | 9.0053 | 0.23712
| 7:09 | 9.0056 | 0.2373
| 7:09 | 9.0058 | 0.23748
| 7:09 | 9.0061 | 0.23764
| 7:09 | 9.0064 | 0.2378
| 7:09 | 9.0067 | 0.23795
| 7:09 | 9.0069 | 0.23809
| 7:09 | 9.0072 | 0.23822
| 7:09 | 9.0075 | 0.23834
| 7:09 | 9.0078 | 0.23845
| 7:09 | 9.0081 | 0.23856
| 7:09 | 9.0083 | 0.23865
| 7:09 | 9.0086 | 0.23874
| 7:09 | 9.0089 | 0.23881
| 7:09 | 9.0092 | 0.23886
| 7:09 | 9.0094 | 0.23891
| 7:09 | 9.0097 | 0.23894
| 7:09 | 9.01 | 0.23897
| 7:09 | 9.0103 | 0.239
| 7:09 | 9.0106 | 0.23902
| 7:09 | 9.0108 | 0.23904
| 7:09 | 9.0111 | 0.23906
| 7:09 | 9.0114 | 0.23908
| 7:10 | 9.0117 | 0.23909
| 7:10 | 9.0119 | 0.2391
| 7:10 | 9.0122 | 0.23908
| 7:10 | 9.0125 | 0.23903
| 7:10 | 9.0128 | 0.23895
| 7:10 | 9.0131 | 0.23883
| 7:10 | 9.0133 | 0.2387
| 7:10 | 9.0136 | 0.23856
| 7:10 | 9.0139 | 0.23839
| 7:10 | 9.0142 | 0.23821
| 7:10 | 9.0144 | 0.23802
| 7:10 | 9.0147 | 0.23783
| 7:10 | 9.015 | 0.23762
| 7:10 | 9.0153 | 0.23741
| 7:10 | 9.0156 | 0.23719
| 7:10 | 9.0158 | 0.23696
| 7:10 | 9.0161 | 0.23672
| 7:10 | 9.0164 | 0.23648
| 7:10 | 9.0167 | 0.23623
| 7:10 | 9.0169 | 0.23597
| 7:10 | 9.0172 | 0.23572
| 7:10 | 9.0175 | 0.23548
| 7:10 | 9.0178 | 0.23526
| 7:10 | 9.0181 | 0.23504
| 7:10 | 9.0183 | 0.23482
| 7:10 | 9.0186 | 0.23459
| 7:10 | 9.0189 | 0.23437
| 7:10 | 9.0192 | 0.23414
| 7:10 | 9.0194 | 0.23391
| 7:10 | 9.0197 | 0.23368
| 7:10 | 9.02 | 0.23345
| 7:10 | 9.0203 | 0.23323
| 7:10 | 9.0206 | 0.23301
| 7:10 | 9.0208 | 0.2328
| 7:10 | 9.0211 | 0.23259
| 7:10 | 9.0214 | 0.23238
| 7:10 | 9.0217 | 0.23217
| 7:10 | 9.0219 | 0.23195
| 7:10 | 9.0222 | 0.23174
| 7:10 | 9.0225 | 0.23153
| 7:10 | 9.0228 | 0.23132
| 7:10 | 9.0231 | 0.23111
| 7:10 | 9.0233 | 0.2309
| 7:10 | 9.0236 | 0.2307
| 7:10 | 9.0239 | 0.2305
| 7:10 | 9.0242 | 0.2303
| 7:10 | 9.0244 | 0.23011
| 7:10 | 9.0247 | 0.22991
| 7:10 | 9.025 | 0.22972
| 7:10 | 9.0253 | 0.22954
| 7:10 | 9.0256 | 0.22935
| 7:10 | 9.0258 | 0.22917
| 7:10 | 9.0261 | 0.229
| 7:10 | 9.0264 | 0.22883
| 7:10 | 9.0267 | 0.22865
| 7:10 | 9.0269 | 0.22847
| 7:10 | 9.0272 | 0.22829
| 7:10 | 9.0275 | 0.2281
| 7:10 | 9.0278 | 0.22791
| 7:10 | 9.0281 | 0.2277
| 7:10 | 9.0283 | 0.22747
| 7:11 | 9.0286 | 0.22725
| 7:11 | 9.0289 | 0.22701
| 7:11 | 9.0292 | 0.22677
| 7:11 | 9.0294 | 0.22652
| 7:11 | 9.0297 | 0.22626
| 7:11 | 9.03 | 0.22599
| 7:11 | 9.0303 | 0.22572
| 7:11 | 9.0306 | 0.22544
| 7:11 | 9.0308 | 0.22516
| 7:11 | 9.0311 | 0.22486
| 7:11 | 9.0314 | 0.22456
| 7:11 | 9.0317 | 0.22424
| 7:11 | 9.0319 | 0.22392
| 7:11 | 9.0322 | 0.22358
| 7:11 | 9.0325 | 0.22324
| 7:11 | 9.0328 | 0.22289
| 7:11 | 9.0331 | 0.22252
| 7:11 | 9.0333 | 0.22214
| 7:11 | 9.0336 | 0.22176
| 7:11 | 9.0339 | 0.22136
| 7:11 | 9.0342 | 0.22096
| 7:11 | 9.0344 | 0.22054
| 7:11 | 9.0347 | 0.22011
| 7:11 | 9.035 | 0.21967
| 7:11 | 9.0353 | 0.21922
| 7:11 | 9.0356 | 0.21876
| 7:11 | 9.0358 | 0.2183
| 7:11 | 9.0361 | 0.21785
| 7:11 | 9.0364 | 0.21739
| 7:11 | 9.0367 | 0.21693
| 7:11 | 9.0369 | 0.21646
| 7:11 | 9.0372 | 0.216
| 7:11 | 9.0375 | 0.21554
| 7:11 | 9.0378 | 0.21507
| 7:11 | 9.0381 | 0.21459
| 7:11 | 9.0383 | 0.2141
| 7:11 | 9.0386 | 0.21362
| 7:11 | 9.0389 | 0.21313
| 7:11 | 9.0392 | 0.21264
| 7:11 | 9.0394 | 0.21215
| 7:11 | 9.0397 | 0.21166
| 7:11 | 9.04 | 0.21116
| 7:11 | 9.0403 | 0.21066
| 7:11 | 9.0406 | 0.21017
| 7:11 | 9.0408 | 0.20966
| 7:11 | 9.0411 | 0.20916
| 7:11 | 9.0414 | 0.20866
| 7:11 | 9.0417 | 0.20816
| 7:11 | 9.0419 | 0.20766
| 7:11 | 9.0422 | 0.20716
| 7:11 | 9.0425 | 0.20666
| 7:11 | 9.0428 | 0.20616
| 7:11 | 9.0431 | 0.20567
| 7:11 | 9.0433 | 0.20518
| 7:11 | 9.0436 | 0.2047
| 7:11 | 9.0439 | 0.20422
| 7:11 | 9.0442 | 0.20374
| 7:11 | 9.0444 | 0.20327
| 7:11 | 9.0447 | 0.20281
| 7:12 | 9.045 | 0.20234
| 7:12 | 9.0453 | 0.20188
| 7:12 | 9.0456 | 0.20142
| 7:12 | 9.0458 | 0.20097
| 7:12 | 9.0461 | 0.20053
| 7:12 | 9.0464 | 0.2001
| 7:12 | 9.0467 | 0.19967
| 7:12 | 9.0469 | 0.19924
| 7:12 | 9.0472 | 0.19881
| 7:12 | 9.0475 | 0.19838
| 7:12 | 9.0478 | 0.19793
| 7:12 | 9.0481 | 0.19749
| 7:12 | 9.0483 | 0.19704
| 7:12 | 9.0486 | 0.19658
| 7:12 | 9.0489 | 0.19612
| 7:12 | 9.0492 | 0.19565
| 7:12 | 9.0494 | 0.19518
| 7:12 | 9.0497 | 0.1947
| 7:12 | 9.05 | 0.19422
| 7:12 | 9.0503 | 0.19373
| 7:12 | 9.0506 | 0.19324
| 7:12 | 9.0508 | 0.19276
| 7:12 | 9.0511 | 0.19226
| 7:12 | 9.0514 | 0.19177
| 7:12 | 9.0517 | 0.19126
| 7:12 | 9.0519 | 0.19076
| 7:12 | 9.0522 | 0.19025
| 7:12 | 9.0525 | 0.18974
| 7:12 | 9.0528 | 0.18922
| 7:12 | 9.0531 | 0.18871
| 7:12 | 9.0533 | 0.18819
| 7:12 | 9.0536 | 0.18767
| 7:12 | 9.0539 | 0.18716
| 7:12 | 9.0542 | 0.18664
| 7:12 | 9.0544 | 0.18613
| 7:12 | 9.0547 | 0.18564
| 7:12 | 9.055 | 0.18514
| 7:12 | 9.0553 | 0.18466
| 7:12 | 9.0556 | 0.18418
| 7:12 | 9.0558 | 0.1837
| 7:12 | 9.0561 | 0.18323
| 7:12 | 9.0564 | 0.18276
| 7:12 | 9.0567 | 0.18229
| 7:12 | 9.0569 | 0.18184
| 7:12 | 9.0572 | 0.18138
| 7:12 | 9.0575 | 0.18093
| 7:12 | 9.0578 | 0.18049
| 7:12 | 9.0581 | 0.18005
| 7:12 | 9.0583 | 0.17961
| 7:12 | 9.0586 | 0.17919
| 7:12 | 9.0589 | 0.17877
| 7:12 | 9.0592 | 0.17835
| 7:12 | 9.0594 | 0.17795
| 7:12 | 9.0597 | 0.17754
| 7:12 | 9.06 | 0.17714
| 7:12 | 9.0603 | 0.17675
| 7:12 | 9.0606 | 0.17635
| 7:12 | 9.0608 | 0.17596
| 7:12 | 9.0611 | 0.17557
| 7:12 | 9.0614 | 0.17518
| 7:12 | 9.0617 | 0.17479
| 7:13 | 9.0619 | 0.17441
| 7:13 | 9.0622 | 0.17403
| 7:13 | 9.0625 | 0.17367
| 7:13 | 9.0628 | 0.17331
| 7:13 | 9.0631 | 0.17296
| 7:13 | 9.0633 | 0.17262
| 7:13 | 9.0636 | 0.17228
| 7:13 | 9.0639 | 0.17197
| 7:13 | 9.0642 | 0.17165
| 7:13 | 9.0644 | 0.17134
| 7:13 | 9.0647 | 0.17101
| 7:13 | 9.065 | 0.17068
| 7:13 | 9.0653 | 0.17034
| 7:13 | 9.0656 | 0.16999
| 7:13 | 9.0658 | 0.16964
| 7:13 | 9.0661 | 0.16928
| 7:13 | 9.0664 | 0.16891
| 7:13 | 9.0667 | 0.16853
| 7:13 | 9.0669 | 0.16815
| 7:13 | 9.0672 | 0.16777
| 7:13 | 9.0675 | 0.16738
| 7:13 | 9.0678 | 0.167
| 7:13 | 9.0681 | 0.16662
| 7:13 | 9.0683 | 0.16624
| 7:13 | 9.0686 | 0.16587
| 7:13 | 9.0689 | 0.1655
| 7:13 | 9.0692 | 0.16513
| 7:13 | 9.0694 | 0.16478
| 7:13 | 9.0697 | 0.16445
| 7:13 | 9.07 | 0.16416
| 7:13 | 9.0703 | 0.1639
| 7:13 | 9.0706 | 0.16365
| 7:13 | 9.0708 | 0.1634
| 7:13 | 9.0711 | 0.16316
| 7:13 | 9.0714 | 0.16289
| 7:13 | 9.0717 | 0.16261
| 7:13 | 9.0719 | 0.16231
| 7:13 | 9.0722 | 0.162
| 7:13 | 9.0725 | 0.16168
| 7:13 | 9.0728 | 0.16134
| 7:13 | 9.0731 | 0.16099
| 7:13 | 9.0733 | 0.16062
| 7:13 | 9.0736 | 0.16024
| 7:13 | 9.0739 | 0.15984
| 7:13 | 9.0742 | 0.15942
| 7:13 | 9.0744 | 0.15899
| 7:13 | 9.0747 | 0.15854
| 7:13 | 9.075 | 0.15809
| 7:13 | 9.0753 | 0.15763
| 7:13 | 9.0756 | 0.15719
| 7:13 | 9.0758 | 0.15676
| 7:13 | 9.0761 | 0.15633
| 7:13 | 9.0764 | 0.1559
| 7:13 | 9.0767 | 0.15546
| 7:13 | 9.0769 | 0.15503
| 7:13 | 9.0772 | 0.15459
| 7:13 | 9.0775 | 0.15416
| 7:13 | 9.0778 | 0.15372
| 7:13 | 9.0781 | 0.15328
| 7:14 | 9.0783 | 0.15285
| 7:14 | 9.0786 | 0.15241
| 7:14 | 9.0789 | 0.15198
| 7:14 | 9.0792 | 0.15155
| 7:14 | 9.0794 | 0.15112
| 7:14 | 9.0797 | 0.15068
| 7:14 | 9.08 | 0.15025
| 7:14 | 9.0803 | 0.14982
| 7:14 | 9.0806 | 0.1494
| 7:14 | 9.0808 | 0.14899
| 7:14 | 9.0811 | 0.14858
| 7:14 | 9.0814 | 0.14817
| 7:14 | 9.0817 | 0.14776
| 7:14 | 9.0819 | 0.14735
| 7:14 | 9.0822 | 0.14693
| 7:14 | 9.0825 | 0.14651
| 7:14 | 9.0828 | 0.14609
| 7:14 | 9.0831 | 0.14567
| 7:14 | 9.0833 | 0.14524
| 7:14 | 9.0836 | 0.14482
| 7:14 | 9.0839 | 0.1444
| 7:14 | 9.0842 | 0.14399
| 7:14 | 9.0844 | 0.14359
| 7:14 | 9.0847 | 0.14319
| 7:14 | 9.085 | 0.14279
| 7:14 | 9.0853 | 0.1424
| 7:14 | 9.0856 | 0.14201
| 7:14 | 9.0858 | 0.14163
| 7:14 | 9.0861 | 0.14125
| 7:14 | 9.0864 | 0.14088
| 7:14 | 9.0867 | 0.14052
| 7:14 | 9.0869 | 0.14016
| 7:14 | 9.0872 | 0.13982
| 7:14 | 9.0875 | 0.1395
| 7:14 | 9.0878 | 0.13918
| 7:14 | 9.0881 | 0.13887
| 7:14 | 9.0883 | 0.13858
| 7:14 | 9.0886 | 0.13829
| 7:14 | 9.0889 | 0.13802
| 7:14 | 9.0892 | 0.13775
| 7:14 | 9.0894 | 0.13749
| 7:14 | 9.0897 | 0.13723
| 7:14 | 9.09 | 0.13698
| 7:14 | 9.0903 | 0.13673
| 7:14 | 9.0906 | 0.1365
| 7:14 | 9.0908 | 0.13626
| 7:14 | 9.0911 | 0.13603
| 7:14 | 9.0914 | 0.13581
| 7:14 | 9.0917 | 0.13559
| 7:14 | 9.0919 | 0.13536
| 7:14 | 9.0922 | 0.13512
| 7:14 | 9.0925 | 0.13488
| 7:14 | 9.0928 | 0.13463
| 7:14 | 9.0931 | 0.13437
| 7:14 | 9.0933 | 0.13412
| 7:14 | 9.0936 | 0.13386
| 7:14 | 9.0939 | 0.13361
| 7:14 | 9.0942 | 0.13336
| 7:14 | 9.0944 | 0.13311
| 7:14 | 9.0947 | 0.13288
| 7:14 | 9.095 | 0.13264
| 7:15 | 9.0953 | 0.1324
| 7:15 | 9.0956 | 0.13217
| 7:15 | 9.0958 | 0.13194
| 7:15 | 9.0961 | 0.13171
| 7:15 | 9.0964 | 0.13148
| 7:15 | 9.0967 | 0.13126
| 7:15 | 9.0969 | 0.13103
| 7:15 | 9.0972 | 0.13081
| 7:15 | 9.0975 | 0.13059
| 7:15 | 9.0978 | 0.13037
| 7:15 | 9.0981 | 0.13015
| 7:15 | 9.0983 | 0.12994
| 7:15 | 9.0986 | 0.12973
| 7:15 | 9.0989 | 0.12951
| 7:15 | 9.0992 | 0.1293
| 7:15 | 9.0994 | 0.1291
| 7:15 | 9.0997 | 0.12889
| 7:15 | 9.1 | 0.12869
| 7:15 | 9.1003 | 0.12849
| 7:15 | 9.1006 | 0.1283
| 7:15 | 9.1008 | 0.12811
| 7:15 | 9.1011 | 0.12794
| 7:15 | 9.1014 | 0.12777
| 7:15 | 9.1017 | 0.1276
| 7:15 | 9.1019 | 0.12743
| 7:15 | 9.1022 | 0.12727
| 7:15 | 9.1025 | 0.12711
| 7:15 | 9.1028 | 0.12695
| 7:15 | 9.1031 | 0.1268
| 7:15 | 9.1033 | 0.12664
| 7:15 | 9.1036 | 0.12649
| 7:15 | 9.1039 | 0.12635
| 7:15 | 9.1042 | 0.12622
| 7:15 | 9.1044 | 0.12609
| 7:15 | 9.1047 | 0.12596
| 7:15 | 9.105 | 0.12584
| 7:15 | 9.1053 | 0.12573
| 7:15 | 9.1056 | 0.12564
| 7:15 | 9.1058 | 0.12554
| 7:15 | 9.1061 | 0.12546
| 7:15 | 9.1064 | 0.12538
| 7:15 | 9.1067 | 0.12531
| 7:15 | 9.1069 | 0.12524
| 7:15 | 9.1072 | 0.12518
| 7:15 | 9.1075 | 0.12512
| 7:15 | 9.1078 | 0.12507
| 7:15 | 9.1081 | 0.12502
| 7:15 | 9.1083 | 0.12498
| 7:15 | 9.1086 | 0.12494
| 7:15 | 9.1089 | 0.1249
| 7:15 | 9.1092 | 0.12487
| 7:15 | 9.1094 | 0.12483
| 7:15 | 9.1097 | 0.12481
| 7:15 | 9.11 | 0.12478
| 7:15 | 9.1103 | 0.12475
| 7:15 | 9.1106 | 0.12473
| 7:15 | 9.1108 | 0.12471
| 7:15 | 9.1111 | 0.12468
| 7:15 | 9.1114 | 0.12466
| 7:16 | 9.1117 | 0.12465
| 7:16 | 9.1119 | 0.12463
| 7:16 | 9.1122 | 0.12461
| 7:16 | 9.1125 | 0.1246
| 7:16 | 9.1128 | 0.12458
| 7:16 | 9.1131 | 0.12458
| 7:16 | 9.1133 | 0.12458
| 7:16 | 9.1136 | 0.12459
| 7:16 | 9.1139 | 0.1246
| 7:16 | 9.1142 | 0.12461
| 7:16 | 9.1144 | 0.12463
| 7:16 | 9.1147 | 0.12465
| 7:16 | 9.115 | 0.12468
| 7:16 | 9.1153 | 0.12471
| 7:16 | 9.1156 | 0.12475
| 7:16 | 9.1158 | 0.12479
| 7:16 | 9.1161 | 0.12483
| 7:16 | 9.1164 | 0.12488
| 7:16 | 9.1167 | 0.12493
| 7:16 | 9.1169 | 0.12499
| 7:16 | 9.1172 | 0.12505
| 7:16 | 9.1175 | 0.12513
| 7:16 | 9.1178 | 0.12522
| 7:16 | 9.1181 | 0.12531
| 7:16 | 9.1183 | 0.12541
| 7:16 | 9.1186 | 0.12551
| 7:16 | 9.1189 | 0.12561
| 7:16 | 9.1192 | 0.12571
| 7:16 | 9.1194 | 0.12582
| 7:16 | 9.1197 | 0.12594
| 7:16 | 9.12 | 0.12606
| 7:16 | 9.1203 | 0.12619
| 7:16 | 9.1206 | 0.12633
| 7:16 | 9.1208 | 0.12647
| 7:16 | 9.1211 | 0.12661
| 7:16 | 9.1214 | 0.12676
| 7:16 | 9.1217 | 0.12691
| 7:16 | 9.1219 | 0.12706
| 7:16 | 9.1222 | 0.12722
| 7:16 | 9.1225 | 0.12738
| 7:16 | 9.1228 | 0.12755
| 7:16 | 9.1231 | 0.12771
| 7:16 | 9.1233 | 0.12788
| 7:16 | 9.1236 | 0.12805
| 7:16 | 9.1239 | 0.12821
| 7:16 | 9.1242 | 0.12838
| 7:16 | 9.1244 | 0.12856
| 7:16 | 9.1247 | 0.12873
| 7:16 | 9.125 | 0.12892
| 7:16 | 9.1253 | 0.12911
| 7:16 | 9.1256 | 0.1293
| 7:16 | 9.1258 | 0.1295
| 7:16 | 9.1261 | 0.12971
| 7:16 | 9.1264 | 0.12991
| 7:16 | 9.1267 | 0.13011
| 7:16 | 9.1269 | 0.13031
| 7:16 | 9.1272 | 0.13051
| 7:16 | 9.1275 | 0.13071
| 7:16 | 9.1278 | 0.1309
| 7:16 | 9.1281 | 0.1311
| 7:16 | 9.1283 | 0.13129
| 7:17 | 9.1286 | 0.13148
| 7:17 | 9.1289 | 0.13166
| 7:17 | 9.1292 | 0.13185
| 7:17 | 9.1294 | 0.13203
| 7:17 | 9.1297 | 0.1322
| 7:17 | 9.13 | 0.13236
| 7:17 | 9.1303 | 0.13251
| 7:17 | 9.1306 | 0.13267
| 7:17 | 9.1308 | 0.13282
| 7:17 | 9.1311 | 0.13297
| 7:17 | 9.1314 | 0.13312
| 7:17 | 9.1317 | 0.13327
| 7:17 | 9.1319 | 0.13342
| 7:17 | 9.1322 | 0.13357
| 7:17 | 9.1325 | 0.13372
| 7:17 | 9.1328 | 0.13386
| 7:17 | 9.1331 | 0.134
| 7:17 | 9.1333 | 0.13415
| 7:17 | 9.1336 | 0.13429
| 7:17 | 9.1339 | 0.13443
| 7:17 | 9.1342 | 0.13457
| 7:17 | 9.1344 | 0.13471
| 7:17 | 9.1347 | 0.13484
| 7:17 | 9.135 | 0.13497
| 7:17 | 9.1353 | 0.13509
| 7:17 | 9.1356 | 0.1352
| 7:17 | 9.1358 | 0.13531
| 7:17 | 9.1361 | 0.1354
| 7:17 | 9.1364 | 0.13548
| 7:17 | 9.1367 | 0.13555
| 7:17 | 9.1369 | 0.13562
| 7:17 | 9.1372 | 0.13567
| 7:17 | 9.1375 | 0.13574
| 7:17 | 9.1378 | 0.1358
| 7:17 | 9.1381 | 0.13587
| 7:17 | 9.1383 | 0.13596
| 7:17 | 9.1386 | 0.13606
| 7:17 | 9.1389 | 0.13615
| 7:17 | 9.1392 | 0.13625
| 7:17 | 9.1394 | 0.13633
| 7:17 | 9.1397 | 0.13639
| 7:17 | 9.14 | 0.13644
| 7:17 | 9.1403 | 0.13648
| 7:17 | 9.1406 | 0.1365
| 7:17 | 9.1408 | 0.1365
| 7:17 | 9.1411 | 0.13649
| 7:17 | 9.1414 | 0.13647
| 7:17 | 9.1417 | 0.13645
| 7:17 | 9.1419 | 0.13644
| 7:17 | 9.1422 | 0.13642
| 7:17 | 9.1425 | 0.13641
| 7:17 | 9.1428 | 0.13639
| 7:17 | 9.1431 | 0.13638
| 7:17 | 9.1433 | 0.13636
| 7:17 | 9.1436 | 0.13635
| 7:17 | 9.1439 | 0.13634
| 7:17 | 9.1442 | 0.13633
| 7:17 | 9.1444 | 0.13632
| 7:17 | 9.1447 | 0.13631
| 7:17 | 9.145 | 0.1363
| 7:18 | 9.1453 | 0.13629
| 7:18 | 9.1456 | 0.13628
| 7:18 | 9.1458 | 0.13627
| 7:18 | 9.1461 | 0.13627
| 7:18 | 9.1464 | 0.13627
| 7:18 | 9.1467 | 0.13628
| 7:18 | 9.1469 | 0.1363
| 7:18 | 9.1472 | 0.13634
| 7:18 | 9.1475 | 0.13639
| 7:18 | 9.1478 | 0.13645
| 7:18 | 9.1481 | 0.13651
| 7:18 | 9.1483 | 0.13658
| 7:18 | 9.1486 | 0.13666
| 7:18 | 9.1489 | 0.13674
| 7:18 | 9.1492 | 0.13683
| 7:18 | 9.1494 | 0.13692
| 7:18 | 9.1497 | 0.13702
| 7:18 | 9.15 | 0.13712
| 7:18 | 9.1503 | 0.13723
| 7:18 | 9.1506 | 0.13734
| 7:18 | 9.1508 | 0.13743
| 7:18 | 9.1511 | 0.13752
| 7:18 | 9.1514 | 0.13759
| 7:18 | 9.1517 | 0.13765
| 7:18 | 9.1519 | 0.13771
| 7:18 | 9.1522 | 0.13776
| 7:18 | 9.1525 | 0.13779
| 7:18 | 9.1528 | 0.13782
| 7:18 | 9.1531 | 0.13783
| 7:18 | 9.1533 | 0.13783
| 7:18 | 9.1536 | 0.13783
| 7:18 | 9.1539 | 0.13782
| 7:18 | 9.1542 | 0.13782
| 7:18 | 9.1544 | 0.13781
| 7:18 | 9.1547 | 0.1378
| 7:18 | 9.155 | 0.13779
| 7:18 | 9.1553 | 0.13778
| 7:18 | 9.1556 | 0.13777
| 7:18 | 9.1558 | 0.13776
| 7:18 | 9.1561 | 0.13775
| 7:18 | 9.1564 | 0.13773
| 7:18 | 9.1567 | 0.13772
| 7:18 | 9.1569 | 0.1377
| 7:18 | 9.1572 | 0.13768
| 7:18 | 9.1575 | 0.13767
| 7:18 | 9.1578 | 0.13765
| 7:18 | 9.1581 | 0.13762
| 7:18 | 9.1583 | 0.13759
| 7:18 | 9.1586 | 0.13757
| 7:18 | 9.1589 | 0.13754
| 7:18 | 9.1592 | 0.13752
| 7:18 | 9.1594 | 0.13749
| 7:18 | 9.1597 | 0.13747
| 7:18 | 9.16 | 0.13744
| 7:18 | 9.1603 | 0.13742
| 7:18 | 9.1606 | 0.1374
| 7:18 | 9.1608 | 0.13737
| 7:18 | 9.1611 | 0.13735
| 7:18 | 9.1614 | 0.13733
| 7:18 | 9.1617 | 0.13731
| 7:19 | 9.1619 | 0.13729
| 7:19 | 9.1622 | 0.13727
| 7:19 | 9.1625 | 0.13724
| 7:19 | 9.1628 | 0.13722
| 7:19 | 9.1631 | 0.1372
| 7:19 | 9.1633 | 0.13718
| 7:19 | 9.1636 | 0.13717
| 7:19 | 9.1639 | 0.13715
| 7:19 | 9.1642 | 0.13714
| 7:19 | 9.1644 | 0.13713
| 7:19 | 9.1647 | 0.13711
| 7:19 | 9.165 | 0.13709
| 7:19 | 9.1653 | 0.13707
| 7:19 | 9.1656 | 0.13704
| 7:19 | 9.1658 | 0.13702
| 7:19 | 9.1661 | 0.13699
| 7:19 | 9.1664 | 0.13696
| 7:19 | 9.1667 | 0.13693
| 7:19 | 9.1669 | 0.13688
| 7:19 | 9.1672 | 0.13684
| 7:19 | 9.1675 | 0.13679
| 7:19 | 9.1678 | 0.13675
| 7:19 | 9.1681 | 0.13671
| 7:19 | 9.1683 | 0.13667
| 7:19 | 9.1686 | 0.13663
| 7:19 | 9.1689 | 0.13659
| 7:19 | 9.1692 | 0.13656
| 7:19 | 9.1694 | 0.13652
| 7:19 | 9.1697 | 0.13649
| 7:19 | 9.17 | 0.13646
| 7:19 | 9.1703 | 0.13643
| 7:19 | 9.1706 | 0.1364
| 7:19 | 9.1708 | 0.13636
| 7:19 | 9.1711 | 0.13633
| 7:19 | 9.1714 | 0.13629
| 7:19 | 9.1717 | 0.13624
| 7:19 | 9.1719 | 0.13619
| 7:19 | 9.1722 | 0.13613
| 7:19 | 9.1725 | 0.13608
| 7:19 | 9.1728 | 0.13603
| 7:19 | 9.1731 | 0.13599
| 7:19 | 9.1733 | 0.13596
| 7:19 | 9.1736 | 0.13594
| 7:19 | 9.1739 | 0.13592
| 7:19 | 9.1742 | 0.13591
| 7:19 | 9.1744 | 0.13591
| 7:19 | 9.1747 | 0.13591
| 7:19 | 9.175 | 0.13589
| 7:19 | 9.1753 | 0.13588
| 7:19 | 9.1756 | 0.13586
| 7:19 | 9.1758 | 0.13585
| 7:19 | 9.1761 | 0.13584
| 7:19 | 9.1764 | 0.13583
| 7:19 | 9.1767 | 0.13582
| 7:19 | 9.1769 | 0.13582
| 7:19 | 9.1772 | 0.13581
| 7:19 | 9.1775 | 0.13581
| 7:19 | 9.1778 | 0.13581
| 7:19 | 9.1781 | 0.13581
| 7:20 | 9.1783 | 0.13581
| 7:20 | 9.1786 | 0.13581
| 7:20 | 9.1789 | 0.13582
| 7:20 | 9.1792 | 0.13582
| 7:20 | 9.1794 | 0.13583
| 7:20 | 9.1797 | 0.13584
| 7:20 | 9.18 | 0.13585
| 7:20 | 9.1803 | 0.13587
| 7:20 | 9.1806 | 0.13589
| 7:20 | 9.1808 | 0.13592
| 7:20 | 9.1811 | 0.13594
| 7:20 | 9.1814 | 0.13596
| 7:20 | 9.1817 | 0.13597
| 7:20 | 9.1819 | 0.13598
| 7:20 | 9.1822 | 0.13598
| 7:20 | 9.1825 | 0.13597
| 7:20 | 9.1828 | 0.13596
| 7:20 | 9.1831 | 0.13594
| 7:20 | 9.1833 | 0.13591
| 7:20 | 9.1836 | 0.13589
| 7:20 | 9.1839 | 0.13586
| 7:20 | 9.1842 | 0.13583
| 7:20 | 9.1844 | 0.13579
| 7:20 | 9.1847 | 0.13576
| 7:20 | 9.185 | 0.13572
| 7:20 | 9.1853 | 0.13568
| 7:20 | 9.1856 | 0.13564
| 7:20 | 9.1858 | 0.1356
| 7:20 | 9.1861 | 0.13557
| 7:20 | 9.1864 | 0.13553
| 7:20 | 9.1867 | 0.1355
| 7:20 | 9.1869 | 0.13547
| 7:20 | 9.1872 | 0.13544
| 7:20 | 9.1875 | 0.13541
| 7:20 | 9.1878 | 0.13539
| 7:20 | 9.1881 | 0.13536
| 7:20 | 9.1883 | 0.13534
| 7:20 | 9.1886 | 0.13532
| 7:20 | 9.1889 | 0.1353
| 7:20 | 9.1892 | 0.13529
| 7:20 | 9.1894 | 0.13528
| 7:20 | 9.1897 | 0.13528
| 7:20 | 9.19 | 0.13528
| 7:20 | 9.1903 | 0.1353
| 7:20 | 9.1906 | 0.13532
| 7:20 | 9.1908 | 0.13534
| 7:20 | 9.1911 | 0.13538
| 7:20 | 9.1914 | 0.13542
| 7:20 | 9.1917 | 0.13546
| 7:20 | 9.1919 | 0.13552
| 7:20 | 9.1922 | 0.13557
| 7:20 | 9.1925 | 0.13563
| 7:20 | 9.1928 | 0.13569
| 7:20 | 9.1931 | 0.13576
| 7:20 | 9.1933 | 0.13583
| 7:20 | 9.1936 | 0.1359
| 7:20 | 9.1939 | 0.13597
| 7:20 | 9.1942 | 0.13604
| 7:20 | 9.1944 | 0.13612
| 7:20 | 9.1947 | 0.1362
| 7:21 | 9.195 | 0.13629
| 7:21 | 9.1953 | 0.13637
| 7:21 | 9.1956 | 0.13646
| 7:21 | 9.1958 | 0.13655
| 7:21 | 9.1961 | 0.13664
| 7:21 | 9.1964 | 0.13674
| 7:21 | 9.1967 | 0.13684
| 7:21 | 9.1969 | 0.13695
| 7:21 | 9.1972 | 0.13707
| 7:21 | 9.1975 | 0.1372
| 7:21 | 9.1978 | 0.13732
| 7:21 | 9.1981 | 0.13745
| 7:21 | 9.1983 | 0.13757
| 7:21 | 9.1986 | 0.1377
| 7:21 | 9.1989 | 0.13782
| 7:21 | 9.1992 | 0.13795
| 7:21 | 9.1994 | 0.13808
| 7:21 | 9.1997 | 0.13821
| 7:21 | 9.2 | 0.13834
| 7:21 | 9.2003 | 0.13848
| 7:21 | 9.2006 | 0.13861
| 7:21 | 9.2008 | 0.13874
| 7:21 | 9.2011 | 0.13888
| 7:21 | 9.2014 | 0.13901
| 7:21 | 9.2017 | 0.13915
| 7:21 | 9.2019 | 0.13929
| 7:21 | 9.2022 | 0.13942
| 7:21 | 9.2025 | 0.13955
| 7:21 | 9.2028 | 0.13968
| 7:21 | 9.2031 | 0.13981
| 7:21 | 9.2033 | 0.13994
| 7:21 | 9.2036 | 0.14006
| 7:21 | 9.2039 | 0.14019
| 7:21 | 9.2042 | 0.1403
| 7:21 | 9.2044 | 0.14041
| 7:21 | 9.2047 | 0.14052
| 7:21 | 9.205 | 0.14062
| 7:21 | 9.2053 | 0.14073
| 7:21 | 9.2056 | 0.14084
| 7:21 | 9.2058 | 0.14095
| 7:21 | 9.2061 | 0.14106
| 7:21 | 9.2064 | 0.14117
| 7:21 | 9.2067 | 0.14129
| 7:21 | 9.2069 | 0.14141
| 7:21 | 9.2072 | 0.14153
| 7:21 | 9.2075 | 0.14166
| 7:21 | 9.2078 | 0.14178
| 7:21 | 9.2081 | 0.14191
| 7:21 | 9.2083 | 0.14204
| 7:21 | 9.2086 | 0.14216
| 7:21 | 9.2089 | 0.14228
| 7:21 | 9.2092 | 0.1424
| 7:21 | 9.2094 | 0.14252
| 7:21 | 9.2097 | 0.14263
| 7:21 | 9.21 | 0.14274
| 7:21 | 9.2103 | 0.14285
| 7:21 | 9.2106 | 0.14295
| 7:21 | 9.2108 | 0.14306
| 7:21 | 9.2111 | 0.14316
| 7:21 | 9.2114 | 0.14326
| 7:22 | 9.2117 | 0.14335
| 7:22 | 9.2119 | 0.14345
| 7:22 | 9.2122 | 0.14354
| 7:22 | 9.2125 | 0.14364
| 7:22 | 9.2128 | 0.14373
| 7:22 | 9.2131 | 0.14382
| 7:22 | 9.2133 | 0.14392
| 7:22 | 9.2136 | 0.14401
| 7:22 | 9.2139 | 0.1441
| 7:22 | 9.2142 | 0.14419
| 7:22 | 9.2144 | 0.14428
| 7:22 | 9.2147 | 0.14437
| 7:22 | 9.215 | 0.14446
| 7:22 | 9.2153 | 0.14454
| 7:22 | 9.2156 | 0.14463
| 7:22 | 9.2158 | 0.14471
| 7:22 | 9.2161 | 0.14479
| 7:22 | 9.2164 | 0.14487
| 7:22 | 9.2167 | 0.14494
| 7:22 | 9.2169 | 0.14502
| 7:22 | 9.2172 | 0.1451
| 7:22 | 9.2175 | 0.14518
| 7:22 | 9.2178 | 0.14526
| 7:22 | 9.2181 | 0.14535
| 7:22 | 9.2183 | 0.14544
| 7:22 | 9.2186 | 0.14554
| 7:22 | 9.2189 | 0.14565
| 7:22 | 9.2192 | 0.14579
| 7:22 | 9.2194 | 0.14594
| 7:22 | 9.2197 | 0.1461
| 7:22 | 9.22 | 0.14626
| 7:22 | 9.2203 | 0.14642
| 7:22 | 9.2206 | 0.14658
| 7:22 | 9.2208 | 0.14675
| 7:22 | 9.2211 | 0.14694
| 7:22 | 9.2214 | 0.14715
| 7:22 | 9.2217 | 0.14737
| 7:22 | 9.2219 | 0.14761
| 7:22 | 9.2222 | 0.14785
| 7:22 | 9.2225 | 0.14808
| 7:22 | 9.2228 | 0.14831
| 7:22 | 9.2231 | 0.14854
| 7:22 | 9.2233 | 0.14876
| 7:22 | 9.2236 | 0.14897
| 7:22 | 9.2239 | 0.14918
| 7:22 | 9.2242 | 0.14938
| 7:22 | 9.2244 | 0.14958
| 7:22 | 9.2247 | 0.1498
| 7:22 | 9.225 | 0.15002
| 7:22 | 9.2253 | 0.15023
| 7:22 | 9.2256 | 0.15045
| 7:22 | 9.2258 | 0.15067
| 7:22 | 9.2261 | 0.15088
| 7:22 | 9.2264 | 0.15109
| 7:22 | 9.2267 | 0.1513
| 7:22 | 9.2269 | 0.15152
| 7:22 | 9.2272 | 0.15173
| 7:22 | 9.2275 | 0.15194
| 7:22 | 9.2278 | 0.15214
| 7:22 | 9.2281 | 0.15235
| 7:22 | 9.2283 | 0.15256
| 7:23 | 9.2286 | 0.15276
| 7:23 | 9.2289 | 0.15295
| 7:23 | 9.2292 | 0.15314
| 7:23 | 9.2294 | 0.15332
| 7:23 | 9.2297 | 0.1535
| 7:23 | 9.23 | 0.15368
| 7:23 | 9.2303 | 0.15386
| 7:23 | 9.2306 | 0.15404
| 7:23 | 9.2308 | 0.15421
| 7:23 | 9.2311 | 0.15439
| 7:23 | 9.2314 | 0.15456
| 7:23 | 9.2317 | 0.15473
| 7:23 | 9.2319 | 0.1549
| 7:23 | 9.2322 | 0.15507
| 7:23 | 9.2325 | 0.15524
| 7:23 | 9.2328 | 0.1554
| 7:23 | 9.2331 | 0.15556
| 7:23 | 9.2333 | 0.15573
| 7:23 | 9.2336 | 0.15589
| 7:23 | 9.2339 | 0.15604
| 7:23 | 9.2342 | 0.15619
| 7:23 | 9.2344 | 0.15634
| 7:23 | 9.2347 | 0.15648
| 7:23 | 9.235 | 0.15662
| 7:23 | 9.2353 | 0.15676
| 7:23 | 9.2356 | 0.1569
| 7:23 | 9.2358 | 0.15703
| 7:23 | 9.2361 | 0.15715
| 7:23 | 9.2364 | 0.15726
| 7:23 | 9.2367 | 0.15738
| 7:23 | 9.2369 | 0.15752
| 7:23 | 9.2372 | 0.15765
| 7:23 | 9.2375 | 0.15778
| 7:23 | 9.2378 | 0.15791
| 7:23 | 9.2381 | 0.15804
| 7:23 | 9.2383 | 0.15817
| 7:23 | 9.2386 | 0.15829
| 7:23 | 9.2389 | 0.15842
| 7:23 | 9.2392 | 0.15854
| 7:23 | 9.2394 | 0.15865
| 7:23 | 9.2397 | 0.15877
| 7:23 | 9.24 | 0.15887
| 7:23 | 9.2403 | 0.15897
| 7:23 | 9.2406 | 0.15907
| 7:23 | 9.2408 | 0.15917
| 7:23 | 9.2411 | 0.15925
| 7:23 | 9.2414 | 0.15934
| 7:23 | 9.2417 | 0.15942
| 7:23 | 9.2419 | 0.15951
| 7:23 | 9.2422 | 0.15959
| 7:23 | 9.2425 | 0.15967
| 7:23 | 9.2428 | 0.15975
| 7:23 | 9.2431 | 0.15983
| 7:23 | 9.2433 | 0.15989
| 7:23 | 9.2436 | 0.15996
| 7:23 | 9.2439 | 0.16002
| 7:23 | 9.2442 | 0.16008
| 7:23 | 9.2444 | 0.16015
| 7:23 | 9.2447 | 0.1602
| 7:24 | 9.245 | 0.16026
| 7:24 | 9.2453 | 0.16032
| 7:24 | 9.2456 | 0.16037
| 7:24 | 9.2458 | 0.16043
| 7:24 | 9.2461 | 0.16048
| 7:24 | 9.2464 | 0.16053
| 7:24 | 9.2467 | 0.16058
| 7:24 | 9.2469 | 0.16063
| 7:24 | 9.2472 | 0.16066
| 7:24 | 9.2475 | 0.1607
| 7:24 | 9.2478 | 0.16074
| 7:24 | 9.2481 | 0.16079
| 7:24 | 9.2483 | 0.16084
| 7:24 | 9.2486 | 0.1609
| 7:24 | 9.2489 | 0.16097
| 7:24 | 9.2492 | 0.16104
| 7:24 | 9.2494 | 0.16112
| 7:24 | 9.2497 | 0.16121
| 7:24 | 9.25 | 0.1613
| 7:24 | 9.2503 | 0.16139
| 7:24 | 9.2506 | 0.16149
| 7:24 | 9.2508 | 0.16158
| 7:24 | 9.2511 | 0.16167
| 7:24 | 9.2514 | 0.16177
| 7:24 | 9.2517 | 0.16186
| 7:24 | 9.2519 | 0.16194
| 7:24 | 9.2522 | 0.16203
| 7:24 | 9.2525 | 0.1621
| 7:24 | 9.2528 | 0.16216
| 7:24 | 9.2531 | 0.16221
| 7:24 | 9.2533 | 0.16227
| 7:24 | 9.2536 | 0.16232
| 7:24 | 9.2539 | 0.16237
| 7:24 | 9.2542 | 0.16243
| 7:24 | 9.2544 | 0.16248
| 7:24 | 9.2547 | 0.16254
| 7:24 | 9.255 | 0.16259
| 7:24 | 9.2553 | 0.16265
| 7:24 | 9.2556 | 0.16271
| 7:24 | 9.2558 | 0.16276
| 7:24 | 9.2561 | 0.16282
| 7:24 | 9.2564 | 0.16288
| 7:24 | 9.2567 | 0.16294
| 7:24 | 9.2569 | 0.163
| 7:24 | 9.2572 | 0.16306
| 7:24 | 9.2575 | 0.16313
| 7:24 | 9.2578 | 0.16319
| 7:24 | 9.2581 | 0.16325
| 7:24 | 9.2583 | 0.16332
| 7:24 | 9.2586 | 0.16338
| 7:24 | 9.2589 | 0.16346
| 7:24 | 9.2592 | 0.16355
| 7:24 | 9.2594 | 0.16365
| 7:24 | 9.2597 | 0.16375
| 7:24 | 9.26 | 0.16387
| 7:24 | 9.2603 | 0.16398
| 7:24 | 9.2606 | 0.1641
| 7:24 | 9.2608 | 0.16422
| 7:24 | 9.2611 | 0.16434
| 7:24 | 9.2614 | 0.16447
| 7:24 | 9.2617 | 0.1646
| 7:25 | 9.2619 | 0.16473
| 7:25 | 9.2622 | 0.16489
| 7:25 | 9.2625 | 0.16506
| 7:25 | 9.2628 | 0.16526
| 7:25 | 9.2631 | 0.16549
| 7:25 | 9.2633 | 0.16573
| 7:25 | 9.2636 | 0.16597
| 7:25 | 9.2639 | 0.16624
| 7:25 | 9.2642 | 0.16652
| 7:25 | 9.2644 | 0.16681
| 7:25 | 9.2647 | 0.1671
| 7:25 | 9.265 | 0.16739
| 7:25 | 9.2653 | 0.16769
| 7:25 | 9.2656 | 0.16799
| 7:25 | 9.2658 | 0.1683
| 7:25 | 9.2661 | 0.16861
| 7:25 | 9.2664 | 0.16893
| 7:25 | 9.2667 | 0.16925
| 7:25 | 9.2669 | 0.16957
| 7:25 | 9.2672 | 0.16988
| 7:25 | 9.2675 | 0.17019
| 7:25 | 9.2678 | 0.17048
| 7:25 | 9.2681 | 0.17077
| 7:25 | 9.2683 | 0.17107
| 7:25 | 9.2686 | 0.17136
| 7:25 | 9.2689 | 0.17166
| 7:25 | 9.2692 | 0.17196
| 7:25 | 9.2694 | 0.17227
| 7:25 | 9.2697 | 0.17258
| 7:25 | 9.27 | 0.17289
| 7:25 | 9.2703 | 0.1732
| 7:25 | 9.2706 | 0.17352
| 7:25 | 9.2708 | 0.17383
| 7:25 | 9.2711 | 0.17415
| 7:25 | 9.2714 | 0.17447
| 7:25 | 9.2717 | 0.17479
| 7:25 | 9.2719 | 0.17512
| 7:25 | 9.2722 | 0.17545
| 7:25 | 9.2725 | 0.17578
| 7:25 | 9.2728 | 0.17611
| 7:25 | 9.2731 | 0.17644
| 7:25 | 9.2733 | 0.17676
| 7:25 | 9.2736 | 0.17707
| 7:25 | 9.2739 | 0.17738
| 7:25 | 9.2742 | 0.17769
| 7:25 | 9.2744 | 0.178
| 7:25 | 9.2747 | 0.1783
| 7:25 | 9.275 | 0.17859
| 7:25 | 9.2753 | 0.17889
| 7:25 | 9.2756 | 0.17917
| 7:25 | 9.2758 | 0.17945
| 7:25 | 9.2761 | 0.17973
| 7:25 | 9.2764 | 0.18
| 7:25 | 9.2767 | 0.18027
| 7:25 | 9.2769 | 0.18055
| 7:25 | 9.2772 | 0.18083
| 7:25 | 9.2775 | 0.1811
| 7:25 | 9.2778 | 0.18138
| 7:25 | 9.2781 | 0.18167
| 7:26 | 9.2783 | 0.18197
| 7:26 | 9.2786 | 0.18226
| 7:26 | 9.2789 | 0.18256
| 7:26 | 9.2792 | 0.18286
| 7:26 | 9.2794 | 0.18316
| 7:26 | 9.2797 | 0.18346
| 7:26 | 9.28 | 0.18376
| 7:26 | 9.2803 | 0.18407
| 7:26 | 9.2806 | 0.18437
| 7:26 | 9.2808 | 0.18469
| 7:26 | 9.2811 | 0.185
| 7:26 | 9.2814 | 0.18532
| 7:26 | 9.2817 | 0.18564
| 7:26 | 9.2819 | 0.18597
| 7:26 | 9.2822 | 0.1863
| 7:26 | 9.2825 | 0.18663
| 7:26 | 9.2828 | 0.18697
| 7:26 | 9.2831 | 0.18731
| 7:26 | 9.2833 | 0.18765
| 7:26 | 9.2836 | 0.18798
| 7:26 | 9.2839 | 0.18831
| 7:26 | 9.2842 | 0.18864
| 7:26 | 9.2844 | 0.18897
| 7:26 | 9.2847 | 0.18931
| 7:26 | 9.285 | 0.18965
| 7:26 | 9.2853 | 0.19
| 7:26 | 9.2856 | 0.19034
| 7:26 | 9.2858 | 0.19069
| 7:26 | 9.2861 | 0.19103
| 7:26 | 9.2864 | 0.19137
| 7:26 | 9.2867 | 0.19171
| 7:26 | 9.2869 | 0.19205
| 7:26 | 9.2872 | 0.19239
| 7:26 | 9.2875 | 0.19272
| 7:26 | 9.2878 | 0.19306
| 7:26 | 9.2881 | 0.19339
| 7:26 | 9.2883 | 0.19373
| 7:26 | 9.2886 | 0.19407
| 7:26 | 9.2889 | 0.19441
| 7:26 | 9.2892 | 0.19475
| 7:26 | 9.2894 | 0.19509
| 7:26 | 9.2897 | 0.19544
| 7:26 | 9.29 | 0.19579
| 7:26 | 9.2903 | 0.19614
| 7:26 | 9.2906 | 0.19649
| 7:26 | 9.2908 | 0.19685
| 7:26 | 9.2911 | 0.19721
| 7:26 | 9.2914 | 0.19757
| 7:26 | 9.2917 | 0.19793
| 7:26 | 9.2919 | 0.19829
| 7:26 | 9.2922 | 0.19865
| 7:26 | 9.2925 | 0.19901
| 7:26 | 9.2928 | 0.19936
| 7:26 | 9.2931 | 0.19972
| 7:26 | 9.2933 | 0.20007
| 7:26 | 9.2936 | 0.20043
| 7:26 | 9.2939 | 0.20078
| 7:26 | 9.2942 | 0.20114
| 7:26 | 9.2944 | 0.20149
| 7:26 | 9.2947 | 0.20185
| 7:26 | 9.295 | 0.2022
| 7:27 | 9.2953 | 0.20255
| 7:27 | 9.2956 | 0.2029
| 7:27 | 9.2958 | 0.20325
| 7:27 | 9.2961 | 0.2036
| 7:27 | 9.2964 | 0.20395
| 7:27 | 9.2967 | 0.2043
| 7:27 | 9.2969 | 0.20465
| 7:27 | 9.2972 | 0.205
| 7:27 | 9.2975 | 0.20535
| 7:27 | 9.2978 | 0.20569
| 7:27 | 9.2981 | 0.20603
| 7:27 | 9.2983 | 0.20637
| 7:27 | 9.2986 | 0.2067
| 7:27 | 9.2989 | 0.20704
| 7:27 | 9.2992 | 0.20737
| 7:27 | 9.2994 | 0.20769
| 7:27 | 9.2997 | 0.20802
| 7:27 | 9.3 | 0.20834
| 7:27 | 9.3003 | 0.20866
| 7:27 | 9.3006 | 0.20897
| 7:27 | 9.3008 | 0.20928
| 7:27 | 9.3011 | 0.20959
| 7:27 | 9.3014 | 0.20991
| 7:27 | 9.3017 | 0.21023
| 7:27 | 9.3019 | 0.21055
| 7:27 | 9.3022 | 0.21087
| 7:27 | 9.3025 | 0.21121
| 7:27 | 9.3028 | 0.21154
| 7:27 | 9.3031 | 0.21188
| 7:27 | 9.3033 | 0.21222
| 7:27 | 9.3036 | 0.21256
| 7:27 | 9.3039 | 0.2129
| 7:27 | 9.3042 | 0.21324
| 7:27 | 9.3044 | 0.21357
| 7:27 | 9.3047 | 0.21391
| 7:27 | 9.305 | 0.21424
| 7:27 | 9.3053 | 0.21458
| 7:27 | 9.3056 | 0.21491
| 7:27 | 9.3058 | 0.21524
| 7:27 | 9.3061 | 0.21556
| 7:27 | 9.3064 | 0.21588
| 7:27 | 9.3067 | 0.21619
| 7:27 | 9.3069 | 0.2165
| 7:27 | 9.3072 | 0.2168
| 7:27 | 9.3075 | 0.21709
| 7:27 | 9.3078 | 0.21738
| 7:27 | 9.3081 | 0.21766
| 7:27 | 9.3083 | 0.21794
| 7:27 | 9.3086 | 0.2182
| 7:27 | 9.3089 | 0.21846
| 7:27 | 9.3092 | 0.21872
| 7:27 | 9.3094 | 0.21896
| 7:27 | 9.3097 | 0.2192
| 7:27 | 9.31 | 0.21944
| 7:27 | 9.3103 | 0.21968
| 7:27 | 9.3106 | 0.21991
| 7:27 | 9.3108 | 0.22014
| 7:27 | 9.3111 | 0.22038
| 7:27 | 9.3114 | 0.22061
| 7:28 | 9.3117 | 0.22084
| 7:28 | 9.3119 | 0.22106
| 7:28 | 9.3122 | 0.22128
| 7:28 | 9.3125 | 0.2215
| 7:28 | 9.3128 | 0.22172
| 7:28 | 9.3131 | 0.22194
| 7:28 | 9.3133 | 0.22215
| 7:28 | 9.3136 | 0.22236
| 7:28 | 9.3139 | 0.22257
| 7:28 | 9.3142 | 0.22278
| 7:28 | 9.3144 | 0.22299
| 7:28 | 9.3147 | 0.22321
| 7:28 | 9.315 | 0.22343
| 7:28 | 9.3153 | 0.22365
| 7:28 | 9.3156 | 0.22387
| 7:28 | 9.3158 | 0.2241
| 7:28 | 9.3161 | 0.22434
| 7:28 | 9.3164 | 0.22457
| 7:28 | 9.3167 | 0.22481
| 7:28 | 9.3169 | 0.22505
| 7:28 | 9.3172 | 0.2253
| 7:28 | 9.3175 | 0.22555
| 7:28 | 9.3178 | 0.2258
| 7:28 | 9.3181 | 0.22605
| 7:28 | 9.3183 | 0.22631
| 7:28 | 9.3186 | 0.22656
| 7:28 | 9.3189 | 0.22682
| 7:28 | 9.3192 | 0.22708
| 7:28 | 9.3194 | 0.22733
| 7:28 | 9.3197 | 0.22759
| 7:28 | 9.32 | 0.22785
| 7:28 | 9.3203 | 0.22811
| 7:28 | 9.3206 | 0.22836
| 7:28 | 9.3208 | 0.22862
| 7:28 | 9.3211 | 0.22888
| 7:28 | 9.3214 | 0.22914
| 7:28 | 9.3217 | 0.2294
| 7:28 | 9.3219 | 0.22966
| 7:28 | 9.3222 | 0.22992
| 7:28 | 9.3225 | 0.23018
| 7:28 | 9.3228 | 0.23044
| 7:28 | 9.3231 | 0.23072
| 7:28 | 9.3233 | 0.23101
| 7:28 | 9.3236 | 0.2313
| 7:28 | 9.3239 | 0.2316
| 7:28 | 9.3242 | 0.23191
| 7:28 | 9.3244 | 0.23223
| 7:28 | 9.3247 | 0.23256
| 7:28 | 9.325 | 0.23289
| 7:28 | 9.3253 | 0.23323
| 7:28 | 9.3256 | 0.23355
| 7:28 | 9.3258 | 0.23387
| 7:28 | 9.3261 | 0.2342
| 7:28 | 9.3264 | 0.23452
| 7:28 | 9.3267 | 0.23485
| 7:28 | 9.3269 | 0.23518
| 7:28 | 9.3272 | 0.23551
| 7:28 | 9.3275 | 0.23585
| 7:28 | 9.3278 | 0.23618
| 7:28 | 9.3281 | 0.23652
| 7:28 | 9.3283 | 0.23685
| 7:29 | 9.3286 | 0.23719
| 7:29 | 9.3289 | 0.23752
| 7:29 | 9.3292 | 0.23786
| 7:29 | 9.3294 | 0.2382
| 7:29 | 9.3297 | 0.23853
| 7:29 | 9.33 | 0.23887
| 7:29 | 9.3303 | 0.23921
| 7:29 | 9.3306 | 0.23954
| 7:29 | 9.3308 | 0.23988
| 7:29 | 9.3311 | 0.24022
| 7:29 | 9.3314 | 0.24055
| 7:29 | 9.3317 | 0.24088
| 7:29 | 9.3319 | 0.24121
| 7:29 | 9.3322 | 0.24154
| 7:29 | 9.3325 | 0.24187
| 7:29 | 9.3328 | 0.24219
| 7:29 | 9.3331 | 0.24251
| 7:29 | 9.3333 | 0.24283
| 7:29 | 9.3336 | 0.24315
| 7:29 | 9.3339 | 0.24346
| 7:29 | 9.3342 | 0.24376
| 7:29 | 9.3344 | 0.24404
| 7:29 | 9.3347 | 0.24432
| 7:29 | 9.335 | 0.2446
| 7:29 | 9.3353 | 0.24487
| 7:29 | 9.3356 | 0.24513
| 7:29 | 9.3358 | 0.24539
| 7:29 | 9.3361 | 0.24564
| 7:29 | 9.3364 | 0.24589
| 7:29 | 9.3367 | 0.24613
| 7:29 | 9.3369 | 0.24636
| 7:29 | 9.3372 | 0.24657
| 7:29 | 9.3375 | 0.24678
| 7:29 | 9.3378 | 0.24697
| 7:29 | 9.3381 | 0.24716
| 7:29 | 9.3383 | 0.24733
| 7:29 | 9.3386 | 0.2475
| 7:29 | 9.3389 | 0.24765
| 7:29 | 9.3392 | 0.24779
| 7:29 | 9.3394 | 0.24793
| 7:29 | 9.3397 | 0.24807
| 7:29 | 9.34 | 0.2482
| 7:29 | 9.3403 | 0.24832
| 7:29 | 9.3406 | 0.24844
| 7:29 | 9.3408 | 0.24856
| 7:29 | 9.3411 | 0.24867
| 7:29 | 9.3414 | 0.24877
| 7:29 | 9.3417 | 0.24887
| 7:29 | 9.3419 | 0.24898
| 7:29 | 9.3422 | 0.2491
| 7:29 | 9.3425 | 0.24923
| 7:29 | 9.3428 | 0.24936
| 7:29 | 9.3431 | 0.2495
| 7:29 | 9.3433 | 0.24963
| 7:29 | 9.3436 | 0.24977
| 7:29 | 9.3439 | 0.2499
| 7:29 | 9.3442 | 0.25004
| 7:29 | 9.3444 | 0.25017
| 7:29 | 9.3447 | 0.25029
| 7:30 | 9.345 | 0.25041
| 7:30 | 9.3453 | 0.25053
| 7:30 | 9.3456 | 0.25065
| 7:30 | 9.3458 | 0.25076
| 7:30 | 9.3461 | 0.25088
| 7:30 | 9.3464 | 0.25099
| 7:30 | 9.3467 | 0.2511
| 7:30 | 9.3469 | 0.25121
| 7:30 | 9.3472 | 0.25132
| 7:30 | 9.3475 | 0.25143
| 7:30 | 9.3478 | 0.25153
| 7:30 | 9.3481 | 0.25164
| 7:30 | 9.3483 | 0.25174
| 7:30 | 9.3486 | 0.25184
| 7:30 | 9.3489 | 0.25194
| 7:30 | 9.3492 | 0.25203
| 7:30 | 9.3494 | 0.25213
| 7:30 | 9.3497 | 0.25222
| 7:30 | 9.35 | 0.25232
| 7:30 | 9.3503 | 0.2524
| 7:30 | 9.3506 | 0.25249
| 7:30 | 9.3508 | 0.25256
| 7:30 | 9.3511 | 0.25262
| 7:30 | 9.3514 | 0.25268
| 7:30 | 9.3517 | 0.25274
| 7:30 | 9.3519 | 0.2528
| 7:30 | 9.3522 | 0.25285
| 7:30 | 9.3525 | 0.2529
| 7:30 | 9.3528 | 0.25295
| 7:30 | 9.3531 | 0.253
| 7:30 | 9.3533 | 0.25304
| 7:30 | 9.3536 | 0.25309
| 7:30 | 9.3539 | 0.25312
| 7:30 | 9.3542 | 0.25315
| 7:30 | 9.3544 | 0.25317
| 7:30 | 9.3547 | 0.25319
| 7:30 | 9.355 | 0.25321
| 7:30 | 9.3553 | 0.25322
| 7:30 | 9.3556 | 0.25322
| 7:30 | 9.3558 | 0.25321
| 7:30 | 9.3561 | 0.25321
| 7:30 | 9.3564 | 0.25319
| 7:30 | 9.3567 | 0.25318
| 7:30 | 9.3569 | 0.25316
| 7:30 | 9.3572 | 0.25314
| 7:30 | 9.3575 | 0.25312
| 7:30 | 9.3578 | 0.25309
| 7:30 | 9.3581 | 0.25306
| 7:30 | 9.3583 | 0.25303
| 7:30 | 9.3586 | 0.253
| 7:30 | 9.3589 | 0.25296
| 7:30 | 9.3592 | 0.25292
| 7:30 | 9.3594 | 0.25288
| 7:30 | 9.3597 | 0.25284
| 7:30 | 9.36 | 0.2528
| 7:30 | 9.3603 | 0.25276
| 7:30 | 9.3606 | 0.25271
| 7:30 | 9.3608 | 0.25267
| 7:30 | 9.3611 | 0.25263
| 7:30 | 9.3614 | 0.25258
| 7:30 | 9.3617 | 0.25254
| 7:31 | 9.3619 | 0.25249
| 7:31 | 9.3622 | 0.25245
| 7:31 | 9.3625 | 0.2524
| 7:31 | 9.3628 | 0.25236
| 7:31 | 9.3631 | 0.25231
| 7:31 | 9.3633 | 0.25226
| 7:31 | 9.3636 | 0.25222
| 7:31 | 9.3639 | 0.25217
| 7:31 | 9.3642 | 0.25212
| 7:31 | 9.3644 | 0.25207
| 7:31 | 9.3647 | 0.25201
| 7:31 | 9.365 | 0.25195
| 7:31 | 9.3653 | 0.25187
| 7:31 | 9.3656 | 0.2518
| 7:31 | 9.3658 | 0.25171
| 7:31 | 9.3661 | 0.25162
| 7:31 | 9.3664 | 0.25152
| 7:31 | 9.3667 | 0.25141
| 7:31 | 9.3669 | 0.2513
| 7:31 | 9.3672 | 0.25118
| 7:31 | 9.3675 | 0.25104
| 7:31 | 9.3678 | 0.25084
| 7:31 | 9.3681 | 0.25064
| 7:31 | 9.3683 | 0.25042
| 7:31 | 9.3686 | 0.25019
| 7:31 | 9.3689 | 0.24996
| 7:31 | 9.3692 | 0.24972
| 7:31 | 9.3694 | 0.2495
| 7:31 | 9.3697 | 0.24927
| 7:31 | 9.37 | 0.24905
| 7:31 | 9.3703 | 0.24884
| 7:31 | 9.3706 | 0.24864
| 7:31 | 9.3708 | 0.24846
| 7:31 | 9.3711 | 0.24828
| 7:31 | 9.3714 | 0.24811
| 7:31 | 9.3717 | 0.24794
| 7:31 | 9.3719 | 0.24777
| 7:31 | 9.3722 | 0.2476
| 7:31 | 9.3725 | 0.24743
| 7:31 | 9.3728 | 0.24727
| 7:31 | 9.3731 | 0.24711
| 7:31 | 9.3733 | 0.24696
| 7:31 | 9.3736 | 0.2468
| 7:31 | 9.3739 | 0.24665
| 7:31 | 9.3742 | 0.24651
| 7:31 | 9.3744 | 0.24637
| 7:31 | 9.3747 | 0.24623
| 7:31 | 9.375 | 0.2461
| 7:31 | 9.3753 | 0.24597
| 7:31 | 9.3756 | 0.24584
| 7:31 | 9.3758 | 0.24571
| 7:31 | 9.3761 | 0.24559
| 7:31 | 9.3764 | 0.24546
| 7:31 | 9.3767 | 0.24534
| 7:31 | 9.3769 | 0.24523
| 7:31 | 9.3772 | 0.24511
| 7:31 | 9.3775 | 0.245
| 7:31 | 9.3778 | 0.24489
| 7:31 | 9.3781 | 0.24478
| 7:32 | 9.3783 | 0.24467
| 7:32 | 9.3786 | 0.24457
| 7:32 | 9.3789 | 0.24447
| 7:32 | 9.3792 | 0.24437
| 7:32 | 9.3794 | 0.24427
| 7:32 | 9.3797 | 0.24418
| 7:32 | 9.38 | 0.24409
| 7:32 | 9.3803 | 0.244
| 7:32 | 9.3806 | 0.24391
| 7:32 | 9.3808 | 0.24382
| 7:32 | 9.3811 | 0.24373
| 7:32 | 9.3814 | 0.24364
| 7:32 | 9.3817 | 0.24356
| 7:32 | 9.3819 | 0.24347
| 7:32 | 9.3822 | 0.24339
| 7:32 | 9.3825 | 0.2433
| 7:32 | 9.3828 | 0.24322
| 7:32 | 9.3831 | 0.24314
| 7:32 | 9.3833 | 0.24306
| 7:32 | 9.3836 | 0.24298
| 7:32 | 9.3839 | 0.2429
| 7:32 | 9.3842 | 0.24283
| 7:32 | 9.3844 | 0.24275
| 7:32 | 9.3847 | 0.24268
| 7:32 | 9.385 | 0.2426
| 7:32 | 9.3853 | 0.24253
| 7:32 | 9.3856 | 0.24246
| 7:32 | 9.3858 | 0.24239
| 7:32 | 9.3861 | 0.24232
| 7:32 | 9.3864 | 0.24225
| 7:32 | 9.3867 | 0.24218
| 7:32 | 9.3869 | 0.24211
| 7:32 | 9.3872 | 0.24204
| 7:32 | 9.3875 | 0.24198
| 7:32 | 9.3878 | 0.24191
| 7:32 | 9.3881 | 0.24185
| 7:32 | 9.3883 | 0.24179
| 7:32 | 9.3886 | 0.24173
| 7:32 | 9.3889 | 0.24167
| 7:32 | 9.3892 | 0.24161
| 7:32 | 9.3894 | 0.24155
| 7:32 | 9.3897 | 0.2415
| 7:32 | 9.39 | 0.24145
| 7:32 | 9.3903 | 0.24139
| 7:32 | 9.3906 | 0.24135
| 7:32 | 9.3908 | 0.2413
| 7:32 | 9.3911 | 0.24126
| 7:32 | 9.3914 | 0.24121
| 7:32 | 9.3917 | 0.24117
| 7:32 | 9.3919 | 0.24113
| 7:32 | 9.3922 | 0.24109
| 7:32 | 9.3925 | 0.24106
| 7:32 | 9.3928 | 0.24102
| 7:32 | 9.3931 | 0.24098
| 7:32 | 9.3933 | 0.24095
| 7:32 | 9.3936 | 0.24092
| 7:32 | 9.3939 | 0.24088
| 7:32 | 9.3942 | 0.24085
| 7:32 | 9.3944 | 0.24082
| 7:32 | 9.3947 | 0.2408
| 7:32 | 9.395 | 0.24077
| 7:33 | 9.3953 | 0.24074
| 7:33 | 9.3956 | 0.24072
| 7:33 | 9.3958 | 0.24069
| 7:33 | 9.3961 | 0.24067
| 7:33 | 9.3964 | 0.24065
| 7:33 | 9.3967 | 0.24063
| 7:33 | 9.3969 | 0.24061
| 7:33 | 9.3972 | 0.2406
| 7:33 | 9.3975 | 0.2406
| 7:33 | 9.3978 | 0.24059
| 7:33 | 9.3981 | 0.24059
| 7:33 | 9.3983 | 0.24058
| 7:33 | 9.3986 | 0.24058
| 7:33 | 9.3989 | 0.24058
| 7:33 | 9.3992 | 0.24058
| 7:33 | 9.3994 | 0.24059
| 7:33 | 9.3997 | 0.24059
| 7:33 | 9.4 | 0.2406
| 7:33 | 9.4003 | 0.24061
| 7:33 | 9.4006 | 0.24062
| 7:33 | 9.4008 | 0.24063
| 7:33 | 9.4011 | 0.24064
| 7:33 | 9.4014 | 0.24065
| 7:33 | 9.4017 | 0.24067
| 7:33 | 9.4019 | 0.24068
| 7:33 | 9.4022 | 0.2407
| 7:33 | 9.4025 | 0.24072
| 7:33 | 9.4028 | 0.24074
| 7:33 | 9.4031 | 0.24077
| 7:33 | 9.4033 | 0.24079
| 7:33 | 9.4036 | 0.24082
| 7:33 | 9.4039 | 0.24084
| 7:33 | 9.4042 | 0.24087
| 7:33 | 9.4044 | 0.2409
| 7:33 | 9.4047 | 0.24094
| 7:33 | 9.405 | 0.24097
| 7:33 | 9.4053 | 0.241
| 7:33 | 9.4056 | 0.24103
| 7:33 | 9.4058 | 0.24106
| 7:33 | 9.4061 | 0.2411
| 7:33 | 9.4064 | 0.24113
| 7:33 | 9.4067 | 0.24116
| 7:33 | 9.4069 | 0.24119
| 7:33 | 9.4072 | 0.24122
| 7:33 | 9.4075 | 0.24126
| 7:33 | 9.4078 | 0.24129
| 7:33 | 9.4081 | 0.24132
| 7:33 | 9.4083 | 0.24135
| 7:33 | 9.4086 | 0.24138
| 7:33 | 9.4089 | 0.24141
| 7:33 | 9.4092 | 0.24144
| 7:33 | 9.4094 | 0.24146
| 7:33 | 9.4097 | 0.24147
| 7:33 | 9.41 | 0.24148
| 7:33 | 9.4103 | 0.24148
| 7:33 | 9.4106 | 0.24148
| 7:33 | 9.4108 | 0.24144
| 7:33 | 9.4111 | 0.24137
| 7:33 | 9.4114 | 0.24127
| 7:34 | 9.4117 | 0.24117
| 7:34 | 9.4119 | 0.24106
| 7:34 | 9.4122 | 0.24094
| 7:34 | 9.4125 | 0.24082
| 7:34 | 9.4128 | 0.24069
| 7:34 | 9.4131 | 0.24057
| 7:34 | 9.4133 | 0.24043
| 7:34 | 9.4136 | 0.24029
| 7:34 | 9.4139 | 0.24012
| 7:34 | 9.4142 | 0.23992
| 7:34 | 9.4144 | 0.2397
| 7:34 | 9.4147 | 0.23947
| 7:34 | 9.415 | 0.23922
| 7:34 | 9.4153 | 0.23895
| 7:34 | 9.4156 | 0.23867
| 7:34 | 9.4158 | 0.23837
| 7:34 | 9.4161 | 0.23805
| 7:34 | 9.4164 | 0.23772
| 7:34 | 9.4167 | 0.23739
| 7:34 | 9.4169 | 0.23707
| 7:34 | 9.4172 | 0.23677
| 7:34 | 9.4175 | 0.23647
| 7:34 | 9.4178 | 0.23618
| 7:34 | 9.4181 | 0.23589
| 7:34 | 9.4183 | 0.23562
| 7:34 | 9.4186 | 0.23535
| 7:34 | 9.4189 | 0.23507
| 7:34 | 9.4192 | 0.23479
| 7:34 | 9.4194 | 0.23453
| 7:34 | 9.4197 | 0.23427
| 7:34 | 9.42 | 0.23402
| 7:34 | 9.4203 | 0.23379
| 7:34 | 9.4206 | 0.23356
| 7:34 | 9.4208 | 0.23334
| 7:34 | 9.4211 | 0.23314
| 7:34 | 9.4214 | 0.23294
| 7:34 | 9.4217 | 0.23277
| 7:34 | 9.4219 | 0.23264
| 7:34 | 9.4222 | 0.23254
| 7:34 | 9.4225 | 0.23247
| 7:34 | 9.4228 | 0.23239
| 7:34 | 9.4231 | 0.23231
| 7:34 | 9.4233 | 0.23223
| 7:34 | 9.4236 | 0.23215
| 7:34 | 9.4239 | 0.23206
| 7:34 | 9.4242 | 0.23197
| 7:34 | 9.4244 | 0.23188
| 7:34 | 9.4247 | 0.23178
| 7:34 | 9.425 | 0.23168
| 7:34 | 9.4253 | 0.23158
| 7:34 | 9.4256 | 0.23148
| 7:34 | 9.4258 | 0.23138
| 7:34 | 9.4261 | 0.23127
| 7:34 | 9.4264 | 0.23116
| 7:34 | 9.4267 | 0.23105
| 7:34 | 9.4269 | 0.23094
| 7:34 | 9.4272 | 0.23084
| 7:34 | 9.4275 | 0.23073
| 7:34 | 9.4278 | 0.23062
| 7:34 | 9.4281 | 0.23051
| 7:34 | 9.4283 | 0.23041
| 7:35 | 9.4286 | 0.23032
| 7:35 | 9.4289 | 0.23024
| 7:35 | 9.4292 | 0.23016
| 7:35 | 9.4294 | 0.23009
| 7:35 | 9.4297 | 0.23004
| 7:35 | 9.43 | 0.22999
| 7:35 | 9.4303 | 0.22996
| 7:35 | 9.4306 | 0.22994
| 7:35 | 9.4308 | 0.22992
| 7:35 | 9.4311 | 0.2299
| 7:35 | 9.4314 | 0.2299
| 7:35 | 9.4317 | 0.22989
| 7:35 | 9.4319 | 0.22989
| 7:35 | 9.4322 | 0.22989
| 7:35 | 9.4325 | 0.2299
| 7:35 | 9.4328 | 0.22991
| 7:35 | 9.4331 | 0.22993
| 7:35 | 9.4333 | 0.22994
| 7:35 | 9.4336 | 0.22997
| 7:35 | 9.4339 | 0.22999
| 7:35 | 9.4342 | 0.23002
| 7:35 | 9.4344 | 0.23004
| 7:35 | 9.4347 | 0.23007
| 7:35 | 9.435 | 0.2301
| 7:35 | 9.4353 | 0.23013
| 7:35 | 9.4356 | 0.23017
| 7:35 | 9.4358 | 0.2302
| 7:35 | 9.4361 | 0.23024
| 7:35 | 9.4364 | 0.23027
| 7:35 | 9.4367 | 0.23031
| 7:35 | 9.4369 | 0.23035
| 7:35 | 9.4372 | 0.23038
| 7:35 | 9.4375 | 0.23042
| 7:35 | 9.4378 | 0.23045
| 7:35 | 9.4381 | 0.23048
| 7:35 | 9.4383 | 0.23051
| 7:35 | 9.4386 | 0.23054
| 7:35 | 9.4389 | 0.23057
| 7:35 | 9.4392 | 0.2306
| 7:35 | 9.4394 | 0.23063
| 7:35 | 9.4397 | 0.23066
| 7:35 | 9.44 | 0.23069
| 7:35 | 9.4403 | 0.23071
| 7:35 | 9.4406 | 0.23074
| 7:35 | 9.4408 | 0.23076
| 7:35 | 9.4411 | 0.23078
| 7:35 | 9.4414 | 0.23081
| 7:35 | 9.4417 | 0.23083
| 7:35 | 9.4419 | 0.23085
| 7:35 | 9.4422 | 0.23088
| 7:35 | 9.4425 | 0.2309
| 7:35 | 9.4428 | 0.23093
| 7:35 | 9.4431 | 0.23095
| 7:35 | 9.4433 | 0.23098
| 7:35 | 9.4436 | 0.231
| 7:35 | 9.4439 | 0.23103
| 7:35 | 9.4442 | 0.23106
| 7:35 | 9.4444 | 0.23108
| 7:35 | 9.4447 | 0.23111
| 7:36 | 9.445 | 0.23114
| 7:36 | 9.4453 | 0.23116
| 7:36 | 9.4456 | 0.23119
| 7:36 | 9.4458 | 0.23122
| 7:36 | 9.4461 | 0.23125
| 7:36 | 9.4464 | 0.23128
| 7:36 | 9.4467 | 0.23131
| 7:36 | 9.4469 | 0.23134
| 7:36 | 9.4472 | 0.23136
| 7:36 | 9.4475 | 0.23139
| 7:36 | 9.4478 | 0.23142
| 7:36 | 9.4481 | 0.23146
| 7:36 | 9.4483 | 0.23149
| 7:36 | 9.4486 | 0.23152
| 7:36 | 9.4489 | 0.23155
| 7:36 | 9.4492 | 0.23158
| 7:36 | 9.4494 | 0.23161
| 7:36 | 9.4497 | 0.23164
| 7:36 | 9.45 | 0.23168
| 7:36 | 9.4503 | 0.23171
| 7:36 | 9.4506 | 0.23174
| 7:36 | 9.4508 | 0.23178
| 7:36 | 9.4511 | 0.23181
| 7:36 | 9.4514 | 0.23184
| 7:36 | 9.4517 | 0.23188
| 7:36 | 9.4519 | 0.23191
| 7:36 | 9.4522 | 0.23195
| 7:36 | 9.4525 | 0.23198
| 7:36 | 9.4528 | 0.23202
| 7:36 | 9.4531 | 0.23205
| 7:36 | 9.4533 | 0.23209
| 7:36 | 9.4536 | 0.23213
| 7:36 | 9.4539 | 0.23216
| 7:36 | 9.4542 | 0.2322
| 7:36 | 9.4544 | 0.23224
| 7:36 | 9.4547 | 0.23227
| 7:36 | 9.455 | 0.23231
| 7:36 | 9.4553 | 0.23235
| 7:36 | 9.4556 | 0.23239
| 7:36 | 9.4558 | 0.23243
| 7:36 | 9.4561 | 0.23247
| 7:36 | 9.4564 | 0.23251
| 7:36 | 9.4567 | 0.23255
| 7:36 | 9.4569 | 0.23259
| 7:36 | 9.4572 | 0.23263
| 7:36 | 9.4575 | 0.23267
| 7:36 | 9.4578 | 0.23271
| 7:36 | 9.4581 | 0.23275
| 7:36 | 9.4583 | 0.23279
| 7:36 | 9.4586 | 0.23283
| 7:36 | 9.4589 | 0.23287
| 7:36 | 9.4592 | 0.23292
| 7:36 | 9.4594 | 0.23296
| 7:36 | 9.4597 | 0.233
| 7:36 | 9.46 | 0.23304
| 7:36 | 9.4603 | 0.23309
| 7:36 | 9.4606 | 0.23313
| 7:36 | 9.4608 | 0.23317
| 7:36 | 9.4611 | 0.23322
| 7:36 | 9.4614 | 0.23326
| 7:36 | 9.4617 | 0.2333
| 7:37 | 9.4619 | 0.23335
| 7:37 | 9.4622 | 0.23339
| 7:37 | 9.4625 | 0.23344
| 7:37 | 9.4628 | 0.23348
| 7:37 | 9.4631 | 0.23352
| 7:37 | 9.4633 | 0.23357
| 7:37 | 9.4636 | 0.23361
| 7:37 | 9.4639 | 0.23365
| 7:37 | 9.4642 | 0.2337
| 7:37 | 9.4644 | 0.23374
| 7:37 | 9.4647 | 0.23378
| 7:37 | 9.465 | 0.23383
| 7:37 | 9.4653 | 0.23387
| 7:37 | 9.4656 | 0.23391
| 7:37 | 9.4658 | 0.23396
| 7:37 | 9.4661 | 0.234
| 7:37 | 9.4664 | 0.23404
| 7:37 | 9.4667 | 0.23409
| 7:37 | 9.4669 | 0.23413
| 7:37 | 9.4672 | 0.23417
| 7:37 | 9.4675 | 0.23422
| 7:37 | 9.4678 | 0.23426
| 7:37 | 9.4681 | 0.2343
| 7:37 | 9.4683 | 0.23435
| 7:37 | 9.4686 | 0.23439
| 7:37 | 9.4689 | 0.23444
| 7:37 | 9.4692 | 0.23448
| 7:37 | 9.4694 | 0.23452
| 7:37 | 9.4697 | 0.23457
| 7:37 | 9.47 | 0.23461
| 7:37 | 9.4703 | 0.23465
| 7:37 | 9.4706 | 0.2347
| 7:37 | 9.4708 | 0.23474
| 7:37 | 9.4711 | 0.23478
| 7:37 | 9.4714 | 0.23483
| 7:37 | 9.4717 | 0.23487
| 7:37 | 9.4719 | 0.23491
| 7:37 | 9.4722 | 0.23496
| 7:37 | 9.4725 | 0.235
| 7:37 | 9.4728 | 0.23505
| 7:37 | 9.4731 | 0.23509
| 7:37 | 9.4733 | 0.23513
| 7:37 | 9.4736 | 0.23518
| 7:37 | 9.4739 | 0.23522
| 7:37 | 9.4742 | 0.23526
| 7:37 | 9.4744 | 0.23531
| 7:37 | 9.4747 | 0.23535
| 7:37 | 9.475 | 0.23539
| 7:37 | 9.4753 | 0.23544
| 7:37 | 9.4756 | 0.23548
| 7:37 | 9.4758 | 0.23553
| 7:37 | 9.4761 | 0.23557
| 7:37 | 9.4764 | 0.23561
| 7:37 | 9.4767 | 0.23566
| 7:37 | 9.4769 | 0.2357
| 7:37 | 9.4772 | 0.23574
| 7:37 | 9.4775 | 0.23579
| 7:37 | 9.4778 | 0.23583
| 7:37 | 9.4781 | 0.23588
| 7:38 | 9.4783 | 0.23592
| 7:38 | 9.4786 | 0.23596
| 7:38 | 9.4789 | 0.23601
| 7:38 | 9.4792 | 0.23605
| 7:38 | 9.4794 | 0.23609
| 7:38 | 9.4797 | 0.23614
| 7:38 | 9.48 | 0.23618
| 7:38 | 9.4803 | 0.23623
| 7:38 | 9.4806 | 0.23627
| 7:38 | 9.4808 | 0.23631
| 7:38 | 9.4811 | 0.23636
| 7:38 | 9.4814 | 0.2364
| 7:38 | 9.4817 | 0.23644
| 7:38 | 9.4819 | 0.23649
| 7:38 | 9.4822 | 0.23653
| 7:38 | 9.4825 | 0.23658
| 7:38 | 9.4828 | 0.23662
| 7:38 | 9.4831 | 0.23666
| 7:38 | 9.4833 | 0.23671
| 7:38 | 9.4836 | 0.23675
| 7:38 | 9.4839 | 0.23679
| 7:38 | 9.4842 | 0.23684
| 7:38 | 9.4844 | 0.23688
| 7:38 | 9.4847 | 0.23693
| 7:38 | 9.485 | 0.23697
| 7:38 | 9.4853 | 0.23701
| 7:38 | 9.4856 | 0.23706
| 7:38 | 9.4858 | 0.2371
| 7:38 | 9.4861 | 0.23715
| 7:38 | 9.4864 | 0.23719
| 7:38 | 9.4867 | 0.23723
| 7:38 | 9.4869 | 0.23728
| 7:38 | 9.4872 | 0.23732
| 7:38 | 9.4875 | 0.23736
| 7:38 | 9.4878 | 0.23741
| 7:38 | 9.4881 | 0.23745
| 7:38 | 9.4883 | 0.2375
| 7:38 | 9.4886 | 0.23754
| 7:38 | 9.4889 | 0.23758
| 7:38 | 9.4892 | 0.23763
| 7:38 | 9.4894 | 0.23767
| 7:38 | 9.4897 | 0.23771
| 7:38 | 9.49 | 0.23776
| 7:38 | 9.4903 | 0.2378
| 7:38 | 9.4906 | 0.23784
| 7:38 | 9.4908 | 0.23789
| 7:38 | 9.4911 | 0.23793
| 7:38 | 9.4914 | 0.23797
| 7:38 | 9.4917 | 0.23801
| 7:38 | 9.4919 | 0.23806
| 7:38 | 9.4922 | 0.2381
| 7:38 | 9.4925 | 0.23814
| 7:38 | 9.4928 | 0.23819
| 7:38 | 9.4931 | 0.23823
| 7:38 | 9.4933 | 0.23827
| 7:38 | 9.4936 | 0.23831
| 7:38 | 9.4939 | 0.23836
| 7:38 | 9.4942 | 0.2384
| 7:38 | 9.4944 | 0.23844
| 7:38 | 9.4947 | 0.23848
| 7:38 | 9.495 | 0.23853
| 7:39 | 9.4953 | 0.23857
| 7:39 | 9.4956 | 0.23861
| 7:39 | 9.4958 | 0.23865
| 7:39 | 9.4961 | 0.2387
| 7:39 | 9.4964 | 0.23874
| 7:39 | 9.4967 | 0.23878
| 7:39 | 9.4969 | 0.23882
| 7:39 | 9.4972 | 0.23886
| 7:39 | 9.4975 | 0.2389
| 7:39 | 9.4978 | 0.23895
| 7:39 | 9.4981 | 0.23899
| 7:39 | 9.4983 | 0.23903
| 7:39 | 9.4986 | 0.23907
| 7:39 | 9.4989 | 0.23911
| 7:39 | 9.4992 | 0.23915
| 7:39 | 9.4994 | 0.2392
| 7:39 | 9.4997 | 0.23924
| 7:39 | 9.5 | 0.23928
| 7:39 | 9.5003 | 0.23932
| 7:39 | 9.5006 | 0.23936
| 7:39 | 9.5008 | 0.2394
| 7:39 | 9.5011 | 0.23944
| 7:39 | 9.5014 | 0.23949
| 7:39 | 9.5017 | 0.23953
| 7:39 | 9.5019 | 0.23957
| 7:39 | 9.5022 | 0.23961
| 7:39 | 9.5025 | 0.23965
| 7:39 | 9.5028 | 0.23969
| 7:39 | 9.5031 | 0.23973
| 7:39 | 9.5033 | 0.23977
| 7:39 | 9.5036 | 0.23981
| 7:39 | 9.5039 | 0.23985
| 7:39 | 9.5042 | 0.23989
| 7:39 | 9.5044 | 0.23993
| 7:39 | 9.5047 | 0.23997
| 7:39 | 9.505 | 0.24001
| 7:39 | 9.5053 | 0.24005
| 7:39 | 9.5056 | 0.2401
| 7:39 | 9.5058 | 0.24014
| 7:39 | 9.5061 | 0.24018
| 7:39 | 9.5064 | 0.24022
| 7:39 | 9.5067 | 0.24026
| 7:39 | 9.5069 | 0.2403
| 7:39 | 9.5072 | 0.24034
| 7:39 | 9.5075 | 0.24038
| 7:39 | 9.5078 | 0.24042
| 7:39 | 9.5081 | 0.24046
| 7:39 | 9.5083 | 0.2405
| 7:39 | 9.5086 | 0.24054
| 7:39 | 9.5089 | 0.24057
| 7:39 | 9.5092 | 0.24061
| 7:39 | 9.5094 | 0.24065
| 7:39 | 9.5097 | 0.24069
| 7:39 | 9.51 | 0.24073
| 7:39 | 9.5103 | 0.24077
| 7:39 | 9.5106 | 0.24081
| 7:39 | 9.5108 | 0.24085
| 7:39 | 9.5111 | 0.24089
| 7:39 | 9.5114 | 0.24093
| 7:39 | 9.5117 | 0.24097
| 7:40 | 9.5119 | 0.24101
| 7:40 | 9.5122 | 0.24105
| 7:40 | 9.5125 | 0.24109
| 7:40 | 9.5128 | 0.24112
| 7:40 | 9.5131 | 0.24116
| 7:40 | 9.5133 | 0.2412
| 7:40 | 9.5136 | 0.24124
| 7:40 | 9.5139 | 0.24128
| 7:40 | 9.5142 | 0.24132
| 7:40 | 9.5144 | 0.24136
| 7:40 | 9.5147 | 0.2414
| 7:40 | 9.515 | 0.24143
| 7:40 | 9.5153 | 0.24147
| 7:40 | 9.5156 | 0.24151
| 7:40 | 9.5158 | 0.24155
| 7:40 | 9.5161 | 0.24159
| 7:40 | 9.5164 | 0.24163
| 7:40 | 9.5167 | 0.24166
| 7:40 | 9.5169 | 0.2417
| 7:40 | 9.5172 | 0.24174
| 7:40 | 9.5175 | 0.24178
| 7:40 | 9.5178 | 0.24182
| 7:40 | 9.5181 | 0.24185
| 7:40 | 9.5183 | 0.24189
| 7:40 | 9.5186 | 0.24193
| 7:40 | 9.5189 | 0.24197
| 7:40 | 9.5192 | 0.24201
| 7:40 | 9.5194 | 0.24204
| 7:40 | 9.5197 | 0.24208
| 7:40 | 9.52 | 0.24212
| 7:40 | 9.5203 | 0.24216
| 7:40 | 9.5206 | 0.24219
| 7:40 | 9.5208 | 0.24223
| 7:40 | 9.5211 | 0.24227
| 7:40 | 9.5214 | 0.2423
| 7:40 | 9.5217 | 0.24234
| 7:40 | 9.5219 | 0.24238
| 7:40 | 9.5222 | 0.24242
| 7:40 | 9.5225 | 0.24245
| 7:40 | 9.5228 | 0.24249
| 7:40 | 9.5231 | 0.24253
| 7:40 | 9.5233 | 0.24256
| 7:40 | 9.5236 | 0.2426
| 7:40 | 9.5239 | 0.24264
| 7:40 | 9.5242 | 0.24267
| 7:40 | 9.5244 | 0.24271
| 7:40 | 9.5247 | 0.24275
| 7:40 | 9.525 | 0.24278
| 7:40 | 9.5253 | 0.24282
| 7:40 | 9.5256 | 0.24286
| 7:40 | 9.5258 | 0.24289
| 7:40 | 9.5261 | 0.24293
| 7:40 | 9.5264 | 0.24297
| 7:40 | 9.5267 | 0.243
| 7:40 | 9.5269 | 0.24304
| 7:40 | 9.5272 | 0.24308
| 7:40 | 9.5275 | 0.24311
| 7:40 | 9.5278 | 0.24315
| 7:40 | 9.5281 | 0.24318
| 7:40 | 9.5283 | 0.24322
| 7:41 | 9.5286 | 0.24325
| 7:41 | 9.5289 | 0.24328
| 7:41 | 9.5292 | 0.24331
| 7:41 | 9.5294 | 0.24333
| 7:41 | 9.5297 | 0.24336
| 7:41 | 9.53 | 0.24337
| 7:41 | 9.5303 | 0.24336
| 7:41 | 9.5306 | 0.24334
| 7:41 | 9.5308 | 0.24332
| 7:41 | 9.5311 | 0.24329
| 7:41 | 9.5314 | 0.24324
| 7:41 | 9.5317 | 0.24318
| 7:41 | 9.5319 | 0.24311
| 7:41 | 9.5322 | 0.24302
| 7:41 | 9.5325 | 0.24292
| 7:41 | 9.5328 | 0.24281
| 7:41 | 9.5331 | 0.24269
| 7:41 | 9.5333 | 0.24255
| 7:41 | 9.5336 | 0.2424
| 7:41 | 9.5339 | 0.24224
| 7:41 | 9.5342 | 0.24206
| 7:41 | 9.5344 | 0.24188
| 7:41 | 9.5347 | 0.24169
| 7:41 | 9.535 | 0.2415
| 7:41 | 9.5353 | 0.24131
| 7:41 | 9.5356 | 0.2411
| 7:41 | 9.5358 | 0.24086
| 7:41 | 9.5361 | 0.24058
| 7:41 | 9.5364 | 0.24028
| 7:41 | 9.5367 | 0.23995
| 7:41 | 9.5369 | 0.23962
| 7:41 | 9.5372 | 0.23928
| 7:41 | 9.5375 | 0.23893
| 7:41 | 9.5378 | 0.23858
| 7:41 | 9.5381 | 0.23823
| 7:41 | 9.5383 | 0.23788
| 7:41 | 9.5386 | 0.23753
| 7:41 | 9.5389 | 0.23717
| 7:41 | 9.5392 | 0.23682
| 7:41 | 9.5394 | 0.23647
| 7:41 | 9.5397 | 0.23613
| 7:41 | 9.54 | 0.23579
| 7:41 | 9.5403 | 0.23545
| 7:41 | 9.5406 | 0.23513
| 7:41 | 9.5408 | 0.2348
| 7:41 | 9.5411 | 0.23449
| 7:41 | 9.5414 | 0.23418
| 7:41 | 9.5417 | 0.23387
| 7:41 | 9.5419 | 0.23359
| 7:41 | 9.5422 | 0.23333
| 7:41 | 9.5425 | 0.23309
| 7:41 | 9.5428 | 0.23286
| 7:41 | 9.5431 | 0.23264
| 7:41 | 9.5433 | 0.23241
| 7:41 | 9.5436 | 0.23219
| 7:41 | 9.5439 | 0.23196
| 7:41 | 9.5442 | 0.23173
| 7:41 | 9.5444 | 0.2315
| 7:41 | 9.5447 | 0.23127
| 7:42 | 9.545 | 0.23103
| 7:42 | 9.5453 | 0.2308
| 7:42 | 9.5456 | 0.23056
| 7:42 | 9.5458 | 0.23031
| 7:42 | 9.5461 | 0.23007
| 7:42 | 9.5464 | 0.22982
| 7:42 | 9.5467 | 0.22957
| 7:42 | 9.5469 | 0.22932
| 7:42 | 9.5472 | 0.22905
| 7:42 | 9.5475 | 0.22877
| 7:42 | 9.5478 | 0.2285
| 7:42 | 9.5481 | 0.22824
| 7:42 | 9.5483 | 0.22799
| 7:42 | 9.5486 | 0.22775
| 7:42 | 9.5489 | 0.22752
| 7:42 | 9.5492 | 0.22729
| 7:42 | 9.5494 | 0.22708
| 7:42 | 9.5497 | 0.22688
| 7:42 | 9.55 | 0.22669
| 7:42 | 9.5503 | 0.22651
| 7:42 | 9.5506 | 0.22632
| 7:42 | 9.5508 | 0.22613
| 7:42 | 9.5511 | 0.22594
| 7:42 | 9.5514 | 0.22574
| 7:42 | 9.5517 | 0.22554
| 7:42 | 9.5519 | 0.22534
| 7:42 | 9.5522 | 0.22514
| 7:42 | 9.5525 | 0.22495
| 7:42 | 9.5528 | 0.22476
| 7:42 | 9.5531 | 0.22457
| 7:42 | 9.5533 | 0.22439
| 7:42 | 9.5536 | 0.22421
| 7:42 | 9.5539 | 0.22403
| 7:42 | 9.5542 | 0.22384
| 7:42 | 9.5544 | 0.22365
| 7:42 | 9.5547 | 0.22346
| 7:42 | 9.555 | 0.22325
| 7:42 | 9.5553 | 0.22302
| 7:42 | 9.5556 | 0.22276
| 7:42 | 9.5558 | 0.22251
| 7:42 | 9.5561 | 0.22225
| 7:42 | 9.5564 | 0.222
| 7:42 | 9.5567 | 0.22175
| 7:42 | 9.5569 | 0.22151
| 7:42 | 9.5572 | 0.22128
| 7:42 | 9.5575 | 0.22105
| 7:42 | 9.5578 | 0.22083
| 7:42 | 9.5581 | 0.22061
| 7:42 | 9.5583 | 0.22037
| 7:42 | 9.5586 | 0.22012
| 7:42 | 9.5589 | 0.21984
| 7:42 | 9.5592 | 0.21957
| 7:42 | 9.5594 | 0.2193
| 7:42 | 9.5597 | 0.21904
| 7:42 | 9.56 | 0.21877
| 7:42 | 9.5603 | 0.2185
| 7:42 | 9.5606 | 0.21826
| 7:42 | 9.5608 | 0.21803
| 7:42 | 9.5611 | 0.21782
| 7:42 | 9.5614 | 0.21763
| 7:43 | 9.5617 | 0.21747
| 7:43 | 9.5619 | 0.21733
| 7:43 | 9.5622 | 0.21719
| 7:43 | 9.5625 | 0.21706
| 7:43 | 9.5628 | 0.21694
| 7:43 | 9.5631 | 0.21681
| 7:43 | 9.5633 | 0.21671
| 7:43 | 9.5636 | 0.21659
| 7:43 | 9.5639 | 0.21647
| 7:43 | 9.5642 | 0.21632
| 7:43 | 9.5644 | 0.21615
| 7:43 | 9.5647 | 0.21597
| 7:43 | 9.565 | 0.21577
| 7:43 | 9.5653 | 0.21556
| 7:43 | 9.5656 | 0.21533
| 7:43 | 9.5658 | 0.21509
| 7:43 | 9.5661 | 0.21483
| 7:43 | 9.5664 | 0.21456
| 7:43 | 9.5667 | 0.21427
| 7:43 | 9.5669 | 0.21396
| 7:43 | 9.5672 | 0.21365
| 7:43 | 9.5675 | 0.21334
| 7:43 | 9.5678 | 0.21301
| 7:43 | 9.5681 | 0.21269
| 7:43 | 9.5683 | 0.21237
| 7:43 | 9.5686 | 0.21204
| 7:43 | 9.5689 | 0.21171
| 7:43 | 9.5692 | 0.21138
| 7:43 | 9.5694 | 0.21105
| 7:43 | 9.5697 | 0.2107
| 7:43 | 9.57 | 0.21034
| 7:43 | 9.5703 | 0.20998
| 7:43 | 9.5706 | 0.20961
| 7:43 | 9.5708 | 0.20924
| 7:43 | 9.5711 | 0.20886
| 7:43 | 9.5714 | 0.20847
| 7:43 | 9.5717 | 0.20808
| 7:43 | 9.5719 | 0.20768
| 7:43 | 9.5722 | 0.20726
| 7:43 | 9.5725 | 0.20683
| 7:43 | 9.5728 | 0.2064
| 7:43 | 9.5731 | 0.20596
| 7:43 | 9.5733 | 0.20551
| 7:43 | 9.5736 | 0.20505
| 7:43 | 9.5739 | 0.20459
| 7:43 | 9.5742 | 0.20412
| 7:43 | 9.5744 | 0.20364
| 7:43 | 9.5747 | 0.20316
| 7:43 | 9.575 | 0.20268
| 7:43 | 9.5753 | 0.20221
| 7:43 | 9.5756 | 0.20173
| 7:43 | 9.5758 | 0.20125
| 7:43 | 9.5761 | 0.20078
| 7:43 | 9.5764 | 0.2003
| 7:43 | 9.5767 | 0.19982
| 7:43 | 9.5769 | 0.19934
| 7:43 | 9.5772 | 0.19887
| 7:43 | 9.5775 | 0.19839
| 7:43 | 9.5778 | 0.19791
| 7:43 | 9.5781 | 0.19743
| 7:44 | 9.5783 | 0.19696
| 7:44 | 9.5786 | 0.19648
| 7:44 | 9.5789 | 0.196
| 7:44 | 9.5792 | 0.19552
| 7:44 | 9.5794 | 0.19505
| 7:44 | 9.5797 | 0.19457
| 7:44 | 9.58 | 0.19409
| 7:44 | 9.5803 | 0.19361
| 7:44 | 9.5806 | 0.19314
| 7:44 | 9.5808 | 0.19266
| 7:44 | 9.5811 | 0.19218
| 7:44 | 9.5814 | 0.19169
| 7:44 | 9.5817 | 0.1912
| 7:44 | 9.5819 | 0.19071
| 7:44 | 9.5822 | 0.19022
| 7:44 | 9.5825 | 0.18972
| 7:44 | 9.5828 | 0.18922
| 7:44 | 9.5831 | 0.18872
| 7:44 | 9.5833 | 0.18822
| 7:44 | 9.5836 | 0.18771
| 7:44 | 9.5839 | 0.1872
| 7:44 | 9.5842 | 0.18669
| 7:44 | 9.5844 | 0.18617
| 7:44 | 9.5847 | 0.18565
| 7:44 | 9.585 | 0.18513
| 7:44 | 9.5853 | 0.18461
| 7:44 | 9.5856 | 0.18408
| 7:44 | 9.5858 | 0.18356
| 7:44 | 9.5861 | 0.18304
| 7:44 | 9.5864 | 0.18251
| 7:44 | 9.5867 | 0.18198
| 7:44 | 9.5869 | 0.18146
| 7:44 | 9.5872 | 0.18093
| 7:44 | 9.5875 | 0.1804
| 7:44 | 9.5878 | 0.17987
| 7:44 | 9.5881 | 0.17935
| 7:44 | 9.5883 | 0.17882
| 7:44 | 9.5886 | 0.17828
| 7:44 | 9.5889 | 0.17775
| 7:44 | 9.5892 | 0.17722
| 7:44 | 9.5894 | 0.17669
| 7:44 | 9.5897 | 0.17616
| 7:44 | 9.59 | 0.17562
| 7:44 | 9.5903 | 0.17509
| 7:44 | 9.5906 | 0.17455
| 7:44 | 9.5908 | 0.17401
| 7:44 | 9.5911 | 0.17348
| 7:44 | 9.5914 | 0.17294
| 7:44 | 9.5917 | 0.17241
| 7:44 | 9.5919 | 0.17188
| 7:44 | 9.5922 | 0.17135
| 7:44 | 9.5925 | 0.17082
| 7:44 | 9.5928 | 0.17029
| 7:44 | 9.5931 | 0.16977
| 7:44 | 9.5933 | 0.16925
| 7:44 | 9.5936 | 0.16872
| 7:44 | 9.5939 | 0.1682
| 7:44 | 9.5942 | 0.16768
| 7:44 | 9.5944 | 0.16716
| 7:44 | 9.5947 | 0.16663
| 7:44 | 9.595 | 0.16611
| 7:45 | 9.5953 | 0.16559
| 7:45 | 9.5956 | 0.16506
| 7:45 | 9.5958 | 0.16454
| 7:45 | 9.5961 | 0.16401
| 7:45 | 9.5964 | 0.16349
| 7:45 | 9.5967 | 0.16296
| 7:45 | 9.5969 | 0.16243
| 7:45 | 9.5972 | 0.16191
| 7:45 | 9.5975 | 0.16138
| 7:45 | 9.5978 | 0.16086
| 7:45 | 9.5981 | 0.16034
| 7:45 | 9.5983 | 0.15983
| 7:45 | 9.5986 | 0.15933
| 7:45 | 9.5989 | 0.15883
| 7:45 | 9.5992 | 0.15834
| 7:45 | 9.5994 | 0.15785
| 7:45 | 9.5997 | 0.15737
| 7:45 | 9.6 | 0.15689
| 7:45 | 9.6003 | 0.15641
| 7:45 | 9.6006 | 0.15593
| 7:45 | 9.6008 | 0.15546
| 7:45 | 9.6011 | 0.15499
| 7:45 | 9.6014 | 0.15451
| 7:45 | 9.6017 | 0.15404
| 7:45 | 9.6019 | 0.15357
| 7:45 | 9.6022 | 0.1531
| 7:45 | 9.6025 | 0.15263
| 7:45 | 9.6028 | 0.15217
| 7:45 | 9.6031 | 0.15172
| 7:45 | 9.6033 | 0.15128
| 7:45 | 9.6036 | 0.15086
| 7:45 | 9.6039 | 0.15046
| 7:45 | 9.6042 | 0.15007
| 7:45 | 9.6044 | 0.14969
| 7:45 | 9.6047 | 0.14932
| 7:45 | 9.605 | 0.14895
| 7:45 | 9.6053 | 0.14859
| 7:45 | 9.6056 | 0.14823
| 7:45 | 9.6058 | 0.14788
| 7:45 | 9.6061 | 0.14754
| 7:45 | 9.6064 | 0.1472
| 7:45 | 9.6067 | 0.14688
| 7:45 | 9.6069 | 0.14656
| 7:45 | 9.6072 | 0.14626
| 7:45 | 9.6075 | 0.14596
| 7:45 | 9.6078 | 0.14567
| 7:45 | 9.6081 | 0.14539
| 7:45 | 9.6083 | 0.1451
| 7:45 | 9.6086 | 0.14482
| 7:45 | 9.6089 | 0.14453
| 7:45 | 9.6092 | 0.14423
| 7:45 | 9.6094 | 0.14393
| 7:45 | 9.6097 | 0.14362
| 7:45 | 9.61 | 0.14329
| 7:45 | 9.6103 | 0.14294
| 7:45 | 9.6106 | 0.14258
| 7:45 | 9.6108 | 0.14222
| 7:45 | 9.6111 | 0.14185
| 7:45 | 9.6114 | 0.14148
| 7:46 | 9.6117 | 0.1411
| 7:46 | 9.6119 | 0.14072
| 7:46 | 9.6122 | 0.14035
| 7:46 | 9.6125 | 0.13997
| 7:46 | 9.6128 | 0.13959
| 7:46 | 9.6131 | 0.13922
| 7:46 | 9.6133 | 0.13884
| 7:46 | 9.6136 | 0.13846
| 7:46 | 9.6139 | 0.13809
| 7:46 | 9.6142 | 0.13771
| 7:46 | 9.6144 | 0.13734
| 7:46 | 9.6147 | 0.13698
| 7:46 | 9.615 | 0.13663
| 7:46 | 9.6153 | 0.13628
| 7:46 | 9.6156 | 0.13594
| 7:46 | 9.6158 | 0.13561
| 7:46 | 9.6161 | 0.13529
| 7:46 | 9.6164 | 0.13498
| 7:46 | 9.6167 | 0.13468
| 7:46 | 9.6169 | 0.13442
| 7:46 | 9.6172 | 0.13416
| 7:46 | 9.6175 | 0.13396
| 7:46 | 9.6178 | 0.13382
| 7:46 | 9.6181 | 0.13374
| 7:46 | 9.6183 | 0.13369
| 7:46 | 9.6186 | 0.13368
| 7:46 | 9.6189 | 0.13372
| 7:46 | 9.6192 | 0.13383
| 7:46 | 9.6194 | 0.13399
| 7:46 | 9.6197 | 0.13418
| 7:46 | 9.62 | 0.1344
| 7:46 | 9.6203 | 0.13461
| 7:46 | 9.6206 | 0.13481
| 7:46 | 9.6208 | 0.13501
| 7:46 | 9.6211 | 0.13521
| 7:46 | 9.6214 | 0.1354
| 7:46 | 9.6217 | 0.1356
| 7:46 | 9.6219 | 0.1358
| 7:46 | 9.6222 | 0.13602
| 7:46 | 9.6225 | 0.13623
| 7:46 | 9.6228 | 0.13645
| 7:46 | 9.6231 | 0.13665
| 7:46 | 9.6233 | 0.13685
| 7:46 | 9.6236 | 0.13705
| 7:46 | 9.6239 | 0.13724
| 7:46 | 9.6242 | 0.13742
| 7:46 | 9.6244 | 0.1376
| 7:46 | 9.6247 | 0.13778
| 7:46 | 9.625 | 0.13794
| 7:46 | 9.6253 | 0.1381
| 7:46 | 9.6256 | 0.13826
| 7:46 | 9.6258 | 0.13842
| 7:46 | 9.6261 | 0.13858
| 7:46 | 9.6264 | 0.13874
| 7:46 | 9.6267 | 0.1389
| 7:46 | 9.6269 | 0.13905
| 7:46 | 9.6272 | 0.13921
| 7:46 | 9.6275 | 0.13937
| 7:46 | 9.6278 | 0.13952
| 7:46 | 9.6281 | 0.13968
| 7:46 | 9.6283 | 0.13984
| 7:47 | 9.6286 | 0.14002
| 7:47 | 9.6289 | 0.1402
| 7:47 | 9.6292 | 0.14038
| 7:47 | 9.6294 | 0.14057
| 7:47 | 9.6297 | 0.14075
| 7:47 | 9.63 | 0.14093
| 7:47 | 9.6303 | 0.14111
| 7:47 | 9.6306 | 0.1413
| 7:47 | 9.6308 | 0.14149
| 7:47 | 9.6311 | 0.14167
| 7:47 | 9.6314 | 0.14186
| 7:47 | 9.6317 | 0.14205
| 7:47 | 9.6319 | 0.14223
| 7:47 | 9.6322 | 0.14242
| 7:47 | 9.6325 | 0.1426
| 7:47 | 9.6328 | 0.14278
| 7:47 | 9.6331 | 0.14296
| 7:47 | 9.6333 | 0.14314
| 7:47 | 9.6336 | 0.14332
| 7:47 | 9.6339 | 0.14349
| 7:47 | 9.6342 | 0.14367
| 7:47 | 9.6344 | 0.14384
| 7:47 | 9.6347 | 0.14402
| 7:47 | 9.635 | 0.14419
| 7:47 | 9.6353 | 0.14435
| 7:47 | 9.6356 | 0.14451
| 7:47 | 9.6358 | 0.14466
| 7:47 | 9.6361 | 0.14481
| 7:47 | 9.6364 | 0.14496
| 7:47 | 9.6367 | 0.14509
| 7:47 | 9.6369 | 0.14523
| 7:47 | 9.6372 | 0.14535
| 7:47 | 9.6375 | 0.14544
| 7:47 | 9.6378 | 0.1455
| 7:47 | 9.6381 | 0.14555
| 7:47 | 9.6383 | 0.14559
| 7:47 | 9.6386 | 0.14562
| 7:47 | 9.6389 | 0.14565
| 7:47 | 9.6392 | 0.14566
| 7:47 | 9.6394 | 0.14567
| 7:47 | 9.6397 | 0.14569
| 7:47 | 9.64 | 0.14572
| 7:47 | 9.6403 | 0.14575
| 7:47 | 9.6406 | 0.1458
| 7:47 | 9.6408 | 0.14585
| 7:47 | 9.6411 | 0.14591
| 7:47 | 9.6414 | 0.14597
| 7:47 | 9.6417 | 0.14603
| 7:47 | 9.6419 | 0.14609
| 7:47 | 9.6422 | 0.14614
| 7:47 | 9.6425 | 0.14619
| 7:47 | 9.6428 | 0.14624
| 7:47 | 9.6431 | 0.14628
| 7:47 | 9.6433 | 0.14632
| 7:47 | 9.6436 | 0.14636
| 7:47 | 9.6439 | 0.14634
| 7:47 | 9.6442 | 0.14632
| 7:47 | 9.6444 | 0.14627
| 7:47 | 9.6447 | 0.14621
| 7:48 | 9.645 | 0.14614
| 7:48 | 9.6453 | 0.14605
| 7:48 | 9.6456 | 0.14594
| 7:48 | 9.6458 | 0.14583
| 7:48 | 9.6461 | 0.14569
| 7:48 | 9.6464 | 0.14555
| 7:48 | 9.6467 | 0.1454
| 7:48 | 9.6469 | 0.14524
| 7:48 | 9.6472 | 0.14507
| 7:48 | 9.6475 | 0.14489
| 7:48 | 9.6478 | 0.14471
| 7:48 | 9.6481 | 0.14452
| 7:48 | 9.6483 | 0.14433
| 7:48 | 9.6486 | 0.14413
| 7:48 | 9.6489 | 0.14393
| 7:48 | 9.6492 | 0.14373
| 7:48 | 9.6494 | 0.14352
| 7:48 | 9.6497 | 0.1433
| 7:48 | 9.65 | 0.14308
| 7:48 | 9.6503 | 0.14285
| 7:48 | 9.6506 | 0.14262
| 7:48 | 9.6508 | 0.14238
| 7:48 | 9.6511 | 0.14214
| 7:48 | 9.6514 | 0.14189
| 7:48 | 9.6517 | 0.14164
| 7:48 | 9.6519 | 0.14139
| 7:48 | 9.6522 | 0.14114
| 7:48 | 9.6525 | 0.14088
| 7:48 | 9.6528 | 0.14062
| 7:48 | 9.6531 | 0.14036
| 7:48 | 9.6533 | 0.1401
| 7:48 | 9.6536 | 0.13984
| 7:48 | 9.6539 | 0.13959
| 7:48 | 9.6542 | 0.13934
| 7:48 | 9.6544 | 0.13909
| 7:48 | 9.6547 | 0.13886
| 7:48 | 9.655 | 0.13862
| 7:48 | 9.6553 | 0.13838
| 7:48 | 9.6556 | 0.13815
| 7:48 | 9.6558 | 0.13791
| 7:48 | 9.6561 | 0.13767
| 7:48 | 9.6564 | 0.13744
| 7:48 | 9.6567 | 0.1372
| 7:48 | 9.6569 | 0.13696
| 7:48 | 9.6572 | 0.13673
| 7:48 | 9.6575 | 0.13649
| 7:48 | 9.6578 | 0.13625
| 7:48 | 9.6581 | 0.13601
| 7:48 | 9.6583 | 0.13577
| 7:48 | 9.6586 | 0.13554
| 7:48 | 9.6589 | 0.1353
| 7:48 | 9.6592 | 0.13505
| 7:48 | 9.6594 | 0.13481
| 7:48 | 9.6597 | 0.13458
| 7:48 | 9.66 | 0.13434
| 7:48 | 9.6603 | 0.1341
| 7:48 | 9.6606 | 0.13387
| 7:48 | 9.6608 | 0.13368
| 7:48 | 9.6611 | 0.13353
| 7:48 | 9.6614 | 0.13339
| 7:48 | 9.6617 | 0.13327
| 7:49 | 9.6619 | 0.13315
| 7:49 | 9.6622 | 0.13305
| 7:49 | 9.6625 | 0.13297
| 7:49 | 9.6628 | 0.1329
| 7:49 | 9.6631 | 0.13285
| 7:49 | 9.6633 | 0.13283
| 7:49 | 9.6636 | 0.13282
| 7:49 | 9.6639 | 0.13289
| 7:49 | 9.6642 | 0.133
| 7:49 | 9.6644 | 0.13314
| 7:49 | 9.6647 | 0.13332
| 7:49 | 9.665 | 0.13352
| 7:49 | 9.6653 | 0.13377
| 7:49 | 9.6656 | 0.13404
| 7:49 | 9.6658 | 0.13435
| 7:49 | 9.6661 | 0.1347
| 7:49 | 9.6664 | 0.13507
| 7:49 | 9.6667 | 0.13547
| 7:49 | 9.6669 | 0.13588
| 7:49 | 9.6672 | 0.13628
| 7:49 | 9.6675 | 0.13666
| 7:49 | 9.6678 | 0.13704
| 7:49 | 9.6681 | 0.13739
| 7:49 | 9.6683 | 0.13773
| 7:49 | 9.6686 | 0.13804
| 7:49 | 9.6689 | 0.13834
| 7:49 | 9.6692 | 0.13863
| 7:49 | 9.6694 | 0.13887
| 7:49 | 9.6697 | 0.13909
| 7:49 | 9.67 | 0.13927
| 7:49 | 9.6703 | 0.1394
| 7:49 | 9.6706 | 0.1395
| 7:49 | 9.6708 | 0.13958
| 7:49 | 9.6711 | 0.13965
| 7:49 | 9.6714 | 0.1397
| 7:49 | 9.6717 | 0.13972
| 7:49 | 9.6719 | 0.1397
| 7:49 | 9.6722 | 0.13963
| 7:49 | 9.6725 | 0.13951
| 7:49 | 9.6728 | 0.13938
| 7:49 | 9.6731 | 0.13924
| 7:49 | 9.6733 | 0.13909
| 7:49 | 9.6736 | 0.13892
| 7:49 | 9.6739 | 0.13875
| 7:49 | 9.6742 | 0.13856
| 7:49 | 9.6744 | 0.13836
| 7:49 | 9.6747 | 0.13816
| 7:49 | 9.675 | 0.13795
| 7:49 | 9.6753 | 0.13775
| 7:49 | 9.6756 | 0.13754
| 7:49 | 9.6758 | 0.13732
| 7:49 | 9.6761 | 0.13709
| 7:49 | 9.6764 | 0.13684
| 7:49 | 9.6767 | 0.13658
| 7:49 | 9.6769 | 0.13629
| 7:49 | 9.6772 | 0.136
| 7:49 | 9.6775 | 0.1357
| 7:49 | 9.6778 | 0.1354
| 7:49 | 9.6781 | 0.1351
| 7:50 | 9.6783 | 0.13479
| 7:50 | 9.6786 | 0.13447
| 7:50 | 9.6789 | 0.13414
| 7:50 | 9.6792 | 0.13381
| 7:50 | 9.6794 | 0.13347
| 7:50 | 9.6797 | 0.13311
| 7:50 | 9.68 | 0.13275
| 7:50 | 9.6803 | 0.13237
| 7:50 | 9.6806 | 0.13198
| 7:50 | 9.6808 | 0.13158
| 7:50 | 9.6811 | 0.13118
| 7:50 | 9.6814 | 0.13077
| 7:50 | 9.6817 | 0.13035
| 7:50 | 9.6819 | 0.12992
| 7:50 | 9.6822 | 0.12948
| 7:50 | 9.6825 | 0.12903
| 7:50 | 9.6828 | 0.12858
| 7:50 | 9.6831 | 0.12811
| 7:50 | 9.6833 | 0.12764
| 7:50 | 9.6836 | 0.12716
| 7:50 | 9.6839 | 0.12667
| 7:50 | 9.6842 | 0.12618
| 7:50 | 9.6844 | 0.12569
| 7:50 | 9.6847 | 0.1252
| 7:50 | 9.685 | 0.1247
| 7:50 | 9.6853 | 0.12419
| 7:50 | 9.6856 | 0.12369
| 7:50 | 9.6858 | 0.12318
| 7:50 | 9.6861 | 0.12267
| 7:50 | 9.6864 | 0.12215
| 7:50 | 9.6867 | 0.12164
| 7:50 | 9.6869 | 0.12112
| 7:50 | 9.6872 | 0.12061
| 7:50 | 9.6875 | 0.1201
| 7:50 | 9.6878 | 0.11958
| 7:50 | 9.6881 | 0.11907
| 7:50 | 9.6883 | 0.11855
| 7:50 | 9.6886 | 0.11804
| 7:50 | 9.6889 | 0.11752
| 7:50 | 9.6892 | 0.11701
| 7:50 | 9.6894 | 0.11649
| 7:50 | 9.6897 | 0.11598
| 7:50 | 9.69 | 0.11546
| 7:50 | 9.6903 | 0.11495
| 7:50 | 9.6906 | 0.11443
| 7:50 | 9.6908 | 0.11391
| 7:50 | 9.6911 | 0.1134
| 7:50 | 9.6914 | 0.11288
| 7:50 | 9.6917 | 0.11237
| 7:50 | 9.6919 | 0.11185
| 7:50 | 9.6922 | 0.11133
| 7:50 | 9.6925 | 0.11082
| 7:50 | 9.6928 | 0.1103
| 7:50 | 9.6931 | 0.10979
| 7:50 | 9.6933 | 0.10927
| 7:50 | 9.6936 | 0.10876
| 7:50 | 9.6939 | 0.10824
| 7:50 | 9.6942 | 0.10773
| 7:50 | 9.6944 | 0.10721
| 7:50 | 9.6947 | 0.10669
| 7:50 | 9.695 | 0.10618
| 7:51 | 9.6953 | 0.10567
| 7:51 | 9.6956 | 0.10515
| 7:51 | 9.6958 | 0.10464
| 7:51 | 9.6961 | 0.10412
| 7:51 | 9.6964 | 0.10361
| 7:51 | 9.6967 | 0.10309
| 7:51 | 9.6969 | 0.10258
| 7:51 | 9.6972 | 0.10206
| 7:51 | 9.6975 | 0.10155
| 7:51 | 9.6978 | 0.10104
| 7:51 | 9.6981 | 0.10052
| 7:51 | 9.6983 | 0.10001
| 7:51 | 9.6986 | 0.099496
| 7:51 | 9.6989 | 0.098983
| 7:51 | 9.6992 | 0.09847
| 7:51 | 9.6994 | 0.097956
| 7:51 | 9.6997 | 0.097443
| 7:51 | 9.7 | 0.09693
| 7:51 | 9.7003 | 0.096418
| 7:51 | 9.7006 | 0.095905
| 7:51 | 9.7008 | 0.095392
| 7:51 | 9.7011 | 0.09488
| 7:51 | 9.7014 | 0.094367
| 7:51 | 9.7017 | 0.093855
| 7:51 | 9.7019 | 0.093343
| 7:51 | 9.7022 | 0.092831
| 7:51 | 9.7025 | 0.092319
| 7:51 | 9.7028 | 0.091807
| 7:51 | 9.7031 | 0.091295
| 7:51 | 9.7033 | 0.090783
| 7:51 | 9.7036 | 0.090272
| 7:51 | 9.7039 | 0.08976
| 7:51 | 9.7042 | 0.089249
| 7:51 | 9.7044 | 0.088738
| 7:51 | 9.7047 | 0.088228
| 7:51 | 9.705 | 0.087718
| 7:51 | 9.7053 | 0.087208
| 7:51 | 9.7056 | 0.086699
| 7:51 | 9.7058 | 0.08619
| 7:51 | 9.7061 | 0.085682
| 7:51 | 9.7064 | 0.085174
| 7:51 | 9.7067 | 0.084666
| 7:51 | 9.7069 | 0.084159
| 7:51 | 9.7072 | 0.083652
| 7:51 | 9.7075 | 0.083146
| 7:51 | 9.7078 | 0.08264
| 7:51 | 9.7081 | 0.082135
| 7:51 | 9.7083 | 0.081629
| 7:51 | 9.7086 | 0.081125
| 7:51 | 9.7089 | 0.08062
| 7:51 | 9.7092 | 0.080117
| 7:51 | 9.7094 | 0.079613
| 7:51 | 9.7097 | 0.07911
| 7:51 | 9.71 | 0.078607
| 7:51 | 9.7103 | 0.078105
| 7:51 | 9.7106 | 0.077604
| 7:51 | 9.7108 | 0.077103
| 7:51 | 9.7111 | 0.076603
| 7:51 | 9.7114 | 0.076104
| 7:52 | 9.7117 | 0.075605
| 7:52 | 9.7119 | 0.075107
| 7:52 | 9.7122 | 0.07461
| 7:52 | 9.7125 | 0.074113
| 7:52 | 9.7128 | 0.073618
| 7:52 | 9.7131 | 0.073123
| 7:52 | 9.7133 | 0.072628
| 7:52 | 9.7136 | 0.072134
| 7:52 | 9.7139 | 0.071641
| 7:52 | 9.7142 | 0.071149
| 7:52 | 9.7144 | 0.070658
| 7:52 | 9.7147 | 0.070167
| 7:52 | 9.715 | 0.069676
| 7:52 | 9.7153 | 0.069187
| 7:52 | 9.7156 | 0.068698
| 7:52 | 9.7158 | 0.06821
| 7:52 | 9.7161 | 0.067723
| 7:52 | 9.7164 | 0.067236
| 7:52 | 9.7167 | 0.066751
| 7:52 | 9.7169 | 0.066269
| 7:52 | 9.7172 | 0.065791
| 7:52 | 9.7175 | 0.065317
| 7:52 | 9.7178 | 0.064846
| 7:52 | 9.7181 | 0.064379
| 7:52 | 9.7183 | 0.063916
| 7:52 | 9.7186 | 0.063457
| 7:52 | 9.7189 | 0.063001
| 7:52 | 9.7192 | 0.062549
| 7:52 | 9.7194 | 0.062102
| 7:52 | 9.7197 | 0.06166
| 7:52 | 9.72 | 0.061224
| 7:52 | 9.7203 | 0.060793
| 7:52 | 9.7206 | 0.060367
| 7:52 | 9.7208 | 0.059946
| 7:52 | 9.7211 | 0.059531
| 7:52 | 9.7214 | 0.059121
| 7:52 | 9.7217 | 0.058722
| 7:52 | 9.7219 | 0.058326
| 7:52 | 9.7222 | 0.05793
| 7:52 | 9.7225 | 0.057536
| 7:52 | 9.7228 | 0.057144
| 7:52 | 9.7231 | 0.056754
| 7:52 | 9.7233 | 0.056364
| 7:52 | 9.7236 | 0.055977
| 7:52 | 9.7239 | 0.055591
| 7:52 | 9.7242 | 0.055206
| 7:52 | 9.7244 | 0.054823
| 7:52 | 9.7247 | 0.054441
| 7:52 | 9.725 | 0.05406
| 7:52 | 9.7253 | 0.05368
| 7:52 | 9.7256 | 0.053301
| 7:52 | 9.7258 | 0.052922
| 7:52 | 9.7261 | 0.052544
| 7:52 | 9.7264 | 0.052167
| 7:52 | 9.7267 | 0.051791
| 7:52 | 9.7269 | 0.051415
| 7:52 | 9.7272 | 0.05104
| 7:52 | 9.7275 | 0.050667
| 7:52 | 9.7278 | 0.050293
| 7:52 | 9.7281 | 0.049921
| 7:52 | 9.7283 | 0.04955
| 7:53 | 9.7286 | 0.049179
| 7:53 | 9.7289 | 0.048809
| 7:53 | 9.7292 | 0.04844
| 7:53 | 9.7294 | 0.048071
| 7:53 | 9.7297 | 0.047704
| 7:53 | 9.73 | 0.047337
| 7:53 | 9.7303 | 0.046971
| 7:53 | 9.7306 | 0.046605
| 7:53 | 9.7308 | 0.04624
| 7:53 | 9.7311 | 0.045876
| 7:53 | 9.7314 | 0.045512
| 7:53 | 9.7317 | 0.045149
| 7:53 | 9.7319 | 0.044787
| 7:53 | 9.7322 | 0.044425
| 7:53 | 9.7325 | 0.044065
| 7:53 | 9.7328 | 0.043705
| 7:53 | 9.7331 | 0.043346
| 7:53 | 9.7333 | 0.042987
| 7:53 | 9.7336 | 0.042629
| 7:53 | 9.7339 | 0.042273
| 7:53 | 9.7342 | 0.041916
| 7:53 | 9.7344 | 0.041565
| 7:53 | 9.7347 | 0.04122
| 7:53 | 9.735 | 0.040881
| 7:53 | 9.7353 | 0.040555
| 7:53 | 9.7356 | 0.040243
| 7:53 | 9.7358 | 0.03994
| 7:53 | 9.7361 | 0.039656
| 7:53 | 9.7364 | 0.039391
| 7:53 | 9.7367 | 0.03914
| 7:53 | 9.7369 | 0.038909
| 7:53 | 9.7372 | 0.03869
| 7:53 | 9.7375 | 0.038486
| 7:53 | 9.7378 | 0.038289
| 7:53 | 9.7381 | 0.038094
| 7:53 | 9.7383 | 0.037901
| 7:53 | 9.7386 | 0.037709
| 7:53 | 9.7389 | 0.037519
| 7:53 | 9.7392 | 0.037331
| 7:53 | 9.7394 | 0.037144
| 7:53 | 9.7397 | 0.036958
| 7:53 | 9.74 | 0.036774
| 7:53 | 9.7403 | 0.036592
| 7:53 | 9.7406 | 0.036412
| 7:53 | 9.7408 | 0.036233
| 7:53 | 9.7411 | 0.036055
| 7:53 | 9.7414 | 0.035879
| 7:53 | 9.7417 | 0.035704
| 7:53 | 9.7419 | 0.035527
| 7:53 | 9.7422 | 0.035349
| 7:53 | 9.7425 | 0.03517
| 7:53 | 9.7428 | 0.03499
| 7:53 | 9.7431 | 0.034809
| 7:53 | 9.7433 | 0.034605
| 7:53 | 9.7436 | 0.034381
| 7:53 | 9.7439 | 0.034148
| 7:53 | 9.7442 | 0.033908
| 7:53 | 9.7444 | 0.033659
| 7:53 | 9.7447 | 0.033393
| 7:54 | 9.745 | 0.033129
| 7:54 | 9.7453 | 0.032866
| 7:54 | 9.7456 | 0.032605
| 7:54 | 9.7458 | 0.032345
| 7:54 | 9.7461 | 0.032097
| 7:54 | 9.7464 | 0.031859
| 7:54 | 9.7467 | 0.031631
| 7:54 | 9.7469 | 0.031412
| 7:54 | 9.7472 | 0.03121
| 7:54 | 9.7475 | 0.031016
| 7:54 | 9.7478 | 0.030828
| 7:54 | 9.7481 | 0.03065
| 7:54 | 9.7483 | 0.030481
| 7:54 | 9.7486 | 0.030321
| 7:54 | 9.7489 | 0.030171
| 7:54 | 9.7492 | 0.03003
| 7:54 | 9.7494 | 0.029899
| 7:54 | 9.7497 | 0.029777
| 7:54 | 9.75 | 0.029664
| 7:54 | 9.7503 | 0.029561
| 7:54 | 9.7506 | 0.029462
| 7:54 | 9.7508 | 0.029377
| 7:54 | 9.7511 | 0.029305
| 7:54 | 9.7514 | 0.029246
| 7:54 | 9.7517 | 0.029188
| 7:54 | 9.7519 | 0.02913
| 7:54 | 9.7522 | 0.029071
| 7:54 | 9.7525 | 0.029013
| 7:54 | 9.7528 | 0.028938
| 7:54 | 9.7531 | 0.028867
| 7:54 | 9.7533 | 0.028802
| 7:54 | 9.7536 | 0.028751
| 7:54 | 9.7539 | 0.028704
| 7:54 | 9.7542 | 0.028659
| 7:54 | 9.7544 | 0.028616
| 7:54 | 9.7547 | 0.028575
| 7:54 | 9.755 | 0.028536
| 7:54 | 9.7553 | 0.028509
| 7:54 | 9.7556 | 0.0285
| 7:54 | 9.7558 | 0.028493
| 7:54 | 9.7561 | 0.028487
| 7:54 | 9.7564 | 0.028462
| 7:54 | 9.7567 | 0.028415
| 7:54 | 9.7569 | 0.028344
| 7:54 | 9.7572 | 0.02825
| 7:54 | 9.7575 | 0.028132
| 7:54 | 9.7578 | 0.027992
| 7:54 | 9.7581 | 0.027828
| 7:54 | 9.7583 | 0.027643
| 7:54 | 9.7586 | 0.027449
| 7:54 | 9.7589 | 0.027248
| 7:54 | 9.7592 | 0.02705
| 7:54 | 9.7594 | 0.026855
| 7:54 | 9.7597 | 0.026676
| 7:54 | 9.76 | 0.026519
| 7:54 | 9.7603 | 0.026384
| 7:54 | 9.7606 | 0.026275
| 7:54 | 9.7608 | 0.026195
| 7:54 | 9.7611 | 0.02611
| 7:54 | 9.7614 | 0.025999
| 7:54 | 9.7617 | 0.025873
| 7:55 | 9.7619 | 0.025746
| 7:55 | 9.7622 | 0.025616
| 7:55 | 9.7625 | 0.025485
| 7:55 | 9.7628 | 0.025352
| 7:55 | 9.7631 | 0.02521
| 7:55 | 9.7633 | 0.025057
| 7:55 | 9.7636 | 0.024895
| 7:55 | 9.7639 | 0.024722
| 7:55 | 9.7642 | 0.024547
| 7:55 | 9.7644 | 0.024375
| 7:55 | 9.7647 | 0.024211
| 7:55 | 9.765 | 0.024055
| 7:55 | 9.7653 | 0.023907
| 7:55 | 9.7656 | 0.023767
| 7:55 | 9.7658 | 0.023634
| 7:55 | 9.7661 | 0.02351
| 7:55 | 9.7664 | 0.023394
| 7:55 | 9.7667 | 0.023286
| 7:55 | 9.7669 | 0.023185
| 7:55 | 9.7672 | 0.023184
| 7:55 | 9.7675 | 0.023209
| 7:55 | 9.7678 | 0.023237
| 7:55 | 9.7681 | 0.023267
| 7:55 | 9.7683 | 0.023298
| 7:55 | 9.7686 | 0.023332
| 7:55 | 9.7689 | 0.023367
| 7:55 | 9.7692 | 0.023405
| 7:55 | 9.7694 | 0.023444
| 7:55 | 9.7697 | 0.023485
| 7:55 | 9.77 | 0.023528
| 7:55 | 9.7703 | 0.023571
| 7:55 | 9.7706 | 0.023613
| 7:55 | 9.7708 | 0.023653
| 7:55 | 9.7711 | 0.023691
| 7:55 | 9.7714 | 0.023728
| 7:55 | 9.7717 | 0.023763
| 7:55 | 9.7719 | 0.023796
| 7:55 | 9.7722 | 0.023822
| 7:55 | 9.7725 | 0.023848
| 7:55 | 9.7728 | 0.023872
| 7:55 | 9.7731 | 0.023888
| 7:55 | 9.7733 | 0.023894
| 7:55 | 9.7736 | 0.023891
| 7:55 | 9.7739 | 0.023878
| 7:55 | 9.7742 | 0.023856
| 7:55 | 9.7744 | 0.023824
| 7:55 | 9.7747 | 0.023783
| 7:55 | 9.775 | 0.023722
| 7:55 | 9.7753 | 0.023644
| 7:55 | 9.7756 | 0.023565
| 7:55 | 9.7758 | 0.023486
| 7:55 | 9.7761 | 0.023406
| 7:55 | 9.7764 | 0.023325
| 7:55 | 9.7767 | 0.023243
| 7:55 | 9.7769 | 0.023161
| 7:55 | 9.7772 | 0.023077
| 7:55 | 9.7775 | 0.022994
| 7:55 | 9.7778 | 0.022909
| 7:55 | 9.7781 | 0.022824
| 7:56 | 9.7783 | 0.022739
| 7:56 | 9.7786 | 0.02265
| 7:56 | 9.7789 | 0.022556
| 7:56 | 9.7792 | 0.022453
| 7:56 | 9.7794 | 0.022345
| 7:56 | 9.7797 | 0.022234
| 7:56 | 9.78 | 0.022137
| 7:56 | 9.7803 | 0.022056
| 7:56 | 9.7806 | 0.021984
| 7:56 | 9.7808 | 0.021917
| 7:56 | 9.7811 | 0.021864
| 7:56 | 9.7814 | 0.021824
| 7:56 | 9.7817 | 0.021798
| 7:56 | 9.7819 | 0.021785
| 7:56 | 9.7822 | 0.021787
| 7:56 | 9.7825 | 0.021801
| 7:56 | 9.7828 | 0.02183
| 7:56 | 9.7831 | 0.021872
| 7:56 | 9.7833 | 0.021928
| 7:56 | 9.7836 | 0.021992
| 7:56 | 9.7839 | 0.022073
| 7:56 | 9.7842 | 0.022173
| 7:56 | 9.7844 | 0.022277
| 7:56 | 9.7847 | 0.022385
| 7:56 | 9.785 | 0.022497
| 7:56 | 9.7853 | 0.022612
| 7:56 | 9.7856 | 0.022744
| 7:56 | 9.7858 | 0.022923
| 7:56 | 9.7861 | 0.023172
| 7:56 | 9.7864 | 0.023492
| 7:56 | 9.7867 | 0.023873
| 7:56 | 9.7869 | 0.024282
| 7:56 | 9.7872 | 0.024726
| 7:56 | 9.7875 | 0.025188
| 7:56 | 9.7878 | 0.025661
| 7:56 | 9.7881 | 0.026141
| 7:56 | 9.7883 | 0.026628
| 7:56 | 9.7886 | 0.027121
| 7:56 | 9.7889 | 0.027621
| 7:56 | 9.7892 | 0.028128
| 7:56 | 9.7894 | 0.028633
| 7:56 | 9.7897 | 0.029132
| 7:56 | 9.79 | 0.029623
| 7:56 | 9.7903 | 0.030107
| 7:56 | 9.7906 | 0.030584
| 7:56 | 9.7908 | 0.031054
| 7:56 | 9.7911 | 0.031517
| 7:56 | 9.7914 | 0.031973
| 7:56 | 9.7917 | 0.032416
| 7:56 | 9.7919 | 0.032831
| 7:56 | 9.7922 | 0.033226
| 7:56 | 9.7925 | 0.033604
| 7:56 | 9.7928 | 0.03397
| 7:56 | 9.7931 | 0.034329
| 7:56 | 9.7933 | 0.034688
| 7:56 | 9.7936 | 0.03505
| 7:56 | 9.7939 | 0.035415
| 7:56 | 9.7942 | 0.035782
| 7:56 | 9.7944 | 0.036151
| 7:56 | 9.7947 | 0.036523
| 7:56 | 9.795 | 0.036898
| 7:57 | 9.7953 | 0.037275
| 7:57 | 9.7956 | 0.037654
| 7:57 | 9.7958 | 0.038037
| 7:57 | 9.7961 | 0.038422
| 7:57 | 9.7964 | 0.03881
| 7:57 | 9.7967 | 0.039201
| 7:57 | 9.7969 | 0.039601
| 7:57 | 9.7972 | 0.040011
| 7:57 | 9.7975 | 0.040431
| 7:57 | 9.7978 | 0.040844
| 7:57 | 9.7981 | 0.041249
| 7:57 | 9.7983 | 0.041644
| 7:57 | 9.7986 | 0.042029
| 7:57 | 9.7989 | 0.042406
| 7:57 | 9.7992 | 0.042772
| 7:57 | 9.7994 | 0.04313
| 7:57 | 9.7997 | 0.043478
| 7:57 | 9.8 | 0.043817
| 7:57 | 9.8003 | 0.044146
| 7:57 | 9.8006 | 0.044479
| 7:57 | 9.8008 | 0.044816
| 7:57 | 9.8011 | 0.045159
| 7:57 | 9.8014 | 0.045508
| 7:57 | 9.8017 | 0.045856
| 7:57 | 9.8019 | 0.046202
| 7:57 | 9.8022 | 0.046547
| 7:57 | 9.8025 | 0.04689
| 7:57 | 9.8028 | 0.047231
| 7:57 | 9.8031 | 0.047571
| 7:57 | 9.8033 | 0.047905
| 7:57 | 9.8036 | 0.048237
| 7:57 | 9.8039 | 0.048572
| 7:57 | 9.8042 | 0.048909
| 7:57 | 9.8044 | 0.049248
| 7:57 | 9.8047 | 0.049589
| 7:57 | 9.805 | 0.049948
| 7:57 | 9.8053 | 0.050331
| 7:57 | 9.8056 | 0.050732
| 7:57 | 9.8058 | 0.051138
| 7:57 | 9.8061 | 0.051542
| 7:57 | 9.8064 | 0.051939
| 7:57 | 9.8067 | 0.05233
| 7:57 | 9.8069 | 0.052715
| 7:57 | 9.8072 | 0.053094
| 7:57 | 9.8075 | 0.053467
| 7:57 | 9.8078 | 0.053833
| 7:57 | 9.8081 | 0.054195
| 7:57 | 9.8083 | 0.054571
| 7:57 | 9.8086 | 0.054969
| 7:57 | 9.8089 | 0.055382
| 7:57 | 9.8092 | 0.055792
| 7:57 | 9.8094 | 0.056202
| 7:57 | 9.8097 | 0.056609
| 7:57 | 9.81 | 0.057015
| 7:57 | 9.8103 | 0.057418
| 7:57 | 9.8106 | 0.057802
| 7:57 | 9.8108 | 0.058167
| 7:57 | 9.8111 | 0.058512
| 7:57 | 9.8114 | 0.05883
| 7:58 | 9.8117 | 0.059124
| 7:58 | 9.8119 | 0.059396
| 7:58 | 9.8122 | 0.059662
| 7:58 | 9.8125 | 0.059922
| 7:58 | 9.8128 | 0.060174
| 7:58 | 9.8131 | 0.060416
| 7:58 | 9.8133 | 0.060639
| 7:58 | 9.8136 | 0.060866
| 7:58 | 9.8139 | 0.061095
| 7:58 | 9.8142 | 0.06135
| 7:58 | 9.8144 | 0.061616
| 7:58 | 9.8147 | 0.061892
| 7:58 | 9.815 | 0.062178
| 7:58 | 9.8153 | 0.062475
| 7:58 | 9.8156 | 0.062782
| 7:58 | 9.8158 | 0.063099
| 7:58 | 9.8161 | 0.063426
| 7:58 | 9.8164 | 0.063764
| 7:58 | 9.8167 | 0.064112
| 7:58 | 9.8169 | 0.06447
| 7:58 | 9.8172 | 0.064835
| 7:58 | 9.8175 | 0.065206
| 7:58 | 9.8178 | 0.065585
| 7:58 | 9.8181 | 0.065966
| 7:58 | 9.8183 | 0.066351
| 7:58 | 9.8186 | 0.066738
| 7:58 | 9.8189 | 0.067128
| 7:58 | 9.8192 | 0.067521
| 7:58 | 9.8194 | 0.067924
| 7:58 | 9.8197 | 0.068339
| 7:58 | 9.82 | 0.068767
| 7:58 | 9.8203 | 0.069207
| 7:58 | 9.8206 | 0.06966
| 7:58 | 9.8208 | 0.070126
| 7:58 | 9.8211 | 0.070604
| 7:58 | 9.8214 | 0.071093
| 7:58 | 9.8217 | 0.071588
| 7:58 | 9.8219 | 0.072091
| 7:58 | 9.8222 | 0.072611
| 7:58 | 9.8225 | 0.073141
| 7:58 | 9.8228 | 0.073671
| 7:58 | 9.8231 | 0.0742
| 7:58 | 9.8233 | 0.074726
| 7:58 | 9.8236 | 0.07525
| 7:58 | 9.8239 | 0.075773
| 7:58 | 9.8242 | 0.076293
| 7:58 | 9.8244 | 0.076809
| 7:58 | 9.8247 | 0.077316
| 7:58 | 9.825 | 0.077814
| 7:58 | 9.8253 | 0.078308
| 7:58 | 9.8256 | 0.078798
| 7:58 | 9.8258 | 0.079284
| 7:58 | 9.8261 | 0.079766
| 7:58 | 9.8264 | 0.080235
| 7:58 | 9.8267 | 0.080696
| 7:58 | 9.8269 | 0.08115
| 7:58 | 9.8272 | 0.081585
| 7:58 | 9.8275 | 0.082022
| 7:58 | 9.8278 | 0.08246
| 7:58 | 9.8281 | 0.0829
| 7:58 | 9.8283 | 0.083342
| 7:59 | 9.8286 | 0.083786
| 7:59 | 9.8289 | 0.084233
| 7:59 | 9.8292 | 0.084695
| 7:59 | 9.8294 | 0.085167
| 7:59 | 9.8297 | 0.085655
| 7:59 | 9.83 | 0.086153
| 7:59 | 9.8303 | 0.086659
| 7:59 | 9.8306 | 0.087168
| 7:59 | 9.8308 | 0.087684
| 7:59 | 9.8311 | 0.088206
| 7:59 | 9.8314 | 0.08873
| 7:59 | 9.8317 | 0.089258
| 7:59 | 9.8319 | 0.08979
| 7:59 | 9.8322 | 0.090324
| 7:59 | 9.8325 | 0.090862
| 7:59 | 9.8328 | 0.091403
| 7:59 | 9.8331 | 0.091947
| 7:59 | 9.8333 | 0.092495
| 7:59 | 9.8336 | 0.093046
| 7:59 | 9.8339 | 0.0936
| 7:59 | 9.8342 | 0.094156
| 7:59 | 9.8344 | 0.094713
| 7:59 | 9.8347 | 0.095272
| 7:59 | 9.835 | 0.095832
| 7:59 | 9.8353 | 0.096392
| 7:59 | 9.8356 | 0.09695
| 7:59 | 9.8358 | 0.097504
| 7:59 | 9.8361 | 0.098048
| 7:59 | 9.8364 | 0.098587
| 7:59 | 9.8367 | 0.09912
| 7:59 | 9.8369 | 0.099655
| 7:59 | 9.8372 | 0.10019
| 7:59 | 9.8375 | 0.10073
| 7:59 | 9.8378 | 0.10126
| 7:59 | 9.8381 | 0.1018
| 7:59 | 9.8383 | 0.10234
| 7:59 | 9.8386 | 0.10288
| 7:59 | 9.8389 | 0.10345
| 7:59 | 9.8392 | 0.10403
| 7:59 | 9.8394 | 0.10463
| 7:59 | 9.8397 | 0.10523
| 7:59 | 9.84 | 0.10584
| 7:59 | 9.8403 | 0.10644
| 7:59 | 9.8406 | 0.10705
| 7:59 | 9.8408 | 0.10765
| 7:59 | 9.8411 | 0.10826
| 7:59 | 9.8414 | 0.10886
| 7:59 | 9.8417 | 0.10946
| 7:59 | 9.8419 | 0.11007
| 7:59 | 9.8422 | 0.11066
| 7:59 | 9.8425 | 0.11126
| 7:59 | 9.8428 | 0.11186
| 7:59 | 9.8431 | 0.11245
| 7:59 | 9.8433 | 0.11304
| 7:59 | 9.8436 | 0.11363
| 7:59 | 9.8439 | 0.11422
| 7:59 | 9.8442 | 0.11481
| 7:59 | 9.8444 | 0.1154
| 7:59 | 9.8447 | 0.11599
| 8:00 | 9.845 | 0.11658
| 8:00 | 9.8453 | 0.11717
| 8:00 | 9.8456 | 0.11776
| 8:00 | 9.8458 | 0.11835
| 8:00 | 9.8461 | 0.11894
| 8:00 | 9.8464 | 0.11953
| 8:00 | 9.8467 | 0.12013
| 8:00 | 9.8469 | 0.12072
| 8:00 | 9.8472 | 0.12131
| 8:00 | 9.8475 | 0.1219
| 8:00 | 9.8478 | 0.12249
| 8:00 | 9.8481 | 0.12307
| 8:00 | 9.8483 | 0.12365
| 8:00 | 9.8486 | 0.12422
| 8:00 | 9.8489 | 0.12478
| 8:00 | 9.8492 | 0.12534
| 8:00 | 9.8494 | 0.12589
| 8:00 | 9.8497 | 0.12644
| 8:00 | 9.85 | 0.12698
| 8:00 | 9.8503 | 0.12752
| 8:00 | 9.8506 | 0.12806
| 8:00 | 9.8508 | 0.1286
| 8:00 | 9.8511 | 0.12914
| 8:00 | 9.8514 | 0.12967
| 8:00 | 9.8517 | 0.13021
| 8:00 | 9.8519 | 0.13074
| 8:00 | 9.8522 | 0.13127
| 8:00 | 9.8525 | 0.1318
| 8:00 | 9.8528 | 0.13233
| 8:00 | 9.8531 | 0.13284
| 8:00 | 9.8533 | 0.13334
| 8:00 | 9.8536 | 0.13382
| 8:00 | 9.8539 | 0.13428
| 8:00 | 9.8542 | 0.13474
| 8:00 | 9.8544 | 0.13518
| 8:00 | 9.8547 | 0.13561
| 8:00 | 9.855 | 0.13604
| 8:00 | 9.8553 | 0.13646
| 8:00 | 9.8556 | 0.13688
| 8:00 | 9.8558 | 0.13729
| 8:00 | 9.8561 | 0.1377
| 8:00 | 9.8564 | 0.13809
| 8:00 | 9.8567 | 0.13848
| 8:00 | 9.8569 | 0.13885
| 8:00 | 9.8572 | 0.13922
| 8:00 | 9.8575 | 0.13957
| 8:00 | 9.8578 | 0.13992
| 8:00 | 9.8581 | 0.14026
| 8:00 | 9.8583 | 0.14061
| 8:00 | 9.8586 | 0.14095
| 8:00 | 9.8589 | 0.1413
| 8:00 | 9.8592 | 0.14165
| 8:00 | 9.8594 | 0.14201
| 8:00 | 9.8597 | 0.14239
| 8:00 | 9.86 | 0.14277
| 8:00 | 9.8603 | 0.14318
| 8:00 | 9.8606 | 0.14359
| 8:00 | 9.8608 | 0.14401
| 8:00 | 9.8611 | 0.14444
| 8:00 | 9.8614 | 0.14487
| 8:00 | 9.8617 | 0.1453
| 8:01 | 9.8619 | 0.14574
| 8:01 | 9.8622 | 0.14617
| 8:01 | 9.8625 | 0.14661
| 8:01 | 9.8628 | 0.14704
| 8:01 | 9.8631 | 0.14747
| 8:01 | 9.8633 | 0.14791
| 8:01 | 9.8636 | 0.14834
| 8:01 | 9.8639 | 0.14877
| 8:01 | 9.8642 | 0.1492
| 8:01 | 9.8644 | 0.14963
| 8:01 | 9.8647 | 0.15006
| 8:01 | 9.865 | 0.15048
| 8:01 | 9.8653 | 0.15091
| 8:01 | 9.8656 | 0.15133
| 8:01 | 9.8658 | 0.15175
| 8:01 | 9.8661 | 0.15217
| 8:01 | 9.8664 | 0.15259
| 8:01 | 9.8667 | 0.15299
| 8:01 | 9.8669 | 0.15338
| 8:01 | 9.8672 | 0.15376
| 8:01 | 9.8675 | 0.15411
| 8:01 | 9.8678 | 0.15444
| 8:01 | 9.8681 | 0.15472
| 8:01 | 9.8683 | 0.155
| 8:01 | 9.8686 | 0.15524
| 8:01 | 9.8689 | 0.15543
| 8:01 | 9.8692 | 0.15556
| 8:01 | 9.8694 | 0.15563
| 8:01 | 9.8697 | 0.15566
| 8:01 | 9.87 | 0.15566
| 8:01 | 9.8703 | 0.15566
| 8:01 | 9.8706 | 0.15565
| 8:01 | 9.8708 | 0.15563
| 8:01 | 9.8711 | 0.15561
| 8:01 | 9.8714 | 0.15558
| 8:01 | 9.8717 | 0.15555
| 8:01 | 9.8719 | 0.15551
| 8:01 | 9.8722 | 0.15546
| 8:01 | 9.8725 | 0.1554
| 8:01 | 9.8728 | 0.15535
| 8:01 | 9.8731 | 0.1553
| 8:01 | 9.8733 | 0.15524
| 8:01 | 9.8736 | 0.15518
| 8:01 | 9.8739 | 0.15513
| 8:01 | 9.8742 | 0.15507
| 8:01 | 9.8744 | 0.15501
| 8:01 | 9.8747 | 0.15495
| 8:01 | 9.875 | 0.1549
| 8:01 | 9.8753 | 0.15485
| 8:01 | 9.8756 | 0.15479
| 8:01 | 9.8758 | 0.15474
| 8:01 | 9.8761 | 0.15468
| 8:01 | 9.8764 | 0.15462
| 8:01 | 9.8767 | 0.15456
| 8:01 | 9.8769 | 0.1545
| 8:01 | 9.8772 | 0.15444
| 8:01 | 9.8775 | 0.15437
| 8:01 | 9.8778 | 0.1543
| 8:01 | 9.8781 | 0.15423
| 8:01 | 9.8783 | 0.15416
| 8:02 | 9.8786 | 0.15406
| 8:02 | 9.8789 | 0.15395
| 8:02 | 9.8792 | 0.15382
| 8:02 | 9.8794 | 0.15368
| 8:02 | 9.8797 | 0.15352
| 8:02 | 9.88 | 0.15333
| 8:02 | 9.8803 | 0.15314
| 8:02 | 9.8806 | 0.15294
| 8:02 | 9.8808 | 0.15272
| 8:02 | 9.8811 | 0.1525
| 8:02 | 9.8814 | 0.15226
| 8:02 | 9.8817 | 0.15203
| 8:02 | 9.8819 | 0.15179
| 8:02 | 9.8822 | 0.15154
| 8:02 | 9.8825 | 0.15128
| 8:02 | 9.8828 | 0.15103
| 8:02 | 9.8831 | 0.15076
| 8:02 | 9.8833 | 0.15049
| 8:02 | 9.8836 | 0.15022
| 8:02 | 9.8839 | 0.14994
| 8:02 | 9.8842 | 0.14967
| 8:02 | 9.8844 | 0.14939
| 8:02 | 9.8847 | 0.14912
| 8:02 | 9.885 | 0.14886
| 8:02 | 9.8853 | 0.1486
| 8:02 | 9.8856 | 0.14835
| 8:02 | 9.8858 | 0.1481
| 8:02 | 9.8861 | 0.14787
| 8:02 | 9.8864 | 0.14764
| 8:02 | 9.8867 | 0.14741
| 8:02 | 9.8869 | 0.14721
| 8:02 | 9.8872 | 0.14704
| 8:02 | 9.8875 | 0.1469
| 8:02 | 9.8878 | 0.14678
| 8:02 | 9.8881 | 0.14668
| 8:02 | 9.8883 | 0.14658
| 8:02 | 9.8886 | 0.14649
| 8:02 | 9.8889 | 0.14641
| 8:02 | 9.8892 | 0.14633
| 8:02 | 9.8894 | 0.14624
| 8:02 | 9.8897 | 0.14614
| 8:02 | 9.89 | 0.14603
| 8:02 | 9.8903 | 0.14591
| 8:02 | 9.8906 | 0.14578
| 8:02 | 9.8908 | 0.14564
| 8:02 | 9.8911 | 0.14548
| 8:02 | 9.8914 | 0.14533
| 8:02 | 9.8917 | 0.14517
| 8:02 | 9.8919 | 0.145
| 8:02 | 9.8922 | 0.14483
| 8:02 | 9.8925 | 0.14467
| 8:02 | 9.8928 | 0.14451
| 8:02 | 9.8931 | 0.14436
| 8:02 | 9.8933 | 0.14422
| 8:02 | 9.8936 | 0.14411
| 8:02 | 9.8939 | 0.14404
| 8:02 | 9.8942 | 0.14398
| 8:02 | 9.8944 | 0.14394
| 8:02 | 9.8947 | 0.1439
| 8:02 | 9.895 | 0.14387
| 8:03 | 9.8953 | 0.14386
| 8:03 | 9.8956 | 0.14386
| 8:03 | 9.8958 | 0.14388
| 8:03 | 9.8961 | 0.14391
| 8:03 | 9.8964 | 0.14396
| 8:03 | 9.8967 | 0.14402
| 8:03 | 9.8969 | 0.14409
| 8:03 | 9.8972 | 0.14417
| 8:03 | 9.8975 | 0.14426
| 8:03 | 9.8978 | 0.14435
| 8:03 | 9.8981 | 0.14444
| 8:03 | 9.8983 | 0.14453
| 8:03 | 9.8986 | 0.14461
| 8:03 | 9.8989 | 0.14469
| 8:03 | 9.8992 | 0.14477
| 8:03 | 9.8994 | 0.14484
| 8:03 | 9.8997 | 0.14491
| 8:03 | 9.9 | 0.14498
| 8:03 | 9.9003 | 0.14505
| 8:03 | 9.9006 | 0.14512
| 8:03 | 9.9008 | 0.1452
| 8:03 | 9.9011 | 0.14528
| 8:03 | 9.9014 | 0.14536
| 8:03 | 9.9017 | 0.14544
| 8:03 | 9.9019 | 0.14552
| 8:03 | 9.9022 | 0.1456
| 8:03 | 9.9025 | 0.14567
| 8:03 | 9.9028 | 0.14576
| 8:03 | 9.9031 | 0.14583
| 8:03 | 9.9033 | 0.14589
| 8:03 | 9.9036 | 0.14594
| 8:03 | 9.9039 | 0.14599
| 8:03 | 9.9042 | 0.14604
| 8:03 | 9.9044 | 0.14608
| 8:03 | 9.9047 | 0.14613
| 8:03 | 9.905 | 0.14617
| 8:03 | 9.9053 | 0.14622
| 8:03 | 9.9056 | 0.14627
| 8:03 | 9.9058 | 0.14635
| 8:03 | 9.9061 | 0.14645
| 8:03 | 9.9064 | 0.14654
| 8:03 | 9.9067 | 0.14663
| 8:03 | 9.9069 | 0.14672
| 8:03 | 9.9072 | 0.1468
| 8:03 | 9.9075 | 0.14688
| 8:03 | 9.9078 | 0.14695
| 8:03 | 9.9081 | 0.14702
| 8:03 | 9.9083 | 0.14709
| 8:03 | 9.9086 | 0.14718
| 8:03 | 9.9089 | 0.14729
| 8:03 | 9.9092 | 0.14741
| 8:03 | 9.9094 | 0.14754
| 8:03 | 9.9097 | 0.14768
| 8:03 | 9.91 | 0.14782
| 8:03 | 9.9103 | 0.14797
| 8:03 | 9.9106 | 0.14812
| 8:03 | 9.9108 | 0.14827
| 8:03 | 9.9111 | 0.14843
| 8:03 | 9.9114 | 0.1486
| 8:03 | 9.9117 | 0.14877
| 8:04 | 9.9119 | 0.14894
| 8:04 | 9.9122 | 0.14911
| 8:04 | 9.9125 | 0.14927
| 8:04 | 9.9128 | 0.14943
| 8:04 | 9.9131 | 0.14958
| 8:04 | 9.9133 | 0.14973
| 8:04 | 9.9136 | 0.14987
| 8:04 | 9.9139 | 0.14997
| 8:04 | 9.9142 | 0.15006
| 8:04 | 9.9144 | 0.15015
| 8:04 | 9.9147 | 0.15022
| 8:04 | 9.915 | 0.15027
| 8:04 | 9.9153 | 0.15032
| 8:04 | 9.9156 | 0.15035
| 8:04 | 9.9158 | 0.15037
| 8:04 | 9.9161 | 0.15037
| 8:04 | 9.9164 | 0.15036
| 8:04 | 9.9167 | 0.15034
| 8:04 | 9.9169 | 0.1503
| 8:04 | 9.9172 | 0.15026
| 8:04 | 9.9175 | 0.15022
| 8:04 | 9.9178 | 0.15018
| 8:04 | 9.9181 | 0.15014
| 8:04 | 9.9183 | 0.15012
| 8:04 | 9.9186 | 0.15011
| 8:04 | 9.9189 | 0.15013
| 8:04 | 9.9192 | 0.15015
| 8:04 | 9.9194 | 0.15021
| 8:04 | 9.9197 | 0.15028
| 8:04 | 9.92 | 0.15038
| 8:04 | 9.9203 | 0.15052
| 8:04 | 9.9206 | 0.1507
| 8:04 | 9.9208 | 0.15089
| 8:04 | 9.9211 | 0.15109
| 8:04 | 9.9214 | 0.15129
| 8:04 | 9.9217 | 0.15152
| 8:04 | 9.9219 | 0.15175
| 8:04 | 9.9222 | 0.152
| 8:04 | 9.9225 | 0.15227
| 8:04 | 9.9228 | 0.15256
| 8:04 | 9.9231 | 0.15285
| 8:04 | 9.9233 | 0.15316
| 8:04 | 9.9236 | 0.15347
| 8:04 | 9.9239 | 0.15379
| 8:04 | 9.9242 | 0.15413
| 8:04 | 9.9244 | 0.15447
| 8:04 | 9.9247 | 0.15482
| 8:04 | 9.925 | 0.15517
| 8:04 | 9.9253 | 0.15553
| 8:04 | 9.9256 | 0.15589
| 8:04 | 9.9258 | 0.15626
| 8:04 | 9.9261 | 0.15665
| 8:04 | 9.9264 | 0.15706
| 8:04 | 9.9267 | 0.15748
| 8:04 | 9.9269 | 0.15792
| 8:04 | 9.9272 | 0.15837
| 8:04 | 9.9275 | 0.15883
| 8:04 | 9.9278 | 0.15929
| 8:04 | 9.9281 | 0.15974
| 8:05 | 9.9283 | 0.1602
| 8:05 | 9.9286 | 0.16066
| 8:05 | 9.9289 | 0.16112
| 8:05 | 9.9292 | 0.16157
| 8:05 | 9.9294 | 0.16203
| 8:05 | 9.9297 | 0.16249
| 8:05 | 9.93 | 0.16295
| 8:05 | 9.9303 | 0.16341
| 8:05 | 9.9306 | 0.16386
| 8:05 | 9.9308 | 0.16432
| 8:05 | 9.9311 | 0.16479
| 8:05 | 9.9314 | 0.16525
| 8:05 | 9.9317 | 0.16572
| 8:05 | 9.9319 | 0.16619
| 8:05 | 9.9322 | 0.16667
| 8:05 | 9.9325 | 0.16715
| 8:05 | 9.9328 | 0.16763
| 8:05 | 9.9331 | 0.16812
| 8:05 | 9.9333 | 0.16861
| 8:05 | 9.9336 | 0.1691
| 8:05 | 9.9339 | 0.16959
| 8:05 | 9.9342 | 0.17009
| 8:05 | 9.9344 | 0.17059
| 8:05 | 9.9347 | 0.17109
| 8:05 | 9.935 | 0.17159
| 8:05 | 9.9353 | 0.17209
| 8:05 | 9.9356 | 0.1726
| 8:05 | 9.9358 | 0.1731
| 8:05 | 9.9361 | 0.17361
| 8:05 | 9.9364 | 0.17412
| 8:05 | 9.9367 | 0.17463
| 8:05 | 9.9369 | 0.17514
| 8:05 | 9.9372 | 0.17565
| 8:05 | 9.9375 | 0.17616
| 8:05 | 9.9378 | 0.17668
| 8:05 | 9.9381 | 0.17719
| 8:05 | 9.9383 | 0.17771
| 8:05 | 9.9386 | 0.17822
| 8:05 | 9.9389 | 0.17874
| 8:05 | 9.9392 | 0.17926
| 8:05 | 9.9394 | 0.17978
| 8:05 | 9.9397 | 0.18029
| 8:05 | 9.94 | 0.18082
| 8:05 | 9.9403 | 0.18134
| 8:05 | 9.9406 | 0.18186
| 8:05 | 9.9408 | 0.18238
| 8:05 | 9.9411 | 0.18291
| 8:05 | 9.9414 | 0.18343
| 8:05 | 9.9417 | 0.18395
| 8:05 | 9.9419 | 0.18448
| 8:05 | 9.9422 | 0.185
| 8:05 | 9.9425 | 0.18552
| 8:05 | 9.9428 | 0.18605
| 8:05 | 9.9431 | 0.18657
| 8:05 | 9.9433 | 0.18709
| 8:05 | 9.9436 | 0.18761
| 8:05 | 9.9439 | 0.18813
| 8:05 | 9.9442 | 0.18865
| 8:05 | 9.9444 | 0.18917
| 8:05 | 9.9447 | 0.18969
| 8:06 | 9.945 | 0.19021
| 8:06 | 9.9453 | 0.19073
| 8:06 | 9.9456 | 0.19124
| 8:06 | 9.9458 | 0.19176
| 8:06 | 9.9461 | 0.19228
| 8:06 | 9.9464 | 0.1928
| 8:06 | 9.9467 | 0.19331
| 8:06 | 9.9469 | 0.19383
| 8:06 | 9.9472 | 0.19434
| 8:06 | 9.9475 | 0.19486
| 8:06 | 9.9478 | 0.19537
| 8:06 | 9.9481 | 0.19589
| 8:06 | 9.9483 | 0.1964
| 8:06 | 9.9486 | 0.19691
| 8:06 | 9.9489 | 0.19742
| 8:06 | 9.9492 | 0.19794
| 8:06 | 9.9494 | 0.19845
| 8:06 | 9.9497 | 0.19896
| 8:06 | 9.95 | 0.19947
| 8:06 | 9.9503 | 0.19998
| 8:06 | 9.9506 | 0.20049
| 8:06 | 9.9508 | 0.201
| 8:06 | 9.9511 | 0.20151
| 8:06 | 9.9514 | 0.20202
| 8:06 | 9.9517 | 0.20253
| 8:06 | 9.9519 | 0.20303
| 8:06 | 9.9522 | 0.20354
| 8:06 | 9.9525 | 0.20405
| 8:06 | 9.9528 | 0.20455
| 8:06 | 9.9531 | 0.20506
| 8:06 | 9.9533 | 0.20556
| 8:06 | 9.9536 | 0.20607
| 8:06 | 9.9539 | 0.20657
| 8:06 | 9.9542 | 0.20708
| 8:06 | 9.9544 | 0.20758
| 8:06 | 9.9547 | 0.20808
| 8:06 | 9.955 | 0.20859
| 8:06 | 9.9553 | 0.20909
| 8:06 | 9.9556 | 0.20959
| 8:06 | 9.9558 | 0.21009
| 8:06 | 9.9561 | 0.21059
| 8:06 | 9.9564 | 0.21108
| 8:06 | 9.9567 | 0.21158
| 8:06 | 9.9569 | 0.21208
| 8:06 | 9.9572 | 0.21257
| 8:06 | 9.9575 | 0.21307
| 8:06 | 9.9578 | 0.21356
| 8:06 | 9.9581 | 0.21406
| 8:06 | 9.9583 | 0.21455
| 8:06 | 9.9586 | 0.21504
| 8:06 | 9.9589 | 0.21553
| 8:06 | 9.9592 | 0.21602
| 8:06 | 9.9594 | 0.21651
| 8:06 | 9.9597 | 0.217
| 8:06 | 9.96 | 0.21749
| 8:06 | 9.9603 | 0.21798
| 8:06 | 9.9606 | 0.21846
| 8:06 | 9.9608 | 0.21895
| 8:06 | 9.9611 | 0.21944
| 8:06 | 9.9614 | 0.21992
| 8:07 | 9.9617 | 0.2204
| 8:07 | 9.9619 | 0.22089
| 8:07 | 9.9622 | 0.22137
| 8:07 | 9.9625 | 0.22185
| 8:07 | 9.9628 | 0.22233
| 8:07 | 9.9631 | 0.2228
| 8:07 | 9.9633 | 0.22324
| 8:07 | 9.9636 | 0.22368
| 8:07 | 9.9639 | 0.22411
| 8:07 | 9.9642 | 0.22454
| 8:07 | 9.9644 | 0.22498
| 8:07 | 9.9647 | 0.22542
| 8:07 | 9.965 | 0.22586
| 8:07 | 9.9653 | 0.22631
| 8:07 | 9.9656 | 0.22676
| 8:07 | 9.9658 | 0.22722
| 8:07 | 9.9661 | 0.22768
| 8:07 | 9.9664 | 0.22814
| 8:07 | 9.9667 | 0.22861
| 8:07 | 9.9669 | 0.22908
| 8:07 | 9.9672 | 0.22955
| 8:07 | 9.9675 | 0.23001
| 8:07 | 9.9678 | 0.23047
| 8:07 | 9.9681 | 0.23092
| 8:07 | 9.9683 | 0.23137
| 8:07 | 9.9686 | 0.23181
| 8:07 | 9.9689 | 0.23225
| 8:07 | 9.9692 | 0.23269
| 8:07 | 9.9694 | 0.23312
| 8:07 | 9.9697 | 0.23355
| 8:07 | 9.97 | 0.23397
| 8:07 | 9.9703 | 0.23438
| 8:07 | 9.9706 | 0.23479
| 8:07 | 9.9708 | 0.23519
| 8:07 | 9.9711 | 0.23559
| 8:07 | 9.9714 | 0.23598
| 8:07 | 9.9717 | 0.23636
| 8:07 | 9.9719 | 0.23674
| 8:07 | 9.9722 | 0.23711
| 8:07 | 9.9725 | 0.23748
| 8:07 | 9.9728 | 0.23784
| 8:07 | 9.9731 | 0.23819
| 8:07 | 9.9733 | 0.23854
| 8:07 | 9.9736 | 0.23887
| 8:07 | 9.9739 | 0.2392
| 8:07 | 9.9742 | 0.23952
| 8:07 | 9.9744 | 0.23983
| 8:07 | 9.9747 | 0.24013
| 8:07 | 9.975 | 0.24043
| 8:07 | 9.9753 | 0.24073
| 8:07 | 9.9756 | 0.24104
| 8:07 | 9.9758 | 0.24134
| 8:07 | 9.9761 | 0.24165
| 8:07 | 9.9764 | 0.24195
| 8:07 | 9.9767 | 0.24226
| 8:07 | 9.9769 | 0.24257
| 8:07 | 9.9772 | 0.24288
| 8:07 | 9.9775 | 0.2432
| 8:07 | 9.9778 | 0.24351
| 8:07 | 9.9781 | 0.24383
| 8:08 | 9.9783 | 0.24414
| 8:08 | 9.9786 | 0.24446
| 8:08 | 9.9789 | 0.24478
| 8:08 | 9.9792 | 0.2451
| 8:08 | 9.9794 | 0.24543
| 8:08 | 9.9797 | 0.24576
| 8:08 | 9.98 | 0.24609
| 8:08 | 9.9803 | 0.24642
| 8:08 | 9.9806 | 0.24675
| 8:08 | 9.9808 | 0.24709
| 8:08 | 9.9811 | 0.24742
| 8:08 | 9.9814 | 0.24775
| 8:08 | 9.9817 | 0.24808
| 8:08 | 9.9819 | 0.2484
| 8:08 | 9.9822 | 0.24873
| 8:08 | 9.9825 | 0.24905
| 8:08 | 9.9828 | 0.24938
| 8:08 | 9.9831 | 0.2497
| 8:08 | 9.9833 | 0.25002
| 8:08 | 9.9836 | 0.25034
| 8:08 | 9.9839 | 0.25066
| 8:08 | 9.9842 | 0.25098
| 8:08 | 9.9844 | 0.25129
| 8:08 | 9.9847 | 0.25159
| 8:08 | 9.985 | 0.25189
| 8:08 | 9.9853 | 0.25218
| 8:08 | 9.9856 | 0.25244
| 8:08 | 9.9858 | 0.25269
| 8:08 | 9.9861 | 0.25291
| 8:08 | 9.9864 | 0.2531
| 8:08 | 9.9867 | 0.25326
| 8:08 | 9.9869 | 0.2534
| 8:08 | 9.9872 | 0.25352
| 8:08 | 9.9875 | 0.25361
| 8:08 | 9.9878 | 0.25367
| 8:08 | 9.9881 | 0.25372
| 8:08 | 9.9883 | 0.25375
| 8:08 | 9.9886 | 0.25376
| 8:08 | 9.9889 | 0.25377
| 8:08 | 9.9892 | 0.25376
| 8:08 | 9.9894 | 0.25373
| 8:08 | 9.9897 | 0.25369
| 8:08 | 9.99 | 0.25364
| 8:08 | 9.9903 | 0.25357
| 8:08 | 9.9906 | 0.25349
| 8:08 | 9.9908 | 0.2534
| 8:08 | 9.9911 | 0.25329
| 8:08 | 9.9914 | 0.25317
| 8:08 | 9.9917 | 0.25304
| 8:08 | 9.9919 | 0.25291
| 8:08 | 9.9922 | 0.25278
| 8:08 | 9.9925 | 0.25265
| 8:08 | 9.9928 | 0.25251
| 8:08 | 9.9931 | 0.25236
| 8:08 | 9.9933 | 0.25222
| 8:08 | 9.9936 | 0.25209
| 8:08 | 9.9939 | 0.25195
| 8:08 | 9.9942 | 0.25181
| 8:08 | 9.9944 | 0.25168
| 8:08 | 9.9947 | 0.25156
| 8:08 | 9.995 | 0.25144
| 8:09 | 9.9953 | 0.25133
| 8:09 | 9.9956 | 0.25121
| 8:09 | 9.9958 | 0.25108
| 8:09 | 9.9961 | 0.25095
| 8:09 | 9.9964 | 0.25081
| 8:09 | 9.9967 | 0.25066
| 8:09 | 9.9969 | 0.2505
| 8:09 | 9.9972 | 0.25032
| 8:09 | 9.9975 | 0.25014
| 8:09 | 9.9978 | 0.24995
| 8:09 | 9.9981 | 0.24975
| 8:09 | 9.9983 | 0.24953
| 8:09 | 9.9986 | 0.2493
| 8:09 | 9.9989 | 0.24906
| 8:09 | 9.9992 | 0.2488
| 8:09 | 9.9994 | 0.24853
| 8:09 | 9.9997 | 0.24824
| 8:09 | 10 | 0.24794
| 8:09 | 10.0003 | 0.24762
| 8:09 | 10.0006 | 0.2473
| 8:09 | 10.0008 | 0.24696
| 8:09 | 10.0011 | 0.24659
| 8:09 | 10.0014 | 0.24622
| 8:09 | 10.0017 | 0.24583
| 8:09 | 10.0019 | 0.24545
| 8:09 | 10.0022 | 0.24506
| 8:09 | 10.0025 | 0.24467
| 8:09 | 10.0028 | 0.24429
| 8:09 | 10.0031 | 0.24389
| 8:09 | 10.0033 | 0.24348
| 8:09 | 10.0036 | 0.24305
| 8:09 | 10.0039 | 0.24261
| 8:09 | 10.0042 | 0.24217
| 8:09 | 10.0044 | 0.24173
| 8:09 | 10.0047 | 0.24128
| 8:09 | 10.005 | 0.24083
| 8:09 | 10.0053 | 0.24036
| 8:09 | 10.0056 | 0.23987
| 8:09 | 10.0058 | 0.23938
| 8:09 | 10.0061 | 0.23889
| 8:09 | 10.0064 | 0.23842
| 8:09 | 10.0067 | 0.23797
| 8:09 | 10.0069 | 0.23755
| 8:09 | 10.0072 | 0.23715
| 8:09 | 10.0075 | 0.23678
| 8:09 | 10.0078 | 0.23643
| 8:09 | 10.0081 | 0.2361
| 8:09 | 10.0083 | 0.2358
| 8:09 | 10.0086 | 0.23551
| 8:09 | 10.0089 | 0.23522
| 8:09 | 10.0092 | 0.23494
| 8:09 | 10.0094 | 0.23465
| 8:09 | 10.0097 | 0.23434
| 8:09 | 10.01 | 0.23402
| 8:09 | 10.0103 | 0.23367
| 8:09 | 10.0106 | 0.2333
| 8:09 | 10.0108 | 0.2329
| 8:09 | 10.0111 | 0.23251
| 8:09 | 10.0114 | 0.23215
| 8:10 | 10.0117 | 0.23182
| 8:10 | 10.0119 | 0.2315
| 8:10 | 10.0122 | 0.23119
| 8:10 | 10.0125 | 0.23089
| 8:10 | 10.0128 | 0.23061
| 8:10 | 10.0131 | 0.23035
| 8:10 | 10.0133 | 0.2301
| 8:10 | 10.0136 | 0.22987
| 8:10 | 10.0139 | 0.22966
| 8:10 | 10.0142 | 0.22946
| 8:10 | 10.0144 | 0.22926
| 8:10 | 10.0147 | 0.22907
| 8:10 | 10.015 | 0.22889
| 8:10 | 10.0153 | 0.22872
| 8:10 | 10.0156 | 0.22856
| 8:10 | 10.0158 | 0.22841
| 8:10 | 10.0161 | 0.22827
| 8:10 | 10.0164 | 0.22813
| 8:10 | 10.0167 | 0.22801
| 8:10 | 10.0169 | 0.2279
| 8:10 | 10.0172 | 0.22769
| 8:10 | 10.0175 | 0.22747
| 8:10 | 10.0178 | 0.22726
| 8:10 | 10.0181 | 0.22706
| 8:10 | 10.0183 | 0.22687
| 8:10 | 10.0186 | 0.2267
| 8:10 | 10.0189 | 0.22654
| 8:10 | 10.0192 | 0.22641
| 8:10 | 10.0194 | 0.22628
| 8:10 | 10.0197 | 0.22614
| 8:10 | 10.02 | 0.22601
| 8:10 | 10.0203 | 0.22587
| 8:10 | 10.0206 | 0.22573
| 8:10 | 10.0208 | 0.2256
| 8:10 | 10.0211 | 0.22549
| 8:10 | 10.0214 | 0.22541
| 8:10 | 10.0217 | 0.22534
| 8:10 | 10.0219 | 0.22528
| 8:10 | 10.0222 | 0.22521
| 8:10 | 10.0225 | 0.22511
| 8:10 | 10.0228 | 0.22498
| 8:10 | 10.0231 | 0.22482
| 8:10 | 10.0233 | 0.22464
| 8:10 | 10.0236 | 0.22444
| 8:10 | 10.0239 | 0.22422
| 8:10 | 10.0242 | 0.22397
| 8:10 | 10.0244 | 0.2237
| 8:10 | 10.0247 | 0.2234
| 8:10 | 10.025 | 0.22309
| 8:10 | 10.0253 | 0.22277
| 8:10 | 10.0256 | 0.22245
| 8:10 | 10.0258 | 0.22214
| 8:10 | 10.0261 | 0.22184
| 8:10 | 10.0264 | 0.22154
| 8:10 | 10.0267 | 0.22125
| 8:10 | 10.0269 | 0.22097
| 8:10 | 10.0272 | 0.2207
| 8:10 | 10.0275 | 0.22044
| 8:10 | 10.0278 | 0.22019
| 8:10 | 10.0281 | 0.21995
| 8:10 | 10.0283 | 0.21973
| 8:11 | 10.0286 | 0.21953
| 8:11 | 10.0289 | 0.21934
| 8:11 | 10.0292 | 0.21918
| 8:11 | 10.0294 | 0.21901
| 8:11 | 10.0297 | 0.21884
| 8:11 | 10.03 | 0.21867
| 8:11 | 10.0303 | 0.2185
| 8:11 | 10.0306 | 0.21832
| 8:11 | 10.0308 | 0.21813
| 8:11 | 10.0311 | 0.21795
| 8:11 | 10.0314 | 0.21775
| 8:11 | 10.0317 | 0.21753
| 8:11 | 10.0319 | 0.2173
| 8:11 | 10.0322 | 0.21706
| 8:11 | 10.0325 | 0.2168
| 8:11 | 10.0328 | 0.21653
| 8:11 | 10.0331 | 0.21625
| 8:11 | 10.0333 | 0.21595
| 8:11 | 10.0336 | 0.21564
| 8:11 | 10.0339 | 0.21531
| 8:11 | 10.0342 | 0.21498
| 8:11 | 10.0344 | 0.21464
| 8:11 | 10.0347 | 0.21431
| 8:11 | 10.035 | 0.21397
| 8:11 | 10.0353 | 0.21363
| 8:11 | 10.0356 | 0.21328
| 8:11 | 10.0358 | 0.21292
| 8:11 | 10.0361 | 0.21252
| 8:11 | 10.0364 | 0.21208
| 8:11 | 10.0367 | 0.2116
| 8:11 | 10.0369 | 0.21109
| 8:11 | 10.0372 | 0.21056
| 8:11 | 10.0375 | 0.21001
| 8:11 | 10.0378 | 0.20945
| 8:11 | 10.0381 | 0.20889
| 8:11 | 10.0383 | 0.20831
| 8:11 | 10.0386 | 0.20773
| 8:11 | 10.0389 | 0.20713
| 8:11 | 10.0392 | 0.20653
| 8:11 | 10.0394 | 0.20591
| 8:11 | 10.0397 | 0.20528
| 8:11 | 10.04 | 0.20466
| 8:11 | 10.0403 | 0.20403
| 8:11 | 10.0406 | 0.2034
| 8:11 | 10.0408 | 0.20277
| 8:11 | 10.0411 | 0.20214
| 8:11 | 10.0414 | 0.20151
| 8:11 | 10.0417 | 0.20088
| 8:11 | 10.0419 | 0.20025
| 8:11 | 10.0422 | 0.19963
| 8:11 | 10.0425 | 0.199
| 8:11 | 10.0428 | 0.19838
| 8:11 | 10.0431 | 0.19775
| 8:11 | 10.0433 | 0.19713
| 8:11 | 10.0436 | 0.1965
| 8:11 | 10.0439 | 0.19588
| 8:11 | 10.0442 | 0.19525
| 8:11 | 10.0444 | 0.19463
| 8:11 | 10.0447 | 0.194
| 8:12 | 10.045 | 0.19338
| 8:12 | 10.0453 | 0.19275
| 8:12 | 10.0456 | 0.19213
| 8:12 | 10.0458 | 0.1915
| 8:12 | 10.0461 | 0.19088
| 8:12 | 10.0464 | 0.19025
| 8:12 | 10.0467 | 0.18963
| 8:12 | 10.0469 | 0.189
| 8:12 | 10.0472 | 0.18838
| 8:12 | 10.0475 | 0.18775
| 8:12 | 10.0478 | 0.18713
| 8:12 | 10.0481 | 0.1865
| 8:12 | 10.0483 | 0.18588
| 8:12 | 10.0486 | 0.18525
| 8:12 | 10.0489 | 0.18463
| 8:12 | 10.0492 | 0.184
| 8:12 | 10.0494 | 0.18338
| 8:12 | 10.0497 | 0.18275
| 8:12 | 10.05 | 0.18213
| 8:12 | 10.0503 | 0.1815
| 8:12 | 10.0506 | 0.18088
| 8:12 | 10.0508 | 0.18025
| 8:12 | 10.0511 | 0.17963
| 8:12 | 10.0514 | 0.179
| 8:12 | 10.0517 | 0.17838
| 8:12 | 10.0519 | 0.17775
| 8:12 | 10.0522 | 0.17713
| 8:12 | 10.0525 | 0.17651
| 8:12 | 10.0528 | 0.17589
| 8:12 | 10.0531 | 0.17528
| 8:12 | 10.0533 | 0.17466
| 8:12 | 10.0536 | 0.17405
| 8:12 | 10.0539 | 0.17344
| 8:12 | 10.0542 | 0.17283
| 8:12 | 10.0544 | 0.17223
| 8:12 | 10.0547 | 0.17164
| 8:12 | 10.055 | 0.17105
| 8:12 | 10.0553 | 0.17047
| 8:12 | 10.0556 | 0.16991
| 8:12 | 10.0558 | 0.16935
| 8:12 | 10.0561 | 0.1688
| 8:12 | 10.0564 | 0.16826
| 8:12 | 10.0567 | 0.16773
| 8:12 | 10.0569 | 0.1672
| 8:12 | 10.0572 | 0.16668
| 8:12 | 10.0575 | 0.16617
| 8:12 | 10.0578 | 0.16566
| 8:12 | 10.0581 | 0.16516
| 8:12 | 10.0583 | 0.16467
| 8:12 | 10.0586 | 0.16419
| 8:12 | 10.0589 | 0.16372
| 8:12 | 10.0592 | 0.16326
| 8:12 | 10.0594 | 0.16281
| 8:12 | 10.0597 | 0.16239
| 8:12 | 10.06 | 0.16198
| 8:12 | 10.0603 | 0.1616
| 8:12 | 10.0606 | 0.16122
| 8:12 | 10.0608 | 0.16085
| 8:12 | 10.0611 | 0.16047
| 8:12 | 10.0614 | 0.1601
| 8:12 | 10.0617 | 0.15971
| 8:13 | 10.0619 | 0.15931
| 8:13 | 10.0622 | 0.1589
| 8:13 | 10.0625 | 0.15847
| 8:13 | 10.0628 | 0.15804
| 8:13 | 10.0631 | 0.15762
| 8:13 | 10.0633 | 0.15721
| 8:13 | 10.0636 | 0.1568
| 8:13 | 10.0639 | 0.1564
| 8:13 | 10.0642 | 0.15602
| 8:13 | 10.0644 | 0.15565
| 8:13 | 10.0647 | 0.1553
| 8:13 | 10.065 | 0.15497
| 8:13 | 10.0653 | 0.15465
| 8:13 | 10.0656 | 0.15434
| 8:13 | 10.0658 | 0.15405
| 8:13 | 10.0661 | 0.15378
| 8:13 | 10.0664 | 0.15352
| 8:13 | 10.0667 | 0.15328
| 8:13 | 10.0669 | 0.15306
| 8:13 | 10.0672 | 0.15284
| 8:13 | 10.0675 | 0.15263
| 8:13 | 10.0678 | 0.15243
| 8:13 | 10.0681 | 0.15224
| 8:13 | 10.0683 | 0.15206
| 8:13 | 10.0686 | 0.1519
| 8:13 | 10.0689 | 0.15177
| 8:13 | 10.0692 | 0.15166
| 8:13 | 10.0694 | 0.15157
| 8:13 | 10.0697 | 0.15148
| 8:13 | 10.07 | 0.15139
| 8:13 | 10.0703 | 0.15129
| 8:13 | 10.0706 | 0.15115
| 8:13 | 10.0708 | 0.15099
| 8:13 | 10.0711 | 0.1508
| 8:13 | 10.0714 | 0.15059
| 8:13 | 10.0717 | 0.15036
| 8:13 | 10.0719 | 0.15012
| 8:13 | 10.0722 | 0.14987
| 8:13 | 10.0725 | 0.1496
| 8:13 | 10.0728 | 0.14934
| 8:13 | 10.0731 | 0.14909
| 8:13 | 10.0733 | 0.14885
| 8:13 | 10.0736 | 0.14862
| 8:13 | 10.0739 | 0.1484
| 8:13 | 10.0742 | 0.14819
| 8:13 | 10.0744 | 0.148
| 8:13 | 10.0747 | 0.14781
| 8:13 | 10.075 | 0.14764
| 8:13 | 10.0753 | 0.14747
| 8:13 | 10.0756 | 0.14731
| 8:13 | 10.0758 | 0.14717
| 8:13 | 10.0761 | 0.14704
| 8:13 | 10.0764 | 0.14696
| 8:13 | 10.0767 | 0.1469
| 8:13 | 10.0769 | 0.14687
| 8:13 | 10.0772 | 0.14688
| 8:13 | 10.0775 | 0.14692
| 8:13 | 10.0778 | 0.14698
| 8:13 | 10.0781 | 0.14708
| 8:14 | 10.0783 | 0.14719
| 8:14 | 10.0786 | 0.14732
| 8:14 | 10.0789 | 0.14744
| 8:14 | 10.0792 | 0.14754
| 8:14 | 10.0794 | 0.14764
| 8:14 | 10.0797 | 0.14772
| 8:14 | 10.08 | 0.14779
| 8:14 | 10.0803 | 0.14785
| 8:14 | 10.0806 | 0.14791
| 8:14 | 10.0808 | 0.14797
| 8:14 | 10.0811 | 0.14802
| 8:14 | 10.0814 | 0.14808
| 8:14 | 10.0817 | 0.14814
| 8:14 | 10.0819 | 0.1482
| 8:14 | 10.0822 | 0.14826
| 8:14 | 10.0825 | 0.14833
| 8:14 | 10.0828 | 0.1484
| 8:14 | 10.0831 | 0.14846
| 8:14 | 10.0833 | 0.14854
| 8:14 | 10.0836 | 0.14861
| 8:14 | 10.0839 | 0.14868
| 8:14 | 10.0842 | 0.14875
| 8:14 | 10.0844 | 0.14883
| 8:14 | 10.0847 | 0.1489
| 8:14 | 10.085 | 0.14898
| 8:14 | 10.0853 | 0.14905
| 8:14 | 10.0856 | 0.14913
| 8:14 | 10.0858 | 0.14921
| 8:14 | 10.0861 | 0.14931
| 8:14 | 10.0864 | 0.1494
| 8:14 | 10.0867 | 0.14951
| 8:14 | 10.0869 | 0.14961
| 8:14 | 10.0872 | 0.14972
| 8:14 | 10.0875 | 0.14982
| 8:14 | 10.0878 | 0.14992
| 8:14 | 10.0881 | 0.15002
| 8:14 | 10.0883 | 0.15013
| 8:14 | 10.0886 | 0.15023
| 8:14 | 10.0889 | 0.1503
| 8:14 | 10.0892 | 0.15036
| 8:14 | 10.0894 | 0.1504
| 8:14 | 10.0897 | 0.15044
| 8:14 | 10.09 | 0.15048
| 8:14 | 10.0903 | 0.15051
| 8:14 | 10.0906 | 0.15055
| 8:14 | 10.0908 | 0.15059
| 8:14 | 10.0911 | 0.15063
| 8:14 | 10.0914 | 0.15067
| 8:14 | 10.0917 | 0.1507
| 8:14 | 10.0919 | 0.15074
| 8:14 | 10.0922 | 0.15078
| 8:14 | 10.0925 | 0.15081
| 8:14 | 10.0928 | 0.15085
| 8:14 | 10.0931 | 0.15089
| 8:14 | 10.0933 | 0.15092
| 8:14 | 10.0936 | 0.15096
| 8:14 | 10.0939 | 0.151
| 8:14 | 10.0942 | 0.15103
| 8:14 | 10.0944 | 0.15107
| 8:14 | 10.0947 | 0.15111
| 8:14 | 10.095 | 0.15114
| 8:15 | 10.0953 | 0.15118
| 8:15 | 10.0956 | 0.15121
| 8:15 | 10.0958 | 0.15125
| 8:15 | 10.0961 | 0.15128
| 8:15 | 10.0964 | 0.15132
| 8:15 | 10.0967 | 0.15135
| 8:15 | 10.0969 | 0.15139
| 8:15 | 10.0972 | 0.15142
| 8:15 | 10.0975 | 0.15146
| 8:15 | 10.0978 | 0.15149
| 8:15 | 10.0981 | 0.15152
| 8:15 | 10.0983 | 0.15156
| 8:15 | 10.0986 | 0.15159
| 8:15 | 10.0989 | 0.15163
| 8:15 | 10.0992 | 0.15166
| 8:15 | 10.0994 | 0.15169
| 8:15 | 10.0997 | 0.15173
| 8:15 | 10.1 | 0.15176
| 8:15 | 10.1003 | 0.15179
| 8:15 | 10.1006 | 0.15182
| 8:15 | 10.1008 | 0.15186
| 8:15 | 10.1011 | 0.15189
| 8:15 | 10.1014 | 0.15192
| 8:15 | 10.1017 | 0.15195
| 8:15 | 10.1019 | 0.15199
| 8:15 | 10.1022 | 0.15202
| 8:15 | 10.1025 | 0.15205
| 8:15 | 10.1028 | 0.15208
| 8:15 | 10.1031 | 0.15211
| 8:15 | 10.1033 | 0.15214
| 8:15 | 10.1036 | 0.15218
| 8:15 | 10.1039 | 0.15221
| 8:15 | 10.1042 | 0.15224
| 8:15 | 10.1044 | 0.15227
| 8:15 | 10.1047 | 0.1523
| 8:15 | 10.105 | 0.15233
| 8:15 | 10.1053 | 0.15236
| 8:15 | 10.1056 | 0.15239
| 8:15 | 10.1058 | 0.15242
| 8:15 | 10.1061 | 0.15245
| 8:15 | 10.1064 | 0.15248
| 8:15 | 10.1067 | 0.15251
| 8:15 | 10.1069 | 0.15254
| 8:15 | 10.1072 | 0.15257
| 8:15 | 10.1075 | 0.1526
| 8:15 | 10.1078 | 0.15263
| 8:15 | 10.1081 | 0.15265
| 8:15 | 10.1083 | 0.15268
| 8:15 | 10.1086 | 0.15271
| 8:15 | 10.1089 | 0.15274
| 8:15 | 10.1092 | 0.15277
| 8:15 | 10.1094 | 0.1528
| 8:15 | 10.1097 | 0.15282
| 8:15 | 10.11 | 0.15285
| 8:15 | 10.1103 | 0.15288
| 8:15 | 10.1106 | 0.15291
| 8:15 | 10.1108 | 0.15294
| 8:15 | 10.1111 | 0.15296
| 8:15 | 10.1114 | 0.15299
| 8:16 | 10.1117 | 0.15302
| 8:16 | 10.1119 | 0.15304
| 8:16 | 10.1122 | 0.15307
| 8:16 | 10.1125 | 0.1531
| 8:16 | 10.1128 | 0.15312
| 8:16 | 10.1131 | 0.15315
| 8:16 | 10.1133 | 0.15318
| 8:16 | 10.1136 | 0.1532
| 8:16 | 10.1139 | 0.15323
| 8:16 | 10.1142 | 0.15325
| 8:16 | 10.1144 | 0.15328
| 8:16 | 10.1147 | 0.1533
| 8:16 | 10.115 | 0.15333
| 8:16 | 10.1153 | 0.15335
| 8:16 | 10.1156 | 0.15338
| 8:16 | 10.1158 | 0.1534
| 8:16 | 10.1161 | 0.15343
| 8:16 | 10.1164 | 0.15345
| 8:16 | 10.1167 | 0.15348
| 8:16 | 10.1169 | 0.1535
| 8:16 | 10.1172 | 0.15353
| 8:16 | 10.1175 | 0.15355
| 8:16 | 10.1178 | 0.15357
| 8:16 | 10.1181 | 0.1536
| 8:16 | 10.1183 | 0.15362
| 8:16 | 10.1186 | 0.15364
| 8:16 | 10.1189 | 0.15367
| 8:16 | 10.1192 | 0.15369
| 8:16 | 10.1194 | 0.15371
| 8:16 | 10.1197 | 0.15374
| 8:16 | 10.12 | 0.15376
| 8:16 | 10.1203 | 0.15378
| 8:16 | 10.1206 | 0.1538
| 8:16 | 10.1208 | 0.15383
| 8:16 | 10.1211 | 0.15385
| 8:16 | 10.1214 | 0.15387
| 8:16 | 10.1217 | 0.15389
| 8:16 | 10.1219 | 0.15392
| 8:16 | 10.1222 | 0.15394
| 8:16 | 10.1225 | 0.15396
| 8:16 | 10.1228 | 0.15398
| 8:16 | 10.1231 | 0.154
| 8:16 | 10.1233 | 0.15403
| 8:16 | 10.1236 | 0.15405
| 8:16 | 10.1239 | 0.15408
| 8:16 | 10.1242 | 0.15411
| 8:16 | 10.1244 | 0.15414
| 8:16 | 10.1247 | 0.15418
| 8:16 | 10.125 | 0.15421
| 8:16 | 10.1253 | 0.15425
| 8:16 | 10.1256 | 0.15428
| 8:16 | 10.1258 | 0.15432
| 8:16 | 10.1261 | 0.15436
| 8:16 | 10.1264 | 0.15439
| 8:16 | 10.1267 | 0.15443
| 8:16 | 10.1269 | 0.15447
| 8:16 | 10.1272 | 0.1545
| 8:16 | 10.1275 | 0.15454
| 8:16 | 10.1278 | 0.15458
| 8:16 | 10.1281 | 0.15462
| 8:16 | 10.1283 | 0.15466
| 8:17 | 10.1286 | 0.1547
| 8:17 | 10.1289 | 0.15474
| 8:17 | 10.1292 | 0.1548
| 8:17 | 10.1294 | 0.15487
| 8:17 | 10.1297 | 0.15497
| 8:17 | 10.13 | 0.15508
| 8:17 | 10.1303 | 0.1552
| 8:17 | 10.1306 | 0.15532
| 8:17 | 10.1308 | 0.15546
| 8:17 | 10.1311 | 0.15561
| 8:17 | 10.1314 | 0.15576
| 8:17 | 10.1317 | 0.15591
| 8:17 | 10.1319 | 0.15607
| 8:17 | 10.1322 | 0.15624
| 8:17 | 10.1325 | 0.1564
| 8:17 | 10.1328 | 0.15658
| 8:17 | 10.1331 | 0.15676
| 8:17 | 10.1333 | 0.15694
| 8:17 | 10.1336 | 0.15713
| 8:17 | 10.1339 | 0.15732
| 8:17 | 10.1342 | 0.1575
| 8:17 | 10.1344 | 0.15769
| 8:17 | 10.1347 | 0.15787
| 8:17 | 10.135 | 0.15805
| 8:17 | 10.1353 | 0.15823
| 8:17 | 10.1356 | 0.15841
| 8:17 | 10.1358 | 0.15858
| 8:17 | 10.1361 | 0.15875
| 8:17 | 10.1364 | 0.15892
| 8:17 | 10.1367 | 0.15908
| 8:17 | 10.1369 | 0.15923
| 8:17 | 10.1372 | 0.15936
| 8:17 | 10.1375 | 0.15949
| 8:17 | 10.1378 | 0.15962
| 8:17 | 10.1381 | 0.15975
| 8:17 | 10.1383 | 0.15988
| 8:17 | 10.1386 | 0.16001
| 8:17 | 10.1389 | 0.16014
| 8:17 | 10.1392 | 0.16028
| 8:17 | 10.1394 | 0.16042
| 8:17 | 10.1397 | 0.16057
| 8:17 | 10.14 | 0.16071
| 8:17 | 10.1403 | 0.16086
| 8:17 | 10.1406 | 0.16101
| 8:17 | 10.1408 | 0.16116
| 8:17 | 10.1411 | 0.16131
| 8:17 | 10.1414 | 0.16146
| 8:17 | 10.1417 | 0.16161
| 8:17 | 10.1419 | 0.16177
| 8:17 | 10.1422 | 0.16194
| 8:17 | 10.1425 | 0.1621
| 8:17 | 10.1428 | 0.16225
| 8:17 | 10.1431 | 0.1624
| 8:17 | 10.1433 | 0.16253
| 8:17 | 10.1436 | 0.16265
| 8:17 | 10.1439 | 0.16276
| 8:17 | 10.1442 | 0.16287
| 8:17 | 10.1444 | 0.16299
| 8:17 | 10.1447 | 0.16312
| 8:18 | 10.145 | 0.16325
| 8:18 | 10.1453 | 0.16338
| 8:18 | 10.1456 | 0.1635
| 8:18 | 10.1458 | 0.16362
| 8:18 | 10.1461 | 0.16373
| 8:18 | 10.1464 | 0.16385
| 8:18 | 10.1467 | 0.16396
| 8:18 | 10.1469 | 0.16406
| 8:18 | 10.1472 | 0.16416
| 8:18 | 10.1475 | 0.16424
| 8:18 | 10.1478 | 0.16432
| 8:18 | 10.1481 | 0.1644
| 8:18 | 10.1483 | 0.1645
| 8:18 | 10.1486 | 0.16461
| 8:18 | 10.1489 | 0.16472
| 8:18 | 10.1492 | 0.16485
| 8:18 | 10.1494 | 0.16498
| 8:18 | 10.1497 | 0.16513
| 8:18 | 10.15 | 0.16528
| 8:18 | 10.1503 | 0.16544
| 8:18 | 10.1506 | 0.16561
| 8:18 | 10.1508 | 0.16578
| 8:18 | 10.1511 | 0.16595
| 8:18 | 10.1514 | 0.16612
| 8:18 | 10.1517 | 0.16629
| 8:18 | 10.1519 | 0.16646
| 8:18 | 10.1522 | 0.16664
| 8:18 | 10.1525 | 0.16682
| 8:18 | 10.1528 | 0.16699
| 8:18 | 10.1531 | 0.16718
| 8:18 | 10.1533 | 0.16738
| 8:18 | 10.1536 | 0.16759
| 8:18 | 10.1539 | 0.16779
| 8:18 | 10.1542 | 0.16798
| 8:18 | 10.1544 | 0.16818
| 8:18 | 10.1547 | 0.16837
| 8:18 | 10.155 | 0.16855
| 8:18 | 10.1553 | 0.16874
| 8:18 | 10.1556 | 0.16892
| 8:18 | 10.1558 | 0.16907
| 8:18 | 10.1561 | 0.1692
| 8:18 | 10.1564 | 0.16934
| 8:18 | 10.1567 | 0.16947
| 8:18 | 10.1569 | 0.16961
| 8:18 | 10.1572 | 0.16975
| 8:18 | 10.1575 | 0.16988
| 8:18 | 10.1578 | 0.17002
| 8:18 | 10.1581 | 0.17016
| 8:18 | 10.1583 | 0.1703
| 8:18 | 10.1586 | 0.17042
| 8:18 | 10.1589 | 0.17051
| 8:18 | 10.1592 | 0.1706
| 8:18 | 10.1594 | 0.17069
| 8:18 | 10.1597 | 0.17077
| 8:18 | 10.16 | 0.17084
| 8:18 | 10.1603 | 0.1709
| 8:18 | 10.1606 | 0.17096
| 8:18 | 10.1608 | 0.17101
| 8:18 | 10.1611 | 0.17105
| 8:18 | 10.1614 | 0.17108
| 8:18 | 10.1617 | 0.17112
| 8:19 | 10.1619 | 0.17115
| 8:19 | 10.1622 | 0.17118
| 8:19 | 10.1625 | 0.1712
| 8:19 | 10.1628 | 0.17122
| 8:19 | 10.1631 | 0.17123
| 8:19 | 10.1633 | 0.17125
| 8:19 | 10.1636 | 0.17127
| 8:19 | 10.1639 | 0.17128
| 8:19 | 10.1642 | 0.17129
| 8:19 | 10.1644 | 0.17129
| 8:19 | 10.1647 | 0.17129
| 8:19 | 10.165 | 0.1713
| 8:19 | 10.1653 | 0.1713
| 8:19 | 10.1656 | 0.1713
| 8:19 | 10.1658 | 0.17131
| 8:19 | 10.1661 | 0.17131
| 8:19 | 10.1664 | 0.17131
| 8:19 | 10.1667 | 0.17132
| 8:19 | 10.1669 | 0.17132
| 8:19 | 10.1672 | 0.17132
| 8:19 | 10.1675 | 0.17133
| 8:19 | 10.1678 | 0.17134
| 8:19 | 10.1681 | 0.17136
| 8:19 | 10.1683 | 0.17138
| 8:19 | 10.1686 | 0.17139
| 8:19 | 10.1689 | 0.1714
| 8:19 | 10.1692 | 0.17141
| 8:19 | 10.1694 | 0.17142
| 8:19 | 10.1697 | 0.17143
| 8:19 | 10.17 | 0.17144
| 8:19 | 10.1703 | 0.17144
| 8:19 | 10.1706 | 0.17144
| 8:19 | 10.1708 | 0.17143
| 8:19 | 10.1711 | 0.17142
| 8:19 | 10.1714 | 0.1714
| 8:19 | 10.1717 | 0.17139
| 8:19 | 10.1719 | 0.17138
| 8:19 | 10.1722 | 0.17136
| 8:19 | 10.1725 | 0.17134
| 8:19 | 10.1728 | 0.17132
| 8:19 | 10.1731 | 0.17131
| 8:19 | 10.1733 | 0.17128
| 8:19 | 10.1736 | 0.17126
| 8:19 | 10.1739 | 0.17124
| 8:19 | 10.1742 | 0.17122
| 8:19 | 10.1744 | 0.17119
| 8:19 | 10.1747 | 0.17116
| 8:19 | 10.175 | 0.17114
| 8:19 | 10.1753 | 0.17111
| 8:19 | 10.1756 | 0.17108
| 8:19 | 10.1758 | 0.17106
| 8:19 | 10.1761 | 0.17103
| 8:19 | 10.1764 | 0.171
| 8:19 | 10.1767 | 0.17097
| 8:19 | 10.1769 | 0.17095
| 8:19 | 10.1772 | 0.17092
| 8:19 | 10.1775 | 0.1709
| 8:19 | 10.1778 | 0.17087
| 8:19 | 10.1781 | 0.17084
| 8:20 | 10.1783 | 0.17082
| 8:20 | 10.1786 | 0.17079
| 8:20 | 10.1789 | 0.17076
| 8:20 | 10.1792 | 0.17074
| 8:20 | 10.1794 | 0.17071
| 8:20 | 10.1797 | 0.17069
| 8:20 | 10.18 | 0.17066
| 8:20 | 10.1803 | 0.17064
| 8:20 | 10.1806 | 0.17061
| 8:20 | 10.1808 | 0.17059
| 8:20 | 10.1811 | 0.17056
| 8:20 | 10.1814 | 0.17054
| 8:20 | 10.1817 | 0.17051
| 8:20 | 10.1819 | 0.17049
| 8:20 | 10.1822 | 0.17047
| 8:20 | 10.1825 | 0.17045
| 8:20 | 10.1828 | 0.17043
| 8:20 | 10.1831 | 0.17042
| 8:20 | 10.1833 | 0.1704
| 8:20 | 10.1836 | 0.17039
| 8:20 | 10.1839 | 0.17037
| 8:20 | 10.1842 | 0.17036
| 8:20 | 10.1844 | 0.17034
| 8:20 | 10.1847 | 0.17033
| 8:20 | 10.185 | 0.17031
| 8:20 | 10.1853 | 0.17028
| 8:20 | 10.1856 | 0.17024
| 8:20 | 10.1858 | 0.17015
| 8:20 | 10.1861 | 0.17003
| 8:20 | 10.1864 | 0.16987
| 8:20 | 10.1867 | 0.16968
| 8:20 | 10.1869 | 0.1695
| 8:20 | 10.1872 | 0.16931
| 8:20 | 10.1875 | 0.16913
| 8:20 | 10.1878 | 0.16896
| 8:20 | 10.1881 | 0.16879
| 8:20 | 10.1883 | 0.16861
| 8:20 | 10.1886 | 0.16843
| 8:20 | 10.1889 | 0.16824
| 8:20 | 10.1892 | 0.16804
| 8:20 | 10.1894 | 0.16783
| 8:20 | 10.1897 | 0.16763
| 8:20 | 10.19 | 0.16743
| 8:20 | 10.1903 | 0.16724
| 8:20 | 10.1906 | 0.16705
| 8:20 | 10.1908 | 0.16687
| 8:20 | 10.1911 | 0.16669
| 8:20 | 10.1914 | 0.16652
| 8:20 | 10.1917 | 0.16634
| 8:20 | 10.1919 | 0.16615
| 8:20 | 10.1922 | 0.16596
| 8:20 | 10.1925 | 0.16575
| 8:20 | 10.1928 | 0.16551
| 8:20 | 10.1931 | 0.16527
| 8:20 | 10.1933 | 0.16502
| 8:20 | 10.1936 | 0.16476
| 8:20 | 10.1939 | 0.16448
| 8:20 | 10.1942 | 0.16417
| 8:20 | 10.1944 | 0.16381
| 8:20 | 10.1947 | 0.16341
| 8:20 | 10.195 | 0.16301
| 8:21 | 10.1953 | 0.1626
| 8:21 | 10.1956 | 0.1622
| 8:21 | 10.1958 | 0.16179
| 8:21 | 10.1961 | 0.16139
| 8:21 | 10.1964 | 0.16098
| 8:21 | 10.1967 | 0.16058
| 8:21 | 10.1969 | 0.16016
| 8:21 | 10.1972 | 0.15974
| 8:21 | 10.1975 | 0.1593
| 8:21 | 10.1978 | 0.15884
| 8:21 | 10.1981 | 0.15838
| 8:21 | 10.1983 | 0.15791
| 8:21 | 10.1986 | 0.15743
| 8:21 | 10.1989 | 0.15695
| 8:21 | 10.1992 | 0.15646
| 8:21 | 10.1994 | 0.15596
| 8:21 | 10.1997 | 0.15545
| 8:21 | 10.2 | 0.15494
| 8:21 | 10.2003 | 0.15442
| 8:21 | 10.2006 | 0.1539
| 8:21 | 10.2008 | 0.15338
| 8:21 | 10.2011 | 0.15286
| 8:21 | 10.2014 | 0.15234
| 8:21 | 10.2017 | 0.15182
| 8:21 | 10.2019 | 0.15131
| 8:21 | 10.2022 | 0.15079
| 8:21 | 10.2025 | 0.15027
| 8:21 | 10.2028 | 0.14976
| 8:21 | 10.2031 | 0.14924
| 8:21 | 10.2033 | 0.14872
| 8:21 | 10.2036 | 0.14821
| 8:21 | 10.2039 | 0.14769
| 8:21 | 10.2042 | 0.14718
| 8:21 | 10.2044 | 0.14667
| 8:21 | 10.2047 | 0.14615
| 8:21 | 10.205 | 0.14564
| 8:21 | 10.2053 | 0.14513
| 8:21 | 10.2056 | 0.14462
| 8:21 | 10.2058 | 0.1441
| 8:21 | 10.2061 | 0.14359
| 8:21 | 10.2064 | 0.14308
| 8:21 | 10.2067 | 0.14257
| 8:21 | 10.2069 | 0.14206
| 8:21 | 10.2072 | 0.14155
| 8:21 | 10.2075 | 0.14104
| 8:21 | 10.2078 | 0.14053
| 8:21 | 10.2081 | 0.14002
| 8:21 | 10.2083 | 0.13952
| 8:21 | 10.2086 | 0.13901
| 8:21 | 10.2089 | 0.1385
| 8:21 | 10.2092 | 0.13799
| 8:21 | 10.2094 | 0.13749
| 8:21 | 10.2097 | 0.13698
| 8:21 | 10.21 | 0.13648
| 8:21 | 10.2103 | 0.13597
| 8:21 | 10.2106 | 0.13547
| 8:21 | 10.2108 | 0.13496
| 8:21 | 10.2111 | 0.13446
| 8:21 | 10.2114 | 0.13395
| 8:22 | 10.2117 | 0.13345
| 8:22 | 10.2119 | 0.13295
| 8:22 | 10.2122 | 0.13245
| 8:22 | 10.2125 | 0.13194
| 8:22 | 10.2128 | 0.13144
| 8:22 | 10.2131 | 0.13096
| 8:22 | 10.2133 | 0.13049
| 8:22 | 10.2136 | 0.13003
| 8:22 | 10.2139 | 0.12958
| 8:22 | 10.2142 | 0.12912
| 8:22 | 10.2144 | 0.12867
| 8:22 | 10.2147 | 0.12821
| 8:22 | 10.215 | 0.12775
| 8:22 | 10.2153 | 0.12728
| 8:22 | 10.2156 | 0.12681
| 8:22 | 10.2158 | 0.12633
| 8:22 | 10.2161 | 0.12585
| 8:22 | 10.2164 | 0.12536
| 8:22 | 10.2167 | 0.12487
| 8:22 | 10.2169 | 0.12438
| 8:22 | 10.2172 | 0.12389
| 8:22 | 10.2175 | 0.1234
| 8:22 | 10.2178 | 0.12291
| 8:22 | 10.2181 | 0.12242
| 8:22 | 10.2183 | 0.12194
| 8:22 | 10.2186 | 0.12145
| 8:22 | 10.2189 | 0.12097
| 8:22 | 10.2192 | 0.12049
| 8:22 | 10.2194 | 0.12
| 8:22 | 10.2197 | 0.11953
| 8:22 | 10.22 | 0.11905
| 8:22 | 10.2203 | 0.11858
| 8:22 | 10.2206 | 0.11811
| 8:22 | 10.2208 | 0.11765
| 8:22 | 10.2211 | 0.11719
| 8:22 | 10.2214 | 0.11673
| 8:22 | 10.2217 | 0.11627
| 8:22 | 10.2219 | 0.11581
| 8:22 | 10.2222 | 0.11535
| 8:22 | 10.2225 | 0.1149
| 8:22 | 10.2228 | 0.11445
| 8:22 | 10.2231 | 0.11402
| 8:22 | 10.2233 | 0.11359
| 8:22 | 10.2236 | 0.11316
| 8:22 | 10.2239 | 0.11275
| 8:22 | 10.2242 | 0.11234
| 8:22 | 10.2244 | 0.11194
| 8:22 | 10.2247 | 0.11155
| 8:22 | 10.225 | 0.11116
| 8:22 | 10.2253 | 0.11076
| 8:22 | 10.2256 | 0.11037
| 8:22 | 10.2258 | 0.10997
| 8:22 | 10.2261 | 0.10958
| 8:22 | 10.2264 | 0.10918
| 8:22 | 10.2267 | 0.10878
| 8:22 | 10.2269 | 0.10838
| 8:22 | 10.2272 | 0.10797
| 8:22 | 10.2275 | 0.10757
| 8:22 | 10.2278 | 0.10716
| 8:22 | 10.2281 | 0.10675
| 8:22 | 10.2283 | 0.10634
| 8:23 | 10.2286 | 0.10593
| 8:23 | 10.2289 | 0.10552
| 8:23 | 10.2292 | 0.1051
| 8:23 | 10.2294 | 0.10469
| 8:23 | 10.2297 | 0.10427
| 8:23 | 10.23 | 0.10386
| 8:23 | 10.2303 | 0.10345
| 8:23 | 10.2306 | 0.10304
| 8:23 | 10.2308 | 0.10264
| 8:23 | 10.2311 | 0.10225
| 8:23 | 10.2314 | 0.10185
| 8:23 | 10.2317 | 0.10145
| 8:23 | 10.2319 | 0.10105
| 8:23 | 10.2322 | 0.10064
| 8:23 | 10.2325 | 0.10022
| 8:23 | 10.2328 | 0.099805
| 8:23 | 10.2331 | 0.09938
| 8:23 | 10.2333 | 0.098951
| 8:23 | 10.2336 | 0.098516
| 8:23 | 10.2339 | 0.098079
| 8:23 | 10.2342 | 0.097643
| 8:23 | 10.2344 | 0.097209
| 8:23 | 10.2347 | 0.096777
| 8:23 | 10.235 | 0.096347
| 8:23 | 10.2353 | 0.09592
| 8:23 | 10.2356 | 0.095501
| 8:23 | 10.2358 | 0.09509
| 8:23 | 10.2361 | 0.094694
| 8:23 | 10.2364 | 0.094307
| 8:23 | 10.2367 | 0.093929
| 8:23 | 10.2369 | 0.093566
| 8:23 | 10.2372 | 0.093217
| 8:23 | 10.2375 | 0.092885
| 8:23 | 10.2378 | 0.092575
| 8:23 | 10.2381 | 0.092286
| 8:23 | 10.2383 | 0.09202
| 8:23 | 10.2386 | 0.091774
| 8:23 | 10.2389 | 0.091536
| 8:23 | 10.2392 | 0.091315
| 8:23 | 10.2394 | 0.091115
| 8:23 | 10.2397 | 0.090928
| 8:23 | 10.24 | 0.090754
| 8:23 | 10.2403 | 0.090593
| 8:23 | 10.2406 | 0.090444
| 8:23 | 10.2408 | 0.090308
| 8:23 | 10.2411 | 0.090185
| 8:23 | 10.2414 | 0.090075
| 8:23 | 10.2417 | 0.089973
| 8:23 | 10.2419 | 0.089879
| 8:23 | 10.2422 | 0.089793
| 8:23 | 10.2425 | 0.089716
| 8:23 | 10.2428 | 0.089653
| 8:23 | 10.2431 | 0.089606
| 8:23 | 10.2433 | 0.089578
| 8:23 | 10.2436 | 0.089571
| 8:23 | 10.2439 | 0.089584
| 8:23 | 10.2442 | 0.089615
| 8:23 | 10.2444 | 0.08967
| 8:23 | 10.2447 | 0.089733
| 8:23 | 10.245 | 0.089816
| 8:24 | 10.2453 | 0.089907
| 8:24 | 10.2456 | 0.090004
| 8:24 | 10.2458 | 0.090099
| 8:24 | 10.2461 | 0.090179
| 8:24 | 10.2464 | 0.09025
| 8:24 | 10.2467 | 0.090306
| 8:24 | 10.2469 | 0.090353
| 8:24 | 10.2472 | 0.090392
| 8:24 | 10.2475 | 0.090431
| 8:24 | 10.2478 | 0.09047
| 8:24 | 10.2481 | 0.090512
| 8:24 | 10.2483 | 0.090558
| 8:24 | 10.2486 | 0.090606
| 8:24 | 10.2489 | 0.090655
| 8:24 | 10.2492 | 0.090705
| 8:24 | 10.2494 | 0.090757
| 8:24 | 10.2497 | 0.090811
| 8:24 | 10.25 | 0.090866
| 8:24 | 10.2503 | 0.090923
| 8:24 | 10.2506 | 0.090981
| 8:24 | 10.2508 | 0.091041
| 8:24 | 10.2511 | 0.091107
| 8:24 | 10.2514 | 0.09118
| 8:24 | 10.2517 | 0.091258
| 8:24 | 10.2519 | 0.091341
| 8:24 | 10.2522 | 0.091428
| 8:24 | 10.2525 | 0.09152
| 8:24 | 10.2528 | 0.091625
| 8:24 | 10.2531 | 0.091742
| 8:24 | 10.2533 | 0.091868
| 8:24 | 10.2536 | 0.092002
| 8:24 | 10.2539 | 0.09214
| 8:24 | 10.2542 | 0.092287
| 8:24 | 10.2544 | 0.092438
| 8:24 | 10.2547 | 0.092591
| 8:24 | 10.255 | 0.092746
| 8:24 | 10.2553 | 0.092903
| 8:24 | 10.2556 | 0.093062
| 8:24 | 10.2558 | 0.093221
| 8:24 | 10.2561 | 0.093378
| 8:24 | 10.2564 | 0.093532
| 8:24 | 10.2567 | 0.093683
| 8:24 | 10.2569 | 0.093829
| 8:24 | 10.2572 | 0.093973
| 8:24 | 10.2575 | 0.094112
| 8:24 | 10.2578 | 0.094248
| 8:24 | 10.2581 | 0.094381
| 8:24 | 10.2583 | 0.094511
| 8:24 | 10.2586 | 0.094641
| 8:24 | 10.2589 | 0.094772
| 8:24 | 10.2592 | 0.094904
| 8:24 | 10.2594 | 0.095036
| 8:24 | 10.2597 | 0.095168
| 8:24 | 10.26 | 0.095301
| 8:24 | 10.2603 | 0.095436
| 8:24 | 10.2606 | 0.095575
| 8:24 | 10.2608 | 0.095718
| 8:24 | 10.2611 | 0.095862
| 8:24 | 10.2614 | 0.096005
| 8:24 | 10.2617 | 0.096138
| 8:25 | 10.2619 | 0.096267
| 8:25 | 10.2622 | 0.096385
| 8:25 | 10.2625 | 0.096492
| 8:25 | 10.2628 | 0.096599
| 8:25 | 10.2631 | 0.096708
| 8:25 | 10.2633 | 0.096814
| 8:25 | 10.2636 | 0.096931
| 8:25 | 10.2639 | 0.097058
| 8:25 | 10.2642 | 0.097184
| 8:25 | 10.2644 | 0.097312
| 8:25 | 10.2647 | 0.097432
| 8:25 | 10.265 | 0.097546
| 8:25 | 10.2653 | 0.097652
| 8:25 | 10.2656 | 0.097751
| 8:25 | 10.2658 | 0.097843
| 8:25 | 10.2661 | 0.097927
| 8:25 | 10.2664 | 0.098004
| 8:25 | 10.2667 | 0.098075
| 8:25 | 10.2669 | 0.098139
| 8:25 | 10.2672 | 0.098201
| 8:25 | 10.2675 | 0.098254
| 8:25 | 10.2678 | 0.098297
| 8:25 | 10.2681 | 0.098337
| 8:25 | 10.2683 | 0.098365
| 8:25 | 10.2686 | 0.098386
| 8:25 | 10.2689 | 0.098406
| 8:25 | 10.2692 | 0.098411
| 8:25 | 10.2694 | 0.098426
| 8:25 | 10.2697 | 0.098439
| 8:25 | 10.27 | 0.098449
| 8:25 | 10.2703 | 0.098455
| 8:25 | 10.2706 | 0.098437
| 8:25 | 10.2708 | 0.098409
| 8:25 | 10.2711 | 0.098334
| 8:25 | 10.2714 | 0.098221
| 8:25 | 10.2717 | 0.098085
| 8:25 | 10.2719 | 0.097937
| 8:25 | 10.2722 | 0.097767
| 8:25 | 10.2725 | 0.097628
| 8:25 | 10.2728 | 0.097521
| 8:25 | 10.2731 | 0.097444
| 8:25 | 10.2733 | 0.097396
| 8:25 | 10.2736 | 0.097377
| 8:25 | 10.2739 | 0.097387
| 8:25 | 10.2742 | 0.097427
| 8:25 | 10.2744 | 0.097497
| 8:25 | 10.2747 | 0.097593
| 8:25 | 10.275 | 0.097721
| 8:25 | 10.2753 | 0.097858
| 8:25 | 10.2756 | 0.097986
| 8:25 | 10.2758 | 0.098104
| 8:25 | 10.2761 | 0.098212
| 8:25 | 10.2764 | 0.098303
| 8:25 | 10.2767 | 0.098383
| 8:25 | 10.2769 | 0.098451
| 8:25 | 10.2772 | 0.098496
| 8:25 | 10.2775 | 0.098524
| 8:25 | 10.2778 | 0.098534
| 8:25 | 10.2781 | 0.098532
| 8:25 | 10.2783 | 0.09851
| 8:26 | 10.2786 | 0.098466
| 8:26 | 10.2789 | 0.098407
| 8:26 | 10.2792 | 0.098338
| 8:26 | 10.2794 | 0.09826
| 8:26 | 10.2797 | 0.098181
| 8:26 | 10.28 | 0.098099
| 8:26 | 10.2803 | 0.098
| 8:26 | 10.2806 | 0.0979
| 8:26 | 10.2808 | 0.097801
| 8:26 | 10.2811 | 0.097701
| 8:26 | 10.2814 | 0.097609
| 8:26 | 10.2817 | 0.097528
| 8:26 | 10.2819 | 0.097456
| 8:26 | 10.2822 | 0.097395
| 8:26 | 10.2825 | 0.097343
| 8:26 | 10.2828 | 0.097301
| 8:26 | 10.2831 | 0.097269
| 8:26 | 10.2833 | 0.097247
| 8:26 | 10.2836 | 0.097238
| 8:26 | 10.2839 | 0.097243
| 8:26 | 10.2842 | 0.097252
| 8:26 | 10.2844 | 0.097264
| 8:26 | 10.2847 | 0.097278
| 8:26 | 10.285 | 0.097294
| 8:26 | 10.2853 | 0.097313
| 8:26 | 10.2856 | 0.097335
| 8:26 | 10.2858 | 0.097358
| 8:26 | 10.2861 | 0.097385
| 8:26 | 10.2864 | 0.097414
| 8:26 | 10.2867 | 0.097445
| 8:26 | 10.2869 | 0.097479
| 8:26 | 10.2872 | 0.097515
| 8:26 | 10.2875 | 0.097554
| 8:26 | 10.2878 | 0.097596
| 8:26 | 10.2881 | 0.09764
| 8:26 | 10.2883 | 0.097686
| 8:26 | 10.2886 | 0.097736
| 8:26 | 10.2889 | 0.097795
| 8:26 | 10.2892 | 0.097861
| 8:26 | 10.2894 | 0.097937
| 8:26 | 10.2897 | 0.09802
| 8:26 | 10.29 | 0.098109
| 8:26 | 10.2903 | 0.098203
| 8:26 | 10.2906 | 0.098304
| 8:26 | 10.2908 | 0.098411
| 8:26 | 10.2911 | 0.098524
| 8:26 | 10.2914 | 0.098642
| 8:26 | 10.2917 | 0.098763
| 8:26 | 10.2919 | 0.098883
| 8:26 | 10.2922 | 0.099001
| 8:26 | 10.2925 | 0.099118
| 8:26 | 10.2928 | 0.099234
| 8:26 | 10.2931 | 0.099349
| 8:26 | 10.2933 | 0.099462
| 8:26 | 10.2936 | 0.099574
| 8:26 | 10.2939 | 0.099685
| 8:26 | 10.2942 | 0.099795
| 8:26 | 10.2944 | 0.099902
| 8:26 | 10.2947 | 0.10001
| 8:27 | 10.295 | 0.1001
| 8:27 | 10.2953 | 0.1002
| 8:27 | 10.2956 | 0.10028
| 8:27 | 10.2958 | 0.10037
| 8:27 | 10.2961 | 0.10046
| 8:27 | 10.2964 | 0.10055
| 8:27 | 10.2967 | 0.10064
| 8:27 | 10.2969 | 0.10074
| 8:27 | 10.2972 | 0.10084
| 8:27 | 10.2975 | 0.10094
| 8:27 | 10.2978 | 0.10105
| 8:27 | 10.2981 | 0.10117
| 8:27 | 10.2983 | 0.10129
| 8:27 | 10.2986 | 0.10141
| 8:27 | 10.2989 | 0.10155
| 8:27 | 10.2992 | 0.10168
| 8:27 | 10.2994 | 0.10183
| 8:27 | 10.2997 | 0.10198
| 8:27 | 10.3 | 0.10213
| 8:27 | 10.3003 | 0.10229
| 8:27 | 10.3006 | 0.10246
| 8:27 | 10.3008 | 0.10263
| 8:27 | 10.3011 | 0.1028
| 8:27 | 10.3014 | 0.10299
| 8:27 | 10.3017 | 0.10317
| 8:27 | 10.3019 | 0.10336
| 8:27 | 10.3022 | 0.10355
| 8:27 | 10.3025 | 0.10374
| 8:27 | 10.3028 | 0.10393
| 8:27 | 10.3031 | 0.10412
| 8:27 | 10.3033 | 0.1043
| 8:27 | 10.3036 | 0.10448
| 8:27 | 10.3039 | 0.10467
| 8:27 | 10.3042 | 0.10485
| 8:27 | 10.3044 | 0.10503
| 8:27 | 10.3047 | 0.10522
| 8:27 | 10.305 | 0.10541
| 8:27 | 10.3053 | 0.10559
| 8:27 | 10.3056 | 0.10577
| 8:27 | 10.3058 | 0.10594
| 8:27 | 10.3061 | 0.10611
| 8:27 | 10.3064 | 0.10628
| 8:27 | 10.3067 | 0.10647
| 8:27 | 10.3069 | 0.10665
| 8:27 | 10.3072 | 0.10684
| 8:27 | 10.3075 | 0.10704
| 8:27 | 10.3078 | 0.10724
| 8:27 | 10.3081 | 0.10744
| 8:27 | 10.3083 | 0.10765
| 8:27 | 10.3086 | 0.10784
| 8:27 | 10.3089 | 0.10801
| 8:27 | 10.3092 | 0.10818
| 8:27 | 10.3094 | 0.10833
| 8:27 | 10.3097 | 0.10846
| 8:27 | 10.31 | 0.10856
| 8:27 | 10.3103 | 0.10865
| 8:27 | 10.3106 | 0.10872
| 8:27 | 10.3108 | 0.1088
| 8:27 | 10.3111 | 0.10891
| 8:27 | 10.3114 | 0.10904
| 8:28 | 10.3117 | 0.1092
| 8:28 | 10.3119 | 0.1094
| 8:28 | 10.3122 | 0.10961
| 8:28 | 10.3125 | 0.10985
| 8:28 | 10.3128 | 0.11009
| 8:28 | 10.3131 | 0.11035
| 8:28 | 10.3133 | 0.11062
| 8:28 | 10.3136 | 0.11088
| 8:28 | 10.3139 | 0.11116
| 8:28 | 10.3142 | 0.11142
| 8:28 | 10.3144 | 0.11168
| 8:28 | 10.3147 | 0.11192
| 8:28 | 10.315 | 0.11216
| 8:28 | 10.3153 | 0.11238
| 8:28 | 10.3156 | 0.1126
| 8:28 | 10.3158 | 0.1128
| 8:28 | 10.3161 | 0.113
| 8:28 | 10.3164 | 0.11319
| 8:28 | 10.3167 | 0.11336
| 8:28 | 10.3169 | 0.11353
| 8:28 | 10.3172 | 0.11369
| 8:28 | 10.3175 | 0.11383
| 8:28 | 10.3178 | 0.11398
| 8:28 | 10.3181 | 0.11411
| 8:28 | 10.3183 | 0.11422
| 8:28 | 10.3186 | 0.11431
| 8:28 | 10.3189 | 0.11438
| 8:28 | 10.3192 | 0.11442
| 8:28 | 10.3194 | 0.11445
| 8:28 | 10.3197 | 0.11447
| 8:28 | 10.32 | 0.1145
| 8:28 | 10.3203 | 0.11452
| 8:28 | 10.3206 | 0.11458
| 8:28 | 10.3208 | 0.11467
| 8:28 | 10.3211 | 0.11478
| 8:28 | 10.3214 | 0.11491
| 8:28 | 10.3217 | 0.11506
| 8:28 | 10.3219 | 0.11521
| 8:28 | 10.3222 | 0.11537
| 8:28 | 10.3225 | 0.11555
| 8:28 | 10.3228 | 0.11573
| 8:28 | 10.3231 | 0.1159
| 8:28 | 10.3233 | 0.11607
| 8:28 | 10.3236 | 0.11623
| 8:28 | 10.3239 | 0.11638
| 8:28 | 10.3242 | 0.11653
| 8:28 | 10.3244 | 0.11667
| 8:28 | 10.3247 | 0.1168
| 8:28 | 10.325 | 0.11695
| 8:28 | 10.3253 | 0.11711
| 8:28 | 10.3256 | 0.11726
| 8:28 | 10.3258 | 0.11739
| 8:28 | 10.3261 | 0.11751
| 8:28 | 10.3264 | 0.11761
| 8:28 | 10.3267 | 0.11767
| 8:28 | 10.3269 | 0.11771
| 8:28 | 10.3272 | 0.11774
| 8:28 | 10.3275 | 0.11773
| 8:28 | 10.3278 | 0.11771
| 8:28 | 10.3281 | 0.11765
| 8:29 | 10.3283 | 0.11758
| 8:29 | 10.3286 | 0.11749
| 8:29 | 10.3289 | 0.1174
| 8:29 | 10.3292 | 0.1173
| 8:29 | 10.3294 | 0.11717
| 8:29 | 10.3297 | 0.11701
| 8:29 | 10.33 | 0.11684
| 8:29 | 10.3303 | 0.11665
| 8:29 | 10.3306 | 0.11644
| 8:29 | 10.3308 | 0.11622
| 8:29 | 10.3311 | 0.11599
| 8:29 | 10.3314 | 0.11575
| 8:29 | 10.3317 | 0.1155
| 8:29 | 10.3319 | 0.11523
| 8:29 | 10.3322 | 0.11496
| 8:29 | 10.3325 | 0.11467
| 8:29 | 10.3328 | 0.11438
| 8:29 | 10.3331 | 0.11407
| 8:29 | 10.3333 | 0.11375
| 8:29 | 10.3336 | 0.11342
| 8:29 | 10.3339 | 0.11309
| 8:29 | 10.3342 | 0.11276
| 8:29 | 10.3344 | 0.11244
| 8:29 | 10.3347 | 0.11211
| 8:29 | 10.335 | 0.11179
| 8:29 | 10.3353 | 0.11148
| 8:29 | 10.3356 | 0.11117
| 8:29 | 10.3358 | 0.11086
| 8:29 | 10.3361 | 0.11054
| 8:29 | 10.3364 | 0.11021
| 8:29 | 10.3367 | 0.10987
| 8:29 | 10.3369 | 0.1095
| 8:29 | 10.3372 | 0.10912
| 8:29 | 10.3375 | 0.10871
| 8:29 | 10.3378 | 0.1083
| 8:29 | 10.3381 | 0.10787
| 8:29 | 10.3383 | 0.1074
| 8:29 | 10.3386 | 0.10694
| 8:29 | 10.3389 | 0.10646
| 8:29 | 10.3392 | 0.10598
| 8:29 | 10.3394 | 0.1055
| 8:29 | 10.3397 | 0.10501
| 8:29 | 10.34 | 0.10452
| 8:29 | 10.3403 | 0.10402
| 8:29 | 10.3406 | 0.10351
| 8:29 | 10.3408 | 0.103
| 8:29 | 10.3411 | 0.10248
| 8:29 | 10.3414 | 0.10196
| 8:29 | 10.3417 | 0.10144
| 8:29 | 10.3419 | 0.10091
| 8:29 | 10.3422 | 0.10039
| 8:29 | 10.3425 | 0.099857
| 8:29 | 10.3428 | 0.099324
| 8:29 | 10.3431 | 0.09879
| 8:29 | 10.3433 | 0.098253
| 8:29 | 10.3436 | 0.097714
| 8:29 | 10.3439 | 0.097173
| 8:29 | 10.3442 | 0.09663
| 8:29 | 10.3444 | 0.096084
| 8:29 | 10.3447 | 0.095536
| 8:30 | 10.345 | 0.094985
| 8:30 | 10.3453 | 0.094432
| 8:30 | 10.3456 | 0.093877
| 8:30 | 10.3458 | 0.093319
| 8:30 | 10.3461 | 0.092759
| 8:30 | 10.3464 | 0.092198
| 8:30 | 10.3467 | 0.091637
| 8:30 | 10.3469 | 0.091076
| 8:30 | 10.3472 | 0.090516
| 8:30 | 10.3475 | 0.089956
| 8:30 | 10.3478 | 0.089396
| 8:30 | 10.3481 | 0.088838
| 8:30 | 10.3483 | 0.088279
| 8:30 | 10.3486 | 0.087721
| 8:30 | 10.3489 | 0.087164
| 8:30 | 10.3492 | 0.086607
| 8:30 | 10.3494 | 0.08605
| 8:30 | 10.3497 | 0.085494
| 8:30 | 10.35 | 0.084939
| 8:30 | 10.3503 | 0.084384
| 8:30 | 10.3506 | 0.083829
| 8:30 | 10.3508 | 0.083275
| 8:30 | 10.3511 | 0.082722
| 8:30 | 10.3514 | 0.082168
| 8:30 | 10.3517 | 0.081616
| 8:30 | 10.3519 | 0.081064
| 8:30 | 10.3522 | 0.080512
| 8:30 | 10.3525 | 0.079961
| 8:30 | 10.3528 | 0.07941
| 8:30 | 10.3531 | 0.078859
| 8:30 | 10.3533 | 0.07831
| 8:30 | 10.3536 | 0.07776
| 8:30 | 10.3539 | 0.077211
| 8:30 | 10.3542 | 0.076663
| 8:30 | 10.3544 | 0.076115
| 8:30 | 10.3547 | 0.075567
| 8:30 | 10.355 | 0.07502
| 8:30 | 10.3553 | 0.074474
| 8:30 | 10.3556 | 0.073928
| 8:30 | 10.3558 | 0.073382
| 8:30 | 10.3561 | 0.072837
| 8:30 | 10.3564 | 0.072292
| 8:30 | 10.3567 | 0.071748
| 8:30 | 10.3569 | 0.071204
| 8:30 | 10.3572 | 0.070661
| 8:30 | 10.3575 | 0.070118
| 8:30 | 10.3578 | 0.069576
| 8:30 | 10.3581 | 0.069034
| 8:30 | 10.3583 | 0.068493
| 8:30 | 10.3586 | 0.067952
| 8:30 | 10.3589 | 0.067411
| 8:30 | 10.3592 | 0.066871
| 8:30 | 10.3594 | 0.066332
| 8:30 | 10.3597 | 0.065793
| 8:30 | 10.36 | 0.065254
| 8:30 | 10.3603 | 0.064716
| 8:30 | 10.3606 | 0.064178
| 8:30 | 10.3608 | 0.063641
| 8:30 | 10.3611 | 0.063104
| 8:30 | 10.3614 | 0.062568
| 8:30 | 10.3617 | 0.062032
| 8:31 | 10.3619 | 0.061497
| 8:31 | 10.3622 | 0.060962
| 8:31 | 10.3625 | 0.060428
| 8:31 | 10.3628 | 0.059894
| 8:31 | 10.3631 | 0.05936
| 8:31 | 10.3633 | 0.058827
| 8:31 | 10.3636 | 0.058295
| 8:31 | 10.3639 | 0.057763
| 8:31 | 10.3642 | 0.057231
| 8:31 | 10.3644 | 0.0567
| 8:31 | 10.3647 | 0.056169
| 8:31 | 10.365 | 0.055639
| 8:31 | 10.3653 | 0.055109
| 8:31 | 10.3656 | 0.05458
| 8:31 | 10.3658 | 0.054051
| 8:31 | 10.3661 | 0.053523
| 8:31 | 10.3664 | 0.052995
| 8:31 | 10.3667 | 0.052467
| 8:31 | 10.3669 | 0.05194
| 8:31 | 10.3672 | 0.051414
| 8:31 | 10.3675 | 0.050888
| 8:31 | 10.3678 | 0.050362
| 8:31 | 10.3681 | 0.049837
| 8:31 | 10.3683 | 0.049313
| 8:31 | 10.3686 | 0.048788
| 8:31 | 10.3689 | 0.048265
| 8:31 | 10.3692 | 0.047742
| 8:31 | 10.3694 | 0.047219
| 8:31 | 10.3697 | 0.046698
| 8:31 | 10.37 | 0.046177
| 8:31 | 10.3703 | 0.045657
| 8:31 | 10.3706 | 0.045137
| 8:31 | 10.3708 | 0.044619
| 8:31 | 10.3711 | 0.044101
| 8:31 | 10.3714 | 0.043584
| 8:31 | 10.3717 | 0.043068
| 8:31 | 10.3719 | 0.042552
| 8:31 | 10.3722 | 0.042038
| 8:31 | 10.3725 | 0.041524
| 8:31 | 10.3728 | 0.041011
| 8:31 | 10.3731 | 0.040498
| 8:31 | 10.3733 | 0.039987
| 8:31 | 10.3736 | 0.039476
| 8:31 | 10.3739 | 0.038966
| 8:31 | 10.3742 | 0.038456
| 8:31 | 10.3744 | 0.037948
| 8:31 | 10.3747 | 0.03744
| 8:31 | 10.375 | 0.036933
| 8:31 | 10.3753 | 0.036427
| 8:31 | 10.3756 | 0.035921
| 8:31 | 10.3758 | 0.035416
| 8:31 | 10.3761 | 0.034912
| 8:31 | 10.3764 | 0.034409
| 8:31 | 10.3767 | 0.033907
| 8:31 | 10.3769 | 0.033405
| 8:31 | 10.3772 | 0.032904
| 8:31 | 10.3775 | 0.032404
| 8:31 | 10.3778 | 0.031905
| 8:31 | 10.3781 | 0.031406
| 8:32 | 10.3783 | 0.030908
| 8:32 | 10.3786 | 0.030411
| 8:32 | 10.3789 | 0.029914
| 8:32 | 10.3792 | 0.029419
| 8:32 | 10.3794 | 0.028924
| 8:32 | 10.3797 | 0.02843
| 8:32 | 10.38 | 0.027936
| 8:32 | 10.3803 | 0.027444
| 8:32 | 10.3806 | 0.026952
| 8:32 | 10.3808 | 0.026461
| 8:32 | 10.3811 | 0.025971
| 8:32 | 10.3814 | 0.025482
| 8:32 | 10.3817 | 0.024996
| 8:32 | 10.3819 | 0.024511
| 8:32 | 10.3822 | 0.024029
| 8:32 | 10.3825 | 0.023548
| 8:32 | 10.3828 | 0.02307
| 8:32 | 10.3831 | 0.022594
| 8:32 | 10.3833 | 0.022119
| 8:32 | 10.3836 | 0.021647
| 8:32 | 10.3839 | 0.021176
| 8:32 | 10.3842 | 0.020707
| 8:32 | 10.3844 | 0.020239
| 8:32 | 10.3847 | 0.019772
| 8:32 | 10.385 | 0.019306
| 8:32 | 10.3853 | 0.018841
| 8:32 | 10.3856 | 0.018377
| 8:32 | 10.3858 | 0.017915
| 8:32 | 10.3861 | 0.017453
| 8:32 | 10.3864 | 0.016992
| 8:32 | 10.3867 | 0.016534
| 8:32 | 10.3869 | 0.016078
| 8:32 | 10.3872 | 0.015626
| 8:32 | 10.3875 | 0.015176
| 8:32 | 10.3878 | 0.014729
| 8:32 | 10.3881 | 0.014286
| 8:32 | 10.3883 | 0.013845
| 8:32 | 10.3886 | 0.013406
| 8:32 | 10.3889 | 0.012971
| 8:32 | 10.3892 | 0.012539
| 8:32 | 10.3894 | 0.012111
| 8:32 | 10.3897 | 0.011695
| 8:32 | 10.39 | 0.011291
| 8:32 | 10.3903 | 0.010898
| 8:32 | 10.3906 | 0.010518
| 8:32 | 10.3908 | 0.010148
| 8:32 | 10.3911 | 0.0097906
| 8:32 | 10.3914 | 0.0094447
| 8:32 | 10.3917 | 0.0091104
| 8:32 | 10.3919 | 0.0087852
| 8:32 | 10.3922 | 0.0084597
| 8:32 | 10.3925 | 0.0081364
| 8:32 | 10.3928 | 0.0078151
| 8:32 | 10.3931 | 0.0074958
| 8:32 | 10.3933 | 0.0071786
| 8:32 | 10.3936 | 0.0068635
| 8:32 | 10.3939 | 0.0065484
| 8:32 | 10.3942 | 0.0062334
| 8:32 | 10.3944 | 0.0059183
| 8:32 | 10.3947 | 0.0056033
| 8:32 | 10.395 | 0.0052883
| 8:33 | 10.3953 | 0.0049733
| 8:33 | 10.3956 | 0.0046583
| 8:33 | 10.3958 | 0.0043433
| 8:33 | 10.3961 | 0.0040284
| 8:33 | 10.3964 | 0.0037136
| 8:33 | 10.3967 | 0.0034001
| 8:33 | 10.3969 | 0.0030879
| 8:33 | 10.3972 | 0.002777
| 8:33 | 10.3975 | 0.0024726
| 8:33 | 10.3978 | 0.0021752
| 8:33 | 10.3981 | 0.0018757
| 8:33 | 10.3983 | 0.0015735
| 8:33 | 10.3986 | 0.0012685
| 8:33 | 10.3989 | 0.00096075
| 8:33 | 10.3992 | 0.00065025
| 8:33 | 10.3994 | 0.00033699
| 8:33 | 10.3997 | 2.0973e-05
| 8:33 | 10.4 | -0.00029781
| 8:33 | 10.4003 | -0.00061935
| 8:33 | 10.4006 | -0.00094253
| 8:33 | 10.4008 | -0.0012658
| 8:33 | 10.4011 | -0.0015891
| 8:33 | 10.4014 | -0.0019124
| 8:33 | 10.4017 | -0.0022359
| 8:33 | 10.4019 | -0.0025593
| 8:33 | 10.4022 | -0.0028829
| 8:33 | 10.4025 | -0.0032065
| 8:33 | 10.4028 | -0.0035302
| 8:33 | 10.4031 | -0.0038539
| 8:33 | 10.4033 | -0.0041777
| 8:33 | 10.4036 | -0.0045015
| 8:33 | 10.4039 | -0.0048254
| 8:33 | 10.4042 | -0.0051494
| 8:33 | 10.4044 | -0.0054642
| 8:33 | 10.4047 | -0.0057697
| 8:33 | 10.405 | -0.006066
| 8:33 | 10.4053 | -0.0063582
| 8:33 | 10.4056 | -0.0066464
| 8:33 | 10.4058 | -0.0069306
| 8:33 | 10.4061 | -0.0072074
| 8:33 | 10.4064 | -0.007487
| 8:33 | 10.4067 | -0.0077698
| 8:33 | 10.4069 | -0.0080561
| 8:33 | 10.4072 | -0.0083456
| 8:33 | 10.4075 | -0.0086385
| 8:33 | 10.4078 | -0.0089348
| 8:33 | 10.4081 | -0.0092348
| 8:33 | 10.4083 | -0.0095387
| 8:33 | 10.4086 | -0.0098447
| 8:33 | 10.4089 | -0.010153
| 8:33 | 10.4092 | -0.010463
| 8:33 | 10.4094 | -0.010776
| 8:33 | 10.4097 | -0.011084
| 8:33 | 10.41 | -0.011383
| 8:33 | 10.4103 | -0.011674
| 8:33 | 10.4106 | -0.011956
| 8:33 | 10.4108 | -0.012234
| 8:33 | 10.4111 | -0.012513
| 8:33 | 10.4114 | -0.01279
| 8:34 | 10.4117 | -0.013068
| 8:34 | 10.4119 | -0.013345
| 8:34 | 10.4122 | -0.01362
| 8:34 | 10.4125 | -0.013894
| 8:34 | 10.4128 | -0.014172
| 8:34 | 10.4131 | -0.014453
| 8:34 | 10.4133 | -0.014738
| 8:34 | 10.4136 | -0.015022
| 8:34 | 10.4139 | -0.015304
| 8:34 | 10.4142 | -0.015583
| 8:34 | 10.4144 | -0.015859
| 8:34 | 10.4147 | -0.016132
| 8:34 | 10.415 | -0.016403
| 8:34 | 10.4153 | -0.016671
| 8:34 | 10.4156 | -0.016936
| 8:34 | 10.4158 | -0.017199
| 8:34 | 10.4161 | -0.017458
| 8:34 | 10.4164 | -0.017715
| 8:34 | 10.4167 | -0.01797
| 8:34 | 10.4169 | -0.01822
| 8:34 | 10.4172 | -0.018469
| 8:34 | 10.4175 | -0.018722
| 8:34 | 10.4178 | -0.018981
| 8:34 | 10.4181 | -0.019251
| 8:34 | 10.4183 | -0.019523
| 8:34 | 10.4186 | -0.019795
| 8:34 | 10.4189 | -0.020065
| 8:34 | 10.4192 | -0.020335
| 8:34 | 10.4194 | -0.020603
| 8:34 | 10.4197 | -0.02087
| 8:34 | 10.42 | -0.021136
| 8:34 | 10.4203 | -0.021401
| 8:34 | 10.4206 | -0.021665
| 8:34 | 10.4208 | -0.021928
| 8:34 | 10.4211 | -0.022189
| 8:34 | 10.4214 | -0.02245
| 8:34 | 10.4217 | -0.022705
| 8:34 | 10.4219 | -0.022955
| 8:34 | 10.4222 | -0.023196
| 8:34 | 10.4225 | -0.02343
| 8:34 | 10.4228 | -0.023663
| 8:34 | 10.4231 | -0.023896
| 8:34 | 10.4233 | -0.024127
| 8:34 | 10.4236 | -0.024357
| 8:34 | 10.4239 | -0.024586
| 8:34 | 10.4242 | -0.024814
| 8:34 | 10.4244 | -0.025041
| 8:34 | 10.4247 | -0.025267
| 8:34 | 10.425 | -0.025492
| 8:34 | 10.4253 | -0.025716
| 8:34 | 10.4256 | -0.025939
| 8:34 | 10.4258 | -0.02616
| 8:34 | 10.4261 | -0.026381
| 8:34 | 10.4264 | -0.0266
| 8:34 | 10.4267 | -0.026819
| 8:34 | 10.4269 | -0.027036
| 8:34 | 10.4272 | -0.027251
| 8:34 | 10.4275 | -0.027457
| 8:34 | 10.4278 | -0.027652
| 8:34 | 10.4281 | -0.027839
| 8:34 | 10.4283 | -0.028003
| 8:35 | 10.4286 | -0.028148
| 8:35 | 10.4289 | -0.028272
| 8:35 | 10.4292 | -0.028371
| 8:35 | 10.4294 | -0.028452
| 8:35 | 10.4297 | -0.028517
| 8:35 | 10.43 | -0.02858
| 8:35 | 10.4303 | -0.028645
| 8:35 | 10.4306 | -0.028711
| 8:35 | 10.4308 | -0.028797
| 8:35 | 10.4311 | -0.028918
| 8:35 | 10.4314 | -0.029055
| 8:35 | 10.4317 | -0.029207
| 8:35 | 10.4319 | -0.029373
| 8:35 | 10.4322 | -0.029554
| 8:35 | 10.4325 | -0.029749
| 8:35 | 10.4328 | -0.029959
| 8:35 | 10.4331 | -0.030183
| 8:35 | 10.4333 | -0.030422
| 8:35 | 10.4336 | -0.030675
| 8:35 | 10.4339 | -0.030942
| 8:35 | 10.4342 | -0.031211
| 8:35 | 10.4344 | -0.031478
| 8:35 | 10.4347 | -0.031744
| 8:35 | 10.435 | -0.032002
| 8:35 | 10.4353 | -0.032252
| 8:35 | 10.4356 | -0.032481
| 8:35 | 10.4358 | -0.032675
| 8:35 | 10.4361 | -0.032817
| 8:35 | 10.4364 | -0.032909
| 8:35 | 10.4367 | -0.032956
| 8:35 | 10.4369 | -0.032986
| 8:35 | 10.4372 | -0.033005
| 8:35 | 10.4375 | -0.033008
| 8:35 | 10.4378 | -0.032999
| 8:35 | 10.4381 | -0.032969
| 8:35 | 10.4383 | -0.032919
| 8:35 | 10.4386 | -0.032847
| 8:35 | 10.4389 | -0.032742
| 8:35 | 10.4392 | -0.032595
| 8:35 | 10.4394 | -0.032417
| 8:35 | 10.4397 | -0.032223
| 8:35 | 10.44 | -0.032023
| 8:35 | 10.4403 | -0.031817
| 8:35 | 10.4406 | -0.031604
| 8:35 | 10.4408 | -0.031384
| 8:35 | 10.4411 | -0.031158
| 8:35 | 10.4414 | -0.030926
| 8:35 | 10.4417 | -0.030681
| 8:35 | 10.4419 | -0.030425
| 8:35 | 10.4422 | -0.030159
| 8:35 | 10.4425 | -0.029874
| 8:35 | 10.4428 | -0.029568
| 8:35 | 10.4431 | -0.029254
| 8:35 | 10.4433 | -0.028921
| 8:35 | 10.4436 | -0.028581
| 8:35 | 10.4439 | -0.028222
| 8:35 | 10.4442 | -0.027834
| 8:35 | 10.4444 | -0.027391
| 8:35 | 10.4447 | -0.026907
| 8:36 | 10.445 | -0.026419
| 8:36 | 10.4453 | -0.025931
| 8:36 | 10.4456 | -0.025443
| 8:36 | 10.4458 | -0.024954
| 8:36 | 10.4461 | -0.024466
| 8:36 | 10.4464 | -0.023977
| 8:36 | 10.4467 | -0.023489
| 8:36 | 10.4469 | -0.022989
| 8:36 | 10.4472 | -0.022485
| 8:36 | 10.4475 | -0.021961
| 8:36 | 10.4478 | -0.021423
| 8:36 | 10.4481 | -0.020878
| 8:36 | 10.4483 | -0.020326
| 8:36 | 10.4486 | -0.019766
| 8:36 | 10.4489 | -0.019198
| 8:36 | 10.4492 | -0.018623
| 8:36 | 10.4494 | -0.018041
| 8:36 | 10.4497 | -0.017451
| 8:36 | 10.45 | -0.016853
| 8:36 | 10.4503 | -0.016251
| 8:36 | 10.4506 | -0.015649
| 8:36 | 10.4508 | -0.015047
| 8:36 | 10.4511 | -0.014446
| 8:36 | 10.4514 | -0.013846
| 8:36 | 10.4517 | -0.013246
| 8:36 | 10.4519 | -0.012646
| 8:36 | 10.4522 | -0.012047
| 8:36 | 10.4525 | -0.011448
| 8:36 | 10.4528 | -0.01085
| 8:36 | 10.4531 | -0.010252
| 8:36 | 10.4533 | -0.0096545
| 8:36 | 10.4536 | -0.0090577
| 8:36 | 10.4539 | -0.0084613
| 8:36 | 10.4542 | -0.0078653
| 8:36 | 10.4544 | -0.0072699
| 8:36 | 10.4547 | -0.0066749
| 8:36 | 10.455 | -0.0060804
| 8:36 | 10.4553 | -0.0054863
| 8:36 | 10.4556 | -0.0048927
| 8:36 | 10.4558 | -0.0042995
| 8:36 | 10.4561 | -0.0037069
| 8:36 | 10.4564 | -0.0031147
| 8:36 | 10.4567 | -0.0025229
| 8:36 | 10.4569 | -0.0019317
| 8:36 | 10.4572 | -0.0013408
| 8:36 | 10.4575 | -0.0007505
| 8:36 | 10.4578 | -0.00016061
| 8:36 | 10.4581 | 0.00042881
| 8:36 | 10.4583 | 0.0010178
| 8:36 | 10.4586 | 0.0016063
| 8:36 | 10.4589 | 0.0021943
| 8:36 | 10.4592 | 0.0027818
| 8:36 | 10.4594 | 0.003369
| 8:36 | 10.4597 | 0.0039556
| 8:36 | 10.46 | 0.0045418
| 8:36 | 10.4603 | 0.0051275
| 8:36 | 10.4606 | 0.0057127
| 8:36 | 10.4608 | 0.0062975
| 8:36 | 10.4611 | 0.0068819
| 8:36 | 10.4614 | 0.0074657
| 8:36 | 10.4617 | 0.0080492
| 8:37 | 10.4619 | 0.0086321
| 8:37 | 10.4622 | 0.0092146
| 8:37 | 10.4625 | 0.0097966
| 8:37 | 10.4628 | 0.010378
| 8:37 | 10.4631 | 0.010959
| 8:37 | 10.4633 | 0.01154
| 8:37 | 10.4636 | 0.01212
| 8:37 | 10.4639 | 0.012699
| 8:37 | 10.4642 | 0.013277
| 8:37 | 10.4644 | 0.013854
| 8:37 | 10.4647 | 0.01443
| 8:37 | 10.465 | 0.015006
| 8:37 | 10.4653 | 0.01558
| 8:37 | 10.4656 | 0.016153
| 8:37 | 10.4658 | 0.016725
| 8:37 | 10.4661 | 0.017297
| 8:37 | 10.4664 | 0.017867
| 8:37 | 10.4667 | 0.018437
| 8:37 | 10.4669 | 0.019005
| 8:37 | 10.4672 | 0.019573
| 8:37 | 10.4675 | 0.020139
| 8:37 | 10.4678 | 0.020705
| 8:37 | 10.4681 | 0.021269
| 8:37 | 10.4683 | 0.021833
| 8:37 | 10.4686 | 0.022396
| 8:37 | 10.4689 | 0.022958
| 8:37 | 10.4692 | 0.023518
| 8:37 | 10.4694 | 0.024078
| 8:37 | 10.4697 | 0.024635
| 8:37 | 10.47 | 0.025189
| 8:37 | 10.4703 | 0.02574
| 8:37 | 10.4706 | 0.026287
| 8:37 | 10.4708 | 0.026831
| 8:37 | 10.4711 | 0.027374
| 8:37 | 10.4714 | 0.027916
| 8:37 | 10.4717 | 0.028458
| 8:37 | 10.4719 | 0.028998
| 8:37 | 10.4722 | 0.029538
| 8:37 | 10.4725 | 0.030077
| 8:37 | 10.4728 | 0.030614
| 8:37 | 10.4731 | 0.031148
| 8:37 | 10.4733 | 0.031678
| 8:37 | 10.4736 | 0.032205
| 8:37 | 10.4739 | 0.032729
| 8:37 | 10.4742 | 0.03325
| 8:37 | 10.4744 | 0.033767
| 8:37 | 10.4747 | 0.03428
| 8:37 | 10.475 | 0.034784
| 8:37 | 10.4753 | 0.035267
| 8:37 | 10.4756 | 0.035742
| 8:37 | 10.4758 | 0.036202
| 8:37 | 10.4761 | 0.036656
| 8:37 | 10.4764 | 0.037102
| 8:37 | 10.4767 | 0.03754
| 8:37 | 10.4769 | 0.037979
| 8:37 | 10.4772 | 0.038423
| 8:37 | 10.4775 | 0.038871
| 8:37 | 10.4778 | 0.039314
| 8:37 | 10.4781 | 0.039747
| 8:38 | 10.4783 | 0.040155
| 8:38 | 10.4786 | 0.040531
| 8:38 | 10.4789 | 0.040876
| 8:38 | 10.4792 | 0.041193
| 8:38 | 10.4794 | 0.041481
| 8:38 | 10.4797 | 0.041737
| 8:38 | 10.48 | 0.041964
| 8:38 | 10.4803 | 0.042167
| 8:38 | 10.4806 | 0.04235
| 8:38 | 10.4808 | 0.04252
| 8:38 | 10.4811 | 0.042681
| 8:38 | 10.4814 | 0.042842
| 8:38 | 10.4817 | 0.043008
| 8:38 | 10.4819 | 0.043177
| 8:38 | 10.4822 | 0.043351
| 8:38 | 10.4825 | 0.043528
| 8:38 | 10.4828 | 0.043709
| 8:38 | 10.4831 | 0.043894
| 8:38 | 10.4833 | 0.044083
| 8:38 | 10.4836 | 0.04428
| 8:38 | 10.4839 | 0.044488
| 8:38 | 10.4842 | 0.04471
| 8:38 | 10.4844 | 0.044942
| 8:38 | 10.4847 | 0.045171
| 8:38 | 10.485 | 0.045398
| 8:38 | 10.4853 | 0.045622
| 8:38 | 10.4856 | 0.045844
| 8:38 | 10.4858 | 0.046062
| 8:38 | 10.4861 | 0.046278
| 8:38 | 10.4864 | 0.046491
| 8:38 | 10.4867 | 0.046694
| 8:38 | 10.4869 | 0.046885
| 8:38 | 10.4872 | 0.047056
| 8:38 | 10.4875 | 0.047204
| 8:38 | 10.4878 | 0.047333
| 8:38 | 10.4881 | 0.047443
| 8:38 | 10.4883 | 0.047537
| 8:38 | 10.4886 | 0.047624
| 8:38 | 10.4889 | 0.047707
| 8:38 | 10.4892 | 0.047785
| 8:38 | 10.4894 | 0.047858
| 8:38 | 10.4897 | 0.047928
| 8:38 | 10.49 | 0.047996
| 8:38 | 10.4903 | 0.048062
| 8:38 | 10.4906 | 0.048127
| 8:38 | 10.4908 | 0.04819
| 8:38 | 10.4911 | 0.048251
| 8:38 | 10.4914 | 0.04831
| 8:38 | 10.4917 | 0.048366
| 8:38 | 10.4919 | 0.048416
| 8:38 | 10.4922 | 0.04846
| 8:38 | 10.4925 | 0.048496
| 8:38 | 10.4928 | 0.048527
| 8:38 | 10.4931 | 0.04855
| 8:38 | 10.4933 | 0.048566
| 8:38 | 10.4936 | 0.048574
| 8:38 | 10.4939 | 0.048573
| 8:38 | 10.4942 | 0.048559
| 8:38 | 10.4944 | 0.048526
| 8:38 | 10.4947 | 0.048482
| 8:38 | 10.495 | 0.048417
| 8:39 | 10.4953 | 0.048335
| 8:39 | 10.4956 | 0.048247
| 8:39 | 10.4958 | 0.048162
| 8:39 | 10.4961 | 0.048091
| 8:39 | 10.4964 | 0.048029
| 8:39 | 10.4967 | 0.047984
| 8:39 | 10.4969 | 0.047946
| 8:39 | 10.4972 | 0.047916
| 8:39 | 10.4975 | 0.047898
| 8:39 | 10.4978 | 0.047878
| 8:39 | 10.4981 | 0.047858
| 8:39 | 10.4983 | 0.047838
| 8:39 | 10.4986 | 0.047821
| 8:39 | 10.4989 | 0.047806
| 8:39 | 10.4992 | 0.047794
| 8:39 | 10.4994 | 0.047784
| 8:39 | 10.4997 | 0.047776
| 8:39 | 10.5 | 0.047771
| 8:39 | 10.5003 | 0.047769
| 8:39 | 10.5006 | 0.047768
| 8:39 | 10.5008 | 0.047771
| 8:39 | 10.5011 | 0.04777
| 8:39 | 10.5014 | 0.047767
| 8:39 | 10.5017 | 0.047761
| 8:39 | 10.5019 | 0.047752
| 8:39 | 10.5022 | 0.047739
| 8:39 | 10.5025 | 0.047724
| 8:39 | 10.5028 | 0.047706
| 8:39 | 10.5031 | 0.047683
| 8:39 | 10.5033 | 0.047656
| 8:39 | 10.5036 | 0.047623
| 8:39 | 10.5039 | 0.047586
| 8:39 | 10.5042 | 0.04754
| 8:39 | 10.5044 | 0.04749
| 8:39 | 10.5047 | 0.047435
| 8:39 | 10.505 | 0.047376
| 8:39 | 10.5053 | 0.047312
| 8:39 | 10.5056 | 0.047244
| 8:39 | 10.5058 | 0.047171
| 8:39 | 10.5061 | 0.047095
| 8:39 | 10.5064 | 0.047017
| 8:39 | 10.5067 | 0.046938
| 8:39 | 10.5069 | 0.046858
| 8:39 | 10.5072 | 0.046777
| 8:39 | 10.5075 | 0.046696
| 8:39 | 10.5078 | 0.046613
| 8:39 | 10.5081 | 0.04653
| 8:39 | 10.5083 | 0.046446
| 8:39 | 10.5086 | 0.046361
| 8:39 | 10.5089 | 0.046273
| 8:39 | 10.5092 | 0.046182
| 8:39 | 10.5094 | 0.046089
| 8:39 | 10.5097 | 0.045993
| 8:39 | 10.51 | 0.045895
| 8:39 | 10.5103 | 0.045792
| 8:39 | 10.5106 | 0.045683
| 8:39 | 10.5108 | 0.045569
| 8:39 | 10.5111 | 0.045449
| 8:39 | 10.5114 | 0.045324
| 8:40 | 10.5117 | 0.045194
| 8:40 | 10.5119 | 0.045061
| 8:40 | 10.5122 | 0.044926
| 8:40 | 10.5125 | 0.044788
| 8:40 | 10.5128 | 0.044642
| 8:40 | 10.5131 | 0.044487
| 8:40 | 10.5133 | 0.044324
| 8:40 | 10.5136 | 0.044145
| 8:40 | 10.5139 | 0.043946
| 8:40 | 10.5142 | 0.043743
| 8:40 | 10.5144 | 0.043531
| 8:40 | 10.5147 | 0.04331
| 8:40 | 10.515 | 0.043079
| 8:40 | 10.5153 | 0.042837
| 8:40 | 10.5156 | 0.042586
| 8:40 | 10.5158 | 0.042324
| 8:40 | 10.5161 | 0.042053
| 8:40 | 10.5164 | 0.041771
| 8:40 | 10.5167 | 0.04148
| 8:40 | 10.5169 | 0.041178
| 8:40 | 10.5172 | 0.040869
| 8:40 | 10.5175 | 0.040557
| 8:40 | 10.5178 | 0.040242
| 8:40 | 10.5181 | 0.039923
| 8:40 | 10.5183 | 0.039598
| 8:40 | 10.5186 | 0.039264
| 8:40 | 10.5189 | 0.038912
| 8:40 | 10.5192 | 0.038548
| 8:40 | 10.5194 | 0.038175
| 8:40 | 10.5197 | 0.037805
| 8:40 | 10.52 | 0.037438
| 8:40 | 10.5203 | 0.037075
| 8:40 | 10.5206 | 0.036737
| 8:40 | 10.5208 | 0.036406
| 8:40 | 10.5211 | 0.036101
| 8:40 | 10.5214 | 0.035808
| 8:40 | 10.5217 | 0.035522
| 8:40 | 10.5219 | 0.035251
| 8:40 | 10.5222 | 0.03501
| 8:40 | 10.5225 | 0.034771
| 8:40 | 10.5228 | 0.034536
| 8:40 | 10.5231 | 0.034303
| 8:40 | 10.5233 | 0.034074
| 8:40 | 10.5236 | 0.033848
| 8:40 | 10.5239 | 0.033625
| 8:40 | 10.5242 | 0.033404
| 8:40 | 10.5244 | 0.033187
| 8:40 | 10.5247 | 0.032975
| 8:40 | 10.525 | 0.032777
| 8:40 | 10.5253 | 0.032587
| 8:40 | 10.5256 | 0.032403
| 8:40 | 10.5258 | 0.032225
| 8:40 | 10.5261 | 0.032053
| 8:40 | 10.5264 | 0.031887
| 8:40 | 10.5267 | 0.031728
| 8:40 | 10.5269 | 0.031576
| 8:40 | 10.5272 | 0.031433
| 8:40 | 10.5275 | 0.0313
| 8:40 | 10.5278 | 0.031176
| 8:40 | 10.5281 | 0.031057
| 8:40 | 10.5283 | 0.030941
| 8:41 | 10.5286 | 0.030829
| 8:41 | 10.5289 | 0.030721
| 8:41 | 10.5292 | 0.03062
| 8:41 | 10.5294 | 0.030531
| 8:41 | 10.5297 | 0.030455
| 8:41 | 10.53 | 0.030386
| 8:41 | 10.5303 | 0.030337
| 8:41 | 10.5306 | 0.030292
| 8:41 | 10.5308 | 0.03025
| 8:41 | 10.5311 | 0.030213
| 8:41 | 10.5314 | 0.030179
| 8:41 | 10.5317 | 0.030148
| 8:41 | 10.5319 | 0.030122
| 8:41 | 10.5322 | 0.030099
| 8:41 | 10.5325 | 0.03008
| 8:41 | 10.5328 | 0.030064
| 8:41 | 10.5331 | 0.030052
| 8:41 | 10.5333 | 0.030044
| 8:41 | 10.5336 | 0.030037
| 8:41 | 10.5339 | 0.030029
| 8:41 | 10.5342 | 0.030021
| 8:41 | 10.5344 | 0.030012
| 8:41 | 10.5347 | 0.030002
| 8:41 | 10.535 | 0.029991
| 8:41 | 10.5353 | 0.02998
| 8:41 | 10.5356 | 0.029968
| 8:41 | 10.5358 | 0.029956
| 8:41 | 10.5361 | 0.029942
| 8:41 | 10.5364 | 0.029928
| 8:41 | 10.5367 | 0.029914
| 8:41 | 10.5369 | 0.029899
| 8:41 | 10.5372 | 0.029883
| 8:41 | 10.5375 | 0.029866
| 8:41 | 10.5378 | 0.029849
| 8:41 | 10.5381 | 0.029831
| 8:41 | 10.5383 | 0.029812
| 8:41 | 10.5386 | 0.029793
| 8:41 | 10.5389 | 0.029773
| 8:41 | 10.5392 | 0.029752
| 8:41 | 10.5394 | 0.02973
| 8:41 | 10.5397 | 0.029706
| 8:41 | 10.54 | 0.029679
| 8:41 | 10.5403 | 0.029649
| 8:41 | 10.5406 | 0.029617
| 8:41 | 10.5408 | 0.029582
| 8:41 | 10.5411 | 0.029545
| 8:41 | 10.5414 | 0.029505
| 8:41 | 10.5417 | 0.029465
| 8:41 | 10.5419 | 0.029426
| 8:41 | 10.5422 | 0.029387
| 8:41 | 10.5425 | 0.02935
| 8:41 | 10.5428 | 0.029314
| 8:41 | 10.5431 | 0.029278
| 8:41 | 10.5433 | 0.029243
| 8:41 | 10.5436 | 0.02921
| 8:41 | 10.5439 | 0.029177
| 8:41 | 10.5442 | 0.029145
| 8:41 | 10.5444 | 0.029114
| 8:41 | 10.5447 | 0.029089
| 8:42 | 10.545 | 0.029067
| 8:42 | 10.5453 | 0.02905
| 8:42 | 10.5456 | 0.029038
| 8:42 | 10.5458 | 0.029029
| 8:42 | 10.5461 | 0.029016
| 8:42 | 10.5464 | 0.029001
| 8:42 | 10.5467 | 0.028982
| 8:42 | 10.5469 | 0.028961
| 8:42 | 10.5472 | 0.028936
| 8:42 | 10.5475 | 0.028905
| 8:42 | 10.5478 | 0.028868
| 8:42 | 10.5481 | 0.028825
| 8:42 | 10.5483 | 0.028777
| 8:42 | 10.5486 | 0.028722
| 8:42 | 10.5489 | 0.028662
| 8:42 | 10.5492 | 0.028595
| 8:42 | 10.5494 | 0.028523
| 8:42 | 10.5497 | 0.028445
| 8:42 | 10.55 | 0.028361
| 8:42 | 10.5503 | 0.028271
| 8:42 | 10.5506 | 0.028175
| 8:42 | 10.5508 | 0.028073
| 8:42 | 10.5511 | 0.027966
| 8:42 | 10.5514 | 0.027852
| 8:42 | 10.5517 | 0.027734
| 8:42 | 10.5519 | 0.027611
| 8:42 | 10.5522 | 0.027485
| 8:42 | 10.5525 | 0.027359
| 8:42 | 10.5528 | 0.027231
| 8:42 | 10.5531 | 0.027103
| 8:42 | 10.5533 | 0.026974
| 8:42 | 10.5536 | 0.026844
| 8:42 | 10.5539 | 0.026714
| 8:42 | 10.5542 | 0.026581
| 8:42 | 10.5544 | 0.026438
| 8:42 | 10.5547 | 0.02629
| 8:42 | 10.555 | 0.026132
| 8:42 | 10.5553 | 0.02597
| 8:42 | 10.5556 | 0.025805
| 8:42 | 10.5558 | 0.025635
| 8:42 | 10.5561 | 0.025458
| 8:42 | 10.5564 | 0.025271
| 8:42 | 10.5567 | 0.025075
| 8:42 | 10.5569 | 0.024869
| 8:42 | 10.5572 | 0.024654
| 8:42 | 10.5575 | 0.024429
| 8:42 | 10.5578 | 0.024195
| 8:42 | 10.5581 | 0.023952
| 8:42 | 10.5583 | 0.023706
| 8:42 | 10.5586 | 0.023464
| 8:42 | 10.5589 | 0.023224
| 8:42 | 10.5592 | 0.022988
| 8:42 | 10.5594 | 0.022755
| 8:42 | 10.5597 | 0.022533
| 8:42 | 10.56 | 0.022311
| 8:42 | 10.5603 | 0.022092
| 8:42 | 10.5606 | 0.021875
| 8:42 | 10.5608 | 0.021659
| 8:42 | 10.5611 | 0.021416
| 8:42 | 10.5614 | 0.021157
| 8:42 | 10.5617 | 0.020885
| 8:43 | 10.5619 | 0.020601
| 8:43 | 10.5622 | 0.02032
| 8:43 | 10.5625 | 0.020041
| 8:43 | 10.5628 | 0.01976
| 8:43 | 10.5631 | 0.019484
| 8:43 | 10.5633 | 0.019211
| 8:43 | 10.5636 | 0.018941
| 8:43 | 10.5639 | 0.018675
| 8:43 | 10.5642 | 0.018418
| 8:43 | 10.5644 | 0.01817
| 8:43 | 10.5647 | 0.017931
| 8:43 | 10.565 | 0.017701
| 8:43 | 10.5653 | 0.01748
| 8:43 | 10.5656 | 0.017268
| 8:43 | 10.5658 | 0.017064
| 8:43 | 10.5661 | 0.01687
| 8:43 | 10.5664 | 0.016684
| 8:43 | 10.5667 | 0.016508
| 8:43 | 10.5669 | 0.016339
| 8:43 | 10.5672 | 0.016167
| 8:43 | 10.5675 | 0.01599
| 8:43 | 10.5678 | 0.015801
| 8:43 | 10.5681 | 0.015614
| 8:43 | 10.5683 | 0.015428
| 8:43 | 10.5686 | 0.015243
| 8:43 | 10.5689 | 0.015058
| 8:43 | 10.5692 | 0.014874
| 8:43 | 10.5694 | 0.014692
| 8:43 | 10.5697 | 0.01451
| 8:43 | 10.57 | 0.014329
| 8:43 | 10.5703 | 0.014146
| 8:43 | 10.5706 | 0.01396
| 8:43 | 10.5708 | 0.013771
| 8:43 | 10.5711 | 0.013583
| 8:43 | 10.5714 | 0.013399
| 8:43 | 10.5717 | 0.013221
| 8:43 | 10.5719 | 0.013048
| 8:43 | 10.5722 | 0.012881
| 8:43 | 10.5725 | 0.01272
| 8:43 | 10.5728 | 0.012565
| 8:43 | 10.5731 | 0.012415
| 8:43 | 10.5733 | 0.012271
| 8:43 | 10.5736 | 0.012133
| 8:43 | 10.5739 | 0.012
| 8:43 | 10.5742 | 0.011873
| 8:43 | 10.5744 | 0.011751
| 8:43 | 10.5747 | 0.011634
| 8:43 | 10.575 | 0.011508
| 8:43 | 10.5753 | 0.011363
| 8:43 | 10.5756 | 0.011221
| 8:43 | 10.5758 | 0.011081
| 8:43 | 10.5761 | 0.010943
| 8:43 | 10.5764 | 0.010808
| 8:43 | 10.5767 | 0.010697
| 8:43 | 10.5769 | 0.010587
| 8:43 | 10.5772 | 0.010472
| 8:43 | 10.5775 | 0.01035
| 8:43 | 10.5778 | 0.010214
| 8:43 | 10.5781 | 0.010061
| 8:44 | 10.5783 | 0.0098886
| 8:44 | 10.5786 | 0.0097137
| 8:44 | 10.5789 | 0.0095386
| 8:44 | 10.5792 | 0.0093799
| 8:44 | 10.5794 | 0.0092465
| 8:44 | 10.5797 | 0.0091394
| 8:44 | 10.58 | 0.0090464
| 8:44 | 10.5803 | 0.0089742
| 8:44 | 10.5806 | 0.0089339
| 8:44 | 10.5808 | 0.0089121
| 8:44 | 10.5811 | 0.008909
| 8:44 | 10.5814 | 0.0089221
| 8:44 | 10.5817 | 0.0089509
| 8:44 | 10.5819 | 0.0089953
| 8:44 | 10.5822 | 0.0090554
| 8:44 | 10.5825 | 0.0091311
| 8:44 | 10.5828 | 0.0092224
| 8:44 | 10.5831 | 0.0093294
| 8:44 | 10.5833 | 0.0094521
| 8:44 | 10.5836 | 0.0095904
| 8:44 | 10.5839 | 0.0097347
| 8:44 | 10.5842 | 0.0098779
| 8:44 | 10.5844 | 0.01002
| 8:44 | 10.5847 | 0.010161
| 8:44 | 10.585 | 0.010301
| 8:44 | 10.5853 | 0.01044
| 8:44 | 10.5856 | 0.010583
| 8:44 | 10.5858 | 0.010734
| 8:44 | 10.5861 | 0.010904
| 8:44 | 10.5864 | 0.011092
| 8:44 | 10.5867 | 0.011317
| 8:44 | 10.5869 | 0.011571
| 8:44 | 10.5872 | 0.011857
| 8:44 | 10.5875 | 0.012165
| 8:44 | 10.5878 | 0.012488
| 8:44 | 10.5881 | 0.01283
| 8:44 | 10.5883 | 0.013205
| 8:44 | 10.5886 | 0.013589
| 8:44 | 10.5889 | 0.013981
| 8:44 | 10.5892 | 0.014388
| 8:44 | 10.5894 | 0.014811
| 8:44 | 10.5897 | 0.015244
| 8:44 | 10.59 | 0.015686
| 8:44 | 10.5903 | 0.016138
| 8:44 | 10.5906 | 0.016599
| 8:44 | 10.5908 | 0.01707
| 8:44 | 10.5911 | 0.01755
| 8:44 | 10.5914 | 0.018039
| 8:44 | 10.5917 | 0.018533
| 8:44 | 10.5919 | 0.019031
| 8:44 | 10.5922 | 0.019533
| 8:44 | 10.5925 | 0.020038
| 8:44 | 10.5928 | 0.020547
| 8:44 | 10.5931 | 0.021059
| 8:44 | 10.5933 | 0.021575
| 8:44 | 10.5936 | 0.022095
| 8:44 | 10.5939 | 0.022619
| 8:44 | 10.5942 | 0.023146
| 8:44 | 10.5944 | 0.023677
| 8:44 | 10.5947 | 0.024212
| 8:44 | 10.595 | 0.024751
| 8:45 | 10.5953 | 0.025294
| 8:45 | 10.5956 | 0.025838
| 8:45 | 10.5958 | 0.026385
| 8:45 | 10.5961 | 0.026935
| 8:45 | 10.5964 | 0.027485
| 8:45 | 10.5967 | 0.028035
| 8:45 | 10.5969 | 0.028585
| 8:45 | 10.5972 | 0.029134
| 8:45 | 10.5975 | 0.029682
| 8:45 | 10.5978 | 0.03023
| 8:45 | 10.5981 | 0.030777
| 8:45 | 10.5983 | 0.031323
| 8:45 | 10.5986 | 0.031869
| 8:45 | 10.5989 | 0.032414
| 8:45 | 10.5992 | 0.032959
| 8:45 | 10.5994 | 0.033502
| 8:45 | 10.5997 | 0.034046
| 8:45 | 10.6 | 0.034588
| 8:45 | 10.6003 | 0.03513
| 8:45 | 10.6006 | 0.035672
| 8:45 | 10.6008 | 0.036212
| 8:45 | 10.6011 | 0.036753
| 8:45 | 10.6014 | 0.037292
| 8:45 | 10.6017 | 0.037831
| 8:45 | 10.6019 | 0.038369
| 8:45 | 10.6022 | 0.038907
| 8:45 | 10.6025 | 0.039444
| 8:45 | 10.6028 | 0.03998
| 8:45 | 10.6031 | 0.040516
| 8:45 | 10.6033 | 0.041051
| 8:45 | 10.6036 | 0.041586
| 8:45 | 10.6039 | 0.04212
| 8:45 | 10.6042 | 0.042653
| 8:45 | 10.6044 | 0.043186
| 8:45 | 10.6047 | 0.043718
| 8:45 | 10.605 | 0.044249
| 8:45 | 10.6053 | 0.04478
| 8:45 | 10.6056 | 0.04531
| 8:45 | 10.6058 | 0.045839
| 8:45 | 10.6061 | 0.046368
| 8:45 | 10.6064 | 0.046897
| 8:45 | 10.6067 | 0.047424
| 8:45 | 10.6069 | 0.047951
| 8:45 | 10.6072 | 0.048478
| 8:45 | 10.6075 | 0.049004
| 8:45 | 10.6078 | 0.049529
| 8:45 | 10.6081 | 0.050053
| 8:45 | 10.6083 | 0.050577
| 8:45 | 10.6086 | 0.051101
| 8:45 | 10.6089 | 0.051623
| 8:45 | 10.6092 | 0.052146
| 8:45 | 10.6094 | 0.052667
| 8:45 | 10.6097 | 0.053188
| 8:45 | 10.61 | 0.053708
| 8:45 | 10.6103 | 0.054228
| 8:45 | 10.6106 | 0.054747
| 8:45 | 10.6108 | 0.055265
| 8:45 | 10.6111 | 0.055783
| 8:45 | 10.6114 | 0.0563
| 8:46 | 10.6117 | 0.056817
| 8:46 | 10.6119 | 0.057333
| 8:46 | 10.6122 | 0.057848
| 8:46 | 10.6125 | 0.058362
| 8:46 | 10.6128 | 0.058877
| 8:46 | 10.6131 | 0.05939
| 8:46 | 10.6133 | 0.059903
| 8:46 | 10.6136 | 0.060415
| 8:46 | 10.6139 | 0.060927
| 8:46 | 10.6142 | 0.061438
| 8:46 | 10.6144 | 0.061948
| 8:46 | 10.6147 | 0.062458
| 8:46 | 10.615 | 0.062967
| 8:46 | 10.6153 | 0.063475
| 8:46 | 10.6156 | 0.063983
| 8:46 | 10.6158 | 0.06449
| 8:46 | 10.6161 | 0.064997
| 8:46 | 10.6164 | 0.065503
| 8:46 | 10.6167 | 0.066009
| 8:46 | 10.6169 | 0.066513
| 8:46 | 10.6172 | 0.067018
| 8:46 | 10.6175 | 0.067521
| 8:46 | 10.6178 | 0.068024
| 8:46 | 10.6181 | 0.068526
| 8:46 | 10.6183 | 0.069028
| 8:46 | 10.6186 | 0.069529
| 8:46 | 10.6189 | 0.07003
| 8:46 | 10.6192 | 0.070529
| 8:46 | 10.6194 | 0.071028
| 8:46 | 10.6197 | 0.071526
| 8:46 | 10.62 | 0.072023
| 8:46 | 10.6203 | 0.072519
| 8:46 | 10.6206 | 0.073014
| 8:46 | 10.6208 | 0.073509
| 8:46 | 10.6211 | 0.074002
| 8:46 | 10.6214 | 0.074494
| 8:46 | 10.6217 | 0.074986
| 8:46 | 10.6219 | 0.075476
| 8:46 | 10.6222 | 0.075966
| 8:46 | 10.6225 | 0.076455
| 8:46 | 10.6228 | 0.076942
| 8:46 | 10.6231 | 0.077429
| 8:46 | 10.6233 | 0.077915
| 8:46 | 10.6236 | 0.0784
| 8:46 | 10.6239 | 0.078884
| 8:46 | 10.6242 | 0.079367
| 8:46 | 10.6244 | 0.079849
| 8:46 | 10.6247 | 0.080331
| 8:46 | 10.625 | 0.080811
| 8:46 | 10.6253 | 0.08129
| 8:46 | 10.6256 | 0.081768
| 8:46 | 10.6258 | 0.082246
| 8:46 | 10.6261 | 0.082722
| 8:46 | 10.6264 | 0.083197
| 8:46 | 10.6267 | 0.083671
| 8:46 | 10.6269 | 0.084144
| 8:46 | 10.6272 | 0.084616
| 8:46 | 10.6275 | 0.085087
| 8:46 | 10.6278 | 0.085557
| 8:46 | 10.6281 | 0.086026
| 8:46 | 10.6283 | 0.086494
| 8:47 | 10.6286 | 0.086961
| 8:47 | 10.6289 | 0.087427
| 8:47 | 10.6292 | 0.087892
| 8:47 | 10.6294 | 0.088356
| 8:47 | 10.6297 | 0.088818
| 8:47 | 10.63 | 0.08928
| 8:47 | 10.6303 | 0.089741
| 8:47 | 10.6306 | 0.090201
| 8:47 | 10.6308 | 0.090659
| 8:47 | 10.6311 | 0.091117
| 8:47 | 10.6314 | 0.091574
| 8:47 | 10.6317 | 0.092029
| 8:47 | 10.6319 | 0.092484
| 8:47 | 10.6322 | 0.092938
| 8:47 | 10.6325 | 0.09339
| 8:47 | 10.6328 | 0.093842
| 8:47 | 10.6331 | 0.094292
| 8:47 | 10.6333 | 0.094742
| 8:47 | 10.6336 | 0.09519
| 8:47 | 10.6339 | 0.095638
| 8:47 | 10.6342 | 0.096084
| 8:47 | 10.6344 | 0.09653
| 8:47 | 10.6347 | 0.096974
| 8:47 | 10.635 | 0.097417
| 8:47 | 10.6353 | 0.09786
| 8:47 | 10.6356 | 0.098301
| 8:47 | 10.6358 | 0.098741
| 8:47 | 10.6361 | 0.09918
| 8:47 | 10.6364 | 0.099619
| 8:47 | 10.6367 | 0.10005
| 8:47 | 10.6369 | 0.10049
| 8:47 | 10.6372 | 0.10092
| 8:47 | 10.6375 | 0.10134
| 8:47 | 10.6378 | 0.10177
| 8:47 | 10.6381 | 0.10219
| 8:47 | 10.6383 | 0.10261
| 8:47 | 10.6386 | 0.10303
| 8:47 | 10.6389 | 0.10344
| 8:47 | 10.6392 | 0.10385
| 8:47 | 10.6394 | 0.10425
| 8:47 | 10.6397 | 0.10465
| 8:47 | 10.64 | 0.10503
| 8:47 | 10.6403 | 0.1054
| 8:47 | 10.6406 | 0.10576
| 8:47 | 10.6408 | 0.10611
| 8:47 | 10.6411 | 0.10644
| 8:47 | 10.6414 | 0.10677
| 8:47 | 10.6417 | 0.10708
| 8:47 | 10.6419 | 0.10738
| 8:47 | 10.6422 | 0.10769
| 8:47 | 10.6425 | 0.10799
| 8:47 | 10.6428 | 0.10829
| 8:47 | 10.6431 | 0.1086
| 8:47 | 10.6433 | 0.1089
| 8:47 | 10.6436 | 0.10921
| 8:47 | 10.6439 | 0.10952
| 8:47 | 10.6442 | 0.10982
| 8:47 | 10.6444 | 0.11013
| 8:47 | 10.6447 | 0.11044
| 8:48 | 10.645 | 0.11075
| 8:48 | 10.6453 | 0.11106
| 8:48 | 10.6456 | 0.11137
| 8:48 | 10.6458 | 0.11167
| 8:48 | 10.6461 | 0.11198
| 8:48 | 10.6464 | 0.11229
| 8:48 | 10.6467 | 0.1126
| 8:48 | 10.6469 | 0.11291
| 8:48 | 10.6472 | 0.11322
| 8:48 | 10.6475 | 0.11353
| 8:48 | 10.6478 | 0.11383
| 8:48 | 10.6481 | 0.11414
| 8:48 | 10.6483 | 0.11444
| 8:48 | 10.6486 | 0.11475
| 8:48 | 10.6489 | 0.11505
| 8:48 | 10.6492 | 0.11535
| 8:48 | 10.6494 | 0.11565
| 8:48 | 10.6497 | 0.11595
| 8:48 | 10.65 | 0.11625
| 8:48 | 10.6503 | 0.11655
| 8:48 | 10.6506 | 0.11685
| 8:48 | 10.6508 | 0.11714
| 8:48 | 10.6511 | 0.11744
| 8:48 | 10.6514 | 0.11774
| 8:48 | 10.6517 | 0.11803
| 8:48 | 10.6519 | 0.11832
| 8:48 | 10.6522 | 0.11862
| 8:48 | 10.6525 | 0.11891
| 8:48 | 10.6528 | 0.1192
| 8:48 | 10.6531 | 0.11949
| 8:48 | 10.6533 | 0.11978
| 8:48 | 10.6536 | 0.12007
| 8:48 | 10.6539 | 0.12035
| 8:48 | 10.6542 | 0.12064
| 8:48 | 10.6544 | 0.12092
| 8:48 | 10.6547 | 0.12118
| 8:48 | 10.655 | 0.12144
| 8:48 | 10.6553 | 0.12169
| 8:48 | 10.6556 | 0.12194
| 8:48 | 10.6558 | 0.12218
| 8:48 | 10.6561 | 0.12242
| 8:48 | 10.6564 | 0.12266
| 8:48 | 10.6567 | 0.12291
| 8:48 | 10.6569 | 0.12317
| 8:48 | 10.6572 | 0.12343
| 8:48 | 10.6575 | 0.1237
| 8:48 | 10.6578 | 0.12397
| 8:48 | 10.6581 | 0.12425
| 8:48 | 10.6583 | 0.12454
| 8:48 | 10.6586 | 0.12483
| 8:48 | 10.6589 | 0.12513
| 8:48 | 10.6592 | 0.12542
| 8:48 | 10.6594 | 0.12573
| 8:48 | 10.6597 | 0.12603
| 8:48 | 10.66 | 0.12632
| 8:48 | 10.6603 | 0.12662
| 8:48 | 10.6606 | 0.12691
| 8:48 | 10.6608 | 0.1272
| 8:48 | 10.6611 | 0.12749
| 8:48 | 10.6614 | 0.12778
| 8:48 | 10.6617 | 0.12806
| 8:49 | 10.6619 | 0.12834
| 8:49 | 10.6622 | 0.12862
| 8:49 | 10.6625 | 0.1289
| 8:49 | 10.6628 | 0.12917
| 8:49 | 10.6631 | 0.12943
| 8:49 | 10.6633 | 0.12969
| 8:49 | 10.6636 | 0.12995
| 8:49 | 10.6639 | 0.1302
| 8:49 | 10.6642 | 0.13045
| 8:49 | 10.6644 | 0.1307
| 8:49 | 10.6647 | 0.13094
| 8:49 | 10.665 | 0.13117
| 8:49 | 10.6653 | 0.1314
| 8:49 | 10.6656 | 0.13163
| 8:49 | 10.6658 | 0.13185
| 8:49 | 10.6661 | 0.13207
| 8:49 | 10.6664 | 0.13228
| 8:49 | 10.6667 | 0.13249
| 8:49 | 10.6669 | 0.13269
| 8:49 | 10.6672 | 0.1329
| 8:49 | 10.6675 | 0.1331
| 8:49 | 10.6678 | 0.13332
| 8:49 | 10.6681 | 0.13354
| 8:49 | 10.6683 | 0.13376
| 8:49 | 10.6686 | 0.13399
| 8:49 | 10.6689 | 0.13421
| 8:49 | 10.6692 | 0.13443
| 8:49 | 10.6694 | 0.13465
| 8:49 | 10.6697 | 0.13487
| 8:49 | 10.67 | 0.13509
| 8:49 | 10.6703 | 0.13531
| 8:49 | 10.6706 | 0.13552
| 8:49 | 10.6708 | 0.13574
| 8:49 | 10.6711 | 0.13595
| 8:49 | 10.6714 | 0.13616
| 8:49 | 10.6717 | 0.13637
| 8:49 | 10.6719 | 0.13657
| 8:49 | 10.6722 | 0.13676
| 8:49 | 10.6725 | 0.13694
| 8:49 | 10.6728 | 0.13713
| 8:49 | 10.6731 | 0.13731
| 8:49 | 10.6733 | 0.13749
| 8:49 | 10.6736 | 0.13767
| 8:49 | 10.6739 | 0.13785
| 8:49 | 10.6742 | 0.13803
| 8:49 | 10.6744 | 0.1382
| 8:49 | 10.6747 | 0.13838
| 8:49 | 10.675 | 0.13855
| 8:49 | 10.6753 | 0.13872
| 8:49 | 10.6756 | 0.13889
| 8:49 | 10.6758 | 0.13906
| 8:49 | 10.6761 | 0.13923
| 8:49 | 10.6764 | 0.1394
| 8:49 | 10.6767 | 0.13957
| 8:49 | 10.6769 | 0.13973
| 8:49 | 10.6772 | 0.1399
| 8:49 | 10.6775 | 0.14005
| 8:49 | 10.6778 | 0.14019
| 8:49 | 10.6781 | 0.14032
| 8:50 | 10.6783 | 0.14044
| 8:50 | 10.6786 | 0.14053
| 8:50 | 10.6789 | 0.1406
| 8:50 | 10.6792 | 0.14064
| 8:50 | 10.6794 | 0.14067
| 8:50 | 10.6797 | 0.14068
| 8:50 | 10.68 | 0.14069
| 8:50 | 10.6803 | 0.1407
| 8:50 | 10.6806 | 0.14071
| 8:50 | 10.6808 | 0.14075
| 8:50 | 10.6811 | 0.14081
| 8:50 | 10.6814 | 0.14089
| 8:50 | 10.6817 | 0.14099
| 8:50 | 10.6819 | 0.1411
| 8:50 | 10.6822 | 0.14123
| 8:50 | 10.6825 | 0.14137
| 8:50 | 10.6828 | 0.14152
| 8:50 | 10.6831 | 0.14169
| 8:50 | 10.6833 | 0.14187
| 8:50 | 10.6836 | 0.14207
| 8:50 | 10.6839 | 0.14228
| 8:50 | 10.6842 | 0.14249
| 8:50 | 10.6844 | 0.1427
| 8:50 | 10.6847 | 0.14291
| 8:50 | 10.685 | 0.14312
| 8:50 | 10.6853 | 0.14332
| 8:50 | 10.6856 | 0.14353
| 8:50 | 10.6858 | 0.14373
| 8:50 | 10.6861 | 0.14392
| 8:50 | 10.6864 | 0.1441
| 8:50 | 10.6867 | 0.14427
| 8:50 | 10.6869 | 0.14441
| 8:50 | 10.6872 | 0.14454
| 8:50 | 10.6875 | 0.14465
| 8:50 | 10.6878 | 0.14474
| 8:50 | 10.6881 | 0.14481
| 8:50 | 10.6883 | 0.14486
| 8:50 | 10.6886 | 0.14489
| 8:50 | 10.6889 | 0.1449
| 8:50 | 10.6892 | 0.14488
| 8:50 | 10.6894 | 0.14483
| 8:50 | 10.6897 | 0.14477
| 8:50 | 10.69 | 0.14469
| 8:50 | 10.6903 | 0.1446
| 8:50 | 10.6906 | 0.1445
| 8:50 | 10.6908 | 0.14438
| 8:50 | 10.6911 | 0.14426
| 8:50 | 10.6914 | 0.14412
| 8:50 | 10.6917 | 0.14397
| 8:50 | 10.6919 | 0.14383
| 8:50 | 10.6922 | 0.14368
| 8:50 | 10.6925 | 0.14353
| 8:50 | 10.6928 | 0.14337
| 8:50 | 10.6931 | 0.14322
| 8:50 | 10.6933 | 0.14306
| 8:50 | 10.6936 | 0.14291
| 8:50 | 10.6939 | 0.14274
| 8:50 | 10.6942 | 0.14257
| 8:50 | 10.6944 | 0.1424
| 8:50 | 10.6947 | 0.14222
| 8:50 | 10.695 | 0.14202
| 8:51 | 10.6953 | 0.14181
| 8:51 | 10.6956 | 0.14159
| 8:51 | 10.6958 | 0.14136
| 8:51 | 10.6961 | 0.14111
| 8:51 | 10.6964 | 0.14085
| 8:51 | 10.6967 | 0.14058
| 8:51 | 10.6969 | 0.14029
| 8:51 | 10.6972 | 0.13999
| 8:51 | 10.6975 | 0.13969
| 8:51 | 10.6978 | 0.13938
| 8:51 | 10.6981 | 0.13909
| 8:51 | 10.6983 | 0.13881
| 8:51 | 10.6986 | 0.13855
| 8:51 | 10.6989 | 0.13829
| 8:51 | 10.6992 | 0.13805
| 8:51 | 10.6994 | 0.13782
| 8:51 | 10.6997 | 0.1376
| 8:51 | 10.7 | 0.1374
| 8:51 | 10.7003 | 0.13721
| 8:51 | 10.7006 | 0.13703
| 8:51 | 10.7008 | 0.13685
| 8:51 | 10.7011 | 0.13669
| 8:51 | 10.7014 | 0.13653
| 8:51 | 10.7017 | 0.13636
| 8:51 | 10.7019 | 0.1362
| 8:51 | 10.7022 | 0.13604
| 8:51 | 10.7025 | 0.13587
| 8:51 | 10.7028 | 0.13571
| 8:51 | 10.7031 | 0.13554
| 8:51 | 10.7033 | 0.13538
| 8:51 | 10.7036 | 0.13521
| 8:51 | 10.7039 | 0.13505
| 8:51 | 10.7042 | 0.13488
| 8:51 | 10.7044 | 0.13472
| 8:51 | 10.7047 | 0.13455
| 8:51 | 10.705 | 0.13438
| 8:51 | 10.7053 | 0.13421
| 8:51 | 10.7056 | 0.13405
| 8:51 | 10.7058 | 0.13388
| 8:51 | 10.7061 | 0.13371
| 8:51 | 10.7064 | 0.13354
| 8:51 | 10.7067 | 0.13337
| 8:51 | 10.7069 | 0.1332
| 8:51 | 10.7072 | 0.13303
| 8:51 | 10.7075 | 0.13286
| 8:51 | 10.7078 | 0.13269
| 8:51 | 10.7081 | 0.13252
| 8:51 | 10.7083 | 0.13235
| 8:51 | 10.7086 | 0.13218
| 8:51 | 10.7089 | 0.132
| 8:51 | 10.7092 | 0.13181
| 8:51 | 10.7094 | 0.13161
| 8:51 | 10.7097 | 0.13139
| 8:51 | 10.71 | 0.13115
| 8:51 | 10.7103 | 0.1309
| 8:51 | 10.7106 | 0.13063
| 8:51 | 10.7108 | 0.13034
| 8:51 | 10.7111 | 0.13004
| 8:51 | 10.7114 | 0.12973
| 8:52 | 10.7117 | 0.12941
| 8:52 | 10.7119 | 0.12909
| 8:52 | 10.7122 | 0.12876
| 8:52 | 10.7125 | 0.12843
| 8:52 | 10.7128 | 0.1281
| 8:52 | 10.7131 | 0.12777
| 8:52 | 10.7133 | 0.12743
| 8:52 | 10.7136 | 0.12709
| 8:52 | 10.7139 | 0.12674
| 8:52 | 10.7142 | 0.12639
| 8:52 | 10.7144 | 0.12604
| 8:52 | 10.7147 | 0.12569
| 8:52 | 10.715 | 0.12534
| 8:52 | 10.7153 | 0.12499
| 8:52 | 10.7156 | 0.12465
| 8:52 | 10.7158 | 0.12431
| 8:52 | 10.7161 | 0.12397
| 8:52 | 10.7164 | 0.12364
| 8:52 | 10.7167 | 0.12331
| 8:52 | 10.7169 | 0.12298
| 8:52 | 10.7172 | 0.12265
| 8:52 | 10.7175 | 0.12232
| 8:52 | 10.7178 | 0.12198
| 8:52 | 10.7181 | 0.12164
| 8:52 | 10.7183 | 0.1213
| 8:52 | 10.7186 | 0.12095
| 8:52 | 10.7189 | 0.1206
| 8:52 | 10.7192 | 0.12025
| 8:52 | 10.7194 | 0.11991
| 8:52 | 10.7197 | 0.1196
| 8:52 | 10.72 | 0.1193
| 8:52 | 10.7203 | 0.119
| 8:52 | 10.7206 | 0.1187
| 8:52 | 10.7208 | 0.11839
| 8:52 | 10.7211 | 0.11808
| 8:52 | 10.7214 | 0.11776
| 8:52 | 10.7217 | 0.11742
| 8:52 | 10.7219 | 0.11708
| 8:52 | 10.7222 | 0.11674
| 8:52 | 10.7225 | 0.1164
| 8:52 | 10.7228 | 0.11606
| 8:52 | 10.7231 | 0.11572
| 8:52 | 10.7233 | 0.1154
| 8:52 | 10.7236 | 0.11508
| 8:52 | 10.7239 | 0.11477
| 8:52 | 10.7242 | 0.11447
| 8:52 | 10.7244 | 0.11418
| 8:52 | 10.7247 | 0.11389
| 8:52 | 10.725 | 0.11363
| 8:52 | 10.7253 | 0.11341
| 8:52 | 10.7256 | 0.1132
| 8:52 | 10.7258 | 0.11303
| 8:52 | 10.7261 | 0.11287
| 8:52 | 10.7264 | 0.11272
| 8:52 | 10.7267 | 0.11259
| 8:52 | 10.7269 | 0.11245
| 8:52 | 10.7272 | 0.1123
| 8:52 | 10.7275 | 0.11215
| 8:52 | 10.7278 | 0.11201
| 8:52 | 10.7281 | 0.11187
| 8:52 | 10.7283 | 0.11175
| 8:53 | 10.7286 | 0.11166
| 8:53 | 10.7289 | 0.1116
| 8:53 | 10.7292 | 0.11156
| 8:53 | 10.7294 | 0.11156
| 8:53 | 10.7297 | 0.11157
| 8:53 | 10.73 | 0.11162
| 8:53 | 10.7303 | 0.11168
| 8:53 | 10.7306 | 0.11177
| 8:53 | 10.7308 | 0.11187
| 8:53 | 10.7311 | 0.11208
| 8:53 | 10.7314 | 0.11229
| 8:53 | 10.7317 | 0.1125
| 8:53 | 10.7319 | 0.11271
| 8:53 | 10.7322 | 0.11292
| 8:53 | 10.7325 | 0.11313
| 8:53 | 10.7328 | 0.11335
| 8:53 | 10.7331 | 0.11356
| 8:53 | 10.7333 | 0.11378
| 8:53 | 10.7336 | 0.11399
| 8:53 | 10.7339 | 0.1142
| 8:53 | 10.7342 | 0.11439
| 8:53 | 10.7344 | 0.11458
| 8:53 | 10.7347 | 0.11476
| 8:53 | 10.735 | 0.11494
| 8:53 | 10.7353 | 0.11513
| 8:53 | 10.7356 | 0.11532
| 8:53 | 10.7358 | 0.11551
| 8:53 | 10.7361 | 0.1157
| 8:53 | 10.7364 | 0.11589
| 8:53 | 10.7367 | 0.11609
| 8:53 | 10.7369 | 0.1163
| 8:53 | 10.7372 | 0.11652
| 8:53 | 10.7375 | 0.11676
| 8:53 | 10.7378 | 0.11702
| 8:53 | 10.7381 | 0.11729
| 8:53 | 10.7383 | 0.11757
| 8:53 | 10.7386 | 0.11785
| 8:53 | 10.7389 | 0.11813
| 8:53 | 10.7392 | 0.11842
| 8:53 | 10.7394 | 0.1187
| 8:53 | 10.7397 | 0.11899
| 8:53 | 10.74 | 0.11928
| 8:53 | 10.7403 | 0.11957
| 8:53 | 10.7406 | 0.11986
| 8:53 | 10.7408 | 0.12015
| 8:53 | 10.7411 | 0.12044
| 8:53 | 10.7414 | 0.12074
| 8:53 | 10.7417 | 0.12103
| 8:53 | 10.7419 | 0.12133
| 8:53 | 10.7422 | 0.12162
| 8:53 | 10.7425 | 0.12192
| 8:53 | 10.7428 | 0.12222
| 8:53 | 10.7431 | 0.12253
| 8:53 | 10.7433 | 0.12283
| 8:53 | 10.7436 | 0.12313
| 8:53 | 10.7439 | 0.12344
| 8:53 | 10.7442 | 0.12375
| 8:53 | 10.7444 | 0.12406
| 8:53 | 10.7447 | 0.12437
| 8:54 | 10.745 | 0.12468
| 8:54 | 10.7453 | 0.125
| 8:54 | 10.7456 | 0.12532
| 8:54 | 10.7458 | 0.12564
| 8:54 | 10.7461 | 0.12597
| 8:54 | 10.7464 | 0.12629
| 8:54 | 10.7467 | 0.12661
| 8:54 | 10.7469 | 0.12693
| 8:54 | 10.7472 | 0.12724
| 8:54 | 10.7475 | 0.12755
| 8:54 | 10.7478 | 0.12786
| 8:54 | 10.7481 | 0.12817
| 8:54 | 10.7483 | 0.12848
| 8:54 | 10.7486 | 0.12879
| 8:54 | 10.7489 | 0.1291
| 8:54 | 10.7492 | 0.12941
| 8:54 | 10.7494 | 0.12973
| 8:54 | 10.7497 | 0.13004
| 8:54 | 10.75 | 0.13036
| 8:54 | 10.7503 | 0.13067
| 8:54 | 10.7506 | 0.13099
| 8:54 | 10.7508 | 0.13131
| 8:54 | 10.7511 | 0.13163
| 8:54 | 10.7514 | 0.13195
| 8:54 | 10.7517 | 0.13227
| 8:54 | 10.7519 | 0.13259
| 8:54 | 10.7522 | 0.13292
| 8:54 | 10.7525 | 0.13324
| 8:54 | 10.7528 | 0.13357
| 8:54 | 10.7531 | 0.1339
| 8:54 | 10.7533 | 0.13423
| 8:54 | 10.7536 | 0.13456
| 8:54 | 10.7539 | 0.1349
| 8:54 | 10.7542 | 0.13524
| 8:54 | 10.7544 | 0.13558
| 8:54 | 10.7547 | 0.13593
| 8:54 | 10.755 | 0.13628
| 8:54 | 10.7553 | 0.13664
| 8:54 | 10.7556 | 0.137
| 8:54 | 10.7558 | 0.13737
| 8:54 | 10.7561 | 0.13774
| 8:54 | 10.7564 | 0.13812
| 8:54 | 10.7567 | 0.1385
| 8:54 | 10.7569 | 0.13888
| 8:54 | 10.7572 | 0.13927
| 8:54 | 10.7575 | 0.13966
| 8:54 | 10.7578 | 0.14005
| 8:54 | 10.7581 | 0.14045
| 8:54 | 10.7583 | 0.14085
| 8:54 | 10.7586 | 0.14125
| 8:54 | 10.7589 | 0.14165
| 8:54 | 10.7592 | 0.14205
| 8:54 | 10.7594 | 0.14246
| 8:54 | 10.7597 | 0.14286
| 8:54 | 10.76 | 0.14327
| 8:54 | 10.7603 | 0.14368
| 8:54 | 10.7606 | 0.14409
| 8:54 | 10.7608 | 0.1445
| 8:54 | 10.7611 | 0.14491
| 8:54 | 10.7614 | 0.14532
| 8:54 | 10.7617 | 0.14574
| 8:55 | 10.7619 | 0.14615
| 8:55 | 10.7622 | 0.14657
| 8:55 | 10.7625 | 0.14699
| 8:55 | 10.7628 | 0.1474
| 8:55 | 10.7631 | 0.14782
| 8:55 | 10.7633 | 0.14823
| 8:55 | 10.7636 | 0.14865
| 8:55 | 10.7639 | 0.14907
| 8:55 | 10.7642 | 0.14948
| 8:55 | 10.7644 | 0.1499
| 8:55 | 10.7647 | 0.15031
| 8:55 | 10.765 | 0.15073
| 8:55 | 10.7653 | 0.15114
| 8:55 | 10.7656 | 0.15156
| 8:55 | 10.7658 | 0.15197
| 8:55 | 10.7661 | 0.15238
| 8:55 | 10.7664 | 0.1528
| 8:55 | 10.7667 | 0.15321
| 8:55 | 10.7669 | 0.15362
| 8:55 | 10.7672 | 0.15403
| 8:55 | 10.7675 | 0.15444
| 8:55 | 10.7678 | 0.15486
| 8:55 | 10.7681 | 0.15526
| 8:55 | 10.7683 | 0.15567
| 8:55 | 10.7686 | 0.15608
| 8:55 | 10.7689 | 0.15648
| 8:55 | 10.7692 | 0.15688
| 8:55 | 10.7694 | 0.15728
| 8:55 | 10.7697 | 0.15768
| 8:55 | 10.77 | 0.15808
| 8:55 | 10.7703 | 0.15848
| 8:55 | 10.7706 | 0.15887
| 8:55 | 10.7708 | 0.15926
| 8:55 | 10.7711 | 0.15965
| 8:55 | 10.7714 | 0.16004
| 8:55 | 10.7717 | 0.16043
| 8:55 | 10.7719 | 0.16081
| 8:55 | 10.7722 | 0.1612
| 8:55 | 10.7725 | 0.16159
| 8:55 | 10.7728 | 0.16198
| 8:55 | 10.7731 | 0.16238
| 8:55 | 10.7733 | 0.16278
| 8:55 | 10.7736 | 0.16319
| 8:55 | 10.7739 | 0.1636
| 8:55 | 10.7742 | 0.16401
| 8:55 | 10.7744 | 0.16443
| 8:55 | 10.7747 | 0.16485
| 8:55 | 10.775 | 0.16527
| 8:55 | 10.7753 | 0.1657
| 8:55 | 10.7756 | 0.16612
| 8:55 | 10.7758 | 0.16655
| 8:55 | 10.7761 | 0.16698
| 8:55 | 10.7764 | 0.16741
| 8:55 | 10.7767 | 0.16784
| 8:55 | 10.7769 | 0.16827
| 8:55 | 10.7772 | 0.16869
| 8:55 | 10.7775 | 0.16912
| 8:55 | 10.7778 | 0.16955
| 8:55 | 10.7781 | 0.16998
| 8:56 | 10.7783 | 0.17041
| 8:56 | 10.7786 | 0.17084
| 8:56 | 10.7789 | 0.17128
| 8:56 | 10.7792 | 0.17171
| 8:56 | 10.7794 | 0.17214
| 8:56 | 10.7797 | 0.17257
| 8:56 | 10.78 | 0.173
| 8:56 | 10.7803 | 0.17343
| 8:56 | 10.7806 | 0.17386
| 8:56 | 10.7808 | 0.17429
| 8:56 | 10.7811 | 0.17472
| 8:56 | 10.7814 | 0.17515
| 8:56 | 10.7817 | 0.17558
| 8:56 | 10.7819 | 0.17601
| 8:56 | 10.7822 | 0.17643
| 8:56 | 10.7825 | 0.17686
| 8:56 | 10.7828 | 0.17728
| 8:56 | 10.7831 | 0.17771
| 8:56 | 10.7833 | 0.17813
| 8:56 | 10.7836 | 0.17855
| 8:56 | 10.7839 | 0.17897
| 8:56 | 10.7842 | 0.17939
| 8:56 | 10.7844 | 0.17981
| 8:56 | 10.7847 | 0.18023
| 8:56 | 10.785 | 0.18065
| 8:56 | 10.7853 | 0.18107
| 8:56 | 10.7856 | 0.18149
| 8:56 | 10.7858 | 0.18191
| 8:56 | 10.7861 | 0.18233
| 8:56 | 10.7864 | 0.18275
| 8:56 | 10.7867 | 0.18317
| 8:56 | 10.7869 | 0.1836
| 8:56 | 10.7872 | 0.18403
| 8:56 | 10.7875 | 0.18446
| 8:56 | 10.7878 | 0.18489
| 8:56 | 10.7881 | 0.18533
| 8:56 | 10.7883 | 0.18576
| 8:56 | 10.7886 | 0.1862
| 8:56 | 10.7889 | 0.18664
| 8:56 | 10.7892 | 0.18708
| 8:56 | 10.7894 | 0.18752
| 8:56 | 10.7897 | 0.18796
| 8:56 | 10.79 | 0.1884
| 8:56 | 10.7903 | 0.18884
| 8:56 | 10.7906 | 0.18929
| 8:56 | 10.7908 | 0.18973
| 8:56 | 10.7911 | 0.19017
| 8:56 | 10.7914 | 0.19061
| 8:56 | 10.7917 | 0.19106
| 8:56 | 10.7919 | 0.1915
| 8:56 | 10.7922 | 0.19195
| 8:56 | 10.7925 | 0.19239
| 8:56 | 10.7928 | 0.19284
| 8:56 | 10.7931 | 0.19328
| 8:56 | 10.7933 | 0.19373
| 8:56 | 10.7936 | 0.19417
| 8:56 | 10.7939 | 0.19462
| 8:56 | 10.7942 | 0.19506
| 8:56 | 10.7944 | 0.19551
| 8:56 | 10.7947 | 0.19596
| 8:56 | 10.795 | 0.19641
| 8:57 | 10.7953 | 0.19685
| 8:57 | 10.7956 | 0.1973
| 8:57 | 10.7958 | 0.19774
| 8:57 | 10.7961 | 0.19819
| 8:57 | 10.7964 | 0.19864
| 8:57 | 10.7967 | 0.19908
| 8:57 | 10.7969 | 0.19953
| 8:57 | 10.7972 | 0.19997
| 8:57 | 10.7975 | 0.20042
| 8:57 | 10.7978 | 0.20086
| 8:57 | 10.7981 | 0.20131
| 8:57 | 10.7983 | 0.20175
| 8:57 | 10.7986 | 0.2022
| 8:57 | 10.7989 | 0.20264
| 8:57 | 10.7992 | 0.20309
| 8:57 | 10.7994 | 0.20353
| 8:57 | 10.7997 | 0.20398
| 8:57 | 10.8 | 0.20442
| 8:57 | 10.8003 | 0.20487
| 8:57 | 10.8006 | 0.20531
| 8:57 | 10.8008 | 0.20576
| 8:57 | 10.8011 | 0.2062
| 8:57 | 10.8014 | 0.20665
| 8:57 | 10.8017 | 0.20709
| 8:57 | 10.8019 | 0.20753
| 8:57 | 10.8022 | 0.20798
| 8:57 | 10.8025 | 0.20842
| 8:57 | 10.8028 | 0.20887
| 8:57 | 10.8031 | 0.20931
| 8:57 | 10.8033 | 0.20976
| 8:57 | 10.8036 | 0.2102
| 8:57 | 10.8039 | 0.21064
| 8:57 | 10.8042 | 0.21109
| 8:57 | 10.8044 | 0.21153
| 8:57 | 10.8047 | 0.21197
| 8:57 | 10.805 | 0.21241
| 8:57 | 10.8053 | 0.21286
| 8:57 | 10.8056 | 0.2133
| 8:57 | 10.8058 | 0.21374
| 8:57 | 10.8061 | 0.21418
| 8:57 | 10.8064 | 0.21462
| 8:57 | 10.8067 | 0.21506
| 8:57 | 10.8069 | 0.2155
| 8:57 | 10.8072 | 0.21593
| 8:57 | 10.8075 | 0.21636
| 8:57 | 10.8078 | 0.21679
| 8:57 | 10.8081 | 0.21722
| 8:57 | 10.8083 | 0.21765
| 8:57 | 10.8086 | 0.21807
| 8:57 | 10.8089 | 0.2185
| 8:57 | 10.8092 | 0.21892
| 8:57 | 10.8094 | 0.21934
| 8:57 | 10.8097 | 0.21976
| 8:57 | 10.81 | 0.22017
| 8:57 | 10.8103 | 0.22058
| 8:57 | 10.8106 | 0.22099
| 8:57 | 10.8108 | 0.2214
| 8:57 | 10.8111 | 0.22181
| 8:57 | 10.8114 | 0.22221
| 8:58 | 10.8117 | 0.2226
| 8:58 | 10.8119 | 0.22299
| 8:58 | 10.8122 | 0.22337
| 8:58 | 10.8125 | 0.22375
| 8:58 | 10.8128 | 0.22412
| 8:58 | 10.8131 | 0.22447
| 8:58 | 10.8133 | 0.22481
| 8:58 | 10.8136 | 0.22514
| 8:58 | 10.8139 | 0.22546
| 8:58 | 10.8142 | 0.22576
| 8:58 | 10.8144 | 0.22605
| 8:58 | 10.8147 | 0.22634
| 8:58 | 10.815 | 0.22661
| 8:58 | 10.8153 | 0.22688
| 8:58 | 10.8156 | 0.22714
| 8:58 | 10.8158 | 0.22738
| 8:58 | 10.8161 | 0.22762
| 8:58 | 10.8164 | 0.22785
| 8:58 | 10.8167 | 0.22806
| 8:58 | 10.8169 | 0.22827
| 8:58 | 10.8172 | 0.22849
| 8:58 | 10.8175 | 0.2287
| 8:58 | 10.8178 | 0.22893
| 8:58 | 10.8181 | 0.22916
| 8:58 | 10.8183 | 0.22938
| 8:58 | 10.8186 | 0.22961
| 8:58 | 10.8189 | 0.22983
| 8:58 | 10.8192 | 0.23005
| 8:58 | 10.8194 | 0.23027
| 8:58 | 10.8197 | 0.23049
| 8:58 | 10.82 | 0.2307
| 8:58 | 10.8203 | 0.23092
| 8:58 | 10.8206 | 0.23113
| 8:58 | 10.8208 | 0.23134
| 8:58 | 10.8211 | 0.23155
| 8:58 | 10.8214 | 0.23175
| 8:58 | 10.8217 | 0.23195
| 8:58 | 10.8219 | 0.23215
| 8:58 | 10.8222 | 0.23234
| 8:58 | 10.8225 | 0.23252
| 8:58 | 10.8228 | 0.23271
| 8:58 | 10.8231 | 0.23289
| 8:58 | 10.8233 | 0.23307
| 8:58 | 10.8236 | 0.23325
| 8:58 | 10.8239 | 0.23342
| 8:58 | 10.8242 | 0.2336
| 8:58 | 10.8244 | 0.23378
| 8:58 | 10.8247 | 0.23396
| 8:58 | 10.825 | 0.23414
| 8:58 | 10.8253 | 0.23431
| 8:58 | 10.8256 | 0.23448
| 8:58 | 10.8258 | 0.23466
| 8:58 | 10.8261 | 0.23483
| 8:58 | 10.8264 | 0.23499
| 8:58 | 10.8267 | 0.23515
| 8:58 | 10.8269 | 0.2353
| 8:58 | 10.8272 | 0.23546
| 8:58 | 10.8275 | 0.23562
| 8:58 | 10.8278 | 0.23579
| 8:58 | 10.8281 | 0.23597
| 8:58 | 10.8283 | 0.23617
| 8:59 | 10.8286 | 0.23637
| 8:59 | 10.8289 | 0.23658
| 8:59 | 10.8292 | 0.23678
| 8:59 | 10.8294 | 0.23699
| 8:59 | 10.8297 | 0.2372
| 8:59 | 10.83 | 0.2374
| 8:59 | 10.8303 | 0.23761
| 8:59 | 10.8306 | 0.23781
| 8:59 | 10.8308 | 0.238
| 8:59 | 10.8311 | 0.23818
| 8:59 | 10.8314 | 0.23836
| 8:59 | 10.8317 | 0.23853
| 8:59 | 10.8319 | 0.2387
| 8:59 | 10.8322 | 0.23885
| 8:59 | 10.8325 | 0.23901
| 8:59 | 10.8328 | 0.23915
| 8:59 | 10.8331 | 0.23929
| 8:59 | 10.8333 | 0.23942
| 8:59 | 10.8336 | 0.23955
| 8:59 | 10.8339 | 0.23967
| 8:59 | 10.8342 | 0.23979
| 8:59 | 10.8344 | 0.2399
| 8:59 | 10.8347 | 0.24002
| 8:59 | 10.835 | 0.24014
| 8:59 | 10.8353 | 0.24025
| 8:59 | 10.8356 | 0.24035
| 8:59 | 10.8358 | 0.24045
| 8:59 | 10.8361 | 0.24053
| 8:59 | 10.8364 | 0.24061
| 8:59 | 10.8367 | 0.24066
| 8:59 | 10.8369 | 0.24071
| 8:59 | 10.8372 | 0.24075
| 8:59 | 10.8375 | 0.24078
| 8:59 | 10.8378 | 0.24081
| 8:59 | 10.8381 | 0.24084
| 8:59 | 10.8383 | 0.24086
| 8:59 | 10.8386 | 0.24088
| 8:59 | 10.8389 | 0.2409
| 8:59 | 10.8392 | 0.24091
| 8:59 | 10.8394 | 0.24091
| 8:59 | 10.8397 | 0.2409
| 8:59 | 10.84 | 0.24089
| 8:59 | 10.8403 | 0.24088
| 8:59 | 10.8406 | 0.24086
| 8:59 | 10.8408 | 0.24084
| 8:59 | 10.8411 | 0.24081
| 8:59 | 10.8414 | 0.24077
| 8:59 | 10.8417 | 0.24074
| 8:59 | 10.8419 | 0.24069
| 8:59 | 10.8422 | 0.24065
| 8:59 | 10.8425 | 0.24061
| 8:59 | 10.8428 | 0.24056
| 8:59 | 10.8431 | 0.24051
| 8:59 | 10.8433 | 0.24046
| 8:59 | 10.8436 | 0.24041
| 8:59 | 10.8439 | 0.24036
| 8:59 | 10.8442 | 0.2403
| 8:59 | 10.8444 | 0.24025
| 8:59 | 10.8447 | 0.24019
| 9:00 | 10.845 | 0.24013
| 9:00 | 10.8453 | 0.24008
| 9:00 | 10.8456 | 0.24002
| 9:00 | 10.8458 | 0.23996
| 9:00 | 10.8461 | 0.2399
| 9:00 | 10.8464 | 0.23985
| 9:00 | 10.8467 | 0.23979
| 9:00 | 10.8469 | 0.23974
| 9:00 | 10.8472 | 0.23969
| 9:00 | 10.8475 | 0.23964
| 9:00 | 10.8478 | 0.23959
| 9:00 | 10.8481 | 0.23955
| 9:00 | 10.8483 | 0.2395
| 9:00 | 10.8486 | 0.23945
| 9:00 | 10.8489 | 0.23941
| 9:00 | 10.8492 | 0.23936
| 9:00 | 10.8494 | 0.23932
| 9:00 | 10.8497 | 0.23928
| 9:00 | 10.85 | 0.23924
| 9:00 | 10.8503 | 0.2392
| 9:00 | 10.8506 | 0.23916
| 9:00 | 10.8508 | 0.23912
| 9:00 | 10.8511 | 0.23908
| 9:00 | 10.8514 | 0.23904
| 9:00 | 10.8517 | 0.239
| 9:00 | 10.8519 | 0.23896
| 9:00 | 10.8522 | 0.23892
| 9:00 | 10.8525 | 0.23888
| 9:00 | 10.8528 | 0.23884
| 9:00 | 10.8531 | 0.23881
| 9:00 | 10.8533 | 0.23877
| 9:00 | 10.8536 | 0.23873
| 9:00 | 10.8539 | 0.23869
| 9:00 | 10.8542 | 0.23865
| 9:00 | 10.8544 | 0.23861
| 9:00 | 10.8547 | 0.23857
| 9:00 | 10.855 | 0.23853
| 9:00 | 10.8553 | 0.23849
| 9:00 | 10.8556 | 0.23845
| 9:00 | 10.8558 | 0.23841
| 9:00 | 10.8561 | 0.23837
| 9:00 | 10.8564 | 0.23833
| 9:00 | 10.8567 | 0.23829
| 9:00 | 10.8569 | 0.23825
| 9:00 | 10.8572 | 0.23821
| 9:00 | 10.8575 | 0.23817
| 9:00 | 10.8578 | 0.23812
| 9:00 | 10.8581 | 0.23808
| 9:00 | 10.8583 | 0.23804
| 9:00 | 10.8586 | 0.23799
| 9:00 | 10.8589 | 0.23795
| 9:00 | 10.8592 | 0.23791
| 9:00 | 10.8594 | 0.23786
| 9:00 | 10.8597 | 0.23782
| 9:00 | 10.86 | 0.23779
| 9:00 | 10.8603 | 0.23775
| 9:00 | 10.8606 | 0.23771
| 9:00 | 10.8608 | 0.23768
| 9:00 | 10.8611 | 0.23764
| 9:00 | 10.8614 | 0.23761
| 9:00 | 10.8617 | 0.23758
| 9:01 | 10.8619 | 0.23754
| 9:01 | 10.8622 | 0.23751
| 9:01 | 10.8625 | 0.23748
| 9:01 | 10.8628 | 0.23745
| 9:01 | 10.8631 | 0.23742
| 9:01 | 10.8633 | 0.23739
| 9:01 | 10.8636 | 0.23737
| 9:01 | 10.8639 | 0.23734
| 9:01 | 10.8642 | 0.23732
| 9:01 | 10.8644 | 0.23729
| 9:01 | 10.8647 | 0.23726
| 9:01 | 10.865 | 0.23724
| 9:01 | 10.8653 | 0.23722
| 9:01 | 10.8656 | 0.23719
| 9:01 | 10.8658 | 0.23717
| 9:01 | 10.8661 | 0.23714
| 9:01 | 10.8664 | 0.23712
| 9:01 | 10.8667 | 0.2371
| 9:01 | 10.8669 | 0.23707
| 9:01 | 10.8672 | 0.23705
| 9:01 | 10.8675 | 0.23703
| 9:01 | 10.8678 | 0.237
| 9:01 | 10.8681 | 0.23697
| 9:01 | 10.8683 | 0.23694
| 9:01 | 10.8686 | 0.23691
| 9:01 | 10.8689 | 0.23686
| 9:01 | 10.8692 | 0.23679
| 9:01 | 10.8694 | 0.23672
| 9:01 | 10.8697 | 0.23663
| 9:01 | 10.87 | 0.23652
| 9:01 | 10.8703 | 0.23638
| 9:01 | 10.8706 | 0.23623
| 9:01 | 10.8708 | 0.23606
| 9:01 | 10.8711 | 0.23586
| 9:01 | 10.8714 | 0.23565
| 9:01 | 10.8717 | 0.23544
| 9:01 | 10.8719 | 0.23522
| 9:01 | 10.8722 | 0.235
| 9:01 | 10.8725 | 0.23478
| 9:01 | 10.8728 | 0.23456
| 9:01 | 10.8731 | 0.23435
| 9:01 | 10.8733 | 0.23415
| 9:01 | 10.8736 | 0.23396
| 9:01 | 10.8739 | 0.2338
| 9:01 | 10.8742 | 0.23365
| 9:01 | 10.8744 | 0.23352
| 9:01 | 10.8747 | 0.23341
| 9:01 | 10.875 | 0.23331
| 9:01 | 10.8753 | 0.23323
| 9:01 | 10.8756 | 0.23317
| 9:01 | 10.8758 | 0.23312
| 9:01 | 10.8761 | 0.23308
| 9:01 | 10.8764 | 0.23304
| 9:01 | 10.8767 | 0.233
| 9:01 | 10.8769 | 0.23297
| 9:01 | 10.8772 | 0.23293
| 9:01 | 10.8775 | 0.2329
| 9:01 | 10.8778 | 0.23287
| 9:01 | 10.8781 | 0.23284
| 9:02 | 10.8783 | 0.2328
| 9:02 | 10.8786 | 0.23277
| 9:02 | 10.8789 | 0.23274
| 9:02 | 10.8792 | 0.2327
| 9:02 | 10.8794 | 0.23266
| 9:02 | 10.8797 | 0.23261
| 9:02 | 10.88 | 0.23255
| 9:02 | 10.8803 | 0.23249
| 9:02 | 10.8806 | 0.23243
| 9:02 | 10.8808 | 0.23235
| 9:02 | 10.8811 | 0.23227
| 9:02 | 10.8814 | 0.23217
| 9:02 | 10.8817 | 0.23205
| 9:02 | 10.8819 | 0.23193
| 9:02 | 10.8822 | 0.23179
| 9:02 | 10.8825 | 0.23164
| 9:02 | 10.8828 | 0.23148
| 9:02 | 10.8831 | 0.2313
| 9:02 | 10.8833 | 0.23112
| 9:02 | 10.8836 | 0.23092
| 9:02 | 10.8839 | 0.23071
| 9:02 | 10.8842 | 0.23049
| 9:02 | 10.8844 | 0.23027
| 9:02 | 10.8847 | 0.23003
| 9:02 | 10.885 | 0.22979
| 9:02 | 10.8853 | 0.22953
| 9:02 | 10.8856 | 0.22927
| 9:02 | 10.8858 | 0.229
| 9:02 | 10.8861 | 0.22873
| 9:02 | 10.8864 | 0.22844
| 9:02 | 10.8867 | 0.22815
| 9:02 | 10.8869 | 0.22784
| 9:02 | 10.8872 | 0.22753
| 9:02 | 10.8875 | 0.22722
| 9:02 | 10.8878 | 0.2269
| 9:02 | 10.8881 | 0.22657
| 9:02 | 10.8883 | 0.22623
| 9:02 | 10.8886 | 0.22588
| 9:02 | 10.8889 | 0.22553
| 9:02 | 10.8892 | 0.22516
| 9:02 | 10.8894 | 0.22479
| 9:02 | 10.8897 | 0.22442
| 9:02 | 10.89 | 0.22404
| 9:02 | 10.8903 | 0.22366
| 9:02 | 10.8906 | 0.22328
| 9:02 | 10.8908 | 0.2229
| 9:02 | 10.8911 | 0.22252
| 9:02 | 10.8914 | 0.22214
| 9:02 | 10.8917 | 0.22176
| 9:02 | 10.8919 | 0.22137
| 9:02 | 10.8922 | 0.22099
| 9:02 | 10.8925 | 0.22061
| 9:02 | 10.8928 | 0.22023
| 9:02 | 10.8931 | 0.21985
| 9:02 | 10.8933 | 0.21947
| 9:02 | 10.8936 | 0.21909
| 9:02 | 10.8939 | 0.21871
| 9:02 | 10.8942 | 0.21833
| 9:02 | 10.8944 | 0.21795
| 9:02 | 10.8947 | 0.21757
| 9:02 | 10.895 | 0.2172
| 9:03 | 10.8953 | 0.21682
| 9:03 | 10.8956 | 0.21645
| 9:03 | 10.8958 | 0.21608
| 9:03 | 10.8961 | 0.2157
| 9:03 | 10.8964 | 0.21533
| 9:03 | 10.8967 | 0.21496
| 9:03 | 10.8969 | 0.21459
| 9:03 | 10.8972 | 0.21422
| 9:03 | 10.8975 | 0.21385
| 9:03 | 10.8978 | 0.21349
| 9:03 | 10.8981 | 0.21313
| 9:03 | 10.8983 | 0.21277
| 9:03 | 10.8986 | 0.21244
| 9:03 | 10.8989 | 0.21211
| 9:03 | 10.8992 | 0.21181
| 9:03 | 10.8994 | 0.21152
| 9:03 | 10.8997 | 0.21124
| 9:03 | 10.9 | 0.21099
| 9:03 | 10.9003 | 0.21075
| 9:03 | 10.9006 | 0.21052
| 9:03 | 10.9008 | 0.21032
| 9:03 | 10.9011 | 0.21012
| 9:03 | 10.9014 | 0.20994
| 9:03 | 10.9017 | 0.20978
| 9:03 | 10.9019 | 0.20963
| 9:03 | 10.9022 | 0.2095
| 9:03 | 10.9025 | 0.20939
| 9:03 | 10.9028 | 0.20928
| 9:03 | 10.9031 | 0.20919
| 9:03 | 10.9033 | 0.2091
| 9:03 | 10.9036 | 0.20901
| 9:03 | 10.9039 | 0.20892
| 9:03 | 10.9042 | 0.20883
| 9:03 | 10.9044 | 0.20874
| 9:03 | 10.9047 | 0.20865
| 9:03 | 10.905 | 0.20856
| 9:03 | 10.9053 | 0.20848
| 9:03 | 10.9056 | 0.2084
| 9:03 | 10.9058 | 0.20833
| 9:03 | 10.9061 | 0.20825
| 9:03 | 10.9064 | 0.20818
| 9:03 | 10.9067 | 0.2081
| 9:03 | 10.9069 | 0.20802
| 9:03 | 10.9072 | 0.20794
| 9:03 | 10.9075 | 0.20785
| 9:03 | 10.9078 | 0.20776
| 9:03 | 10.9081 | 0.20767
| 9:03 | 10.9083 | 0.20757
| 9:03 | 10.9086 | 0.20747
| 9:03 | 10.9089 | 0.20735
| 9:03 | 10.9092 | 0.20722
| 9:03 | 10.9094 | 0.20708
| 9:03 | 10.9097 | 0.20693
| 9:03 | 10.91 | 0.20676
| 9:03 | 10.9103 | 0.20657
| 9:03 | 10.9106 | 0.20637
| 9:03 | 10.9108 | 0.20615
| 9:03 | 10.9111 | 0.20593
| 9:03 | 10.9114 | 0.20569
| 9:04 | 10.9117 | 0.20543
| 9:04 | 10.9119 | 0.20517
| 9:04 | 10.9122 | 0.2049
| 9:04 | 10.9125 | 0.20462
| 9:04 | 10.9128 | 0.20434
| 9:04 | 10.9131 | 0.20405
| 9:04 | 10.9133 | 0.20375
| 9:04 | 10.9136 | 0.20344
| 9:04 | 10.9139 | 0.20313
| 9:04 | 10.9142 | 0.2028
| 9:04 | 10.9144 | 0.20248
| 9:04 | 10.9147 | 0.20216
| 9:04 | 10.915 | 0.20184
| 9:04 | 10.9153 | 0.20153
| 9:04 | 10.9156 | 0.20122
| 9:04 | 10.9158 | 0.20092
| 9:04 | 10.9161 | 0.20062
| 9:04 | 10.9164 | 0.20033
| 9:04 | 10.9167 | 0.20004
| 9:04 | 10.9169 | 0.19976
| 9:04 | 10.9172 | 0.19949
| 9:04 | 10.9175 | 0.19922
| 9:04 | 10.9178 | 0.19896
| 9:04 | 10.9181 | 0.19871
| 9:04 | 10.9183 | 0.19845
| 9:04 | 10.9186 | 0.19821
| 9:04 | 10.9189 | 0.19796
| 9:04 | 10.9192 | 0.19771
| 9:04 | 10.9194 | 0.19747
| 9:04 | 10.9197 | 0.19723
| 9:04 | 10.92 | 0.19699
| 9:04 | 10.9203 | 0.19675
| 9:04 | 10.9206 | 0.19652
| 9:04 | 10.9208 | 0.1963
| 9:04 | 10.9211 | 0.19608
| 9:04 | 10.9214 | 0.19587
| 9:04 | 10.9217 | 0.1957
| 9:04 | 10.9219 | 0.19554
| 9:04 | 10.9222 | 0.1954
| 9:04 | 10.9225 | 0.19528
| 9:04 | 10.9228 | 0.19518
| 9:04 | 10.9231 | 0.19509
| 9:04 | 10.9233 | 0.195
| 9:04 | 10.9236 | 0.1949
| 9:04 | 10.9239 | 0.1948
| 9:04 | 10.9242 | 0.19469
| 9:04 | 10.9244 | 0.19458
| 9:04 | 10.9247 | 0.19447
| 9:04 | 10.925 | 0.19433
| 9:04 | 10.9253 | 0.19416
| 9:04 | 10.9256 | 0.19399
| 9:04 | 10.9258 | 0.19379
| 9:04 | 10.9261 | 0.19356
| 9:04 | 10.9264 | 0.19331
| 9:04 | 10.9267 | 0.19303
| 9:04 | 10.9269 | 0.19274
| 9:04 | 10.9272 | 0.19243
| 9:04 | 10.9275 | 0.19211
| 9:04 | 10.9278 | 0.19178
| 9:04 | 10.9281 | 0.19144
| 9:04 | 10.9283 | 0.1911
| 9:05 | 10.9286 | 0.19076
| 9:05 | 10.9289 | 0.19041
| 9:05 | 10.9292 | 0.19006
| 9:05 | 10.9294 | 0.18971
| 9:05 | 10.9297 | 0.18937
| 9:05 | 10.93 | 0.18902
| 9:05 | 10.9303 | 0.18867
| 9:05 | 10.9306 | 0.18832
| 9:05 | 10.9308 | 0.18797
| 9:05 | 10.9311 | 0.18762
| 9:05 | 10.9314 | 0.18727
| 9:05 | 10.9317 | 0.18692
| 9:05 | 10.9319 | 0.18657
| 9:05 | 10.9322 | 0.18623
| 9:05 | 10.9325 | 0.18588
| 9:05 | 10.9328 | 0.18553
| 9:05 | 10.9331 | 0.18518
| 9:05 | 10.9333 | 0.18484
| 9:05 | 10.9336 | 0.18449
| 9:05 | 10.9339 | 0.18415
| 9:05 | 10.9342 | 0.1838
| 9:05 | 10.9344 | 0.18345
| 9:05 | 10.9347 | 0.18311
| 9:05 | 10.935 | 0.18276
| 9:05 | 10.9353 | 0.18241
| 9:05 | 10.9356 | 0.18207
| 9:05 | 10.9358 | 0.18172
| 9:05 | 10.9361 | 0.18138
| 9:05 | 10.9364 | 0.18103
| 9:05 | 10.9367 | 0.18068
| 9:05 | 10.9369 | 0.18034
| 9:05 | 10.9372 | 0.17999
| 9:05 | 10.9375 | 0.17965
| 9:05 | 10.9378 | 0.1793
| 9:05 | 10.9381 | 0.17895
| 9:05 | 10.9383 | 0.17861
| 9:05 | 10.9386 | 0.17826
| 9:05 | 10.9389 | 0.17792
| 9:05 | 10.9392 | 0.17757
| 9:05 | 10.9394 | 0.17723
| 9:05 | 10.9397 | 0.17688
| 9:05 | 10.94 | 0.17654
| 9:05 | 10.9403 | 0.1762
| 9:05 | 10.9406 | 0.17586
| 9:05 | 10.9408 | 0.17551
| 9:05 | 10.9411 | 0.17517
| 9:05 | 10.9414 | 0.17483
| 9:05 | 10.9417 | 0.17449
| 9:05 | 10.9419 | 0.17415
| 9:05 | 10.9422 | 0.1738
| 9:05 | 10.9425 | 0.17346
| 9:05 | 10.9428 | 0.17312
| 9:05 | 10.9431 | 0.17278
| 9:05 | 10.9433 | 0.17244
| 9:05 | 10.9436 | 0.17211
| 9:05 | 10.9439 | 0.17177
| 9:05 | 10.9442 | 0.17144
| 9:05 | 10.9444 | 0.17112
| 9:05 | 10.9447 | 0.1708
| 9:06 | 10.945 | 0.17049
| 9:06 | 10.9453 | 0.1702
| 9:06 | 10.9456 | 0.16992
| 9:06 | 10.9458 | 0.16965
| 9:06 | 10.9461 | 0.1694
| 9:06 | 10.9464 | 0.16916
| 9:06 | 10.9467 | 0.16894
| 9:06 | 10.9469 | 0.16873
| 9:06 | 10.9472 | 0.16854
| 9:06 | 10.9475 | 0.16835
| 9:06 | 10.9478 | 0.16816
| 9:06 | 10.9481 | 0.16796
| 9:06 | 10.9483 | 0.16775
| 9:06 | 10.9486 | 0.16753
| 9:06 | 10.9489 | 0.1673
| 9:06 | 10.9492 | 0.16705
| 9:06 | 10.9494 | 0.1668
| 9:06 | 10.9497 | 0.16653
| 9:06 | 10.95 | 0.16626
| 9:06 | 10.9503 | 0.16597
| 9:06 | 10.9506 | 0.16567
| 9:06 | 10.9508 | 0.16537
| 9:06 | 10.9511 | 0.16506
| 9:06 | 10.9514 | 0.16475
| 9:06 | 10.9517 | 0.16444
| 9:06 | 10.9519 | 0.16414
| 9:06 | 10.9522 | 0.16383
| 9:06 | 10.9525 | 0.16353
| 9:06 | 10.9528 | 0.16322
| 9:06 | 10.9531 | 0.16292
| 9:06 | 10.9533 | 0.16262
| 9:06 | 10.9536 | 0.16232
| 9:06 | 10.9539 | 0.16201
| 9:06 | 10.9542 | 0.16171
| 9:06 | 10.9544 | 0.1614
| 9:06 | 10.9547 | 0.16109
| 9:06 | 10.955 | 0.16078
| 9:06 | 10.9553 | 0.16047
| 9:06 | 10.9556 | 0.16016
| 9:06 | 10.9558 | 0.15984
| 9:06 | 10.9561 | 0.15953
| 9:06 | 10.9564 | 0.15921
| 9:06 | 10.9567 | 0.1589
| 9:06 | 10.9569 | 0.15859
| 9:06 | 10.9572 | 0.15828
| 9:06 | 10.9575 | 0.15797
| 9:06 | 10.9578 | 0.15766
| 9:06 | 10.9581 | 0.15735
| 9:06 | 10.9583 | 0.15704
| 9:06 | 10.9586 | 0.15674
| 9:06 | 10.9589 | 0.15644
| 9:06 | 10.9592 | 0.15615
| 9:06 | 10.9594 | 0.15588
| 9:06 | 10.9597 | 0.15564
| 9:06 | 10.96 | 0.1554
| 9:06 | 10.9603 | 0.15519
| 9:06 | 10.9606 | 0.15499
| 9:06 | 10.9608 | 0.15481
| 9:06 | 10.9611 | 0.15464
| 9:06 | 10.9614 | 0.15448
| 9:06 | 10.9617 | 0.15433
| 9:07 | 10.9619 | 0.15419
| 9:07 | 10.9622 | 0.15404
| 9:07 | 10.9625 | 0.1539
| 9:07 | 10.9628 | 0.15376
| 9:07 | 10.9631 | 0.15362
| 9:07 | 10.9633 | 0.15349
| 9:07 | 10.9636 | 0.15336
| 9:07 | 10.9639 | 0.15323
| 9:07 | 10.9642 | 0.15311
| 9:07 | 10.9644 | 0.15299
| 9:07 | 10.9647 | 0.15288
| 9:07 | 10.965 | 0.15276
| 9:07 | 10.9653 | 0.15266
| 9:07 | 10.9656 | 0.15255
| 9:07 | 10.9658 | 0.15246
| 9:07 | 10.9661 | 0.15236
| 9:07 | 10.9664 | 0.15227
| 9:07 | 10.9667 | 0.15219
| 9:07 | 10.9669 | 0.15211
| 9:07 | 10.9672 | 0.15203
| 9:07 | 10.9675 | 0.15197
| 9:07 | 10.9678 | 0.15192
| 9:07 | 10.9681 | 0.15188
| 9:07 | 10.9683 | 0.15187
| 9:07 | 10.9686 | 0.15186
| 9:07 | 10.9689 | 0.15187
| 9:07 | 10.9692 | 0.15189
| 9:07 | 10.9694 | 0.15191
| 9:07 | 10.9697 | 0.15191
| 9:07 | 10.97 | 0.15191
| 9:07 | 10.9703 | 0.15192
| 9:07 | 10.9706 | 0.15194
| 9:07 | 10.9708 | 0.15197
| 9:07 | 10.9711 | 0.152
| 9:07 | 10.9714 | 0.15206
| 9:07 | 10.9717 | 0.15213
| 9:07 | 10.9719 | 0.15221
| 9:07 | 10.9722 | 0.15229
| 9:07 | 10.9725 | 0.15238
| 9:07 | 10.9728 | 0.15246
| 9:07 | 10.9731 | 0.15253
| 9:07 | 10.9733 | 0.15258
| 9:07 | 10.9736 | 0.15263
| 9:07 | 10.9739 | 0.15267
| 9:07 | 10.9742 | 0.1527
| 9:07 | 10.9744 | 0.15271
| 9:07 | 10.9747 | 0.15272
| 9:07 | 10.975 | 0.1527
| 9:07 | 10.9753 | 0.15266
| 9:07 | 10.9756 | 0.1526
| 9:07 | 10.9758 | 0.15251
| 9:07 | 10.9761 | 0.15241
| 9:07 | 10.9764 | 0.15229
| 9:07 | 10.9767 | 0.15217
| 9:07 | 10.9769 | 0.15205
| 9:07 | 10.9772 | 0.15192
| 9:07 | 10.9775 | 0.15179
| 9:07 | 10.9778 | 0.15164
| 9:07 | 10.9781 | 0.1515
| 9:08 | 10.9783 | 0.15134
| 9:08 | 10.9786 | 0.15118
| 9:08 | 10.9789 | 0.15101
| 9:08 | 10.9792 | 0.15084
| 9:08 | 10.9794 | 0.15066
| 9:08 | 10.9797 | 0.15046
| 9:08 | 10.98 | 0.15026
| 9:08 | 10.9803 | 0.15006
| 9:08 | 10.9806 | 0.14984
| 9:08 | 10.9808 | 0.1496
| 9:08 | 10.9811 | 0.14926
| 9:08 | 10.9814 | 0.14891
| 9:08 | 10.9817 | 0.14856
| 9:08 | 10.9819 | 0.14821
| 9:08 | 10.9822 | 0.14786
| 9:08 | 10.9825 | 0.1475
| 9:08 | 10.9828 | 0.14714
| 9:08 | 10.9831 | 0.14678
| 9:08 | 10.9833 | 0.14641
| 9:08 | 10.9836 | 0.14604
| 9:08 | 10.9839 | 0.14568
| 9:08 | 10.9842 | 0.14531
| 9:08 | 10.9844 | 0.14494
| 9:08 | 10.9847 | 0.14457
| 9:08 | 10.985 | 0.1442
| 9:08 | 10.9853 | 0.14383
| 9:08 | 10.9856 | 0.14347
| 9:08 | 10.9858 | 0.1431
| 9:08 | 10.9861 | 0.14273
| 9:08 | 10.9864 | 0.14237
| 9:08 | 10.9867 | 0.142
| 9:08 | 10.9869 | 0.14164
| 9:08 | 10.9872 | 0.14128
| 9:08 | 10.9875 | 0.14092
| 9:08 | 10.9878 | 0.14057
| 9:08 | 10.9881 | 0.14021
| 9:08 | 10.9883 | 0.13986
| 9:08 | 10.9886 | 0.13951
| 9:08 | 10.9889 | 0.13916
| 9:08 | 10.9892 | 0.13881
| 9:08 | 10.9894 | 0.13846
| 9:08 | 10.9897 | 0.13812
| 9:08 | 10.99 | 0.13777
| 9:08 | 10.9903 | 0.13742
| 9:08 | 10.9906 | 0.13708
| 9:08 | 10.9908 | 0.13674
| 9:08 | 10.9911 | 0.1364
| 9:08 | 10.9914 | 0.13606
| 9:08 | 10.9917 | 0.13572
| 9:08 | 10.9919 | 0.13538
| 9:08 | 10.9922 | 0.13503
| 9:08 | 10.9925 | 0.13469
| 9:08 | 10.9928 | 0.13434
| 9:08 | 10.9931 | 0.13399
| 9:08 | 10.9933 | 0.13364
| 9:08 | 10.9936 | 0.13328
| 9:08 | 10.9939 | 0.13293
| 9:08 | 10.9942 | 0.13258
| 9:08 | 10.9944 | 0.13222
| 9:08 | 10.9947 | 0.13186
| 9:08 | 10.995 | 0.13151
| 9:09 | 10.9953 | 0.13115
| 9:09 | 10.9956 | 0.1308
| 9:09 | 10.9958 | 0.13044
| 9:09 | 10.9961 | 0.13009
| 9:09 | 10.9964 | 0.12974
| 9:09 | 10.9967 | 0.1294
| 9:09 | 10.9969 | 0.12905
| 9:09 | 10.9972 | 0.12871
| 9:09 | 10.9975 | 0.12837
| 9:09 | 10.9978 | 0.12804
| 9:09 | 10.9981 | 0.1277
| 9:09 | 10.9983 | 0.12735
| 9:09 | 10.9986 | 0.12701
| 9:09 | 10.9989 | 0.12667
| 9:09 | 10.9992 | 0.12632
| 9:09 | 10.9994 | 0.12597
| 9:09 | 10.9997 | 0.12563
| 9:09 | 11 | 0.12528
| 9:09 | 11.0003 | 0.12492
| 9:09 | 11.0006 | 0.12457
| 9:09 | 11.0008 | 0.12421
| 9:09 | 11.0011 | 0.12385
| 9:09 | 11.0014 | 0.12348
| 9:09 | 11.0017 | 0.12311
| 9:09 | 11.0019 | 0.12274
| 9:09 | 11.0022 | 0.12236
| 9:09 | 11.0025 | 0.12198
| 9:09 | 11.0028 | 0.12159
| 9:09 | 11.0031 | 0.12121
| 9:09 | 11.0033 | 0.12082
| 9:09 | 11.0036 | 0.12044
| 9:09 | 11.0039 | 0.12005
| 9:09 | 11.0042 | 0.11966
| 9:09 | 11.0044 | 0.11927
| 9:09 | 11.0047 | 0.11887
| 9:09 | 11.005 | 0.11848
| 9:09 | 11.0053 | 0.11809
| 9:09 | 11.0056 | 0.11769
| 9:09 | 11.0058 | 0.1173
| 9:09 | 11.0061 | 0.1169
| 9:09 | 11.0064 | 0.1165
| 9:09 | 11.0067 | 0.1161
| 9:09 | 11.0069 | 0.1157
| 9:09 | 11.0072 | 0.1153
| 9:09 | 11.0075 | 0.1149
| 9:09 | 11.0078 | 0.1145
| 9:09 | 11.0081 | 0.1141
| 9:09 | 11.0083 | 0.1137
| 9:09 | 11.0086 | 0.1133
| 9:09 | 11.0089 | 0.1129
| 9:09 | 11.0092 | 0.11249
| 9:09 | 11.0094 | 0.11209
| 9:09 | 11.0097 | 0.11169
| 9:09 | 11.01 | 0.11129
| 9:09 | 11.0103 | 0.11088
| 9:09 | 11.0106 | 0.11048
| 9:09 | 11.0108 | 0.11009
| 9:09 | 11.0111 | 0.10969
| 9:09 | 11.0114 | 0.10929
| 9:10 | 11.0117 | 0.10889
| 9:10 | 11.0119 | 0.1085
| 9:10 | 11.0122 | 0.10811
| 9:10 | 11.0125 | 0.10773
| 9:10 | 11.0128 | 0.10734
| 9:10 | 11.0131 | 0.10696
| 9:10 | 11.0133 | 0.10658
| 9:10 | 11.0136 | 0.1062
| 9:10 | 11.0139 | 0.10582
| 9:10 | 11.0142 | 0.10544
| 9:10 | 11.0144 | 0.10505
| 9:10 | 11.0147 | 0.10467
| 9:10 | 11.015 | 0.10429
| 9:10 | 11.0153 | 0.1039
| 9:10 | 11.0156 | 0.10351
| 9:10 | 11.0158 | 0.10312
| 9:10 | 11.0161 | 0.10273
| 9:10 | 11.0164 | 0.10234
| 9:10 | 11.0167 | 0.10194
| 9:10 | 11.0169 | 0.10155
| 9:10 | 11.0172 | 0.10115
| 9:10 | 11.0175 | 0.10076
| 9:10 | 11.0178 | 0.10037
| 9:10 | 11.0181 | 0.099981
| 9:10 | 11.0183 | 0.099596
| 9:10 | 11.0186 | 0.099217
| 9:10 | 11.0189 | 0.098844
| 9:10 | 11.0192 | 0.098477
| 9:10 | 11.0194 | 0.098117
| 9:10 | 11.0197 | 0.097779
| 9:10 | 11.02 | 0.097446
| 9:10 | 11.0203 | 0.097129
| 9:10 | 11.0206 | 0.09683
| 9:10 | 11.0208 | 0.096559
| 9:10 | 11.0211 | 0.096298
| 9:10 | 11.0214 | 0.096076
| 9:10 | 11.0217 | 0.095876
| 9:10 | 11.0219 | 0.095705
| 9:10 | 11.0222 | 0.095543
| 9:10 | 11.0225 | 0.095401
| 9:10 | 11.0228 | 0.095283
| 9:10 | 11.0231 | 0.095177
| 9:10 | 11.0233 | 0.09508
| 9:10 | 11.0236 | 0.094993
| 9:10 | 11.0239 | 0.094916
| 9:10 | 11.0242 | 0.094847
| 9:10 | 11.0244 | 0.094789
| 9:10 | 11.0247 | 0.094739
| 9:10 | 11.025 | 0.094699
| 9:10 | 11.0253 | 0.094664
| 9:10 | 11.0256 | 0.094631
| 9:10 | 11.0258 | 0.094601
| 9:10 | 11.0261 | 0.094567
| 9:10 | 11.0264 | 0.094532
| 9:10 | 11.0267 | 0.094496
| 9:10 | 11.0269 | 0.09446
| 9:10 | 11.0272 | 0.094425
| 9:10 | 11.0275 | 0.094389
| 9:10 | 11.0278 | 0.094354
| 9:10 | 11.0281 | 0.094318
| 9:10 | 11.0283 | 0.094281
| 9:11 | 11.0286 | 0.094243
| 9:11 | 11.0289 | 0.094206
| 9:11 | 11.0292 | 0.094169
| 9:11 | 11.0294 | 0.094131
| 9:11 | 11.0297 | 0.094093
| 9:11 | 11.03 | 0.094055
| 9:11 | 11.0303 | 0.094017
| 9:11 | 11.0306 | 0.093977
| 9:11 | 11.0308 | 0.093936
| 9:11 | 11.0311 | 0.093894
| 9:11 | 11.0314 | 0.093852
| 9:11 | 11.0317 | 0.09381
| 9:11 | 11.0319 | 0.093766
| 9:11 | 11.0322 | 0.093722
| 9:11 | 11.0325 | 0.093677
| 9:11 | 11.0328 | 0.093631
| 9:11 | 11.0331 | 0.093585
| 9:11 | 11.0333 | 0.093538
| 9:11 | 11.0336 | 0.09349
| 9:11 | 11.0339 | 0.093439
| 9:11 | 11.0342 | 0.093385
| 9:11 | 11.0344 | 0.093323
| 9:11 | 11.0347 | 0.093256
| 9:11 | 11.035 | 0.093182
| 9:11 | 11.0353 | 0.093104
| 9:11 | 11.0356 | 0.093019
| 9:11 | 11.0358 | 0.09293
| 9:11 | 11.0361 | 0.092833
| 9:11 | 11.0364 | 0.092732
| 9:11 | 11.0367 | 0.092618
| 9:11 | 11.0369 | 0.092496
| 9:11 | 11.0372 | 0.092359
| 9:11 | 11.0375 | 0.092219
| 9:11 | 11.0378 | 0.092076
| 9:11 | 11.0381 | 0.09193
| 9:11 | 11.0383 | 0.091783
| 9:11 | 11.0386 | 0.091635
| 9:11 | 11.0389 | 0.091491
| 9:11 | 11.0392 | 0.09135
| 9:11 | 11.0394 | 0.091215
| 9:11 | 11.0397 | 0.091078
| 9:11 | 11.04 | 0.090955
| 9:11 | 11.0403 | 0.090838
| 9:11 | 11.0406 | 0.090726
| 9:11 | 11.0408 | 0.090619
| 9:11 | 11.0411 | 0.090518
| 9:11 | 11.0414 | 0.090421
| 9:11 | 11.0417 | 0.090329
| 9:11 | 11.0419 | 0.090242
| 9:11 | 11.0422 | 0.090157
| 9:11 | 11.0425 | 0.090074
| 9:11 | 11.0428 | 0.089988
| 9:11 | 11.0431 | 0.089902
| 9:11 | 11.0433 | 0.089814
| 9:11 | 11.0436 | 0.089725
| 9:11 | 11.0439 | 0.089625
| 9:11 | 11.0442 | 0.089522
| 9:11 | 11.0444 | 0.089396
| 9:11 | 11.0447 | 0.089263
| 9:12 | 11.045 | 0.089123
| 9:12 | 11.0453 | 0.088972
| 9:12 | 11.0456 | 0.088815
| 9:12 | 11.0458 | 0.088646
| 9:12 | 11.0461 | 0.088458
| 9:12 | 11.0464 | 0.088263
| 9:12 | 11.0467 | 0.088059
| 9:12 | 11.0469 | 0.087851
| 9:12 | 11.0472 | 0.087629
| 9:12 | 11.0475 | 0.087397
| 9:12 | 11.0478 | 0.087157
| 9:12 | 11.0481 | 0.086904
| 9:12 | 11.0483 | 0.086638
| 9:12 | 11.0486 | 0.08636
| 9:12 | 11.0489 | 0.08607
| 9:12 | 11.0492 | 0.085767
| 9:12 | 11.0494 | 0.085452
| 9:12 | 11.0497 | 0.085125
| 9:12 | 11.05 | 0.084785
| 9:12 | 11.0503 | 0.084432
| 9:12 | 11.0506 | 0.084067
| 9:12 | 11.0508 | 0.08368
| 9:12 | 11.0511 | 0.083285
| 9:12 | 11.0514 | 0.082883
| 9:12 | 11.0517 | 0.082478
| 9:12 | 11.0519 | 0.082067
| 9:12 | 11.0522 | 0.081651
| 9:12 | 11.0525 | 0.08123
| 9:12 | 11.0528 | 0.080807
| 9:12 | 11.0531 | 0.080378
| 9:12 | 11.0533 | 0.079947
| 9:12 | 11.0536 | 0.079513
| 9:12 | 11.0539 | 0.079081
| 9:12 | 11.0542 | 0.078649
| 9:12 | 11.0544 | 0.078218
| 9:12 | 11.0547 | 0.077794
| 9:12 | 11.055 | 0.077376
| 9:12 | 11.0553 | 0.076964
| 9:12 | 11.0556 | 0.076557
| 9:12 | 11.0558 | 0.076161
| 9:12 | 11.0561 | 0.075776
| 9:12 | 11.0564 | 0.0754
| 9:12 | 11.0567 | 0.075031
| 9:12 | 11.0569 | 0.074664
| 9:12 | 11.0572 | 0.0743
| 9:12 | 11.0575 | 0.07394
| 9:12 | 11.0578 | 0.073582
| 9:12 | 11.0581 | 0.073227
| 9:12 | 11.0583 | 0.072874
| 9:12 | 11.0586 | 0.072517
| 9:12 | 11.0589 | 0.072153
| 9:12 | 11.0592 | 0.071774
| 9:12 | 11.0594 | 0.071388
| 9:12 | 11.0597 | 0.070995
| 9:12 | 11.06 | 0.070592
| 9:12 | 11.0603 | 0.070177
| 9:12 | 11.0606 | 0.069754
| 9:12 | 11.0608 | 0.069325
| 9:12 | 11.0611 | 0.06889
| 9:12 | 11.0614 | 0.068453
| 9:12 | 11.0617 | 0.068006
| 9:13 | 11.0619 | 0.067559
| 9:13 | 11.0622 | 0.067107
| 9:13 | 11.0625 | 0.06665
| 9:13 | 11.0628 | 0.066192
| 9:13 | 11.0631 | 0.065729
| 9:13 | 11.0633 | 0.065263
| 9:13 | 11.0636 | 0.064796
| 9:13 | 11.0639 | 0.064327
| 9:13 | 11.0642 | 0.063858
| 9:13 | 11.0644 | 0.063387
| 9:13 | 11.0647 | 0.062916
| 9:13 | 11.065 | 0.062445
| 9:13 | 11.0653 | 0.061975
| 9:13 | 11.0656 | 0.061507
| 9:13 | 11.0658 | 0.061039
| 9:13 | 11.0661 | 0.060573
| 9:13 | 11.0664 | 0.060108
| 9:13 | 11.0667 | 0.059645
| 9:13 | 11.0669 | 0.059183
| 9:13 | 11.0672 | 0.058722
| 9:13 | 11.0675 | 0.058262
| 9:13 | 11.0678 | 0.057801
| 9:13 | 11.0681 | 0.05734
| 9:13 | 11.0683 | 0.056882
| 9:13 | 11.0686 | 0.056427
| 9:13 | 11.0689 | 0.055977
| 9:13 | 11.0692 | 0.05553
| 9:13 | 11.0694 | 0.055085
| 9:13 | 11.0697 | 0.054643
| 9:13 | 11.07 | 0.054208
| 9:13 | 11.0703 | 0.053774
| 9:13 | 11.0706 | 0.053347
| 9:13 | 11.0708 | 0.052922
| 9:13 | 11.0711 | 0.052504
| 9:13 | 11.0714 | 0.052084
| 9:13 | 11.0717 | 0.051671
| 9:13 | 11.0719 | 0.051259
| 9:13 | 11.0722 | 0.05084
| 9:13 | 11.0725 | 0.050419
| 9:13 | 11.0728 | 0.049994
| 9:13 | 11.0731 | 0.049569
| 9:13 | 11.0733 | 0.049149
| 9:13 | 11.0736 | 0.048734
| 9:13 | 11.0739 | 0.048322
| 9:13 | 11.0742 | 0.047915
| 9:13 | 11.0744 | 0.047513
| 9:13 | 11.0747 | 0.047115
| 9:13 | 11.075 | 0.046722
| 9:13 | 11.0753 | 0.046344
| 9:13 | 11.0756 | 0.045979
| 9:13 | 11.0758 | 0.045619
| 9:13 | 11.0761 | 0.045268
| 9:13 | 11.0764 | 0.044923
| 9:13 | 11.0767 | 0.044582
| 9:13 | 11.0769 | 0.044241
| 9:13 | 11.0772 | 0.043895
| 9:13 | 11.0775 | 0.043545
| 9:13 | 11.0778 | 0.043196
| 9:13 | 11.0781 | 0.042838
| 9:14 | 11.0783 | 0.042475
| 9:14 | 11.0786 | 0.042104
| 9:14 | 11.0789 | 0.04171
| 9:14 | 11.0792 | 0.041303
| 9:14 | 11.0794 | 0.040887
| 9:14 | 11.0797 | 0.040464
| 9:14 | 11.08 | 0.040035
| 9:14 | 11.0803 | 0.0396
| 9:14 | 11.0806 | 0.039155
| 9:14 | 11.0808 | 0.038706
| 9:14 | 11.0811 | 0.038254
| 9:14 | 11.0814 | 0.037798
| 9:14 | 11.0817 | 0.037338
| 9:14 | 11.0819 | 0.036875
| 9:14 | 11.0822 | 0.036409
| 9:14 | 11.0825 | 0.03594
| 9:14 | 11.0828 | 0.035468
| 9:14 | 11.0831 | 0.034993
| 9:14 | 11.0833 | 0.034514
| 9:14 | 11.0836 | 0.034033
| 9:14 | 11.0839 | 0.03355
| 9:14 | 11.0842 | 0.033066
| 9:14 | 11.0844 | 0.032582
| 9:14 | 11.0847 | 0.032095
| 9:14 | 11.085 | 0.031607
| 9:14 | 11.0853 | 0.031119
| 9:14 | 11.0856 | 0.03063
| 9:14 | 11.0858 | 0.030142
| 9:14 | 11.0861 | 0.029651
| 9:14 | 11.0864 | 0.02916
| 9:14 | 11.0867 | 0.02867
| 9:14 | 11.0869 | 0.028179
| 9:14 | 11.0872 | 0.027688
| 9:14 | 11.0875 | 0.027199
| 9:14 | 11.0878 | 0.02671
| 9:14 | 11.0881 | 0.026221
| 9:14 | 11.0883 | 0.025733
| 9:14 | 11.0886 | 0.025244
| 9:14 | 11.0889 | 0.024757
| 9:14 | 11.0892 | 0.02427
| 9:14 | 11.0894 | 0.023781
| 9:14 | 11.0897 | 0.023294
| 9:14 | 11.09 | 0.022807
| 9:14 | 11.0903 | 0.022321
| 9:14 | 11.0906 | 0.021837
| 9:14 | 11.0908 | 0.021354
| 9:14 | 11.0911 | 0.020872
| 9:14 | 11.0914 | 0.020391
| 9:14 | 11.0917 | 0.019912
| 9:14 | 11.0919 | 0.019436
| 9:14 | 11.0922 | 0.01896
| 9:14 | 11.0925 | 0.018485
| 9:14 | 11.0928 | 0.018012
| 9:14 | 11.0931 | 0.017538
| 9:14 | 11.0933 | 0.017065
| 9:14 | 11.0936 | 0.016593
| 9:14 | 11.0939 | 0.016121
| 9:14 | 11.0942 | 0.01565
| 9:14 | 11.0944 | 0.015179
| 9:14 | 11.0947 | 0.014708
| 9:14 | 11.095 | 0.014235
| 9:15 | 11.0953 | 0.013764
| 9:15 | 11.0956 | 0.013293
| 9:15 | 11.0958 | 0.012824
| 9:15 | 11.0961 | 0.012352
| 9:15 | 11.0964 | 0.011881
| 9:15 | 11.0967 | 0.011409
| 9:15 | 11.0969 | 0.010938
| 9:15 | 11.0972 | 0.010466
| 9:15 | 11.0975 | 0.0099966
| 9:15 | 11.0978 | 0.0095247
| 9:15 | 11.0981 | 0.0090518
| 9:15 | 11.0983 | 0.0085778
| 9:15 | 11.0986 | 0.0081026
| 9:15 | 11.0989 | 0.0076263
| 9:15 | 11.0992 | 0.0071487
| 9:15 | 11.0994 | 0.00667
| 9:15 | 11.0997 | 0.00619
| 9:15 | 11.1 | 0.0057089
| 9:15 | 11.1003 | 0.005227
| 9:15 | 11.1006 | 0.0047436
| 9:15 | 11.1008 | 0.0042571
| 9:15 | 11.1011 | 0.0037713
| 9:15 | 11.1014 | 0.003284
| 9:15 | 11.1017 | 0.0027974
| 9:15 | 11.1019 | 0.0023123
| 9:15 | 11.1022 | 0.0018249
| 9:15 | 11.1025 | 0.0013374
| 9:15 | 11.1028 | 0.00084999
| 9:15 | 11.1031 | 0.00036253
| 9:15 | 11.1033 | -0.000126
| 9:15 | 11.1036 | -0.00061443
| 9:15 | 11.1039 | -0.0011019
| 9:15 | 11.1042 | -0.0015905
| 9:15 | 11.1044 | -0.0020802
| 9:15 | 11.1047 | -0.0025685
| 9:15 | 11.105 | -0.003056
| 9:15 | 11.1053 | -0.0035421
| 9:15 | 11.1056 | -0.0040274
| 9:15 | 11.1058 | -0.0045127
| 9:15 | 11.1061 | -0.0049981
| 9:15 | 11.1064 | -0.0054828
| 9:15 | 11.1067 | -0.005967
| 9:15 | 11.1069 | -0.0064506
| 9:15 | 11.1072 | -0.0069336
| 9:15 | 11.1075 | -0.007416
| 9:15 | 11.1078 | -0.0078978
| 9:15 | 11.1081 | -0.008379
| 9:15 | 11.1083 | -0.0088596
| 9:15 | 11.1086 | -0.0093384
| 9:15 | 11.1089 | -0.0098171
| 9:15 | 11.1092 | -0.010297
| 9:15 | 11.1094 | -0.010779
| 9:15 | 11.1097 | -0.011263
| 9:15 | 11.11 | -0.011748
| 9:15 | 11.1103 | -0.012234
| 9:15 | 11.1106 | -0.012719
| 9:15 | 11.1108 | -0.013205
| 9:15 | 11.1111 | -0.01369
| 9:15 | 11.1114 | -0.014176
| 9:16 | 11.1117 | -0.014663
| 9:16 | 11.1119 | -0.015151
| 9:16 | 11.1122 | -0.015639
| 9:16 | 11.1125 | -0.016126
| 9:16 | 11.1128 | -0.016614
| 9:16 | 11.1131 | -0.017104
| 9:16 | 11.1133 | -0.017594
| 9:16 | 11.1136 | -0.018087
| 9:16 | 11.1139 | -0.018579
| 9:16 | 11.1142 | -0.019071
| 9:16 | 11.1144 | -0.019563
| 9:16 | 11.1147 | -0.020055
| 9:16 | 11.115 | -0.020546
| 9:16 | 11.1153 | -0.021038
| 9:16 | 11.1156 | -0.021529
| 9:16 | 11.1158 | -0.02202
| 9:16 | 11.1161 | -0.02251
| 9:16 | 11.1164 | -0.023001
| 9:16 | 11.1167 | -0.023491
| 9:16 | 11.1169 | -0.023981
| 9:16 | 11.1172 | -0.02447
| 9:16 | 11.1175 | -0.024958
| 9:16 | 11.1178 | -0.025445
| 9:16 | 11.1181 | -0.025928
| 9:16 | 11.1183 | -0.026407
| 9:16 | 11.1186 | -0.026882
| 9:16 | 11.1189 | -0.027341
| 9:16 | 11.1192 | -0.027786
| 9:16 | 11.1194 | -0.028222
| 9:16 | 11.1197 | -0.02864
| 9:16 | 11.12 | -0.029034
| 9:16 | 11.1203 | -0.0294
| 9:16 | 11.1206 | -0.029757
| 9:16 | 11.1208 | -0.030097
| 9:16 | 11.1211 | -0.030407
| 9:16 | 11.1214 | -0.030706
| 9:16 | 11.1217 | -0.030998
| 9:16 | 11.1219 | -0.031287
| 9:16 | 11.1222 | -0.031575
| 9:16 | 11.1225 | -0.03186
| 9:16 | 11.1228 | -0.032146
| 9:16 | 11.1231 | -0.032436
| 9:16 | 11.1233 | -0.032742
| 9:16 | 11.1236 | -0.033065
| 9:16 | 11.1239 | -0.033404
| 9:16 | 11.1242 | -0.03376
| 9:16 | 11.1244 | -0.034132
| 9:16 | 11.1247 | -0.034521
| 9:16 | 11.125 | -0.034927
| 9:16 | 11.1253 | -0.035356
| 9:16 | 11.1256 | -0.035796
| 9:16 | 11.1258 | -0.036248
| 9:16 | 11.1261 | -0.036703
| 9:16 | 11.1264 | -0.037166
| 9:16 | 11.1267 | -0.037633
| 9:16 | 11.1269 | -0.038101
| 9:16 | 11.1272 | -0.038568
| 9:16 | 11.1275 | -0.039036
| 9:16 | 11.1278 | -0.039503
| 9:16 | 11.1281 | -0.039968
| 9:16 | 11.1283 | -0.040434
| 9:17 | 11.1286 | -0.040901
| 9:17 | 11.1289 | -0.041365
| 9:17 | 11.1292 | -0.041821
| 9:17 | 11.1294 | -0.042274
| 9:17 | 11.1297 | -0.042721
| 9:17 | 11.13 | -0.04316
| 9:17 | 11.1303 | -0.043596
| 9:17 | 11.1306 | -0.044027
| 9:17 | 11.1308 | -0.044442
| 9:17 | 11.1311 | -0.044849
| 9:17 | 11.1314 | -0.045242
| 9:17 | 11.1317 | -0.045621
| 9:17 | 11.1319 | -0.045987
| 9:17 | 11.1322 | -0.04634
| 9:17 | 11.1325 | -0.04668
| 9:17 | 11.1328 | -0.047006
| 9:17 | 11.1331 | -0.047319
| 9:17 | 11.1333 | -0.047619
| 9:17 | 11.1336 | -0.047906
| 9:17 | 11.1339 | -0.048187
| 9:17 | 11.1342 | -0.048457
| 9:17 | 11.1344 | -0.048721
| 9:17 | 11.1347 | -0.048965
| 9:17 | 11.135 | -0.049209
| 9:17 | 11.1353 | -0.049444
| 9:17 | 11.1356 | -0.049664
| 9:17 | 11.1358 | -0.04988
| 9:17 | 11.1361 | -0.050086
| 9:17 | 11.1364 | -0.050282
| 9:17 | 11.1367 | -0.050467
| 9:17 | 11.1369 | -0.050645
| 9:17 | 11.1372 | -0.050812
| 9:17 | 11.1375 | -0.050977
| 9:17 | 11.1378 | -0.051134
| 9:17 | 11.1381 | -0.051285
| 9:17 | 11.1383 | -0.05143
| 9:17 | 11.1386 | -0.051561
| 9:17 | 11.1389 | -0.051681
| 9:17 | 11.1392 | -0.051793
| 9:17 | 11.1394 | -0.051895
| 9:17 | 11.1397 | -0.051996
| 9:17 | 11.14 | -0.052094
| 9:17 | 11.1403 | -0.052191
| 9:17 | 11.1406 | -0.052285
| 9:17 | 11.1408 | -0.052377
| 9:17 | 11.1411 | -0.052467
| 9:17 | 11.1414 | -0.052555
| 9:17 | 11.1417 | -0.052642
| 9:17 | 11.1419 | -0.052729
| 9:17 | 11.1422 | -0.052816
| 9:17 | 11.1425 | -0.052904
| 9:17 | 11.1428 | -0.052991
| 9:17 | 11.1431 | -0.05308
| 9:17 | 11.1433 | -0.053169
| 9:17 | 11.1436 | -0.053259
| 9:17 | 11.1439 | -0.053346
| 9:17 | 11.1442 | -0.053433
| 9:17 | 11.1444 | -0.05352
| 9:17 | 11.1447 | -0.053607
| 9:18 | 11.145 | -0.053694
| 9:18 | 11.1453 | -0.053782
| 9:18 | 11.1456 | -0.053871
| 9:18 | 11.1458 | -0.05396
| 9:18 | 11.1461 | -0.05405
| 9:18 | 11.1464 | -0.054139
| 9:18 | 11.1467 | -0.054228
| 9:18 | 11.1469 | -0.054318
| 9:18 | 11.1472 | -0.054407
| 9:18 | 11.1475 | -0.054499
| 9:18 | 11.1478 | -0.054592
| 9:18 | 11.1481 | -0.05469
| 9:18 | 11.1483 | -0.054792
| 9:18 | 11.1486 | -0.054909
| 9:18 | 11.1489 | -0.055043
| 9:18 | 11.1492 | -0.055192
| 9:18 | 11.1494 | -0.055357
| 9:18 | 11.1497 | -0.055538
| 9:18 | 11.15 | -0.055734
| 9:18 | 11.1503 | -0.055946
| 9:18 | 11.1506 | -0.056175
| 9:18 | 11.1508 | -0.056418
| 9:18 | 11.1511 | -0.056674
| 9:18 | 11.1514 | -0.05695
| 9:18 | 11.1517 | -0.057235
| 9:18 | 11.1519 | -0.057536
| 9:18 | 11.1522 | -0.057853
| 9:18 | 11.1525 | -0.058187
| 9:18 | 11.1528 | -0.058532
| 9:18 | 11.1531 | -0.058884
| 9:18 | 11.1533 | -0.059242
| 9:18 | 11.1536 | -0.059601
| 9:18 | 11.1539 | -0.059957
| 9:18 | 11.1542 | -0.060311
| 9:18 | 11.1544 | -0.060665
| 9:18 | 11.1547 | -0.061019
| 9:18 | 11.155 | -0.061374
| 9:18 | 11.1553 | -0.061734
| 9:18 | 11.1556 | -0.062097
| 9:18 | 11.1558 | -0.062463
| 9:18 | 11.1561 | -0.06283
| 9:18 | 11.1564 | -0.063198
| 9:18 | 11.1567 | -0.063562
| 9:18 | 11.1569 | -0.063921
| 9:18 | 11.1572 | -0.064276
| 9:18 | 11.1575 | -0.064627
| 9:18 | 11.1578 | -0.064974
| 9:18 | 11.1581 | -0.065317
| 9:18 | 11.1583 | -0.065655
| 9:18 | 11.1586 | -0.065985
| 9:18 | 11.1589 | -0.066305
| 9:18 | 11.1592 | -0.066614
| 9:18 | 11.1594 | -0.066905
| 9:18 | 11.1597 | -0.067185
| 9:18 | 11.16 | -0.067446
| 9:18 | 11.1603 | -0.067691
| 9:18 | 11.1606 | -0.067918
| 9:18 | 11.1608 | -0.068133
| 9:18 | 11.1611 | -0.068339
| 9:18 | 11.1614 | -0.068527
| 9:18 | 11.1617 | -0.068703
| 9:19 | 11.1619 | -0.068868
| 9:19 | 11.1622 | -0.069023
| 9:19 | 11.1625 | -0.069174
| 9:19 | 11.1628 | -0.069316
| 9:19 | 11.1631 | -0.069454
| 9:19 | 11.1633 | -0.069586
| 9:19 | 11.1636 | -0.0697
| 9:19 | 11.1639 | -0.069812
| 9:19 | 11.1642 | -0.069914
| 9:19 | 11.1644 | -0.070014
| 9:19 | 11.1647 | -0.070117
| 9:19 | 11.165 | -0.070224
| 9:19 | 11.1653 | -0.070336
| 9:19 | 11.1656 | -0.070452
| 9:19 | 11.1658 | -0.070573
| 9:19 | 11.1661 | -0.070699
| 9:19 | 11.1664 | -0.070829
| 9:19 | 11.1667 | -0.070965
| 9:19 | 11.1669 | -0.071104
| 9:19 | 11.1672 | -0.071251
| 9:19 | 11.1675 | -0.071406
| 9:19 | 11.1678 | -0.071566
| 9:19 | 11.1681 | -0.071731
| 9:19 | 11.1683 | -0.0719
| 9:19 | 11.1686 | -0.072071
| 9:19 | 11.1689 | -0.072243
| 9:19 | 11.1692 | -0.072415
| 9:19 | 11.1694 | -0.072589
| 9:19 | 11.1697 | -0.072764
| 9:19 | 11.17 | -0.072942
| 9:19 | 11.1703 | -0.073124
| 9:19 | 11.1706 | -0.073309
| 9:19 | 11.1708 | -0.073499
| 9:19 | 11.1711 | -0.073696
| 9:19 | 11.1714 | -0.073904
| 9:19 | 11.1717 | -0.074145
| 9:19 | 11.1719 | -0.0744
| 9:19 | 11.1722 | -0.074676
| 9:19 | 11.1725 | -0.07497
| 9:19 | 11.1728 | -0.075283
| 9:19 | 11.1731 | -0.075607
| 9:19 | 11.1733 | -0.075925
| 9:19 | 11.1736 | -0.07624
| 9:19 | 11.1739 | -0.076549
| 9:19 | 11.1742 | -0.076854
| 9:19 | 11.1744 | -0.077154
| 9:19 | 11.1747 | -0.077449
| 9:19 | 11.175 | -0.077713
| 9:19 | 11.1753 | -0.077958
| 9:19 | 11.1756 | -0.078195
| 9:19 | 11.1758 | -0.0784
| 9:19 | 11.1761 | -0.078575
| 9:19 | 11.1764 | -0.078727
| 9:19 | 11.1767 | -0.078856
| 9:19 | 11.1769 | -0.07897
| 9:19 | 11.1772 | -0.079067
| 9:19 | 11.1775 | -0.079152
| 9:19 | 11.1778 | -0.079226
| 9:19 | 11.1781 | -0.079293
| 9:20 | 11.1783 | -0.079356
| 9:20 | 11.1786 | -0.079414
| 9:20 | 11.1789 | -0.079468
| 9:20 | 11.1792 | -0.079523
| 9:20 | 11.1794 | -0.079575
| 9:20 | 11.1797 | -0.079627
| 9:20 | 11.18 | -0.079679
| 9:20 | 11.1803 | -0.079731
| 9:20 | 11.1806 | -0.079783
| 9:20 | 11.1808 | -0.079833
| 9:20 | 11.1811 | -0.079882
| 9:20 | 11.1814 | -0.079932
| 9:20 | 11.1817 | -0.079981
| 9:20 | 11.1819 | -0.080031
| 9:20 | 11.1822 | -0.08008
| 9:20 | 11.1825 | -0.080128
| 9:20 | 11.1828 | -0.080177
| 9:20 | 11.1831 | -0.080225
| 9:20 | 11.1833 | -0.080273
| 9:20 | 11.1836 | -0.080321
| 9:20 | 11.1839 | -0.080368
| 9:20 | 11.1842 | -0.080415
| 9:20 | 11.1844 | -0.080461
| 9:20 | 11.1847 | -0.080506
| 9:20 | 11.185 | -0.080551
| 9:20 | 11.1853 | -0.080596
| 9:20 | 11.1856 | -0.080642
| 9:20 | 11.1858 | -0.080685
| 9:20 | 11.1861 | -0.080728
| 9:20 | 11.1864 | -0.080772
| 9:20 | 11.1867 | -0.080815
| 9:20 | 11.1869 | -0.080858
| 9:20 | 11.1872 | -0.080901
| 9:20 | 11.1875 | -0.080944
| 9:20 | 11.1878 | -0.080985
| 9:20 | 11.1881 | -0.081026
| 9:20 | 11.1883 | -0.081067
| 9:20 | 11.1886 | -0.081107
| 9:20 | 11.1889 | -0.081146
| 9:20 | 11.1892 | -0.081185
| 9:20 | 11.1894 | -0.081223
| 9:20 | 11.1897 | -0.081262
| 9:20 | 11.19 | -0.081301
| 9:20 | 11.1903 | -0.08134
| 9:20 | 11.1906 | -0.081378
| 9:20 | 11.1908 | -0.081417
| 9:20 | 11.1911 | -0.081456
| 9:20 | 11.1914 | -0.081494
| 9:20 | 11.1917 | -0.081533
| 9:20 | 11.1919 | -0.08157
| 9:20 | 11.1922 | -0.081607
| 9:20 | 11.1925 | -0.081644
| 9:20 | 11.1928 | -0.081682
| 9:20 | 11.1931 | -0.081721
| 9:20 | 11.1933 | -0.08176
| 9:20 | 11.1936 | -0.081799
| 9:20 | 11.1939 | -0.081837
| 9:20 | 11.1942 | -0.081876
| 9:20 | 11.1944 | -0.081913
| 9:20 | 11.1947 | -0.081949
| 9:20 | 11.195 | -0.081986
| 9:21 | 11.1953 | -0.082022
| 9:21 | 11.1956 | -0.082059
| 9:21 | 11.1958 | -0.082095
| 9:21 | 11.1961 | -0.082133
| 9:21 | 11.1964 | -0.082172
| 9:21 | 11.1967 | -0.082213
| 9:21 | 11.1969 | -0.082254
| 9:21 | 11.1972 | -0.082296
| 9:21 | 11.1975 | -0.082339
| 9:21 | 11.1978 | -0.082383
| 9:21 | 11.1981 | -0.082428
| 9:21 | 11.1983 | -0.082475
| 9:21 | 11.1986 | -0.082522
| 9:21 | 11.1989 | -0.08257
| 9:21 | 11.1992 | -0.082619
| 9:21 | 11.1994 | -0.082669
| 9:21 | 11.1997 | -0.08272
| 9:21 | 11.2 | -0.082772
| 9:21 | 11.2003 | -0.082826
| 9:21 | 11.2006 | -0.08288
| 9:21 | 11.2008 | -0.082936
| 9:21 | 11.2011 | -0.082995
| 9:21 | 11.2014 | -0.083054
| 9:21 | 11.2017 | -0.083114
| 9:21 | 11.2019 | -0.083175
| 9:21 | 11.2022 | -0.083236
| 9:21 | 11.2025 | -0.083299
| 9:21 | 11.2028 | -0.083362
| 9:21 | 11.2031 | -0.083425
| 9:21 | 11.2033 | -0.083488
| 9:21 | 11.2036 | -0.083551
| 9:21 | 11.2039 | -0.083613
| 9:21 | 11.2042 | -0.083671
| 9:21 | 11.2044 | -0.08373
| 9:21 | 11.2047 | -0.083783
| 9:21 | 11.205 | -0.083835
| 9:21 | 11.2053 | -0.083885
| 9:21 | 11.2056 | -0.08393
| 9:21 | 11.2058 | -0.083973
| 9:21 | 11.2061 | -0.084016
| 9:21 | 11.2064 | -0.084059
| 9:21 | 11.2067 | -0.084102
| 9:21 | 11.2069 | -0.084146
| 9:21 | 11.2072 | -0.084191
| 9:21 | 11.2075 | -0.084236
| 9:21 | 11.2078 | -0.084282
| 9:21 | 11.2081 | -0.084329
| 9:21 | 11.2083 | -0.084376
| 9:21 | 11.2086 | -0.084424
| 9:21 | 11.2089 | -0.084474
| 9:21 | 11.2092 | -0.084523
| 9:21 | 11.2094 | -0.084575
| 9:21 | 11.2097 | -0.084629
| 9:21 | 11.21 | -0.084683
| 9:21 | 11.2103 | -0.084739
| 9:21 | 11.2106 | -0.084793
| 9:21 | 11.2108 | -0.084847
| 9:21 | 11.2111 | -0.084901
| 9:21 | 11.2114 | -0.084953
| 9:22 | 11.2117 | -0.085005
| 9:22 | 11.2119 | -0.085054
| 9:22 | 11.2122 | -0.085104
| 9:22 | 11.2125 | -0.085153
| 9:22 | 11.2128 | -0.085203
| 9:22 | 11.2131 | -0.08525
| 9:22 | 11.2133 | -0.085297
| 9:22 | 11.2136 | -0.085345
| 9:22 | 11.2139 | -0.085392
| 9:22 | 11.2142 | -0.08544
| 9:22 | 11.2144 | -0.08549
| 9:22 | 11.2147 | -0.085541
| 9:22 | 11.215 | -0.085599
| 9:22 | 11.2153 | -0.085663
| 9:22 | 11.2156 | -0.085735
| 9:22 | 11.2158 | -0.085813
| 9:22 | 11.2161 | -0.085898
| 9:22 | 11.2164 | -0.08599
| 9:22 | 11.2167 | -0.086089
| 9:22 | 11.2169 | -0.086195
| 9:22 | 11.2172 | -0.086307
| 9:22 | 11.2175 | -0.086427
| 9:22 | 11.2178 | -0.086557
| 9:22 | 11.2181 | -0.086696
| 9:22 | 11.2183 | -0.086847
| 9:22 | 11.2186 | -0.087003
| 9:22 | 11.2189 | -0.087177
| 9:22 | 11.2192 | -0.087363
| 9:22 | 11.2194 | -0.087562
| 9:22 | 11.2197 | -0.087767
| 9:22 | 11.22 | -0.087984
| 9:22 | 11.2203 | -0.088208
| 9:22 | 11.2206 | -0.088433
| 9:22 | 11.2208 | -0.088667
| 9:22 | 11.2211 | -0.088903
| 9:22 | 11.2214 | -0.089141
| 9:22 | 11.2217 | -0.089387
| 9:22 | 11.2219 | -0.089636
| 9:22 | 11.2222 | -0.089891
| 9:22 | 11.2225 | -0.090142
| 9:22 | 11.2228 | -0.090389
| 9:22 | 11.2231 | -0.090631
| 9:22 | 11.2233 | -0.090868
| 9:22 | 11.2236 | -0.091099
| 9:22 | 11.2239 | -0.091324
| 9:22 | 11.2242 | -0.091543
| 9:22 | 11.2244 | -0.091757
| 9:22 | 11.2247 | -0.091965
| 9:22 | 11.225 | -0.092168
| 9:22 | 11.2253 | -0.092359
| 9:22 | 11.2256 | -0.092543
| 9:22 | 11.2258 | -0.09272
| 9:22 | 11.2261 | -0.092888
| 9:22 | 11.2264 | -0.093053
| 9:22 | 11.2267 | -0.093215
| 9:22 | 11.2269 | -0.093374
| 9:22 | 11.2272 | -0.093524
| 9:22 | 11.2275 | -0.093667
| 9:22 | 11.2278 | -0.093797
| 9:22 | 11.2281 | -0.093924
| 9:22 | 11.2283 | -0.094042
| 9:23 | 11.2286 | -0.094146
| 9:23 | 11.2289 | -0.094243
| 9:23 | 11.2292 | -0.094334
| 9:23 | 11.2294 | -0.094416
| 9:23 | 11.2297 | -0.094487
| 9:23 | 11.23 | -0.094554
| 9:23 | 11.2303 | -0.094614
| 9:23 | 11.2306 | -0.094669
| 9:23 | 11.2308 | -0.094715
| 9:23 | 11.2311 | -0.094757
| 9:23 | 11.2314 | -0.094795
| 9:23 | 11.2317 | -0.094829
| 9:23 | 11.2319 | -0.094861
| 9:23 | 11.2322 | -0.09489
| 9:23 | 11.2325 | -0.094916
| 9:23 | 11.2328 | -0.094939
| 9:23 | 11.2331 | -0.094959
| 9:23 | 11.2333 | -0.094976
| 9:23 | 11.2336 | -0.09499
| 9:23 | 11.2339 | -0.095003
| 9:23 | 11.2342 | -0.095016
| 9:23 | 11.2344 | -0.095031
| 9:23 | 11.2347 | -0.095045
| 9:23 | 11.235 | -0.095059
| 9:23 | 11.2353 | -0.095074
| 9:23 | 11.2356 | -0.09509
| 9:23 | 11.2358 | -0.095105
| 9:23 | 11.2361 | -0.095121
| 9:23 | 11.2364 | -0.095139
| 9:23 | 11.2367 | -0.095158
| 9:23 | 11.2369 | -0.095177
| 9:23 | 11.2372 | -0.095199
| 9:23 | 11.2375 | -0.095222
| 9:23 | 11.2378 | -0.095248
| 9:23 | 11.2381 | -0.095278
| 9:23 | 11.2383 | -0.095309
| 9:23 | 11.2386 | -0.095342
| 9:23 | 11.2389 | -0.095375
| 9:23 | 11.2392 | -0.095411
| 9:23 | 11.2394 | -0.095446
| 9:23 | 11.2397 | -0.095482
| 9:23 | 11.24 | -0.09552
| 9:23 | 11.2403 | -0.095558
| 9:23 | 11.2406 | -0.095598
| 9:23 | 11.2408 | -0.095639
| 9:23 | 11.2411 | -0.095681
| 9:23 | 11.2414 | -0.095724
| 9:23 | 11.2417 | -0.095766
| 9:23 | 11.2419 | -0.095807
| 9:23 | 11.2422 | -0.095846
| 9:23 | 11.2425 | -0.095884
| 9:23 | 11.2428 | -0.09592
| 9:23 | 11.2431 | -0.095954
| 9:23 | 11.2433 | -0.095987
| 9:23 | 11.2436 | -0.096017
| 9:23 | 11.2439 | -0.096048
| 9:23 | 11.2442 | -0.096078
| 9:23 | 11.2444 | -0.096104
| 9:23 | 11.2447 | -0.096131
| 9:24 | 11.245 | -0.09616
| 9:24 | 11.2453 | -0.096188
| 9:24 | 11.2456 | -0.096217
| 9:24 | 11.2458 | -0.096247
| 9:24 | 11.2461 | -0.096282
| 9:24 | 11.2464 | -0.09632
| 9:24 | 11.2467 | -0.096359
| 9:24 | 11.2469 | -0.0964
| 9:24 | 11.2472 | -0.096444
| 9:24 | 11.2475 | -0.096489
| 9:24 | 11.2478 | -0.096536
| 9:24 | 11.2481 | -0.096582
| 9:24 | 11.2483 | -0.096626
| 9:24 | 11.2486 | -0.096669
| 9:24 | 11.2489 | -0.096709
| 9:24 | 11.2492 | -0.096748
| 9:24 | 11.2494 | -0.096786
| 9:24 | 11.2497 | -0.096821
| 9:24 | 11.25 | -0.096855
| 9:24 | 11.2503 | -0.096888
| 9:24 | 11.2506 | -0.096918
| 9:24 | 11.2508 | -0.096944
| 9:24 | 11.2511 | -0.096963
| 9:24 | 11.2514 | -0.096978
| 9:24 | 11.2517 | -0.096992
| 9:24 | 11.2519 | -0.097003
| 9:24 | 11.2522 | -0.097011
| 9:24 | 11.2525 | -0.097015
| 9:24 | 11.2528 | -0.097017
| 9:24 | 11.2531 | -0.097019
| 9:24 | 11.2533 | -0.097018
| 9:24 | 11.2536 | -0.097017
| 9:24 | 11.2539 | -0.097014
| 9:24 | 11.2542 | -0.09701
| 9:24 | 11.2544 | -0.097005
| 9:24 | 11.2547 | -0.096998
| 9:24 | 11.255 | -0.096991
| 9:24 | 11.2553 | -0.096984
| 9:24 | 11.2556 | -0.096975
| 9:24 | 11.2558 | -0.096966
| 9:24 | 11.2561 | -0.096955
| 9:24 | 11.2564 | -0.096942
| 9:24 | 11.2567 | -0.09693
| 9:24 | 11.2569 | -0.096916
| 9:24 | 11.2572 | -0.096902
| 9:24 | 11.2575 | -0.096887
| 9:24 | 11.2578 | -0.096872
| 9:24 | 11.2581 | -0.096856
| 9:24 | 11.2583 | -0.09684
| 9:24 | 11.2586 | -0.096824
| 9:24 | 11.2589 | -0.096808
| 9:24 | 11.2592 | -0.096792
| 9:24 | 11.2594 | -0.096776
| 9:24 | 11.2597 | -0.09676
| 9:24 | 11.26 | -0.096745
| 9:24 | 11.2603 | -0.096729
| 9:24 | 11.2606 | -0.096715
| 9:24 | 11.2608 | -0.096701
| 9:24 | 11.2611 | -0.09669
| 9:24 | 11.2614 | -0.096681
| 9:24 | 11.2617 | -0.096674
| 9:25 | 11.2619 | -0.096669
| 9:25 | 11.2622 | -0.096667
| 9:25 | 11.2625 | -0.096669
| 9:25 | 11.2628 | -0.096672
| 9:25 | 11.2631 | -0.096676
| 9:25 | 11.2633 | -0.096683
| 9:25 | 11.2636 | -0.096691
| 9:25 | 11.2639 | -0.096699
| 9:25 | 11.2642 | -0.096705
| 9:25 | 11.2644 | -0.09671
| 9:25 | 11.2647 | -0.096714
| 9:25 | 11.265 | -0.096715
| 9:25 | 11.2653 | -0.096714
| 9:25 | 11.2656 | -0.096712
| 9:25 | 11.2658 | -0.096707
| 9:25 | 11.2661 | -0.096701
| 9:25 | 11.2664 | -0.096692
| 9:25 | 11.2667 | -0.096681
| 9:25 | 11.2669 | -0.09667
| 9:25 | 11.2672 | -0.096658
| 9:25 | 11.2675 | -0.096646
| 9:25 | 11.2678 | -0.096635
| 9:25 | 11.2681 | -0.096625
| 9:25 | 11.2683 | -0.096616
| 9:25 | 11.2686 | -0.096614
| 9:25 | 11.2689 | -0.096615
| 9:25 | 11.2692 | -0.096622
| 9:25 | 11.2694 | -0.096633
| 9:25 | 11.2697 | -0.096666
| 9:25 | 11.27 | -0.0967
| 9:25 | 11.2703 | -0.096748
| 9:25 | 11.2706 | -0.096813
| 9:25 | 11.2708 | -0.096903
| 9:25 | 11.2711 | -0.097003
| 9:25 | 11.2714 | -0.09714
| 9:25 | 11.2717 | -0.097298
| 9:25 | 11.2719 | -0.097486
| 9:25 | 11.2722 | -0.097683
| 9:25 | 11.2725 | -0.097902
| 9:25 | 11.2728 | -0.098148
| 9:25 | 11.2731 | -0.09841
| 9:25 | 11.2733 | -0.098685
| 9:25 | 11.2736 | -0.098974
| 9:25 | 11.2739 | -0.099277
| 9:25 | 11.2742 | -0.099593
| 9:25 | 11.2744 | -0.099923
| 9:25 | 11.2747 | -0.10027
| 9:25 | 11.275 | -0.10062
| 9:25 | 11.2753 | -0.10098
| 9:25 | 11.2756 | -0.10135
| 9:25 | 11.2758 | -0.10171
| 9:25 | 11.2761 | -0.10208
| 9:25 | 11.2764 | -0.10244
| 9:25 | 11.2767 | -0.10281
| 9:25 | 11.2769 | -0.10317
| 9:25 | 11.2772 | -0.10353
| 9:25 | 11.2775 | -0.1039
| 9:25 | 11.2778 | -0.10426
| 9:25 | 11.2781 | -0.10462
| 9:26 | 11.2783 | -0.10499
| 9:26 | 11.2786 | -0.10535
| 9:26 | 11.2789 | -0.10571
| 9:26 | 11.2792 | -0.10608
| 9:26 | 11.2794 | -0.10644
| 9:26 | 11.2797 | -0.1068
| 9:26 | 11.28 | -0.10716
| 9:26 | 11.2803 | -0.10753
| 9:26 | 11.2806 | -0.10789
| 9:26 | 11.2808 | -0.10825
| 9:26 | 11.2811 | -0.10861
| 9:26 | 11.2814 | -0.10896
| 9:26 | 11.2817 | -0.10932
| 9:26 | 11.2819 | -0.10967
| 9:26 | 11.2822 | -0.11002
| 9:26 | 11.2825 | -0.11037
| 9:26 | 11.2828 | -0.11072
| 9:26 | 11.2831 | -0.11107
| 9:26 | 11.2833 | -0.11141
| 9:26 | 11.2836 | -0.11176
| 9:26 | 11.2839 | -0.1121
| 9:26 | 11.2842 | -0.11243
| 9:26 | 11.2844 | -0.11276
| 9:26 | 11.2847 | -0.11309
| 9:26 | 11.285 | -0.1134
| 9:26 | 11.2853 | -0.11371
| 9:26 | 11.2856 | -0.11402
| 9:26 | 11.2858 | -0.11432
| 9:26 | 11.2861 | -0.11461
| 9:26 | 11.2864 | -0.1149
| 9:26 | 11.2867 | -0.11518
| 9:26 | 11.2869 | -0.11545
| 9:26 | 11.2872 | -0.11571
| 9:26 | 11.2875 | -0.11597
| 9:26 | 11.2878 | -0.11623
| 9:26 | 11.2881 | -0.11648
| 9:26 | 11.2883 | -0.11674
| 9:26 | 11.2886 | -0.117
| 9:26 | 11.2889 | -0.11727
| 9:26 | 11.2892 | -0.11753
| 9:26 | 11.2894 | -0.11781
| 9:26 | 11.2897 | -0.11808
| 9:26 | 11.29 | -0.11837
| 9:26 | 11.2903 | -0.11866
| 9:26 | 11.2906 | -0.11896
| 9:26 | 11.2908 | -0.11926
| 9:26 | 11.2911 | -0.11957
| 9:26 | 11.2914 | -0.11989
| 9:26 | 11.2917 | -0.12021
| 9:26 | 11.2919 | -0.12053
| 9:26 | 11.2922 | -0.12086
| 9:26 | 11.2925 | -0.12119
| 9:26 | 11.2928 | -0.12152
| 9:26 | 11.2931 | -0.12185
| 9:26 | 11.2933 | -0.12218
| 9:26 | 11.2936 | -0.12251
| 9:26 | 11.2939 | -0.12282
| 9:26 | 11.2942 | -0.12313
| 9:26 | 11.2944 | -0.12342
| 9:26 | 11.2947 | -0.12371
| 9:26 | 11.295 | -0.12398
| 9:27 | 11.2953 | -0.12425
| 9:27 | 11.2956 | -0.12451
| 9:27 | 11.2958 | -0.12475
| 9:27 | 11.2961 | -0.12498
| 9:27 | 11.2964 | -0.1252
| 9:27 | 11.2967 | -0.12542
| 9:27 | 11.2969 | -0.12562
| 9:27 | 11.2972 | -0.12581
| 9:27 | 11.2975 | -0.126
| 9:27 | 11.2978 | -0.12617
| 9:27 | 11.2981 | -0.12633
| 9:27 | 11.2983 | -0.12648
| 9:27 | 11.2986 | -0.12662
| 9:27 | 11.2989 | -0.12675
| 9:27 | 11.2992 | -0.12686
| 9:27 | 11.2994 | -0.12696
| 9:27 | 11.2997 | -0.12704
| 9:27 | 11.3 | -0.12712
| 9:27 | 11.3003 | -0.12718
| 9:27 | 11.3006 | -0.12723
| 9:27 | 11.3008 | -0.12726
| 9:27 | 11.3011 | -0.12728
| 9:27 | 11.3014 | -0.12729
| 9:27 | 11.3017 | -0.1273
| 9:27 | 11.3019 | -0.12731
| 9:27 | 11.3022 | -0.12731
| 9:27 | 11.3025 | -0.1273
| 9:27 | 11.3028 | -0.12729
| 9:27 | 11.3031 | -0.12728
| 9:27 | 11.3033 | -0.12726
| 9:27 | 11.3036 | -0.12724
| 9:27 | 11.3039 | -0.12723
| 9:27 | 11.3042 | -0.12721
| 9:27 | 11.3044 | -0.12719
| 9:27 | 11.3047 | -0.12718
| 9:27 | 11.305 | -0.12717
| 9:27 | 11.3053 | -0.12718
| 9:27 | 11.3056 | -0.12718
| 9:27 | 11.3058 | -0.1272
| 9:27 | 11.3061 | -0.12723
| 9:27 | 11.3064 | -0.12726
| 9:27 | 11.3067 | -0.12731
| 9:27 | 11.3069 | -0.12735
| 9:27 | 11.3072 | -0.1274
| 9:27 | 11.3075 | -0.12745
| 9:27 | 11.3078 | -0.12751
| 9:27 | 11.3081 | -0.12756
| 9:27 | 11.3083 | -0.12762
| 9:27 | 11.3086 | -0.12767
| 9:27 | 11.3089 | -0.12772
| 9:27 | 11.3092 | -0.12775
| 9:27 | 11.3094 | -0.12777
| 9:27 | 11.3097 | -0.12779
| 9:27 | 11.31 | -0.1278
| 9:27 | 11.3103 | -0.12779
| 9:27 | 11.3106 | -0.12778
| 9:27 | 11.3108 | -0.12776
| 9:27 | 11.3111 | -0.12773
| 9:27 | 11.3114 | -0.1277
| 9:28 | 11.3117 | -0.12767
| 9:28 | 11.3119 | -0.12763
| 9:28 | 11.3122 | -0.12758
| 9:28 | 11.3125 | -0.12754
| 9:28 | 11.3128 | -0.12749
| 9:28 | 11.3131 | -0.12743
| 9:28 | 11.3133 | -0.12738
| 9:28 | 11.3136 | -0.12732
| 9:28 | 11.3139 | -0.12727
| 9:28 | 11.3142 | -0.12721
| 9:28 | 11.3144 | -0.12715
| 9:28 | 11.3147 | -0.12709
| 9:28 | 11.315 | -0.12703
| 9:28 | 11.3153 | -0.12697
| 9:28 | 11.3156 | -0.12691
| 9:28 | 11.3158 | -0.12686
| 9:28 | 11.3161 | -0.1268
| 9:28 | 11.3164 | -0.12675
| 9:28 | 11.3167 | -0.1267
| 9:28 | 11.3169 | -0.12665
| 9:28 | 11.3172 | -0.1266
| 9:28 | 11.3175 | -0.12655
| 9:28 | 11.3178 | -0.1265
| 9:28 | 11.3181 | -0.12645
| 9:28 | 11.3183 | -0.12641
| 9:28 | 11.3186 | -0.12637
| 9:28 | 11.3189 | -0.12633
| 9:28 | 11.3192 | -0.1263
| 9:28 | 11.3194 | -0.12627
| 9:28 | 11.3197 | -0.12624
| 9:28 | 11.32 | -0.12622
| 9:28 | 11.3203 | -0.1262
| 9:28 | 11.3206 | -0.12618
| 9:28 | 11.3208 | -0.12617
| 9:28 | 11.3211 | -0.12617
| 9:28 | 11.3214 | -0.12616
| 9:28 | 11.3217 | -0.12617
| 9:28 | 11.3219 | -0.12617
| 9:28 | 11.3222 | -0.12617
| 9:28 | 11.3225 | -0.12616
| 9:28 | 11.3228 | -0.12615
| 9:28 | 11.3231 | -0.12614
| 9:28 | 11.3233 | -0.12613
| 9:28 | 11.3236 | -0.12613
| 9:28 | 11.3239 | -0.12614
| 9:28 | 11.3242 | -0.12615
| 9:28 | 11.3244 | -0.12616
| 9:28 | 11.3247 | -0.12618
| 9:28 | 11.325 | -0.1262
| 9:28 | 11.3253 | -0.12624
| 9:28 | 11.3256 | -0.12628
| 9:28 | 11.3258 | -0.12633
| 9:28 | 11.3261 | -0.12639
| 9:28 | 11.3264 | -0.12645
| 9:28 | 11.3267 | -0.12652
| 9:28 | 11.3269 | -0.12659
| 9:28 | 11.3272 | -0.12665
| 9:28 | 11.3275 | -0.1267
| 9:28 | 11.3278 | -0.12676
| 9:28 | 11.3281 | -0.12681
| 9:28 | 11.3283 | -0.12686
| 9:29 | 11.3286 | -0.12689
| 9:29 | 11.3289 | -0.1269
| 9:29 | 11.3292 | -0.1269
| 9:29 | 11.3294 | -0.12689
| 9:29 | 11.3297 | -0.12688
| 9:29 | 11.33 | -0.12686
| 9:29 | 11.3303 | -0.12684
| 9:29 | 11.3306 | -0.12681
| 9:29 | 11.3308 | -0.12678
| 9:29 | 11.3311 | -0.12675
| 9:29 | 11.3314 | -0.12671
| 9:29 | 11.3317 | -0.12667
| 9:29 | 11.3319 | -0.12663
| 9:29 | 11.3322 | -0.12659
| 9:29 | 11.3325 | -0.12654
| 9:29 | 11.3328 | -0.12649
| 9:29 | 11.3331 | -0.12644
| 9:29 | 11.3333 | -0.12638
| 9:29 | 11.3336 | -0.12632
| 9:29 | 11.3339 | -0.12626
| 9:29 | 11.3342 | -0.1262
| 9:29 | 11.3344 | -0.12614
| 9:29 | 11.3347 | -0.12608
| 9:29 | 11.335 | -0.12602
| 9:29 | 11.3353 | -0.12595
| 9:29 | 11.3356 | -0.12589
| 9:29 | 11.3358 | -0.12582
| 9:29 | 11.3361 | -0.12575
| 9:29 | 11.3364 | -0.12568
| 9:29 | 11.3367 | -0.12562
| 9:29 | 11.3369 | -0.12555
| 9:29 | 11.3372 | -0.12549
| 9:29 | 11.3375 | -0.12542
| 9:29 | 11.3378 | -0.12535
| 9:29 | 11.3381 | -0.12529
| 9:29 | 11.3383 | -0.12522
| 9:29 | 11.3386 | -0.12516
| 9:29 | 11.3389 | -0.12509
| 9:29 | 11.3392 | -0.12502
| 9:29 | 11.3394 | -0.12495
| 9:29 | 11.3397 | -0.12489
| 9:29 | 11.34 | -0.12482
| 9:29 | 11.3403 | -0.12475
| 9:29 | 11.3406 | -0.12468
| 9:29 | 11.3408 | -0.12462
| 9:29 | 11.3411 | -0.12455
| 9:29 | 11.3414 | -0.12449
| 9:29 | 11.3417 | -0.12442
| 9:29 | 11.3419 | -0.12435
| 9:29 | 11.3422 | -0.12429
| 9:29 | 11.3425 | -0.12422
| 9:29 | 11.3428 | -0.12416
| 9:29 | 11.3431 | -0.12409
| 9:29 | 11.3433 | -0.12403
| 9:29 | 11.3436 | -0.12396
| 9:29 | 11.3439 | -0.1239
| 9:29 | 11.3442 | -0.12383
| 9:29 | 11.3444 | -0.12377
| 9:29 | 11.3447 | -0.1237
| 9:30 | 11.345 | -0.12364
| 9:30 | 11.3453 | -0.12357
| 9:30 | 11.3456 | -0.12351
| 9:30 | 11.3458 | -0.12344
| 9:30 | 11.3461 | -0.12338
| 9:30 | 11.3464 | -0.12332
| 9:30 | 11.3467 | -0.12325
| 9:30 | 11.3469 | -0.12319
| 9:30 | 11.3472 | -0.12313
| 9:30 | 11.3475 | -0.12307
| 9:30 | 11.3478 | -0.12301
| 9:30 | 11.3481 | -0.12295
| 9:30 | 11.3483 | -0.12289
| 9:30 | 11.3486 | -0.12283
| 9:30 | 11.3489 | -0.12277
| 9:30 | 11.3492 | -0.12271
| 9:30 | 11.3494 | -0.12264
| 9:30 | 11.3497 | -0.12258
| 9:30 | 11.35 | -0.12251
| 9:30 | 11.3503 | -0.12245
| 9:30 | 11.3506 | -0.12238
| 9:30 | 11.3508 | -0.12231
| 9:30 | 11.3511 | -0.12224
| 9:30 | 11.3514 | -0.12217
| 9:30 | 11.3517 | -0.1221
| 9:30 | 11.3519 | -0.12202
| 9:30 | 11.3522 | -0.12195
| 9:30 | 11.3525 | -0.12188
| 9:30 | 11.3528 | -0.1218
| 9:30 | 11.3531 | -0.12173
| 9:30 | 11.3533 | -0.12165
| 9:30 | 11.3536 | -0.12157
| 9:30 | 11.3539 | -0.1215
| 9:30 | 11.3542 | -0.12142
| 9:30 | 11.3544 | -0.12134
| 9:30 | 11.3547 | -0.12126
| 9:30 | 11.355 | -0.12118
| 9:30 | 11.3553 | -0.1211
| 9:30 | 11.3556 | -0.12103
| 9:30 | 11.3558 | -0.12095
| 9:30 | 11.3561 | -0.12087
| 9:30 | 11.3564 | -0.12079
| 9:30 | 11.3567 | -0.12071
| 9:30 | 11.3569 | -0.12063
| 9:30 | 11.3572 | -0.12055
| 9:30 | 11.3575 | -0.12047
| 9:30 | 11.3578 | -0.12039
| 9:30 | 11.3581 | -0.12031
| 9:30 | 11.3583 | -0.12022
| 9:30 | 11.3586 | -0.12014
| 9:30 | 11.3589 | -0.12006
| 9:30 | 11.3592 | -0.11998
| 9:30 | 11.3594 | -0.1199
| 9:30 | 11.3597 | -0.11981
| 9:30 | 11.36 | -0.11973
| 9:30 | 11.3603 | -0.11965
| 9:30 | 11.3606 | -0.11956
| 9:30 | 11.3608 | -0.11948
| 9:30 | 11.3611 | -0.1194
| 9:30 | 11.3614 | -0.11931
| 9:30 | 11.3617 | -0.11923
| 9:31 | 11.3619 | -0.11915
| 9:31 | 11.3622 | -0.11907
| 9:31 | 11.3625 | -0.11898
| 9:31 | 11.3628 | -0.1189
| 9:31 | 11.3631 | -0.11881
| 9:31 | 11.3633 | -0.11873
| 9:31 | 11.3636 | -0.11864
| 9:31 | 11.3639 | -0.11856
| 9:31 | 11.3642 | -0.11847
| 9:31 | 11.3644 | -0.11839
| 9:31 | 11.3647 | -0.1183
| 9:31 | 11.365 | -0.11822
| 9:31 | 11.3653 | -0.11813
| 9:31 | 11.3656 | -0.11805
| 9:31 | 11.3658 | -0.11796
| 9:31 | 11.3661 | -0.11788
| 9:31 | 11.3664 | -0.1178
| 9:31 | 11.3667 | -0.11771
| 9:31 | 11.3669 | -0.11763
| 9:31 | 11.3672 | -0.11755
| 9:31 | 11.3675 | -0.11747
| 9:31 | 11.3678 | -0.11738
| 9:31 | 11.3681 | -0.1173
| 9:31 | 11.3683 | -0.11722
| 9:31 | 11.3686 | -0.11713
| 9:31 | 11.3689 | -0.11705
| 9:31 | 11.3692 | -0.11697
| 9:31 | 11.3694 | -0.11688
| 9:31 | 11.3697 | -0.1168
| 9:31 | 11.37 | -0.11672
| 9:31 | 11.3703 | -0.11664
| 9:31 | 11.3706 | -0.11655
| 9:31 | 11.3708 | -0.11647
| 9:31 | 11.3711 | -0.11638
| 9:31 | 11.3714 | -0.1163
| 9:31 | 11.3717 | -0.11622
| 9:31 | 11.3719 | -0.11613
| 9:31 | 11.3722 | -0.11605
| 9:31 | 11.3725 | -0.11597
| 9:31 | 11.3728 | -0.11588
| 9:31 | 11.3731 | -0.1158
| 9:31 | 11.3733 | -0.11572
| 9:31 | 11.3736 | -0.11563
| 9:31 | 11.3739 | -0.11555
| 9:31 | 11.3742 | -0.11547
| 9:31 | 11.3744 | -0.11538
| 9:31 | 11.3747 | -0.1153
| 9:31 | 11.375 | -0.11521
| 9:31 | 11.3753 | -0.11513
| 9:31 | 11.3756 | -0.11504
| 9:31 | 11.3758 | -0.11496
| 9:31 | 11.3761 | -0.11487
| 9:31 | 11.3764 | -0.11479
| 9:31 | 11.3767 | -0.1147
| 9:31 | 11.3769 | -0.11461
| 9:31 | 11.3772 | -0.11452
| 9:31 | 11.3775 | -0.11444
| 9:31 | 11.3778 | -0.11435
| 9:31 | 11.3781 | -0.11427
| 9:32 | 11.3783 | -0.11418
| 9:32 | 11.3786 | -0.1141
| 9:32 | 11.3789 | -0.11401
| 9:32 | 11.3792 | -0.11393
| 9:32 | 11.3794 | -0.11384
| 9:32 | 11.3797 | -0.11376
| 9:32 | 11.38 | -0.11367
| 9:32 | 11.3803 | -0.11359
| 9:32 | 11.3806 | -0.1135
| 9:32 | 11.3808 | -0.11342
| 9:32 | 11.3811 | -0.11333
| 9:32 | 11.3814 | -0.11325
| 9:32 | 11.3817 | -0.11317
| 9:32 | 11.3819 | -0.11308
| 9:32 | 11.3822 | -0.113
| 9:32 | 11.3825 | -0.11292
| 9:32 | 11.3828 | -0.11283
| 9:32 | 11.3831 | -0.11275
| 9:32 | 11.3833 | -0.11267
| 9:32 | 11.3836 | -0.11259
| 9:32 | 11.3839 | -0.1125
| 9:32 | 11.3842 | -0.11242
| 9:32 | 11.3844 | -0.11234
| 9:32 | 11.3847 | -0.11226
| 9:32 | 11.385 | -0.11217
| 9:32 | 11.3853 | -0.11209
| 9:32 | 11.3856 | -0.112
| 9:32 | 11.3858 | -0.11192
| 9:32 | 11.3861 | -0.11184
| 9:32 | 11.3864 | -0.11176
| 9:32 | 11.3867 | -0.11168
| 9:32 | 11.3869 | -0.1116
| 9:32 | 11.3872 | -0.11152
| 9:32 | 11.3875 | -0.11144
| 9:32 | 11.3878 | -0.11136
| 9:32 | 11.3881 | -0.11128
| 9:32 | 11.3883 | -0.1112
| 9:32 | 11.3886 | -0.11111
| 9:32 | 11.3889 | -0.11103
| 9:32 | 11.3892 | -0.11095
| 9:32 | 11.3894 | -0.11087
| 9:32 | 11.3897 | -0.11079
| 9:32 | 11.39 | -0.11072
| 9:32 | 11.3903 | -0.11064
| 9:32 | 11.3906 | -0.11056
| 9:32 | 11.3908 | -0.11048
| 9:32 | 11.3911 | -0.1104
| 9:32 | 11.3914 | -0.11032
| 9:32 | 11.3917 | -0.11025
| 9:32 | 11.3919 | -0.11017
| 9:32 | 11.3922 | -0.11009
| 9:32 | 11.3925 | -0.11001
| 9:32 | 11.3928 | -0.10994
| 9:32 | 11.3931 | -0.10986
| 9:32 | 11.3933 | -0.10978
| 9:32 | 11.3936 | -0.1097
| 9:32 | 11.3939 | -0.10962
| 9:32 | 11.3942 | -0.10954
| 9:32 | 11.3944 | -0.10946
| 9:32 | 11.3947 | -0.10939
| 9:32 | 11.395 | -0.10931
| 9:33 | 11.3953 | -0.10924
| 9:33 | 11.3956 | -0.10916
| 9:33 | 11.3958 | -0.10908
| 9:33 | 11.3961 | -0.10901
| 9:33 | 11.3964 | -0.10893
| 9:33 | 11.3967 | -0.10886
| 9:33 | 11.3969 | -0.10878
| 9:33 | 11.3972 | -0.10871
| 9:33 | 11.3975 | -0.10863
| 9:33 | 11.3978 | -0.10856
| 9:33 | 11.3981 | -0.10848
| 9:33 | 11.3983 | -0.10841
| 9:33 | 11.3986 | -0.10833
| 9:33 | 11.3989 | -0.10825
| 9:33 | 11.3992 | -0.10818
| 9:33 | 11.3994 | -0.1081
| 9:33 | 11.3997 | -0.10803
| 9:33 | 11.4 | -0.10795
| 9:33 | 11.4003 | -0.10788
| 9:33 | 11.4006 | -0.1078
| 9:33 | 11.4008 | -0.10773
| 9:33 | 11.4011 | -0.10765
| 9:33 | 11.4014 | -0.10758
| 9:33 | 11.4017 | -0.1075
| 9:33 | 11.4019 | -0.10743
| 9:33 | 11.4022 | -0.10736
| 9:33 | 11.4025 | -0.10728
| 9:33 | 11.4028 | -0.10721
| 9:33 | 11.4031 | -0.10714
| 9:33 | 11.4033 | -0.10706
| 9:33 | 11.4036 | -0.10699
| 9:33 | 11.4039 | -0.10692
| 9:33 | 11.4042 | -0.10684
| 9:33 | 11.4044 | -0.10677
| 9:33 | 11.4047 | -0.1067
| 9:33 | 11.405 | -0.10663
| 9:33 | 11.4053 | -0.10655
| 9:33 | 11.4056 | -0.10648
| 9:33 | 11.4058 | -0.10641
| 9:33 | 11.4061 | -0.10633
| 9:33 | 11.4064 | -0.10626
| 9:33 | 11.4067 | -0.10619
| 9:33 | 11.4069 | -0.10611
| 9:33 | 11.4072 | -0.10604
| 9:33 | 11.4075 | -0.10597
| 9:33 | 11.4078 | -0.10589
| 9:33 | 11.4081 | -0.10582
| 9:33 | 11.4083 | -0.10575
| 9:33 | 11.4086 | -0.10568
| 9:33 | 11.4089 | -0.1056
| 9:33 | 11.4092 | -0.10553
| 9:33 | 11.4094 | -0.10546
| 9:33 | 11.4097 | -0.10538
| 9:33 | 11.41 | -0.10531
| 9:33 | 11.4103 | -0.10524
| 9:33 | 11.4106 | -0.10517
| 9:33 | 11.4108 | -0.1051
| 9:33 | 11.4111 | -0.10503
| 9:33 | 11.4114 | -0.10496
| 9:34 | 11.4117 | -0.10489
| 9:34 | 11.4119 | -0.10483
| 9:34 | 11.4122 | -0.10476
| 9:34 | 11.4125 | -0.10469
| 9:34 | 11.4128 | -0.10462
| 9:34 | 11.4131 | -0.10455
| 9:34 | 11.4133 | -0.10448
| 9:34 | 11.4136 | -0.10441
| 9:34 | 11.4139 | -0.10435
| 9:34 | 11.4142 | -0.10428
| 9:34 | 11.4144 | -0.10421
| 9:34 | 11.4147 | -0.10414
| 9:34 | 11.415 | -0.10407
| 9:34 | 11.4153 | -0.104
| 9:34 | 11.4156 | -0.10394
| 9:34 | 11.4158 | -0.10387
| 9:34 | 11.4161 | -0.1038
| 9:34 | 11.4164 | -0.10373
| 9:34 | 11.4167 | -0.10366
| 9:34 | 11.4169 | -0.10359
| 9:34 | 11.4172 | -0.10353
| 9:34 | 11.4175 | -0.10346
| 9:34 | 11.4178 | -0.10339
| 9:34 | 11.4181 | -0.10332
| 9:34 | 11.4183 | -0.10325
| 9:34 | 11.4186 | -0.10319
| 9:34 | 11.4189 | -0.10312
| 9:34 | 11.4192 | -0.10305
| 9:34 | 11.4194 | -0.10298
| 9:34 | 11.4197 | -0.10291
| 9:34 | 11.42 | -0.10285
| 9:34 | 11.4203 | -0.10278
| 9:34 | 11.4206 | -0.10271
| 9:34 | 11.4208 | -0.10264
| 9:34 | 11.4211 | -0.10257
| 9:34 | 11.4214 | -0.10251
| 9:34 | 11.4217 | -0.10244
| 9:34 | 11.4219 | -0.10237
| 9:34 | 11.4222 | -0.1023
| 9:34 | 11.4225 | -0.10223
| 9:34 | 11.4228 | -0.10217
| 9:34 | 11.4231 | -0.1021
| 9:34 | 11.4233 | -0.10203
| 9:34 | 11.4236 | -0.10196
| 9:34 | 11.4239 | -0.10189
| 9:34 | 11.4242 | -0.10183
| 9:34 | 11.4244 | -0.10176
| 9:34 | 11.4247 | -0.10169
| 9:34 | 11.425 | -0.10162
| 9:34 | 11.4253 | -0.10156
| 9:34 | 11.4256 | -0.10149
| 9:34 | 11.4258 | -0.10142
| 9:34 | 11.4261 | -0.10135
| 9:34 | 11.4264 | -0.10128
| 9:34 | 11.4267 | -0.10122
| 9:34 | 11.4269 | -0.10115
| 9:34 | 11.4272 | -0.10108
| 9:34 | 11.4275 | -0.10101
| 9:34 | 11.4278 | -0.10095
| 9:34 | 11.4281 | -0.10088
| 9:34 | 11.4283 | -0.10081
| 9:35 | 11.4286 | -0.10074
| 9:35 | 11.4289 | -0.10068
| 9:35 | 11.4292 | -0.10061
| 9:35 | 11.4294 | -0.10054
| 9:35 | 11.4297 | -0.10047
| 9:35 | 11.43 | -0.1004
| 9:35 | 11.4303 | -0.10034
| 9:35 | 11.4306 | -0.10027
| 9:35 | 11.4308 | -0.1002
| 9:35 | 11.4311 | -0.10013
| 9:35 | 11.4314 | -0.10007
| 9:35 | 11.4317 | -0.1
| 9:35 | 11.4319 | -0.099932
| 9:35 | 11.4322 | -0.099866
| 9:35 | 11.4325 | -0.099799
| 9:35 | 11.4328 | -0.099733
| 9:35 | 11.4331 | -0.099667
| 9:35 | 11.4333 | -0.099601
| 9:35 | 11.4336 | -0.099535
| 9:35 | 11.4339 | -0.09947
| 9:35 | 11.4342 | -0.099404
| 9:35 | 11.4344 | -0.099339
| 9:35 | 11.4347 | -0.099274
| 9:35 | 11.435 | -0.099208
| 9:35 | 11.4353 | -0.099143
| 9:35 | 11.4356 | -0.099078
| 9:35 | 11.4358 | -0.099012
| 9:35 | 11.4361 | -0.098947
| 9:35 | 11.4364 | -0.098882
| 9:35 | 11.4367 | -0.098816
| 9:35 | 11.4369 | -0.098751
| 9:35 | 11.4372 | -0.098686
| 9:35 | 11.4375 | -0.09862
| 9:35 | 11.4378 | -0.098555
| 9:35 | 11.4381 | -0.09849
| 9:35 | 11.4383 | -0.098427
| 9:35 | 11.4386 | -0.098364
| 9:35 | 11.4389 | -0.098301
| 9:35 | 11.4392 | -0.098238
| 9:35 | 11.4394 | -0.098175
| 9:35 | 11.4397 | -0.098112
| 9:35 | 11.44 | -0.09805
| 9:35 | 11.4403 | -0.097987
| 9:35 | 11.4406 | -0.097925
| 9:35 | 11.4408 | -0.097864
| 9:35 | 11.4411 | -0.097803
| 9:35 | 11.4414 | -0.097742
| 9:35 | 11.4417 | -0.097681
| 9:35 | 11.4419 | -0.09762
| 9:35 | 11.4422 | -0.097556
| 9:35 | 11.4425 | -0.097493
| 9:35 | 11.4428 | -0.09743
| 9:35 | 11.4431 | -0.097367
| 9:35 | 11.4433 | -0.097304
| 9:35 | 11.4436 | -0.097241
| 9:35 | 11.4439 | -0.097178
| 9:35 | 11.4442 | -0.097115
| 9:35 | 11.4444 | -0.097054
| 9:35 | 11.4447 | -0.096995
| 9:36 | 11.445 | -0.096936
| 9:36 | 11.4453 | -0.096878
| 9:36 | 11.4456 | -0.096818
| 9:36 | 11.4458 | -0.096757
| 9:36 | 11.4461 | -0.096696
| 9:36 | 11.4464 | -0.096635
| 9:36 | 11.4467 | -0.096575
| 9:36 | 11.4469 | -0.096514
| 9:36 | 11.4472 | -0.096453
| 9:36 | 11.4475 | -0.096392
| 9:36 | 11.4478 | -0.096331
| 9:36 | 11.4481 | -0.09627
| 9:36 | 11.4483 | -0.09621
| 9:36 | 11.4486 | -0.09615
| 9:36 | 11.4489 | -0.09609
| 9:36 | 11.4492 | -0.09603
| 9:36 | 11.4494 | -0.095971
| 9:36 | 11.4497 | -0.095912
| 9:36 | 11.45 | -0.095853
| 9:36 | 11.4503 | -0.095794
| 9:36 | 11.4506 | -0.095736
| 9:36 | 11.4508 | -0.095677
| 9:36 | 11.4511 | -0.095618
| 9:36 | 11.4514 | -0.09556
| 9:36 | 11.4517 | -0.095501
| 9:36 | 11.4519 | -0.095443
| 9:36 | 11.4522 | -0.095384
| 9:36 | 11.4525 | -0.095325
| 9:36 | 11.4528 | -0.095267
| 9:36 | 11.4531 | -0.095208
| 9:36 | 11.4533 | -0.095149
| 9:36 | 11.4536 | -0.095091
| 9:36 | 11.4539 | -0.095032
| 9:36 | 11.4542 | -0.094974
| 9:36 | 11.4544 | -0.094915
| 9:36 | 11.4547 | -0.094856
| 9:36 | 11.455 | -0.094798
| 9:36 | 11.4553 | -0.094739
| 9:36 | 11.4556 | -0.094683
| 9:36 | 11.4558 | -0.094626
| 9:36 | 11.4561 | -0.09457
| 9:36 | 11.4564 | -0.094513
| 9:36 | 11.4567 | -0.094457
| 9:36 | 11.4569 | -0.094401
| 9:36 | 11.4572 | -0.094344
| 9:36 | 11.4575 | -0.094288
| 9:36 | 11.4578 | -0.094231
| 9:36 | 11.4581 | -0.094175
| 9:36 | 11.4583 | -0.094119
| 9:36 | 11.4586 | -0.094062
| 9:36 | 11.4589 | -0.094006
| 9:36 | 11.4592 | -0.093949
| 9:36 | 11.4594 | -0.093893
| 9:36 | 11.4597 | -0.093837
| 9:36 | 11.46 | -0.09378
| 9:36 | 11.4603 | -0.093724
| 9:36 | 11.4606 | -0.093669
| 9:36 | 11.4608 | -0.093615
| 9:36 | 11.4611 | -0.093561
| 9:36 | 11.4614 | -0.093507
| 9:36 | 11.4617 | -0.093453
| 9:37 | 11.4619 | -0.093398
| 9:37 | 11.4622 | -0.093344
| 9:37 | 11.4625 | -0.09329
| 9:37 | 11.4628 | -0.093236
| 9:37 | 11.4631 | -0.093182
| 9:37 | 11.4633 | -0.093128
| 9:37 | 11.4636 | -0.093073
| 9:37 | 11.4639 | -0.093019
| 9:37 | 11.4642 | -0.092965
| 9:37 | 11.4644 | -0.092911
| 9:37 | 11.4647 | -0.092857
| 9:37 | 11.465 | -0.092803
| 9:37 | 11.4653 | -0.09275
| 9:37 | 11.4656 | -0.092697
| 9:37 | 11.4658 | -0.092644
| 9:37 | 11.4661 | -0.092591
| 9:37 | 11.4664 | -0.092538
| 9:37 | 11.4667 | -0.092486
| 9:37 | 11.4669 | -0.092434
| 9:37 | 11.4672 | -0.092382
| 9:37 | 11.4675 | -0.09233
| 9:37 | 11.4678 | -0.092278
| 9:37 | 11.4681 | -0.092226
| 9:37 | 11.4683 | -0.092174
| 9:37 | 11.4686 | -0.092122
| 9:37 | 11.4689 | -0.09207
| 9:37 | 11.4692 | -0.092018
| 9:37 | 11.4694 | -0.091966
| 9:37 | 11.4697 | -0.091915
| 9:37 | 11.47 | -0.091863
| 9:37 | 11.4703 | -0.091811
| 9:37 | 11.4706 | -0.091759
| 9:37 | 11.4708 | -0.091708
| 9:37 | 11.4711 | -0.091658
| 9:37 | 11.4714 | -0.091609
| 9:37 | 11.4717 | -0.091559
| 9:37 | 11.4719 | -0.091509
| 9:37 | 11.4722 | -0.091457
| 9:37 | 11.4725 | -0.091405
| 9:37 | 11.4728 | -0.091353
| 9:37 | 11.4731 | -0.091301
| 9:37 | 11.4733 | -0.091249
| 9:37 | 11.4736 | -0.091197
| 9:37 | 11.4739 | -0.091145
| 9:37 | 11.4742 | -0.091093
| 9:37 | 11.4744 | -0.091042
| 9:37 | 11.4747 | -0.09099
| 9:37 | 11.475 | -0.090938
| 9:37 | 11.4753 | -0.090886
| 9:37 | 11.4756 | -0.090834
| 9:37 | 11.4758 | -0.090782
| 9:37 | 11.4761 | -0.09073
| 9:37 | 11.4764 | -0.090678
| 9:37 | 11.4767 | -0.090626
| 9:37 | 11.4769 | -0.090574
| 9:37 | 11.4772 | -0.090522
| 9:37 | 11.4775 | -0.090472
| 9:37 | 11.4778 | -0.090422
| 9:37 | 11.4781 | -0.090373
| 9:38 | 11.4783 | -0.090323
| 9:38 | 11.4786 | -0.090273
| 9:38 | 11.4789 | -0.090223
| 9:38 | 11.4792 | -0.090174
| 9:38 | 11.4794 | -0.090124
| 9:38 | 11.4797 | -0.090074
| 9:38 | 11.48 | -0.090024
| 9:38 | 11.4803 | -0.089975
| 9:38 | 11.4806 | -0.089925
| 9:38 | 11.4808 | -0.089875
| 9:38 | 11.4811 | -0.089825
| 9:38 | 11.4814 | -0.089776
| 9:38 | 11.4817 | -0.089726
| 9:38 | 11.4819 | -0.089676
| 9:38 | 11.4822 | -0.089627
| 9:38 | 11.4825 | -0.089577
| 9:38 | 11.4828 | -0.089527
| 9:38 | 11.4831 | -0.089477
| 9:38 | 11.4833 | -0.089428
| 9:38 | 11.4836 | -0.089378
| 9:38 | 11.4839 | -0.089328
| 9:38 | 11.4842 | -0.089278
| 9:38 | 11.4844 | -0.089229
| 9:38 | 11.4847 | -0.089181
| 9:38 | 11.485 | -0.089133
| 9:38 | 11.4853 | -0.089085
| 9:38 | 11.4856 | -0.089038
| 9:38 | 11.4858 | -0.08899
| 9:38 | 11.4861 | -0.088943
| 9:38 | 11.4864 | -0.088895
| 9:38 | 11.4867 | -0.088848
| 9:38 | 11.4869 | -0.0888
| 9:38 | 11.4872 | -0.088753
| 9:38 | 11.4875 | -0.088705
| 9:38 | 11.4878 | -0.088658
| 9:38 | 11.4881 | -0.08861
| 9:38 | 11.4883 | -0.088563
| 9:38 | 11.4886 | -0.088515
| 9:38 | 11.4889 | -0.088468
| 9:38 | 11.4892 | -0.08842
| 9:38 | 11.4894 | -0.088373
| 9:38 | 11.4897 | -0.088325
| 9:38 | 11.49 | -0.088278
| 9:38 | 11.4903 | -0.088232
| 9:38 | 11.4906 | -0.088185
| 9:38 | 11.4908 | -0.088139
| 9:38 | 11.4911 | -0.088093
| 9:38 | 11.4914 | -0.088048
| 9:38 | 11.4917 | -0.088002
| 9:38 | 11.4919 | -0.087957
| 9:38 | 11.4922 | -0.087912
| 9:38 | 11.4925 | -0.087867
| 9:38 | 11.4928 | -0.087821
| 9:38 | 11.4931 | -0.087776
| 9:38 | 11.4933 | -0.087731
| 9:38 | 11.4936 | -0.087685
| 9:38 | 11.4939 | -0.08764
| 9:38 | 11.4942 | -0.087595
| 9:38 | 11.4944 | -0.087549
| 9:38 | 11.4947 | -0.087504
| 9:38 | 11.495 | -0.087459
| 9:39 | 11.4953 | -0.087413
| 9:39 | 11.4956 | -0.087367
| 9:39 | 11.4958 | -0.087319
| 9:39 | 11.4961 | -0.087271
| 9:39 | 11.4964 | -0.087226
| 9:39 | 11.4967 | -0.08718
| 9:39 | 11.4969 | -0.087135
| 9:39 | 11.4972 | -0.087088
| 9:39 | 11.4975 | -0.087041
| 9:39 | 11.4978 | -0.086993
| 9:39 | 11.4981 | -0.086946
| 9:39 | 11.4983 | -0.0869
| 9:39 | 11.4986 | -0.086854
| 9:39 | 11.4989 | -0.086808
| 9:39 | 11.4992 | -0.086764
| 9:39 | 11.4994 | -0.086719
| 9:39 | 11.4997 | -0.086675
| 9:39 | 11.5 | -0.086632
| 9:39 | 11.5003 | -0.086589
| 9:39 | 11.5006 | -0.086544
| 9:39 | 11.5008 | -0.086499
| 9:39 | 11.5011 | -0.086453
| 9:39 | 11.5014 | -0.086408
| 9:39 | 11.5017 | -0.086363
| 9:39 | 11.5019 | -0.086317
| 9:39 | 11.5022 | -0.086272
| 9:39 | 11.5025 | -0.086227
| 9:39 | 11.5028 | -0.086181
| 9:39 | 11.5031 | -0.086136
| 9:39 | 11.5033 | -0.086091
| 9:39 | 11.5036 | -0.086045
| 9:39 | 11.5039 | -0.086
| 9:39 | 11.5042 | -0.085955
| 9:39 | 11.5044 | -0.08591
| 9:39 | 11.5047 | -0.085864
| 9:39 | 11.505 | -0.085819
| 9:39 | 11.5053 | -0.085774
| 9:39 | 11.5056 | -0.085728
| 9:39 | 11.5058 | -0.085683
| 9:39 | 11.5061 | -0.085639
| 9:39 | 11.5064 | -0.085596
| 9:39 | 11.5067 | -0.085553
| 9:39 | 11.5069 | -0.08551
| 9:39 | 11.5072 | -0.085467
| 9:39 | 11.5075 | -0.085423
| 9:39 | 11.5078 | -0.08538
| 9:39 | 11.5081 | -0.085337
| 9:39 | 11.5083 | -0.085296
| 9:39 | 11.5086 | -0.085255
| 9:39 | 11.5089 | -0.085214
| 9:39 | 11.5092 | -0.085171
| 9:39 | 11.5094 | -0.085127
| 9:39 | 11.5097 | -0.085084
| 9:39 | 11.51 | -0.085042
| 9:39 | 11.5103 | -0.085001
| 9:39 | 11.5106 | -0.08496
| 9:39 | 11.5108 | -0.08492
| 9:39 | 11.5111 | -0.084879
| 9:39 | 11.5114 | -0.084838
| 9:40 | 11.5117 | -0.084797
| 9:40 | 11.5119 | -0.084756
| 9:40 | 11.5122 | -0.084715
| 9:40 | 11.5125 | -0.084674
| 9:40 | 11.5128 | -0.084634
| 9:40 | 11.5131 | -0.084593
| 9:40 | 11.5133 | -0.084552
| 9:40 | 11.5136 | -0.084511
| 9:40 | 11.5139 | -0.08447
| 9:40 | 11.5142 | -0.084429
| 9:40 | 11.5144 | -0.084388
| 9:40 | 11.5147 | -0.084348
| 9:40 | 11.515 | -0.084307
| 9:40 | 11.5153 | -0.084267
| 9:40 | 11.5156 | -0.084227
| 9:40 | 11.5158 | -0.084187
| 9:40 | 11.5161 | -0.084147
| 9:40 | 11.5164 | -0.084108
| 9:40 | 11.5167 | -0.084069
| 9:40 | 11.5169 | -0.08403
| 9:40 | 11.5172 | -0.083991
| 9:40 | 11.5175 | -0.083953
| 9:40 | 11.5178 | -0.083914
| 9:40 | 11.5181 | -0.083876
| 9:40 | 11.5183 | -0.083837
| 9:40 | 11.5186 | -0.083798
| 9:40 | 11.5189 | -0.08376
| 9:40 | 11.5192 | -0.083721
| 9:40 | 11.5194 | -0.083682
| 9:40 | 11.5197 | -0.083644
| 9:40 | 11.52 | -0.083605
| 9:40 | 11.5203 | -0.083566
| 9:40 | 11.5206 | -0.083528
| 9:40 | 11.5208 | -0.083489
| 9:40 | 11.5211 | -0.083451
| 9:40 | 11.5214 | -0.083412
| 9:40 | 11.5217 | -0.083373
| 9:40 | 11.5219 | -0.083335
| 9:40 | 11.5222 | -0.083296
| 9:40 | 11.5225 | -0.083257
| 9:40 | 11.5228 | -0.083219
| 9:40 | 11.5231 | -0.083181
| 9:40 | 11.5233 | -0.083143
| 9:40 | 11.5236 | -0.083105
| 9:40 | 11.5239 | -0.083067
| 9:40 | 11.5242 | -0.08303
| 9:40 | 11.5244 | -0.082994
| 9:40 | 11.5247 | -0.082957
| 9:40 | 11.525 | -0.082921
| 9:40 | 11.5253 | -0.082883
| 9:40 | 11.5256 | -0.082844
| 9:40 | 11.5258 | -0.082806
| 9:40 | 11.5261 | -0.082767
| 9:40 | 11.5264 | -0.082729
| 9:40 | 11.5267 | -0.082693
| 9:40 | 11.5269 | -0.082656
| 9:40 | 11.5272 | -0.08262
| 9:40 | 11.5275 | -0.082583
| 9:40 | 11.5278 | -0.082547
| 9:40 | 11.5281 | -0.08251
| 9:40 | 11.5283 | -0.082474
| 9:41 | 11.5286 | -0.082438
| 9:41 | 11.5289 | -0.082401
| 9:41 | 11.5292 | -0.082365
| 9:41 | 11.5294 | -0.082328
| 9:41 | 11.5297 | -0.082292
| 9:41 | 11.53 | -0.082256
| 9:41 | 11.5303 | -0.082219
| 9:41 | 11.5306 | -0.082183
| 9:41 | 11.5308 | -0.082147
| 9:41 | 11.5311 | -0.08211
| 9:41 | 11.5314 | -0.082074
| 9:41 | 11.5317 | -0.082038
| 9:41 | 11.5319 | -0.082003
| 9:41 | 11.5322 | -0.081968
| 9:41 | 11.5325 | -0.081933
| 9:41 | 11.5328 | -0.081898
| 9:41 | 11.5331 | -0.081863
| 9:41 | 11.5333 | -0.081829
| 9:41 | 11.5336 | -0.081795
| 9:41 | 11.5339 | -0.081759
| 9:41 | 11.5342 | -0.081724
| 9:41 | 11.5344 | -0.08169
| 9:41 | 11.5347 | -0.081656
| 9:41 | 11.535 | -0.081622
| 9:41 | 11.5353 | -0.081588
| 9:41 | 11.5356 | -0.081554
| 9:41 | 11.5358 | -0.08152
| 9:41 | 11.5361 | -0.081489
| 9:41 | 11.5364 | -0.081457
| 9:41 | 11.5367 | -0.081425
| 9:41 | 11.5369 | -0.081394
| 9:41 | 11.5372 | -0.081362
| 9:41 | 11.5375 | -0.081331
| 9:41 | 11.5378 | -0.081299
| 9:41 | 11.5381 | -0.081267
| 9:41 | 11.5383 | -0.081236
| 9:41 | 11.5386 | -0.081205
| 9:41 | 11.5389 | -0.081173
| 9:41 | 11.5392 | -0.081142
| 9:41 | 11.5394 | -0.08111
| 9:41 | 11.5397 | -0.081079
| 9:41 | 11.54 | -0.081048
| 9:41 | 11.5403 | -0.081016
| 9:41 | 11.5406 | -0.080985
| 9:41 | 11.5408 | -0.080954
| 9:41 | 11.5411 | -0.080923
| 9:41 | 11.5414 | -0.080891
| 9:41 | 11.5417 | -0.08086
| 9:41 | 11.5419 | -0.080829
| 9:41 | 11.5422 | -0.080798
| 9:41 | 11.5425 | -0.080767
| 9:41 | 11.5428 | -0.080736
| 9:41 | 11.5431 | -0.080705
| 9:41 | 11.5433 | -0.080674
| 9:41 | 11.5436 | -0.080643
| 9:41 | 11.5439 | -0.080612
| 9:41 | 11.5442 | -0.080581
| 9:41 | 11.5444 | -0.08055
| 9:41 | 11.5447 | -0.080519
| 9:42 | 11.545 | -0.080488
| 9:42 | 11.5453 | -0.080457
| 9:42 | 11.5456 | -0.080426
| 9:42 | 11.5458 | -0.080395
| 9:42 | 11.5461 | -0.080364
| 9:42 | 11.5464 | -0.080333
| 9:42 | 11.5467 | -0.080303
| 9:42 | 11.5469 | -0.080272
| 9:42 | 11.5472 | -0.080241
| 9:42 | 11.5475 | -0.08021
| 9:42 | 11.5478 | -0.080179
| 9:42 | 11.5481 | -0.080149
| 9:42 | 11.5483 | -0.080118
| 9:42 | 11.5486 | -0.080087
| 9:42 | 11.5489 | -0.080057
| 9:42 | 11.5492 | -0.080026
| 9:42 | 11.5494 | -0.079996
| 9:42 | 11.5497 | -0.079965
| 9:42 | 11.55 | -0.079934
| 9:42 | 11.5503 | -0.079904
| 9:42 | 11.5506 | -0.079873
| 9:42 | 11.5508 | -0.079843
| 9:42 | 11.5511 | -0.079812
| 9:42 | 11.5514 | -0.079781
| 9:42 | 11.5517 | -0.07975
| 9:42 | 11.5519 | -0.079719
| 9:42 | 11.5522 | -0.079687
| 9:42 | 11.5525 | -0.079654
| 9:42 | 11.5528 | -0.079621
| 9:42 | 11.5531 | -0.079589
| 9:42 | 11.5533 | -0.079556
| 9:42 | 11.5536 | -0.079524
| 9:42 | 11.5539 | -0.079491
| 9:42 | 11.5542 | -0.079458
| 9:42 | 11.5544 | -0.079426
| 9:42 | 11.5547 | -0.079393
| 9:42 | 11.555 | -0.079361
| 9:42 | 11.5553 | -0.079328
| 9:42 | 11.5556 | -0.079296
| 9:42 | 11.5558 | -0.079263
| 9:42 | 11.5561 | -0.079231
| 9:42 | 11.5564 | -0.079199
| 9:42 | 11.5567 | -0.079166
| 9:42 | 11.5569 | -0.079134
| 9:42 | 11.5572 | -0.079101
| 9:42 | 11.5575 | -0.079069
| 9:42 | 11.5578 | -0.079037
| 9:42 | 11.5581 | -0.079005
| 9:42 | 11.5583 | -0.078972
| 9:42 | 11.5586 | -0.07894
| 9:42 | 11.5589 | -0.078906
| 9:42 | 11.5592 | -0.078871
| 9:42 | 11.5594 | -0.078837
| 9:42 | 11.5597 | -0.078802
| 9:42 | 11.56 | -0.078768
| 9:42 | 11.5603 | -0.078734
| 9:42 | 11.5606 | -0.078699
| 9:42 | 11.5608 | -0.078665
| 9:42 | 11.5611 | -0.078631
| 9:42 | 11.5614 | -0.078596
| 9:42 | 11.5617 | -0.078562
| 9:43 | 11.5619 | -0.078528
| 9:43 | 11.5622 | -0.078494
| 9:43 | 11.5625 | -0.078459
| 9:43 | 11.5628 | -0.078425
| 9:43 | 11.5631 | -0.07839
| 9:43 | 11.5633 | -0.078353
| 9:43 | 11.5636 | -0.078317
| 9:43 | 11.5639 | -0.07828
| 9:43 | 11.5642 | -0.078244
| 9:43 | 11.5644 | -0.078208
| 9:43 | 11.5647 | -0.078171
| 9:43 | 11.565 | -0.078135
| 9:43 | 11.5653 | -0.078098
| 9:43 | 11.5656 | -0.078061
| 9:43 | 11.5658 | -0.078024
| 9:43 | 11.5661 | -0.077986
| 9:43 | 11.5664 | -0.077948
| 9:43 | 11.5667 | -0.07791
| 9:43 | 11.5669 | -0.077872
| 9:43 | 11.5672 | -0.077834
| 9:43 | 11.5675 | -0.077796
| 9:43 | 11.5678 | -0.077757
| 9:43 | 11.5681 | -0.077719
| 9:43 | 11.5683 | -0.077681
| 9:43 | 11.5686 | -0.077642
| 9:43 | 11.5689 | -0.077604
| 9:43 | 11.5692 | -0.077566
| 9:43 | 11.5694 | -0.077528
| 9:43 | 11.5697 | -0.07749
| 9:43 | 11.57 | -0.077451
| 9:43 | 11.5703 | -0.077413
| 9:43 | 11.5706 | -0.077373
| 9:43 | 11.5708 | -0.077333
| 9:43 | 11.5711 | -0.077293
| 9:43 | 11.5714 | -0.077253
| 9:43 | 11.5717 | -0.077213
| 9:43 | 11.5719 | -0.077173
| 9:43 | 11.5722 | -0.077133
| 9:43 | 11.5725 | -0.077095
| 9:43 | 11.5728 | -0.077057
| 9:43 | 11.5731 | -0.077019
| 9:43 | 11.5733 | -0.07698
| 9:43 | 11.5736 | -0.076941
| 9:43 | 11.5739 | -0.076901
| 9:43 | 11.5742 | -0.076861
| 9:43 | 11.5744 | -0.07682
| 9:43 | 11.5747 | -0.076778
| 9:43 | 11.575 | -0.076736
| 9:43 | 11.5753 | -0.076694
| 9:43 | 11.5756 | -0.076653
| 9:43 | 11.5758 | -0.076614
| 9:43 | 11.5761 | -0.076574
| 9:43 | 11.5764 | -0.076534
| 9:43 | 11.5767 | -0.076495
| 9:43 | 11.5769 | -0.076455
| 9:43 | 11.5772 | -0.076416
| 9:43 | 11.5775 | -0.076376
| 9:43 | 11.5778 | -0.076336
| 9:43 | 11.5781 | -0.076295
| 9:44 | 11.5783 | -0.076253
| 9:44 | 11.5786 | -0.076211
| 9:44 | 11.5789 | -0.07617
| 9:44 | 11.5792 | -0.076129
| 9:44 | 11.5794 | -0.076088
| 9:44 | 11.5797 | -0.076046
| 9:44 | 11.58 | -0.076004
| 9:44 | 11.5803 | -0.075961
| 9:44 | 11.5806 | -0.075917
| 9:44 | 11.5808 | -0.075875
| 9:44 | 11.5811 | -0.075834
| 9:44 | 11.5814 | -0.075793
| 9:44 | 11.5817 | -0.075752
| 9:44 | 11.5819 | -0.075711
| 9:44 | 11.5822 | -0.07567
| 9:44 | 11.5825 | -0.075629
| 9:44 | 11.5828 | -0.075588
| 9:44 | 11.5831 | -0.075547
| 9:44 | 11.5833 | -0.075506
| 9:44 | 11.5836 | -0.075465
| 9:44 | 11.5839 | -0.075424
| 9:44 | 11.5842 | -0.075381
| 9:44 | 11.5844 | -0.075339
| 9:44 | 11.5847 | -0.075294
| 9:44 | 11.585 | -0.075249
| 9:44 | 11.5853 | -0.075204
| 9:44 | 11.5856 | -0.075161
| 9:44 | 11.5858 | -0.075119
| 9:44 | 11.5861 | -0.075076
| 9:44 | 11.5864 | -0.075033
| 9:44 | 11.5867 | -0.074988
| 9:44 | 11.5869 | -0.074944
| 9:44 | 11.5872 | -0.074899
| 9:44 | 11.5875 | -0.074855
| 9:44 | 11.5878 | -0.074812
| 9:44 | 11.5881 | -0.074769
| 9:44 | 11.5883 | -0.074725
| 9:44 | 11.5886 | -0.07468
| 9:44 | 11.5889 | -0.074635
| 9:44 | 11.5892 | -0.07459
| 9:44 | 11.5894 | -0.074546
| 9:44 | 11.5897 | -0.074501
| 9:44 | 11.59 | -0.074457
| 9:44 | 11.5903 | -0.074413
| 9:44 | 11.5906 | -0.074368
| 9:44 | 11.5908 | -0.074324
| 9:44 | 11.5911 | -0.07428
| 9:44 | 11.5914 | -0.074236
| 9:44 | 11.5917 | -0.074192
| 9:44 | 11.5919 | -0.074147
| 9:44 | 11.5922 | -0.074103
| 9:44 | 11.5925 | -0.074059
| 9:44 | 11.5928 | -0.074015
| 9:44 | 11.5931 | -0.073971
| 9:44 | 11.5933 | -0.073927
| 9:44 | 11.5936 | -0.073884
| 9:44 | 11.5939 | -0.07384
| 9:44 | 11.5942 | -0.073795
| 9:44 | 11.5944 | -0.073749
| 9:44 | 11.5947 | -0.073703
| 9:44 | 11.595 | -0.073657
| 9:45 | 11.5953 | -0.073611
| 9:45 | 11.5956 | -0.073565
| 9:45 | 11.5958 | -0.07352
| 9:45 | 11.5961 | -0.073474
| 9:45 | 11.5964 | -0.073428
| 9:45 | 11.5967 | -0.073382
| 9:45 | 11.5969 | -0.073337
| 9:45 | 11.5972 | -0.073291
| 9:45 | 11.5975 | -0.073246
| 9:45 | 11.5978 | -0.0732
| 9:45 | 11.5981 | -0.073155
| 9:45 | 11.5983 | -0.073109
| 9:45 | 11.5986 | -0.073064
| 9:45 | 11.5989 | -0.073018
| 9:45 | 11.5992 | -0.072973
| 9:45 | 11.5994 | -0.072928
| 9:45 | 11.5997 | -0.072883
| 9:45 | 11.6 | -0.072837
| 9:45 | 11.6003 | -0.072792
| 9:45 | 11.6006 | -0.072747
| 9:45 | 11.6008 | -0.072701
| 9:45 | 11.6011 | -0.072654
| 9:45 | 11.6014 | -0.072606
| 9:45 | 11.6017 | -0.072559
| 9:45 | 11.6019 | -0.072512
| 9:45 | 11.6022 | -0.072465
| 9:45 | 11.6025 | -0.072418
| 9:45 | 11.6028 | -0.072371
| 9:45 | 11.6031 | -0.072324
| 9:45 | 11.6033 | -0.072277
| 9:45 | 11.6036 | -0.07223
| 9:45 | 11.6039 | -0.072183
| 9:45 | 11.6042 | -0.072136
| 9:45 | 11.6044 | -0.072089
| 9:45 | 11.6047 | -0.072042
| 9:45 | 11.605 | -0.071995
| 9:45 | 11.6053 | -0.071948
| 9:45 | 11.6056 | -0.071902
| 9:45 | 11.6058 | -0.071855
| 9:45 | 11.6061 | -0.071808
| 9:45 | 11.6064 | -0.071761
| 9:45 | 11.6067 | -0.071714
| 9:45 | 11.6069 | -0.071667
| 9:45 | 11.6072 | -0.071619
| 9:45 | 11.6075 | -0.071571
| 9:45 | 11.6078 | -0.071523
| 9:45 | 11.6081 | -0.071475
| 9:45 | 11.6083 | -0.071426
| 9:45 | 11.6086 | -0.071377
| 9:45 | 11.6089 | -0.071329
| 9:45 | 11.6092 | -0.07128
| 9:45 | 11.6094 | -0.071231
| 9:45 | 11.6097 | -0.071183
| 9:45 | 11.61 | -0.071134
| 9:45 | 11.6103 | -0.071085
| 9:45 | 11.6106 | -0.071037
| 9:45 | 11.6108 | -0.070988
| 9:45 | 11.6111 | -0.07094
| 9:45 | 11.6114 | -0.070891
| 9:46 | 11.6117 | -0.070843
| 9:46 | 11.6119 | -0.070794
| 9:46 | 11.6122 | -0.070746
| 9:46 | 11.6125 | -0.070698
| 9:46 | 11.6128 | -0.070649
| 9:46 | 11.6131 | -0.070601
| 9:46 | 11.6133 | -0.070553
| 9:46 | 11.6136 | -0.070505
| 9:46 | 11.6139 | -0.070456
| 9:46 | 11.6142 | -0.070408
| 9:46 | 11.6144 | -0.07036
| 9:46 | 11.6147 | -0.070309
| 9:46 | 11.615 | -0.070258
| 9:46 | 11.6153 | -0.070207
| 9:46 | 11.6156 | -0.070156
| 9:46 | 11.6158 | -0.070104
| 9:46 | 11.6161 | -0.070052
| 9:46 | 11.6164 | -0.07
| 9:46 | 11.6167 | -0.069947
| 9:46 | 11.6169 | -0.069895
| 9:46 | 11.6172 | -0.069843
| 9:46 | 11.6175 | -0.06979
| 9:46 | 11.6178 | -0.069738
| 9:46 | 11.6181 | -0.069686
| 9:46 | 11.6183 | -0.069634
| 9:46 | 11.6186 | -0.069581
| 9:46 | 11.6189 | -0.069529
| 9:46 | 11.6192 | -0.069477
| 9:46 | 11.6194 | -0.069424
| 9:46 | 11.6197 | -0.069372
| 9:46 | 11.62 | -0.06932
| 9:46 | 11.6203 | -0.069267
| 9:46 | 11.6206 | -0.069215
| 9:46 | 11.6208 | -0.069163
| 9:46 | 11.6211 | -0.06911
| 9:46 | 11.6214 | -0.069056
| 9:46 | 11.6217 | -0.069001
| 9:46 | 11.6219 | -0.068947
| 9:46 | 11.6222 | -0.068892
| 9:46 | 11.6225 | -0.068837
| 9:46 | 11.6228 | -0.068783
| 9:46 | 11.6231 | -0.068728
| 9:46 | 11.6233 | -0.068673
| 9:46 | 11.6236 | -0.068617
| 9:46 | 11.6239 | -0.068562
| 9:46 | 11.6242 | -0.068506
| 9:46 | 11.6244 | -0.06845
| 9:46 | 11.6247 | -0.068393
| 9:46 | 11.625 | -0.068336
| 9:46 | 11.6253 | -0.068279
| 9:46 | 11.6256 | -0.068222
| 9:46 | 11.6258 | -0.068165
| 9:46 | 11.6261 | -0.068108
| 9:46 | 11.6264 | -0.068051
| 9:46 | 11.6267 | -0.067994
| 9:46 | 11.6269 | -0.067937
| 9:46 | 11.6272 | -0.06788
| 9:46 | 11.6275 | -0.067823
| 9:46 | 11.6278 | -0.067766
| 9:46 | 11.6281 | -0.067707
| 9:46 | 11.6283 | -0.067648
| 9:47 | 11.6286 | -0.067588
| 9:47 | 11.6289 | -0.067529
| 9:47 | 11.6292 | -0.06747
| 9:47 | 11.6294 | -0.06741
| 9:47 | 11.6297 | -0.067351
| 9:47 | 11.63 | -0.067292
| 9:47 | 11.6303 | -0.067232
| 9:47 | 11.6306 | -0.067173
| 9:47 | 11.6308 | -0.067114
| 9:47 | 11.6311 | -0.067054
| 9:47 | 11.6314 | -0.066994
| 9:47 | 11.6317 | -0.066934
| 9:47 | 11.6319 | -0.066874
| 9:47 | 11.6322 | -0.066814
| 9:47 | 11.6325 | -0.066753
| 9:47 | 11.6328 | -0.066692
| 9:47 | 11.6331 | -0.066631
| 9:47 | 11.6333 | -0.066569
| 9:47 | 11.6336 | -0.066507
| 9:47 | 11.6339 | -0.066446
| 9:47 | 11.6342 | -0.066384
| 9:47 | 11.6344 | -0.066322
| 9:47 | 11.6347 | -0.06626
| 9:47 | 11.635 | -0.066199
| 9:47 | 11.6353 | -0.066137
| 9:47 | 11.6356 | -0.066075
| 9:47 | 11.6358 | -0.066013
| 9:47 | 11.6361 | -0.065951
| 9:47 | 11.6364 | -0.065887
| 9:47 | 11.6367 | -0.065823
| 9:47 | 11.6369 | -0.065759
| 9:47 | 11.6372 | -0.065695
| 9:47 | 11.6375 | -0.065631
| 9:47 | 11.6378 | -0.065567
| 9:47 | 11.6381 | -0.065503
| 9:47 | 11.6383 | -0.065439
| 9:47 | 11.6386 | -0.065375
| 9:47 | 11.6389 | -0.065311
| 9:47 | 11.6392 | -0.065247
| 9:47 | 11.6394 | -0.065183
| 9:47 | 11.6397 | -0.065118
| 9:47 | 11.64 | -0.065053
| 9:47 | 11.6403 | -0.064988
| 9:47 | 11.6406 | -0.064923
| 9:47 | 11.6408 | -0.064857
| 9:47 | 11.6411 | -0.064792
| 9:47 | 11.6414 | -0.064725
| 9:47 | 11.6417 | -0.064659
| 9:47 | 11.6419 | -0.064593
| 9:47 | 11.6422 | -0.064527
| 9:47 | 11.6425 | -0.06446
| 9:47 | 11.6428 | -0.064394
| 9:47 | 11.6431 | -0.064328
| 9:47 | 11.6433 | -0.064262
| 9:47 | 11.6436 | -0.064195
| 9:47 | 11.6439 | -0.064129
| 9:47 | 11.6442 | -0.064063
| 9:47 | 11.6444 | -0.063997
| 9:47 | 11.6447 | -0.06393
| 9:48 | 11.645 | -0.063861
| 9:48 | 11.6453 | -0.063793
| 9:48 | 11.6456 | -0.063726
| 9:48 | 11.6458 | -0.063658
| 9:48 | 11.6461 | -0.063589
| 9:48 | 11.6464 | -0.063521
| 9:48 | 11.6467 | -0.063452
| 9:48 | 11.6469 | -0.063384
| 9:48 | 11.6472 | -0.063316
| 9:48 | 11.6475 | -0.063247
| 9:48 | 11.6478 | -0.063179
| 9:48 | 11.6481 | -0.063111
| 9:48 | 11.6483 | -0.063042
| 9:48 | 11.6486 | -0.062974
| 9:48 | 11.6489 | -0.062906
| 9:48 | 11.6492 | -0.062838
| 9:48 | 11.6494 | -0.062769
| 9:48 | 11.6497 | -0.062701
| 9:48 | 11.65 | -0.062633
| 9:48 | 11.6503 | -0.062565
| 9:48 | 11.6506 | -0.062497
| 9:48 | 11.6508 | -0.062429
| 9:48 | 11.6511 | -0.062361
| 9:48 | 11.6514 | -0.062292
| 9:48 | 11.6517 | -0.062222
| 9:48 | 11.6519 | -0.062151
| 9:48 | 11.6522 | -0.062083
| 9:48 | 11.6525 | -0.062012
| 9:48 | 11.6528 | -0.061942
| 9:48 | 11.6531 | -0.061872
| 9:48 | 11.6533 | -0.061802
| 9:48 | 11.6536 | -0.061732
| 9:48 | 11.6539 | -0.061662
| 9:48 | 11.6542 | -0.061591
| 9:48 | 11.6544 | -0.061521
| 9:48 | 11.6547 | -0.061451
| 9:48 | 11.655 | -0.061381
| 9:48 | 11.6553 | -0.061311
| 9:48 | 11.6556 | -0.061241
| 9:48 | 11.6558 | -0.061171
| 9:48 | 11.6561 | -0.061101
| 9:48 | 11.6564 | -0.061031
| 9:48 | 11.6567 | -0.060961
| 9:48 | 11.6569 | -0.060891
| 9:48 | 11.6572 | -0.06082
| 9:48 | 11.6575 | -0.060749
| 9:48 | 11.6578 | -0.060677
| 9:48 | 11.6581 | -0.060606
| 9:48 | 11.6583 | -0.060534
| 9:48 | 11.6586 | -0.060462
| 9:48 | 11.6589 | -0.06039
| 9:48 | 11.6592 | -0.060318
| 9:48 | 11.6594 | -0.060246
| 9:48 | 11.6597 | -0.060177
| 9:48 | 11.66 | -0.060107
| 9:48 | 11.6603 | -0.060037
| 9:48 | 11.6606 | -0.059965
| 9:48 | 11.6608 | -0.059893
| 9:48 | 11.6611 | -0.059819
| 9:48 | 11.6614 | -0.059745
| 9:48 | 11.6617 | -0.059671
| 9:49 | 11.6619 | -0.059597
| 9:49 | 11.6622 | -0.059523
| 9:49 | 11.6625 | -0.059449
| 9:49 | 11.6628 | -0.059375
| 9:49 | 11.6631 | -0.059301
| 9:49 | 11.6633 | -0.059227
| 9:49 | 11.6636 | -0.059153
| 9:49 | 11.6639 | -0.059079
| 9:49 | 11.6642 | -0.059005
| 9:49 | 11.6644 | -0.058931
| 9:49 | 11.6647 | -0.058857
| 9:49 | 11.665 | -0.058783
| 9:49 | 11.6653 | -0.058709
| 9:49 | 11.6656 | -0.058635
| 9:49 | 11.6658 | -0.058561
| 9:49 | 11.6661 | -0.058487
| 9:49 | 11.6664 | -0.058413
| 9:49 | 11.6667 | -0.058338
| 9:49 | 11.6669 | -0.058264
| 9:49 | 11.6672 | -0.05819
| 9:49 | 11.6675 | -0.058116
| 9:49 | 11.6678 | -0.058042
| 9:49 | 11.6681 | -0.057967
| 9:49 | 11.6683 | -0.057893
| 9:49 | 11.6686 | -0.057819
| 9:49 | 11.6689 | -0.057744
| 9:49 | 11.6692 | -0.05767
| 9:49 | 11.6694 | -0.057596
| 9:49 | 11.6697 | -0.057521
| 9:49 | 11.67 | -0.057447
| 9:49 | 11.6703 | -0.057373
| 9:49 | 11.6706 | -0.057298
| 9:49 | 11.6708 | -0.057224
| 9:49 | 11.6711 | -0.05715
| 9:49 | 11.6714 | -0.057075
| 9:49 | 11.6717 | -0.057001
| 9:49 | 11.6719 | -0.056926
| 9:49 | 11.6722 | -0.056852
| 9:49 | 11.6725 | -0.056778
| 9:49 | 11.6728 | -0.056703
| 9:49 | 11.6731 | -0.056629
| 9:49 | 11.6733 | -0.056555
| 9:49 | 11.6736 | -0.05648
| 9:49 | 11.6739 | -0.056406
| 9:49 | 11.6742 | -0.056332
| 9:49 | 11.6744 | -0.056258
| 9:49 | 11.6747 | -0.056184
| 9:49 | 11.675 | -0.056109
| 9:49 | 11.6753 | -0.056035
| 9:49 | 11.6756 | -0.055961
| 9:49 | 11.6758 | -0.055887
| 9:49 | 11.6761 | -0.055813
| 9:49 | 11.6764 | -0.055738
| 9:49 | 11.6767 | -0.055664
| 9:49 | 11.6769 | -0.05559
| 9:49 | 11.6772 | -0.055516
| 9:49 | 11.6775 | -0.055442
| 9:49 | 11.6778 | -0.055368
| 9:49 | 11.6781 | -0.055294
| 9:50 | 11.6783 | -0.05522
| 9:50 | 11.6786 | -0.055146
| 9:50 | 11.6789 | -0.055072
| 9:50 | 11.6792 | -0.054998
| 9:50 | 11.6794 | -0.054924
| 9:50 | 11.6797 | -0.054851
| 9:50 | 11.68 | -0.054777
| 9:50 | 11.6803 | -0.054703
| 9:50 | 11.6806 | -0.054629
| 9:50 | 11.6808 | -0.054556
| 9:50 | 11.6811 | -0.054482
| 9:50 | 11.6814 | -0.054408
| 9:50 | 11.6817 | -0.054335
| 9:50 | 11.6819 | -0.054261
| 9:50 | 11.6822 | -0.054187
| 9:50 | 11.6825 | -0.054114
| 9:50 | 11.6828 | -0.05404
| 9:50 | 11.6831 | -0.053967
| 9:50 | 11.6833 | -0.053893
| 9:50 | 11.6836 | -0.05382
| 9:50 | 11.6839 | -0.053747
| 9:50 | 11.6842 | -0.053673
| 9:50 | 11.6844 | -0.053598
| 9:50 | 11.6847 | -0.053523
| 9:50 | 11.685 | -0.053447
| 9:50 | 11.6853 | -0.053372
| 9:50 | 11.6856 | -0.053296
| 9:50 | 11.6858 | -0.053221
| 9:50 | 11.6861 | -0.053146
| 9:50 | 11.6864 | -0.053071
| 9:50 | 11.6867 | -0.052997
| 9:50 | 11.6869 | -0.052924
| 9:50 | 11.6872 | -0.052849
| 9:50 | 11.6875 | -0.052774
| 9:50 | 11.6878 | -0.052699
| 9:50 | 11.6881 | -0.052624
| 9:50 | 11.6883 | -0.052547
| 9:50 | 11.6886 | -0.05247
| 9:50 | 11.6889 | -0.052395
| 9:50 | 11.6892 | -0.052321
| 9:50 | 11.6894 | -0.052246
| 9:50 | 11.6897 | -0.052171
| 9:50 | 11.69 | -0.052095
| 9:50 | 11.6903 | -0.05202
| 9:50 | 11.6906 | -0.051944
| 9:50 | 11.6908 | -0.051868
| 9:50 | 11.6911 | -0.051791
| 9:50 | 11.6914 | -0.051715
| 9:50 | 11.6917 | -0.051638
| 9:50 | 11.6919 | -0.051561
| 9:50 | 11.6922 | -0.051487
| 9:50 | 11.6925 | -0.051413
| 9:50 | 11.6928 | -0.051338
| 9:50 | 11.6931 | -0.051264
| 9:50 | 11.6933 | -0.05119
| 9:50 | 11.6936 | -0.051115
| 9:50 | 11.6939 | -0.051041
| 9:50 | 11.6942 | -0.050967
| 9:50 | 11.6944 | -0.050893
| 9:50 | 11.6947 | -0.050817
| 9:50 | 11.695 | -0.05074
| 9:51 | 11.6953 | -0.050664
| 9:51 | 11.6956 | -0.050589
| 9:51 | 11.6958 | -0.050515
| 9:51 | 11.6961 | -0.050441
| 9:51 | 11.6964 | -0.050367
| 9:51 | 11.6967 | -0.050294
| 9:51 | 11.6969 | -0.05022
| 9:51 | 11.6972 | -0.050146
| 9:51 | 11.6975 | -0.050072
| 9:51 | 11.6978 | -0.049999
| 9:51 | 11.6981 | -0.049925
| 9:51 | 11.6983 | -0.049852
| 9:51 | 11.6986 | -0.049778
| 9:51 | 11.6989 | -0.049705
| 9:51 | 11.6992 | -0.049631
| 9:51 | 11.6994 | -0.049558
| 9:51 | 11.6997 | -0.049484
| 9:51 | 11.7 | -0.049411
| 9:51 | 11.7003 | -0.049338
| 9:51 | 11.7006 | -0.049264
| 9:51 | 11.7008 | -0.049191
| 9:51 | 11.7011 | -0.049118
| 9:51 | 11.7014 | -0.049045
| 9:51 | 11.7017 | -0.048972
| 9:51 | 11.7019 | -0.048899
| 9:51 | 11.7022 | -0.048826
| 9:51 | 11.7025 | -0.048753
| 9:51 | 11.7028 | -0.04868
| 9:51 | 11.7031 | -0.048607
| 9:51 | 11.7033 | -0.048534
| 9:51 | 11.7036 | -0.048461
| 9:51 | 11.7039 | -0.048388
| 9:51 | 11.7042 | -0.048315
| 9:51 | 11.7044 | -0.04824
| 9:51 | 11.7047 | -0.048165
| 9:51 | 11.705 | -0.04809
| 9:51 | 11.7053 | -0.048015
| 9:51 | 11.7056 | -0.04794
| 9:51 | 11.7058 | -0.047866
| 9:51 | 11.7061 | -0.047791
| 9:51 | 11.7064 | -0.047716
| 9:51 | 11.7067 | -0.047642
| 9:51 | 11.7069 | -0.047567
| 9:51 | 11.7072 | -0.047492
| 9:51 | 11.7075 | -0.047418
| 9:51 | 11.7078 | -0.047343
| 9:51 | 11.7081 | -0.047269
| 9:51 | 11.7083 | -0.047194
| 9:51 | 11.7086 | -0.04712
| 9:51 | 11.7089 | -0.047046
| 9:51 | 11.7092 | -0.046971
| 9:51 | 11.7094 | -0.046897
| 9:51 | 11.7097 | -0.046823
| 9:51 | 11.71 | -0.046749
| 9:51 | 11.7103 | -0.046675
| 9:51 | 11.7106 | -0.046601
| 9:51 | 11.7108 | -0.046526
| 9:51 | 11.7111 | -0.046452
| 9:51 | 11.7114 | -0.046378
| 9:52 | 11.7117 | -0.046304
| 9:52 | 11.7119 | -0.046231
| 9:52 | 11.7122 | -0.046157
| 9:52 | 11.7125 | -0.046083
| 9:52 | 11.7128 | -0.046009
| 9:52 | 11.7131 | -0.045935
| 9:52 | 11.7133 | -0.045861
| 9:52 | 11.7136 | -0.045788
| 9:52 | 11.7139 | -0.045714
| 9:52 | 11.7142 | -0.04564
| 9:52 | 11.7144 | -0.045567
| 9:52 | 11.7147 | -0.045493
| 9:52 | 11.715 | -0.04542
| 9:52 | 11.7153 | -0.045346
| 9:52 | 11.7156 | -0.045272
| 9:52 | 11.7158 | -0.045197
| 9:52 | 11.7161 | -0.045123
| 9:52 | 11.7164 | -0.045048
| 9:52 | 11.7167 | -0.044973
| 9:52 | 11.7169 | -0.044898
| 9:52 | 11.7172 | -0.044822
| 9:52 | 11.7175 | -0.044747
| 9:52 | 11.7178 | -0.044672
| 9:52 | 11.7181 | -0.044596
| 9:52 | 11.7183 | -0.044521
| 9:52 | 11.7186 | -0.044446
| 9:52 | 11.7189 | -0.04437
| 9:52 | 11.7192 | -0.044295
| 9:52 | 11.7194 | -0.04422
| 9:52 | 11.7197 | -0.044145
| 9:52 | 11.72 | -0.04407
| 9:52 | 11.7203 | -0.043995
| 9:52 | 11.7206 | -0.04392
| 9:52 | 11.7208 | -0.043845
| 9:52 | 11.7211 | -0.04377
| 9:52 | 11.7214 | -0.043695
| 9:52 | 11.7217 | -0.04362
| 9:52 | 11.7219 | -0.043545
| 9:52 | 11.7222 | -0.043472
| 9:52 | 11.7225 | -0.0434
| 9:52 | 11.7228 | -0.043327
| 9:52 | 11.7231 | -0.043255
| 9:52 | 11.7233 | -0.043182
| 9:52 | 11.7236 | -0.04311
| 9:52 | 11.7239 | -0.043037
| 9:52 | 11.7242 | -0.042965
| 9:52 | 11.7244 | -0.042892
| 9:52 | 11.7247 | -0.04282
| 9:52 | 11.725 | -0.042748
| 9:52 | 11.7253 | -0.042675
| 9:52 | 11.7256 | -0.042603
| 9:52 | 11.7258 | -0.042531
| 9:52 | 11.7261 | -0.042459
| 9:52 | 11.7264 | -0.042386
| 9:52 | 11.7267 | -0.042314
| 9:52 | 11.7269 | -0.042242
| 9:52 | 11.7272 | -0.04217
| 9:52 | 11.7275 | -0.042098
| 9:52 | 11.7278 | -0.042026
| 9:52 | 11.7281 | -0.041954
| 9:52 | 11.7283 | -0.041882
| 9:53 | 11.7286 | -0.04181
| 9:53 | 11.7289 | -0.041738
| 9:53 | 11.7292 | -0.041666
| 9:53 | 11.7294 | -0.041594
| 9:53 | 11.7297 | -0.041523
| 9:53 | 11.73 | -0.041451
| 9:53 | 11.7303 | -0.041379
| 9:53 | 11.7306 | -0.041307
| 9:53 | 11.7308 | -0.041235
| 9:53 | 11.7311 | -0.041164
| 9:53 | 11.7314 | -0.041092
| 9:53 | 11.7317 | -0.04102
| 9:53 | 11.7319 | -0.040949
| 9:53 | 11.7322 | -0.040877
| 9:53 | 11.7325 | -0.040806
| 9:53 | 11.7328 | -0.040734
| 9:53 | 11.7331 | -0.040663
| 9:53 | 11.7333 | -0.040591
| 9:53 | 11.7336 | -0.04052
| 9:53 | 11.7339 | -0.040448
| 9:53 | 11.7342 | -0.040375
| 9:53 | 11.7344 | -0.040301
| 9:53 | 11.7347 | -0.040228
| 9:53 | 11.735 | -0.040154
| 9:53 | 11.7353 | -0.04008
| 9:53 | 11.7356 | -0.040007
| 9:53 | 11.7358 | -0.039934
| 9:53 | 11.7361 | -0.03986
| 9:53 | 11.7364 | -0.039787
| 9:53 | 11.7367 | -0.039713
| 9:53 | 11.7369 | -0.03964
| 9:53 | 11.7372 | -0.039567
| 9:53 | 11.7375 | -0.039493
| 9:53 | 11.7378 | -0.03942
| 9:53 | 11.7381 | -0.039347
| 9:53 | 11.7383 | -0.039273
| 9:53 | 11.7386 | -0.0392
| 9:53 | 11.7389 | -0.039127
| 9:53 | 11.7392 | -0.039054
| 9:53 | 11.7394 | -0.03898
| 9:53 | 11.7397 | -0.038907
| 9:53 | 11.74 | -0.038834
| 9:53 | 11.7403 | -0.038761
| 9:53 | 11.7406 | -0.038688
| 9:53 | 11.7408 | -0.038614
| 9:53 | 11.7411 | -0.038541
| 9:53 | 11.7414 | -0.038468
| 9:53 | 11.7417 | -0.038395
| 9:53 | 11.7419 | -0.038322
| 9:53 | 11.7422 | -0.038249
| 9:53 | 11.7425 | -0.038176
| 9:53 | 11.7428 | -0.038103
| 9:53 | 11.7431 | -0.03803
| 9:53 | 11.7433 | -0.037957
| 9:53 | 11.7436 | -0.037884
| 9:53 | 11.7439 | -0.037811
| 9:53 | 11.7442 | -0.037738
| 9:53 | 11.7444 | -0.037665
| 9:53 | 11.7447 | -0.037592
| 9:54 | 11.745 | -0.037519
| 9:54 | 11.7453 | -0.037446
| 9:54 | 11.7456 | -0.037375
| 9:54 | 11.7458 | -0.037304
| 9:54 | 11.7461 | -0.037234
| 9:54 | 11.7464 | -0.037161
| 9:54 | 11.7467 | -0.037089
| 9:54 | 11.7469 | -0.037016
| 9:54 | 11.7472 | -0.036945
| 9:54 | 11.7475 | -0.036874
| 9:54 | 11.7478 | -0.036804
| 9:54 | 11.7481 | -0.036733
| 9:54 | 11.7483 | -0.036662
| 9:54 | 11.7486 | -0.03659
| 9:54 | 11.7489 | -0.036519
| 9:54 | 11.7492 | -0.036447
| 9:54 | 11.7494 | -0.036375
| 9:54 | 11.7497 | -0.036302
| 9:54 | 11.75 | -0.03623
| 9:54 | 11.7503 | -0.036157
| 9:54 | 11.7506 | -0.036086
| 9:54 | 11.7508 | -0.036016
| 9:54 | 11.7511 | -0.035946
| 9:54 | 11.7514 | -0.035875
| 9:54 | 11.7517 | -0.035805
| 9:54 | 11.7519 | -0.035735
| 9:54 | 11.7522 | -0.035664
| 9:54 | 11.7525 | -0.035594
| 9:54 | 11.7528 | -0.035524
| 9:54 | 11.7531 | -0.035453
| 9:54 | 11.7533 | -0.035383
| 9:54 | 11.7536 | -0.035313
| 9:54 | 11.7539 | -0.035243
| 9:54 | 11.7542 | -0.035172
| 9:54 | 11.7544 | -0.035102
| 9:54 | 11.7547 | -0.035032
| 9:54 | 11.755 | -0.034961
| 9:54 | 11.7553 | -0.034891
| 9:54 | 11.7556 | -0.034821
| 9:54 | 11.7558 | -0.034751
| 9:54 | 11.7561 | -0.03468
| 9:54 | 11.7564 | -0.03461
| 9:54 | 11.7567 | -0.03454
| 9:54 | 11.7569 | -0.034471
| 9:54 | 11.7572 | -0.034402
| 9:54 | 11.7575 | -0.034333
| 9:54 | 11.7578 | -0.034264
| 9:54 | 11.7581 | -0.034196
| 9:54 | 11.7583 | -0.034126
| 9:54 | 11.7586 | -0.034056
| 9:54 | 11.7589 | -0.033986
| 9:54 | 11.7592 | -0.033918
| 9:54 | 11.7594 | -0.03385
| 9:54 | 11.7597 | -0.033783
| 9:54 | 11.76 | -0.033714
| 9:54 | 11.7603 | -0.033644
| 9:54 | 11.7606 | -0.033574
| 9:54 | 11.7608 | -0.033504
| 9:54 | 11.7611 | -0.033434
| 9:54 | 11.7614 | -0.033364
| 9:54 | 11.7617 | -0.033294
| 9:55 | 11.7619 | -0.033224
| 9:55 | 11.7622 | -0.033154
| 9:55 | 11.7625 | -0.033084
| 9:55 | 11.7628 | -0.033014
| 9:55 | 11.7631 | -0.032944
| 9:55 | 11.7633 | -0.032874
| 9:55 | 11.7636 | -0.032804
| 9:55 | 11.7639 | -0.032734
| 9:55 | 11.7642 | -0.032664
| 9:55 | 11.7644 | -0.032594
| 9:55 | 11.7647 | -0.032524
| 9:55 | 11.765 | -0.032455
| 9:55 | 11.7653 | -0.032386
| 9:55 | 11.7656 | -0.032317
| 9:55 | 11.7658 | -0.032248
| 9:55 | 11.7661 | -0.03218
| 9:55 | 11.7664 | -0.032111
| 9:55 | 11.7667 | -0.032043
| 9:55 | 11.7669 | -0.031976
| 9:55 | 11.7672 | -0.031908
| 9:55 | 11.7675 | -0.031841
| 9:55 | 11.7678 | -0.031773
| 9:55 | 11.7681 | -0.031706
| 9:55 | 11.7683 | -0.031638
| 9:55 | 11.7686 | -0.031571
| 9:55 | 11.7689 | -0.031503
| 9:55 | 11.7692 | -0.031435
| 9:55 | 11.7694 | -0.031368
| 9:55 | 11.7697 | -0.0313
| 9:55 | 11.77 | -0.031233
| 9:55 | 11.7703 | -0.031165
| 9:55 | 11.7706 | -0.031098
| 9:55 | 11.7708 | -0.03103
| 9:55 | 11.7711 | -0.030963
| 9:55 | 11.7714 | -0.030895
| 9:55 | 11.7717 | -0.030828
| 9:55 | 11.7719 | -0.03076
| 9:55 | 11.7722 | -0.030692
| 9:55 | 11.7725 | -0.030625
| 9:55 | 11.7728 | -0.030557
| 9:55 | 11.7731 | -0.030489
| 9:55 | 11.7733 | -0.030421
| 9:55 | 11.7736 | -0.030353
| 9:55 | 11.7739 | -0.030284
| 9:55 | 11.7742 | -0.030215
| 9:55 | 11.7744 | -0.030146
| 9:55 | 11.7747 | -0.030076
| 9:55 | 11.775 | -0.030006
| 9:55 | 11.7753 | -0.029938
| 9:55 | 11.7756 | -0.02987
| 9:55 | 11.7758 | -0.029803
| 9:55 | 11.7761 | -0.029735
| 9:55 | 11.7764 | -0.029669
| 9:55 | 11.7767 | -0.029603
| 9:55 | 11.7769 | -0.029538
| 9:55 | 11.7772 | -0.029473
| 9:55 | 11.7775 | -0.029406
| 9:55 | 11.7778 | -0.029339
| 9:55 | 11.7781 | -0.029274
| 9:56 | 11.7783 | -0.029209
| 9:56 | 11.7786 | -0.029144
| 9:56 | 11.7789 | -0.029078
| 9:56 | 11.7792 | -0.029013
| 9:56 | 11.7794 | -0.028948
| 9:56 | 11.7797 | -0.028883
| 9:56 | 11.78 | -0.028818
| 9:56 | 11.7803 | -0.028753
| 9:56 | 11.7806 | -0.028688
| 9:56 | 11.7808 | -0.028622
| 9:56 | 11.7811 | -0.028557
| 9:56 | 11.7814 | -0.028492
| 9:56 | 11.7817 | -0.028426
| 9:56 | 11.7819 | -0.02836
| 9:56 | 11.7822 | -0.028294
| 9:56 | 11.7825 | -0.028228
| 9:56 | 11.7828 | -0.028161
| 9:56 | 11.7831 | -0.028094
| 9:56 | 11.7833 | -0.028027
| 9:56 | 11.7836 | -0.02796
| 9:56 | 11.7839 | -0.027894
| 9:56 | 11.7842 | -0.027828
| 9:56 | 11.7844 | -0.027761
| 9:56 | 11.7847 | -0.027694
| 9:56 | 11.785 | -0.027626
| 9:56 | 11.7853 | -0.027559
| 9:56 | 11.7856 | -0.027492
| 9:56 | 11.7858 | -0.027424
| 9:56 | 11.7861 | -0.027357
| 9:56 | 11.7864 | -0.02729
| 9:56 | 11.7867 | -0.027222
| 9:56 | 11.7869 | -0.027155
| 9:56 | 11.7872 | -0.027087
| 9:56 | 11.7875 | -0.02702
| 9:56 | 11.7878 | -0.026952
| 9:56 | 11.7881 | -0.026885
| 9:56 | 11.7883 | -0.026817
| 9:56 | 11.7886 | -0.026749
| 9:56 | 11.7889 | -0.026682
| 9:56 | 11.7892 | -0.026614
| 9:56 | 11.7894 | -0.026546
| 9:56 | 11.7897 | -0.026479
| 9:56 | 11.79 | -0.026411
| 9:56 | 11.7903 | -0.026344
| 9:56 | 11.7906 | -0.026277
| 9:56 | 11.7908 | -0.02621
| 9:56 | 11.7911 | -0.026144
| 9:56 | 11.7914 | -0.026078
| 9:56 | 11.7917 | -0.026012
| 9:56 | 11.7919 | -0.025946
| 9:56 | 11.7922 | -0.02588
| 9:56 | 11.7925 | -0.025814
| 9:56 | 11.7928 | -0.025748
| 9:56 | 11.7931 | -0.025683
| 9:56 | 11.7933 | -0.025617
| 9:56 | 11.7936 | -0.025551
| 9:56 | 11.7939 | -0.025485
| 9:56 | 11.7942 | -0.025419
| 9:56 | 11.7944 | -0.025353
| 9:56 | 11.7947 | -0.025287
| 9:56 | 11.795 | -0.025221
| 9:57 | 11.7953 | -0.025155
| 9:57 | 11.7956 | -0.025089
| 9:57 | 11.7958 | -0.025023
| 9:57 | 11.7961 | -0.024957
| 9:57 | 11.7964 | -0.02489
| 9:57 | 11.7967 | -0.024824
| 9:57 | 11.7969 | -0.024758
| 9:57 | 11.7972 | -0.024692
| 9:57 | 11.7975 | -0.024626
| 9:57 | 11.7978 | -0.024559
| 9:57 | 11.7981 | -0.024493
| 9:57 | 11.7983 | -0.024427
| 9:57 | 11.7986 | -0.02436
| 9:57 | 11.7989 | -0.024294
| 9:57 | 11.7992 | -0.024228
| 9:57 | 11.7994 | -0.024161
| 9:57 | 11.7997 | -0.024095
| 9:57 | 11.8 | -0.024028
| 9:57 | 11.8003 | -0.023962
| 9:57 | 11.8006 | -0.023895
| 9:57 | 11.8008 | -0.023829
| 9:57 | 11.8011 | -0.023762
| 9:57 | 11.8014 | -0.023697
| 9:57 | 11.8017 | -0.023632
| 9:57 | 11.8019 | -0.023568
| 9:57 | 11.8022 | -0.023506
| 9:57 | 11.8025 | -0.023444
| 9:57 | 11.8028 | -0.023381
| 9:57 | 11.8031 | -0.023319
| 9:57 | 11.8033 | -0.023257
| 9:57 | 11.8036 | -0.023195
| 9:57 | 11.8039 | -0.023132
| 9:57 | 11.8042 | -0.02307
| 9:57 | 11.8044 | -0.023008
| 9:57 | 11.8047 | -0.022945
| 9:57 | 11.805 | -0.022883
| 9:57 | 11.8053 | -0.02282
| 9:57 | 11.8056 | -0.022758
| 9:57 | 11.8058 | -0.022695
| 9:57 | 11.8061 | -0.022633
| 9:57 | 11.8064 | -0.02257
| 9:57 | 11.8067 | -0.022508
| 9:57 | 11.8069 | -0.022445
| 9:57 | 11.8072 | -0.022383
| 9:57 | 11.8075 | -0.02232
| 9:57 | 11.8078 | -0.022257
| 9:57 | 11.8081 | -0.022195
| 9:57 | 11.8083 | -0.022132
| 9:57 | 11.8086 | -0.022069
| 9:57 | 11.8089 | -0.022009
| 9:57 | 11.8092 | -0.021948
| 9:57 | 11.8094 | -0.021888
| 9:57 | 11.8097 | -0.021827
| 9:57 | 11.81 | -0.021766
| 9:57 | 11.8103 | -0.021706
| 9:57 | 11.8106 | -0.021645
| 9:57 | 11.8108 | -0.021584
| 9:57 | 11.8111 | -0.021524
| 9:57 | 11.8114 | -0.021463
| 9:58 | 11.8117 | -0.021402
| 9:58 | 11.8119 | -0.021341
| 9:58 | 11.8122 | -0.021281
| 9:58 | 11.8125 | -0.02122
| 9:58 | 11.8128 | -0.021159
| 9:58 | 11.8131 | -0.021099
| 9:58 | 11.8133 | -0.021043
| 9:58 | 11.8136 | -0.020986
| 9:58 | 11.8139 | -0.02093
| 9:58 | 11.8142 | -0.020871
| 9:58 | 11.8144 | -0.020813
| 9:58 | 11.8147 | -0.020754
| 9:58 | 11.815 | -0.020696
| 9:58 | 11.8153 | -0.020638
| 9:58 | 11.8156 | -0.020581
| 9:58 | 11.8158 | -0.020524
| 9:58 | 11.8161 | -0.020468
| 9:58 | 11.8164 | -0.020412
| 9:58 | 11.8167 | -0.020356
| 9:58 | 11.8169 | -0.020301
| 9:58 | 11.8172 | -0.020247
| 9:58 | 11.8175 | -0.020192
| 9:58 | 11.8178 | -0.020137
| 9:58 | 11.8181 | -0.02008
| 9:58 | 11.8183 | -0.020024
| 9:58 | 11.8186 | -0.01997
| 9:58 | 11.8189 | -0.019915
| 9:58 | 11.8192 | -0.019861
| 9:58 | 11.8194 | -0.019806
| 9:58 | 11.8197 | -0.019751
| 9:58 | 11.82 | -0.019697
| 9:58 | 11.8203 | -0.019642
| 9:58 | 11.8206 | -0.01959
| 9:58 | 11.8208 | -0.019537
| 9:58 | 11.8211 | -0.019484
| 9:58 | 11.8214 | -0.019432
| 9:58 | 11.8217 | -0.019379
| 9:58 | 11.8219 | -0.019326
| 9:58 | 11.8222 | -0.019274
| 9:58 | 11.8225 | -0.019221
| 9:58 | 11.8228 | -0.019168
| 9:58 | 11.8231 | -0.019115
| 9:58 | 11.8233 | -0.019063
| 9:58 | 11.8236 | -0.019011
| 9:58 | 11.8239 | -0.018958
| 9:58 | 11.8242 | -0.018907
| 9:58 | 11.8244 | -0.018855
| 9:58 | 11.8247 | -0.018804
| 9:58 | 11.825 | -0.018753
| 9:58 | 11.8253 | -0.018702
| 9:58 | 11.8256 | -0.018651
| 9:58 | 11.8258 | -0.0186
| 9:58 | 11.8261 | -0.018549
| 9:58 | 11.8264 | -0.018498
| 9:58 | 11.8267 | -0.018447
| 9:58 | 11.8269 | -0.018396
| 9:58 | 11.8272 | -0.018345
| 9:58 | 11.8275 | -0.018294
| 9:58 | 11.8278 | -0.018243
| 9:58 | 11.8281 | -0.018192
| 9:58 | 11.8283 | -0.018141
| 9:59 | 11.8286 | -0.018089
| 9:59 | 11.8289 | -0.018039
| 9:59 | 11.8292 | -0.01799
| 9:59 | 11.8294 | -0.017941
| 9:59 | 11.8297 | -0.017892
| 9:59 | 11.83 | -0.017843
| 9:59 | 11.8303 | -0.017794
| 9:59 | 11.8306 | -0.017744
| 9:59 | 11.8308 | -0.017695
| 9:59 | 11.8311 | -0.017646
| 9:59 | 11.8314 | -0.017597
| 9:59 | 11.8317 | -0.017547
| 9:59 | 11.8319 | -0.017498
| 9:59 | 11.8322 | -0.017449
| 9:59 | 11.8325 | -0.017399
| 9:59 | 11.8328 | -0.01735
| 9:59 | 11.8331 | -0.0173
| 9:59 | 11.8333 | -0.017251
| 9:59 | 11.8336 | -0.017201
| 9:59 | 11.8339 | -0.017151
| 9:59 | 11.8342 | -0.017104
| 9:59 | 11.8344 | -0.017056
| 9:59 | 11.8347 | -0.017009
| 9:59 | 11.835 | -0.016961
| 9:59 | 11.8353 | -0.016914
| 9:59 | 11.8356 | -0.016866
| 9:59 | 11.8358 | -0.016818
| 9:59 | 11.8361 | -0.016771
| 9:59 | 11.8364 | -0.016723
| 9:59 | 11.8367 | -0.016675
| 9:59 | 11.8369 | -0.016627
| 9:59 | 11.8372 | -0.016579
| 9:59 | 11.8375 | -0.016532
| 9:59 | 11.8378 | -0.016484
| 9:59 | 11.8381 | -0.016436
| 9:59 | 11.8383 | -0.016388
| 9:59 | 11.8386 | -0.01634
| 9:59 | 11.8389 | -0.016294
| 9:59 | 11.8392 | -0.016248
| 9:59 | 11.8394 | -0.016202
| 9:59 | 11.8397 | -0.016156
| 9:59 | 11.84 | -0.01611
| 9:59 | 11.8403 | -0.016064
| 9:59 | 11.8406 | -0.016018
| 9:59 | 11.8408 | -0.015972
| 9:59 | 11.8411 | -0.015926
| 9:59 | 11.8414 | -0.01588
| 9:59 | 11.8417 | -0.015833
| 9:59 | 11.8419 | -0.015787
| 9:59 | 11.8422 | -0.015741
| 9:59 | 11.8425 | -0.015694
| 9:59 | 11.8428 | -0.015648
| 9:59 | 11.8431 | -0.015602
| 9:59 | 11.8433 | -0.015555
| 9:59 | 11.8436 | -0.015509
| 9:59 | 11.8439 | -0.015462
| 9:59 | 11.8442 | -0.015417
| 9:59 | 11.8444 | -0.015372
| 9:59 | 11.8447 | -0.015328
| 10:00 | 11.845 | -0.015283
| 10:00 | 11.8453 | -0.015239
| 10:00 | 11.8456 | -0.015194
| 10:00 | 11.8458 | -0.01515
| 10:00 | 11.8461 | -0.015105
| 10:00 | 11.8464 | -0.01506
| 10:00 | 11.8467 | -0.015016
| 10:00 | 11.8469 | -0.014971
| 10:00 | 11.8472 | -0.014926
| 10:00 | 11.8475 | -0.014881
| 10:00 | 11.8478 | -0.014837
| 10:00 | 11.8481 | -0.014792
| 10:00 | 11.8483 | -0.014747
| 10:00 | 11.8486 | -0.014702
| 10:00 | 11.8489 | -0.014657
| 10:00 | 11.8492 | -0.014612
| 10:00 | 11.8494 | -0.014567
| 10:00 | 11.8497 | -0.014522
| 10:00 | 11.85 | -0.014476
| 10:00 | 11.8503 | -0.014431
| 10:00 | 11.8506 | -0.014386
| 10:00 | 11.8508 | -0.014342
| 10:00 | 11.8511 | -0.014299
| 10:00 | 11.8514 | -0.014256
| 10:00 | 11.8517 | -0.014212
| 10:00 | 11.8519 | -0.014169
| 10:00 | 11.8522 | -0.014126
| 10:00 | 11.8525 | -0.014083
| 10:00 | 11.8528 | -0.01404
| 10:00 | 11.8531 | -0.013999
| 10:00 | 11.8533 | -0.013957

## Freq Reg Duty Cycle test
Frequency Regulation - perform once per year
Test procedure
Initial SOC | 1
Target SOC | 0.6
BESS duration (h) | 10
RTE | 0.8
Duration (h)
1) Bring BESS to the required starting SOC. Note: since 1 power unit is the rated power, which is the 10-h rate, applying a 24-h energy neutral duty cycle is not expected to have a delta SOC of > 5%. To avoid voltage excursion on charge pulses, the starting SOC is set at 60%.
a. Charge or discharge the BESS to 60% SOC. Compare the charge or discharge energy to the required energy to bring to start SOC based on the measured energy capacity from the RPT.
i. during charge, the charge energy = (Measured discharge energy capacity from RPT)*(60% SOC-BES SOC)/(SOCmax-SOCmin)/RTE from RPT test
ii. during discharge, the discharge energy = (Measured discharge energy capacity from RPT)*( BESS SOC -60% SOC)/(SOCmax-SOCmin) | 4
2) Rest for 20min for 10-h duration, 10 min for 24-h duration | 0.33333
3) Apply the frequency regulation signal | 24
4) Bring battery back to initial 60% SOC (assume DOD for duty cycle is 10%) | 1.25
|  | Time | Time (h) | Fraction of Rated Power | SOC
|  |  | 0 | 0 | 1
|  |  | 0.01 | 1 | 1
|  |  | 4 | 1 | 0.6 |  | Time (h) | 24
|  |  | 4.01 | 0 |  |  | Time (s) | 86400
|  |  | 4.3333 | 0 |  |  | delta SOC | 0.05
|  | 0:00 | 4.3433 | -0.14425 | 0.6 |  | Delta SOC/4s | 2.3148e-06
|  | 0:00 | 4.3444 | -0.12965 | 0.6
|  | 0:00 | 4.3456 | -0.13601 | 0.6
|  | 0:00 | 4.3467 | -0.14238 | 0.59999
|  | 0:00 | 4.3478 | -0.14874 | 0.59999
|  | 0:00 | 4.3489 | -0.15511 | 0.59999
|  | 0:00 | 4.35 | -0.16147 | 0.59999
|  | 0:00 | 4.3511 | -0.15001 | 0.59998
|  | 0:01 | 4.3522 | -0.13855 | 0.59998
|  | 0:01 | 4.3533 | -0.11353 | 0.59998
|  | 0:01 | 4.3544 | -0.083978 | 0.59998
|  | 0:01 | 4.3556 | -0.05443 | 0.59997
|  | 0:01 | 4.3567 | -0.032121 | 0.59997
|  | 0:01 | 4.3578 | -0.0098121 | 0.59997
|  | 0:01 | 4.3589 | 0.0050135 | 0.59997
|  | 0:01 | 4.36 | 0.012356 | 0.59997
|  | 0:01 | 4.3611 | 0.019698 | 0.59996
|  | 0:01 | 4.3622 | 0.0056427 | 0.59996
|  | 0:01 | 4.3633 | -0.0084124 | 0.59996
|  | 0:01 | 4.3644 | -0.016135 | 0.59996
|  | 0:01 | 4.3656 | -0.017526 | 0.59995
|  | 0:01 | 4.3667 | -0.018917 | 0.59995 | 0.0011111
|  | 0:01 | 4.3678 | -0.0074832 | 0.59995
|  | 0:02 | 4.3689 | 0.0039504 | 0.59995
|  | 0:02 | 4.37 | 0.016937 | 0.59994
|  | 0:02 | 4.3711 | 0.030441 | 0.59994
|  | 0:02 | 4.3722 | 0.043946 | 0.59994
|  | 0:02 | 4.3733 | 0.065859 | 0.59994
|  | 0:02 | 4.3744 | 0.087772 | 0.59994
|  | 0:02 | 4.3756 | 0.10268 | 0.59993
|  | 0:02 | 4.3767 | 0.11526 | 0.59993
|  | 0:02 | 4.3778 | 0.12783 | 0.59993
|  | 0:02 | 4.3789 | 0.13629 | 0.59993
|  | 0:02 | 4.38 | 0.14474 | 0.59992
|  | 0:02 | 4.3811 | 0.1681 | 0.59992
|  | 0:02 | 4.3822 | 0.20635 | 0.59992
|  | 0:02 | 4.3833 | 0.2446 | 0.59992
|  | 0:02 | 4.3844 | 0.28614 | 0.59991
|  | 0:03 | 4.3856 | 0.32769 | 0.59991
|  | 0:03 | 4.3867 | 0.37177 | 0.59991
|  | 0:03 | 4.3878 | 0.41839 | 0.59991
|  | 0:03 | 4.3889 | 0.4646 | 0.59991
|  | 0:03 | 4.39 | 0.50955 | 0.5999
|  | 0:03 | 4.3911 | 0.55451 | 0.5999
|  | 0:03 | 4.3922 | 0.60292 | 0.5999
|  | 0:03 | 4.3933 | 0.65481 | 0.5999
|  | 0:03 | 4.3944 | 0.70669 | 0.59989
|  | 0:03 | 4.3956 | 0.72091 | 0.59989
|  | 0:03 | 4.3967 | 0.73513 | 0.59989
|  | 0:03 | 4.3978 | 0.73769 | 0.59989
|  | 0:03 | 4.3989 | 0.7286 | 0.59988
|  | 0:03 | 4.4 | 0.71951 | 0.59988
|  | 0:03 | 4.4011 | 0.69733 | 0.59988
|  | 0:04 | 4.4022 | 0.66208 | 0.59988
|  | 0:04 | 4.4033 | 0.6161 | 0.59987
|  | 0:04 | 4.4044 | 0.5594 | 0.59987
|  | 0:04 | 4.4056 | 0.50271 | 0.59987
|  | 0:04 | 4.4067 | 0.43484 | 0.59987
|  | 0:04 | 4.4078 | 0.36696 | 0.59987
|  | 0:04 | 4.4089 | 0.2997 | 0.59986
|  | 0:04 | 4.41 | 0.23306 | 0.59986
|  | 0:04 | 4.4111 | 0.16641 | 0.59986
|  | 0:04 | 4.4122 | 0.1269 | 0.59986
|  | 0:04 | 4.4133 | 0.087393 | 0.59985
|  | 0:04 | 4.4144 | 0.062752 | 0.59985
|  | 0:04 | 4.4156 | 0.052981 | 0.59985
|  | 0:04 | 4.4167 | 0.04321 | 0.59985
|  | 0:04 | 4.4178 | 0.031374 | 0.59984
|  | 0:05 | 4.4189 | 0.019538 | 0.59984
|  | 0:05 | 4.42 | 0.0014623 | 0.59984
|  | 0:05 | 4.4211 | -0.022852 | 0.59984
|  | 0:05 | 4.4222 | -0.047167 | 0.59984
|  | 0:05 | 4.4233 | -0.057435 | 0.59983
|  | 0:05 | 4.4244 | -0.067703 | 0.59983
|  | 0:05 | 4.4256 | -0.080728 | 0.59983
|  | 0:05 | 4.4267 | -0.096511 | 0.59983
|  | 0:05 | 4.4278 | -0.11229 | 0.59982
|  | 0:05 | 4.4289 | -0.14181 | 0.59982
|  | 0:05 | 4.43 | -0.17133 | 0.59982
|  | 0:05 | 4.4311 | -0.19213 | 0.59982
|  | 0:05 | 4.4322 | -0.21003 | 0.59981
|  | 0:05 | 4.4333 | -0.22794 | 0.59981
|  | 0:05 | 4.4344 | -0.25217 | 0.59981
|  | 0:06 | 4.4356 | -0.2764 | 0.59981
|  | 0:06 | 4.4367 | -0.29614 | 0.59981
|  | 0:06 | 4.4378 | -0.31141 | 0.5998
|  | 0:06 | 4.4389 | -0.32668 | 0.5998
|  | 0:06 | 4.44 | -0.33634 | 0.5998
|  | 0:06 | 4.4411 | -0.346 | 0.5998
|  | 0:06 | 4.4422 | -0.35417 | 0.59979
|  | 0:06 | 4.4433 | -0.36184 | 0.59979
|  | 0:06 | 4.4444 | -0.3695 | 0.59979
|  | 0:06 | 4.4456 | -0.38223 | 0.59979
|  | 0:06 | 4.4467 | -0.39495 | 0.59978
|  | 0:06 | 4.4478 | -0.41366 | 0.59978
|  | 0:06 | 4.4489 | -0.43836 | 0.59978
|  | 0:06 | 4.45 | -0.46307 | 0.59978
|  | 0:06 | 4.4511 | -0.49142 | 0.59978
|  | 0:07 | 4.4522 | -0.51976 | 0.59977
|  | 0:07 | 4.4533 | -0.53557 | 0.59977
|  | 0:07 | 4.4544 | -0.53885 | 0.59977
|  | 0:07 | 4.4556 | -0.54212 | 0.59977
|  | 0:07 | 4.4567 | -0.52588 | 0.59976
|  | 0:07 | 4.4578 | -0.50964 | 0.59976
|  | 0:07 | 4.4589 | -0.48512 | 0.59976
|  | 0:07 | 4.46 | -0.45232 | 0.59976
|  | 0:07 | 4.4611 | -0.41952 | 0.59975
|  | 0:07 | 4.4622 | -0.39896 | 0.59975
|  | 0:07 | 4.4633 | -0.3784 | 0.59975
|  | 0:07 | 4.4644 | -0.36069 | 0.59975
|  | 0:07 | 4.4656 | -0.34581 | 0.59975
|  | 0:07 | 4.4667 | -0.33094 | 0.59974
|  | 0:07 | 4.4678 | -0.31151 | 0.59974
|  | 0:08 | 4.4689 | -0.29208 | 0.59974
|  | 0:08 | 4.47 | -0.26401 | 0.59974
|  | 0:08 | 4.4711 | -0.2273 | 0.59973
|  | 0:08 | 4.4722 | -0.1906 | 0.59973
|  | 0:08 | 4.4733 | -0.15165 | 0.59973
|  | 0:08 | 4.4744 | -0.1127 | 0.59973
|  | 0:08 | 4.4756 | -0.070709 | 0.59972
|  | 0:08 | 4.4767 | -0.025681 | 0.59972
|  | 0:08 | 4.4778 | 0.019348 | 0.59972
|  | 0:08 | 4.4789 | 0.066808 | 0.59972
|  | 0:08 | 4.48 | 0.11427 | 0.59972
|  | 0:08 | 4.4811 | 0.14906 | 0.59971
|  | 0:08 | 4.4822 | 0.17962 | 0.59971
|  | 0:08 | 4.4833 | 0.21018 | 0.59971
|  | 0:08 | 4.4844 | 0.22659 | 0.59971
|  | 0:09 | 4.4856 | 0.243 | 0.5997
|  | 0:09 | 4.4867 | 0.26015 | 0.5997
|  | 0:09 | 4.4878 | 0.27804 | 0.5997
|  | 0:09 | 4.4889 | 0.29593 | 0.5997
|  | 0:09 | 4.49 | 0.34579 | 0.59969
|  | 0:09 | 4.4911 | 0.39566 | 0.59969
|  | 0:09 | 4.4922 | 0.41648 | 0.59969
|  | 0:09 | 4.4933 | 0.42761 | 0.59969
|  | 0:09 | 4.4944 | 0.43875 | 0.59969
|  | 0:09 | 4.4956 | 0.48488 | 0.59968
|  | 0:09 | 4.4967 | 0.53101 | 0.59968
|  | 0:09 | 4.4978 | 0.56431 | 0.59968
|  | 0:09 | 4.4989 | 0.58479 | 0.59968
|  | 0:09 | 4.5 | 0.60527 | 0.59967
|  | 0:09 | 4.5011 | 0.62576 | 0.59967
|  | 0:10 | 4.5022 | 0.64624 | 0.59967
|  | 0:10 | 4.5033 | 0.65386 | 0.59967
|  | 0:10 | 4.5044 | 0.64862 | 0.59966
|  | 0:10 | 4.5056 | 0.64337 | 0.59966
|  | 0:10 | 4.5067 | 0.61858 | 0.59966
|  | 0:10 | 4.5078 | 0.59379 | 0.59966
|  | 0:10 | 4.5089 | 0.57945 | 0.59966
|  | 0:10 | 4.51 | 0.5686 | 0.59965
|  | 0:10 | 4.5111 | 0.55774 | 0.59965
|  | 0:10 | 4.5122 | 0.53406 | 0.59965
|  | 0:10 | 4.5133 | 0.51037 | 0.59965
|  | 0:10 | 4.5144 | 0.48484 | 0.59964
|  | 0:10 | 4.5156 | 0.45747 | 0.59964
|  | 0:10 | 4.5167 | 0.43009 | 0.59964
|  | 0:10 | 4.5178 | 0.40661 | 0.59964
|  | 0:11 | 4.5189 | 0.38313 | 0.59963
|  | 0:11 | 4.52 | 0.35578 | 0.59963
|  | 0:11 | 4.5211 | 0.32455 | 0.59963
|  | 0:11 | 4.5222 | 0.29332 | 0.59963
|  | 0:11 | 4.5233 | 0.24981 | 0.59962
|  | 0:11 | 4.5244 | 0.20629 | 0.59962
|  | 0:11 | 4.5256 | 0.16355 | 0.59962
|  | 0:11 | 4.5267 | 0.12106 | 0.59962
|  | 0:11 | 4.5278 | 0.078582 | 0.59962
|  | 0:11 | 4.5289 | 0.031632 | 0.59961
|  | 0:11 | 4.53 | -0.015318 | 0.59961
|  | 0:11 | 4.5311 | -0.035845 | 0.59961
|  | 0:11 | 4.5322 | -0.047565 | 0.59961
|  | 0:11 | 4.5333 | -0.059285 | 0.5996
|  | 0:11 | 4.5344 | -0.081598 | 0.5996
|  | 0:12 | 4.5356 | -0.10391 | 0.5996
|  | 0:12 | 4.5367 | -0.13323 | 0.5996
|  | 0:12 | 4.5378 | -0.16956 | 0.59959
|  | 0:12 | 4.5389 | -0.20588 | 0.59959
|  | 0:12 | 4.54 | -0.24997 | 0.59959
|  | 0:12 | 4.5411 | -0.29406 | 0.59959
|  | 0:12 | 4.5422 | -0.33234 | 0.59959
|  | 0:12 | 4.5433 | -0.3648 | 0.59958
|  | 0:12 | 4.5444 | -0.39726 | 0.59958
|  | 0:12 | 4.5456 | -0.42357 | 0.59958
|  | 0:12 | 4.5467 | -0.44987 | 0.59958
|  | 0:12 | 4.5478 | -0.46847 | 0.59957
|  | 0:12 | 4.5489 | -0.47935 | 0.59957
|  | 0:12 | 4.55 | -0.49023 | 0.59957
|  | 0:12 | 4.5511 | -0.5088 | 0.59957
|  | 0:13 | 4.5522 | -0.52738 | 0.59956
|  | 0:13 | 4.5533 | -0.54595 | 0.59956
|  | 0:13 | 4.5544 | -0.56452 | 0.59956
|  | 0:13 | 4.5556 | -0.58056 | 0.59956
|  | 0:13 | 4.5567 | -0.58899 | 0.59956
|  | 0:13 | 4.5578 | -0.59741 | 0.59955
|  | 0:13 | 4.5589 | -0.60464 | 0.59955
|  | 0:13 | 4.56 | -0.61068 | 0.59955
|  | 0:13 | 4.5611 | -0.61671 | 0.59955
|  | 0:13 | 4.5622 | -0.62274 | 0.59954
|  | 0:13 | 4.5633 | -0.62878 | 0.59954
|  | 0:13 | 4.5644 | -0.64556 | 0.59954
|  | 0:13 | 4.5656 | -0.67309 | 0.59954
|  | 0:13 | 4.5667 | -0.70062 | 0.59953
|  | 0:13 | 4.5678 | -0.7259 | 0.59953
|  | 0:14 | 4.5689 | -0.75118 | 0.59953
|  | 0:14 | 4.57 | -0.76373 | 0.59953
|  | 0:14 | 4.5711 | -0.76355 | 0.59953
|  | 0:14 | 4.5722 | -0.76336 | 0.59952
|  | 0:14 | 4.5733 | -0.74165 | 0.59952
|  | 0:14 | 4.5744 | -0.71995 | 0.59952
|  | 0:14 | 4.5756 | -0.69328 | 0.59952
|  | 0:14 | 4.5767 | -0.66166 | 0.59951
|  | 0:14 | 4.5778 | -0.63004 | 0.59951
|  | 0:14 | 4.5789 | -0.60123 | 0.59951
|  | 0:14 | 4.58 | -0.57243 | 0.59951
|  | 0:14 | 4.5811 | -0.55891 | 0.5995
|  | 0:14 | 4.5822 | -0.56068 | 0.5995
|  | 0:14 | 4.5833 | -0.56245 | 0.5995
|  | 0:14 | 4.5844 | -0.54412 | 0.5995
|  | 0:15 | 4.5856 | -0.52578 | 0.5995
|  | 0:15 | 4.5867 | -0.51626 | 0.59949
|  | 0:15 | 4.5878 | -0.51554 | 0.59949
|  | 0:15 | 4.5889 | -0.51483 | 0.59949
|  | 0:15 | 4.59 | -0.51658 | 0.59949
|  | 0:15 | 4.5911 | -0.51832 | 0.59948
|  | 0:15 | 4.5922 | -0.51742 | 0.59948
|  | 0:15 | 4.5933 | -0.51387 | 0.59948
|  | 0:15 | 4.5944 | -0.51032 | 0.59948
|  | 0:15 | 4.5956 | -0.49265 | 0.59947
|  | 0:15 | 4.5967 | -0.47497 | 0.59947
|  | 0:15 | 4.5978 | -0.4573 | 0.59947
|  | 0:15 | 4.5989 | -0.43963 | 0.59947
|  | 0:15 | 4.6 | -0.42195 | 0.59947
|  | 0:15 | 4.6011 | -0.40033 | 0.59946
|  | 0:16 | 4.6022 | -0.3787 | 0.59946
|  | 0:16 | 4.6033 | -0.35755 | 0.59946
|  | 0:16 | 4.6044 | -0.33687 | 0.59946
|  | 0:16 | 4.6056 | -0.31619 | 0.59945
|  | 0:16 | 4.6067 | -0.27026 | 0.59945
|  | 0:16 | 4.6078 | -0.22432 | 0.59945
|  | 0:16 | 4.6089 | -0.18079 | 0.59945
|  | 0:16 | 4.61 | -0.13806 | 0.59944
|  | 0:16 | 4.6111 | -0.095326 | 0.59944
|  | 0:16 | 4.6122 | -0.056057 | 0.59944
|  | 0:16 | 4.6133 | -0.016788 | 0.59944
|  | 0:16 | 4.6144 | 0.015659 | 0.59944
|  | 0:16 | 4.6156 | 0.041284 | 0.59943
|  | 0:16 | 4.6167 | 0.066908 | 0.59943
|  | 0:16 | 4.6178 | 0.067889 | 0.59943
|  | 0:17 | 4.6189 | 0.06887 | 0.59943
|  | 0:17 | 4.62 | 0.077604 | 0.59942
|  | 0:17 | 4.6211 | 0.094089 | 0.59942
|  | 0:17 | 4.6222 | 0.11057 | 0.59942
|  | 0:17 | 4.6233 | 0.13697 | 0.59942
|  | 0:17 | 4.6244 | 0.16337 | 0.59941
|  | 0:17 | 4.6256 | 0.18555 | 0.59941
|  | 0:17 | 4.6267 | 0.2035 | 0.59941
|  | 0:17 | 4.6278 | 0.22146 | 0.59941
|  | 0:17 | 4.6289 | 0.25483 | 0.59941
|  | 0:17 | 4.63 | 0.2882 | 0.5994
|  | 0:17 | 4.6311 | 0.30837 | 0.5994
|  | 0:17 | 4.6322 | 0.31533 | 0.5994
|  | 0:17 | 4.6333 | 0.32229 | 0.5994
|  | 0:17 | 4.6344 | 0.34371 | 0.59939
|  | 0:18 | 4.6356 | 0.36513 | 0.59939
|  | 0:18 | 4.6367 | 0.39495 | 0.59939
|  | 0:18 | 4.6378 | 0.43316 | 0.59939
|  | 0:18 | 4.6389 | 0.47137 | 0.59938
|  | 0:18 | 4.64 | 0.50421 | 0.59938
|  | 0:18 | 4.6411 | 0.53705 | 0.59938
|  | 0:18 | 4.6422 | 0.56677 | 0.59938
|  | 0:18 | 4.6433 | 0.59337 | 0.59937
|  | 0:18 | 4.6444 | 0.61996 | 0.59937
|  | 0:18 | 4.6456 | 0.63533 | 0.59937
|  | 0:18 | 4.6467 | 0.6507 | 0.59937
|  | 0:18 | 4.6478 | 0.67478 | 0.59937
|  | 0:18 | 4.6489 | 0.70756 | 0.59936
|  | 0:18 | 4.65 | 0.74033 | 0.59936
|  | 0:18 | 4.6511 | 0.7188 | 0.59936
|  | 0:19 | 4.6522 | 0.69726 | 0.59936
|  | 0:19 | 4.6533 | 0.69924 | 0.59935
|  | 0:19 | 4.6544 | 0.72473 | 0.59935
|  | 0:19 | 4.6556 | 0.75023 | 0.59935
|  | 0:19 | 4.6567 | 0.75876 | 0.59935
|  | 0:19 | 4.6578 | 0.76729 | 0.59934
|  | 0:19 | 4.6589 | 0.77299 | 0.59934
|  | 0:19 | 4.66 | 0.77774 | 0.59934
|  | 0:19 | 4.6611 | 0.7825 | 0.59934
|  | 0:19 | 4.6622 | 0.76741 | 0.59934
|  | 0:19 | 4.6633 | 0.75232 | 0.59933
|  | 0:19 | 4.6644 | 0.7296 | 0.59933
|  | 0:19 | 4.6656 | 0.69925 | 0.59933
|  | 0:19 | 4.6667 | 0.6689 | 0.59933
|  | 0:19 | 4.6678 | 0.62576 | 0.59932
|  | 0:20 | 4.6689 | 0.58261 | 0.59932
|  | 0:20 | 4.67 | 0.54949 | 0.59932
|  | 0:20 | 4.6711 | 0.5264 | 0.59932
|  | 0:20 | 4.6722 | 0.50331 | 0.59931
|  | 0:20 | 4.6733 | 0.4765 | 0.59931
|  | 0:20 | 4.6744 | 0.44968 | 0.59931
|  | 0:20 | 4.6756 | 0.4167 | 0.59931
|  | 0:20 | 4.6767 | 0.37755 | 0.59931
|  | 0:20 | 4.6778 | 0.33841 | 0.5993
|  | 0:20 | 4.6789 | 0.29386 | 0.5993
|  | 0:20 | 4.68 | 0.24932 | 0.5993
|  | 0:20 | 4.6811 | 0.21533 | 0.5993
|  | 0:20 | 4.6822 | 0.19189 | 0.59929
|  | 0:20 | 4.6833 | 0.16844 | 0.59929
|  | 0:20 | 4.6844 | 0.16499 | 0.59929
|  | 0:21 | 4.6856 | 0.16153 | 0.59929
|  | 0:21 | 4.6867 | 0.15986 | 0.59928
|  | 0:21 | 4.6878 | 0.15996 | 0.59928
|  | 0:21 | 4.6889 | 0.16005 | 0.59928
|  | 0:21 | 4.69 | 0.14796 | 0.59928
|  | 0:21 | 4.6911 | 0.13587 | 0.59928
|  | 0:21 | 4.6922 | 0.12378 | 0.59927
|  | 0:21 | 4.6933 | 0.1117 | 0.59927
|  | 0:21 | 4.6944 | 0.099605 | 0.59927
|  | 0:21 | 4.6956 | 0.079349 | 0.59927
|  | 0:21 | 4.6967 | 0.059092 | 0.59926
|  | 0:21 | 4.6978 | 0.042185 | 0.59926
|  | 0:21 | 4.6989 | 0.028626 | 0.59926
|  | 0:21 | 4.7 | 0.015067 | 0.59926
|  | 0:21 | 4.7011 | 0.017848 | 0.59925
|  | 0:22 | 4.7022 | 0.020629 | 0.59925
|  | 0:22 | 4.7033 | 0.02341 | 0.59925
|  | 0:22 | 4.7044 | 0.02619 | 0.59925
|  | 0:22 | 4.7056 | 0.028971 | 0.59925
|  | 0:22 | 4.7067 | 0.040168 | 0.59924
|  | 0:22 | 4.7078 | 0.051364 | 0.59924
|  | 0:22 | 4.7089 | 0.060832 | 0.59924
|  | 0:22 | 4.71 | 0.068571 | 0.59924
|  | 0:22 | 4.7111 | 0.076309 | 0.59923
|  | 0:22 | 4.7122 | 0.077437 | 0.59923
|  | 0:22 | 4.7133 | 0.078564 | 0.59923
|  | 0:22 | 4.7144 | 0.080322 | 0.59923
|  | 0:22 | 4.7156 | 0.082711 | 0.59922
|  | 0:22 | 4.7167 | 0.085099 | 0.59922
|  | 0:22 | 4.7178 | 0.082506 | 0.59922
|  | 0:23 | 4.7189 | 0.079913 | 0.59922
|  | 0:23 | 4.72 | 0.07732 | 0.59922
|  | 0:23 | 4.7211 | 0.074727 | 0.59921
|  | 0:23 | 4.7222 | 0.072134 | 0.59921
|  | 0:23 | 4.7233 | 0.05751 | 0.59921
|  | 0:23 | 4.7244 | 0.042887 | 0.59921
|  | 0:23 | 4.7256 | 0.041184 | 0.5992
|  | 0:23 | 4.7267 | 0.052402 | 0.5992
|  | 0:23 | 4.7278 | 0.063621 | 0.5992
|  | 0:23 | 4.7289 | 0.059618 | 0.5992
|  | 0:23 | 4.73 | 0.055615 | 0.59919
|  | 0:23 | 4.7311 | 0.053782 | 0.59919
|  | 0:23 | 4.7322 | 0.054119 | 0.59919
|  | 0:23 | 4.7333 | 0.054456 | 0.59919
|  | 0:23 | 4.7344 | 0.052728 | 0.59919
|  | 0:24 | 4.7356 | 0.051 | 0.59918
|  | 0:24 | 4.7367 | 0.053232 | 0.59918
|  | 0:24 | 4.7378 | 0.059425 | 0.59918
|  | 0:24 | 4.7389 | 0.065617 | 0.59918
|  | 0:24 | 4.74 | 0.089973 | 0.59917
|  | 0:24 | 4.7411 | 0.11433 | 0.59917
|  | 0:24 | 4.7422 | 0.13104 | 0.59917
|  | 0:24 | 4.7433 | 0.14009 | 0.59917
|  | 0:24 | 4.7444 | 0.14915 | 0.59916
|  | 0:24 | 4.7456 | 0.14294 | 0.59916
|  | 0:24 | 4.7467 | 0.13674 | 0.59916
|  | 0:24 | 4.7478 | 0.13903 | 0.59916
|  | 0:24 | 4.7489 | 0.14981 | 0.59916
|  | 0:24 | 4.75 | 0.16059 | 0.59915
|  | 0:24 | 4.7511 | 0.17604 | 0.59915
|  | 0:25 | 4.7522 | 0.1915 | 0.59915
|  | 0:25 | 4.7533 | 0.20614 | 0.59915
|  | 0:25 | 4.7544 | 0.21996 | 0.59914
|  | 0:25 | 4.7556 | 0.23378 | 0.59914
|  | 0:25 | 4.7567 | 0.22649 | 0.59914
|  | 0:25 | 4.7578 | 0.2192 | 0.59914
|  | 0:25 | 4.7589 | 0.2103 | 0.59913
|  | 0:25 | 4.76 | 0.1998 | 0.59913
|  | 0:25 | 4.7611 | 0.18929 | 0.59913
|  | 0:25 | 4.7622 | 0.16969 | 0.59913
|  | 0:25 | 4.7633 | 0.15009 | 0.59912
|  | 0:25 | 4.7644 | 0.12595 | 0.59912
|  | 0:25 | 4.7656 | 0.09729 | 0.59912
|  | 0:25 | 4.7667 | 0.068625 | 0.59912
|  | 0:25 | 4.7678 | 0.07361 | 0.59912
|  | 0:26 | 4.7689 | 0.078594 | 0.59911
|  | 0:26 | 4.77 | 0.072993 | 0.59911
|  | 0:26 | 4.7711 | 0.056805 | 0.59911
|  | 0:26 | 4.7722 | 0.040617 | 0.59911
|  | 0:26 | 4.7733 | 0.014632 | 0.5991
|  | 0:26 | 4.7744 | -0.011353 | 0.5991
|  | 0:26 | 4.7756 | -0.035552 | 0.5991
|  | 0:26 | 4.7767 | -0.057963 | 0.5991
|  | 0:26 | 4.7778 | -0.080375 | 0.59909
|  | 0:26 | 4.7789 | -0.065543 | 0.59909
|  | 0:26 | 4.78 | -0.050712 | 0.59909
|  | 0:26 | 4.7811 | -0.031837 | 0.59909
|  | 0:26 | 4.7822 | -0.0089175 | 0.59909
|  | 0:26 | 4.7833 | 0.014002 | 0.59908
|  | 0:26 | 4.7844 | 0.0028253 | 0.59908
|  | 0:27 | 4.7856 | -0.0083511 | 0.59908
|  | 0:27 | 4.7867 | -0.022928 | 0.59908
|  | 0:27 | 4.7878 | -0.040906 | 0.59907
|  | 0:27 | 4.7889 | -0.058884 | 0.59907
|  | 0:27 | 4.79 | -0.068746 | 0.59907
|  | 0:27 | 4.7911 | -0.078609 | 0.59907
|  | 0:27 | 4.7922 | -0.07932 | 0.59906
|  | 0:27 | 4.7933 | -0.076982 | 0.59906
|  | 0:27 | 4.7944 | -0.074643 | 0.59906
|  | 0:27 | 4.7956 | -0.075455 | 0.59906
|  | 0:27 | 4.7967 | -0.076267 | 0.59906
|  | 0:27 | 4.7978 | -0.073963 | 0.59905
|  | 0:27 | 4.7989 | -0.07062 | 0.59905
|  | 0:27 | 4.8 | -0.067277 | 0.59905
|  | 0:27 | 4.8011 | -0.087801 | 0.59905
|  | 0:28 | 4.8022 | -0.10832 | 0.59904
|  | 0:28 | 4.8033 | -0.11242 | 0.59904
|  | 0:28 | 4.8044 | -0.10009 | 0.59904
|  | 0:28 | 4.8056 | -0.087763 | 0.59904
|  | 0:28 | 4.8067 | -0.068639 | 0.59903
|  | 0:28 | 4.8078 | -0.049516 | 0.59903
|  | 0:28 | 4.8089 | -0.015747 | 0.59903
|  | 0:28 | 4.81 | 0.032669 | 0.59903
|  | 0:28 | 4.8111 | 0.076313 | 0.59903
|  | 0:28 | 4.8122 | 0.10565 | 0.59902
|  | 0:28 | 4.8133 | 0.13498 | 0.59902
|  | 0:28 | 4.8144 | 0.14996 | 0.59902
|  | 0:28 | 4.8156 | 0.1506 | 0.59902
|  | 0:28 | 4.8167 | 0.15123 | 0.59901
|  | 0:28 | 4.8178 | 0.15947 | 0.59901
|  | 0:29 | 4.8189 | 0.1677 | 0.59901
|  | 0:29 | 4.82 | 0.16361 | 0.59901
|  | 0:29 | 4.8211 | 0.14719 | 0.599
|  | 0:29 | 4.8222 | 0.13078 | 0.599
|  | 0:29 | 4.8233 | 0.11437 | 0.599
|  | 0:29 | 4.8244 | 0.097961 | 0.599
|  | 0:29 | 4.8256 | 0.077558 | 0.599
|  | 0:29 | 4.8267 | 0.055824 | 0.59899
|  | 0:29 | 4.8278 | 0.034089 | 0.59899
|  | 0:29 | 4.8289 | 0.018564 | 0.59899
|  | 0:29 | 4.83 | 0.0030393 | 0.59899
|  | 0:29 | 4.8311 | -0.016027 | 0.59898
|  | 0:29 | 4.8322 | -0.038635 | 0.59898
|  | 0:29 | 4.8333 | -0.061243 | 0.59898
|  | 0:29 | 4.8344 | -0.068344 | 0.59898
|  | 0:30 | 4.8356 | -0.075445 | 0.59897
|  | 0:30 | 4.8367 | -0.080764 | 0.59897
|  | 0:30 | 4.8378 | -0.0843 | 0.59897
|  | 0:30 | 4.8389 | -0.087836 | 0.59897
|  | 0:30 | 4.84 | -0.08516 | 0.59897
|  | 0:30 | 4.8411 | -0.082483 | 0.59896
|  | 0:30 | 4.8422 | -0.079807 | 0.59896
|  | 0:30 | 4.8433 | -0.07713 | 0.59896
|  | 0:30 | 4.8444 | -0.074454 | 0.59896
|  | 0:30 | 4.8456 | -0.076025 | 0.59895
|  | 0:30 | 4.8467 | -0.077597 | 0.59895
|  | 0:30 | 4.8478 | -0.085439 | 0.59895
|  | 0:30 | 4.8489 | -0.09955 | 0.59895
|  | 0:30 | 4.85 | -0.11366 | 0.59894
|  | 0:30 | 4.8511 | -0.11441 | 0.59894
|  | 0:31 | 4.8522 | -0.11516 | 0.59894
|  | 0:31 | 4.8533 | -0.10971 | 0.59894
|  | 0:31 | 4.8544 | -0.09806 | 0.59894
|  | 0:31 | 4.8556 | -0.084509 | 0.59893
|  | 0:31 | 4.8567 | -0.065244 | 0.59893
|  | 0:31 | 4.8578 | -0.045979 | 0.59893
|  | 0:31 | 4.8589 | -0.029559 | 0.59893
|  | 0:31 | 4.86 | -0.015984 | 0.59892
|  | 0:31 | 4.8611 | -0.0024094 | 0.59892
|  | 0:31 | 4.8622 | 0.022238 | 0.59892
|  | 0:31 | 4.8633 | 0.046885 | 0.59892
|  | 0:31 | 4.8644 | 0.074314 | 0.59891
|  | 0:31 | 4.8656 | 0.10453 | 0.59891
|  | 0:31 | 4.8667 | 0.13474 | 0.59891
|  | 0:31 | 4.8678 | 0.15843 | 0.59891
|  | 0:32 | 4.8689 | 0.18212 | 0.59891
|  | 0:32 | 4.87 | 0.20365 | 0.5989
|  | 0:32 | 4.8711 | 0.22304 | 0.5989
|  | 0:32 | 4.8722 | 0.24243 | 0.5989
|  | 0:32 | 4.8733 | 0.2467 | 0.5989
|  | 0:32 | 4.8744 | 0.25097 | 0.59889
|  | 0:32 | 4.8756 | 0.25524 | 0.59889
|  | 0:32 | 4.8767 | 0.25952 | 0.59889
|  | 0:32 | 4.8778 | 0.26379 | 0.59889
|  | 0:32 | 4.8789 | 0.26806 | 0.59888
|  | 0:32 | 4.88 | 0.27234 | 0.59888
|  | 0:32 | 4.8811 | 0.27055 | 0.59888
|  | 0:32 | 4.8822 | 0.26272 | 0.59888
|  | 0:32 | 4.8833 | 0.25488 | 0.59887
|  | 0:32 | 4.8844 | 0.23498 | 0.59887
|  | 0:33 | 4.8856 | 0.21507 | 0.59887
|  | 0:33 | 4.8867 | 0.20228 | 0.59887
|  | 0:33 | 4.8878 | 0.1966 | 0.59887
|  | 0:33 | 4.8889 | 0.19092 | 0.59886
|  | 0:33 | 4.89 | 0.17374 | 0.59886
|  | 0:33 | 4.8911 | 0.15656 | 0.59886
|  | 0:33 | 4.8922 | 0.14737 | 0.59886
|  | 0:33 | 4.8933 | 0.14617 | 0.59885
|  | 0:33 | 4.8944 | 0.14096 | 0.59885
|  | 0:33 | 4.8956 | 0.1237 | 0.59885
|  | 0:33 | 4.8967 | 0.10644 | 0.59885
|  | 0:33 | 4.8978 | 0.091813 | 0.59884
|  | 0:33 | 4.8989 | 0.079822 | 0.59884
|  | 0:33 | 4.9 | 0.067831 | 0.59884
|  | 0:33 | 4.9011 | 0.075896 | 0.59884
|  | 0:34 | 4.9022 | 0.083961 | 0.59884
|  | 0:34 | 4.9033 | 0.086463 | 0.59883
|  | 0:34 | 4.9044 | 0.083403 | 0.59883
|  | 0:34 | 4.9056 | 0.080342 | 0.59883
|  | 0:34 | 4.9067 | 0.086139 | 0.59883
|  | 0:34 | 4.9078 | 0.091936 | 0.59882
|  | 0:34 | 4.9089 | 0.086932 | 0.59882
|  | 0:34 | 4.91 | 0.071129 | 0.59882
|  | 0:34 | 4.9111 | 0.055325 | 0.59882
|  | 0:34 | 4.9122 | 0.058039 | 0.59881
|  | 0:34 | 4.9133 | 0.060754 | 0.59881
|  | 0:34 | 4.9144 | 0.053289 | 0.59881
|  | 0:34 | 4.9156 | 0.035644 | 0.59881
|  | 0:34 | 4.9167 | 0.018 | 0.59881
|  | 0:34 | 4.9178 | -0.013065 | 0.5988
|  | 0:35 | 4.9189 | -0.04413 | 0.5988
|  | 0:35 | 4.92 | -0.070275 | 0.5988
|  | 0:35 | 4.9211 | -0.091499 | 0.5988
|  | 0:35 | 4.9222 | -0.11272 | 0.59879
|  | 0:35 | 4.9233 | -0.1153 | 0.59879
|  | 0:35 | 4.9244 | -0.11788 | 0.59879
|  | 0:35 | 4.9256 | -0.11783 | 0.59879
|  | 0:35 | 4.9267 | -0.11514 | 0.59878
|  | 0:35 | 4.9278 | -0.11272 | 0.59878
|  | 0:35 | 4.9289 | -0.11108 | 0.59878
|  | 0:35 | 4.93 | -0.10944 | 0.59878
|  | 0:35 | 4.9311 | -0.1078 | 0.59878
|  | 0:35 | 4.9322 | -0.12031 | 0.59877
|  | 0:35 | 4.9333 | -0.13283 | 0.59877
|  | 0:35 | 4.9344 | -0.13556 | 0.59877
|  | 0:36 | 4.9356 | -0.1383 | 0.59877
|  | 0:36 | 4.9367 | -0.13564 | 0.59876
|  | 0:36 | 4.9378 | -0.13119 | 0.59876
|  | 0:36 | 4.9389 | -0.1251 | 0.59876
|  | 0:36 | 4.94 | -0.11411 | 0.59876
|  | 0:36 | 4.9411 | -0.10312 | 0.59875
|  | 0:36 | 4.9422 | -0.087127 | 0.59875
|  | 0:36 | 4.9433 | -0.06947 | 0.59875
|  | 0:36 | 4.9444 | -0.057029 | 0.59875
|  | 0:36 | 4.9456 | -0.060235 | 0.59875
|  | 0:36 | 4.9467 | -0.06344 | 0.59874
|  | 0:36 | 4.9478 | -0.059529 | 0.59874
|  | 0:36 | 4.9489 | -0.053247 | 0.59874
|  | 0:36 | 4.95 | -0.048412 | 0.59874
|  | 0:36 | 4.9511 | -0.047923 | 0.59873
|  | 0:37 | 4.9522 | -0.047434 | 0.59873
|  | 0:37 | 4.9533 | -0.052124 | 0.59873
|  | 0:37 | 4.9544 | -0.05854 | 0.59873
|  | 0:37 | 4.9556 | -0.068618 | 0.59872
|  | 0:37 | 4.9567 | -0.08968 | 0.59872
|  | 0:37 | 4.9578 | -0.11074 | 0.59872
|  | 0:37 | 4.9589 | -0.12803 | 0.59872
|  | 0:37 | 4.96 | -0.14405 | 0.59872
|  | 0:37 | 4.9611 | -0.15587 | 0.59871
|  | 0:37 | 4.9622 | -0.15507 | 0.59871
|  | 0:37 | 4.9633 | -0.15427 | 0.59871
|  | 0:37 | 4.9644 | -0.1689 | 0.59871
|  | 0:37 | 4.9656 | -0.18867 | 0.5987
|  | 0:37 | 4.9667 | -0.19879 | 0.5987
|  | 0:37 | 4.9678 | -0.17995 | 0.5987
|  | 0:38 | 4.9689 | -0.16112 | 0.5987
|  | 0:38 | 4.97 | -0.14042 | 0.59869
|  | 0:38 | 4.9711 | -0.1191 | 0.59869
|  | 0:38 | 4.9722 | -0.087246 | 0.59869
|  | 0:38 | 4.9733 | -0.023777 | 0.59869
|  | 0:38 | 4.9744 | 0.039692 | 0.59869
|  | 0:38 | 4.9756 | 0.084628 | 0.59868
|  | 0:38 | 4.9767 | 0.12956 | 0.59868
|  | 0:38 | 4.9778 | 0.17372 | 0.59868
|  | 0:38 | 4.9789 | 0.21556 | 0.59868
|  | 0:38 | 4.98 | 0.2574 | 0.59867
|  | 0:38 | 4.9811 | 0.26371 | 0.59867
|  | 0:38 | 4.9822 | 0.25818 | 0.59867
|  | 0:38 | 4.9833 | 0.25264 | 0.59867
|  | 0:38 | 4.9844 | 0.24711 | 0.59866
|  | 0:39 | 4.9856 | 0.24157 | 0.59866
|  | 0:39 | 4.9867 | 0.24404 | 0.59866
|  | 0:39 | 4.9878 | 0.24918 | 0.59866
|  | 0:39 | 4.9889 | 0.25653 | 0.59866
|  | 0:39 | 4.99 | 0.27053 | 0.59865
|  | 0:39 | 4.9911 | 0.28454 | 0.59865
|  | 0:39 | 4.9922 | 0.28643 | 0.59865
|  | 0:39 | 4.9933 | 0.28428 | 0.59865
|  | 0:39 | 4.9944 | 0.28637 | 0.59864
|  | 0:39 | 4.9956 | 0.30114 | 0.59864
|  | 0:39 | 4.9967 | 0.31592 | 0.59864
|  | 0:39 | 4.9978 | 0.32289 | 0.59864
|  | 0:39 | 4.9989 | 0.32726 | 0.59863
|  | 0:39 | 5 | 0.32399 | 0.59863
|  | 0:39 | 5.0011 | 0.3131 | 0.59863
|  | 0:40 | 5.0022 | 0.3022 | 0.59863
|  | 0:40 | 5.0033 | 0.28574 | 0.59862
|  | 0:40 | 5.0044 | 0.26742 | 0.59862
|  | 0:40 | 5.0056 | 0.24996 | 0.59862
|  | 0:40 | 5.0067 | 0.23337 | 0.59862
|  | 0:40 | 5.0078 | 0.21678 | 0.59862
|  | 0:40 | 5.0089 | 0.18735 | 0.59861
|  | 0:40 | 5.01 | 0.15364 | 0.59861
|  | 0:40 | 5.0111 | 0.13899 | 0.59861
|  | 0:40 | 5.0122 | 0.1434 | 0.59861
|  | 0:40 | 5.0133 | 0.1478 | 0.5986
|  | 0:40 | 5.0144 | 0.16101 | 0.5986
|  | 0:40 | 5.0156 | 0.17715 | 0.5986
|  | 0:40 | 5.0167 | 0.1784 | 0.5986
|  | 0:40 | 5.0178 | 0.16474 | 0.59859
|  | 0:41 | 5.0189 | 0.15109 | 0.59859
|  | 0:41 | 5.02 | 0.12306 | 0.59859
|  | 0:41 | 5.0211 | 0.090241 | 0.59859
|  | 0:41 | 5.0222 | 0.056587 | 0.59859
|  | 0:41 | 5.0233 | 0.020429 | 0.59858
|  | 0:41 | 5.0244 | -0.015729 | 0.59858
|  | 0:41 | 5.0256 | -0.042232 | 0.59858
|  | 0:41 | 5.0267 | -0.065516 | 0.59858
|  | 0:41 | 5.0278 | -0.087599 | 0.59857
|  | 0:41 | 5.0289 | -0.10608 | 0.59857
|  | 0:41 | 5.03 | -0.12456 | 0.59857
|  | 0:41 | 5.0311 | -0.13921 | 0.59857
|  | 0:41 | 5.0322 | -0.15259 | 0.59856
|  | 0:41 | 5.0333 | -0.16354 | 0.59856
|  | 0:41 | 5.0344 | -0.16719 | 0.59856
|  | 0:42 | 5.0356 | -0.17083 | 0.59856
|  | 0:42 | 5.0367 | -0.19514 | 0.59856
|  | 0:42 | 5.0378 | -0.22632 | 0.59855
|  | 0:42 | 5.0389 | -0.24783 | 0.59855
|  | 0:42 | 5.04 | -0.24028 | 0.59855
|  | 0:42 | 5.0411 | -0.23273 | 0.59855
|  | 0:42 | 5.0422 | -0.22091 | 0.59854
|  | 0:42 | 5.0433 | -0.20767 | 0.59854
|  | 0:42 | 5.0444 | -0.19169 | 0.59854
|  | 0:42 | 5.0456 | -0.1675 | 0.59854
|  | 0:42 | 5.0467 | -0.14331 | 0.59853
|  | 0:42 | 5.0478 | -0.12658 | 0.59853
|  | 0:42 | 5.0489 | -0.11235 | 0.59853
|  | 0:42 | 5.05 | -0.099041 | 0.59853
|  | 0:42 | 5.0511 | -0.088485 | 0.59853
|  | 0:43 | 5.0522 | -0.077929 | 0.59852
|  | 0:43 | 5.0533 | -0.06405 | 0.59852
|  | 0:43 | 5.0544 | -0.049063 | 0.59852
|  | 0:43 | 5.0556 | -0.032325 | 0.59852
|  | 0:43 | 5.0567 | -0.01033 | 0.59851
|  | 0:43 | 5.0578 | 0.011664 | 0.59851
|  | 0:43 | 5.0589 | 0.025807 | 0.59851
|  | 0:43 | 5.06 | 0.037333 | 0.59851
|  | 0:43 | 5.0611 | 0.049144 | 0.5985
|  | 0:43 | 5.0622 | 0.06181 | 0.5985
|  | 0:43 | 5.0633 | 0.074475 | 0.5985
|  | 0:43 | 5.0644 | 0.088406 | 0.5985
|  | 0:43 | 5.0656 | 0.10276 | 0.5985
|  | 0:43 | 5.0667 | 0.11637 | 0.59849
|  | 0:43 | 5.0678 | 0.12776 | 0.59849
|  | 0:44 | 5.0689 | 0.13916 | 0.59849
|  | 0:44 | 5.07 | 0.15333 | 0.59849
|  | 0:44 | 5.0711 | 0.16843 | 0.59848
|  | 0:44 | 5.0722 | 0.18226 | 0.59848
|  | 0:44 | 5.0733 | 0.19228 | 0.59848
|  | 0:44 | 5.0744 | 0.20229 | 0.59848
|  | 0:44 | 5.0756 | 0.18703 | 0.59847
|  | 0:44 | 5.0767 | 0.17176 | 0.59847
|  | 0:44 | 5.0778 | 0.15361 | 0.59847
|  | 0:44 | 5.0789 | 0.12677 | 0.59847
|  | 0:44 | 5.08 | 0.099932 | 0.59847
|  | 0:44 | 5.0811 | 0.080254 | 0.59846
|  | 0:44 | 5.0822 | 0.062962 | 0.59846
|  | 0:44 | 5.0833 | 0.049071 | 0.59846
|  | 0:44 | 5.0844 | 0.045383 | 0.59846
|  | 0:45 | 5.0856 | 0.041695 | 0.59845
|  | 0:45 | 5.0867 | 0.032198 | 0.59845
|  | 0:45 | 5.0878 | 0.020765 | 0.59845
|  | 0:45 | 5.0889 | 0.010218 | 0.59845
|  | 0:45 | 5.09 | 0.0023298 | 0.59844
|  | 0:45 | 5.0911 | -0.0055582 | 0.59844
|  | 0:45 | 5.0922 | -0.023576 | 0.59844
|  | 0:45 | 5.0933 | -0.04497 | 0.59844
|  | 0:45 | 5.0944 | -0.063236 | 0.59844
|  | 0:45 | 5.0956 | -0.072119 | 0.59843
|  | 0:45 | 5.0967 | -0.081002 | 0.59843
|  | 0:45 | 5.0978 | -0.091497 | 0.59843
|  | 0:45 | 5.0989 | -0.10253 | 0.59843
|  | 0:45 | 5.1 | -0.11184 | 0.59842
|  | 0:45 | 5.1011 | -0.11599 | 0.59842
|  | 0:46 | 5.1022 | -0.12014 | 0.59842
|  | 0:46 | 5.1033 | -0.12608 | 0.59842
|  | 0:46 | 5.1044 | -0.13383 | 0.59841
|  | 0:46 | 5.1056 | -0.14157 | 0.59841
|  | 0:46 | 5.1067 | -0.14002 | 0.59841
|  | 0:46 | 5.1078 | -0.13847 | 0.59841
|  | 0:46 | 5.1089 | -0.14396 | 0.59841
|  | 0:46 | 5.11 | -0.1565 | 0.5984
|  | 0:46 | 5.1111 | -0.16904 | 0.5984
|  | 0:46 | 5.1122 | -0.18405 | 0.5984
|  | 0:46 | 5.1133 | -0.19905 | 0.5984
|  | 0:46 | 5.1144 | -0.20539 | 0.59839
|  | 0:46 | 5.1156 | -0.20306 | 0.59839
|  | 0:46 | 5.1167 | -0.20073 | 0.59839
|  | 0:46 | 5.1178 | -0.17283 | 0.59839
|  | 0:47 | 5.1189 | -0.14493 | 0.59838
|  | 0:47 | 5.12 | -0.1155 | 0.59838
|  | 0:47 | 5.1211 | -0.084542 | 0.59838
|  | 0:47 | 5.1222 | -0.053583 | 0.59838
|  | 0:47 | 5.1233 | -0.01823 | 0.59837
|  | 0:47 | 5.1244 | 0.017124 | 0.59837
|  | 0:47 | 5.1256 | 0.042132 | 0.59837
|  | 0:47 | 5.1267 | 0.056796 | 0.59837
|  | 0:47 | 5.1278 | 0.07146 | 0.59837
|  | 0:47 | 5.1289 | 0.069582 | 0.59836
|  | 0:47 | 5.13 | 0.067705 | 0.59836
|  | 0:47 | 5.1311 | 0.068706 | 0.59836
|  | 0:47 | 5.1322 | 0.072586 | 0.59836
|  | 0:47 | 5.1333 | 0.076467 | 0.59835
|  | 0:47 | 5.1344 | 0.08665 | 0.59835
|  | 0:48 | 5.1356 | 0.096832 | 0.59835
|  | 0:48 | 5.1367 | 0.097433 | 0.59835
|  | 0:48 | 5.1378 | 0.088452 | 0.59834
|  | 0:48 | 5.1389 | 0.079471 | 0.59834
|  | 0:48 | 5.14 | 0.07049 | 0.59834
|  | 0:48 | 5.1411 | 0.061509 | 0.59834
|  | 0:48 | 5.1422 | 0.044761 | 0.59834
|  | 0:48 | 5.1433 | 0.020245 | 0.59833
|  | 0:48 | 5.1444 | -0.0042709 | 0.59833
|  | 0:48 | 5.1456 | -0.0071686 | 0.59833
|  | 0:48 | 5.1467 | -0.010066 | 0.59833
|  | 0:48 | 5.1478 | -0.015785 | 0.59832
|  | 0:48 | 5.1489 | -0.024325 | 0.59832
|  | 0:48 | 5.15 | -0.032865 | 0.59832
|  | 0:48 | 5.1511 | -0.041405 | 0.59832
|  | 0:49 | 5.1522 | -0.049945 | 0.59831
|  | 0:49 | 5.1533 | -0.061732 | 0.59831
|  | 0:49 | 5.1544 | -0.076764 | 0.59831
|  | 0:49 | 5.1556 | -0.091797 | 0.59831
|  | 0:49 | 5.1567 | -0.081949 | 0.59831
|  | 0:49 | 5.1578 | -0.072101 | 0.5983
|  | 0:49 | 5.1589 | -0.069993 | 0.5983
|  | 0:49 | 5.16 | -0.075625 | 0.5983
|  | 0:49 | 5.1611 | -0.081256 | 0.5983
|  | 0:49 | 5.1622 | -0.10398 | 0.59829
|  | 0:49 | 5.1633 | -0.12671 | 0.59829
|  | 0:49 | 5.1644 | -0.13424 | 0.59829
|  | 0:49 | 5.1656 | -0.13671 | 0.59829
|  | 0:49 | 5.1667 | -0.13917 | 0.59828
|  | 0:49 | 5.1678 | -0.13967 | 0.59828
|  | 0:50 | 5.1689 | -0.14016 | 0.59828
|  | 0:50 | 5.17 | -0.13967 | 0.59828
|  | 0:50 | 5.1711 | -0.1382 | 0.59828
|  | 0:50 | 5.1722 | -0.13672 | 0.59827
|  | 0:50 | 5.1733 | -0.13986 | 0.59827
|  | 0:50 | 5.1744 | -0.143 | 0.59827
|  | 0:50 | 5.1756 | -0.15783 | 0.59827
|  | 0:50 | 5.1767 | -0.18435 | 0.59826
|  | 0:50 | 5.1778 | -0.21088 | 0.59826
|  | 0:50 | 5.1789 | -0.23015 | 0.59826
|  | 0:50 | 5.18 | -0.24943 | 0.59826
|  | 0:50 | 5.1811 | -0.27026 | 0.59825
|  | 0:50 | 5.1822 | -0.29265 | 0.59825
|  | 0:50 | 5.1833 | -0.31503 | 0.59825
|  | 0:50 | 5.1844 | -0.32195 | 0.59825
|  | 0:51 | 5.1856 | -0.32886 | 0.59825
|  | 0:51 | 5.1867 | -0.34119 | 0.59824
|  | 0:51 | 5.1878 | -0.35894 | 0.59824
|  | 0:51 | 5.1889 | -0.37669 | 0.59824
|  | 0:51 | 5.19 | -0.40678 | 0.59824
|  | 0:51 | 5.1911 | -0.43687 | 0.59823
|  | 0:51 | 5.1922 | -0.47126 | 0.59823
|  | 0:51 | 5.1933 | -0.50996 | 0.59823
|  | 0:51 | 5.1944 | -0.54865 | 0.59823
|  | 0:51 | 5.1956 | -0.56956 | 0.59822
|  | 0:51 | 5.1967 | -0.59046 | 0.59822
|  | 0:51 | 5.1978 | -0.60099 | 0.59822
|  | 0:51 | 5.1989 | -0.60114 | 0.59822
|  | 0:51 | 5.2 | -0.60129 | 0.59822
|  | 0:51 | 5.2011 | -0.60725 | 0.59821
|  | 0:52 | 5.2022 | -0.6132 | 0.59821
|  | 0:52 | 5.2033 | -0.61495 | 0.59821
|  | 0:52 | 5.2044 | -0.6125 | 0.59821
|  | 0:52 | 5.2056 | -0.61004 | 0.5982
|  | 0:52 | 5.2067 | -0.60192 | 0.5982
|  | 0:52 | 5.2078 | -0.59379 | 0.5982
|  | 0:52 | 5.2089 | -0.57338 | 0.5982
|  | 0:52 | 5.21 | -0.54068 | 0.59819
|  | 0:52 | 5.2111 | -0.50798 | 0.59819
|  | 0:52 | 5.2122 | -0.44948 | 0.59819
|  | 0:52 | 5.2133 | -0.39097 | 0.59819
|  | 0:52 | 5.2144 | -0.34491 | 0.59819
|  | 0:52 | 5.2156 | -0.30298 | 0.59818
|  | 0:52 | 5.2167 | -0.26106 | 0.59818
|  | 0:52 | 5.2178 | -0.21372 | 0.59818
|  | 0:53 | 5.2189 | -0.16637 | 0.59818
|  | 0:53 | 5.22 | -0.13138 | 0.59817
|  | 0:53 | 5.2211 | -0.10875 | 0.59817
|  | 0:53 | 5.2222 | -0.086123 | 0.59817
|  | 0:53 | 5.2233 | -0.059309 | 0.59817
|  | 0:53 | 5.2244 | -0.032495 | 0.59816
|  | 0:53 | 5.2256 | -0.0085625 | 0.59816
|  | 0:53 | 5.2267 | 0.01441 | 0.59816
|  | 0:53 | 5.2278 | 0.037382 | 0.59816
|  | 0:53 | 5.2289 | 0.066252 | 0.59816
|  | 0:53 | 5.23 | 0.095122 | 0.59815
|  | 0:53 | 5.2311 | 0.10872 | 0.59815
|  | 0:53 | 5.2322 | 0.10704 | 0.59815
|  | 0:53 | 5.2333 | 0.10536 | 0.59815
|  | 0:53 | 5.2344 | 0.10089 | 0.59814
|  | 0:54 | 5.2356 | 0.088038 | 0.59814
|  | 0:54 | 5.2367 | 0.080428 | 0.59814
|  | 0:54 | 5.2378 | 0.078054 | 0.59814
|  | 0:54 | 5.2389 | 0.07568 | 0.59813
|  | 0:54 | 5.24 | 0.060873 | 0.59813
|  | 0:54 | 5.2411 | 0.046067 | 0.59813
|  | 0:54 | 5.2422 | 0.032489 | 0.59813
|  | 0:54 | 5.2433 | 0.02014 | 0.59812
|  | 0:54 | 5.2444 | 0.0077913 | 0.59812
|  | 0:54 | 5.2456 | 0.0089382 | 0.59812
|  | 0:54 | 5.2467 | 0.010085 | 0.59812
|  | 0:54 | 5.2478 | 0.017944 | 0.59812
|  | 0:54 | 5.2489 | 0.032514 | 0.59811
|  | 0:54 | 5.25 | 0.047085 | 0.59811
|  | 0:54 | 5.2511 | 0.076109 | 0.59811
|  | 0:55 | 5.2522 | 0.10513 | 0.59811
|  | 0:55 | 5.2533 | 0.13867 | 0.5981
|  | 0:55 | 5.2544 | 0.17371 | 0.5981
|  | 0:55 | 5.2556 | 0.20875 | 0.5981
|  | 0:55 | 5.2567 | 0.23334 | 0.5981
|  | 0:55 | 5.2578 | 0.25792 | 0.59809
|  | 0:55 | 5.2589 | 0.27615 | 0.59809
|  | 0:55 | 5.26 | 0.28804 | 0.59809
|  | 0:55 | 5.2611 | 0.29992 | 0.59809
|  | 0:55 | 5.2622 | 0.31798 | 0.59809
|  | 0:55 | 5.2633 | 0.33605 | 0.59808
|  | 0:55 | 5.2644 | 0.36385 | 0.59808
|  | 0:55 | 5.2656 | 0.40137 | 0.59808
|  | 0:55 | 5.2667 | 0.4389 | 0.59808
|  | 0:55 | 5.2678 | 0.47837 | 0.59807
|  | 0:56 | 5.2689 | 0.51784 | 0.59807
|  | 0:56 | 5.27 | 0.54605 | 0.59807
|  | 0:56 | 5.2711 | 0.57051 | 0.59807
|  | 0:56 | 5.2722 | 0.59043 | 0.59806
|  | 0:56 | 5.2733 | 0.59672 | 0.59806
|  | 0:56 | 5.2744 | 0.60301 | 0.59806
|  | 0:56 | 5.2756 | 0.61476 | 0.59806
|  | 0:56 | 5.2767 | 0.62833 | 0.59806
|  | 0:56 | 5.2778 | 0.63908 | 0.59805
|  | 0:56 | 5.2789 | 0.64134 | 0.59805
|  | 0:56 | 5.28 | 0.6436 | 0.59805
|  | 0:56 | 5.2811 | 0.64966 | 0.59805
|  | 0:56 | 5.2822 | 0.65699 | 0.59804
|  | 0:56 | 5.2833 | 0.66861 | 0.59804
|  | 0:56 | 5.2844 | 0.69311 | 0.59804
|  | 0:57 | 5.2856 | 0.71761 | 0.59804
|  | 0:57 | 5.2867 | 0.72431 | 0.59803
|  | 0:57 | 5.2878 | 0.72507 | 0.59803
|  | 0:57 | 5.2889 | 0.72324 | 0.59803
|  | 0:57 | 5.29 | 0.71361 | 0.59803
|  | 0:57 | 5.2911 | 0.70399 | 0.59803
|  | 0:57 | 5.2922 | 0.68391 | 0.59802
|  | 0:57 | 5.2933 | 0.66036 | 0.59802
|  | 0:57 | 5.2944 | 0.63042 | 0.59802
|  | 0:57 | 5.2956 | 0.58134 | 0.59802
|  | 0:57 | 5.2967 | 0.53226 | 0.59801
|  | 0:57 | 5.2978 | 0.48119 | 0.59801
|  | 0:57 | 5.2989 | 0.42944 | 0.59801
|  | 0:57 | 5.3 | 0.38903 | 0.59801
|  | 0:57 | 5.3011 | 0.35995 | 0.598
|  | 0:58 | 5.3022 | 0.33088 | 0.598
|  | 0:58 | 5.3033 | 0.2821 | 0.598
|  | 0:58 | 5.3044 | 0.22676 | 0.598
|  | 0:58 | 5.3056 | 0.17658 | 0.598
|  | 0:58 | 5.3067 | 0.1419 | 0.59799
|  | 0:58 | 5.3078 | 0.10722 | 0.59799
|  | 0:58 | 5.3089 | 0.081901 | 0.59799
|  | 0:58 | 5.31 | 0.056586 | 0.59799
|  | 0:58 | 5.3111 | 0.030142 | 0.59798
|  | 0:58 | 5.3122 | 0.00031549 | 0.59798
|  | 0:58 | 5.3133 | -0.029511 | 0.59798
|  | 0:58 | 5.3144 | -0.058698 | 0.59798
|  | 0:58 | 5.3156 | -0.087671 | 0.59797
|  | 0:58 | 5.3167 | -0.11306 | 0.59797
|  | 0:58 | 5.3178 | -0.12771 | 0.59797
|  | 0:59 | 5.3189 | -0.14236 | 0.59797
|  | 0:59 | 5.32 | -0.16624 | 0.59797
|  | 0:59 | 5.3211 | -0.1932 | 0.59796
|  | 0:59 | 5.3222 | -0.22575 | 0.59796
|  | 0:59 | 5.3233 | -0.2751 | 0.59796
|  | 0:59 | 5.3244 | -0.32445 | 0.59796
|  | 0:59 | 5.3256 | -0.35449 | 0.59795
|  | 0:59 | 5.3267 | -0.37809 | 0.59795
|  | 0:59 | 5.3278 | -0.39723 | 0.59795
|  | 0:59 | 5.3289 | -0.40298 | 0.59795
|  | 0:59 | 5.33 | -0.40874 | 0.59794
|  | 0:59 | 5.3311 | -0.41121 | 0.59794
|  | 0:59 | 5.3322 | -0.41258 | 0.59794
|  | 0:59 | 5.3333 | -0.4191 | 0.59794
|  | 0:59 | 5.3344 | -0.44105 | 0.59794
|  | 1:00 | 5.3356 | -0.46301 | 0.59793
|  | 1:00 | 5.3367 | -0.4794 | 0.59793
|  | 1:00 | 5.3378 | -0.49394 | 0.59793
|  | 1:00 | 5.3389 | -0.50803 | 0.59793
|  | 1:00 | 5.34 | -0.52082 | 0.59792
|  | 1:00 | 5.3411 | -0.53361 | 0.59792
|  | 1:00 | 5.3422 | -0.57167 | 0.59792
|  | 1:00 | 5.3433 | -0.61817 | 0.59792
|  | 1:00 | 5.3444 | -0.65686 | 0.59791
|  | 1:00 | 5.3456 | -0.67212 | 0.59791
|  | 1:00 | 5.3467 | -0.68739 | 0.59791
|  | 1:00 | 5.3478 | -0.69862 | 0.59791
|  | 1:00 | 5.3489 | -0.7085 | 0.59791
|  | 1:00 | 5.35 | -0.7136 | 0.5979
|  | 1:00 | 5.3511 | -0.70432 | 0.5979
|  | 1:01 | 5.3522 | -0.69505 | 0.5979
|  | 1:01 | 5.3533 | -0.67207 | 0.5979
|  | 1:01 | 5.3544 | -0.64451 | 0.59789
|  | 1:01 | 5.3556 | -0.61836 | 0.59789
|  | 1:01 | 5.3567 | -0.59644 | 0.59789
|  | 1:01 | 5.3578 | -0.57451 | 0.59789
|  | 1:01 | 5.3589 | -0.55325 | 0.59788
|  | 1:01 | 5.36 | -0.53222 | 0.59788
|  | 1:01 | 5.3611 | -0.51696 | 0.59788
|  | 1:01 | 5.3622 | -0.51903 | 0.59788
|  | 1:01 | 5.3633 | -0.5211 | 0.59787
|  | 1:01 | 5.3644 | -0.52402 | 0.59787
|  | 1:01 | 5.3656 | -0.52724 | 0.59787
|  | 1:01 | 5.3667 | -0.52781 | 0.59787
|  | 1:01 | 5.3678 | -0.52046 | 0.59787
|  | 1:02 | 5.3689 | -0.51311 | 0.59786
|  | 1:02 | 5.37 | -0.49295 | 0.59786
|  | 1:02 | 5.3711 | -0.46852 | 0.59786
|  | 1:02 | 5.3722 | -0.44277 | 0.59786
|  | 1:02 | 5.3733 | -0.41302 | 0.59785
|  | 1:02 | 5.3744 | -0.38327 | 0.59785
|  | 1:02 | 5.3756 | -0.36219 | 0.59785
|  | 1:02 | 5.3767 | -0.34399 | 0.59785
|  | 1:02 | 5.3778 | -0.32331 | 0.59784
|  | 1:02 | 5.3789 | -0.29521 | 0.59784
|  | 1:02 | 5.38 | -0.26711 | 0.59784
|  | 1:02 | 5.3811 | -0.22818 | 0.59784
|  | 1:02 | 5.3822 | -0.18565 | 0.59784
|  | 1:02 | 5.3833 | -0.14681 | 0.59783
|  | 1:02 | 5.3844 | -0.11909 | 0.59783
|  | 1:03 | 5.3856 | -0.091362 | 0.59783
|  | 1:03 | 5.3867 | -0.063635 | 0.59783
|  | 1:03 | 5.3878 | -0.035909 | 0.59782
|  | 1:03 | 5.3889 | -0.010399 | 0.59782
|  | 1:03 | 5.39 | 0.008462 | 0.59782
|  | 1:03 | 5.3911 | 0.027323 | 0.59782
|  | 1:03 | 5.3922 | 0.034398 | 0.59781
|  | 1:03 | 5.3933 | 0.037546 | 0.59781
|  | 1:03 | 5.3944 | 0.043552 | 0.59781
|  | 1:03 | 5.3956 | 0.058133 | 0.59781
|  | 1:03 | 5.3967 | 0.072714 | 0.59781
|  | 1:03 | 5.3978 | 0.058027 | 0.5978
|  | 1:03 | 5.3989 | 0.033585 | 0.5978
|  | 1:03 | 5.4 | 0.0091424 | 0.5978
|  | 1:03 | 5.4011 | -0.0069915 | 0.5978
|  | 1:04 | 5.4022 | -0.014817 | 0.59779
|  | 1:04 | 5.4033 | -0.013008 | 0.59779
|  | 1:04 | 5.4044 | -0.0079873 | 0.59779
|  | 1:04 | 5.4056 | -0.0032145 | 0.59779
|  | 1:04 | 5.4067 | 0.00081442 | 0.59778
|  | 1:04 | 5.4078 | 0.0048433 | 0.59778
|  | 1:04 | 5.4089 | -0.011699 | 0.59778
|  | 1:04 | 5.41 | -0.035099 | 0.59778
|  | 1:04 | 5.4111 | -0.062149 | 0.59778
|  | 1:04 | 5.4122 | -0.10015 | 0.59777
|  | 1:04 | 5.4133 | -0.13814 | 0.59777
|  | 1:04 | 5.4144 | -0.15922 | 0.59777
|  | 1:04 | 5.4156 | -0.17466 | 0.59777
|  | 1:04 | 5.4167 | -0.18651 | 0.59776
|  | 1:04 | 5.4178 | -0.18759 | 0.59776
|  | 1:05 | 5.4189 | -0.18868 | 0.59776
|  | 1:05 | 5.42 | -0.16432 | 0.59776
|  | 1:05 | 5.4211 | -0.13147 | 0.59775
|  | 1:05 | 5.4222 | -0.097254 | 0.59775
|  | 1:05 | 5.4233 | -0.058911 | 0.59775
|  | 1:05 | 5.4244 | -0.020569 | 0.59775
|  | 1:05 | 5.4256 | 0.017096 | 0.59775
|  | 1:05 | 5.4267 | 0.054534 | 0.59774
|  | 1:05 | 5.4278 | 0.085579 | 0.59774
|  | 1:05 | 5.4289 | 0.097447 | 0.59774
|  | 1:05 | 5.43 | 0.10931 | 0.59774
|  | 1:05 | 5.4311 | 0.11074 | 0.59773
|  | 1:05 | 5.4322 | 0.10868 | 0.59773
|  | 1:05 | 5.4333 | 0.10522 | 0.59773
|  | 1:05 | 5.4344 | 0.097578 | 0.59773
|  | 1:06 | 5.4356 | 0.089932 | 0.59772
|  | 1:06 | 5.4367 | 0.073569 | 0.59772
|  | 1:06 | 5.4378 | 0.048491 | 0.59772
|  | 1:06 | 5.4389 | 0.023412 | 0.59772
|  | 1:06 | 5.44 | 0.0095454 | 0.59772
|  | 1:06 | 5.4411 | -0.0043213 | 0.59771
|  | 1:06 | 5.4422 | -0.0022857 | 0.59771
|  | 1:06 | 5.4433 | 0.015652 | 0.59771
|  | 1:06 | 5.4444 | 0.03359 | 0.59771
|  | 1:06 | 5.4456 | 0.10038 | 0.5977
|  | 1:06 | 5.4467 | 0.16717 | 0.5977
|  | 1:06 | 5.4478 | 0.23184 | 0.5977
|  | 1:06 | 5.4489 | 0.29437 | 0.5977
|  | 1:06 | 5.45 | 0.35691 | 0.59769
|  | 1:06 | 5.4511 | 0.38203 | 0.59769
|  | 1:07 | 5.4522 | 0.40715 | 0.59769
|  | 1:07 | 5.4533 | 0.43669 | 0.59769
|  | 1:07 | 5.4544 | 0.47067 | 0.59769
|  | 1:07 | 5.4556 | 0.50464 | 0.59768
|  | 1:07 | 5.4567 | 0.51512 | 0.59768
|  | 1:07 | 5.4578 | 0.52559 | 0.59768
|  | 1:07 | 5.4589 | 0.54013 | 0.59768
|  | 1:07 | 5.46 | 0.55874 | 0.59767
|  | 1:07 | 5.4611 | 0.57735 | 0.59767
|  | 1:07 | 5.4622 | 0.57414 | 0.59767
|  | 1:07 | 5.4633 | 0.57092 | 0.59767
|  | 1:07 | 5.4644 | 0.57038 | 0.59766
|  | 1:07 | 5.4656 | 0.57251 | 0.59766
|  | 1:07 | 5.4667 | 0.57464 | 0.59766
|  | 1:07 | 5.4678 | 0.57446 | 0.59766
|  | 1:08 | 5.4689 | 0.57428 | 0.59766
|  | 1:08 | 5.47 | 0.56794 | 0.59765
|  | 1:08 | 5.4711 | 0.55544 | 0.59765
|  | 1:08 | 5.4722 | 0.54294 | 0.59765
|  | 1:08 | 5.4733 | 0.53362 | 0.59765
|  | 1:08 | 5.4744 | 0.52431 | 0.59764
|  | 1:08 | 5.4756 | 0.51346 | 0.59764
|  | 1:08 | 5.4767 | 0.50109 | 0.59764
|  | 1:08 | 5.4778 | 0.48871 | 0.59764
|  | 1:08 | 5.4789 | 0.46532 | 0.59763
|  | 1:08 | 5.48 | 0.44193 | 0.59763
|  | 1:08 | 5.4811 | 0.41736 | 0.59763
|  | 1:08 | 5.4822 | 0.39241 | 0.59763
|  | 1:08 | 5.4833 | 0.36745 | 0.59762
|  | 1:08 | 5.4844 | 0.32955 | 0.59762
|  | 1:09 | 5.4856 | 0.29165 | 0.59762
|  | 1:09 | 5.4867 | 0.25312 | 0.59762
|  | 1:09 | 5.4878 | 0.21396 | 0.59762
|  | 1:09 | 5.4889 | 0.1748 | 0.59761
|  | 1:09 | 5.49 | 0.11481 | 0.59761
|  | 1:09 | 5.4911 | 0.054818 | 0.59761
|  | 1:09 | 5.4922 | -0.0065868 | 0.59761
|  | 1:09 | 5.4933 | -0.068462 | 0.5976
|  | 1:09 | 5.4944 | -0.13034 | 0.5976
|  | 1:09 | 5.4956 | -0.17611 | 0.5976
|  | 1:09 | 5.4967 | -0.22189 | 0.5976
|  | 1:09 | 5.4978 | -0.26715 | 0.59759
|  | 1:09 | 5.4989 | -0.3119 | 0.59759
|  | 1:09 | 5.5 | -0.35665 | 0.59759
|  | 1:09 | 5.5011 | -0.39577 | 0.59759
|  | 1:10 | 5.5022 | -0.43489 | 0.59759
|  | 1:10 | 5.5033 | -0.45765 | 0.59758
|  | 1:10 | 5.5044 | -0.46406 | 0.59758
|  | 1:10 | 5.5056 | -0.47047 | 0.59758
|  | 1:10 | 5.5067 | -0.45239 | 0.59758
|  | 1:10 | 5.5078 | -0.4343 | 0.59757
|  | 1:10 | 5.5089 | -0.42879 | 0.59757
|  | 1:10 | 5.51 | -0.43588 | 0.59757
|  | 1:10 | 5.5111 | -0.44296 | 0.59757
|  | 1:10 | 5.5122 | -0.44646 | 0.59756
|  | 1:10 | 5.5133 | -0.44997 | 0.59756
|  | 1:10 | 5.5144 | -0.44712 | 0.59756
|  | 1:10 | 5.5156 | -0.43794 | 0.59756
|  | 1:10 | 5.5167 | -0.42875 | 0.59756
|  | 1:10 | 5.5178 | -0.42518 | 0.59755
|  | 1:11 | 5.5189 | -0.42161 | 0.59755
|  | 1:11 | 5.52 | -0.42556 | 0.59755
|  | 1:11 | 5.5211 | -0.43704 | 0.59755
|  | 1:11 | 5.5222 | -0.44852 | 0.59754
|  | 1:11 | 5.5233 | -0.44164 | 0.59754
|  | 1:11 | 5.5244 | -0.43475 | 0.59754
|  | 1:11 | 5.5256 | -0.42925 | 0.59754
|  | 1:11 | 5.5267 | -0.42513 | 0.59753
|  | 1:11 | 5.5278 | -0.421 | 0.59753
|  | 1:11 | 5.5289 | -0.40086 | 0.59753
|  | 1:11 | 5.53 | -0.38072 | 0.59753
|  | 1:11 | 5.5311 | -0.36457 | 0.59753
|  | 1:11 | 5.5322 | -0.35242 | 0.59752
|  | 1:11 | 5.5333 | -0.34187 | 0.59752
|  | 1:11 | 5.5344 | -0.33616 | 0.59752
|  | 1:12 | 5.5356 | -0.33044 | 0.59752
|  | 1:12 | 5.5367 | -0.31632 | 0.59751
|  | 1:12 | 5.5378 | -0.29381 | 0.59751
|  | 1:12 | 5.5389 | -0.2713 | 0.59751
|  | 1:12 | 5.54 | -0.25262 | 0.59751
|  | 1:12 | 5.5411 | -0.23394 | 0.5975
|  | 1:12 | 5.5422 | -0.21066 | 0.5975
|  | 1:12 | 5.5433 | -0.18278 | 0.5975
|  | 1:12 | 5.5444 | -0.1549 | 0.5975
|  | 1:12 | 5.5456 | -0.1598 | 0.5975
|  | 1:12 | 5.5467 | -0.1647 | 0.59749
|  | 1:12 | 5.5478 | -0.16862 | 0.59749
|  | 1:12 | 5.5489 | -0.17156 | 0.59749
|  | 1:12 | 5.55 | -0.17451 | 0.59749
|  | 1:12 | 5.5511 | -0.16854 | 0.59748
|  | 1:13 | 5.5522 | -0.16258 | 0.59748
|  | 1:13 | 5.5533 | -0.16124 | 0.59748
|  | 1:13 | 5.5544 | -0.16454 | 0.59748
|  | 1:13 | 5.5556 | -0.16783 | 0.59747
|  | 1:13 | 5.5567 | -0.15843 | 0.59747
|  | 1:13 | 5.5578 | -0.14903 | 0.59747
|  | 1:13 | 5.5589 | -0.12965 | 0.59747
|  | 1:13 | 5.56 | -0.10029 | 0.59747
|  | 1:13 | 5.5611 | -0.070943 | 0.59746
|  | 1:13 | 5.5622 | -0.066805 | 0.59746
|  | 1:13 | 5.5633 | -0.062667 | 0.59746
|  | 1:13 | 5.5644 | -0.054492 | 0.59746
|  | 1:13 | 5.5656 | -0.042281 | 0.59745
|  | 1:13 | 5.5667 | -0.030069 | 0.59745
|  | 1:13 | 5.5678 | -0.017858 | 0.59745
|  | 1:14 | 5.5689 | 0.0074794 | 0.59745
|  | 1:14 | 5.57 | 0.030449 | 0.59744
|  | 1:14 | 5.5711 | 0.046317 | 0.59744
|  | 1:14 | 5.5722 | 0.062185 | 0.59744
|  | 1:14 | 5.5733 | 0.082672 | 0.59744
|  | 1:14 | 5.5744 | 0.10316 | 0.59744
|  | 1:14 | 5.5756 | 0.12318 | 0.59743
|  | 1:14 | 5.5767 | 0.14273 | 0.59743
|  | 1:14 | 5.5778 | 0.16229 | 0.59743
|  | 1:14 | 5.5789 | 0.17597 | 0.59743
|  | 1:14 | 5.58 | 0.18965 | 0.59742
|  | 1:14 | 5.5811 | 0.21106 | 0.59742
|  | 1:14 | 5.5822 | 0.24018 | 0.59742
|  | 1:14 | 5.5833 | 0.2693 | 0.59742
|  | 1:14 | 5.5844 | 0.28985 | 0.59741
|  | 1:15 | 5.5856 | 0.3104 | 0.59741
|  | 1:15 | 5.5867 | 0.32411 | 0.59741
|  | 1:15 | 5.5878 | 0.33098 | 0.59741
|  | 1:15 | 5.5889 | 0.33785 | 0.59741
|  | 1:15 | 5.59 | 0.3406 | 0.5974
|  | 1:15 | 5.5911 | 0.34335 | 0.5974
|  | 1:15 | 5.5922 | 0.34433 | 0.5974
|  | 1:15 | 5.5933 | 0.34356 | 0.5974
|  | 1:15 | 5.5944 | 0.34278 | 0.59739
|  | 1:15 | 5.5956 | 0.3594 | 0.59739
|  | 1:15 | 5.5967 | 0.37602 | 0.59739
|  | 1:15 | 5.5978 | 0.39263 | 0.59739
|  | 1:15 | 5.5989 | 0.40925 | 0.59738
|  | 1:15 | 5.6 | 0.42587 | 0.59738
|  | 1:15 | 5.6011 | 0.4182 | 0.59738
|  | 1:16 | 5.6022 | 0.41053 | 0.59738
|  | 1:16 | 5.6033 | 0.39842 | 0.59737
|  | 1:16 | 5.6044 | 0.38187 | 0.59737
|  | 1:16 | 5.6056 | 0.36532 | 0.59737
|  | 1:16 | 5.6067 | 0.33087 | 0.59737
|  | 1:16 | 5.6078 | 0.29642 | 0.59737
|  | 1:16 | 5.6089 | 0.28083 | 0.59736
|  | 1:16 | 5.61 | 0.28412 | 0.59736
|  | 1:16 | 5.6111 | 0.2874 | 0.59736
|  | 1:16 | 5.6122 | 0.2724 | 0.59736
|  | 1:16 | 5.6133 | 0.2574 | 0.59735
|  | 1:16 | 5.6144 | 0.2361 | 0.59735
|  | 1:16 | 5.6156 | 0.2085 | 0.59735
|  | 1:16 | 5.6167 | 0.18089 | 0.59735
|  | 1:16 | 5.6178 | 0.14929 | 0.59734
|  | 1:17 | 5.6189 | 0.11769 | 0.59734
|  | 1:17 | 5.62 | 0.10424 | 0.59734
|  | 1:17 | 5.6211 | 0.096831 | 0.59734
|  | 1:17 | 5.6222 | 0.089426 | 0.59734
|  | 1:17 | 5.6233 | 0.072852 | 0.59733
|  | 1:17 | 5.6244 | 0.056277 | 0.59733
|  | 1:17 | 5.6256 | 0.041294 | 0.59733
|  | 1:17 | 5.6267 | 0.027902 | 0.59733
|  | 1:17 | 5.6278 | 0.01451 | 0.59732
|  | 1:17 | 5.6289 | -0.0091688 | 0.59732
|  | 1:17 | 5.63 | -0.032848 | 0.59732
|  | 1:17 | 5.6311 | -0.066966 | 0.59732
|  | 1:17 | 5.6322 | -0.11152 | 0.59731
|  | 1:17 | 5.6333 | -0.15608 | 0.59731
|  | 1:17 | 5.6344 | -0.17782 | 0.59731
|  | 1:18 | 5.6356 | -0.19956 | 0.59731
|  | 1:18 | 5.6367 | -0.21505 | 0.59731
|  | 1:18 | 5.6378 | -0.2243 | 0.5973
|  | 1:18 | 5.6389 | -0.23485 | 0.5973
|  | 1:18 | 5.64 | -0.24933 | 0.5973
|  | 1:18 | 5.6411 | -0.26381 | 0.5973
|  | 1:18 | 5.6422 | -0.28585 | 0.59729
|  | 1:18 | 5.6433 | -0.31041 | 0.59729
|  | 1:18 | 5.6444 | -0.33498 | 0.59729
|  | 1:18 | 5.6456 | -0.35433 | 0.59729
|  | 1:18 | 5.6467 | -0.37369 | 0.59728
|  | 1:18 | 5.6478 | -0.38334 | 0.59728
|  | 1:18 | 5.6489 | -0.38329 | 0.59728
|  | 1:18 | 5.65 | -0.38325 | 0.59728
|  | 1:18 | 5.6511 | -0.37177 | 0.59728
|  | 1:19 | 5.6522 | -0.36028 | 0.59727
|  | 1:19 | 5.6533 | -0.34955 | 0.59727
|  | 1:19 | 5.6544 | -0.33956 | 0.59727
|  | 1:19 | 5.6556 | -0.32957 | 0.59727
|  | 1:19 | 5.6567 | -0.32282 | 0.59726
|  | 1:19 | 5.6578 | -0.31608 | 0.59726
|  | 1:19 | 5.6589 | -0.30933 | 0.59726
|  | 1:19 | 5.66 | -0.30258 | 0.59726
|  | 1:19 | 5.6611 | -0.2977 | 0.59725
|  | 1:19 | 5.6622 | -0.29843 | 0.59725
|  | 1:19 | 5.6633 | -0.29916 | 0.59725
|  | 1:19 | 5.6644 | -0.3059 | 0.59725
|  | 1:19 | 5.6656 | -0.31865 | 0.59725
|  | 1:19 | 5.6667 | -0.33141 | 0.59724
|  | 1:19 | 5.6678 | -0.34928 | 0.59724
|  | 1:20 | 5.6689 | -0.36715 | 0.59724
|  | 1:20 | 5.67 | -0.36743 | 0.59724
|  | 1:20 | 5.6711 | -0.35014 | 0.59723
|  | 1:20 | 5.6722 | -0.33284 | 0.59723
|  | 1:20 | 5.6733 | -0.32614 | 0.59723
|  | 1:20 | 5.6744 | -0.31945 | 0.59723
|  | 1:20 | 5.6756 | -0.32347 | 0.59722
|  | 1:20 | 5.6767 | -0.33105 | 0.59722
|  | 1:20 | 5.6778 | -0.33863 | 0.59722
|  | 1:20 | 5.6789 | -0.34742 | 0.59722
|  | 1:20 | 5.68 | -0.35621 | 0.59722
|  | 1:20 | 5.6811 | -0.35525 | 0.59721
|  | 1:20 | 5.6822 | -0.34453 | 0.59721
|  | 1:20 | 5.6833 | -0.33382 | 0.59721
|  | 1:20 | 5.6844 | -0.32408 | 0.59721
|  | 1:21 | 5.6856 | -0.31435 | 0.5972
|  | 1:21 | 5.6867 | -0.29629 | 0.5972
|  | 1:21 | 5.6878 | -0.2699 | 0.5972
|  | 1:21 | 5.6889 | -0.24351 | 0.5972
|  | 1:21 | 5.69 | -0.22981 | 0.59719
|  | 1:21 | 5.6911 | -0.21611 | 0.59719
|  | 1:21 | 5.6922 | -0.19988 | 0.59719
|  | 1:21 | 5.6933 | -0.18112 | 0.59719
|  | 1:21 | 5.6944 | -0.16235 | 0.59719
|  | 1:21 | 5.6956 | -0.16142 | 0.59718
|  | 1:21 | 5.6967 | -0.16049 | 0.59718
|  | 1:21 | 5.6978 | -0.15389 | 0.59718
|  | 1:21 | 5.6989 | -0.14164 | 0.59718
|  | 1:21 | 5.7 | -0.12939 | 0.59717
|  | 1:21 | 5.7011 | -0.12526 | 0.59717
|  | 1:22 | 5.7022 | -0.12113 | 0.59717
|  | 1:22 | 5.7033 | -0.12313 | 0.59717
|  | 1:22 | 5.7044 | -0.13125 | 0.59716
|  | 1:22 | 5.7056 | -0.13938 | 0.59716
|  | 1:22 | 5.7067 | -0.13197 | 0.59716
|  | 1:22 | 5.7078 | -0.12456 | 0.59716
|  | 1:22 | 5.7089 | -0.11274 | 0.59716
|  | 1:22 | 5.71 | -0.096521 | 0.59715
|  | 1:22 | 5.7111 | -0.080302 | 0.59715
|  | 1:22 | 5.7122 | -0.054155 | 0.59715
|  | 1:22 | 5.7133 | -0.028008 | 0.59715
|  | 1:22 | 5.7144 | -0.0045076 | 0.59714
|  | 1:22 | 5.7156 | 0.016347 | 0.59714
|  | 1:22 | 5.7167 | 0.037201 | 0.59714
|  | 1:22 | 5.7178 | 0.038561 | 0.59714
|  | 1:23 | 5.7189 | 0.039921 | 0.59713
|  | 1:23 | 5.72 | 0.04462 | 0.59713
|  | 1:23 | 5.7211 | 0.052657 | 0.59713
|  | 1:23 | 5.7222 | 0.060695 | 0.59713
|  | 1:23 | 5.7233 | 0.062016 | 0.59712
|  | 1:23 | 5.7244 | 0.063337 | 0.59712
|  | 1:23 | 5.7256 | 0.059152 | 0.59712
|  | 1:23 | 5.7267 | 0.049461 | 0.59712
|  | 1:23 | 5.7278 | 0.039771 | 0.59712
|  | 1:23 | 5.7289 | 0.03008 | 0.59711
|  | 1:23 | 5.73 | 0.02039 | 0.59711
|  | 1:23 | 5.7311 | 0.012533 | 0.59711
|  | 1:23 | 5.7322 | 0.00651 | 0.59711
|  | 1:23 | 5.7333 | 0.00048686 | 0.5971
|  | 1:23 | 5.7344 | -0.0055363 | 0.5971
|  | 1:24 | 5.7356 | -0.028667 | 0.5971
|  | 1:24 | 5.7367 | -0.055754 | 0.5971
|  | 1:24 | 5.7378 | -0.094714 | 0.59709
|  | 1:24 | 5.7389 | -0.13367 | 0.59709
|  | 1:24 | 5.74 | -0.1564 | 0.59709
|  | 1:24 | 5.7411 | -0.17912 | 0.59709
|  | 1:24 | 5.7422 | -0.20465 | 0.59709
|  | 1:24 | 5.7433 | -0.23296 | 0.59708
|  | 1:24 | 5.7444 | -0.26128 | 0.59708
|  | 1:24 | 5.7456 | -0.28713 | 0.59708
|  | 1:24 | 5.7467 | -0.31299 | 0.59708
|  | 1:24 | 5.7478 | -0.3269 | 0.59707
|  | 1:24 | 5.7489 | -0.32887 | 0.59707
|  | 1:24 | 5.75 | -0.33084 | 0.59707
|  | 1:24 | 5.7511 | -0.34417 | 0.59707
|  | 1:25 | 5.7522 | -0.35749 | 0.59706
|  | 1:25 | 5.7533 | -0.36829 | 0.59706
|  | 1:25 | 5.7544 | -0.37657 | 0.59706
|  | 1:25 | 5.7556 | -0.38484 | 0.59706
|  | 1:25 | 5.7567 | -0.39763 | 0.59706
|  | 1:25 | 5.7578 | -0.41043 | 0.59705
|  | 1:25 | 5.7589 | -0.42784 | 0.59705
|  | 1:25 | 5.76 | -0.44987 | 0.59705
|  | 1:25 | 5.7611 | -0.4719 | 0.59705
|  | 1:25 | 5.7622 | -0.49075 | 0.59704
|  | 1:25 | 5.7633 | -0.50959 | 0.59704
|  | 1:25 | 5.7644 | -0.5272 | 0.59704
|  | 1:25 | 5.7656 | -0.54355 | 0.59704
|  | 1:25 | 5.7667 | -0.5599 | 0.59703
|  | 1:25 | 5.7678 | -0.58263 | 0.59703
|  | 1:26 | 5.7689 | -0.60537 | 0.59703
|  | 1:26 | 5.77 | -0.62365 | 0.59703
|  | 1:26 | 5.7711 | -0.63747 | 0.59703
|  | 1:26 | 5.7722 | -0.65129 | 0.59702
|  | 1:26 | 5.7733 | -0.65879 | 0.59702
|  | 1:26 | 5.7744 | -0.66629 | 0.59702
|  | 1:26 | 5.7756 | -0.67986 | 0.59702
|  | 1:26 | 5.7767 | -0.6995 | 0.59701
|  | 1:26 | 5.7778 | -0.71913 | 0.59701
|  | 1:26 | 5.7789 | -0.73168 | 0.59701
|  | 1:26 | 5.78 | -0.74423 | 0.59701
|  | 1:26 | 5.7811 | -0.7505 | 0.597
|  | 1:26 | 5.7822 | -0.75049 | 0.597
|  | 1:26 | 5.7833 | -0.75048 | 0.597
|  | 1:26 | 5.7844 | -0.73916 | 0.597
|  | 1:27 | 5.7856 | -0.72783 | 0.597
|  | 1:27 | 5.7867 | -0.70987 | 0.59699
|  | 1:27 | 5.7878 | -0.68526 | 0.59699
|  | 1:27 | 5.7889 | -0.66066 | 0.59699
|  | 1:27 | 5.79 | -0.6495 | 0.59699
|  | 1:27 | 5.7911 | -0.63834 | 0.59698
|  | 1:27 | 5.7922 | -0.61665 | 0.59698
|  | 1:27 | 5.7933 | -0.58443 | 0.59698
|  | 1:27 | 5.7944 | -0.55221 | 0.59698
|  | 1:27 | 5.7956 | -0.51541 | 0.59697
|  | 1:27 | 5.7967 | -0.47861 | 0.59697
|  | 1:27 | 5.7978 | -0.44523 | 0.59697
|  | 1:27 | 5.7989 | -0.41524 | 0.59697
|  | 1:27 | 5.8 | -0.38526 | 0.59697
|  | 1:27 | 5.8011 | -0.37899 | 0.59696
|  | 1:28 | 5.8022 | -0.37271 | 0.59696
|  | 1:28 | 5.8033 | -0.37159 | 0.59696
|  | 1:28 | 5.8044 | -0.37563 | 0.59696
|  | 1:28 | 5.8056 | -0.37966 | 0.59695
|  | 1:28 | 5.8067 | -0.36377 | 0.59695
|  | 1:28 | 5.8078 | -0.34788 | 0.59695
|  | 1:28 | 5.8089 | -0.32774 | 0.59695
|  | 1:28 | 5.81 | -0.30335 | 0.59694
|  | 1:28 | 5.8111 | -0.27896 | 0.59694
|  | 1:28 | 5.8122 | -0.25074 | 0.59694
|  | 1:28 | 5.8133 | -0.22252 | 0.59694
|  | 1:28 | 5.8144 | -0.19509 | 0.59694
|  | 1:28 | 5.8156 | -0.16792 | 0.59693
|  | 1:28 | 5.8167 | -0.14272 | 0.59693
|  | 1:28 | 5.8178 | -0.12345 | 0.59693
|  | 1:29 | 5.8189 | -0.10417 | 0.59693
|  | 1:29 | 5.82 | -0.087397 | 0.59692
|  | 1:29 | 5.8211 | -0.07313 | 0.59692
|  | 1:29 | 5.8222 | -0.058863 | 0.59692
|  | 1:29 | 5.8233 | -0.061269 | 0.59692
|  | 1:29 | 5.8244 | -0.063676 | 0.59691
|  | 1:29 | 5.8256 | -0.065522 | 0.59691
|  | 1:29 | 5.8267 | -0.066808 | 0.59691
|  | 1:29 | 5.8278 | -0.068094 | 0.59691
|  | 1:29 | 5.8289 | -0.075492 | 0.59691
|  | 1:29 | 5.83 | -0.08289 | 0.5969
|  | 1:29 | 5.8311 | -0.09073 | 0.5969
|  | 1:29 | 5.8322 | -0.099014 | 0.5969
|  | 1:29 | 5.8333 | -0.1073 | 0.5969
|  | 1:29 | 5.8344 | -0.089359 | 0.59689
|  | 1:30 | 5.8356 | -0.071421 | 0.59689
|  | 1:30 | 5.8367 | -0.049309 | 0.59689
|  | 1:30 | 5.8378 | -0.023023 | 0.59689
|  | 1:30 | 5.8389 | 0.0032623 | 0.59688
|  | 1:30 | 5.84 | 0.016532 | 0.59688
|  | 1:30 | 5.8411 | 0.029801 | 0.59688
|  | 1:30 | 5.8422 | 0.036497 | 0.59688
|  | 1:30 | 5.8433 | 0.03662 | 0.59687
|  | 1:30 | 5.8444 | 0.036742 | 0.59687
|  | 1:30 | 5.8456 | 0.031934 | 0.59687
|  | 1:30 | 5.8467 | 0.027126 | 0.59687
|  | 1:30 | 5.8478 | 0.038487 | 0.59687
|  | 1:30 | 5.8489 | 0.06602 | 0.59686
|  | 1:30 | 5.85 | 0.093552 | 0.59686
|  | 1:30 | 5.8511 | 0.12924 | 0.59686
|  | 1:31 | 5.8522 | 0.16492 | 0.59686
|  | 1:31 | 5.8533 | 0.19135 | 0.59685
|  | 1:31 | 5.8544 | 0.20853 | 0.59685
|  | 1:31 | 5.8556 | 0.2257 | 0.59685
|  | 1:31 | 5.8567 | 0.2251 | 0.59685
|  | 1:31 | 5.8578 | 0.22449 | 0.59684
|  | 1:31 | 5.8589 | 0.21902 | 0.59684
|  | 1:31 | 5.86 | 0.2087 | 0.59684
|  | 1:31 | 5.8611 | 0.19838 | 0.59684
|  | 1:31 | 5.8622 | 0.17104 | 0.59684
|  | 1:31 | 5.8633 | 0.14371 | 0.59683
|  | 1:31 | 5.8644 | 0.12041 | 0.59683
|  | 1:31 | 5.8656 | 0.10116 | 0.59683
|  | 1:31 | 5.8667 | 0.081902 | 0.59683
|  | 1:31 | 5.8678 | 0.099815 | 0.59682
|  | 1:32 | 5.8689 | 0.11773 | 0.59682
|  | 1:32 | 5.87 | 0.13342 | 0.59682
|  | 1:32 | 5.8711 | 0.14689 | 0.59682
|  | 1:32 | 5.8722 | 0.16036 | 0.59681
|  | 1:32 | 5.8733 | 0.17384 | 0.59681
|  | 1:32 | 5.8744 | 0.18731 | 0.59681
|  | 1:32 | 5.8756 | 0.20476 | 0.59681
|  | 1:32 | 5.8767 | 0.22619 | 0.59681
|  | 1:32 | 5.8778 | 0.24763 | 0.5968
|  | 1:32 | 5.8789 | 0.26643 | 0.5968
|  | 1:32 | 5.88 | 0.28523 | 0.5968
|  | 1:32 | 5.8811 | 0.29984 | 0.5968
|  | 1:32 | 5.8822 | 0.31025 | 0.59679
|  | 1:32 | 5.8833 | 0.32066 | 0.59679
|  | 1:32 | 5.8844 | 0.33434 | 0.59679
|  | 1:33 | 5.8856 | 0.34802 | 0.59679
|  | 1:33 | 5.8867 | 0.36502 | 0.59678
|  | 1:33 | 5.8878 | 0.38533 | 0.59678
|  | 1:33 | 5.8889 | 0.40565 | 0.59678
|  | 1:33 | 5.89 | 0.42159 | 0.59678
|  | 1:33 | 5.8911 | 0.43753 | 0.59678
|  | 1:33 | 5.8922 | 0.45058 | 0.59677
|  | 1:33 | 5.8933 | 0.46075 | 0.59677
|  | 1:33 | 5.8944 | 0.47091 | 0.59677
|  | 1:33 | 5.8956 | 0.47039 | 0.59677
|  | 1:33 | 5.8967 | 0.46987 | 0.59676
|  | 1:33 | 5.8978 | 0.46317 | 0.59676
|  | 1:33 | 5.8989 | 0.45441 | 0.59676
|  | 1:33 | 5.9 | 0.44565 | 0.59676
|  | 1:33 | 5.9011 | 0.42328 | 0.59675
|  | 1:34 | 5.9022 | 0.4009 | 0.59675
|  | 1:34 | 5.9033 | 0.38572 | 0.59675
|  | 1:34 | 5.9044 | 0.39211 | 0.59675
|  | 1:34 | 5.9056 | 0.3985 | 0.59675
|  | 1:34 | 5.9067 | 0.4237 | 0.59674
|  | 1:34 | 5.9078 | 0.4489 | 0.59674
|  | 1:34 | 5.9089 | 0.46088 | 0.59674
|  | 1:34 | 5.91 | 0.45964 | 0.59674
|  | 1:34 | 5.9111 | 0.45841 | 0.59673
|  | 1:34 | 5.9122 | 0.4475 | 0.59673
|  | 1:34 | 5.9133 | 0.43659 | 0.59673
|  | 1:34 | 5.9144 | 0.42325 | 0.59673
|  | 1:34 | 5.9156 | 0.40749 | 0.59672
|  | 1:34 | 5.9167 | 0.39172 | 0.59672
|  | 1:34 | 5.9178 | 0.40531 | 0.59672
|  | 1:35 | 5.9189 | 0.4189 | 0.59672
|  | 1:35 | 5.92 | 0.43151 | 0.59672
|  | 1:35 | 5.9211 | 0.44314 | 0.59671
|  | 1:35 | 5.9222 | 0.45477 | 0.59671
|  | 1:35 | 5.9233 | 0.4521 | 0.59671
|  | 1:35 | 5.9244 | 0.44943 | 0.59671
|  | 1:35 | 5.9256 | 0.43991 | 0.5967
|  | 1:35 | 5.9267 | 0.42354 | 0.5967
|  | 1:35 | 5.9278 | 0.40717 | 0.5967
|  | 1:35 | 5.9289 | 0.40518 | 0.5967
|  | 1:35 | 5.93 | 0.40319 | 0.59669
|  | 1:35 | 5.9311 | 0.41374 | 0.59669
|  | 1:35 | 5.9322 | 0.43682 | 0.59669
|  | 1:35 | 5.9333 | 0.45991 | 0.59669
|  | 1:35 | 5.9344 | 0.48429 | 0.59669
|  | 1:36 | 5.9356 | 0.50867 | 0.59668
|  | 1:36 | 5.9367 | 0.52763 | 0.59668
|  | 1:36 | 5.9378 | 0.54478 | 0.59668
|  | 1:36 | 5.9389 | 0.56194 | 0.59668
|  | 1:36 | 5.94 | 0.57207 | 0.59667
|  | 1:36 | 5.9411 | 0.58221 | 0.59667
|  | 1:36 | 5.9422 | 0.58718 | 0.59667
|  | 1:36 | 5.9433 | 0.58698 | 0.59667
|  | 1:36 | 5.9444 | 0.58678 | 0.59666
|  | 1:36 | 5.9456 | 0.60128 | 0.59666
|  | 1:36 | 5.9467 | 0.61578 | 0.59666
|  | 1:36 | 5.9478 | 0.62143 | 0.59666
|  | 1:36 | 5.9489 | 0.61825 | 0.59666
|  | 1:36 | 5.95 | 0.61506 | 0.59665
|  | 1:36 | 5.9511 | 0.62239 | 0.59665
|  | 1:37 | 5.9522 | 0.62971 | 0.59665
|  | 1:37 | 5.9533 | 0.63355 | 0.59665
|  | 1:37 | 5.9544 | 0.6339 | 0.59664
|  | 1:37 | 5.9556 | 0.63907 | 0.59664
|  | 1:37 | 5.9567 | 0.65868 | 0.59664
|  | 1:37 | 5.9578 | 0.6783 | 0.59664
|  | 1:37 | 5.9589 | 0.69792 | 0.59663
|  | 1:37 | 5.96 | 0.71754 | 0.59663
|  | 1:37 | 5.9611 | 0.73715 | 0.59663
|  | 1:37 | 5.9622 | 0.75945 | 0.59663
|  | 1:37 | 5.9633 | 0.78175 | 0.59662
|  | 1:37 | 5.9644 | 0.79371 | 0.59662
|  | 1:37 | 5.9656 | 0.79532 | 0.59662
|  | 1:37 | 5.9667 | 0.79693 | 0.59662
|  | 1:37 | 5.9678 | 0.81251 | 0.59662
|  | 1:38 | 5.9689 | 0.82809 | 0.59661
|  | 1:38 | 5.97 | 0.83863 | 0.59661
|  | 1:38 | 5.9711 | 0.84413 | 0.59661
|  | 1:38 | 5.9722 | 0.84963 | 0.59661
|  | 1:38 | 5.9733 | 0.82497 | 0.5966
|  | 1:38 | 5.9744 | 0.8003 | 0.5966
|  | 1:38 | 5.9756 | 0.77953 | 0.5966
|  | 1:38 | 5.9767 | 0.76265 | 0.5966
|  | 1:38 | 5.9778 | 0.74578 | 0.59659
|  | 1:38 | 5.9789 | 0.7289 | 0.59659
|  | 1:38 | 5.98 | 0.71203 | 0.59659
|  | 1:38 | 5.9811 | 0.69599 | 0.59659
|  | 1:38 | 5.9822 | 0.68079 | 0.59659
|  | 1:38 | 5.9833 | 0.66559 | 0.59658
|  | 1:38 | 5.9844 | 0.65039 | 0.59658
|  | 1:39 | 5.9856 | 0.63519 | 0.59658
|  | 1:39 | 5.9867 | 0.6287 | 0.59658
|  | 1:39 | 5.9878 | 0.62511 | 0.59657
|  | 1:39 | 5.9889 | 0.62152 | 0.59657
|  | 1:39 | 5.99 | 0.60905 | 0.59657
|  | 1:39 | 5.9911 | 0.59658 | 0.59657
|  | 1:39 | 5.9922 | 0.59451 | 0.59656
|  | 1:39 | 5.9933 | 0.60285 | 0.59656
|  | 1:39 | 5.9944 | 0.61119 | 0.59656
|  | 1:39 | 5.9956 | 0.62747 | 0.59656
|  | 1:39 | 5.9967 | 0.64374 | 0.59656
|  | 1:39 | 5.9978 | 0.64699 | 0.59655
|  | 1:39 | 5.9989 | 0.6372 | 0.59655
|  | 1:39 | 6 | 0.62494 | 0.59655
|  | 1:39 | 6.0011 | 0.60529 | 0.59655
|  | 1:40 | 6.0022 | 0.58564 | 0.59654
|  | 1:40 | 6.0033 | 0.56408 | 0.59654
|  | 1:40 | 6.0044 | 0.54061 | 0.59654
|  | 1:40 | 6.0056 | 0.51713 | 0.59654
|  | 1:40 | 6.0067 | 0.50205 | 0.59653
|  | 1:40 | 6.0078 | 0.48696 | 0.59653
|  | 1:40 | 6.0089 | 0.46771 | 0.59653
|  | 1:40 | 6.01 | 0.4443 | 0.59653
|  | 1:40 | 6.0111 | 0.4209 | 0.59653
|  | 1:40 | 6.0122 | 0.38558 | 0.59652
|  | 1:40 | 6.0133 | 0.35026 | 0.59652
|  | 1:40 | 6.0144 | 0.31233 | 0.59652
|  | 1:40 | 6.0156 | 0.27179 | 0.59652
|  | 1:40 | 6.0167 | 0.23124 | 0.59651
|  | 1:40 | 6.0178 | 0.20065 | 0.59651
|  | 1:41 | 6.0189 | 0.17005 | 0.59651
|  | 1:41 | 6.02 | 0.14077 | 0.59651
|  | 1:41 | 6.0211 | 0.11281 | 0.5965
|  | 1:41 | 6.0222 | 0.084842 | 0.5965
|  | 1:41 | 6.0233 | 0.038603 | 0.5965
|  | 1:41 | 6.0244 | -0.0076366 | 0.5965
|  | 1:41 | 6.0256 | -0.047739 | 0.5965
|  | 1:41 | 6.0267 | -0.081703 | 0.59649
|  | 1:41 | 6.0278 | -0.11567 | 0.59649
|  | 1:41 | 6.0289 | -0.13646 | 0.59649
|  | 1:41 | 6.03 | -0.15725 | 0.59649
|  | 1:41 | 6.0311 | -0.18325 | 0.59648
|  | 1:41 | 6.0322 | -0.21444 | 0.59648
|  | 1:41 | 6.0333 | -0.24563 | 0.59648
|  | 1:41 | 6.0344 | -0.2745 | 0.59648
|  | 1:42 | 6.0356 | -0.30336 | 0.59647
|  | 1:42 | 6.0367 | -0.34175 | 0.59647
|  | 1:42 | 6.0378 | -0.38967 | 0.59647
|  | 1:42 | 6.0389 | -0.42638 | 0.59647
|  | 1:42 | 6.04 | -0.42948 | 0.59647
|  | 1:42 | 6.0411 | -0.43258 | 0.59646
|  | 1:42 | 6.0422 | -0.44921 | 0.59646
|  | 1:42 | 6.0433 | -0.47935 | 0.59646
|  | 1:42 | 6.0444 | -0.5095 | 0.59646
|  | 1:42 | 6.0456 | -0.53188 | 0.59645
|  | 1:42 | 6.0467 | -0.55427 | 0.59645
|  | 1:42 | 6.0478 | -0.57911 | 0.59645
|  | 1:42 | 6.0489 | -0.60641 | 0.59645
|  | 1:42 | 6.05 | -0.63371 | 0.59644
|  | 1:42 | 6.0511 | -0.64927 | 0.59644
|  | 1:43 | 6.0522 | -0.66484 | 0.59644
|  | 1:43 | 6.0533 | -0.6804 | 0.59644
|  | 1:43 | 6.0544 | -0.69596 | 0.59644
|  | 1:43 | 6.0556 | -0.71153 | 0.59643
|  | 1:43 | 6.0567 | -0.72418 | 0.59643
|  | 1:43 | 6.0578 | -0.73684 | 0.59643
|  | 1:43 | 6.0589 | -0.73522 | 0.59643
|  | 1:43 | 6.06 | -0.71932 | 0.59642
|  | 1:43 | 6.0611 | -0.70341 | 0.59642
|  | 1:43 | 6.0622 | -0.67074 | 0.59642
|  | 1:43 | 6.0633 | -0.63806 | 0.59642
|  | 1:43 | 6.0644 | -0.60994 | 0.59641
|  | 1:43 | 6.0656 | -0.58635 | 0.59641
|  | 1:43 | 6.0667 | -0.56277 | 0.59641
|  | 1:43 | 6.0678 | -0.53527 | 0.59641
|  | 1:44 | 6.0689 | -0.50776 | 0.59641
|  | 1:44 | 6.07 | -0.48763 | 0.5964
|  | 1:44 | 6.0711 | -0.48964 | 0.5964
|  | 1:44 | 6.0722 | -0.49165 | 0.5964
|  | 1:44 | 6.0733 | -0.49001 | 0.5964
|  | 1:44 | 6.0744 | -0.48837 | 0.59639
|  | 1:44 | 6.0756 | -0.48899 | 0.59639
|  | 1:44 | 6.0767 | -0.49188 | 0.59639
|  | 1:44 | 6.0778 | -0.49352 | 0.59639
|  | 1:44 | 6.0789 | -0.49142 | 0.59638
|  | 1:44 | 6.08 | -0.48932 | 0.59638
|  | 1:44 | 6.0811 | -0.49175 | 0.59638
|  | 1:44 | 6.0822 | -0.4987 | 0.59638
|  | 1:44 | 6.0833 | -0.50565 | 0.59637
|  | 1:44 | 6.0844 | -0.50288 | 0.59637
|  | 1:45 | 6.0856 | -0.50011 | 0.59637
|  | 1:45 | 6.0867 | -0.48826 | 0.59637
|  | 1:45 | 6.0878 | -0.46731 | 0.59637
|  | 1:45 | 6.0889 | -0.44636 | 0.59636
|  | 1:45 | 6.09 | -0.413 | 0.59636
|  | 1:45 | 6.0911 | -0.37965 | 0.59636
|  | 1:45 | 6.0922 | -0.35026 | 0.59636
|  | 1:45 | 6.0933 | -0.32485 | 0.59635
|  | 1:45 | 6.0944 | -0.29944 | 0.59635
|  | 1:45 | 6.0956 | -0.27642 | 0.59635
|  | 1:45 | 6.0967 | -0.2534 | 0.59635
|  | 1:45 | 6.0978 | -0.236 | 0.59634
|  | 1:45 | 6.0989 | -0.22421 | 0.59634
|  | 1:45 | 6.1 | -0.21242 | 0.59634
|  | 1:45 | 6.1011 | -0.18995 | 0.59634
|  | 1:46 | 6.1022 | -0.16749 | 0.59634
|  | 1:46 | 6.1033 | -0.14283 | 0.59633
|  | 1:46 | 6.1044 | -0.11597 | 0.59633
|  | 1:46 | 6.1056 | -0.089118 | 0.59633
|  | 1:46 | 6.1067 | -0.051508 | 0.59633
|  | 1:46 | 6.1078 | -0.013898 | 0.59632
|  | 1:46 | 6.1089 | 0.024607 | 0.59632
|  | 1:46 | 6.11 | 0.064006 | 0.59632
|  | 1:46 | 6.1111 | 0.1034 | 0.59632
|  | 1:46 | 6.1122 | 0.12872 | 0.59631
|  | 1:46 | 6.1133 | 0.15403 | 0.59631
|  | 1:46 | 6.1144 | 0.16833 | 0.59631
|  | 1:46 | 6.1156 | 0.17161 | 0.59631
|  | 1:46 | 6.1167 | 0.1749 | 0.59631
|  | 1:46 | 6.1178 | 0.19225 | 0.5963
|  | 1:47 | 6.1189 | 0.2096 | 0.5963
|  | 1:47 | 6.12 | 0.23125 | 0.5963
|  | 1:47 | 6.1211 | 0.25433 | 0.5963
|  | 1:47 | 6.1222 | 0.28118 | 0.59629
|  | 1:47 | 6.1233 | 0.3193 | 0.59629
|  | 1:47 | 6.1244 | 0.35742 | 0.59629
|  | 1:47 | 6.1256 | 0.37481 | 0.59629
|  | 1:47 | 6.1267 | 0.37146 | 0.59628
|  | 1:47 | 6.1278 | 0.36812 | 0.59628
|  | 1:47 | 6.1289 | 0.36814 | 0.59628
|  | 1:47 | 6.13 | 0.36817 | 0.59628
|  | 1:47 | 6.1311 | 0.36493 | 0.59628
|  | 1:47 | 6.1322 | 0.35842 | 0.59627
|  | 1:47 | 6.1333 | 0.35192 | 0.59627
|  | 1:47 | 6.1344 | 0.35745 | 0.59627
|  | 1:48 | 6.1356 | 0.36298 | 0.59627
|  | 1:48 | 6.1367 | 0.38439 | 0.59626
|  | 1:48 | 6.1378 | 0.42166 | 0.59626
|  | 1:48 | 6.1389 | 0.45893 | 0.59626
|  | 1:48 | 6.14 | 0.50834 | 0.59626
|  | 1:48 | 6.1411 | 0.55774 | 0.59625
|  | 1:48 | 6.1422 | 0.59714 | 0.59625
|  | 1:48 | 6.1433 | 0.62655 | 0.59625
|  | 1:48 | 6.1444 | 0.65595 | 0.59625
|  | 1:48 | 6.1456 | 0.68535 | 0.59625
|  | 1:48 | 6.1467 | 0.71475 | 0.59624
|  | 1:48 | 6.1478 | 0.7405 | 0.59624
|  | 1:48 | 6.1489 | 0.7626 | 0.59624
|  | 1:48 | 6.15 | 0.7847 | 0.59624
|  | 1:48 | 6.1511 | 0.78996 | 0.59623
|  | 1:49 | 6.1522 | 0.79522 | 0.59623
|  | 1:49 | 6.1533 | 0.80048 | 0.59623
|  | 1:49 | 6.1544 | 0.80574 | 0.59623
|  | 1:49 | 6.1556 | 0.811 | 0.59622
|  | 1:49 | 6.1567 | 0.80302 | 0.59622
|  | 1:49 | 6.1578 | 0.79504 | 0.59622
|  | 1:49 | 6.1589 | 0.78335 | 0.59622
|  | 1:49 | 6.16 | 0.76794 | 0.59622
|  | 1:49 | 6.1611 | 0.75254 | 0.59621
|  | 1:49 | 6.1622 | 0.73713 | 0.59621
|  | 1:49 | 6.1633 | 0.72173 | 0.59621
|  | 1:49 | 6.1644 | 0.70357 | 0.59621
|  | 1:49 | 6.1656 | 0.68266 | 0.5962
|  | 1:49 | 6.1667 | 0.66175 | 0.5962
|  | 1:49 | 6.1678 | 0.62242 | 0.5962
|  | 1:50 | 6.1689 | 0.58309 | 0.5962
|  | 1:50 | 6.17 | 0.54171 | 0.59619
|  | 1:50 | 6.1711 | 0.49829 | 0.59619
|  | 1:50 | 6.1722 | 0.45486 | 0.59619
|  | 1:50 | 6.1733 | 0.42925 | 0.59619
|  | 1:50 | 6.1744 | 0.40363 | 0.59619
|  | 1:50 | 6.1756 | 0.37379 | 0.59618
|  | 1:50 | 6.1767 | 0.33971 | 0.59618
|  | 1:50 | 6.1778 | 0.30564 | 0.59618
|  | 1:50 | 6.1789 | 0.27379 | 0.59618
|  | 1:50 | 6.18 | 0.24194 | 0.59617
|  | 1:50 | 6.1811 | 0.22435 | 0.59617
|  | 1:50 | 6.1822 | 0.22102 | 0.59617
|  | 1:50 | 6.1833 | 0.21769 | 0.59617
|  | 1:50 | 6.1844 | 0.20566 | 0.59616
|  | 1:51 | 6.1856 | 0.19362 | 0.59616
|  | 1:51 | 6.1867 | 0.18466 | 0.59616
|  | 1:51 | 6.1878 | 0.17879 | 0.59616
|  | 1:51 | 6.1889 | 0.17291 | 0.59616
|  | 1:51 | 6.19 | 0.16918 | 0.59615
|  | 1:51 | 6.1911 | 0.16545 | 0.59615
|  | 1:51 | 6.1922 | 0.15742 | 0.59615
|  | 1:51 | 6.1933 | 0.14511 | 0.59615
|  | 1:51 | 6.1944 | 0.13279 | 0.59614
|  | 1:51 | 6.1956 | 0.11944 | 0.59614
|  | 1:51 | 6.1967 | 0.10609 | 0.59614
|  | 1:51 | 6.1978 | 0.093734 | 0.59614
|  | 1:51 | 6.1989 | 0.082374 | 0.59613
|  | 1:51 | 6.2 | 0.071013 | 0.59613
|  | 1:51 | 6.2011 | 0.066403 | 0.59613
|  | 1:52 | 6.2022 | 0.061792 | 0.59613
|  | 1:52 | 6.2033 | 0.057755 | 0.59612
|  | 1:52 | 6.2044 | 0.05429 | 0.59612
|  | 1:52 | 6.2056 | 0.050825 | 0.59612
|  | 1:52 | 6.2067 | 0.032276 | 0.59612
|  | 1:52 | 6.2078 | 0.013726 | 0.59612
|  | 1:52 | 6.2089 | -0.0155 | 0.59611
|  | 1:52 | 6.21 | -0.055402 | 0.59611
|  | 1:52 | 6.2111 | -0.095305 | 0.59611
|  | 1:52 | 6.2122 | -0.1476 | 0.59611
|  | 1:52 | 6.2133 | -0.19989 | 0.5961
|  | 1:52 | 6.2144 | -0.25319 | 0.5961
|  | 1:52 | 6.2156 | -0.30752 | 0.5961
|  | 1:52 | 6.2167 | -0.36184 | 0.5961
|  | 1:52 | 6.2178 | -0.40614 | 0.59609
|  | 1:53 | 6.2189 | -0.45044 | 0.59609
|  | 1:53 | 6.22 | -0.48112 | 0.59609
|  | 1:53 | 6.2211 | -0.49819 | 0.59609
|  | 1:53 | 6.2222 | -0.51526 | 0.59609
|  | 1:53 | 6.2233 | -0.54146 | 0.59608
|  | 1:53 | 6.2244 | -0.56767 | 0.59608
|  | 1:53 | 6.2256 | -0.58665 | 0.59608
|  | 1:53 | 6.2267 | -0.59843 | 0.59608
|  | 1:53 | 6.2278 | -0.6102 | 0.59607
|  | 1:53 | 6.2289 | -0.60745 | 0.59607
|  | 1:53 | 6.23 | -0.6047 | 0.59607
|  | 1:53 | 6.2311 | -0.60347 | 0.59607
|  | 1:53 | 6.2322 | -0.60376 | 0.59606
|  | 1:53 | 6.2333 | -0.60405 | 0.59606
|  | 1:53 | 6.2344 | -0.60336 | 0.59606
|  | 1:54 | 6.2356 | -0.60266 | 0.59606
|  | 1:54 | 6.2367 | -0.60291 | 0.59606
|  | 1:54 | 6.2378 | -0.60599 | 0.59605
|  | 1:54 | 6.2389 | -0.60906 | 0.59605
|  | 1:54 | 6.24 | -0.61077 | 0.59605
|  | 1:54 | 6.2411 | -0.61248 | 0.59605
|  | 1:54 | 6.2422 | -0.6045 | 0.59604
|  | 1:54 | 6.2433 | -0.58685 | 0.59604
|  | 1:54 | 6.2444 | -0.56919 | 0.59604
|  | 1:54 | 6.2456 | -0.55636 | 0.59604
|  | 1:54 | 6.2467 | -0.54352 | 0.59603
|  | 1:54 | 6.2478 | -0.53564 | 0.59603
|  | 1:54 | 6.2489 | -0.53272 | 0.59603
|  | 1:54 | 6.25 | -0.5298 | 0.59603
|  | 1:54 | 6.2511 | -0.529 | 0.59603
|  | 1:55 | 6.2522 | -0.52819 | 0.59602
|  | 1:55 | 6.2533 | -0.53152 | 0.59602
|  | 1:55 | 6.2544 | -0.539 | 0.59602
|  | 1:55 | 6.2556 | -0.54647 | 0.59602
|  | 1:55 | 6.2567 | -0.54635 | 0.59601
|  | 1:55 | 6.2578 | -0.54623 | 0.59601
|  | 1:55 | 6.2589 | -0.54252 | 0.59601
|  | 1:55 | 6.26 | -0.53522 | 0.59601
|  | 1:55 | 6.2611 | -0.52791 | 0.596
|  | 1:55 | 6.2622 | -0.51653 | 0.596
|  | 1:55 | 6.2633 | -0.50516 | 0.596
|  | 1:55 | 6.2644 | -0.47674 | 0.596
|  | 1:55 | 6.2656 | -0.43128 | 0.596
|  | 1:55 | 6.2667 | -0.38582 | 0.59599
|  | 1:55 | 6.2678 | -0.34134 | 0.59599
|  | 1:56 | 6.2689 | -0.29686 | 0.59599
|  | 1:56 | 6.27 | -0.25636 | 0.59599
|  | 1:56 | 6.2711 | -0.21982 | 0.59598
|  | 1:56 | 6.2722 | -0.18329 | 0.59598
|  | 1:56 | 6.2733 | -0.16697 | 0.59598
|  | 1:56 | 6.2744 | -0.15066 | 0.59598
|  | 1:56 | 6.2756 | -0.13059 | 0.59597
|  | 1:56 | 6.2767 | -0.10676 | 0.59597
|  | 1:56 | 6.2778 | -0.082929 | 0.59597
|  | 1:56 | 6.2789 | -0.064992 | 0.59597
|  | 1:56 | 6.28 | -0.047054 | 0.59597
|  | 1:56 | 6.2811 | -0.033677 | 0.59596
|  | 1:56 | 6.2822 | -0.024861 | 0.59596
|  | 1:56 | 6.2833 | -0.016045 | 0.59596
|  | 1:56 | 6.2844 | -0.015577 | 0.59596
|  | 1:57 | 6.2856 | -0.01511 | 0.59595
|  | 1:57 | 6.2867 | -0.032247 | 0.59595
|  | 1:57 | 6.2878 | -0.066986 | 0.59595
|  | 1:57 | 6.2889 | -0.10173 | 0.59595
|  | 1:57 | 6.29 | -0.11422 | 0.59594
|  | 1:57 | 6.2911 | -0.12672 | 0.59594
|  | 1:57 | 6.2922 | -0.14071 | 0.59594
|  | 1:57 | 6.2933 | -0.15619 | 0.59594
|  | 1:57 | 6.2944 | -0.17167 | 0.59594
|  | 1:57 | 6.2956 | -0.18715 | 0.59593
|  | 1:57 | 6.2967 | -0.20263 | 0.59593
|  | 1:57 | 6.2978 | -0.22463 | 0.59593
|  | 1:57 | 6.2989 | -0.25316 | 0.59593
|  | 1:57 | 6.3 | -0.28168 | 0.59592
|  | 1:57 | 6.3011 | -0.29777 | 0.59592
|  | 1:58 | 6.3022 | -0.31386 | 0.59592
|  | 1:58 | 6.3033 | -0.31394 | 0.59592
|  | 1:58 | 6.3044 | -0.298 | 0.59591
|  | 1:58 | 6.3056 | -0.28207 | 0.59591
|  | 1:58 | 6.3067 | -0.26097 | 0.59591
|  | 1:58 | 6.3078 | -0.23987 | 0.59591
|  | 1:58 | 6.3089 | -0.2201 | 0.59591
|  | 1:58 | 6.31 | -0.20168 | 0.5959
|  | 1:58 | 6.3111 | -0.18325 | 0.5959
|  | 1:58 | 6.3122 | -0.16685 | 0.5959
|  | 1:58 | 6.3133 | -0.15045 | 0.5959
|  | 1:58 | 6.3144 | -0.13497 | 0.59589
|  | 1:58 | 6.3156 | -0.1204 | 0.59589
|  | 1:58 | 6.3167 | -0.10583 | 0.59589
|  | 1:58 | 6.3178 | -0.085856 | 0.59589
|  | 1:59 | 6.3189 | -0.065882 | 0.59588
|  | 1:59 | 6.32 | -0.057483 | 0.59588
|  | 1:59 | 6.3211 | -0.060658 | 0.59588
|  | 1:59 | 6.3222 | -0.063833 | 0.59588
|  | 1:59 | 6.3233 | -0.042603 | 0.59587
|  | 1:59 | 6.3244 | -0.021374 | 0.59587
|  | 1:59 | 6.3256 | -0.0021204 | 0.59587
|  | 1:59 | 6.3267 | 0.015157 | 0.59587
|  | 1:59 | 6.3278 | 0.032435 | 0.59587
|  | 1:59 | 6.3289 | 0.024561 | 0.59586
|  | 1:59 | 6.33 | 0.016687 | 0.59586
|  | 1:59 | 6.3311 | 0.012389 | 0.59586
|  | 1:59 | 6.3322 | 0.011665 | 0.59586
|  | 1:59 | 6.3333 | 0.010942 | 0.59585
|  | 1:59 | 6.3344 | 0.002515 | 0.59585
|  | 2:00 | 6.3356 | -0.0059115 | 0.59585
|  | 2:00 | 6.3367 | -0.026255 | 0.59585
|  | 2:00 | 6.3378 | -0.058516 | 0.59584
|  | 2:00 | 6.3389 | -0.090777 | 0.59584
|  | 2:00 | 6.34 | -0.1219 | 0.59584
|  | 2:00 | 6.3411 | -0.15302 | 0.59584
|  | 2:00 | 6.3422 | -0.18289 | 0.59584
|  | 2:00 | 6.3433 | -0.14425 | 0.59583
|  | 2:00 | 6.3444 | -0.12965 | 0.59583
|  | 2:00 | 6.3456 | -0.13601 | 0.59583
|  | 2:00 | 6.3467 | -0.14238 | 0.59583
|  | 2:00 | 6.3478 | -0.14874 | 0.59582
|  | 2:00 | 6.3489 | -0.15511 | 0.59582
|  | 2:00 | 6.35 | -0.16147 | 0.59582
|  | 2:00 | 6.3511 | -0.15001 | 0.59582
|  | 2:01 | 6.3522 | -0.13855 | 0.59581
|  | 2:01 | 6.3533 | -0.11353 | 0.59581
|  | 2:01 | 6.3544 | -0.083978 | 0.59581
|  | 2:01 | 6.3556 | -0.05443 | 0.59581
|  | 2:01 | 6.3567 | -0.032121 | 0.59581
|  | 2:01 | 6.3578 | -0.0098121 | 0.5958
|  | 2:01 | 6.3589 | 0.0050135 | 0.5958
|  | 2:01 | 6.36 | 0.012356 | 0.5958
|  | 2:01 | 6.3611 | 0.019698 | 0.5958
|  | 2:01 | 6.3622 | 0.0056427 | 0.59579
|  | 2:01 | 6.3633 | -0.0084124 | 0.59579
|  | 2:01 | 6.3644 | -0.016135 | 0.59579
|  | 2:01 | 6.3656 | -0.017526 | 0.59579
|  | 2:01 | 6.3667 | -0.018917 | 0.59578
|  | 2:01 | 6.3678 | -0.0074832 | 0.59578
|  | 2:02 | 6.3689 | 0.0039504 | 0.59578
|  | 2:02 | 6.37 | 0.016937 | 0.59578
|  | 2:02 | 6.3711 | 0.030441 | 0.59578
|  | 2:02 | 6.3722 | 0.043946 | 0.59577
|  | 2:02 | 6.3733 | 0.065859 | 0.59577
|  | 2:02 | 6.3744 | 0.087772 | 0.59577
|  | 2:02 | 6.3756 | 0.10268 | 0.59577
|  | 2:02 | 6.3767 | 0.11526 | 0.59576
|  | 2:02 | 6.3778 | 0.12783 | 0.59576
|  | 2:02 | 6.3789 | 0.13629 | 0.59576
|  | 2:02 | 6.38 | 0.14474 | 0.59576
|  | 2:02 | 6.3811 | 0.1681 | 0.59575
|  | 2:02 | 6.3822 | 0.20635 | 0.59575
|  | 2:02 | 6.3833 | 0.2446 | 0.59575
|  | 2:02 | 6.3844 | 0.28614 | 0.59575
|  | 2:03 | 6.3856 | 0.32769 | 0.59575
|  | 2:03 | 6.3867 | 0.37177 | 0.59574
|  | 2:03 | 6.3878 | 0.41839 | 0.59574
|  | 2:03 | 6.3889 | 0.4646 | 0.59574
|  | 2:03 | 6.39 | 0.50955 | 0.59574
|  | 2:03 | 6.3911 | 0.55451 | 0.59573
|  | 2:03 | 6.3922 | 0.60292 | 0.59573
|  | 2:03 | 6.3933 | 0.65481 | 0.59573
|  | 2:03 | 6.3944 | 0.70669 | 0.59573
|  | 2:03 | 6.3956 | 0.72091 | 0.59572
|  | 2:03 | 6.3967 | 0.73513 | 0.59572
|  | 2:03 | 6.3978 | 0.73769 | 0.59572
|  | 2:03 | 6.3989 | 0.7286 | 0.59572
|  | 2:03 | 6.4 | 0.71951 | 0.59572
|  | 2:03 | 6.4011 | 0.69733 | 0.59571
|  | 2:04 | 6.4022 | 0.66208 | 0.59571
|  | 2:04 | 6.4033 | 0.6161 | 0.59571
|  | 2:04 | 6.4044 | 0.5594 | 0.59571
|  | 2:04 | 6.4056 | 0.50271 | 0.5957
|  | 2:04 | 6.4067 | 0.43484 | 0.5957
|  | 2:04 | 6.4078 | 0.36696 | 0.5957
|  | 2:04 | 6.4089 | 0.2997 | 0.5957
|  | 2:04 | 6.41 | 0.23306 | 0.59569
|  | 2:04 | 6.4111 | 0.16641 | 0.59569
|  | 2:04 | 6.4122 | 0.1269 | 0.59569
|  | 2:04 | 6.4133 | 0.087393 | 0.59569
|  | 2:04 | 6.4144 | 0.062752 | 0.59569
|  | 2:04 | 6.4156 | 0.052981 | 0.59568
|  | 2:04 | 6.4167 | 0.04321 | 0.59568
|  | 2:04 | 6.4178 | 0.031374 | 0.59568
|  | 2:05 | 6.4189 | 0.019538 | 0.59568
|  | 2:05 | 6.42 | 0.0014623 | 0.59567
|  | 2:05 | 6.4211 | -0.022852 | 0.59567
|  | 2:05 | 6.4222 | -0.047167 | 0.59567
|  | 2:05 | 6.4233 | -0.057435 | 0.59567
|  | 2:05 | 6.4244 | -0.067703 | 0.59566
|  | 2:05 | 6.4256 | -0.080728 | 0.59566
|  | 2:05 | 6.4267 | -0.096511 | 0.59566
|  | 2:05 | 6.4278 | -0.11229 | 0.59566
|  | 2:05 | 6.4289 | -0.14181 | 0.59566
|  | 2:05 | 6.43 | -0.17133 | 0.59565
|  | 2:05 | 6.4311 | -0.19213 | 0.59565
|  | 2:05 | 6.4322 | -0.21003 | 0.59565
|  | 2:05 | 6.4333 | -0.22794 | 0.59565
|  | 2:05 | 6.4344 | -0.25217 | 0.59564
|  | 2:06 | 6.4356 | -0.2764 | 0.59564
|  | 2:06 | 6.4367 | -0.29614 | 0.59564
|  | 2:06 | 6.4378 | -0.31141 | 0.59564
|  | 2:06 | 6.4389 | -0.32668 | 0.59563
|  | 2:06 | 6.44 | -0.33634 | 0.59563
|  | 2:06 | 6.4411 | -0.346 | 0.59563
|  | 2:06 | 6.4422 | -0.35417 | 0.59563
|  | 2:06 | 6.4433 | -0.36184 | 0.59562
|  | 2:06 | 6.4444 | -0.3695 | 0.59562
|  | 2:06 | 6.4456 | -0.38223 | 0.59562
|  | 2:06 | 6.4467 | -0.39495 | 0.59562
|  | 2:06 | 6.4478 | -0.41366 | 0.59562
|  | 2:06 | 6.4489 | -0.43836 | 0.59561
|  | 2:06 | 6.45 | -0.46307 | 0.59561
|  | 2:06 | 6.4511 | -0.49142 | 0.59561
|  | 2:07 | 6.4522 | -0.51976 | 0.59561
|  | 2:07 | 6.4533 | -0.53557 | 0.5956
|  | 2:07 | 6.4544 | -0.53885 | 0.5956
|  | 2:07 | 6.4556 | -0.54212 | 0.5956
|  | 2:07 | 6.4567 | -0.52588 | 0.5956
|  | 2:07 | 6.4578 | -0.50964 | 0.59559
|  | 2:07 | 6.4589 | -0.48512 | 0.59559
|  | 2:07 | 6.46 | -0.45232 | 0.59559
|  | 2:07 | 6.4611 | -0.41952 | 0.59559
|  | 2:07 | 6.4622 | -0.39896 | 0.59559
|  | 2:07 | 6.4633 | -0.3784 | 0.59558
|  | 2:07 | 6.4644 | -0.36069 | 0.59558
|  | 2:07 | 6.4656 | -0.34581 | 0.59558
|  | 2:07 | 6.4667 | -0.33094 | 0.59558
|  | 2:07 | 6.4678 | -0.31151 | 0.59557
|  | 2:08 | 6.4689 | -0.29208 | 0.59557
|  | 2:08 | 6.47 | -0.26401 | 0.59557
|  | 2:08 | 6.4711 | -0.2273 | 0.59557
|  | 2:08 | 6.4722 | -0.1906 | 0.59556
|  | 2:08 | 6.4733 | -0.15165 | 0.59556
|  | 2:08 | 6.4744 | -0.1127 | 0.59556
|  | 2:08 | 6.4756 | -0.070709 | 0.59556
|  | 2:08 | 6.4767 | -0.025681 | 0.59556
|  | 2:08 | 6.4778 | 0.019348 | 0.59555
|  | 2:08 | 6.4789 | 0.066808 | 0.59555
|  | 2:08 | 6.48 | 0.11427 | 0.59555
|  | 2:08 | 6.4811 | 0.14906 | 0.59555
|  | 2:08 | 6.4822 | 0.17962 | 0.59554
|  | 2:08 | 6.4833 | 0.21018 | 0.59554
|  | 2:08 | 6.4844 | 0.22659 | 0.59554
|  | 2:09 | 6.4856 | 0.243 | 0.59554
|  | 2:09 | 6.4867 | 0.26015 | 0.59553
|  | 2:09 | 6.4878 | 0.27804 | 0.59553
|  | 2:09 | 6.4889 | 0.29593 | 0.59553
|  | 2:09 | 6.49 | 0.34579 | 0.59553
|  | 2:09 | 6.4911 | 0.39566 | 0.59553
|  | 2:09 | 6.4922 | 0.41648 | 0.59552
|  | 2:09 | 6.4933 | 0.42761 | 0.59552
|  | 2:09 | 6.4944 | 0.43875 | 0.59552
|  | 2:09 | 6.4956 | 0.48488 | 0.59552
|  | 2:09 | 6.4967 | 0.53101 | 0.59551
|  | 2:09 | 6.4978 | 0.56431 | 0.59551
|  | 2:09 | 6.4989 | 0.58479 | 0.59551
|  | 2:09 | 6.5 | 0.60527 | 0.59551
|  | 2:09 | 6.5011 | 0.62576 | 0.5955
|  | 2:10 | 6.5022 | 0.64624 | 0.5955
|  | 2:10 | 6.5033 | 0.65386 | 0.5955
|  | 2:10 | 6.5044 | 0.64862 | 0.5955
|  | 2:10 | 6.5056 | 0.64337 | 0.5955
|  | 2:10 | 6.5067 | 0.61858 | 0.59549
|  | 2:10 | 6.5078 | 0.59379 | 0.59549
|  | 2:10 | 6.5089 | 0.57945 | 0.59549
|  | 2:10 | 6.51 | 0.5686 | 0.59549
|  | 2:10 | 6.5111 | 0.55774 | 0.59548
|  | 2:10 | 6.5122 | 0.53406 | 0.59548
|  | 2:10 | 6.5133 | 0.51037 | 0.59548
|  | 2:10 | 6.5144 | 0.48484 | 0.59548
|  | 2:10 | 6.5156 | 0.45747 | 0.59547
|  | 2:10 | 6.5167 | 0.43009 | 0.59547
|  | 2:10 | 6.5178 | 0.40661 | 0.59547
|  | 2:11 | 6.5189 | 0.38313 | 0.59547
|  | 2:11 | 6.52 | 0.35578 | 0.59547
|  | 2:11 | 6.5211 | 0.32455 | 0.59546
|  | 2:11 | 6.5222 | 0.29332 | 0.59546
|  | 2:11 | 6.5233 | 0.24981 | 0.59546
|  | 2:11 | 6.5244 | 0.20629 | 0.59546
|  | 2:11 | 6.5256 | 0.16355 | 0.59545
|  | 2:11 | 6.5267 | 0.12106 | 0.59545
|  | 2:11 | 6.5278 | 0.078582 | 0.59545
|  | 2:11 | 6.5289 | 0.031632 | 0.59545
|  | 2:11 | 6.53 | -0.015318 | 0.59544
|  | 2:11 | 6.5311 | -0.035845 | 0.59544
|  | 2:11 | 6.5322 | -0.047565 | 0.59544
|  | 2:11 | 6.5333 | -0.059285 | 0.59544
|  | 2:11 | 6.5344 | -0.081598 | 0.59544
|  | 2:12 | 6.5356 | -0.10391 | 0.59543
|  | 2:12 | 6.5367 | -0.13323 | 0.59543
|  | 2:12 | 6.5378 | -0.16956 | 0.59543
|  | 2:12 | 6.5389 | -0.20588 | 0.59543
|  | 2:12 | 6.54 | -0.24997 | 0.59542
|  | 2:12 | 6.5411 | -0.29406 | 0.59542
|  | 2:12 | 6.5422 | -0.33234 | 0.59542
|  | 2:12 | 6.5433 | -0.3648 | 0.59542
|  | 2:12 | 6.5444 | -0.39726 | 0.59541
|  | 2:12 | 6.5456 | -0.42357 | 0.59541
|  | 2:12 | 6.5467 | -0.44987 | 0.59541
|  | 2:12 | 6.5478 | -0.46847 | 0.59541
|  | 2:12 | 6.5489 | -0.47935 | 0.59541
|  | 2:12 | 6.55 | -0.49023 | 0.5954
|  | 2:12 | 6.5511 | -0.5088 | 0.5954
|  | 2:13 | 6.5522 | -0.52738 | 0.5954
|  | 2:13 | 6.5533 | -0.54595 | 0.5954
|  | 2:13 | 6.5544 | -0.56452 | 0.59539
|  | 2:13 | 6.5556 | -0.58056 | 0.59539
|  | 2:13 | 6.5567 | -0.58899 | 0.59539
|  | 2:13 | 6.5578 | -0.59741 | 0.59539
|  | 2:13 | 6.5589 | -0.60464 | 0.59538
|  | 2:13 | 6.56 | -0.61068 | 0.59538
|  | 2:13 | 6.5611 | -0.61671 | 0.59538
|  | 2:13 | 6.5622 | -0.62274 | 0.59538
|  | 2:13 | 6.5633 | -0.62878 | 0.59537
|  | 2:13 | 6.5644 | -0.64556 | 0.59537
|  | 2:13 | 6.5656 | -0.67309 | 0.59537
|  | 2:13 | 6.5667 | -0.70062 | 0.59537
|  | 2:13 | 6.5678 | -0.7259 | 0.59537
|  | 2:14 | 6.5689 | -0.75118 | 0.59536
|  | 2:14 | 6.57 | -0.76373 | 0.59536
|  | 2:14 | 6.5711 | -0.76355 | 0.59536
|  | 2:14 | 6.5722 | -0.76336 | 0.59536
|  | 2:14 | 6.5733 | -0.74165 | 0.59535
|  | 2:14 | 6.5744 | -0.71995 | 0.59535
|  | 2:14 | 6.5756 | -0.69328 | 0.59535
|  | 2:14 | 6.5767 | -0.66166 | 0.59535
|  | 2:14 | 6.5778 | -0.63004 | 0.59534
|  | 2:14 | 6.5789 | -0.60123 | 0.59534
|  | 2:14 | 6.58 | -0.57243 | 0.59534
|  | 2:14 | 6.5811 | -0.55891 | 0.59534
|  | 2:14 | 6.5822 | -0.56068 | 0.59534
|  | 2:14 | 6.5833 | -0.56245 | 0.59533
|  | 2:14 | 6.5844 | -0.54412 | 0.59533
|  | 2:15 | 6.5856 | -0.52578 | 0.59533
|  | 2:15 | 6.5867 | -0.51626 | 0.59533
|  | 2:15 | 6.5878 | -0.51554 | 0.59532
|  | 2:15 | 6.5889 | -0.51483 | 0.59532
|  | 2:15 | 6.59 | -0.51658 | 0.59532
|  | 2:15 | 6.5911 | -0.51832 | 0.59532
|  | 2:15 | 6.5922 | -0.51742 | 0.59531
|  | 2:15 | 6.5933 | -0.51387 | 0.59531
|  | 2:15 | 6.5944 | -0.51032 | 0.59531
|  | 2:15 | 6.5956 | -0.49265 | 0.59531
|  | 2:15 | 6.5967 | -0.47497 | 0.59531
|  | 2:15 | 6.5978 | -0.4573 | 0.5953
|  | 2:15 | 6.5989 | -0.43963 | 0.5953
|  | 2:15 | 6.6 | -0.42195 | 0.5953
|  | 2:15 | 6.6011 | -0.40033 | 0.5953
|  | 2:16 | 6.6022 | -0.3787 | 0.59529
|  | 2:16 | 6.6033 | -0.35755 | 0.59529
|  | 2:16 | 6.6044 | -0.33687 | 0.59529
|  | 2:16 | 6.6056 | -0.31619 | 0.59529
|  | 2:16 | 6.6067 | -0.27026 | 0.59528
|  | 2:16 | 6.6078 | -0.22432 | 0.59528
|  | 2:16 | 6.6089 | -0.18079 | 0.59528
|  | 2:16 | 6.61 | -0.13806 | 0.59528
|  | 2:16 | 6.6111 | -0.095326 | 0.59528
|  | 2:16 | 6.6122 | -0.056057 | 0.59527
|  | 2:16 | 6.6133 | -0.016788 | 0.59527
|  | 2:16 | 6.6144 | 0.015659 | 0.59527
|  | 2:16 | 6.6156 | 0.041284 | 0.59527
|  | 2:16 | 6.6167 | 0.066908 | 0.59526
|  | 2:16 | 6.6178 | 0.067889 | 0.59526
|  | 2:17 | 6.6189 | 0.06887 | 0.59526
|  | 2:17 | 6.62 | 0.077604 | 0.59526
|  | 2:17 | 6.6211 | 0.094089 | 0.59525
|  | 2:17 | 6.6222 | 0.11057 | 0.59525
|  | 2:17 | 6.6233 | 0.13697 | 0.59525
|  | 2:17 | 6.6244 | 0.16337 | 0.59525
|  | 2:17 | 6.6256 | 0.18555 | 0.59525
|  | 2:17 | 6.6267 | 0.2035 | 0.59524
|  | 2:17 | 6.6278 | 0.22146 | 0.59524
|  | 2:17 | 6.6289 | 0.25483 | 0.59524
|  | 2:17 | 6.63 | 0.2882 | 0.59524
|  | 2:17 | 6.6311 | 0.30837 | 0.59523
|  | 2:17 | 6.6322 | 0.31533 | 0.59523
|  | 2:17 | 6.6333 | 0.32229 | 0.59523
|  | 2:17 | 6.6344 | 0.34371 | 0.59523
|  | 2:18 | 6.6356 | 0.36513 | 0.59522
|  | 2:18 | 6.6367 | 0.39495 | 0.59522
|  | 2:18 | 6.6378 | 0.43316 | 0.59522
|  | 2:18 | 6.6389 | 0.47137 | 0.59522
|  | 2:18 | 6.64 | 0.50421 | 0.59522
|  | 2:18 | 6.6411 | 0.53705 | 0.59521
|  | 2:18 | 6.6422 | 0.56677 | 0.59521
|  | 2:18 | 6.6433 | 0.59337 | 0.59521
|  | 2:18 | 6.6444 | 0.61996 | 0.59521
|  | 2:18 | 6.6456 | 0.63533 | 0.5952
|  | 2:18 | 6.6467 | 0.6507 | 0.5952
|  | 2:18 | 6.6478 | 0.67478 | 0.5952
|  | 2:18 | 6.6489 | 0.70756 | 0.5952
|  | 2:18 | 6.65 | 0.74033 | 0.59519
|  | 2:18 | 6.6511 | 0.7188 | 0.59519
|  | 2:19 | 6.6522 | 0.69726 | 0.59519
|  | 2:19 | 6.6533 | 0.69924 | 0.59519
|  | 2:19 | 6.6544 | 0.72473 | 0.59519
|  | 2:19 | 6.6556 | 0.75023 | 0.59518
|  | 2:19 | 6.6567 | 0.75876 | 0.59518
|  | 2:19 | 6.6578 | 0.76729 | 0.59518
|  | 2:19 | 6.6589 | 0.77299 | 0.59518
|  | 2:19 | 6.66 | 0.77774 | 0.59517
|  | 2:19 | 6.6611 | 0.7825 | 0.59517
|  | 2:19 | 6.6622 | 0.76741 | 0.59517
|  | 2:19 | 6.6633 | 0.75232 | 0.59517
|  | 2:19 | 6.6644 | 0.7296 | 0.59516
|  | 2:19 | 6.6656 | 0.69925 | 0.59516
|  | 2:19 | 6.6667 | 0.6689 | 0.59516
|  | 2:19 | 6.6678 | 0.62576 | 0.59516
|  | 2:20 | 6.6689 | 0.58261 | 0.59516
|  | 2:20 | 6.67 | 0.54949 | 0.59515
|  | 2:20 | 6.6711 | 0.5264 | 0.59515
|  | 2:20 | 6.6722 | 0.50331 | 0.59515
|  | 2:20 | 6.6733 | 0.4765 | 0.59515
|  | 2:20 | 6.6744 | 0.44968 | 0.59514
|  | 2:20 | 6.6756 | 0.4167 | 0.59514
|  | 2:20 | 6.6767 | 0.37755 | 0.59514
|  | 2:20 | 6.6778 | 0.33841 | 0.59514
|  | 2:20 | 6.6789 | 0.29386 | 0.59513
|  | 2:20 | 6.68 | 0.24932 | 0.59513
|  | 2:20 | 6.6811 | 0.21533 | 0.59513
|  | 2:20 | 6.6822 | 0.19189 | 0.59513
|  | 2:20 | 6.6833 | 0.16844 | 0.59512
|  | 2:20 | 6.6844 | 0.16499 | 0.59512
|  | 2:21 | 6.6856 | 0.16153 | 0.59512
|  | 2:21 | 6.6867 | 0.15986 | 0.59512
|  | 2:21 | 6.6878 | 0.15996 | 0.59512
|  | 2:21 | 6.6889 | 0.16005 | 0.59511
|  | 2:21 | 6.69 | 0.14796 | 0.59511
|  | 2:21 | 6.6911 | 0.13587 | 0.59511
|  | 2:21 | 6.6922 | 0.12378 | 0.59511
|  | 2:21 | 6.6933 | 0.1117 | 0.5951
|  | 2:21 | 6.6944 | 0.099605 | 0.5951
|  | 2:21 | 6.6956 | 0.079349 | 0.5951
|  | 2:21 | 6.6967 | 0.059092 | 0.5951
|  | 2:21 | 6.6978 | 0.042185 | 0.59509
|  | 2:21 | 6.6989 | 0.028626 | 0.59509
|  | 2:21 | 6.7 | 0.015067 | 0.59509
|  | 2:21 | 6.7011 | 0.017848 | 0.59509
|  | 2:22 | 6.7022 | 0.020629 | 0.59509
|  | 2:22 | 6.7033 | 0.02341 | 0.59508
|  | 2:22 | 6.7044 | 0.02619 | 0.59508
|  | 2:22 | 6.7056 | 0.028971 | 0.59508
|  | 2:22 | 6.7067 | 0.040168 | 0.59508
|  | 2:22 | 6.7078 | 0.051364 | 0.59507
|  | 2:22 | 6.7089 | 0.060832 | 0.59507
|  | 2:22 | 6.71 | 0.068571 | 0.59507
|  | 2:22 | 6.7111 | 0.076309 | 0.59507
|  | 2:22 | 6.7122 | 0.077437 | 0.59506
|  | 2:22 | 6.7133 | 0.078564 | 0.59506
|  | 2:22 | 6.7144 | 0.080322 | 0.59506
|  | 2:22 | 6.7156 | 0.082711 | 0.59506
|  | 2:22 | 6.7167 | 0.085099 | 0.59506
|  | 2:22 | 6.7178 | 0.082506 | 0.59505
|  | 2:23 | 6.7189 | 0.079913 | 0.59505
|  | 2:23 | 6.72 | 0.07732 | 0.59505
|  | 2:23 | 6.7211 | 0.074727 | 0.59505
|  | 2:23 | 6.7222 | 0.072134 | 0.59504
|  | 2:23 | 6.7233 | 0.05751 | 0.59504
|  | 2:23 | 6.7244 | 0.042887 | 0.59504
|  | 2:23 | 6.7256 | 0.041184 | 0.59504
|  | 2:23 | 6.7267 | 0.052402 | 0.59503
|  | 2:23 | 6.7278 | 0.063621 | 0.59503
|  | 2:23 | 6.7289 | 0.059618 | 0.59503
|  | 2:23 | 6.73 | 0.055615 | 0.59503
|  | 2:23 | 6.7311 | 0.053782 | 0.59503
|  | 2:23 | 6.7322 | 0.054119 | 0.59502
|  | 2:23 | 6.7333 | 0.054456 | 0.59502
|  | 2:23 | 6.7344 | 0.052728 | 0.59502
|  | 2:24 | 6.7356 | 0.051 | 0.59502
|  | 2:24 | 6.7367 | 0.053232 | 0.59501
|  | 2:24 | 6.7378 | 0.059425 | 0.59501
|  | 2:24 | 6.7389 | 0.065617 | 0.59501
|  | 2:24 | 6.74 | 0.089973 | 0.59501
|  | 2:24 | 6.7411 | 0.11433 | 0.595
|  | 2:24 | 6.7422 | 0.13104 | 0.595
|  | 2:24 | 6.7433 | 0.14009 | 0.595
|  | 2:24 | 6.7444 | 0.14915 | 0.595
|  | 2:24 | 6.7456 | 0.14294 | 0.595
|  | 2:24 | 6.7467 | 0.13674 | 0.59499
|  | 2:24 | 6.7478 | 0.13903 | 0.59499
|  | 2:24 | 6.7489 | 0.14981 | 0.59499
|  | 2:24 | 6.75 | 0.16059 | 0.59499
|  | 2:24 | 6.7511 | 0.17604 | 0.59498
|  | 2:25 | 6.7522 | 0.1915 | 0.59498
|  | 2:25 | 6.7533 | 0.20614 | 0.59498
|  | 2:25 | 6.7544 | 0.21996 | 0.59498
|  | 2:25 | 6.7556 | 0.23378 | 0.59497
|  | 2:25 | 6.7567 | 0.22649 | 0.59497
|  | 2:25 | 6.7578 | 0.2192 | 0.59497
|  | 2:25 | 6.7589 | 0.2103 | 0.59497
|  | 2:25 | 6.76 | 0.1998 | 0.59497
|  | 2:25 | 6.7611 | 0.18929 | 0.59496
|  | 2:25 | 6.7622 | 0.16969 | 0.59496
|  | 2:25 | 6.7633 | 0.15009 | 0.59496
|  | 2:25 | 6.7644 | 0.12595 | 0.59496
|  | 2:25 | 6.7656 | 0.09729 | 0.59495
|  | 2:25 | 6.7667 | 0.068625 | 0.59495
|  | 2:25 | 6.7678 | 0.07361 | 0.59495
|  | 2:26 | 6.7689 | 0.078594 | 0.59495
|  | 2:26 | 6.77 | 0.072993 | 0.59494
|  | 2:26 | 6.7711 | 0.056805 | 0.59494
|  | 2:26 | 6.7722 | 0.040617 | 0.59494
|  | 2:26 | 6.7733 | 0.014632 | 0.59494
|  | 2:26 | 6.7744 | -0.011353 | 0.59494
|  | 2:26 | 6.7756 | -0.035552 | 0.59493
|  | 2:26 | 6.7767 | -0.057963 | 0.59493
|  | 2:26 | 6.7778 | -0.080375 | 0.59493
|  | 2:26 | 6.7789 | -0.065543 | 0.59493
|  | 2:26 | 6.78 | -0.050712 | 0.59492
|  | 2:26 | 6.7811 | -0.031837 | 0.59492
|  | 2:26 | 6.7822 | -0.0089175 | 0.59492
|  | 2:26 | 6.7833 | 0.014002 | 0.59492
|  | 2:26 | 6.7844 | 0.0028253 | 0.59491
|  | 2:27 | 6.7856 | -0.0083511 | 0.59491
|  | 2:27 | 6.7867 | -0.022928 | 0.59491
|  | 2:27 | 6.7878 | -0.040906 | 0.59491
|  | 2:27 | 6.7889 | -0.058884 | 0.59491
|  | 2:27 | 6.79 | -0.068746 | 0.5949
|  | 2:27 | 6.7911 | -0.078609 | 0.5949
|  | 2:27 | 6.7922 | -0.07932 | 0.5949
|  | 2:27 | 6.7933 | -0.076982 | 0.5949
|  | 2:27 | 6.7944 | -0.074643 | 0.59489
|  | 2:27 | 6.7956 | -0.075455 | 0.59489
|  | 2:27 | 6.7967 | -0.076267 | 0.59489
|  | 2:27 | 6.7978 | -0.073963 | 0.59489
|  | 2:27 | 6.7989 | -0.07062 | 0.59488
|  | 2:27 | 6.8 | -0.067277 | 0.59488
|  | 2:27 | 6.8011 | -0.087801 | 0.59488
|  | 2:28 | 6.8022 | -0.10832 | 0.59488
|  | 2:28 | 6.8033 | -0.11242 | 0.59487
|  | 2:28 | 6.8044 | -0.10009 | 0.59487
|  | 2:28 | 6.8056 | -0.087763 | 0.59487
|  | 2:28 | 6.8067 | -0.068639 | 0.59487
|  | 2:28 | 6.8078 | -0.049516 | 0.59487
|  | 2:28 | 6.8089 | -0.015747 | 0.59486
|  | 2:28 | 6.81 | 0.032669 | 0.59486
|  | 2:28 | 6.8111 | 0.076313 | 0.59486
|  | 2:28 | 6.8122 | 0.10565 | 0.59486
|  | 2:28 | 6.8133 | 0.13498 | 0.59485
|  | 2:28 | 6.8144 | 0.14996 | 0.59485
|  | 2:28 | 6.8156 | 0.1506 | 0.59485
|  | 2:28 | 6.8167 | 0.15123 | 0.59485
|  | 2:28 | 6.8178 | 0.15947 | 0.59484
|  | 2:29 | 6.8189 | 0.1677 | 0.59484
|  | 2:29 | 6.82 | 0.16361 | 0.59484
|  | 2:29 | 6.8211 | 0.14719 | 0.59484
|  | 2:29 | 6.8222 | 0.13078 | 0.59484
|  | 2:29 | 6.8233 | 0.11437 | 0.59483
|  | 2:29 | 6.8244 | 0.097961 | 0.59483
|  | 2:29 | 6.8256 | 0.077558 | 0.59483
|  | 2:29 | 6.8267 | 0.055824 | 0.59483
|  | 2:29 | 6.8278 | 0.034089 | 0.59482
|  | 2:29 | 6.8289 | 0.018564 | 0.59482
|  | 2:29 | 6.83 | 0.0030393 | 0.59482
|  | 2:29 | 6.8311 | -0.016027 | 0.59482
|  | 2:29 | 6.8322 | -0.038635 | 0.59481
|  | 2:29 | 6.8333 | -0.061243 | 0.59481
|  | 2:29 | 6.8344 | -0.068344 | 0.59481
|  | 2:30 | 6.8356 | -0.075445 | 0.59481
|  | 2:30 | 6.8367 | -0.080764 | 0.59481
|  | 2:30 | 6.8378 | -0.0843 | 0.5948
|  | 2:30 | 6.8389 | -0.087836 | 0.5948
|  | 2:30 | 6.84 | -0.08516 | 0.5948
|  | 2:30 | 6.8411 | -0.082483 | 0.5948
|  | 2:30 | 6.8422 | -0.079807 | 0.59479
|  | 2:30 | 6.8433 | -0.07713 | 0.59479
|  | 2:30 | 6.8444 | -0.074454 | 0.59479
|  | 2:30 | 6.8456 | -0.076025 | 0.59479
|  | 2:30 | 6.8467 | -0.077597 | 0.59478
|  | 2:30 | 6.8478 | -0.085439 | 0.59478
|  | 2:30 | 6.8489 | -0.09955 | 0.59478
|  | 2:30 | 6.85 | -0.11366 | 0.59478
|  | 2:30 | 6.8511 | -0.11441 | 0.59478
|  | 2:31 | 6.8522 | -0.11516 | 0.59477
|  | 2:31 | 6.8533 | -0.10971 | 0.59477
|  | 2:31 | 6.8544 | -0.09806 | 0.59477
|  | 2:31 | 6.8556 | -0.084509 | 0.59477
|  | 2:31 | 6.8567 | -0.065244 | 0.59476
|  | 2:31 | 6.8578 | -0.045979 | 0.59476
|  | 2:31 | 6.8589 | -0.029559 | 0.59476
|  | 2:31 | 6.86 | -0.015984 | 0.59476
|  | 2:31 | 6.8611 | -0.0024094 | 0.59475
|  | 2:31 | 6.8622 | 0.022238 | 0.59475
|  | 2:31 | 6.8633 | 0.046885 | 0.59475
|  | 2:31 | 6.8644 | 0.074314 | 0.59475
|  | 2:31 | 6.8656 | 0.10453 | 0.59475
|  | 2:31 | 6.8667 | 0.13474 | 0.59474
|  | 2:31 | 6.8678 | 0.15843 | 0.59474
|  | 2:32 | 6.8689 | 0.18212 | 0.59474
|  | 2:32 | 6.87 | 0.20365 | 0.59474
|  | 2:32 | 6.8711 | 0.22304 | 0.59473
|  | 2:32 | 6.8722 | 0.24243 | 0.59473
|  | 2:32 | 6.8733 | 0.2467 | 0.59473
|  | 2:32 | 6.8744 | 0.25097 | 0.59473
|  | 2:32 | 6.8756 | 0.25524 | 0.59472
|  | 2:32 | 6.8767 | 0.25952 | 0.59472
|  | 2:32 | 6.8778 | 0.26379 | 0.59472
|  | 2:32 | 6.8789 | 0.26806 | 0.59472
|  | 2:32 | 6.88 | 0.27234 | 0.59472
|  | 2:32 | 6.8811 | 0.27055 | 0.59471
|  | 2:32 | 6.8822 | 0.26272 | 0.59471
|  | 2:32 | 6.8833 | 0.25488 | 0.59471
|  | 2:32 | 6.8844 | 0.23498 | 0.59471
|  | 2:33 | 6.8856 | 0.21507 | 0.5947
|  | 2:33 | 6.8867 | 0.20228 | 0.5947
|  | 2:33 | 6.8878 | 0.1966 | 0.5947
|  | 2:33 | 6.8889 | 0.19092 | 0.5947
|  | 2:33 | 6.89 | 0.17374 | 0.59469
|  | 2:33 | 6.8911 | 0.15656 | 0.59469
|  | 2:33 | 6.8922 | 0.14737 | 0.59469
|  | 2:33 | 6.8933 | 0.14617 | 0.59469
|  | 2:33 | 6.8944 | 0.14096 | 0.59469
|  | 2:33 | 6.8956 | 0.1237 | 0.59468
|  | 2:33 | 6.8967 | 0.10644 | 0.59468
|  | 2:33 | 6.8978 | 0.091813 | 0.59468
|  | 2:33 | 6.8989 | 0.079822 | 0.59468
|  | 2:33 | 6.9 | 0.067831 | 0.59467
|  | 2:33 | 6.9011 | 0.075896 | 0.59467
|  | 2:34 | 6.9022 | 0.083961 | 0.59467
|  | 2:34 | 6.9033 | 0.086463 | 0.59467
|  | 2:34 | 6.9044 | 0.083403 | 0.59466
|  | 2:34 | 6.9056 | 0.080342 | 0.59466
|  | 2:34 | 6.9067 | 0.086139 | 0.59466
|  | 2:34 | 6.9078 | 0.091936 | 0.59466
|  | 2:34 | 6.9089 | 0.086932 | 0.59466
|  | 2:34 | 6.91 | 0.071129 | 0.59465
|  | 2:34 | 6.9111 | 0.055325 | 0.59465
|  | 2:34 | 6.9122 | 0.058039 | 0.59465
|  | 2:34 | 6.9133 | 0.060754 | 0.59465
|  | 2:34 | 6.9144 | 0.053289 | 0.59464
|  | 2:34 | 6.9156 | 0.035644 | 0.59464
|  | 2:34 | 6.9167 | 0.018 | 0.59464
|  | 2:34 | 6.9178 | -0.013065 | 0.59464
|  | 2:35 | 6.9189 | -0.04413 | 0.59463
|  | 2:35 | 6.92 | -0.070275 | 0.59463
|  | 2:35 | 6.9211 | -0.091499 | 0.59463
|  | 2:35 | 6.9222 | -0.11272 | 0.59463
|  | 2:35 | 6.9233 | -0.1153 | 0.59462
|  | 2:35 | 6.9244 | -0.11788 | 0.59462
|  | 2:35 | 6.9256 | -0.11783 | 0.59462
|  | 2:35 | 6.9267 | -0.11514 | 0.59462
|  | 2:35 | 6.9278 | -0.11272 | 0.59462
|  | 2:35 | 6.9289 | -0.11108 | 0.59461
|  | 2:35 | 6.93 | -0.10944 | 0.59461
|  | 2:35 | 6.9311 | -0.1078 | 0.59461
|  | 2:35 | 6.9322 | -0.12031 | 0.59461
|  | 2:35 | 6.9333 | -0.13283 | 0.5946
|  | 2:35 | 6.9344 | -0.13556 | 0.5946
|  | 2:36 | 6.9356 | -0.1383 | 0.5946
|  | 2:36 | 6.9367 | -0.13564 | 0.5946
|  | 2:36 | 6.9378 | -0.13119 | 0.59459
|  | 2:36 | 6.9389 | -0.1251 | 0.59459
|  | 2:36 | 6.94 | -0.11411 | 0.59459
|  | 2:36 | 6.9411 | -0.10312 | 0.59459
|  | 2:36 | 6.9422 | -0.087127 | 0.59459
|  | 2:36 | 6.9433 | -0.06947 | 0.59458
|  | 2:36 | 6.9444 | -0.057029 | 0.59458
|  | 2:36 | 6.9456 | -0.060235 | 0.59458
|  | 2:36 | 6.9467 | -0.06344 | 0.59458
|  | 2:36 | 6.9478 | -0.059529 | 0.59457
|  | 2:36 | 6.9489 | -0.053247 | 0.59457
|  | 2:36 | 6.95 | -0.048412 | 0.59457
|  | 2:36 | 6.9511 | -0.047923 | 0.59457
|  | 2:37 | 6.9522 | -0.047434 | 0.59456
|  | 2:37 | 6.9533 | -0.052124 | 0.59456
|  | 2:37 | 6.9544 | -0.05854 | 0.59456
|  | 2:37 | 6.9556 | -0.068618 | 0.59456
|  | 2:37 | 6.9567 | -0.08968 | 0.59456
|  | 2:37 | 6.9578 | -0.11074 | 0.59455
|  | 2:37 | 6.9589 | -0.12803 | 0.59455
|  | 2:37 | 6.96 | -0.14405 | 0.59455
|  | 2:37 | 6.9611 | -0.15587 | 0.59455
|  | 2:37 | 6.9622 | -0.15507 | 0.59454
|  | 2:37 | 6.9633 | -0.15427 | 0.59454
|  | 2:37 | 6.9644 | -0.1689 | 0.59454
|  | 2:37 | 6.9656 | -0.18867 | 0.59454
|  | 2:37 | 6.9667 | -0.19879 | 0.59453
|  | 2:37 | 6.9678 | -0.17995 | 0.59453
|  | 2:38 | 6.9689 | -0.16112 | 0.59453
|  | 2:38 | 6.97 | -0.14042 | 0.59453
|  | 2:38 | 6.9711 | -0.1191 | 0.59453
|  | 2:38 | 6.9722 | -0.087246 | 0.59452
|  | 2:38 | 6.9733 | -0.023777 | 0.59452
|  | 2:38 | 6.9744 | 0.039692 | 0.59452
|  | 2:38 | 6.9756 | 0.084628 | 0.59452
|  | 2:38 | 6.9767 | 0.12956 | 0.59451
|  | 2:38 | 6.9778 | 0.17372 | 0.59451
|  | 2:38 | 6.9789 | 0.21556 | 0.59451
|  | 2:38 | 6.98 | 0.2574 | 0.59451
|  | 2:38 | 6.9811 | 0.26371 | 0.5945
|  | 2:38 | 6.9822 | 0.25818 | 0.5945
|  | 2:38 | 6.9833 | 0.25264 | 0.5945
|  | 2:38 | 6.9844 | 0.24711 | 0.5945
|  | 2:39 | 6.9856 | 0.24157 | 0.5945
|  | 2:39 | 6.9867 | 0.24404 | 0.59449
|  | 2:39 | 6.9878 | 0.24918 | 0.59449
|  | 2:39 | 6.9889 | 0.25653 | 0.59449
|  | 2:39 | 6.99 | 0.27053 | 0.59449
|  | 2:39 | 6.9911 | 0.28454 | 0.59448
|  | 2:39 | 6.9922 | 0.28643 | 0.59448
|  | 2:39 | 6.9933 | 0.28428 | 0.59448
|  | 2:39 | 6.9944 | 0.28637 | 0.59448
|  | 2:39 | 6.9956 | 0.30114 | 0.59447
|  | 2:39 | 6.9967 | 0.31592 | 0.59447
|  | 2:39 | 6.9978 | 0.32289 | 0.59447
|  | 2:39 | 6.9989 | 0.32726 | 0.59447
|  | 2:39 | 7 | 0.32399 | 0.59447
|  | 2:39 | 7.0011 | 0.3131 | 0.59446
|  | 2:40 | 7.0022 | 0.3022 | 0.59446
|  | 2:40 | 7.0033 | 0.28574 | 0.59446
|  | 2:40 | 7.0044 | 0.26742 | 0.59446
|  | 2:40 | 7.0056 | 0.24996 | 0.59445
|  | 2:40 | 7.0067 | 0.23337 | 0.59445
|  | 2:40 | 7.0078 | 0.21678 | 0.59445
|  | 2:40 | 7.0089 | 0.18735 | 0.59445
|  | 2:40 | 7.01 | 0.15364 | 0.59444
|  | 2:40 | 7.0111 | 0.13899 | 0.59444
|  | 2:40 | 7.0122 | 0.1434 | 0.59444
|  | 2:40 | 7.0133 | 0.1478 | 0.59444
|  | 2:40 | 7.0144 | 0.16101 | 0.59444
|  | 2:40 | 7.0156 | 0.17715 | 0.59443
|  | 2:40 | 7.0167 | 0.1784 | 0.59443
|  | 2:40 | 7.0178 | 0.16474 | 0.59443
|  | 2:41 | 7.0189 | 0.15109 | 0.59443
|  | 2:41 | 7.02 | 0.12306 | 0.59442
|  | 2:41 | 7.0211 | 0.090241 | 0.59442
|  | 2:41 | 7.0222 | 0.056587 | 0.59442
|  | 2:41 | 7.0233 | 0.020429 | 0.59442
|  | 2:41 | 7.0244 | -0.015729 | 0.59441
|  | 2:41 | 7.0256 | -0.042232 | 0.59441
|  | 2:41 | 7.0267 | -0.065516 | 0.59441
|  | 2:41 | 7.0278 | -0.087599 | 0.59441
|  | 2:41 | 7.0289 | -0.10608 | 0.59441
|  | 2:41 | 7.03 | -0.12456 | 0.5944
|  | 2:41 | 7.0311 | -0.13921 | 0.5944
|  | 2:41 | 7.0322 | -0.15259 | 0.5944
|  | 2:41 | 7.0333 | -0.16354 | 0.5944
|  | 2:41 | 7.0344 | -0.16719 | 0.59439
|  | 2:42 | 7.0356 | -0.17083 | 0.59439
|  | 2:42 | 7.0367 | -0.19514 | 0.59439
|  | 2:42 | 7.0378 | -0.22632 | 0.59439
|  | 2:42 | 7.0389 | -0.24783 | 0.59438
|  | 2:42 | 7.04 | -0.24028 | 0.59438
|  | 2:42 | 7.0411 | -0.23273 | 0.59438
|  | 2:42 | 7.0422 | -0.22091 | 0.59438
|  | 2:42 | 7.0433 | -0.20767 | 0.59437
|  | 2:42 | 7.0444 | -0.19169 | 0.59437
|  | 2:42 | 7.0456 | -0.1675 | 0.59437
|  | 2:42 | 7.0467 | -0.14331 | 0.59437
|  | 2:42 | 7.0478 | -0.12658 | 0.59437
|  | 2:42 | 7.0489 | -0.11235 | 0.59436
|  | 2:42 | 7.05 | -0.099041 | 0.59436
|  | 2:42 | 7.0511 | -0.088485 | 0.59436
|  | 2:43 | 7.0522 | -0.077929 | 0.59436
|  | 2:43 | 7.0533 | -0.06405 | 0.59435
|  | 2:43 | 7.0544 | -0.049063 | 0.59435
|  | 2:43 | 7.0556 | -0.032325 | 0.59435
|  | 2:43 | 7.0567 | -0.01033 | 0.59435
|  | 2:43 | 7.0578 | 0.011664 | 0.59434
|  | 2:43 | 7.0589 | 0.025807 | 0.59434
|  | 2:43 | 7.06 | 0.037333 | 0.59434
|  | 2:43 | 7.0611 | 0.049144 | 0.59434
|  | 2:43 | 7.0622 | 0.06181 | 0.59434
|  | 2:43 | 7.0633 | 0.074475 | 0.59433
|  | 2:43 | 7.0644 | 0.088406 | 0.59433
|  | 2:43 | 7.0656 | 0.10276 | 0.59433
|  | 2:43 | 7.0667 | 0.11637 | 0.59433
|  | 2:43 | 7.0678 | 0.12776 | 0.59432
|  | 2:44 | 7.0689 | 0.13916 | 0.59432
|  | 2:44 | 7.07 | 0.15333 | 0.59432
|  | 2:44 | 7.0711 | 0.16843 | 0.59432
|  | 2:44 | 7.0722 | 0.18226 | 0.59431
|  | 2:44 | 7.0733 | 0.19228 | 0.59431
|  | 2:44 | 7.0744 | 0.20229 | 0.59431
|  | 2:44 | 7.0756 | 0.18703 | 0.59431
|  | 2:44 | 7.0767 | 0.17176 | 0.59431
|  | 2:44 | 7.0778 | 0.15361 | 0.5943
|  | 2:44 | 7.0789 | 0.12677 | 0.5943
|  | 2:44 | 7.08 | 0.099932 | 0.5943
|  | 2:44 | 7.0811 | 0.080254 | 0.5943
|  | 2:44 | 7.0822 | 0.062962 | 0.59429
|  | 2:44 | 7.0833 | 0.049071 | 0.59429
|  | 2:44 | 7.0844 | 0.045383 | 0.59429
|  | 2:45 | 7.0856 | 0.041695 | 0.59429
|  | 2:45 | 7.0867 | 0.032198 | 0.59428
|  | 2:45 | 7.0878 | 0.020765 | 0.59428
|  | 2:45 | 7.0889 | 0.010218 | 0.59428
|  | 2:45 | 7.09 | 0.0023298 | 0.59428
|  | 2:45 | 7.0911 | -0.0055582 | 0.59428
|  | 2:45 | 7.0922 | -0.023576 | 0.59427
|  | 2:45 | 7.0933 | -0.04497 | 0.59427
|  | 2:45 | 7.0944 | -0.063236 | 0.59427
|  | 2:45 | 7.0956 | -0.072119 | 0.59427
|  | 2:45 | 7.0967 | -0.081002 | 0.59426
|  | 2:45 | 7.0978 | -0.091497 | 0.59426
|  | 2:45 | 7.0989 | -0.10253 | 0.59426
|  | 2:45 | 7.1 | -0.11184 | 0.59426
|  | 2:45 | 7.1011 | -0.11599 | 0.59425
|  | 2:46 | 7.1022 | -0.12014 | 0.59425
|  | 2:46 | 7.1033 | -0.12608 | 0.59425
|  | 2:46 | 7.1044 | -0.13383 | 0.59425
|  | 2:46 | 7.1056 | -0.14157 | 0.59425
|  | 2:46 | 7.1067 | -0.14002 | 0.59424
|  | 2:46 | 7.1078 | -0.13847 | 0.59424
|  | 2:46 | 7.1089 | -0.14396 | 0.59424
|  | 2:46 | 7.11 | -0.1565 | 0.59424
|  | 2:46 | 7.1111 | -0.16904 | 0.59423
|  | 2:46 | 7.1122 | -0.18405 | 0.59423
|  | 2:46 | 7.1133 | -0.19905 | 0.59423
|  | 2:46 | 7.1144 | -0.20539 | 0.59423
|  | 2:46 | 7.1156 | -0.20306 | 0.59422
|  | 2:46 | 7.1167 | -0.20073 | 0.59422
|  | 2:46 | 7.1178 | -0.17283 | 0.59422
|  | 2:47 | 7.1189 | -0.14493 | 0.59422
|  | 2:47 | 7.12 | -0.1155 | 0.59422
|  | 2:47 | 7.1211 | -0.084542 | 0.59421
|  | 2:47 | 7.1222 | -0.053583 | 0.59421
|  | 2:47 | 7.1233 | -0.01823 | 0.59421
|  | 2:47 | 7.1244 | 0.017124 | 0.59421
|  | 2:47 | 7.1256 | 0.042132 | 0.5942
|  | 2:47 | 7.1267 | 0.056796 | 0.5942
|  | 2:47 | 7.1278 | 0.07146 | 0.5942
|  | 2:47 | 7.1289 | 0.069582 | 0.5942
|  | 2:47 | 7.13 | 0.067705 | 0.59419
|  | 2:47 | 7.1311 | 0.068706 | 0.59419
|  | 2:47 | 7.1322 | 0.072586 | 0.59419
|  | 2:47 | 7.1333 | 0.076467 | 0.59419
|  | 2:47 | 7.1344 | 0.08665 | 0.59419
|  | 2:48 | 7.1356 | 0.096832 | 0.59418
|  | 2:48 | 7.1367 | 0.097433 | 0.59418
|  | 2:48 | 7.1378 | 0.088452 | 0.59418
|  | 2:48 | 7.1389 | 0.079471 | 0.59418
|  | 2:48 | 7.14 | 0.07049 | 0.59417
|  | 2:48 | 7.1411 | 0.061509 | 0.59417
|  | 2:48 | 7.1422 | 0.044761 | 0.59417
|  | 2:48 | 7.1433 | 0.020245 | 0.59417
|  | 2:48 | 7.1444 | -0.0042709 | 0.59416
|  | 2:48 | 7.1456 | -0.0071686 | 0.59416
|  | 2:48 | 7.1467 | -0.010066 | 0.59416
|  | 2:48 | 7.1478 | -0.015785 | 0.59416
|  | 2:48 | 7.1489 | -0.024325 | 0.59416
|  | 2:48 | 7.15 | -0.032865 | 0.59415
|  | 2:48 | 7.1511 | -0.041405 | 0.59415
|  | 2:49 | 7.1522 | -0.049945 | 0.59415
|  | 2:49 | 7.1533 | -0.061732 | 0.59415
|  | 2:49 | 7.1544 | -0.076764 | 0.59414
|  | 2:49 | 7.1556 | -0.091797 | 0.59414
|  | 2:49 | 7.1567 | -0.081949 | 0.59414
|  | 2:49 | 7.1578 | -0.072101 | 0.59414
|  | 2:49 | 7.1589 | -0.069993 | 0.59413
|  | 2:49 | 7.16 | -0.075625 | 0.59413
|  | 2:49 | 7.1611 | -0.081256 | 0.59413
|  | 2:49 | 7.1622 | -0.10398 | 0.59413
|  | 2:49 | 7.1633 | -0.12671 | 0.59412
|  | 2:49 | 7.1644 | -0.13424 | 0.59412
|  | 2:49 | 7.1656 | -0.13671 | 0.59412
|  | 2:49 | 7.1667 | -0.13917 | 0.59412
|  | 2:49 | 7.1678 | -0.13967 | 0.59412
|  | 2:50 | 7.1689 | -0.14016 | 0.59411
|  | 2:50 | 7.17 | -0.13967 | 0.59411
|  | 2:50 | 7.1711 | -0.1382 | 0.59411
|  | 2:50 | 7.1722 | -0.13672 | 0.59411
|  | 2:50 | 7.1733 | -0.13986 | 0.5941
|  | 2:50 | 7.1744 | -0.143 | 0.5941
|  | 2:50 | 7.1756 | -0.15783 | 0.5941
|  | 2:50 | 7.1767 | -0.18435 | 0.5941
|  | 2:50 | 7.1778 | -0.21088 | 0.59409
|  | 2:50 | 7.1789 | -0.23015 | 0.59409
|  | 2:50 | 7.18 | -0.24943 | 0.59409
|  | 2:50 | 7.1811 | -0.27026 | 0.59409
|  | 2:50 | 7.1822 | -0.29265 | 0.59409
|  | 2:50 | 7.1833 | -0.31503 | 0.59408
|  | 2:50 | 7.1844 | -0.32195 | 0.59408
|  | 2:51 | 7.1856 | -0.32886 | 0.59408
|  | 2:51 | 7.1867 | -0.34119 | 0.59408
|  | 2:51 | 7.1878 | -0.35894 | 0.59407
|  | 2:51 | 7.1889 | -0.37669 | 0.59407
|  | 2:51 | 7.19 | -0.40678 | 0.59407
|  | 2:51 | 7.1911 | -0.43687 | 0.59407
|  | 2:51 | 7.1922 | -0.47126 | 0.59406
|  | 2:51 | 7.1933 | -0.50996 | 0.59406
|  | 2:51 | 7.1944 | -0.54865 | 0.59406
|  | 2:51 | 7.1956 | -0.56956 | 0.59406
|  | 2:51 | 7.1967 | -0.59046 | 0.59406
|  | 2:51 | 7.1978 | -0.60099 | 0.59405
|  | 2:51 | 7.1989 | -0.60114 | 0.59405
|  | 2:51 | 7.2 | -0.60129 | 0.59405
|  | 2:51 | 7.2011 | -0.60725 | 0.59405
|  | 2:52 | 7.2022 | -0.6132 | 0.59404
|  | 2:52 | 7.2033 | -0.61495 | 0.59404
|  | 2:52 | 7.2044 | -0.6125 | 0.59404
|  | 2:52 | 7.2056 | -0.61004 | 0.59404
|  | 2:52 | 7.2067 | -0.60192 | 0.59403
|  | 2:52 | 7.2078 | -0.59379 | 0.59403
|  | 2:52 | 7.2089 | -0.57338 | 0.59403
|  | 2:52 | 7.21 | -0.54068 | 0.59403
|  | 2:52 | 7.2111 | -0.50798 | 0.59403
|  | 2:52 | 7.2122 | -0.44948 | 0.59402
|  | 2:52 | 7.2133 | -0.39097 | 0.59402
|  | 2:52 | 7.2144 | -0.34491 | 0.59402
|  | 2:52 | 7.2156 | -0.30298 | 0.59402
|  | 2:52 | 7.2167 | -0.26106 | 0.59401
|  | 2:52 | 7.2178 | -0.21372 | 0.59401
|  | 2:53 | 7.2189 | -0.16637 | 0.59401
|  | 2:53 | 7.22 | -0.13138 | 0.59401
|  | 2:53 | 7.2211 | -0.10875 | 0.594
|  | 2:53 | 7.2222 | -0.086123 | 0.594
|  | 2:53 | 7.2233 | -0.059309 | 0.594
|  | 2:53 | 7.2244 | -0.032495 | 0.594
|  | 2:53 | 7.2256 | -0.0085625 | 0.594
|  | 2:53 | 7.2267 | 0.01441 | 0.59399
|  | 2:53 | 7.2278 | 0.037382 | 0.59399
|  | 2:53 | 7.2289 | 0.066252 | 0.59399
|  | 2:53 | 7.23 | 0.095122 | 0.59399
|  | 2:53 | 7.2311 | 0.10872 | 0.59398
|  | 2:53 | 7.2322 | 0.10704 | 0.59398
|  | 2:53 | 7.2333 | 0.10536 | 0.59398
|  | 2:53 | 7.2344 | 0.10089 | 0.59398
|  | 2:54 | 7.2356 | 0.088038 | 0.59397
|  | 2:54 | 7.2367 | 0.080428 | 0.59397
|  | 2:54 | 7.2378 | 0.078054 | 0.59397
|  | 2:54 | 7.2389 | 0.07568 | 0.59397
|  | 2:54 | 7.24 | 0.060873 | 0.59397
|  | 2:54 | 7.2411 | 0.046067 | 0.59396
|  | 2:54 | 7.2422 | 0.032489 | 0.59396
|  | 2:54 | 7.2433 | 0.02014 | 0.59396
|  | 2:54 | 7.2444 | 0.0077913 | 0.59396
|  | 2:54 | 7.2456 | 0.0089382 | 0.59395
|  | 2:54 | 7.2467 | 0.010085 | 0.59395
|  | 2:54 | 7.2478 | 0.017944 | 0.59395
|  | 2:54 | 7.2489 | 0.032514 | 0.59395
|  | 2:54 | 7.25 | 0.047085 | 0.59394
|  | 2:54 | 7.2511 | 0.076109 | 0.59394
|  | 2:55 | 7.2522 | 0.10513 | 0.59394
|  | 2:55 | 7.2533 | 0.13867 | 0.59394
|  | 2:55 | 7.2544 | 0.17371 | 0.59394
|  | 2:55 | 7.2556 | 0.20875 | 0.59393
|  | 2:55 | 7.2567 | 0.23334 | 0.59393
|  | 2:55 | 7.2578 | 0.25792 | 0.59393
|  | 2:55 | 7.2589 | 0.27615 | 0.59393
|  | 2:55 | 7.26 | 0.28804 | 0.59392
|  | 2:55 | 7.2611 | 0.29992 | 0.59392
|  | 2:55 | 7.2622 | 0.31798 | 0.59392
|  | 2:55 | 7.2633 | 0.33605 | 0.59392
|  | 2:55 | 7.2644 | 0.36385 | 0.59391
|  | 2:55 | 7.2656 | 0.40137 | 0.59391
|  | 2:55 | 7.2667 | 0.4389 | 0.59391
|  | 2:55 | 7.2678 | 0.47837 | 0.59391
|  | 2:56 | 7.2689 | 0.51784 | 0.59391
|  | 2:56 | 7.27 | 0.54605 | 0.5939
|  | 2:56 | 7.2711 | 0.57051 | 0.5939
|  | 2:56 | 7.2722 | 0.59043 | 0.5939
|  | 2:56 | 7.2733 | 0.59672 | 0.5939
|  | 2:56 | 7.2744 | 0.60301 | 0.59389
|  | 2:56 | 7.2756 | 0.61476 | 0.59389
|  | 2:56 | 7.2767 | 0.62833 | 0.59389
|  | 2:56 | 7.2778 | 0.63908 | 0.59389
|  | 2:56 | 7.2789 | 0.64134 | 0.59388
|  | 2:56 | 7.28 | 0.6436 | 0.59388
|  | 2:56 | 7.2811 | 0.64966 | 0.59388
|  | 2:56 | 7.2822 | 0.65699 | 0.59388
|  | 2:56 | 7.2833 | 0.66861 | 0.59387
|  | 2:56 | 7.2844 | 0.69311 | 0.59387
|  | 2:57 | 7.2856 | 0.71761 | 0.59387
|  | 2:57 | 7.2867 | 0.72431 | 0.59387
|  | 2:57 | 7.2878 | 0.72507 | 0.59387
|  | 2:57 | 7.2889 | 0.72324 | 0.59386
|  | 2:57 | 7.29 | 0.71361 | 0.59386
|  | 2:57 | 7.2911 | 0.70399 | 0.59386
|  | 2:57 | 7.2922 | 0.68391 | 0.59386
|  | 2:57 | 7.2933 | 0.66036 | 0.59385
|  | 2:57 | 7.2944 | 0.63042 | 0.59385
|  | 2:57 | 7.2956 | 0.58134 | 0.59385
|  | 2:57 | 7.2967 | 0.53226 | 0.59385
|  | 2:57 | 7.2978 | 0.48119 | 0.59384
|  | 2:57 | 7.2989 | 0.42944 | 0.59384
|  | 2:57 | 7.3 | 0.38903 | 0.59384
|  | 2:57 | 7.3011 | 0.35995 | 0.59384
|  | 2:58 | 7.3022 | 0.33088 | 0.59384
|  | 2:58 | 7.3033 | 0.2821 | 0.59383
|  | 2:58 | 7.3044 | 0.22676 | 0.59383
|  | 2:58 | 7.3056 | 0.17658 | 0.59383
|  | 2:58 | 7.3067 | 0.1419 | 0.59383
|  | 2:58 | 7.3078 | 0.10722 | 0.59382
|  | 2:58 | 7.3089 | 0.081901 | 0.59382
|  | 2:58 | 7.31 | 0.056586 | 0.59382
|  | 2:58 | 7.3111 | 0.030142 | 0.59382
|  | 2:58 | 7.3122 | 0.00031549 | 0.59381
|  | 2:58 | 7.3133 | -0.029511 | 0.59381
|  | 2:58 | 7.3144 | -0.058698 | 0.59381
|  | 2:58 | 7.3156 | -0.087671 | 0.59381
|  | 2:58 | 7.3167 | -0.11306 | 0.59381
|  | 2:58 | 7.3178 | -0.12771 | 0.5938
|  | 2:59 | 7.3189 | -0.14236 | 0.5938
|  | 2:59 | 7.32 | -0.16624 | 0.5938
|  | 2:59 | 7.3211 | -0.1932 | 0.5938
|  | 2:59 | 7.3222 | -0.22575 | 0.59379
|  | 2:59 | 7.3233 | -0.2751 | 0.59379
|  | 2:59 | 7.3244 | -0.32445 | 0.59379
|  | 2:59 | 7.3256 | -0.35449 | 0.59379
|  | 2:59 | 7.3267 | -0.37809 | 0.59378
|  | 2:59 | 7.3278 | -0.39723 | 0.59378
|  | 2:59 | 7.3289 | -0.40298 | 0.59378
|  | 2:59 | 7.33 | -0.40874 | 0.59378
|  | 2:59 | 7.3311 | -0.41121 | 0.59378
|  | 2:59 | 7.3322 | -0.41258 | 0.59377
|  | 2:59 | 7.3333 | -0.4191 | 0.59377
|  | 2:59 | 7.3344 | -0.44105 | 0.59377
|  | 3:00 | 7.3356 | -0.46301 | 0.59377
|  | 3:00 | 7.3367 | -0.4794 | 0.59376
|  | 3:00 | 7.3378 | -0.49394 | 0.59376
|  | 3:00 | 7.3389 | -0.50803 | 0.59376
|  | 3:00 | 7.34 | -0.52082 | 0.59376
|  | 3:00 | 7.3411 | -0.53361 | 0.59375
|  | 3:00 | 7.3422 | -0.57167 | 0.59375
|  | 3:00 | 7.3433 | -0.61817 | 0.59375
|  | 3:00 | 7.3444 | -0.65686 | 0.59375
|  | 3:00 | 7.3456 | -0.67212 | 0.59375
|  | 3:00 | 7.3467 | -0.68739 | 0.59374
|  | 3:00 | 7.3478 | -0.69862 | 0.59374
|  | 3:00 | 7.3489 | -0.7085 | 0.59374
|  | 3:00 | 7.35 | -0.7136 | 0.59374
|  | 3:00 | 7.3511 | -0.70432 | 0.59373
|  | 3:01 | 7.3522 | -0.69505 | 0.59373
|  | 3:01 | 7.3533 | -0.67207 | 0.59373
|  | 3:01 | 7.3544 | -0.64451 | 0.59373
|  | 3:01 | 7.3556 | -0.61836 | 0.59372
|  | 3:01 | 7.3567 | -0.59644 | 0.59372
|  | 3:01 | 7.3578 | -0.57451 | 0.59372
|  | 3:01 | 7.3589 | -0.55325 | 0.59372
|  | 3:01 | 7.36 | -0.53222 | 0.59372
|  | 3:01 | 7.3611 | -0.51696 | 0.59371
|  | 3:01 | 7.3622 | -0.51903 | 0.59371
|  | 3:01 | 7.3633 | -0.5211 | 0.59371
|  | 3:01 | 7.3644 | -0.52402 | 0.59371
|  | 3:01 | 7.3656 | -0.52724 | 0.5937
|  | 3:01 | 7.3667 | -0.52781 | 0.5937
|  | 3:01 | 7.3678 | -0.52046 | 0.5937
|  | 3:02 | 7.3689 | -0.51311 | 0.5937
|  | 3:02 | 7.37 | -0.49295 | 0.59369
|  | 3:02 | 7.3711 | -0.46852 | 0.59369
|  | 3:02 | 7.3722 | -0.44277 | 0.59369
|  | 3:02 | 7.3733 | -0.41302 | 0.59369
|  | 3:02 | 7.3744 | -0.38327 | 0.59369
|  | 3:02 | 7.3756 | -0.36219 | 0.59368
|  | 3:02 | 7.3767 | -0.34399 | 0.59368
|  | 3:02 | 7.3778 | -0.32331 | 0.59368
|  | 3:02 | 7.3789 | -0.29521 | 0.59368
|  | 3:02 | 7.38 | -0.26711 | 0.59367
|  | 3:02 | 7.3811 | -0.22818 | 0.59367
|  | 3:02 | 7.3822 | -0.18565 | 0.59367
|  | 3:02 | 7.3833 | -0.14681 | 0.59367
|  | 3:02 | 7.3844 | -0.11909 | 0.59366
|  | 3:03 | 7.3856 | -0.091362 | 0.59366
|  | 3:03 | 7.3867 | -0.063635 | 0.59366
|  | 3:03 | 7.3878 | -0.035909 | 0.59366
|  | 3:03 | 7.3889 | -0.010399 | 0.59366
|  | 3:03 | 7.39 | 0.008462 | 0.59365
|  | 3:03 | 7.3911 | 0.027323 | 0.59365
|  | 3:03 | 7.3922 | 0.034398 | 0.59365
|  | 3:03 | 7.3933 | 0.037546 | 0.59365
|  | 3:03 | 7.3944 | 0.043552 | 0.59364
|  | 3:03 | 7.3956 | 0.058133 | 0.59364
|  | 3:03 | 7.3967 | 0.072714 | 0.59364
|  | 3:03 | 7.3978 | 0.058027 | 0.59364
|  | 3:03 | 7.3989 | 0.033585 | 0.59363
|  | 3:03 | 7.4 | 0.0091424 | 0.59363
|  | 3:03 | 7.4011 | -0.0069915 | 0.59363
|  | 3:04 | 7.4022 | -0.014817 | 0.59363
|  | 3:04 | 7.4033 | -0.013008 | 0.59362
|  | 3:04 | 7.4044 | -0.0079873 | 0.59362
|  | 3:04 | 7.4056 | -0.0032145 | 0.59362
|  | 3:04 | 7.4067 | 0.00081442 | 0.59362
|  | 3:04 | 7.4078 | 0.0048433 | 0.59362
|  | 3:04 | 7.4089 | -0.011699 | 0.59361
|  | 3:04 | 7.41 | -0.035099 | 0.59361
|  | 3:04 | 7.4111 | -0.062149 | 0.59361
|  | 3:04 | 7.4122 | -0.10015 | 0.59361
|  | 3:04 | 7.4133 | -0.13814 | 0.5936
|  | 3:04 | 7.4144 | -0.15922 | 0.5936
|  | 3:04 | 7.4156 | -0.17466 | 0.5936
|  | 3:04 | 7.4167 | -0.18651 | 0.5936
|  | 3:04 | 7.4178 | -0.18759 | 0.59359
|  | 3:05 | 7.4189 | -0.18868 | 0.59359
|  | 3:05 | 7.42 | -0.16432 | 0.59359
|  | 3:05 | 7.4211 | -0.13147 | 0.59359
|  | 3:05 | 7.4222 | -0.097254 | 0.59359
|  | 3:05 | 7.4233 | -0.058911 | 0.59358
|  | 3:05 | 7.4244 | -0.020569 | 0.59358
|  | 3:05 | 7.4256 | 0.017096 | 0.59358
|  | 3:05 | 7.4267 | 0.054534 | 0.59358
|  | 3:05 | 7.4278 | 0.085579 | 0.59357
|  | 3:05 | 7.4289 | 0.097447 | 0.59357
|  | 3:05 | 7.43 | 0.10931 | 0.59357
|  | 3:05 | 7.4311 | 0.11074 | 0.59357
|  | 3:05 | 7.4322 | 0.10868 | 0.59356
|  | 3:05 | 7.4333 | 0.10522 | 0.59356
|  | 3:05 | 7.4344 | 0.097578 | 0.59356
|  | 3:06 | 7.4356 | 0.089932 | 0.59356
|  | 3:06 | 7.4367 | 0.073569 | 0.59356
|  | 3:06 | 7.4378 | 0.048491 | 0.59355
|  | 3:06 | 7.4389 | 0.023412 | 0.59355
|  | 3:06 | 7.44 | 0.0095454 | 0.59355
|  | 3:06 | 7.4411 | -0.0043213 | 0.59355
|  | 3:06 | 7.4422 | -0.0022857 | 0.59354
|  | 3:06 | 7.4433 | 0.015652 | 0.59354
|  | 3:06 | 7.4444 | 0.03359 | 0.59354
|  | 3:06 | 7.4456 | 0.10038 | 0.59354
|  | 3:06 | 7.4467 | 0.16717 | 0.59353
|  | 3:06 | 7.4478 | 0.23184 | 0.59353
|  | 3:06 | 7.4489 | 0.29437 | 0.59353
|  | 3:06 | 7.45 | 0.35691 | 0.59353
|  | 3:06 | 7.4511 | 0.38203 | 0.59353
|  | 3:07 | 7.4522 | 0.40715 | 0.59352
|  | 3:07 | 7.4533 | 0.43669 | 0.59352
|  | 3:07 | 7.4544 | 0.47067 | 0.59352
|  | 3:07 | 7.4556 | 0.50464 | 0.59352
|  | 3:07 | 7.4567 | 0.51512 | 0.59351
|  | 3:07 | 7.4578 | 0.52559 | 0.59351
|  | 3:07 | 7.4589 | 0.54013 | 0.59351
|  | 3:07 | 7.46 | 0.55874 | 0.59351
|  | 3:07 | 7.4611 | 0.57735 | 0.5935
|  | 3:07 | 7.4622 | 0.57414 | 0.5935
|  | 3:07 | 7.4633 | 0.57092 | 0.5935
|  | 3:07 | 7.4644 | 0.57038 | 0.5935
|  | 3:07 | 7.4656 | 0.57251 | 0.5935
|  | 3:07 | 7.4667 | 0.57464 | 0.59349
|  | 3:07 | 7.4678 | 0.57446 | 0.59349
|  | 3:08 | 7.4689 | 0.57428 | 0.59349
|  | 3:08 | 7.47 | 0.56794 | 0.59349
|  | 3:08 | 7.4711 | 0.55544 | 0.59348
|  | 3:08 | 7.4722 | 0.54294 | 0.59348
|  | 3:08 | 7.4733 | 0.53362 | 0.59348
|  | 3:08 | 7.4744 | 0.52431 | 0.59348
|  | 3:08 | 7.4756 | 0.51346 | 0.59347
|  | 3:08 | 7.4767 | 0.50109 | 0.59347
|  | 3:08 | 7.4778 | 0.48871 | 0.59347
|  | 3:08 | 7.4789 | 0.46532 | 0.59347
|  | 3:08 | 7.48 | 0.44193 | 0.59347
|  | 3:08 | 7.4811 | 0.41736 | 0.59346
|  | 3:08 | 7.4822 | 0.39241 | 0.59346
|  | 3:08 | 7.4833 | 0.36745 | 0.59346
|  | 3:08 | 7.4844 | 0.32955 | 0.59346
|  | 3:09 | 7.4856 | 0.29165 | 0.59345
|  | 3:09 | 7.4867 | 0.25312 | 0.59345
|  | 3:09 | 7.4878 | 0.21396 | 0.59345
|  | 3:09 | 7.4889 | 0.1748 | 0.59345
|  | 3:09 | 7.49 | 0.11481 | 0.59344
|  | 3:09 | 7.4911 | 0.054818 | 0.59344
|  | 3:09 | 7.4922 | -0.0065868 | 0.59344
|  | 3:09 | 7.4933 | -0.068462 | 0.59344
|  | 3:09 | 7.4944 | -0.13034 | 0.59344
|  | 3:09 | 7.4956 | -0.17611 | 0.59343
|  | 3:09 | 7.4967 | -0.22189 | 0.59343
|  | 3:09 | 7.4978 | -0.26715 | 0.59343
|  | 3:09 | 7.4989 | -0.3119 | 0.59343
|  | 3:09 | 7.5 | -0.35665 | 0.59342
|  | 3:09 | 7.5011 | -0.39577 | 0.59342
|  | 3:10 | 7.5022 | -0.43489 | 0.59342
|  | 3:10 | 7.5033 | -0.45765 | 0.59342
|  | 3:10 | 7.5044 | -0.46406 | 0.59341
|  | 3:10 | 7.5056 | -0.47047 | 0.59341
|  | 3:10 | 7.5067 | -0.45239 | 0.59341
|  | 3:10 | 7.5078 | -0.4343 | 0.59341
|  | 3:10 | 7.5089 | -0.42879 | 0.59341
|  | 3:10 | 7.51 | -0.43588 | 0.5934
|  | 3:10 | 7.5111 | -0.44296 | 0.5934
|  | 3:10 | 7.5122 | -0.44646 | 0.5934
|  | 3:10 | 7.5133 | -0.44997 | 0.5934
|  | 3:10 | 7.5144 | -0.44712 | 0.59339
|  | 3:10 | 7.5156 | -0.43794 | 0.59339
|  | 3:10 | 7.5167 | -0.42875 | 0.59339
|  | 3:10 | 7.5178 | -0.42518 | 0.59339
|  | 3:11 | 7.5189 | -0.42161 | 0.59338
|  | 3:11 | 7.52 | -0.42556 | 0.59338
|  | 3:11 | 7.5211 | -0.43704 | 0.59338
|  | 3:11 | 7.5222 | -0.44852 | 0.59338
|  | 3:11 | 7.5233 | -0.44164 | 0.59337
|  | 3:11 | 7.5244 | -0.43475 | 0.59337
|  | 3:11 | 7.5256 | -0.42925 | 0.59337
|  | 3:11 | 7.5267 | -0.42513 | 0.59337
|  | 3:11 | 7.5278 | -0.421 | 0.59337
|  | 3:11 | 7.5289 | -0.40086 | 0.59336
|  | 3:11 | 7.53 | -0.38072 | 0.59336
|  | 3:11 | 7.5311 | -0.36457 | 0.59336
|  | 3:11 | 7.5322 | -0.35242 | 0.59336
|  | 3:11 | 7.5333 | -0.34187 | 0.59335
|  | 3:11 | 7.5344 | -0.33616 | 0.59335
|  | 3:12 | 7.5356 | -0.33044 | 0.59335
|  | 3:12 | 7.5367 | -0.31632 | 0.59335
|  | 3:12 | 7.5378 | -0.29381 | 0.59334
|  | 3:12 | 7.5389 | -0.2713 | 0.59334
|  | 3:12 | 7.54 | -0.25262 | 0.59334
|  | 3:12 | 7.5411 | -0.23394 | 0.59334
|  | 3:12 | 7.5422 | -0.21066 | 0.59334
|  | 3:12 | 7.5433 | -0.18278 | 0.59333
|  | 3:12 | 7.5444 | -0.1549 | 0.59333
|  | 3:12 | 7.5456 | -0.1598 | 0.59333
|  | 3:12 | 7.5467 | -0.1647 | 0.59333
|  | 3:12 | 7.5478 | -0.16862 | 0.59332
|  | 3:12 | 7.5489 | -0.17156 | 0.59332
|  | 3:12 | 7.55 | -0.17451 | 0.59332
|  | 3:12 | 7.5511 | -0.16854 | 0.59332
|  | 3:13 | 7.5522 | -0.16258 | 0.59331
|  | 3:13 | 7.5533 | -0.16124 | 0.59331
|  | 3:13 | 7.5544 | -0.16454 | 0.59331
|  | 3:13 | 7.5556 | -0.16783 | 0.59331
|  | 3:13 | 7.5567 | -0.15843 | 0.59331
|  | 3:13 | 7.5578 | -0.14903 | 0.5933
|  | 3:13 | 7.5589 | -0.12965 | 0.5933
|  | 3:13 | 7.56 | -0.10029 | 0.5933
|  | 3:13 | 7.5611 | -0.070943 | 0.5933
|  | 3:13 | 7.5622 | -0.066805 | 0.59329
|  | 3:13 | 7.5633 | -0.062667 | 0.59329
|  | 3:13 | 7.5644 | -0.054492 | 0.59329
|  | 3:13 | 7.5656 | -0.042281 | 0.59329
|  | 3:13 | 7.5667 | -0.030069 | 0.59328
|  | 3:13 | 7.5678 | -0.017858 | 0.59328
|  | 3:14 | 7.5689 | 0.0074794 | 0.59328
|  | 3:14 | 7.57 | 0.030449 | 0.59328
|  | 3:14 | 7.5711 | 0.046317 | 0.59328
|  | 3:14 | 7.5722 | 0.062185 | 0.59327
|  | 3:14 | 7.5733 | 0.082672 | 0.59327
|  | 3:14 | 7.5744 | 0.10316 | 0.59327
|  | 3:14 | 7.5756 | 0.12318 | 0.59327
|  | 3:14 | 7.5767 | 0.14273 | 0.59326
|  | 3:14 | 7.5778 | 0.16229 | 0.59326
|  | 3:14 | 7.5789 | 0.17597 | 0.59326
|  | 3:14 | 7.58 | 0.18965 | 0.59326
|  | 3:14 | 7.5811 | 0.21106 | 0.59325
|  | 3:14 | 7.5822 | 0.24018 | 0.59325
|  | 3:14 | 7.5833 | 0.2693 | 0.59325
|  | 3:14 | 7.5844 | 0.28985 | 0.59325
|  | 3:15 | 7.5856 | 0.3104 | 0.59325
|  | 3:15 | 7.5867 | 0.32411 | 0.59324
|  | 3:15 | 7.5878 | 0.33098 | 0.59324
|  | 3:15 | 7.5889 | 0.33785 | 0.59324
|  | 3:15 | 7.59 | 0.3406 | 0.59324
|  | 3:15 | 7.5911 | 0.34335 | 0.59323
|  | 3:15 | 7.5922 | 0.34433 | 0.59323
|  | 3:15 | 7.5933 | 0.34356 | 0.59323
|  | 3:15 | 7.5944 | 0.34278 | 0.59323
|  | 3:15 | 7.5956 | 0.3594 | 0.59322
|  | 3:15 | 7.5967 | 0.37602 | 0.59322
|  | 3:15 | 7.5978 | 0.39263 | 0.59322
|  | 3:15 | 7.5989 | 0.40925 | 0.59322
|  | 3:15 | 7.6 | 0.42587 | 0.59322
|  | 3:15 | 7.6011 | 0.4182 | 0.59321
|  | 3:16 | 7.6022 | 0.41053 | 0.59321
|  | 3:16 | 7.6033 | 0.39842 | 0.59321
|  | 3:16 | 7.6044 | 0.38187 | 0.59321
|  | 3:16 | 7.6056 | 0.36532 | 0.5932
|  | 3:16 | 7.6067 | 0.33087 | 0.5932
|  | 3:16 | 7.6078 | 0.29642 | 0.5932
|  | 3:16 | 7.6089 | 0.28083 | 0.5932
|  | 3:16 | 7.61 | 0.28412 | 0.59319
|  | 3:16 | 7.6111 | 0.2874 | 0.59319
|  | 3:16 | 7.6122 | 0.2724 | 0.59319
|  | 3:16 | 7.6133 | 0.2574 | 0.59319
|  | 3:16 | 7.6144 | 0.2361 | 0.59319
|  | 3:16 | 7.6156 | 0.2085 | 0.59318
|  | 3:16 | 7.6167 | 0.18089 | 0.59318
|  | 3:16 | 7.6178 | 0.14929 | 0.59318
|  | 3:17 | 7.6189 | 0.11769 | 0.59318
|  | 3:17 | 7.62 | 0.10424 | 0.59317
|  | 3:17 | 7.6211 | 0.096831 | 0.59317
|  | 3:17 | 7.6222 | 0.089426 | 0.59317
|  | 3:17 | 7.6233 | 0.072852 | 0.59317
|  | 3:17 | 7.6244 | 0.056277 | 0.59316
|  | 3:17 | 7.6256 | 0.041294 | 0.59316
|  | 3:17 | 7.6267 | 0.027902 | 0.59316
|  | 3:17 | 7.6278 | 0.01451 | 0.59316
|  | 3:17 | 7.6289 | -0.0091688 | 0.59316
|  | 3:17 | 7.63 | -0.032848 | 0.59315
|  | 3:17 | 7.6311 | -0.066966 | 0.59315
|  | 3:17 | 7.6322 | -0.11152 | 0.59315
|  | 3:17 | 7.6333 | -0.15608 | 0.59315
|  | 3:17 | 7.6344 | -0.17782 | 0.59314
|  | 3:18 | 7.6356 | -0.19956 | 0.59314
|  | 3:18 | 7.6367 | -0.21505 | 0.59314
|  | 3:18 | 7.6378 | -0.2243 | 0.59314
|  | 3:18 | 7.6389 | -0.23485 | 0.59313
|  | 3:18 | 7.64 | -0.24933 | 0.59313
|  | 3:18 | 7.6411 | -0.26381 | 0.59313
|  | 3:18 | 7.6422 | -0.28585 | 0.59313
|  | 3:18 | 7.6433 | -0.31041 | 0.59312
|  | 3:18 | 7.6444 | -0.33498 | 0.59312
|  | 3:18 | 7.6456 | -0.35433 | 0.59312
|  | 3:18 | 7.6467 | -0.37369 | 0.59312
|  | 3:18 | 7.6478 | -0.38334 | 0.59312
|  | 3:18 | 7.6489 | -0.38329 | 0.59311
|  | 3:18 | 7.65 | -0.38325 | 0.59311
|  | 3:18 | 7.6511 | -0.37177 | 0.59311
|  | 3:19 | 7.6522 | -0.36028 | 0.59311
|  | 3:19 | 7.6533 | -0.34955 | 0.5931
|  | 3:19 | 7.6544 | -0.33956 | 0.5931
|  | 3:19 | 7.6556 | -0.32957 | 0.5931
|  | 3:19 | 7.6567 | -0.32282 | 0.5931
|  | 3:19 | 7.6578 | -0.31608 | 0.59309
|  | 3:19 | 7.6589 | -0.30933 | 0.59309
|  | 3:19 | 7.66 | -0.30258 | 0.59309
|  | 3:19 | 7.6611 | -0.2977 | 0.59309
|  | 3:19 | 7.6622 | -0.29843 | 0.59309
|  | 3:19 | 7.6633 | -0.29916 | 0.59308
|  | 3:19 | 7.6644 | -0.3059 | 0.59308
|  | 3:19 | 7.6656 | -0.31865 | 0.59308
|  | 3:19 | 7.6667 | -0.33141 | 0.59308
|  | 3:19 | 7.6678 | -0.34928 | 0.59307
|  | 3:20 | 7.6689 | -0.36715 | 0.59307
|  | 3:20 | 7.67 | -0.36743 | 0.59307
|  | 3:20 | 7.6711 | -0.35014 | 0.59307
|  | 3:20 | 7.6722 | -0.33284 | 0.59306
|  | 3:20 | 7.6733 | -0.32614 | 0.59306
|  | 3:20 | 7.6744 | -0.31945 | 0.59306
|  | 3:20 | 7.6756 | -0.32347 | 0.59306
|  | 3:20 | 7.6767 | -0.33105 | 0.59306
|  | 3:20 | 7.6778 | -0.33863 | 0.59305
|  | 3:20 | 7.6789 | -0.34742 | 0.59305
|  | 3:20 | 7.68 | -0.35621 | 0.59305
|  | 3:20 | 7.6811 | -0.35525 | 0.59305
|  | 3:20 | 7.6822 | -0.34453 | 0.59304
|  | 3:20 | 7.6833 | -0.33382 | 0.59304
|  | 3:20 | 7.6844 | -0.32408 | 0.59304
|  | 3:21 | 7.6856 | -0.31435 | 0.59304
|  | 3:21 | 7.6867 | -0.29629 | 0.59303
|  | 3:21 | 7.6878 | -0.2699 | 0.59303
|  | 3:21 | 7.6889 | -0.24351 | 0.59303
|  | 3:21 | 7.69 | -0.22981 | 0.59303
|  | 3:21 | 7.6911 | -0.21611 | 0.59303
|  | 3:21 | 7.6922 | -0.19988 | 0.59302
|  | 3:21 | 7.6933 | -0.18112 | 0.59302
|  | 3:21 | 7.6944 | -0.16235 | 0.59302
|  | 3:21 | 7.6956 | -0.16142 | 0.59302
|  | 3:21 | 7.6967 | -0.16049 | 0.59301
|  | 3:21 | 7.6978 | -0.15389 | 0.59301
|  | 3:21 | 7.6989 | -0.14164 | 0.59301
|  | 3:21 | 7.7 | -0.12939 | 0.59301
|  | 3:21 | 7.7011 | -0.12526 | 0.593
|  | 3:22 | 7.7022 | -0.12113 | 0.593
|  | 3:22 | 7.7033 | -0.12313 | 0.593
|  | 3:22 | 7.7044 | -0.13125 | 0.593
|  | 3:22 | 7.7056 | -0.13938 | 0.593
|  | 3:22 | 7.7067 | -0.13197 | 0.59299
|  | 3:22 | 7.7078 | -0.12456 | 0.59299
|  | 3:22 | 7.7089 | -0.11274 | 0.59299
|  | 3:22 | 7.71 | -0.096521 | 0.59299
|  | 3:22 | 7.7111 | -0.080302 | 0.59298
|  | 3:22 | 7.7122 | -0.054155 | 0.59298
|  | 3:22 | 7.7133 | -0.028008 | 0.59298
|  | 3:22 | 7.7144 | -0.0045076 | 0.59298
|  | 3:22 | 7.7156 | 0.016347 | 0.59297
|  | 3:22 | 7.7167 | 0.037201 | 0.59297
|  | 3:22 | 7.7178 | 0.038561 | 0.59297
|  | 3:23 | 7.7189 | 0.039921 | 0.59297
|  | 3:23 | 7.72 | 0.04462 | 0.59297
|  | 3:23 | 7.7211 | 0.052657 | 0.59296
|  | 3:23 | 7.7222 | 0.060695 | 0.59296
|  | 3:23 | 7.7233 | 0.062016 | 0.59296
|  | 3:23 | 7.7244 | 0.063337 | 0.59296
|  | 3:23 | 7.7256 | 0.059152 | 0.59295
|  | 3:23 | 7.7267 | 0.049461 | 0.59295
|  | 3:23 | 7.7278 | 0.039771 | 0.59295
|  | 3:23 | 7.7289 | 0.03008 | 0.59295
|  | 3:23 | 7.73 | 0.02039 | 0.59294
|  | 3:23 | 7.7311 | 0.012533 | 0.59294
|  | 3:23 | 7.7322 | 0.00651 | 0.59294
|  | 3:23 | 7.7333 | 0.00048686 | 0.59294
|  | 3:23 | 7.7344 | -0.0055363 | 0.59294
|  | 3:24 | 7.7356 | -0.028667 | 0.59293
|  | 3:24 | 7.7367 | -0.055754 | 0.59293
|  | 3:24 | 7.7378 | -0.094714 | 0.59293
|  | 3:24 | 7.7389 | -0.13367 | 0.59293
|  | 3:24 | 7.74 | -0.1564 | 0.59292
|  | 3:24 | 7.7411 | -0.17912 | 0.59292
|  | 3:24 | 7.7422 | -0.20465 | 0.59292
|  | 3:24 | 7.7433 | -0.23296 | 0.59292
|  | 3:24 | 7.7444 | -0.26128 | 0.59291
|  | 3:24 | 7.7456 | -0.28713 | 0.59291
|  | 3:24 | 7.7467 | -0.31299 | 0.59291
|  | 3:24 | 7.7478 | -0.3269 | 0.59291
|  | 3:24 | 7.7489 | -0.32887 | 0.59291
|  | 3:24 | 7.75 | -0.33084 | 0.5929
|  | 3:24 | 7.7511 | -0.34417 | 0.5929
|  | 3:25 | 7.7522 | -0.35749 | 0.5929
|  | 3:25 | 7.7533 | -0.36829 | 0.5929
|  | 3:25 | 7.7544 | -0.37657 | 0.59289
|  | 3:25 | 7.7556 | -0.38484 | 0.59289
|  | 3:25 | 7.7567 | -0.39763 | 0.59289
|  | 3:25 | 7.7578 | -0.41043 | 0.59289
|  | 3:25 | 7.7589 | -0.42784 | 0.59288
|  | 3:25 | 7.76 | -0.44987 | 0.59288
|  | 3:25 | 7.7611 | -0.4719 | 0.59288
|  | 3:25 | 7.7622 | -0.49075 | 0.59288
|  | 3:25 | 7.7633 | -0.50959 | 0.59287
|  | 3:25 | 7.7644 | -0.5272 | 0.59287
|  | 3:25 | 7.7656 | -0.54355 | 0.59287
|  | 3:25 | 7.7667 | -0.5599 | 0.59287
|  | 3:25 | 7.7678 | -0.58263 | 0.59287
|  | 3:26 | 7.7689 | -0.60537 | 0.59286
|  | 3:26 | 7.77 | -0.62365 | 0.59286
|  | 3:26 | 7.7711 | -0.63747 | 0.59286
|  | 3:26 | 7.7722 | -0.65129 | 0.59286
|  | 3:26 | 7.7733 | -0.65879 | 0.59285
|  | 3:26 | 7.7744 | -0.66629 | 0.59285
|  | 3:26 | 7.7756 | -0.67986 | 0.59285
|  | 3:26 | 7.7767 | -0.6995 | 0.59285
|  | 3:26 | 7.7778 | -0.71913 | 0.59284
|  | 3:26 | 7.7789 | -0.73168 | 0.59284
|  | 3:26 | 7.78 | -0.74423 | 0.59284
|  | 3:26 | 7.7811 | -0.7505 | 0.59284
|  | 3:26 | 7.7822 | -0.75049 | 0.59284
|  | 3:26 | 7.7833 | -0.75048 | 0.59283
|  | 3:26 | 7.7844 | -0.73916 | 0.59283
|  | 3:27 | 7.7856 | -0.72783 | 0.59283
|  | 3:27 | 7.7867 | -0.70987 | 0.59283
|  | 3:27 | 7.7878 | -0.68526 | 0.59282
|  | 3:27 | 7.7889 | -0.66066 | 0.59282
|  | 3:27 | 7.79 | -0.6495 | 0.59282
|  | 3:27 | 7.7911 | -0.63834 | 0.59282
|  | 3:27 | 7.7922 | -0.61665 | 0.59281
|  | 3:27 | 7.7933 | -0.58443 | 0.59281
|  | 3:27 | 7.7944 | -0.55221 | 0.59281
|  | 3:27 | 7.7956 | -0.51541 | 0.59281
|  | 3:27 | 7.7967 | -0.47861 | 0.59281
|  | 3:27 | 7.7978 | -0.44523 | 0.5928
|  | 3:27 | 7.7989 | -0.41524 | 0.5928
|  | 3:27 | 7.8 | -0.38526 | 0.5928
|  | 3:27 | 7.8011 | -0.37899 | 0.5928
|  | 3:28 | 7.8022 | -0.37271 | 0.59279
|  | 3:28 | 7.8033 | -0.37159 | 0.59279
|  | 3:28 | 7.8044 | -0.37563 | 0.59279
|  | 3:28 | 7.8056 | -0.37966 | 0.59279
|  | 3:28 | 7.8067 | -0.36377 | 0.59278
|  | 3:28 | 7.8078 | -0.34788 | 0.59278
|  | 3:28 | 7.8089 | -0.32774 | 0.59278
|  | 3:28 | 7.81 | -0.30335 | 0.59278
|  | 3:28 | 7.8111 | -0.27896 | 0.59278
|  | 3:28 | 7.8122 | -0.25074 | 0.59277
|  | 3:28 | 7.8133 | -0.22252 | 0.59277
|  | 3:28 | 7.8144 | -0.19509 | 0.59277
|  | 3:28 | 7.8156 | -0.16792 | 0.59277
|  | 3:28 | 7.8167 | -0.14272 | 0.59276
|  | 3:28 | 7.8178 | -0.12345 | 0.59276
|  | 3:29 | 7.8189 | -0.10417 | 0.59276
|  | 3:29 | 7.82 | -0.087397 | 0.59276
|  | 3:29 | 7.8211 | -0.07313 | 0.59275
|  | 3:29 | 7.8222 | -0.058863 | 0.59275
|  | 3:29 | 7.8233 | -0.061269 | 0.59275
|  | 3:29 | 7.8244 | -0.063676 | 0.59275
|  | 3:29 | 7.8256 | -0.065522 | 0.59275
|  | 3:29 | 7.8267 | -0.066808 | 0.59274
|  | 3:29 | 7.8278 | -0.068094 | 0.59274
|  | 3:29 | 7.8289 | -0.075492 | 0.59274
|  | 3:29 | 7.83 | -0.08289 | 0.59274
|  | 3:29 | 7.8311 | -0.09073 | 0.59273
|  | 3:29 | 7.8322 | -0.099014 | 0.59273
|  | 3:29 | 7.8333 | -0.1073 | 0.59273
|  | 3:29 | 7.8344 | -0.089359 | 0.59273
|  | 3:30 | 7.8356 | -0.071421 | 0.59272
|  | 3:30 | 7.8367 | -0.049309 | 0.59272
|  | 3:30 | 7.8378 | -0.023023 | 0.59272
|  | 3:30 | 7.8389 | 0.0032623 | 0.59272
|  | 3:30 | 7.84 | 0.016532 | 0.59272
|  | 3:30 | 7.8411 | 0.029801 | 0.59271
|  | 3:30 | 7.8422 | 0.036497 | 0.59271
|  | 3:30 | 7.8433 | 0.03662 | 0.59271
|  | 3:30 | 7.8444 | 0.036742 | 0.59271
|  | 3:30 | 7.8456 | 0.031934 | 0.5927
|  | 3:30 | 7.8467 | 0.027126 | 0.5927
|  | 3:30 | 7.8478 | 0.038487 | 0.5927
|  | 3:30 | 7.8489 | 0.06602 | 0.5927
|  | 3:30 | 7.85 | 0.093552 | 0.59269
|  | 3:30 | 7.8511 | 0.12924 | 0.59269
|  | 3:31 | 7.8522 | 0.16492 | 0.59269
|  | 3:31 | 7.8533 | 0.19135 | 0.59269
|  | 3:31 | 7.8544 | 0.20853 | 0.59269
|  | 3:31 | 7.8556 | 0.2257 | 0.59268
|  | 3:31 | 7.8567 | 0.2251 | 0.59268
|  | 3:31 | 7.8578 | 0.22449 | 0.59268
|  | 3:31 | 7.8589 | 0.21902 | 0.59268
|  | 3:31 | 7.86 | 0.2087 | 0.59267
|  | 3:31 | 7.8611 | 0.19838 | 0.59267
|  | 3:31 | 7.8622 | 0.17104 | 0.59267
|  | 3:31 | 7.8633 | 0.14371 | 0.59267
|  | 3:31 | 7.8644 | 0.12041 | 0.59266
|  | 3:31 | 7.8656 | 0.10116 | 0.59266
|  | 3:31 | 7.8667 | 0.081902 | 0.59266
|  | 3:31 | 7.8678 | 0.099815 | 0.59266
|  | 3:32 | 7.8689 | 0.11773 | 0.59266
|  | 3:32 | 7.87 | 0.13342 | 0.59265
|  | 3:32 | 7.8711 | 0.14689 | 0.59265
|  | 3:32 | 7.8722 | 0.16036 | 0.59265
|  | 3:32 | 7.8733 | 0.17384 | 0.59265
|  | 3:32 | 7.8744 | 0.18731 | 0.59264
|  | 3:32 | 7.8756 | 0.20476 | 0.59264
|  | 3:32 | 7.8767 | 0.22619 | 0.59264
|  | 3:32 | 7.8778 | 0.24763 | 0.59264
|  | 3:32 | 7.8789 | 0.26643 | 0.59263
|  | 3:32 | 7.88 | 0.28523 | 0.59263
|  | 3:32 | 7.8811 | 0.29984 | 0.59263
|  | 3:32 | 7.8822 | 0.31025 | 0.59263
|  | 3:32 | 7.8833 | 0.32066 | 0.59262
|  | 3:32 | 7.8844 | 0.33434 | 0.59262
|  | 3:33 | 7.8856 | 0.34802 | 0.59262
|  | 3:33 | 7.8867 | 0.36502 | 0.59262
|  | 3:33 | 7.8878 | 0.38533 | 0.59262
|  | 3:33 | 7.8889 | 0.40565 | 0.59261
|  | 3:33 | 7.89 | 0.42159 | 0.59261
|  | 3:33 | 7.8911 | 0.43753 | 0.59261
|  | 3:33 | 7.8922 | 0.45058 | 0.59261
|  | 3:33 | 7.8933 | 0.46075 | 0.5926
|  | 3:33 | 7.8944 | 0.47091 | 0.5926
|  | 3:33 | 7.8956 | 0.47039 | 0.5926
|  | 3:33 | 7.8967 | 0.46987 | 0.5926
|  | 3:33 | 7.8978 | 0.46317 | 0.59259
|  | 3:33 | 7.8989 | 0.45441 | 0.59259
|  | 3:33 | 7.9 | 0.44565 | 0.59259
|  | 3:33 | 7.9011 | 0.42328 | 0.59259
|  | 3:34 | 7.9022 | 0.4009 | 0.59259
|  | 3:34 | 7.9033 | 0.38572 | 0.59258
|  | 3:34 | 7.9044 | 0.39211 | 0.59258
|  | 3:34 | 7.9056 | 0.3985 | 0.59258
|  | 3:34 | 7.9067 | 0.4237 | 0.59258
|  | 3:34 | 7.9078 | 0.4489 | 0.59257
|  | 3:34 | 7.9089 | 0.46088 | 0.59257
|  | 3:34 | 7.91 | 0.45964 | 0.59257
|  | 3:34 | 7.9111 | 0.45841 | 0.59257
|  | 3:34 | 7.9122 | 0.4475 | 0.59256
|  | 3:34 | 7.9133 | 0.43659 | 0.59256
|  | 3:34 | 7.9144 | 0.42325 | 0.59256
|  | 3:34 | 7.9156 | 0.40749 | 0.59256
|  | 3:34 | 7.9167 | 0.39172 | 0.59256
|  | 3:34 | 7.9178 | 0.40531 | 0.59255
|  | 3:35 | 7.9189 | 0.4189 | 0.59255
|  | 3:35 | 7.92 | 0.43151 | 0.59255
|  | 3:35 | 7.9211 | 0.44314 | 0.59255
|  | 3:35 | 7.9222 | 0.45477 | 0.59254
|  | 3:35 | 7.9233 | 0.4521 | 0.59254
|  | 3:35 | 7.9244 | 0.44943 | 0.59254
|  | 3:35 | 7.9256 | 0.43991 | 0.59254
|  | 3:35 | 7.9267 | 0.42354 | 0.59253
|  | 3:35 | 7.9278 | 0.40717 | 0.59253
|  | 3:35 | 7.9289 | 0.40518 | 0.59253
|  | 3:35 | 7.93 | 0.40319 | 0.59253
|  | 3:35 | 7.9311 | 0.41374 | 0.59253
|  | 3:35 | 7.9322 | 0.43682 | 0.59252
|  | 3:35 | 7.9333 | 0.45991 | 0.59252
|  | 3:35 | 7.9344 | 0.48429 | 0.59252
|  | 3:36 | 7.9356 | 0.50867 | 0.59252
|  | 3:36 | 7.9367 | 0.52763 | 0.59251
|  | 3:36 | 7.9378 | 0.54478 | 0.59251
|  | 3:36 | 7.9389 | 0.56194 | 0.59251
|  | 3:36 | 7.94 | 0.57207 | 0.59251
|  | 3:36 | 7.9411 | 0.58221 | 0.5925
|  | 3:36 | 7.9422 | 0.58718 | 0.5925
|  | 3:36 | 7.9433 | 0.58698 | 0.5925
|  | 3:36 | 7.9444 | 0.58678 | 0.5925
|  | 3:36 | 7.9456 | 0.60128 | 0.5925
|  | 3:36 | 7.9467 | 0.61578 | 0.59249
|  | 3:36 | 7.9478 | 0.62143 | 0.59249
|  | 3:36 | 7.9489 | 0.61825 | 0.59249
|  | 3:36 | 7.95 | 0.61506 | 0.59249
|  | 3:36 | 7.9511 | 0.62239 | 0.59248
|  | 3:37 | 7.9522 | 0.62971 | 0.59248
|  | 3:37 | 7.9533 | 0.63355 | 0.59248
|  | 3:37 | 7.9544 | 0.6339 | 0.59248
|  | 3:37 | 7.9556 | 0.63907 | 0.59247
|  | 3:37 | 7.9567 | 0.65868 | 0.59247
|  | 3:37 | 7.9578 | 0.6783 | 0.59247
|  | 3:37 | 7.9589 | 0.69792 | 0.59247
|  | 3:37 | 7.96 | 0.71754 | 0.59247
|  | 3:37 | 7.9611 | 0.73715 | 0.59246
|  | 3:37 | 7.9622 | 0.75945 | 0.59246
|  | 3:37 | 7.9633 | 0.78175 | 0.59246
|  | 3:37 | 7.9644 | 0.79371 | 0.59246
|  | 3:37 | 7.9656 | 0.79532 | 0.59245
|  | 3:37 | 7.9667 | 0.79693 | 0.59245
|  | 3:37 | 7.9678 | 0.81251 | 0.59245
|  | 3:38 | 7.9689 | 0.82809 | 0.59245
|  | 3:38 | 7.97 | 0.83863 | 0.59244
|  | 3:38 | 7.9711 | 0.84413 | 0.59244
|  | 3:38 | 7.9722 | 0.84963 | 0.59244
|  | 3:38 | 7.9733 | 0.82497 | 0.59244
|  | 3:38 | 7.9744 | 0.8003 | 0.59244
|  | 3:38 | 7.9756 | 0.77953 | 0.59243
|  | 3:38 | 7.9767 | 0.76265 | 0.59243
|  | 3:38 | 7.9778 | 0.74578 | 0.59243
|  | 3:38 | 7.9789 | 0.7289 | 0.59243
|  | 3:38 | 7.98 | 0.71203 | 0.59242
|  | 3:38 | 7.9811 | 0.69599 | 0.59242
|  | 3:38 | 7.9822 | 0.68079 | 0.59242
|  | 3:38 | 7.9833 | 0.66559 | 0.59242
|  | 3:38 | 7.9844 | 0.65039 | 0.59241
|  | 3:39 | 7.9856 | 0.63519 | 0.59241
|  | 3:39 | 7.9867 | 0.6287 | 0.59241
|  | 3:39 | 7.9878 | 0.62511 | 0.59241
|  | 3:39 | 7.9889 | 0.62152 | 0.59241
|  | 3:39 | 7.99 | 0.60905 | 0.5924
|  | 3:39 | 7.9911 | 0.59658 | 0.5924
|  | 3:39 | 7.9922 | 0.59451 | 0.5924
|  | 3:39 | 7.9933 | 0.60285 | 0.5924
|  | 3:39 | 7.9944 | 0.61119 | 0.59239
|  | 3:39 | 7.9956 | 0.62747 | 0.59239
|  | 3:39 | 7.9967 | 0.64374 | 0.59239
|  | 3:39 | 7.9978 | 0.64699 | 0.59239
|  | 3:39 | 7.9989 | 0.6372 | 0.59238
|  | 3:39 | 8 | 0.62494 | 0.59238
|  | 3:39 | 8.0011 | 0.60529 | 0.59238
|  | 3:40 | 8.0022 | 0.58564 | 0.59238
|  | 3:40 | 8.0033 | 0.56408 | 0.59237
|  | 3:40 | 8.0044 | 0.54061 | 0.59237
|  | 3:40 | 8.0056 | 0.51713 | 0.59237
|  | 3:40 | 8.0067 | 0.50205 | 0.59237
|  | 3:40 | 8.0078 | 0.48696 | 0.59237
|  | 3:40 | 8.0089 | 0.46771 | 0.59236
|  | 3:40 | 8.01 | 0.4443 | 0.59236
|  | 3:40 | 8.0111 | 0.4209 | 0.59236
|  | 3:40 | 8.0122 | 0.38558 | 0.59236
|  | 3:40 | 8.0133 | 0.35026 | 0.59235
|  | 3:40 | 8.0144 | 0.31233 | 0.59235
|  | 3:40 | 8.0156 | 0.27179 | 0.59235
|  | 3:40 | 8.0167 | 0.23124 | 0.59235
|  | 3:40 | 8.0178 | 0.20065 | 0.59234
|  | 3:41 | 8.0189 | 0.17005 | 0.59234
|  | 3:41 | 8.02 | 0.14077 | 0.59234
|  | 3:41 | 8.0211 | 0.11281 | 0.59234
|  | 3:41 | 8.0222 | 0.084842 | 0.59234
|  | 3:41 | 8.0233 | 0.038603 | 0.59233
|  | 3:41 | 8.0244 | -0.0076366 | 0.59233
|  | 3:41 | 8.0256 | -0.047739 | 0.59233
|  | 3:41 | 8.0267 | -0.081703 | 0.59233
|  | 3:41 | 8.0278 | -0.11567 | 0.59232
|  | 3:41 | 8.0289 | -0.13646 | 0.59232
|  | 3:41 | 8.03 | -0.15725 | 0.59232
|  | 3:41 | 8.0311 | -0.18325 | 0.59232
|  | 3:41 | 8.0322 | -0.21444 | 0.59231
|  | 3:41 | 8.0333 | -0.24563 | 0.59231
|  | 3:41 | 8.0344 | -0.2745 | 0.59231
|  | 3:42 | 8.0356 | -0.30336 | 0.59231
|  | 3:42 | 8.0367 | -0.34175 | 0.59231
|  | 3:42 | 8.0378 | -0.38967 | 0.5923
|  | 3:42 | 8.0389 | -0.42638 | 0.5923
|  | 3:42 | 8.04 | -0.42948 | 0.5923
|  | 3:42 | 8.0411 | -0.43258 | 0.5923
|  | 3:42 | 8.0422 | -0.44921 | 0.59229
|  | 3:42 | 8.0433 | -0.47935 | 0.59229
|  | 3:42 | 8.0444 | -0.5095 | 0.59229
|  | 3:42 | 8.0456 | -0.53188 | 0.59229
|  | 3:42 | 8.0467 | -0.55427 | 0.59228
|  | 3:42 | 8.0478 | -0.57911 | 0.59228
|  | 3:42 | 8.0489 | -0.60641 | 0.59228
|  | 3:42 | 8.05 | -0.63371 | 0.59228
|  | 3:42 | 8.0511 | -0.64927 | 0.59228
|  | 3:43 | 8.0522 | -0.66484 | 0.59227
|  | 3:43 | 8.0533 | -0.6804 | 0.59227
|  | 3:43 | 8.0544 | -0.69596 | 0.59227
|  | 3:43 | 8.0556 | -0.71153 | 0.59227
|  | 3:43 | 8.0567 | -0.72418 | 0.59226
|  | 3:43 | 8.0578 | -0.73684 | 0.59226
|  | 3:43 | 8.0589 | -0.73522 | 0.59226
|  | 3:43 | 8.06 | -0.71932 | 0.59226
|  | 3:43 | 8.0611 | -0.70341 | 0.59225
|  | 3:43 | 8.0622 | -0.67074 | 0.59225
|  | 3:43 | 8.0633 | -0.63806 | 0.59225
|  | 3:43 | 8.0644 | -0.60994 | 0.59225
|  | 3:43 | 8.0656 | -0.58635 | 0.59225
|  | 3:43 | 8.0667 | -0.56277 | 0.59224
|  | 3:43 | 8.0678 | -0.53527 | 0.59224
|  | 3:44 | 8.0689 | -0.50776 | 0.59224
|  | 3:44 | 8.07 | -0.48763 | 0.59224
|  | 3:44 | 8.0711 | -0.48964 | 0.59223
|  | 3:44 | 8.0722 | -0.49165 | 0.59223
|  | 3:44 | 8.0733 | -0.49001 | 0.59223
|  | 3:44 | 8.0744 | -0.48837 | 0.59223
|  | 3:44 | 8.0756 | -0.48899 | 0.59222
|  | 3:44 | 8.0767 | -0.49188 | 0.59222
|  | 3:44 | 8.0778 | -0.49352 | 0.59222
|  | 3:44 | 8.0789 | -0.49142 | 0.59222
|  | 3:44 | 8.08 | -0.48932 | 0.59222
|  | 3:44 | 8.0811 | -0.49175 | 0.59221
|  | 3:44 | 8.0822 | -0.4987 | 0.59221
|  | 3:44 | 8.0833 | -0.50565 | 0.59221
|  | 3:44 | 8.0844 | -0.50288 | 0.59221
|  | 3:45 | 8.0856 | -0.50011 | 0.5922
|  | 3:45 | 8.0867 | -0.48826 | 0.5922
|  | 3:45 | 8.0878 | -0.46731 | 0.5922
|  | 3:45 | 8.0889 | -0.44636 | 0.5922
|  | 3:45 | 8.09 | -0.413 | 0.59219
|  | 3:45 | 8.0911 | -0.37965 | 0.59219
|  | 3:45 | 8.0922 | -0.35026 | 0.59219
|  | 3:45 | 8.0933 | -0.32485 | 0.59219
|  | 3:45 | 8.0944 | -0.29944 | 0.59219
|  | 3:45 | 8.0956 | -0.27642 | 0.59218
|  | 3:45 | 8.0967 | -0.2534 | 0.59218
|  | 3:45 | 8.0978 | -0.236 | 0.59218
|  | 3:45 | 8.0989 | -0.22421 | 0.59218
|  | 3:45 | 8.1 | -0.21242 | 0.59217
|  | 3:45 | 8.1011 | -0.18995 | 0.59217
|  | 3:46 | 8.1022 | -0.16749 | 0.59217
|  | 3:46 | 8.1033 | -0.14283 | 0.59217
|  | 3:46 | 8.1044 | -0.11597 | 0.59216
|  | 3:46 | 8.1056 | -0.089118 | 0.59216
|  | 3:46 | 8.1067 | -0.051508 | 0.59216
|  | 3:46 | 8.1078 | -0.013898 | 0.59216
|  | 3:46 | 8.1089 | 0.024607 | 0.59216
|  | 3:46 | 8.11 | 0.064006 | 0.59215
|  | 3:46 | 8.1111 | 0.1034 | 0.59215
|  | 3:46 | 8.1122 | 0.12872 | 0.59215
|  | 3:46 | 8.1133 | 0.15403 | 0.59215
|  | 3:46 | 8.1144 | 0.16833 | 0.59214
|  | 3:46 | 8.1156 | 0.17161 | 0.59214
|  | 3:46 | 8.1167 | 0.1749 | 0.59214
|  | 3:46 | 8.1178 | 0.19225 | 0.59214
|  | 3:47 | 8.1189 | 0.2096 | 0.59213
|  | 3:47 | 8.12 | 0.23125 | 0.59213
|  | 3:47 | 8.1211 | 0.25433 | 0.59213
|  | 3:47 | 8.1222 | 0.28118 | 0.59213
|  | 3:47 | 8.1233 | 0.3193 | 0.59212
|  | 3:47 | 8.1244 | 0.35742 | 0.59212
|  | 3:47 | 8.1256 | 0.37481 | 0.59212
|  | 3:47 | 8.1267 | 0.37146 | 0.59212
|  | 3:47 | 8.1278 | 0.36812 | 0.59212
|  | 3:47 | 8.1289 | 0.36814 | 0.59211
|  | 3:47 | 8.13 | 0.36817 | 0.59211
|  | 3:47 | 8.1311 | 0.36493 | 0.59211
|  | 3:47 | 8.1322 | 0.35842 | 0.59211
|  | 3:47 | 8.1333 | 0.35192 | 0.5921
|  | 3:47 | 8.1344 | 0.35745 | 0.5921
|  | 3:48 | 8.1356 | 0.36298 | 0.5921
|  | 3:48 | 8.1367 | 0.38439 | 0.5921
|  | 3:48 | 8.1378 | 0.42166 | 0.59209
|  | 3:48 | 8.1389 | 0.45893 | 0.59209
|  | 3:48 | 8.14 | 0.50834 | 0.59209
|  | 3:48 | 8.1411 | 0.55774 | 0.59209
|  | 3:48 | 8.1422 | 0.59714 | 0.59209
|  | 3:48 | 8.1433 | 0.62655 | 0.59208
|  | 3:48 | 8.1444 | 0.65595 | 0.59208
|  | 3:48 | 8.1456 | 0.68535 | 0.59208
|  | 3:48 | 8.1467 | 0.71475 | 0.59208
|  | 3:48 | 8.1478 | 0.7405 | 0.59207
|  | 3:48 | 8.1489 | 0.7626 | 0.59207
|  | 3:48 | 8.15 | 0.7847 | 0.59207
|  | 3:48 | 8.1511 | 0.78996 | 0.59207
|  | 3:49 | 8.1522 | 0.79522 | 0.59206
|  | 3:49 | 8.1533 | 0.80048 | 0.59206
|  | 3:49 | 8.1544 | 0.80574 | 0.59206
|  | 3:49 | 8.1556 | 0.811 | 0.59206
|  | 3:49 | 8.1567 | 0.80302 | 0.59206
|  | 3:49 | 8.1578 | 0.79504 | 0.59205
|  | 3:49 | 8.1589 | 0.78335 | 0.59205
|  | 3:49 | 8.16 | 0.76794 | 0.59205
|  | 3:49 | 8.1611 | 0.75254 | 0.59205
|  | 3:49 | 8.1622 | 0.73713 | 0.59204
|  | 3:49 | 8.1633 | 0.72173 | 0.59204
|  | 3:49 | 8.1644 | 0.70357 | 0.59204
|  | 3:49 | 8.1656 | 0.68266 | 0.59204
|  | 3:49 | 8.1667 | 0.66175 | 0.59203
|  | 3:49 | 8.1678 | 0.62242 | 0.59203
|  | 3:50 | 8.1689 | 0.58309 | 0.59203
|  | 3:50 | 8.17 | 0.54171 | 0.59203
|  | 3:50 | 8.1711 | 0.49829 | 0.59203
|  | 3:50 | 8.1722 | 0.45486 | 0.59202
|  | 3:50 | 8.1733 | 0.42925 | 0.59202
|  | 3:50 | 8.1744 | 0.40363 | 0.59202
|  | 3:50 | 8.1756 | 0.37379 | 0.59202
|  | 3:50 | 8.1767 | 0.33971 | 0.59201
|  | 3:50 | 8.1778 | 0.30564 | 0.59201
|  | 3:50 | 8.1789 | 0.27379 | 0.59201
|  | 3:50 | 8.18 | 0.24194 | 0.59201
|  | 3:50 | 8.1811 | 0.22435 | 0.592
|  | 3:50 | 8.1822 | 0.22102 | 0.592
|  | 3:50 | 8.1833 | 0.21769 | 0.592
|  | 3:50 | 8.1844 | 0.20566 | 0.592
|  | 3:51 | 8.1856 | 0.19362 | 0.592
|  | 3:51 | 8.1867 | 0.18466 | 0.59199
|  | 3:51 | 8.1878 | 0.17879 | 0.59199
|  | 3:51 | 8.1889 | 0.17291 | 0.59199
|  | 3:51 | 8.19 | 0.16918 | 0.59199
|  | 3:51 | 8.1911 | 0.16545 | 0.59198
|  | 3:51 | 8.1922 | 0.15742 | 0.59198
|  | 3:51 | 8.1933 | 0.14511 | 0.59198
|  | 3:51 | 8.1944 | 0.13279 | 0.59198
|  | 3:51 | 8.1956 | 0.11944 | 0.59197
|  | 3:51 | 8.1967 | 0.10609 | 0.59197
|  | 3:51 | 8.1978 | 0.093734 | 0.59197
|  | 3:51 | 8.1989 | 0.082374 | 0.59197
|  | 3:51 | 8.2 | 0.071013 | 0.59197
|  | 3:51 | 8.2011 | 0.066403 | 0.59196
|  | 3:52 | 8.2022 | 0.061792 | 0.59196
|  | 3:52 | 8.2033 | 0.057755 | 0.59196
|  | 3:52 | 8.2044 | 0.05429 | 0.59196
|  | 3:52 | 8.2056 | 0.050825 | 0.59195
|  | 3:52 | 8.2067 | 0.032276 | 0.59195
|  | 3:52 | 8.2078 | 0.013726 | 0.59195
|  | 3:52 | 8.2089 | -0.0155 | 0.59195
|  | 3:52 | 8.21 | -0.055402 | 0.59194
|  | 3:52 | 8.2111 | -0.095305 | 0.59194
|  | 3:52 | 8.2122 | -0.1476 | 0.59194
|  | 3:52 | 8.2133 | -0.19989 | 0.59194
|  | 3:52 | 8.2144 | -0.25319 | 0.59194
|  | 3:52 | 8.2156 | -0.30752 | 0.59193
|  | 3:52 | 8.2167 | -0.36184 | 0.59193
|  | 3:52 | 8.2178 | -0.40614 | 0.59193
|  | 3:53 | 8.2189 | -0.45044 | 0.59193
|  | 3:53 | 8.22 | -0.48112 | 0.59192
|  | 3:53 | 8.2211 | -0.49819 | 0.59192
|  | 3:53 | 8.2222 | -0.51526 | 0.59192
|  | 3:53 | 8.2233 | -0.54146 | 0.59192
|  | 3:53 | 8.2244 | -0.56767 | 0.59191
|  | 3:53 | 8.2256 | -0.58665 | 0.59191
|  | 3:53 | 8.2267 | -0.59843 | 0.59191
|  | 3:53 | 8.2278 | -0.6102 | 0.59191
|  | 3:53 | 8.2289 | -0.60745 | 0.59191
|  | 3:53 | 8.23 | -0.6047 | 0.5919
|  | 3:53 | 8.2311 | -0.60347 | 0.5919
|  | 3:53 | 8.2322 | -0.60376 | 0.5919
|  | 3:53 | 8.2333 | -0.60405 | 0.5919
|  | 3:53 | 8.2344 | -0.60336 | 0.59189
|  | 3:54 | 8.2356 | -0.60266 | 0.59189
|  | 3:54 | 8.2367 | -0.60291 | 0.59189
|  | 3:54 | 8.2378 | -0.60599 | 0.59189
|  | 3:54 | 8.2389 | -0.60906 | 0.59188
|  | 3:54 | 8.24 | -0.61077 | 0.59188
|  | 3:54 | 8.2411 | -0.61248 | 0.59188
|  | 3:54 | 8.2422 | -0.6045 | 0.59188
|  | 3:54 | 8.2433 | -0.58685 | 0.59187
|  | 3:54 | 8.2444 | -0.56919 | 0.59187
|  | 3:54 | 8.2456 | -0.55636 | 0.59187
|  | 3:54 | 8.2467 | -0.54352 | 0.59187
|  | 3:54 | 8.2478 | -0.53564 | 0.59187
|  | 3:54 | 8.2489 | -0.53272 | 0.59186
|  | 3:54 | 8.25 | -0.5298 | 0.59186
|  | 3:54 | 8.2511 | -0.529 | 0.59186
|  | 3:55 | 8.2522 | -0.52819 | 0.59186
|  | 3:55 | 8.2533 | -0.53152 | 0.59185
|  | 3:55 | 8.2544 | -0.539 | 0.59185
|  | 3:55 | 8.2556 | -0.54647 | 0.59185
|  | 3:55 | 8.2567 | -0.54635 | 0.59185
|  | 3:55 | 8.2578 | -0.54623 | 0.59184
|  | 3:55 | 8.2589 | -0.54252 | 0.59184
|  | 3:55 | 8.26 | -0.53522 | 0.59184
|  | 3:55 | 8.2611 | -0.52791 | 0.59184
|  | 3:55 | 8.2622 | -0.51653 | 0.59184
|  | 3:55 | 8.2633 | -0.50516 | 0.59183
|  | 3:55 | 8.2644 | -0.47674 | 0.59183
|  | 3:55 | 8.2656 | -0.43128 | 0.59183
|  | 3:55 | 8.2667 | -0.38582 | 0.59183
|  | 3:55 | 8.2678 | -0.34134 | 0.59182
|  | 3:56 | 8.2689 | -0.29686 | 0.59182
|  | 3:56 | 8.27 | -0.25636 | 0.59182
|  | 3:56 | 8.2711 | -0.21982 | 0.59182
|  | 3:56 | 8.2722 | -0.18329 | 0.59181
|  | 3:56 | 8.2733 | -0.16697 | 0.59181
|  | 3:56 | 8.2744 | -0.15066 | 0.59181
|  | 3:56 | 8.2756 | -0.13059 | 0.59181
|  | 3:56 | 8.2767 | -0.10676 | 0.59181
|  | 3:56 | 8.2778 | -0.082929 | 0.5918
|  | 3:56 | 8.2789 | -0.064992 | 0.5918
|  | 3:56 | 8.28 | -0.047054 | 0.5918
|  | 3:56 | 8.2811 | -0.033677 | 0.5918
|  | 3:56 | 8.2822 | -0.024861 | 0.59179
|  | 3:56 | 8.2833 | -0.016045 | 0.59179
|  | 3:56 | 8.2844 | -0.015577 | 0.59179
|  | 3:57 | 8.2856 | -0.01511 | 0.59179
|  | 3:57 | 8.2867 | -0.032247 | 0.59178
|  | 3:57 | 8.2878 | -0.066986 | 0.59178
|  | 3:57 | 8.2889 | -0.10173 | 0.59178
|  | 3:57 | 8.29 | -0.11422 | 0.59178
|  | 3:57 | 8.2911 | -0.12672 | 0.59178
|  | 3:57 | 8.2922 | -0.14071 | 0.59177
|  | 3:57 | 8.2933 | -0.15619 | 0.59177
|  | 3:57 | 8.2944 | -0.17167 | 0.59177
|  | 3:57 | 8.2956 | -0.18715 | 0.59177
|  | 3:57 | 8.2967 | -0.20263 | 0.59176
|  | 3:57 | 8.2978 | -0.22463 | 0.59176
|  | 3:57 | 8.2989 | -0.25316 | 0.59176
|  | 3:57 | 8.3 | -0.28168 | 0.59176
|  | 3:57 | 8.3011 | -0.29777 | 0.59175
|  | 3:58 | 8.3022 | -0.31386 | 0.59175
|  | 3:58 | 8.3033 | -0.31394 | 0.59175
|  | 3:58 | 8.3044 | -0.298 | 0.59175
|  | 3:58 | 8.3056 | -0.28207 | 0.59175
|  | 3:58 | 8.3067 | -0.26097 | 0.59174
|  | 3:58 | 8.3078 | -0.23987 | 0.59174
|  | 3:58 | 8.3089 | -0.2201 | 0.59174
|  | 3:58 | 8.31 | -0.20168 | 0.59174
|  | 3:58 | 8.3111 | -0.18325 | 0.59173
|  | 3:58 | 8.3122 | -0.16685 | 0.59173
|  | 3:58 | 8.3133 | -0.15045 | 0.59173
|  | 3:58 | 8.3144 | -0.13497 | 0.59173
|  | 3:58 | 8.3156 | -0.1204 | 0.59172
|  | 3:58 | 8.3167 | -0.10583 | 0.59172
|  | 3:58 | 8.3178 | -0.085856 | 0.59172
|  | 3:59 | 8.3189 | -0.065882 | 0.59172
|  | 3:59 | 8.32 | -0.057483 | 0.59172
|  | 3:59 | 8.3211 | -0.060658 | 0.59171
|  | 3:59 | 8.3222 | -0.063833 | 0.59171
|  | 3:59 | 8.3233 | -0.042603 | 0.59171
|  | 3:59 | 8.3244 | -0.021374 | 0.59171
|  | 3:59 | 8.3256 | -0.0021204 | 0.5917
|  | 3:59 | 8.3267 | 0.015157 | 0.5917
|  | 3:59 | 8.3278 | 0.032435 | 0.5917
|  | 3:59 | 8.3289 | 0.024561 | 0.5917
|  | 3:59 | 8.33 | 0.016687 | 0.59169
|  | 3:59 | 8.3311 | 0.012389 | 0.59169
|  | 3:59 | 8.3322 | 0.011665 | 0.59169
|  | 3:59 | 8.3333 | 0.010942 | 0.59169
|  | 3:59 | 8.3344 | 0.002515 | 0.59169
|  | 4:00 | 8.3356 | -0.0059115 | 0.59168
|  | 4:00 | 8.3367 | -0.026255 | 0.59168
|  | 4:00 | 8.3378 | -0.058516 | 0.59168
|  | 4:00 | 8.3389 | -0.090777 | 0.59168
|  | 4:00 | 8.34 | -0.1219 | 0.59167
|  | 4:00 | 8.3411 | -0.15302 | 0.59167
|  | 4:00 | 8.3422 | -0.18289 | 0.59167
|  | 4:00 | 8.3433 | -0.14425 | 0.59167
|  | 4:00 | 8.3444 | -0.12965 | 0.59166
|  | 4:00 | 8.3456 | -0.13601 | 0.59166
|  | 4:00 | 8.3467 | -0.14238 | 0.59166
|  | 4:00 | 8.3478 | -0.14874 | 0.59166
|  | 4:00 | 8.3489 | -0.15511 | 0.59166
|  | 4:00 | 8.35 | -0.16147 | 0.59165
|  | 4:00 | 8.3511 | -0.15001 | 0.59165
|  | 4:01 | 8.3522 | -0.13855 | 0.59165
|  | 4:01 | 8.3533 | -0.11353 | 0.59165
|  | 4:01 | 8.3544 | -0.083978 | 0.59164
|  | 4:01 | 8.3556 | -0.05443 | 0.59164
|  | 4:01 | 8.3567 | -0.032121 | 0.59164
|  | 4:01 | 8.3578 | -0.0098121 | 0.59164
|  | 4:01 | 8.3589 | 0.0050135 | 0.59163
|  | 4:01 | 8.36 | 0.012356 | 0.59163
|  | 4:01 | 8.3611 | 0.019698 | 0.59163
|  | 4:01 | 8.3622 | 0.0056427 | 0.59163
|  | 4:01 | 8.3633 | -0.0084124 | 0.59162
|  | 4:01 | 8.3644 | -0.016135 | 0.59162
|  | 4:01 | 8.3656 | -0.017526 | 0.59162
|  | 4:01 | 8.3667 | -0.018917 | 0.59162
|  | 4:01 | 8.3678 | -0.0074832 | 0.59162
|  | 4:02 | 8.3689 | 0.0039504 | 0.59161
|  | 4:02 | 8.37 | 0.016937 | 0.59161
|  | 4:02 | 8.3711 | 0.030441 | 0.59161
|  | 4:02 | 8.3722 | 0.043946 | 0.59161
|  | 4:02 | 8.3733 | 0.065859 | 0.5916
|  | 4:02 | 8.3744 | 0.087772 | 0.5916
|  | 4:02 | 8.3756 | 0.10268 | 0.5916
|  | 4:02 | 8.3767 | 0.11526 | 0.5916
|  | 4:02 | 8.3778 | 0.12783 | 0.59159
|  | 4:02 | 8.3789 | 0.13629 | 0.59159
|  | 4:02 | 8.38 | 0.14474 | 0.59159
|  | 4:02 | 8.3811 | 0.1681 | 0.59159
|  | 4:02 | 8.3822 | 0.20635 | 0.59159
|  | 4:02 | 8.3833 | 0.2446 | 0.59158
|  | 4:02 | 8.3844 | 0.28614 | 0.59158
|  | 4:03 | 8.3856 | 0.32769 | 0.59158
|  | 4:03 | 8.3867 | 0.37177 | 0.59158
|  | 4:03 | 8.3878 | 0.41839 | 0.59157
|  | 4:03 | 8.3889 | 0.4646 | 0.59157
|  | 4:03 | 8.39 | 0.50955 | 0.59157
|  | 4:03 | 8.3911 | 0.55451 | 0.59157
|  | 4:03 | 8.3922 | 0.60292 | 0.59156
|  | 4:03 | 8.3933 | 0.65481 | 0.59156
|  | 4:03 | 8.3944 | 0.70669 | 0.59156
|  | 4:03 | 8.3956 | 0.72091 | 0.59156
|  | 4:03 | 8.3967 | 0.73513 | 0.59156
|  | 4:03 | 8.3978 | 0.73769 | 0.59155
|  | 4:03 | 8.3989 | 0.7286 | 0.59155
|  | 4:03 | 8.4 | 0.71951 | 0.59155
|  | 4:03 | 8.4011 | 0.69733 | 0.59155
|  | 4:04 | 8.4022 | 0.66208 | 0.59154
|  | 4:04 | 8.4033 | 0.6161 | 0.59154
|  | 4:04 | 8.4044 | 0.5594 | 0.59154
|  | 4:04 | 8.4056 | 0.50271 | 0.59154
|  | 4:04 | 8.4067 | 0.43484 | 0.59153
|  | 4:04 | 8.4078 | 0.36696 | 0.59153
|  | 4:04 | 8.4089 | 0.2997 | 0.59153
|  | 4:04 | 8.41 | 0.23306 | 0.59153
|  | 4:04 | 8.4111 | 0.16641 | 0.59153
|  | 4:04 | 8.4122 | 0.1269 | 0.59152
|  | 4:04 | 8.4133 | 0.087393 | 0.59152
|  | 4:04 | 8.4144 | 0.062752 | 0.59152
|  | 4:04 | 8.4156 | 0.052981 | 0.59152
|  | 4:04 | 8.4167 | 0.04321 | 0.59151
|  | 4:04 | 8.4178 | 0.031374 | 0.59151
|  | 4:05 | 8.4189 | 0.019538 | 0.59151
|  | 4:05 | 8.42 | 0.0014623 | 0.59151
|  | 4:05 | 8.4211 | -0.022852 | 0.5915
|  | 4:05 | 8.4222 | -0.047167 | 0.5915
|  | 4:05 | 8.4233 | -0.057435 | 0.5915
|  | 4:05 | 8.4244 | -0.067703 | 0.5915
|  | 4:05 | 8.4256 | -0.080728 | 0.5915
|  | 4:05 | 8.4267 | -0.096511 | 0.59149
|  | 4:05 | 8.4278 | -0.11229 | 0.59149
|  | 4:05 | 8.4289 | -0.14181 | 0.59149
|  | 4:05 | 8.43 | -0.17133 | 0.59149
|  | 4:05 | 8.4311 | -0.19213 | 0.59148
|  | 4:05 | 8.4322 | -0.21003 | 0.59148
|  | 4:05 | 8.4333 | -0.22794 | 0.59148
|  | 4:05 | 8.4344 | -0.25217 | 0.59148
|  | 4:06 | 8.4356 | -0.2764 | 0.59147
|  | 4:06 | 8.4367 | -0.29614 | 0.59147
|  | 4:06 | 8.4378 | -0.31141 | 0.59147
|  | 4:06 | 8.4389 | -0.32668 | 0.59147
|  | 4:06 | 8.44 | -0.33634 | 0.59147
|  | 4:06 | 8.4411 | -0.346 | 0.59146
|  | 4:06 | 8.4422 | -0.35417 | 0.59146
|  | 4:06 | 8.4433 | -0.36184 | 0.59146
|  | 4:06 | 8.4444 | -0.3695 | 0.59146
|  | 4:06 | 8.4456 | -0.38223 | 0.59145
|  | 4:06 | 8.4467 | -0.39495 | 0.59145
|  | 4:06 | 8.4478 | -0.41366 | 0.59145
|  | 4:06 | 8.4489 | -0.43836 | 0.59145
|  | 4:06 | 8.45 | -0.46307 | 0.59144
|  | 4:06 | 8.4511 | -0.49142 | 0.59144
|  | 4:07 | 8.4522 | -0.51976 | 0.59144
|  | 4:07 | 8.4533 | -0.53557 | 0.59144
|  | 4:07 | 8.4544 | -0.53885 | 0.59144
|  | 4:07 | 8.4556 | -0.54212 | 0.59143
|  | 4:07 | 8.4567 | -0.52588 | 0.59143
|  | 4:07 | 8.4578 | -0.50964 | 0.59143
|  | 4:07 | 8.4589 | -0.48512 | 0.59143
|  | 4:07 | 8.46 | -0.45232 | 0.59142
|  | 4:07 | 8.4611 | -0.41952 | 0.59142
|  | 4:07 | 8.4622 | -0.39896 | 0.59142
|  | 4:07 | 8.4633 | -0.3784 | 0.59142
|  | 4:07 | 8.4644 | -0.36069 | 0.59141
|  | 4:07 | 8.4656 | -0.34581 | 0.59141
|  | 4:07 | 8.4667 | -0.33094 | 0.59141
|  | 4:07 | 8.4678 | -0.31151 | 0.59141
|  | 4:08 | 8.4689 | -0.29208 | 0.59141
|  | 4:08 | 8.47 | -0.26401 | 0.5914
|  | 4:08 | 8.4711 | -0.2273 | 0.5914
|  | 4:08 | 8.4722 | -0.1906 | 0.5914
|  | 4:08 | 8.4733 | -0.15165 | 0.5914
|  | 4:08 | 8.4744 | -0.1127 | 0.59139
|  | 4:08 | 8.4756 | -0.070709 | 0.59139
|  | 4:08 | 8.4767 | -0.025681 | 0.59139
|  | 4:08 | 8.4778 | 0.019348 | 0.59139
|  | 4:08 | 8.4789 | 0.066808 | 0.59138
|  | 4:08 | 8.48 | 0.11427 | 0.59138
|  | 4:08 | 8.4811 | 0.14906 | 0.59138
|  | 4:08 | 8.4822 | 0.17962 | 0.59138
|  | 4:08 | 8.4833 | 0.21018 | 0.59137
|  | 4:08 | 8.4844 | 0.22659 | 0.59137
|  | 4:09 | 8.4856 | 0.243 | 0.59137
|  | 4:09 | 8.4867 | 0.26015 | 0.59137
|  | 4:09 | 8.4878 | 0.27804 | 0.59137
|  | 4:09 | 8.4889 | 0.29593 | 0.59136
|  | 4:09 | 8.49 | 0.34579 | 0.59136
|  | 4:09 | 8.4911 | 0.39566 | 0.59136
|  | 4:09 | 8.4922 | 0.41648 | 0.59136
|  | 4:09 | 8.4933 | 0.42761 | 0.59135
|  | 4:09 | 8.4944 | 0.43875 | 0.59135
|  | 4:09 | 8.4956 | 0.48488 | 0.59135
|  | 4:09 | 8.4967 | 0.53101 | 0.59135
|  | 4:09 | 8.4978 | 0.56431 | 0.59134
|  | 4:09 | 8.4989 | 0.58479 | 0.59134
|  | 4:09 | 8.5 | 0.60527 | 0.59134
|  | 4:09 | 8.5011 | 0.62576 | 0.59134
|  | 4:10 | 8.5022 | 0.64624 | 0.59134
|  | 4:10 | 8.5033 | 0.65386 | 0.59133
|  | 4:10 | 8.5044 | 0.64862 | 0.59133
|  | 4:10 | 8.5056 | 0.64337 | 0.59133
|  | 4:10 | 8.5067 | 0.61858 | 0.59133
|  | 4:10 | 8.5078 | 0.59379 | 0.59132
|  | 4:10 | 8.5089 | 0.57945 | 0.59132
|  | 4:10 | 8.51 | 0.5686 | 0.59132
|  | 4:10 | 8.5111 | 0.55774 | 0.59132
|  | 4:10 | 8.5122 | 0.53406 | 0.59131
|  | 4:10 | 8.5133 | 0.51037 | 0.59131
|  | 4:10 | 8.5144 | 0.48484 | 0.59131
|  | 4:10 | 8.5156 | 0.45747 | 0.59131
|  | 4:10 | 8.5167 | 0.43009 | 0.59131
|  | 4:10 | 8.5178 | 0.40661 | 0.5913
|  | 4:11 | 8.5189 | 0.38313 | 0.5913
|  | 4:11 | 8.52 | 0.35578 | 0.5913
|  | 4:11 | 8.5211 | 0.32455 | 0.5913
|  | 4:11 | 8.5222 | 0.29332 | 0.59129
|  | 4:11 | 8.5233 | 0.24981 | 0.59129
|  | 4:11 | 8.5244 | 0.20629 | 0.59129
|  | 4:11 | 8.5256 | 0.16355 | 0.59129
|  | 4:11 | 8.5267 | 0.12106 | 0.59128
|  | 4:11 | 8.5278 | 0.078582 | 0.59128
|  | 4:11 | 8.5289 | 0.031632 | 0.59128
|  | 4:11 | 8.53 | -0.015318 | 0.59128
|  | 4:11 | 8.5311 | -0.035845 | 0.59128
|  | 4:11 | 8.5322 | -0.047565 | 0.59127
|  | 4:11 | 8.5333 | -0.059285 | 0.59127
|  | 4:11 | 8.5344 | -0.081598 | 0.59127
|  | 4:12 | 8.5356 | -0.10391 | 0.59127
|  | 4:12 | 8.5367 | -0.13323 | 0.59126
|  | 4:12 | 8.5378 | -0.16956 | 0.59126
|  | 4:12 | 8.5389 | -0.20588 | 0.59126
|  | 4:12 | 8.54 | -0.24997 | 0.59126
|  | 4:12 | 8.5411 | -0.29406 | 0.59125
|  | 4:12 | 8.5422 | -0.33234 | 0.59125
|  | 4:12 | 8.5433 | -0.3648 | 0.59125
|  | 4:12 | 8.5444 | -0.39726 | 0.59125
|  | 4:12 | 8.5456 | -0.42357 | 0.59125
|  | 4:12 | 8.5467 | -0.44987 | 0.59124
|  | 4:12 | 8.5478 | -0.46847 | 0.59124
|  | 4:12 | 8.5489 | -0.47935 | 0.59124
|  | 4:12 | 8.55 | -0.49023 | 0.59124
|  | 4:12 | 8.5511 | -0.5088 | 0.59123
|  | 4:13 | 8.5522 | -0.52738 | 0.59123
|  | 4:13 | 8.5533 | -0.54595 | 0.59123
|  | 4:13 | 8.5544 | -0.56452 | 0.59123
|  | 4:13 | 8.5556 | -0.58056 | 0.59122
|  | 4:13 | 8.5567 | -0.58899 | 0.59122
|  | 4:13 | 8.5578 | -0.59741 | 0.59122
|  | 4:13 | 8.5589 | -0.60464 | 0.59122
|  | 4:13 | 8.56 | -0.61068 | 0.59122
|  | 4:13 | 8.5611 | -0.61671 | 0.59121
|  | 4:13 | 8.5622 | -0.62274 | 0.59121
|  | 4:13 | 8.5633 | -0.62878 | 0.59121
|  | 4:13 | 8.5644 | -0.64556 | 0.59121
|  | 4:13 | 8.5656 | -0.67309 | 0.5912
|  | 4:13 | 8.5667 | -0.70062 | 0.5912
|  | 4:13 | 8.5678 | -0.7259 | 0.5912
|  | 4:14 | 8.5689 | -0.75118 | 0.5912
|  | 4:14 | 8.57 | -0.76373 | 0.59119
|  | 4:14 | 8.5711 | -0.76355 | 0.59119
|  | 4:14 | 8.5722 | -0.76336 | 0.59119
|  | 4:14 | 8.5733 | -0.74165 | 0.59119
|  | 4:14 | 8.5744 | -0.71995 | 0.59119
|  | 4:14 | 8.5756 | -0.69328 | 0.59118
|  | 4:14 | 8.5767 | -0.66166 | 0.59118
|  | 4:14 | 8.5778 | -0.63004 | 0.59118
|  | 4:14 | 8.5789 | -0.60123 | 0.59118
|  | 4:14 | 8.58 | -0.57243 | 0.59117
|  | 4:14 | 8.5811 | -0.55891 | 0.59117
|  | 4:14 | 8.5822 | -0.56068 | 0.59117
|  | 4:14 | 8.5833 | -0.56245 | 0.59117
|  | 4:14 | 8.5844 | -0.54412 | 0.59116
|  | 4:15 | 8.5856 | -0.52578 | 0.59116
|  | 4:15 | 8.5867 | -0.51626 | 0.59116
|  | 4:15 | 8.5878 | -0.51554 | 0.59116
|  | 4:15 | 8.5889 | -0.51483 | 0.59116
|  | 4:15 | 8.59 | -0.51658 | 0.59115
|  | 4:15 | 8.5911 | -0.51832 | 0.59115
|  | 4:15 | 8.5922 | -0.51742 | 0.59115
|  | 4:15 | 8.5933 | -0.51387 | 0.59115
|  | 4:15 | 8.5944 | -0.51032 | 0.59114
|  | 4:15 | 8.5956 | -0.49265 | 0.59114
|  | 4:15 | 8.5967 | -0.47497 | 0.59114
|  | 4:15 | 8.5978 | -0.4573 | 0.59114
|  | 4:15 | 8.5989 | -0.43963 | 0.59113
|  | 4:15 | 8.6 | -0.42195 | 0.59113
|  | 4:15 | 8.6011 | -0.40033 | 0.59113
|  | 4:16 | 8.6022 | -0.3787 | 0.59113
|  | 4:16 | 8.6033 | -0.35755 | 0.59112
|  | 4:16 | 8.6044 | -0.33687 | 0.59112
|  | 4:16 | 8.6056 | -0.31619 | 0.59112
|  | 4:16 | 8.6067 | -0.27026 | 0.59112
|  | 4:16 | 8.6078 | -0.22432 | 0.59112
|  | 4:16 | 8.6089 | -0.18079 | 0.59111
|  | 4:16 | 8.61 | -0.13806 | 0.59111
|  | 4:16 | 8.6111 | -0.095326 | 0.59111
|  | 4:16 | 8.6122 | -0.056057 | 0.59111
|  | 4:16 | 8.6133 | -0.016788 | 0.5911
|  | 4:16 | 8.6144 | 0.015659 | 0.5911
|  | 4:16 | 8.6156 | 0.041284 | 0.5911
|  | 4:16 | 8.6167 | 0.066908 | 0.5911
|  | 4:16 | 8.6178 | 0.067889 | 0.59109
|  | 4:17 | 8.6189 | 0.06887 | 0.59109
|  | 4:17 | 8.62 | 0.077604 | 0.59109
|  | 4:17 | 8.6211 | 0.094089 | 0.59109
|  | 4:17 | 8.6222 | 0.11057 | 0.59109
|  | 4:17 | 8.6233 | 0.13697 | 0.59108
|  | 4:17 | 8.6244 | 0.16337 | 0.59108
|  | 4:17 | 8.6256 | 0.18555 | 0.59108
|  | 4:17 | 8.6267 | 0.2035 | 0.59108
|  | 4:17 | 8.6278 | 0.22146 | 0.59107
|  | 4:17 | 8.6289 | 0.25483 | 0.59107
|  | 4:17 | 8.63 | 0.2882 | 0.59107
|  | 4:17 | 8.6311 | 0.30837 | 0.59107
|  | 4:17 | 8.6322 | 0.31533 | 0.59106
|  | 4:17 | 8.6333 | 0.32229 | 0.59106
|  | 4:17 | 8.6344 | 0.34371 | 0.59106
|  | 4:18 | 8.6356 | 0.36513 | 0.59106
|  | 4:18 | 8.6367 | 0.39495 | 0.59106
|  | 4:18 | 8.6378 | 0.43316 | 0.59105
|  | 4:18 | 8.6389 | 0.47137 | 0.59105
|  | 4:18 | 8.64 | 0.50421 | 0.59105
|  | 4:18 | 8.6411 | 0.53705 | 0.59105
|  | 4:18 | 8.6422 | 0.56677 | 0.59104
|  | 4:18 | 8.6433 | 0.59337 | 0.59104
|  | 4:18 | 8.6444 | 0.61996 | 0.59104
|  | 4:18 | 8.6456 | 0.63533 | 0.59104
|  | 4:18 | 8.6467 | 0.6507 | 0.59103
|  | 4:18 | 8.6478 | 0.67478 | 0.59103
|  | 4:18 | 8.6489 | 0.70756 | 0.59103
|  | 4:18 | 8.65 | 0.74033 | 0.59103
|  | 4:18 | 8.6511 | 0.7188 | 0.59103
|  | 4:19 | 8.6522 | 0.69726 | 0.59102
|  | 4:19 | 8.6533 | 0.69924 | 0.59102
|  | 4:19 | 8.6544 | 0.72473 | 0.59102
|  | 4:19 | 8.6556 | 0.75023 | 0.59102
|  | 4:19 | 8.6567 | 0.75876 | 0.59101
|  | 4:19 | 8.6578 | 0.76729 | 0.59101
|  | 4:19 | 8.6589 | 0.77299 | 0.59101
|  | 4:19 | 8.66 | 0.77774 | 0.59101
|  | 4:19 | 8.6611 | 0.7825 | 0.591
|  | 4:19 | 8.6622 | 0.76741 | 0.591
|  | 4:19 | 8.6633 | 0.75232 | 0.591
|  | 4:19 | 8.6644 | 0.7296 | 0.591
|  | 4:19 | 8.6656 | 0.69925 | 0.591
|  | 4:19 | 8.6667 | 0.6689 | 0.59099
|  | 4:19 | 8.6678 | 0.62576 | 0.59099
|  | 4:20 | 8.6689 | 0.58261 | 0.59099
|  | 4:20 | 8.67 | 0.54949 | 0.59099
|  | 4:20 | 8.6711 | 0.5264 | 0.59098
|  | 4:20 | 8.6722 | 0.50331 | 0.59098
|  | 4:20 | 8.6733 | 0.4765 | 0.59098
|  | 4:20 | 8.6744 | 0.44968 | 0.59098
|  | 4:20 | 8.6756 | 0.4167 | 0.59097
|  | 4:20 | 8.6767 | 0.37755 | 0.59097
|  | 4:20 | 8.6778 | 0.33841 | 0.59097
|  | 4:20 | 8.6789 | 0.29386 | 0.59097
|  | 4:20 | 8.68 | 0.24932 | 0.59097
|  | 4:20 | 8.6811 | 0.21533 | 0.59096
|  | 4:20 | 8.6822 | 0.19189 | 0.59096
|  | 4:20 | 8.6833 | 0.16844 | 0.59096
|  | 4:20 | 8.6844 | 0.16499 | 0.59096
|  | 4:21 | 8.6856 | 0.16153 | 0.59095
|  | 4:21 | 8.6867 | 0.15986 | 0.59095
|  | 4:21 | 8.6878 | 0.15996 | 0.59095
|  | 4:21 | 8.6889 | 0.16005 | 0.59095
|  | 4:21 | 8.69 | 0.14796 | 0.59094
|  | 4:21 | 8.6911 | 0.13587 | 0.59094
|  | 4:21 | 8.6922 | 0.12378 | 0.59094
|  | 4:21 | 8.6933 | 0.1117 | 0.59094
|  | 4:21 | 8.6944 | 0.099605 | 0.59094
|  | 4:21 | 8.6956 | 0.079349 | 0.59093
|  | 4:21 | 8.6967 | 0.059092 | 0.59093
|  | 4:21 | 8.6978 | 0.042185 | 0.59093
|  | 4:21 | 8.6989 | 0.028626 | 0.59093
|  | 4:21 | 8.7 | 0.015067 | 0.59092
|  | 4:21 | 8.7011 | 0.017848 | 0.59092
|  | 4:22 | 8.7022 | 0.020629 | 0.59092
|  | 4:22 | 8.7033 | 0.02341 | 0.59092
|  | 4:22 | 8.7044 | 0.02619 | 0.59091
|  | 4:22 | 8.7056 | 0.028971 | 0.59091
|  | 4:22 | 8.7067 | 0.040168 | 0.59091
|  | 4:22 | 8.7078 | 0.051364 | 0.59091
|  | 4:22 | 8.7089 | 0.060832 | 0.59091
|  | 4:22 | 8.71 | 0.068571 | 0.5909
|  | 4:22 | 8.7111 | 0.076309 | 0.5909
|  | 4:22 | 8.7122 | 0.077437 | 0.5909
|  | 4:22 | 8.7133 | 0.078564 | 0.5909
|  | 4:22 | 8.7144 | 0.080322 | 0.59089
|  | 4:22 | 8.7156 | 0.082711 | 0.59089
|  | 4:22 | 8.7167 | 0.085099 | 0.59089
|  | 4:22 | 8.7178 | 0.082506 | 0.59089
|  | 4:23 | 8.7189 | 0.079913 | 0.59088
|  | 4:23 | 8.72 | 0.07732 | 0.59088
|  | 4:23 | 8.7211 | 0.074727 | 0.59088
|  | 4:23 | 8.7222 | 0.072134 | 0.59088
|  | 4:23 | 8.7233 | 0.05751 | 0.59087
|  | 4:23 | 8.7244 | 0.042887 | 0.59087
|  | 4:23 | 8.7256 | 0.041184 | 0.59087
|  | 4:23 | 8.7267 | 0.052402 | 0.59087
|  | 4:23 | 8.7278 | 0.063621 | 0.59087
|  | 4:23 | 8.7289 | 0.059618 | 0.59086
|  | 4:23 | 8.73 | 0.055615 | 0.59086
|  | 4:23 | 8.7311 | 0.053782 | 0.59086
|  | 4:23 | 8.7322 | 0.054119 | 0.59086
|  | 4:23 | 8.7333 | 0.054456 | 0.59085
|  | 4:23 | 8.7344 | 0.052728 | 0.59085
|  | 4:24 | 8.7356 | 0.051 | 0.59085
|  | 4:24 | 8.7367 | 0.053232 | 0.59085
|  | 4:24 | 8.7378 | 0.059425 | 0.59084
|  | 4:24 | 8.7389 | 0.065617 | 0.59084
|  | 4:24 | 8.74 | 0.089973 | 0.59084
|  | 4:24 | 8.7411 | 0.11433 | 0.59084
|  | 4:24 | 8.7422 | 0.13104 | 0.59084
|  | 4:24 | 8.7433 | 0.14009 | 0.59083
|  | 4:24 | 8.7444 | 0.14915 | 0.59083
|  | 4:24 | 8.7456 | 0.14294 | 0.59083
|  | 4:24 | 8.7467 | 0.13674 | 0.59083
|  | 4:24 | 8.7478 | 0.13903 | 0.59082
|  | 4:24 | 8.7489 | 0.14981 | 0.59082
|  | 4:24 | 8.75 | 0.16059 | 0.59082
|  | 4:24 | 8.7511 | 0.17604 | 0.59082
|  | 4:25 | 8.7522 | 0.1915 | 0.59081
|  | 4:25 | 8.7533 | 0.20614 | 0.59081
|  | 4:25 | 8.7544 | 0.21996 | 0.59081
|  | 4:25 | 8.7556 | 0.23378 | 0.59081
|  | 4:25 | 8.7567 | 0.22649 | 0.59081
|  | 4:25 | 8.7578 | 0.2192 | 0.5908
|  | 4:25 | 8.7589 | 0.2103 | 0.5908
|  | 4:25 | 8.76 | 0.1998 | 0.5908
|  | 4:25 | 8.7611 | 0.18929 | 0.5908
|  | 4:25 | 8.7622 | 0.16969 | 0.59079
|  | 4:25 | 8.7633 | 0.15009 | 0.59079
|  | 4:25 | 8.7644 | 0.12595 | 0.59079
|  | 4:25 | 8.7656 | 0.09729 | 0.59079
|  | 4:25 | 8.7667 | 0.068625 | 0.59078
|  | 4:25 | 8.7678 | 0.07361 | 0.59078
|  | 4:26 | 8.7689 | 0.078594 | 0.59078
|  | 4:26 | 8.77 | 0.072993 | 0.59078
|  | 4:26 | 8.7711 | 0.056805 | 0.59078
|  | 4:26 | 8.7722 | 0.040617 | 0.59077
|  | 4:26 | 8.7733 | 0.014632 | 0.59077
|  | 4:26 | 8.7744 | -0.011353 | 0.59077
|  | 4:26 | 8.7756 | -0.035552 | 0.59077
|  | 4:26 | 8.7767 | -0.057963 | 0.59076
|  | 4:26 | 8.7778 | -0.080375 | 0.59076
|  | 4:26 | 8.7789 | -0.065543 | 0.59076
|  | 4:26 | 8.78 | -0.050712 | 0.59076
|  | 4:26 | 8.7811 | -0.031837 | 0.59075
|  | 4:26 | 8.7822 | -0.0089175 | 0.59075
|  | 4:26 | 8.7833 | 0.014002 | 0.59075
|  | 4:26 | 8.7844 | 0.0028253 | 0.59075
|  | 4:27 | 8.7856 | -0.0083511 | 0.59075
|  | 4:27 | 8.7867 | -0.022928 | 0.59074
|  | 4:27 | 8.7878 | -0.040906 | 0.59074
|  | 4:27 | 8.7889 | -0.058884 | 0.59074
|  | 4:27 | 8.79 | -0.068746 | 0.59074
|  | 4:27 | 8.7911 | -0.078609 | 0.59073
|  | 4:27 | 8.7922 | -0.07932 | 0.59073
|  | 4:27 | 8.7933 | -0.076982 | 0.59073
|  | 4:27 | 8.7944 | -0.074643 | 0.59073
|  | 4:27 | 8.7956 | -0.075455 | 0.59072
|  | 4:27 | 8.7967 | -0.076267 | 0.59072
|  | 4:27 | 8.7978 | -0.073963 | 0.59072
|  | 4:27 | 8.7989 | -0.07062 | 0.59072
|  | 4:27 | 8.8 | -0.067277 | 0.59072
|  | 4:27 | 8.8011 | -0.087801 | 0.59071
|  | 4:28 | 8.8022 | -0.10832 | 0.59071
|  | 4:28 | 8.8033 | -0.11242 | 0.59071
|  | 4:28 | 8.8044 | -0.10009 | 0.59071
|  | 4:28 | 8.8056 | -0.087763 | 0.5907
|  | 4:28 | 8.8067 | -0.068639 | 0.5907
|  | 4:28 | 8.8078 | -0.049516 | 0.5907
|  | 4:28 | 8.8089 | -0.015747 | 0.5907
|  | 4:28 | 8.81 | 0.032669 | 0.59069
|  | 4:28 | 8.8111 | 0.076313 | 0.59069
|  | 4:28 | 8.8122 | 0.10565 | 0.59069
|  | 4:28 | 8.8133 | 0.13498 | 0.59069
|  | 4:28 | 8.8144 | 0.14996 | 0.59069
|  | 4:28 | 8.8156 | 0.1506 | 0.59068
|  | 4:28 | 8.8167 | 0.15123 | 0.59068
|  | 4:28 | 8.8178 | 0.15947 | 0.59068
|  | 4:29 | 8.8189 | 0.1677 | 0.59068
|  | 4:29 | 8.82 | 0.16361 | 0.59067
|  | 4:29 | 8.8211 | 0.14719 | 0.59067
|  | 4:29 | 8.8222 | 0.13078 | 0.59067
|  | 4:29 | 8.8233 | 0.11437 | 0.59067
|  | 4:29 | 8.8244 | 0.097961 | 0.59066
|  | 4:29 | 8.8256 | 0.077558 | 0.59066
|  | 4:29 | 8.8267 | 0.055824 | 0.59066
|  | 4:29 | 8.8278 | 0.034089 | 0.59066
|  | 4:29 | 8.8289 | 0.018564 | 0.59066
|  | 4:29 | 8.83 | 0.0030393 | 0.59065
|  | 4:29 | 8.8311 | -0.016027 | 0.59065
|  | 4:29 | 8.8322 | -0.038635 | 0.59065
|  | 4:29 | 8.8333 | -0.061243 | 0.59065
|  | 4:29 | 8.8344 | -0.068344 | 0.59064
|  | 4:30 | 8.8356 | -0.075445 | 0.59064
|  | 4:30 | 8.8367 | -0.080764 | 0.59064
|  | 4:30 | 8.8378 | -0.0843 | 0.59064
|  | 4:30 | 8.8389 | -0.087836 | 0.59063
|  | 4:30 | 8.84 | -0.08516 | 0.59063
|  | 4:30 | 8.8411 | -0.082483 | 0.59063
|  | 4:30 | 8.8422 | -0.079807 | 0.59063
|  | 4:30 | 8.8433 | -0.07713 | 0.59062
|  | 4:30 | 8.8444 | -0.074454 | 0.59062
|  | 4:30 | 8.8456 | -0.076025 | 0.59062
|  | 4:30 | 8.8467 | -0.077597 | 0.59062
|  | 4:30 | 8.8478 | -0.085439 | 0.59062
|  | 4:30 | 8.8489 | -0.09955 | 0.59061
|  | 4:30 | 8.85 | -0.11366 | 0.59061
|  | 4:30 | 8.8511 | -0.11441 | 0.59061
|  | 4:31 | 8.8522 | -0.11516 | 0.59061
|  | 4:31 | 8.8533 | -0.10971 | 0.5906
|  | 4:31 | 8.8544 | -0.09806 | 0.5906
|  | 4:31 | 8.8556 | -0.084509 | 0.5906
|  | 4:31 | 8.8567 | -0.065244 | 0.5906
|  | 4:31 | 8.8578 | -0.045979 | 0.59059
|  | 4:31 | 8.8589 | -0.029559 | 0.59059
|  | 4:31 | 8.86 | -0.015984 | 0.59059
|  | 4:31 | 8.8611 | -0.0024094 | 0.59059
|  | 4:31 | 8.8622 | 0.022238 | 0.59059
|  | 4:31 | 8.8633 | 0.046885 | 0.59058
|  | 4:31 | 8.8644 | 0.074314 | 0.59058
|  | 4:31 | 8.8656 | 0.10453 | 0.59058
|  | 4:31 | 8.8667 | 0.13474 | 0.59058
|  | 4:31 | 8.8678 | 0.15843 | 0.59057
|  | 4:32 | 8.8689 | 0.18212 | 0.59057
|  | 4:32 | 8.87 | 0.20365 | 0.59057
|  | 4:32 | 8.8711 | 0.22304 | 0.59057
|  | 4:32 | 8.8722 | 0.24243 | 0.59056
|  | 4:32 | 8.8733 | 0.2467 | 0.59056
|  | 4:32 | 8.8744 | 0.25097 | 0.59056
|  | 4:32 | 8.8756 | 0.25524 | 0.59056
|  | 4:32 | 8.8767 | 0.25952 | 0.59056
|  | 4:32 | 8.8778 | 0.26379 | 0.59055
|  | 4:32 | 8.8789 | 0.26806 | 0.59055
|  | 4:32 | 8.88 | 0.27234 | 0.59055
|  | 4:32 | 8.8811 | 0.27055 | 0.59055
|  | 4:32 | 8.8822 | 0.26272 | 0.59054
|  | 4:32 | 8.8833 | 0.25488 | 0.59054
|  | 4:32 | 8.8844 | 0.23498 | 0.59054
|  | 4:33 | 8.8856 | 0.21507 | 0.59054
|  | 4:33 | 8.8867 | 0.20228 | 0.59053
|  | 4:33 | 8.8878 | 0.1966 | 0.59053
|  | 4:33 | 8.8889 | 0.19092 | 0.59053
|  | 4:33 | 8.89 | 0.17374 | 0.59053
|  | 4:33 | 8.8911 | 0.15656 | 0.59053
|  | 4:33 | 8.8922 | 0.14737 | 0.59052
|  | 4:33 | 8.8933 | 0.14617 | 0.59052
|  | 4:33 | 8.8944 | 0.14096 | 0.59052
|  | 4:33 | 8.8956 | 0.1237 | 0.59052
|  | 4:33 | 8.8967 | 0.10644 | 0.59051
|  | 4:33 | 8.8978 | 0.091813 | 0.59051
|  | 4:33 | 8.8989 | 0.079822 | 0.59051
|  | 4:33 | 8.9 | 0.067831 | 0.59051
|  | 4:33 | 8.9011 | 0.075896 | 0.5905
|  | 4:34 | 8.9022 | 0.083961 | 0.5905
|  | 4:34 | 8.9033 | 0.086463 | 0.5905
|  | 4:34 | 8.9044 | 0.083403 | 0.5905
|  | 4:34 | 8.9056 | 0.080342 | 0.5905
|  | 4:34 | 8.9067 | 0.086139 | 0.59049
|  | 4:34 | 8.9078 | 0.091936 | 0.59049
|  | 4:34 | 8.9089 | 0.086932 | 0.59049
|  | 4:34 | 8.91 | 0.071129 | 0.59049
|  | 4:34 | 8.9111 | 0.055325 | 0.59048
|  | 4:34 | 8.9122 | 0.058039 | 0.59048
|  | 4:34 | 8.9133 | 0.060754 | 0.59048
|  | 4:34 | 8.9144 | 0.053289 | 0.59048
|  | 4:34 | 8.9156 | 0.035644 | 0.59047
|  | 4:34 | 8.9167 | 0.018 | 0.59047
|  | 4:34 | 8.9178 | -0.013065 | 0.59047
|  | 4:35 | 8.9189 | -0.04413 | 0.59047
|  | 4:35 | 8.92 | -0.070275 | 0.59047
|  | 4:35 | 8.9211 | -0.091499 | 0.59046
|  | 4:35 | 8.9222 | -0.11272 | 0.59046
|  | 4:35 | 8.9233 | -0.1153 | 0.59046
|  | 4:35 | 8.9244 | -0.11788 | 0.59046
|  | 4:35 | 8.9256 | -0.11783 | 0.59045
|  | 4:35 | 8.9267 | -0.11514 | 0.59045
|  | 4:35 | 8.9278 | -0.11272 | 0.59045
|  | 4:35 | 8.9289 | -0.11108 | 0.59045
|  | 4:35 | 8.93 | -0.10944 | 0.59044
|  | 4:35 | 8.9311 | -0.1078 | 0.59044
|  | 4:35 | 8.9322 | -0.12031 | 0.59044
|  | 4:35 | 8.9333 | -0.13283 | 0.59044
|  | 4:35 | 8.9344 | -0.13556 | 0.59044
|  | 4:36 | 8.9356 | -0.1383 | 0.59043
|  | 4:36 | 8.9367 | -0.13564 | 0.59043
|  | 4:36 | 8.9378 | -0.13119 | 0.59043
|  | 4:36 | 8.9389 | -0.1251 | 0.59043
|  | 4:36 | 8.94 | -0.11411 | 0.59042
|  | 4:36 | 8.9411 | -0.10312 | 0.59042
|  | 4:36 | 8.9422 | -0.087127 | 0.59042
|  | 4:36 | 8.9433 | -0.06947 | 0.59042
|  | 4:36 | 8.9444 | -0.057029 | 0.59041
|  | 4:36 | 8.9456 | -0.060235 | 0.59041
|  | 4:36 | 8.9467 | -0.06344 | 0.59041
|  | 4:36 | 8.9478 | -0.059529 | 0.59041
|  | 4:36 | 8.9489 | -0.053247 | 0.59041
|  | 4:36 | 8.95 | -0.048412 | 0.5904
|  | 4:36 | 8.9511 | -0.047923 | 0.5904
|  | 4:37 | 8.9522 | -0.047434 | 0.5904
|  | 4:37 | 8.9533 | -0.052124 | 0.5904
|  | 4:37 | 8.9544 | -0.05854 | 0.59039
|  | 4:37 | 8.9556 | -0.068618 | 0.59039
|  | 4:37 | 8.9567 | -0.08968 | 0.59039
|  | 4:37 | 8.9578 | -0.11074 | 0.59039
|  | 4:37 | 8.9589 | -0.12803 | 0.59038
|  | 4:37 | 8.96 | -0.14405 | 0.59038
|  | 4:37 | 8.9611 | -0.15587 | 0.59038
|  | 4:37 | 8.9622 | -0.15507 | 0.59038
|  | 4:37 | 8.9633 | -0.15427 | 0.59037
|  | 4:37 | 8.9644 | -0.1689 | 0.59037
|  | 4:37 | 8.9656 | -0.18867 | 0.59037
|  | 4:37 | 8.9667 | -0.19879 | 0.59037
|  | 4:37 | 8.9678 | -0.17995 | 0.59037
|  | 4:38 | 8.9689 | -0.16112 | 0.59036
|  | 4:38 | 8.97 | -0.14042 | 0.59036
|  | 4:38 | 8.9711 | -0.1191 | 0.59036
|  | 4:38 | 8.9722 | -0.087246 | 0.59036
|  | 4:38 | 8.9733 | -0.023777 | 0.59035
|  | 4:38 | 8.9744 | 0.039692 | 0.59035
|  | 4:38 | 8.9756 | 0.084628 | 0.59035
|  | 4:38 | 8.9767 | 0.12956 | 0.59035
|  | 4:38 | 8.9778 | 0.17372 | 0.59034
|  | 4:38 | 8.9789 | 0.21556 | 0.59034
|  | 4:38 | 8.98 | 0.2574 | 0.59034
|  | 4:38 | 8.9811 | 0.26371 | 0.59034
|  | 4:38 | 8.9822 | 0.25818 | 0.59034
|  | 4:38 | 8.9833 | 0.25264 | 0.59033
|  | 4:38 | 8.9844 | 0.24711 | 0.59033
|  | 4:39 | 8.9856 | 0.24157 | 0.59033
|  | 4:39 | 8.9867 | 0.24404 | 0.59033
|  | 4:39 | 8.9878 | 0.24918 | 0.59032
|  | 4:39 | 8.9889 | 0.25653 | 0.59032
|  | 4:39 | 8.99 | 0.27053 | 0.59032
|  | 4:39 | 8.9911 | 0.28454 | 0.59032
|  | 4:39 | 8.9922 | 0.28643 | 0.59031
|  | 4:39 | 8.9933 | 0.28428 | 0.59031
|  | 4:39 | 8.9944 | 0.28637 | 0.59031
|  | 4:39 | 8.9956 | 0.30114 | 0.59031
|  | 4:39 | 8.9967 | 0.31592 | 0.59031
|  | 4:39 | 8.9978 | 0.32289 | 0.5903
|  | 4:39 | 8.9989 | 0.32726 | 0.5903
|  | 4:39 | 9 | 0.32399 | 0.5903
|  | 4:39 | 9.0011 | 0.3131 | 0.5903
|  | 4:40 | 9.0022 | 0.3022 | 0.59029
|  | 4:40 | 9.0033 | 0.28574 | 0.59029
|  | 4:40 | 9.0044 | 0.26742 | 0.59029
|  | 4:40 | 9.0056 | 0.24996 | 0.59029
|  | 4:40 | 9.0067 | 0.23337 | 0.59028
|  | 4:40 | 9.0078 | 0.21678 | 0.59028
|  | 4:40 | 9.0089 | 0.18735 | 0.59028
|  | 4:40 | 9.01 | 0.15364 | 0.59028
|  | 4:40 | 9.0111 | 0.13899 | 0.59028
|  | 4:40 | 9.0122 | 0.1434 | 0.59027
|  | 4:40 | 9.0133 | 0.1478 | 0.59027
|  | 4:40 | 9.0144 | 0.16101 | 0.59027
|  | 4:40 | 9.0156 | 0.17715 | 0.59027
|  | 4:40 | 9.0167 | 0.1784 | 0.59026
|  | 4:40 | 9.0178 | 0.16474 | 0.59026
|  | 4:41 | 9.0189 | 0.15109 | 0.59026
|  | 4:41 | 9.02 | 0.12306 | 0.59026
|  | 4:41 | 9.0211 | 0.090241 | 0.59025
|  | 4:41 | 9.0222 | 0.056587 | 0.59025
|  | 4:41 | 9.0233 | 0.020429 | 0.59025
|  | 4:41 | 9.0244 | -0.015729 | 0.59025
|  | 4:41 | 9.0256 | -0.042232 | 0.59025
|  | 4:41 | 9.0267 | -0.065516 | 0.59024
|  | 4:41 | 9.0278 | -0.087599 | 0.59024
|  | 4:41 | 9.0289 | -0.10608 | 0.59024
|  | 4:41 | 9.03 | -0.12456 | 0.59024
|  | 4:41 | 9.0311 | -0.13921 | 0.59023
|  | 4:41 | 9.0322 | -0.15259 | 0.59023
|  | 4:41 | 9.0333 | -0.16354 | 0.59023
|  | 4:41 | 9.0344 | -0.16719 | 0.59023
|  | 4:42 | 9.0356 | -0.17083 | 0.59022
|  | 4:42 | 9.0367 | -0.19514 | 0.59022
|  | 4:42 | 9.0378 | -0.22632 | 0.59022
|  | 4:42 | 9.0389 | -0.24783 | 0.59022
|  | 4:42 | 9.04 | -0.24028 | 0.59022
|  | 4:42 | 9.0411 | -0.23273 | 0.59021
|  | 4:42 | 9.0422 | -0.22091 | 0.59021
|  | 4:42 | 9.0433 | -0.20767 | 0.59021
|  | 4:42 | 9.0444 | -0.19169 | 0.59021
|  | 4:42 | 9.0456 | -0.1675 | 0.5902
|  | 4:42 | 9.0467 | -0.14331 | 0.5902
|  | 4:42 | 9.0478 | -0.12658 | 0.5902
|  | 4:42 | 9.0489 | -0.11235 | 0.5902
|  | 4:42 | 9.05 | -0.099041 | 0.59019
|  | 4:42 | 9.0511 | -0.088485 | 0.59019
|  | 4:43 | 9.0522 | -0.077929 | 0.59019
|  | 4:43 | 9.0533 | -0.06405 | 0.59019
|  | 4:43 | 9.0544 | -0.049063 | 0.59019
|  | 4:43 | 9.0556 | -0.032325 | 0.59018
|  | 4:43 | 9.0567 | -0.01033 | 0.59018
|  | 4:43 | 9.0578 | 0.011664 | 0.59018
|  | 4:43 | 9.0589 | 0.025807 | 0.59018
|  | 4:43 | 9.06 | 0.037333 | 0.59017
|  | 4:43 | 9.0611 | 0.049144 | 0.59017
|  | 4:43 | 9.0622 | 0.06181 | 0.59017
|  | 4:43 | 9.0633 | 0.074475 | 0.59017
|  | 4:43 | 9.0644 | 0.088406 | 0.59016
|  | 4:43 | 9.0656 | 0.10276 | 0.59016
|  | 4:43 | 9.0667 | 0.11637 | 0.59016
|  | 4:43 | 9.0678 | 0.12776 | 0.59016
|  | 4:44 | 9.0689 | 0.13916 | 0.59016
|  | 4:44 | 9.07 | 0.15333 | 0.59015
|  | 4:44 | 9.0711 | 0.16843 | 0.59015
|  | 4:44 | 9.0722 | 0.18226 | 0.59015
|  | 4:44 | 9.0733 | 0.19228 | 0.59015
|  | 4:44 | 9.0744 | 0.20229 | 0.59014
|  | 4:44 | 9.0756 | 0.18703 | 0.59014
|  | 4:44 | 9.0767 | 0.17176 | 0.59014
|  | 4:44 | 9.0778 | 0.15361 | 0.59014
|  | 4:44 | 9.0789 | 0.12677 | 0.59013
|  | 4:44 | 9.08 | 0.099932 | 0.59013
|  | 4:44 | 9.0811 | 0.080254 | 0.59013
|  | 4:44 | 9.0822 | 0.062962 | 0.59013
|  | 4:44 | 9.0833 | 0.049071 | 0.59012
|  | 4:44 | 9.0844 | 0.045383 | 0.59012
|  | 4:45 | 9.0856 | 0.041695 | 0.59012
|  | 4:45 | 9.0867 | 0.032198 | 0.59012
|  | 4:45 | 9.0878 | 0.020765 | 0.59012
|  | 4:45 | 9.0889 | 0.010218 | 0.59011
|  | 4:45 | 9.09 | 0.0023298 | 0.59011
|  | 4:45 | 9.0911 | -0.0055582 | 0.59011
|  | 4:45 | 9.0922 | -0.023576 | 0.59011
|  | 4:45 | 9.0933 | -0.04497 | 0.5901
|  | 4:45 | 9.0944 | -0.063236 | 0.5901
|  | 4:45 | 9.0956 | -0.072119 | 0.5901
|  | 4:45 | 9.0967 | -0.081002 | 0.5901
|  | 4:45 | 9.0978 | -0.091497 | 0.59009
|  | 4:45 | 9.0989 | -0.10253 | 0.59009
|  | 4:45 | 9.1 | -0.11184 | 0.59009
|  | 4:45 | 9.1011 | -0.11599 | 0.59009
|  | 4:46 | 9.1022 | -0.12014 | 0.59009
|  | 4:46 | 9.1033 | -0.12608 | 0.59008
|  | 4:46 | 9.1044 | -0.13383 | 0.59008
|  | 4:46 | 9.1056 | -0.14157 | 0.59008
|  | 4:46 | 9.1067 | -0.14002 | 0.59008
|  | 4:46 | 9.1078 | -0.13847 | 0.59007
|  | 4:46 | 9.1089 | -0.14396 | 0.59007
|  | 4:46 | 9.11 | -0.1565 | 0.59007
|  | 4:46 | 9.1111 | -0.16904 | 0.59007
|  | 4:46 | 9.1122 | -0.18405 | 0.59006
|  | 4:46 | 9.1133 | -0.19905 | 0.59006
|  | 4:46 | 9.1144 | -0.20539 | 0.59006
|  | 4:46 | 9.1156 | -0.20306 | 0.59006
|  | 4:46 | 9.1167 | -0.20073 | 0.59006
|  | 4:46 | 9.1178 | -0.17283 | 0.59005
|  | 4:47 | 9.1189 | -0.14493 | 0.59005
|  | 4:47 | 9.12 | -0.1155 | 0.59005
|  | 4:47 | 9.1211 | -0.084542 | 0.59005
|  | 4:47 | 9.1222 | -0.053583 | 0.59004
|  | 4:47 | 9.1233 | -0.01823 | 0.59004
|  | 4:47 | 9.1244 | 0.017124 | 0.59004
|  | 4:47 | 9.1256 | 0.042132 | 0.59004
|  | 4:47 | 9.1267 | 0.056796 | 0.59003
|  | 4:47 | 9.1278 | 0.07146 | 0.59003
|  | 4:47 | 9.1289 | 0.069582 | 0.59003
|  | 4:47 | 9.13 | 0.067705 | 0.59003
|  | 4:47 | 9.1311 | 0.068706 | 0.59003
|  | 4:47 | 9.1322 | 0.072586 | 0.59002
|  | 4:47 | 9.1333 | 0.076467 | 0.59002
|  | 4:47 | 9.1344 | 0.08665 | 0.59002
|  | 4:48 | 9.1356 | 0.096832 | 0.59002
|  | 4:48 | 9.1367 | 0.097433 | 0.59001
|  | 4:48 | 9.1378 | 0.088452 | 0.59001
|  | 4:48 | 9.1389 | 0.079471 | 0.59001
|  | 4:48 | 9.14 | 0.07049 | 0.59001
|  | 4:48 | 9.1411 | 0.061509 | 0.59
|  | 4:48 | 9.1422 | 0.044761 | 0.59
|  | 4:48 | 9.1433 | 0.020245 | 0.59
|  | 4:48 | 9.1444 | -0.0042709 | 0.59
|  | 4:48 | 9.1456 | -0.0071686 | 0.59
|  | 4:48 | 9.1467 | -0.010066 | 0.58999
|  | 4:48 | 9.1478 | -0.015785 | 0.58999
|  | 4:48 | 9.1489 | -0.024325 | 0.58999
|  | 4:48 | 9.15 | -0.032865 | 0.58999
|  | 4:48 | 9.1511 | -0.041405 | 0.58998
|  | 4:49 | 9.1522 | -0.049945 | 0.58998
|  | 4:49 | 9.1533 | -0.061732 | 0.58998
|  | 4:49 | 9.1544 | -0.076764 | 0.58998
|  | 4:49 | 9.1556 | -0.091797 | 0.58997
|  | 4:49 | 9.1567 | -0.081949 | 0.58997
|  | 4:49 | 9.1578 | -0.072101 | 0.58997
|  | 4:49 | 9.1589 | -0.069993 | 0.58997
|  | 4:49 | 9.16 | -0.075625 | 0.58997
|  | 4:49 | 9.1611 | -0.081256 | 0.58996
|  | 4:49 | 9.1622 | -0.10398 | 0.58996
|  | 4:49 | 9.1633 | -0.12671 | 0.58996
|  | 4:49 | 9.1644 | -0.13424 | 0.58996
|  | 4:49 | 9.1656 | -0.13671 | 0.58995
|  | 4:49 | 9.1667 | -0.13917 | 0.58995
|  | 4:49 | 9.1678 | -0.13967 | 0.58995
|  | 4:50 | 9.1689 | -0.14016 | 0.58995
|  | 4:50 | 9.17 | -0.13967 | 0.58994
|  | 4:50 | 9.1711 | -0.1382 | 0.58994
|  | 4:50 | 9.1722 | -0.13672 | 0.58994
|  | 4:50 | 9.1733 | -0.13986 | 0.58994
|  | 4:50 | 9.1744 | -0.143 | 0.58994
|  | 4:50 | 9.1756 | -0.15783 | 0.58993
|  | 4:50 | 9.1767 | -0.18435 | 0.58993
|  | 4:50 | 9.1778 | -0.21088 | 0.58993
|  | 4:50 | 9.1789 | -0.23015 | 0.58993
|  | 4:50 | 9.18 | -0.24943 | 0.58992
|  | 4:50 | 9.1811 | -0.27026 | 0.58992
|  | 4:50 | 9.1822 | -0.29265 | 0.58992
|  | 4:50 | 9.1833 | -0.31503 | 0.58992
|  | 4:50 | 9.1844 | -0.32195 | 0.58991
|  | 4:51 | 9.1856 | -0.32886 | 0.58991
|  | 4:51 | 9.1867 | -0.34119 | 0.58991
|  | 4:51 | 9.1878 | -0.35894 | 0.58991
|  | 4:51 | 9.1889 | -0.37669 | 0.58991
|  | 4:51 | 9.19 | -0.40678 | 0.5899
|  | 4:51 | 9.1911 | -0.43687 | 0.5899
|  | 4:51 | 9.1922 | -0.47126 | 0.5899
|  | 4:51 | 9.1933 | -0.50996 | 0.5899
|  | 4:51 | 9.1944 | -0.54865 | 0.58989
|  | 4:51 | 9.1956 | -0.56956 | 0.58989
|  | 4:51 | 9.1967 | -0.59046 | 0.58989
|  | 4:51 | 9.1978 | -0.60099 | 0.58989
|  | 4:51 | 9.1989 | -0.60114 | 0.58988
|  | 4:51 | 9.2 | -0.60129 | 0.58988
|  | 4:51 | 9.2011 | -0.60725 | 0.58988
|  | 4:52 | 9.2022 | -0.6132 | 0.58988
|  | 4:52 | 9.2033 | -0.61495 | 0.58987
|  | 4:52 | 9.2044 | -0.6125 | 0.58987
|  | 4:52 | 9.2056 | -0.61004 | 0.58987
|  | 4:52 | 9.2067 | -0.60192 | 0.58987
|  | 4:52 | 9.2078 | -0.59379 | 0.58987
|  | 4:52 | 9.2089 | -0.57338 | 0.58986
|  | 4:52 | 9.21 | -0.54068 | 0.58986
|  | 4:52 | 9.2111 | -0.50798 | 0.58986
|  | 4:52 | 9.2122 | -0.44948 | 0.58986
|  | 4:52 | 9.2133 | -0.39097 | 0.58985
|  | 4:52 | 9.2144 | -0.34491 | 0.58985
|  | 4:52 | 9.2156 | -0.30298 | 0.58985
|  | 4:52 | 9.2167 | -0.26106 | 0.58985
|  | 4:52 | 9.2178 | -0.21372 | 0.58984
|  | 4:53 | 9.2189 | -0.16637 | 0.58984
|  | 4:53 | 9.22 | -0.13138 | 0.58984
|  | 4:53 | 9.2211 | -0.10875 | 0.58984
|  | 4:53 | 9.2222 | -0.086123 | 0.58984
|  | 4:53 | 9.2233 | -0.059309 | 0.58983
|  | 4:53 | 9.2244 | -0.032495 | 0.58983
|  | 4:53 | 9.2256 | -0.0085625 | 0.58983
|  | 4:53 | 9.2267 | 0.01441 | 0.58983
|  | 4:53 | 9.2278 | 0.037382 | 0.58982
|  | 4:53 | 9.2289 | 0.066252 | 0.58982
|  | 4:53 | 9.23 | 0.095122 | 0.58982
|  | 4:53 | 9.2311 | 0.10872 | 0.58982
|  | 4:53 | 9.2322 | 0.10704 | 0.58981
|  | 4:53 | 9.2333 | 0.10536 | 0.58981
|  | 4:53 | 9.2344 | 0.10089 | 0.58981
|  | 4:54 | 9.2356 | 0.088038 | 0.58981
|  | 4:54 | 9.2367 | 0.080428 | 0.58981
|  | 4:54 | 9.2378 | 0.078054 | 0.5898
|  | 4:54 | 9.2389 | 0.07568 | 0.5898
|  | 4:54 | 9.24 | 0.060873 | 0.5898
|  | 4:54 | 9.2411 | 0.046067 | 0.5898
|  | 4:54 | 9.2422 | 0.032489 | 0.58979
|  | 4:54 | 9.2433 | 0.02014 | 0.58979
|  | 4:54 | 9.2444 | 0.0077913 | 0.58979
|  | 4:54 | 9.2456 | 0.0089382 | 0.58979
|  | 4:54 | 9.2467 | 0.010085 | 0.58978
|  | 4:54 | 9.2478 | 0.017944 | 0.58978
|  | 4:54 | 9.2489 | 0.032514 | 0.58978
|  | 4:54 | 9.25 | 0.047085 | 0.58978
|  | 4:54 | 9.2511 | 0.076109 | 0.58978
|  | 4:55 | 9.2522 | 0.10513 | 0.58977
|  | 4:55 | 9.2533 | 0.13867 | 0.58977
|  | 4:55 | 9.2544 | 0.17371 | 0.58977
|  | 4:55 | 9.2556 | 0.20875 | 0.58977
|  | 4:55 | 9.2567 | 0.23334 | 0.58976
|  | 4:55 | 9.2578 | 0.25792 | 0.58976
|  | 4:55 | 9.2589 | 0.27615 | 0.58976
|  | 4:55 | 9.26 | 0.28804 | 0.58976
|  | 4:55 | 9.2611 | 0.29992 | 0.58975
|  | 4:55 | 9.2622 | 0.31798 | 0.58975
|  | 4:55 | 9.2633 | 0.33605 | 0.58975
|  | 4:55 | 9.2644 | 0.36385 | 0.58975
|  | 4:55 | 9.2656 | 0.40137 | 0.58975
|  | 4:55 | 9.2667 | 0.4389 | 0.58974
|  | 4:55 | 9.2678 | 0.47837 | 0.58974
|  | 4:56 | 9.2689 | 0.51784 | 0.58974
|  | 4:56 | 9.27 | 0.54605 | 0.58974
|  | 4:56 | 9.2711 | 0.57051 | 0.58973
|  | 4:56 | 9.2722 | 0.59043 | 0.58973
|  | 4:56 | 9.2733 | 0.59672 | 0.58973
|  | 4:56 | 9.2744 | 0.60301 | 0.58973
|  | 4:56 | 9.2756 | 0.61476 | 0.58972
|  | 4:56 | 9.2767 | 0.62833 | 0.58972
|  | 4:56 | 9.2778 | 0.63908 | 0.58972
|  | 4:56 | 9.2789 | 0.64134 | 0.58972
|  | 4:56 | 9.28 | 0.6436 | 0.58972
|  | 4:56 | 9.2811 | 0.64966 | 0.58971
|  | 4:56 | 9.2822 | 0.65699 | 0.58971
|  | 4:56 | 9.2833 | 0.66861 | 0.58971
|  | 4:56 | 9.2844 | 0.69311 | 0.58971
|  | 4:57 | 9.2856 | 0.71761 | 0.5897
|  | 4:57 | 9.2867 | 0.72431 | 0.5897
|  | 4:57 | 9.2878 | 0.72507 | 0.5897
|  | 4:57 | 9.2889 | 0.72324 | 0.5897
|  | 4:57 | 9.29 | 0.71361 | 0.58969
|  | 4:57 | 9.2911 | 0.70399 | 0.58969
|  | 4:57 | 9.2922 | 0.68391 | 0.58969
|  | 4:57 | 9.2933 | 0.66036 | 0.58969
|  | 4:57 | 9.2944 | 0.63042 | 0.58969
|  | 4:57 | 9.2956 | 0.58134 | 0.58968
|  | 4:57 | 9.2967 | 0.53226 | 0.58968
|  | 4:57 | 9.2978 | 0.48119 | 0.58968
|  | 4:57 | 9.2989 | 0.42944 | 0.58968
|  | 4:57 | 9.3 | 0.38903 | 0.58967
|  | 4:57 | 9.3011 | 0.35995 | 0.58967
|  | 4:58 | 9.3022 | 0.33088 | 0.58967
|  | 4:58 | 9.3033 | 0.2821 | 0.58967
|  | 4:58 | 9.3044 | 0.22676 | 0.58966
|  | 4:58 | 9.3056 | 0.17658 | 0.58966
|  | 4:58 | 9.3067 | 0.1419 | 0.58966
|  | 4:58 | 9.3078 | 0.10722 | 0.58966
|  | 4:58 | 9.3089 | 0.081901 | 0.58966
|  | 4:58 | 9.31 | 0.056586 | 0.58965
|  | 4:58 | 9.3111 | 0.030142 | 0.58965
|  | 4:58 | 9.3122 | 0.00031549 | 0.58965
|  | 4:58 | 9.3133 | -0.029511 | 0.58965
|  | 4:58 | 9.3144 | -0.058698 | 0.58964
|  | 4:58 | 9.3156 | -0.087671 | 0.58964
|  | 4:58 | 9.3167 | -0.11306 | 0.58964
|  | 4:58 | 9.3178 | -0.12771 | 0.58964
|  | 4:59 | 9.3189 | -0.14236 | 0.58963
|  | 4:59 | 9.32 | -0.16624 | 0.58963
|  | 4:59 | 9.3211 | -0.1932 | 0.58963
|  | 4:59 | 9.3222 | -0.22575 | 0.58963
|  | 4:59 | 9.3233 | -0.2751 | 0.58962
|  | 4:59 | 9.3244 | -0.32445 | 0.58962
|  | 4:59 | 9.3256 | -0.35449 | 0.58962
|  | 4:59 | 9.3267 | -0.37809 | 0.58962
|  | 4:59 | 9.3278 | -0.39723 | 0.58962
|  | 4:59 | 9.3289 | -0.40298 | 0.58961
|  | 4:59 | 9.33 | -0.40874 | 0.58961
|  | 4:59 | 9.3311 | -0.41121 | 0.58961
|  | 4:59 | 9.3322 | -0.41258 | 0.58961
|  | 4:59 | 9.3333 | -0.4191 | 0.5896
|  | 4:59 | 9.3344 | -0.44105 | 0.5896
|  | 5:00 | 9.3356 | -0.46301 | 0.5896
|  | 5:00 | 9.3367 | -0.4794 | 0.5896
|  | 5:00 | 9.3378 | -0.49394 | 0.58959
|  | 5:00 | 9.3389 | -0.50803 | 0.58959
|  | 5:00 | 9.34 | -0.52082 | 0.58959
|  | 5:00 | 9.3411 | -0.53361 | 0.58959
|  | 5:00 | 9.3422 | -0.57167 | 0.58959
|  | 5:00 | 9.3433 | -0.61817 | 0.58958
|  | 5:00 | 9.3444 | -0.65686 | 0.58958
|  | 5:00 | 9.3456 | -0.67212 | 0.58958
|  | 5:00 | 9.3467 | -0.68739 | 0.58958
|  | 5:00 | 9.3478 | -0.69862 | 0.58957
|  | 5:00 | 9.3489 | -0.7085 | 0.58957
|  | 5:00 | 9.35 | -0.7136 | 0.58957
|  | 5:00 | 9.3511 | -0.70432 | 0.58957
|  | 5:01 | 9.3522 | -0.69505 | 0.58956
|  | 5:01 | 9.3533 | -0.67207 | 0.58956
|  | 5:01 | 9.3544 | -0.64451 | 0.58956
|  | 5:01 | 9.3556 | -0.61836 | 0.58956
|  | 5:01 | 9.3567 | -0.59644 | 0.58956
|  | 5:01 | 9.3578 | -0.57451 | 0.58955
|  | 5:01 | 9.3589 | -0.55325 | 0.58955
|  | 5:01 | 9.36 | -0.53222 | 0.58955
|  | 5:01 | 9.3611 | -0.51696 | 0.58955
|  | 5:01 | 9.3622 | -0.51903 | 0.58954
|  | 5:01 | 9.3633 | -0.5211 | 0.58954
|  | 5:01 | 9.3644 | -0.52402 | 0.58954
|  | 5:01 | 9.3656 | -0.52724 | 0.58954
|  | 5:01 | 9.3667 | -0.52781 | 0.58953
|  | 5:01 | 9.3678 | -0.52046 | 0.58953
|  | 5:02 | 9.3689 | -0.51311 | 0.58953
|  | 5:02 | 9.37 | -0.49295 | 0.58953
|  | 5:02 | 9.3711 | -0.46852 | 0.58953
|  | 5:02 | 9.3722 | -0.44277 | 0.58952
|  | 5:02 | 9.3733 | -0.41302 | 0.58952
|  | 5:02 | 9.3744 | -0.38327 | 0.58952
|  | 5:02 | 9.3756 | -0.36219 | 0.58952
|  | 5:02 | 9.3767 | -0.34399 | 0.58951
|  | 5:02 | 9.3778 | -0.32331 | 0.58951
|  | 5:02 | 9.3789 | -0.29521 | 0.58951
|  | 5:02 | 9.38 | -0.26711 | 0.58951
|  | 5:02 | 9.3811 | -0.22818 | 0.5895
|  | 5:02 | 9.3822 | -0.18565 | 0.5895
|  | 5:02 | 9.3833 | -0.14681 | 0.5895
|  | 5:02 | 9.3844 | -0.11909 | 0.5895
|  | 5:03 | 9.3856 | -0.091362 | 0.5895
|  | 5:03 | 9.3867 | -0.063635 | 0.58949
|  | 5:03 | 9.3878 | -0.035909 | 0.58949
|  | 5:03 | 9.3889 | -0.010399 | 0.58949
|  | 5:03 | 9.39 | 0.008462 | 0.58949
|  | 5:03 | 9.3911 | 0.027323 | 0.58948
|  | 5:03 | 9.3922 | 0.034398 | 0.58948
|  | 5:03 | 9.3933 | 0.037546 | 0.58948
|  | 5:03 | 9.3944 | 0.043552 | 0.58948
|  | 5:03 | 9.3956 | 0.058133 | 0.58947
|  | 5:03 | 9.3967 | 0.072714 | 0.58947
|  | 5:03 | 9.3978 | 0.058027 | 0.58947
|  | 5:03 | 9.3989 | 0.033585 | 0.58947
|  | 5:03 | 9.4 | 0.0091424 | 0.58947
|  | 5:03 | 9.4011 | -0.0069915 | 0.58946
|  | 5:04 | 9.4022 | -0.014817 | 0.58946
|  | 5:04 | 9.4033 | -0.013008 | 0.58946
|  | 5:04 | 9.4044 | -0.0079873 | 0.58946
|  | 5:04 | 9.4056 | -0.0032145 | 0.58945
|  | 5:04 | 9.4067 | 0.00081442 | 0.58945
|  | 5:04 | 9.4078 | 0.0048433 | 0.58945
|  | 5:04 | 9.4089 | -0.011699 | 0.58945
|  | 5:04 | 9.41 | -0.035099 | 0.58944
|  | 5:04 | 9.4111 | -0.062149 | 0.58944
|  | 5:04 | 9.4122 | -0.10015 | 0.58944
|  | 5:04 | 9.4133 | -0.13814 | 0.58944
|  | 5:04 | 9.4144 | -0.15922 | 0.58944
|  | 5:04 | 9.4156 | -0.17466 | 0.58943
|  | 5:04 | 9.4167 | -0.18651 | 0.58943
|  | 5:04 | 9.4178 | -0.18759 | 0.58943
|  | 5:05 | 9.4189 | -0.18868 | 0.58943
|  | 5:05 | 9.42 | -0.16432 | 0.58942
|  | 5:05 | 9.4211 | -0.13147 | 0.58942
|  | 5:05 | 9.4222 | -0.097254 | 0.58942
|  | 5:05 | 9.4233 | -0.058911 | 0.58942
|  | 5:05 | 9.4244 | -0.020569 | 0.58941
|  | 5:05 | 9.4256 | 0.017096 | 0.58941
|  | 5:05 | 9.4267 | 0.054534 | 0.58941
|  | 5:05 | 9.4278 | 0.085579 | 0.58941
|  | 5:05 | 9.4289 | 0.097447 | 0.58941
|  | 5:05 | 9.43 | 0.10931 | 0.5894
|  | 5:05 | 9.4311 | 0.11074 | 0.5894
|  | 5:05 | 9.4322 | 0.10868 | 0.5894
|  | 5:05 | 9.4333 | 0.10522 | 0.5894
|  | 5:05 | 9.4344 | 0.097578 | 0.58939
|  | 5:06 | 9.4356 | 0.089932 | 0.58939
|  | 5:06 | 9.4367 | 0.073569 | 0.58939
|  | 5:06 | 9.4378 | 0.048491 | 0.58939
|  | 5:06 | 9.4389 | 0.023412 | 0.58938
|  | 5:06 | 9.44 | 0.0095454 | 0.58938
|  | 5:06 | 9.4411 | -0.0043213 | 0.58938
|  | 5:06 | 9.4422 | -0.0022857 | 0.58938
|  | 5:06 | 9.4433 | 0.015652 | 0.58937
|  | 5:06 | 9.4444 | 0.03359 | 0.58937
|  | 5:06 | 9.4456 | 0.10038 | 0.58937
|  | 5:06 | 9.4467 | 0.16717 | 0.58937
|  | 5:06 | 9.4478 | 0.23184 | 0.58937
|  | 5:06 | 9.4489 | 0.29437 | 0.58936
|  | 5:06 | 9.45 | 0.35691 | 0.58936
|  | 5:06 | 9.4511 | 0.38203 | 0.58936
|  | 5:07 | 9.4522 | 0.40715 | 0.58936
|  | 5:07 | 9.4533 | 0.43669 | 0.58935
|  | 5:07 | 9.4544 | 0.47067 | 0.58935
|  | 5:07 | 9.4556 | 0.50464 | 0.58935
|  | 5:07 | 9.4567 | 0.51512 | 0.58935
|  | 5:07 | 9.4578 | 0.52559 | 0.58934
|  | 5:07 | 9.4589 | 0.54013 | 0.58934
|  | 5:07 | 9.46 | 0.55874 | 0.58934
|  | 5:07 | 9.4611 | 0.57735 | 0.58934
|  | 5:07 | 9.4622 | 0.57414 | 0.58934
|  | 5:07 | 9.4633 | 0.57092 | 0.58933
|  | 5:07 | 9.4644 | 0.57038 | 0.58933
|  | 5:07 | 9.4656 | 0.57251 | 0.58933
|  | 5:07 | 9.4667 | 0.57464 | 0.58933
|  | 5:07 | 9.4678 | 0.57446 | 0.58932
|  | 5:08 | 9.4689 | 0.57428 | 0.58932
|  | 5:08 | 9.47 | 0.56794 | 0.58932
|  | 5:08 | 9.4711 | 0.55544 | 0.58932
|  | 5:08 | 9.4722 | 0.54294 | 0.58931
|  | 5:08 | 9.4733 | 0.53362 | 0.58931
|  | 5:08 | 9.4744 | 0.52431 | 0.58931
|  | 5:08 | 9.4756 | 0.51346 | 0.58931
|  | 5:08 | 9.4767 | 0.50109 | 0.58931
|  | 5:08 | 9.4778 | 0.48871 | 0.5893
|  | 5:08 | 9.4789 | 0.46532 | 0.5893
|  | 5:08 | 9.48 | 0.44193 | 0.5893
|  | 5:08 | 9.4811 | 0.41736 | 0.5893
|  | 5:08 | 9.4822 | 0.39241 | 0.58929
|  | 5:08 | 9.4833 | 0.36745 | 0.58929
|  | 5:08 | 9.4844 | 0.32955 | 0.58929
|  | 5:09 | 9.4856 | 0.29165 | 0.58929
|  | 5:09 | 9.4867 | 0.25312 | 0.58928
|  | 5:09 | 9.4878 | 0.21396 | 0.58928
|  | 5:09 | 9.4889 | 0.1748 | 0.58928
|  | 5:09 | 9.49 | 0.11481 | 0.58928
|  | 5:09 | 9.4911 | 0.054818 | 0.58928
|  | 5:09 | 9.4922 | -0.0065868 | 0.58927
|  | 5:09 | 9.4933 | -0.068462 | 0.58927
|  | 5:09 | 9.4944 | -0.13034 | 0.58927
|  | 5:09 | 9.4956 | -0.17611 | 0.58927
|  | 5:09 | 9.4967 | -0.22189 | 0.58926
|  | 5:09 | 9.4978 | -0.26715 | 0.58926
|  | 5:09 | 9.4989 | -0.3119 | 0.58926
|  | 5:09 | 9.5 | -0.35665 | 0.58926
|  | 5:09 | 9.5011 | -0.39577 | 0.58925
|  | 5:10 | 9.5022 | -0.43489 | 0.58925
|  | 5:10 | 9.5033 | -0.45765 | 0.58925
|  | 5:10 | 9.5044 | -0.46406 | 0.58925
|  | 5:10 | 9.5056 | -0.47047 | 0.58925
|  | 5:10 | 9.5067 | -0.45239 | 0.58924
|  | 5:10 | 9.5078 | -0.4343 | 0.58924
|  | 5:10 | 9.5089 | -0.42879 | 0.58924
|  | 5:10 | 9.51 | -0.43588 | 0.58924
|  | 5:10 | 9.5111 | -0.44296 | 0.58923
|  | 5:10 | 9.5122 | -0.44646 | 0.58923
|  | 5:10 | 9.5133 | -0.44997 | 0.58923
|  | 5:10 | 9.5144 | -0.44712 | 0.58923
|  | 5:10 | 9.5156 | -0.43794 | 0.58922
|  | 5:10 | 9.5167 | -0.42875 | 0.58922
|  | 5:10 | 9.5178 | -0.42518 | 0.58922
|  | 5:11 | 9.5189 | -0.42161 | 0.58922
|  | 5:11 | 9.52 | -0.42556 | 0.58922
|  | 5:11 | 9.5211 | -0.43704 | 0.58921
|  | 5:11 | 9.5222 | -0.44852 | 0.58921
|  | 5:11 | 9.5233 | -0.44164 | 0.58921
|  | 5:11 | 9.5244 | -0.43475 | 0.58921
|  | 5:11 | 9.5256 | -0.42925 | 0.5892
|  | 5:11 | 9.5267 | -0.42513 | 0.5892
|  | 5:11 | 9.5278 | -0.421 | 0.5892
|  | 5:11 | 9.5289 | -0.40086 | 0.5892
|  | 5:11 | 9.53 | -0.38072 | 0.58919
|  | 5:11 | 9.5311 | -0.36457 | 0.58919
|  | 5:11 | 9.5322 | -0.35242 | 0.58919
|  | 5:11 | 9.5333 | -0.34187 | 0.58919
|  | 5:11 | 9.5344 | -0.33616 | 0.58919
|  | 5:12 | 9.5356 | -0.33044 | 0.58918
|  | 5:12 | 9.5367 | -0.31632 | 0.58918
|  | 5:12 | 9.5378 | -0.29381 | 0.58918
|  | 5:12 | 9.5389 | -0.2713 | 0.58918
|  | 5:12 | 9.54 | -0.25262 | 0.58917
|  | 5:12 | 9.5411 | -0.23394 | 0.58917
|  | 5:12 | 9.5422 | -0.21066 | 0.58917
|  | 5:12 | 9.5433 | -0.18278 | 0.58917
|  | 5:12 | 9.5444 | -0.1549 | 0.58916
|  | 5:12 | 9.5456 | -0.1598 | 0.58916
|  | 5:12 | 9.5467 | -0.1647 | 0.58916
|  | 5:12 | 9.5478 | -0.16862 | 0.58916
|  | 5:12 | 9.5489 | -0.17156 | 0.58916
|  | 5:12 | 9.55 | -0.17451 | 0.58915
|  | 5:12 | 9.5511 | -0.16854 | 0.58915
|  | 5:13 | 9.5522 | -0.16258 | 0.58915
|  | 5:13 | 9.5533 | -0.16124 | 0.58915
|  | 5:13 | 9.5544 | -0.16454 | 0.58914
|  | 5:13 | 9.5556 | -0.16783 | 0.58914
|  | 5:13 | 9.5567 | -0.15843 | 0.58914
|  | 5:13 | 9.5578 | -0.14903 | 0.58914
|  | 5:13 | 9.5589 | -0.12965 | 0.58913
|  | 5:13 | 9.56 | -0.10029 | 0.58913
|  | 5:13 | 9.5611 | -0.070943 | 0.58913
|  | 5:13 | 9.5622 | -0.066805 | 0.58913
|  | 5:13 | 9.5633 | -0.062667 | 0.58912
|  | 5:13 | 9.5644 | -0.054492 | 0.58912
|  | 5:13 | 9.5656 | -0.042281 | 0.58912
|  | 5:13 | 9.5667 | -0.030069 | 0.58912
|  | 5:13 | 9.5678 | -0.017858 | 0.58912
|  | 5:14 | 9.5689 | 0.0074794 | 0.58911
|  | 5:14 | 9.57 | 0.030449 | 0.58911
|  | 5:14 | 9.5711 | 0.046317 | 0.58911
|  | 5:14 | 9.5722 | 0.062185 | 0.58911
|  | 5:14 | 9.5733 | 0.082672 | 0.5891
|  | 5:14 | 9.5744 | 0.10316 | 0.5891
|  | 5:14 | 9.5756 | 0.12318 | 0.5891
|  | 5:14 | 9.5767 | 0.14273 | 0.5891
|  | 5:14 | 9.5778 | 0.16229 | 0.58909
|  | 5:14 | 9.5789 | 0.17597 | 0.58909
|  | 5:14 | 9.58 | 0.18965 | 0.58909
|  | 5:14 | 9.5811 | 0.21106 | 0.58909
|  | 5:14 | 9.5822 | 0.24018 | 0.58909
|  | 5:14 | 9.5833 | 0.2693 | 0.58908
|  | 5:14 | 9.5844 | 0.28985 | 0.58908
|  | 5:15 | 9.5856 | 0.3104 | 0.58908
|  | 5:15 | 9.5867 | 0.32411 | 0.58908
|  | 5:15 | 9.5878 | 0.33098 | 0.58907
|  | 5:15 | 9.5889 | 0.33785 | 0.58907
|  | 5:15 | 9.59 | 0.3406 | 0.58907
|  | 5:15 | 9.5911 | 0.34335 | 0.58907
|  | 5:15 | 9.5922 | 0.34433 | 0.58906
|  | 5:15 | 9.5933 | 0.34356 | 0.58906
|  | 5:15 | 9.5944 | 0.34278 | 0.58906
|  | 5:15 | 9.5956 | 0.3594 | 0.58906
|  | 5:15 | 9.5967 | 0.37602 | 0.58906
|  | 5:15 | 9.5978 | 0.39263 | 0.58905
|  | 5:15 | 9.5989 | 0.40925 | 0.58905
|  | 5:15 | 9.6 | 0.42587 | 0.58905
|  | 5:15 | 9.6011 | 0.4182 | 0.58905
|  | 5:16 | 9.6022 | 0.41053 | 0.58904
|  | 5:16 | 9.6033 | 0.39842 | 0.58904
|  | 5:16 | 9.6044 | 0.38187 | 0.58904
|  | 5:16 | 9.6056 | 0.36532 | 0.58904
|  | 5:16 | 9.6067 | 0.33087 | 0.58903
|  | 5:16 | 9.6078 | 0.29642 | 0.58903
|  | 5:16 | 9.6089 | 0.28083 | 0.58903
|  | 5:16 | 9.61 | 0.28412 | 0.58903
|  | 5:16 | 9.6111 | 0.2874 | 0.58903
|  | 5:16 | 9.6122 | 0.2724 | 0.58902
|  | 5:16 | 9.6133 | 0.2574 | 0.58902
|  | 5:16 | 9.6144 | 0.2361 | 0.58902
|  | 5:16 | 9.6156 | 0.2085 | 0.58902
|  | 5:16 | 9.6167 | 0.18089 | 0.58901
|  | 5:16 | 9.6178 | 0.14929 | 0.58901
|  | 5:17 | 9.6189 | 0.11769 | 0.58901
|  | 5:17 | 9.62 | 0.10424 | 0.58901
|  | 5:17 | 9.6211 | 0.096831 | 0.589
|  | 5:17 | 9.6222 | 0.089426 | 0.589
|  | 5:17 | 9.6233 | 0.072852 | 0.589
|  | 5:17 | 9.6244 | 0.056277 | 0.589
|  | 5:17 | 9.6256 | 0.041294 | 0.589
|  | 5:17 | 9.6267 | 0.027902 | 0.58899
|  | 5:17 | 9.6278 | 0.01451 | 0.58899
|  | 5:17 | 9.6289 | -0.0091688 | 0.58899
|  | 5:17 | 9.63 | -0.032848 | 0.58899
|  | 5:17 | 9.6311 | -0.066966 | 0.58898
|  | 5:17 | 9.6322 | -0.11152 | 0.58898
|  | 5:17 | 9.6333 | -0.15608 | 0.58898
|  | 5:17 | 9.6344 | -0.17782 | 0.58898
|  | 5:18 | 9.6356 | -0.19956 | 0.58897
|  | 5:18 | 9.6367 | -0.21505 | 0.58897
|  | 5:18 | 9.6378 | -0.2243 | 0.58897
|  | 5:18 | 9.6389 | -0.23485 | 0.58897
|  | 5:18 | 9.64 | -0.24933 | 0.58897
|  | 5:18 | 9.6411 | -0.26381 | 0.58896
|  | 5:18 | 9.6422 | -0.28585 | 0.58896
|  | 5:18 | 9.6433 | -0.31041 | 0.58896
|  | 5:18 | 9.6444 | -0.33498 | 0.58896
|  | 5:18 | 9.6456 | -0.35433 | 0.58895
|  | 5:18 | 9.6467 | -0.37369 | 0.58895
|  | 5:18 | 9.6478 | -0.38334 | 0.58895
|  | 5:18 | 9.6489 | -0.38329 | 0.58895
|  | 5:18 | 9.65 | -0.38325 | 0.58894
|  | 5:18 | 9.6511 | -0.37177 | 0.58894
|  | 5:19 | 9.6522 | -0.36028 | 0.58894
|  | 5:19 | 9.6533 | -0.34955 | 0.58894
|  | 5:19 | 9.6544 | -0.33956 | 0.58894
|  | 5:19 | 9.6556 | -0.32957 | 0.58893
|  | 5:19 | 9.6567 | -0.32282 | 0.58893
|  | 5:19 | 9.6578 | -0.31608 | 0.58893
|  | 5:19 | 9.6589 | -0.30933 | 0.58893
|  | 5:19 | 9.66 | -0.30258 | 0.58892
|  | 5:19 | 9.6611 | -0.2977 | 0.58892
|  | 5:19 | 9.6622 | -0.29843 | 0.58892
|  | 5:19 | 9.6633 | -0.29916 | 0.58892
|  | 5:19 | 9.6644 | -0.3059 | 0.58891
|  | 5:19 | 9.6656 | -0.31865 | 0.58891
|  | 5:19 | 9.6667 | -0.33141 | 0.58891
|  | 5:19 | 9.6678 | -0.34928 | 0.58891
|  | 5:20 | 9.6689 | -0.36715 | 0.58891
|  | 5:20 | 9.67 | -0.36743 | 0.5889
|  | 5:20 | 9.6711 | -0.35014 | 0.5889
|  | 5:20 | 9.6722 | -0.33284 | 0.5889
|  | 5:20 | 9.6733 | -0.32614 | 0.5889
|  | 5:20 | 9.6744 | -0.31945 | 0.58889
|  | 5:20 | 9.6756 | -0.32347 | 0.58889
|  | 5:20 | 9.6767 | -0.33105 | 0.58889
|  | 5:20 | 9.6778 | -0.33863 | 0.58889
|  | 5:20 | 9.6789 | -0.34742 | 0.58888
|  | 5:20 | 9.68 | -0.35621 | 0.58888
|  | 5:20 | 9.6811 | -0.35525 | 0.58888
|  | 5:20 | 9.6822 | -0.34453 | 0.58888
|  | 5:20 | 9.6833 | -0.33382 | 0.58887
|  | 5:20 | 9.6844 | -0.32408 | 0.58887
|  | 5:21 | 9.6856 | -0.31435 | 0.58887
|  | 5:21 | 9.6867 | -0.29629 | 0.58887
|  | 5:21 | 9.6878 | -0.2699 | 0.58887
|  | 5:21 | 9.6889 | -0.24351 | 0.58886
|  | 5:21 | 9.69 | -0.22981 | 0.58886
|  | 5:21 | 9.6911 | -0.21611 | 0.58886
|  | 5:21 | 9.6922 | -0.19988 | 0.58886
|  | 5:21 | 9.6933 | -0.18112 | 0.58885
|  | 5:21 | 9.6944 | -0.16235 | 0.58885
|  | 5:21 | 9.6956 | -0.16142 | 0.58885
|  | 5:21 | 9.6967 | -0.16049 | 0.58885
|  | 5:21 | 9.6978 | -0.15389 | 0.58884
|  | 5:21 | 9.6989 | -0.14164 | 0.58884
|  | 5:21 | 9.7 | -0.12939 | 0.58884
|  | 5:21 | 9.7011 | -0.12526 | 0.58884
|  | 5:22 | 9.7022 | -0.12113 | 0.58884
|  | 5:22 | 9.7033 | -0.12313 | 0.58883
|  | 5:22 | 9.7044 | -0.13125 | 0.58883
|  | 5:22 | 9.7056 | -0.13938 | 0.58883
|  | 5:22 | 9.7067 | -0.13197 | 0.58883
|  | 5:22 | 9.7078 | -0.12456 | 0.58882
|  | 5:22 | 9.7089 | -0.11274 | 0.58882
|  | 5:22 | 9.71 | -0.096521 | 0.58882
|  | 5:22 | 9.7111 | -0.080302 | 0.58882
|  | 5:22 | 9.7122 | -0.054155 | 0.58881
|  | 5:22 | 9.7133 | -0.028008 | 0.58881
|  | 5:22 | 9.7144 | -0.0045076 | 0.58881
|  | 5:22 | 9.7156 | 0.016347 | 0.58881
|  | 5:22 | 9.7167 | 0.037201 | 0.58881
|  | 5:22 | 9.7178 | 0.038561 | 0.5888
|  | 5:23 | 9.7189 | 0.039921 | 0.5888
|  | 5:23 | 9.72 | 0.04462 | 0.5888
|  | 5:23 | 9.7211 | 0.052657 | 0.5888
|  | 5:23 | 9.7222 | 0.060695 | 0.58879
|  | 5:23 | 9.7233 | 0.062016 | 0.58879
|  | 5:23 | 9.7244 | 0.063337 | 0.58879
|  | 5:23 | 9.7256 | 0.059152 | 0.58879
|  | 5:23 | 9.7267 | 0.049461 | 0.58878
|  | 5:23 | 9.7278 | 0.039771 | 0.58878
|  | 5:23 | 9.7289 | 0.03008 | 0.58878
|  | 5:23 | 9.73 | 0.02039 | 0.58878
|  | 5:23 | 9.7311 | 0.012533 | 0.58878
|  | 5:23 | 9.7322 | 0.00651 | 0.58877
|  | 5:23 | 9.7333 | 0.00048686 | 0.58877
|  | 5:23 | 9.7344 | -0.0055363 | 0.58877
|  | 5:24 | 9.7356 | -0.028667 | 0.58877
|  | 5:24 | 9.7367 | -0.055754 | 0.58876
|  | 5:24 | 9.7378 | -0.094714 | 0.58876
|  | 5:24 | 9.7389 | -0.13367 | 0.58876
|  | 5:24 | 9.74 | -0.1564 | 0.58876
|  | 5:24 | 9.7411 | -0.17912 | 0.58875
|  | 5:24 | 9.7422 | -0.20465 | 0.58875
|  | 5:24 | 9.7433 | -0.23296 | 0.58875
|  | 5:24 | 9.7444 | -0.26128 | 0.58875
|  | 5:24 | 9.7456 | -0.28713 | 0.58875
|  | 5:24 | 9.7467 | -0.31299 | 0.58874
|  | 5:24 | 9.7478 | -0.3269 | 0.58874
|  | 5:24 | 9.7489 | -0.32887 | 0.58874
|  | 5:24 | 9.75 | -0.33084 | 0.58874
|  | 5:24 | 9.7511 | -0.34417 | 0.58873
|  | 5:25 | 9.7522 | -0.35749 | 0.58873
|  | 5:25 | 9.7533 | -0.36829 | 0.58873
|  | 5:25 | 9.7544 | -0.37657 | 0.58873
|  | 5:25 | 9.7556 | -0.38484 | 0.58872
|  | 5:25 | 9.7567 | -0.39763 | 0.58872
|  | 5:25 | 9.7578 | -0.41043 | 0.58872
|  | 5:25 | 9.7589 | -0.42784 | 0.58872
|  | 5:25 | 9.76 | -0.44987 | 0.58872
|  | 5:25 | 9.7611 | -0.4719 | 0.58871
|  | 5:25 | 9.7622 | -0.49075 | 0.58871
|  | 5:25 | 9.7633 | -0.50959 | 0.58871
|  | 5:25 | 9.7644 | -0.5272 | 0.58871
|  | 5:25 | 9.7656 | -0.54355 | 0.5887
|  | 5:25 | 9.7667 | -0.5599 | 0.5887
|  | 5:25 | 9.7678 | -0.58263 | 0.5887
|  | 5:26 | 9.7689 | -0.60537 | 0.5887
|  | 5:26 | 9.77 | -0.62365 | 0.58869
|  | 5:26 | 9.7711 | -0.63747 | 0.58869
|  | 5:26 | 9.7722 | -0.65129 | 0.58869
|  | 5:26 | 9.7733 | -0.65879 | 0.58869
|  | 5:26 | 9.7744 | -0.66629 | 0.58869
|  | 5:26 | 9.7756 | -0.67986 | 0.58868
|  | 5:26 | 9.7767 | -0.6995 | 0.58868
|  | 5:26 | 9.7778 | -0.71913 | 0.58868
|  | 5:26 | 9.7789 | -0.73168 | 0.58868
|  | 5:26 | 9.78 | -0.74423 | 0.58867
|  | 5:26 | 9.7811 | -0.7505 | 0.58867
|  | 5:26 | 9.7822 | -0.75049 | 0.58867
|  | 5:26 | 9.7833 | -0.75048 | 0.58867
|  | 5:26 | 9.7844 | -0.73916 | 0.58866
|  | 5:27 | 9.7856 | -0.72783 | 0.58866
|  | 5:27 | 9.7867 | -0.70987 | 0.58866
|  | 5:27 | 9.7878 | -0.68526 | 0.58866
|  | 5:27 | 9.7889 | -0.66066 | 0.58866
|  | 5:27 | 9.79 | -0.6495 | 0.58865
|  | 5:27 | 9.7911 | -0.63834 | 0.58865
|  | 5:27 | 9.7922 | -0.61665 | 0.58865
|  | 5:27 | 9.7933 | -0.58443 | 0.58865
|  | 5:27 | 9.7944 | -0.55221 | 0.58864
|  | 5:27 | 9.7956 | -0.51541 | 0.58864
|  | 5:27 | 9.7967 | -0.47861 | 0.58864
|  | 5:27 | 9.7978 | -0.44523 | 0.58864
|  | 5:27 | 9.7989 | -0.41524 | 0.58863
|  | 5:27 | 9.8 | -0.38526 | 0.58863
|  | 5:27 | 9.8011 | -0.37899 | 0.58863
|  | 5:28 | 9.8022 | -0.37271 | 0.58863
|  | 5:28 | 9.8033 | -0.37159 | 0.58862
|  | 5:28 | 9.8044 | -0.37563 | 0.58862
|  | 5:28 | 9.8056 | -0.37966 | 0.58862
|  | 5:28 | 9.8067 | -0.36377 | 0.58862
|  | 5:28 | 9.8078 | -0.34788 | 0.58862
|  | 5:28 | 9.8089 | -0.32774 | 0.58861
|  | 5:28 | 9.81 | -0.30335 | 0.58861
|  | 5:28 | 9.8111 | -0.27896 | 0.58861
|  | 5:28 | 9.8122 | -0.25074 | 0.58861
|  | 5:28 | 9.8133 | -0.22252 | 0.5886
|  | 5:28 | 9.8144 | -0.19509 | 0.5886
|  | 5:28 | 9.8156 | -0.16792 | 0.5886
|  | 5:28 | 9.8167 | -0.14272 | 0.5886
|  | 5:28 | 9.8178 | -0.12345 | 0.58859
|  | 5:29 | 9.8189 | -0.10417 | 0.58859
|  | 5:29 | 9.82 | -0.087397 | 0.58859
|  | 5:29 | 9.8211 | -0.07313 | 0.58859
|  | 5:29 | 9.8222 | -0.058863 | 0.58859
|  | 5:29 | 9.8233 | -0.061269 | 0.58858
|  | 5:29 | 9.8244 | -0.063676 | 0.58858
|  | 5:29 | 9.8256 | -0.065522 | 0.58858
|  | 5:29 | 9.8267 | -0.066808 | 0.58858
|  | 5:29 | 9.8278 | -0.068094 | 0.58857
|  | 5:29 | 9.8289 | -0.075492 | 0.58857
|  | 5:29 | 9.83 | -0.08289 | 0.58857
|  | 5:29 | 9.8311 | -0.09073 | 0.58857
|  | 5:29 | 9.8322 | -0.099014 | 0.58856
|  | 5:29 | 9.8333 | -0.1073 | 0.58856
|  | 5:29 | 9.8344 | -0.089359 | 0.58856
|  | 5:30 | 9.8356 | -0.071421 | 0.58856
|  | 5:30 | 9.8367 | -0.049309 | 0.58856
|  | 5:30 | 9.8378 | -0.023023 | 0.58855
|  | 5:30 | 9.8389 | 0.0032623 | 0.58855
|  | 5:30 | 9.84 | 0.016532 | 0.58855
|  | 5:30 | 9.8411 | 0.029801 | 0.58855
|  | 5:30 | 9.8422 | 0.036497 | 0.58854
|  | 5:30 | 9.8433 | 0.03662 | 0.58854
|  | 5:30 | 9.8444 | 0.036742 | 0.58854
|  | 5:30 | 9.8456 | 0.031934 | 0.58854
|  | 5:30 | 9.8467 | 0.027126 | 0.58853
|  | 5:30 | 9.8478 | 0.038487 | 0.58853
|  | 5:30 | 9.8489 | 0.06602 | 0.58853
|  | 5:30 | 9.85 | 0.093552 | 0.58853
|  | 5:30 | 9.8511 | 0.12924 | 0.58853
|  | 5:31 | 9.8522 | 0.16492 | 0.58852
|  | 5:31 | 9.8533 | 0.19135 | 0.58852
|  | 5:31 | 9.8544 | 0.20853 | 0.58852
|  | 5:31 | 9.8556 | 0.2257 | 0.58852
|  | 5:31 | 9.8567 | 0.2251 | 0.58851
|  | 5:31 | 9.8578 | 0.22449 | 0.58851
|  | 5:31 | 9.8589 | 0.21902 | 0.58851
|  | 5:31 | 9.86 | 0.2087 | 0.58851
|  | 5:31 | 9.8611 | 0.19838 | 0.5885
|  | 5:31 | 9.8622 | 0.17104 | 0.5885
|  | 5:31 | 9.8633 | 0.14371 | 0.5885
|  | 5:31 | 9.8644 | 0.12041 | 0.5885
|  | 5:31 | 9.8656 | 0.10116 | 0.5885
|  | 5:31 | 9.8667 | 0.081902 | 0.58849
|  | 5:31 | 9.8678 | 0.099815 | 0.58849
|  | 5:32 | 9.8689 | 0.11773 | 0.58849
|  | 5:32 | 9.87 | 0.13342 | 0.58849
|  | 5:32 | 9.8711 | 0.14689 | 0.58848
|  | 5:32 | 9.8722 | 0.16036 | 0.58848
|  | 5:32 | 9.8733 | 0.17384 | 0.58848
|  | 5:32 | 9.8744 | 0.18731 | 0.58848
|  | 5:32 | 9.8756 | 0.20476 | 0.58847
|  | 5:32 | 9.8767 | 0.22619 | 0.58847
|  | 5:32 | 9.8778 | 0.24763 | 0.58847
|  | 5:32 | 9.8789 | 0.26643 | 0.58847
|  | 5:32 | 9.88 | 0.28523 | 0.58847
|  | 5:32 | 9.8811 | 0.29984 | 0.58846
|  | 5:32 | 9.8822 | 0.31025 | 0.58846
|  | 5:32 | 9.8833 | 0.32066 | 0.58846
|  | 5:32 | 9.8844 | 0.33434 | 0.58846
|  | 5:33 | 9.8856 | 0.34802 | 0.58845
|  | 5:33 | 9.8867 | 0.36502 | 0.58845
|  | 5:33 | 9.8878 | 0.38533 | 0.58845
|  | 5:33 | 9.8889 | 0.40565 | 0.58845
|  | 5:33 | 9.89 | 0.42159 | 0.58844
|  | 5:33 | 9.8911 | 0.43753 | 0.58844
|  | 5:33 | 9.8922 | 0.45058 | 0.58844
|  | 5:33 | 9.8933 | 0.46075 | 0.58844
|  | 5:33 | 9.8944 | 0.47091 | 0.58844
|  | 5:33 | 9.8956 | 0.47039 | 0.58843
|  | 5:33 | 9.8967 | 0.46987 | 0.58843
|  | 5:33 | 9.8978 | 0.46317 | 0.58843
|  | 5:33 | 9.8989 | 0.45441 | 0.58843
|  | 5:33 | 9.9 | 0.44565 | 0.58842
|  | 5:33 | 9.9011 | 0.42328 | 0.58842
|  | 5:34 | 9.9022 | 0.4009 | 0.58842
|  | 5:34 | 9.9033 | 0.38572 | 0.58842
|  | 5:34 | 9.9044 | 0.39211 | 0.58841
|  | 5:34 | 9.9056 | 0.3985 | 0.58841
|  | 5:34 | 9.9067 | 0.4237 | 0.58841
|  | 5:34 | 9.9078 | 0.4489 | 0.58841
|  | 5:34 | 9.9089 | 0.46088 | 0.58841
|  | 5:34 | 9.91 | 0.45964 | 0.5884
|  | 5:34 | 9.9111 | 0.45841 | 0.5884
|  | 5:34 | 9.9122 | 0.4475 | 0.5884
|  | 5:34 | 9.9133 | 0.43659 | 0.5884
|  | 5:34 | 9.9144 | 0.42325 | 0.58839
|  | 5:34 | 9.9156 | 0.40749 | 0.58839
|  | 5:34 | 9.9167 | 0.39172 | 0.58839
|  | 5:34 | 9.9178 | 0.40531 | 0.58839
|  | 5:35 | 9.9189 | 0.4189 | 0.58838
|  | 5:35 | 9.92 | 0.43151 | 0.58838
|  | 5:35 | 9.9211 | 0.44314 | 0.58838
|  | 5:35 | 9.9222 | 0.45477 | 0.58838
|  | 5:35 | 9.9233 | 0.4521 | 0.58837
|  | 5:35 | 9.9244 | 0.44943 | 0.58837
|  | 5:35 | 9.9256 | 0.43991 | 0.58837
|  | 5:35 | 9.9267 | 0.42354 | 0.58837
|  | 5:35 | 9.9278 | 0.40717 | 0.58837
|  | 5:35 | 9.9289 | 0.40518 | 0.58836
|  | 5:35 | 9.93 | 0.40319 | 0.58836
|  | 5:35 | 9.9311 | 0.41374 | 0.58836
|  | 5:35 | 9.9322 | 0.43682 | 0.58836
|  | 5:35 | 9.9333 | 0.45991 | 0.58835
|  | 5:35 | 9.9344 | 0.48429 | 0.58835
|  | 5:36 | 9.9356 | 0.50867 | 0.58835
|  | 5:36 | 9.9367 | 0.52763 | 0.58835
|  | 5:36 | 9.9378 | 0.54478 | 0.58834
|  | 5:36 | 9.9389 | 0.56194 | 0.58834
|  | 5:36 | 9.94 | 0.57207 | 0.58834
|  | 5:36 | 9.9411 | 0.58221 | 0.58834
|  | 5:36 | 9.9422 | 0.58718 | 0.58834
|  | 5:36 | 9.9433 | 0.58698 | 0.58833
|  | 5:36 | 9.9444 | 0.58678 | 0.58833
|  | 5:36 | 9.9456 | 0.60128 | 0.58833
|  | 5:36 | 9.9467 | 0.61578 | 0.58833
|  | 5:36 | 9.9478 | 0.62143 | 0.58832
|  | 5:36 | 9.9489 | 0.61825 | 0.58832
|  | 5:36 | 9.95 | 0.61506 | 0.58832
|  | 5:36 | 9.9511 | 0.62239 | 0.58832
|  | 5:37 | 9.9522 | 0.62971 | 0.58831
|  | 5:37 | 9.9533 | 0.63355 | 0.58831
|  | 5:37 | 9.9544 | 0.6339 | 0.58831
|  | 5:37 | 9.9556 | 0.63907 | 0.58831
|  | 5:37 | 9.9567 | 0.65868 | 0.58831
|  | 5:37 | 9.9578 | 0.6783 | 0.5883
|  | 5:37 | 9.9589 | 0.69792 | 0.5883
|  | 5:37 | 9.96 | 0.71754 | 0.5883
|  | 5:37 | 9.9611 | 0.73715 | 0.5883
|  | 5:37 | 9.9622 | 0.75945 | 0.58829
|  | 5:37 | 9.9633 | 0.78175 | 0.58829
|  | 5:37 | 9.9644 | 0.79371 | 0.58829
|  | 5:37 | 9.9656 | 0.79532 | 0.58829
|  | 5:37 | 9.9667 | 0.79693 | 0.58828
|  | 5:37 | 9.9678 | 0.81251 | 0.58828
|  | 5:38 | 9.9689 | 0.82809 | 0.58828
|  | 5:38 | 9.97 | 0.83863 | 0.58828
|  | 5:38 | 9.9711 | 0.84413 | 0.58828
|  | 5:38 | 9.9722 | 0.84963 | 0.58827
|  | 5:38 | 9.9733 | 0.82497 | 0.58827
|  | 5:38 | 9.9744 | 0.8003 | 0.58827
|  | 5:38 | 9.9756 | 0.77953 | 0.58827
|  | 5:38 | 9.9767 | 0.76265 | 0.58826
|  | 5:38 | 9.9778 | 0.74578 | 0.58826
|  | 5:38 | 9.9789 | 0.7289 | 0.58826
|  | 5:38 | 9.98 | 0.71203 | 0.58826
|  | 5:38 | 9.9811 | 0.69599 | 0.58825
|  | 5:38 | 9.9822 | 0.68079 | 0.58825
|  | 5:38 | 9.9833 | 0.66559 | 0.58825
|  | 5:38 | 9.9844 | 0.65039 | 0.58825
|  | 5:39 | 9.9856 | 0.63519 | 0.58825
|  | 5:39 | 9.9867 | 0.6287 | 0.58824
|  | 5:39 | 9.9878 | 0.62511 | 0.58824
|  | 5:39 | 9.9889 | 0.62152 | 0.58824
|  | 5:39 | 9.99 | 0.60905 | 0.58824
|  | 5:39 | 9.9911 | 0.59658 | 0.58823
|  | 5:39 | 9.9922 | 0.59451 | 0.58823
|  | 5:39 | 9.9933 | 0.60285 | 0.58823
|  | 5:39 | 9.9944 | 0.61119 | 0.58823
|  | 5:39 | 9.9956 | 0.62747 | 0.58822
|  | 5:39 | 9.9967 | 0.64374 | 0.58822
|  | 5:39 | 9.9978 | 0.64699 | 0.58822
|  | 5:39 | 9.9989 | 0.6372 | 0.58822
|  | 5:39 | 10 | 0.62494 | 0.58822
|  | 5:39 | 10.0011 | 0.60529 | 0.58821
|  | 5:40 | 10.0022 | 0.58564 | 0.58821
|  | 5:40 | 10.0033 | 0.56408 | 0.58821
|  | 5:40 | 10.0044 | 0.54061 | 0.58821
|  | 5:40 | 10.0056 | 0.51713 | 0.5882
|  | 5:40 | 10.0067 | 0.50205 | 0.5882
|  | 5:40 | 10.0078 | 0.48696 | 0.5882
|  | 5:40 | 10.0089 | 0.46771 | 0.5882
|  | 5:40 | 10.01 | 0.4443 | 0.58819
|  | 5:40 | 10.0111 | 0.4209 | 0.58819
|  | 5:40 | 10.0122 | 0.38558 | 0.58819
|  | 5:40 | 10.0133 | 0.35026 | 0.58819
|  | 5:40 | 10.0144 | 0.31233 | 0.58819
|  | 5:40 | 10.0156 | 0.27179 | 0.58818
|  | 5:40 | 10.0167 | 0.23124 | 0.58818
|  | 5:40 | 10.0178 | 0.20065 | 0.58818
|  | 5:41 | 10.0189 | 0.17005 | 0.58818
|  | 5:41 | 10.02 | 0.14077 | 0.58817
|  | 5:41 | 10.0211 | 0.11281 | 0.58817
|  | 5:41 | 10.0222 | 0.084842 | 0.58817
|  | 5:41 | 10.0233 | 0.038603 | 0.58817
|  | 5:41 | 10.0244 | -0.0076366 | 0.58816
|  | 5:41 | 10.0256 | -0.047739 | 0.58816
|  | 5:41 | 10.0267 | -0.081703 | 0.58816
|  | 5:41 | 10.0278 | -0.11567 | 0.58816
|  | 5:41 | 10.0289 | -0.13646 | 0.58816
|  | 5:41 | 10.03 | -0.15725 | 0.58815
|  | 5:41 | 10.0311 | -0.18325 | 0.58815
|  | 5:41 | 10.0322 | -0.21444 | 0.58815
|  | 5:41 | 10.0333 | -0.24563 | 0.58815
|  | 5:41 | 10.0344 | -0.2745 | 0.58814
|  | 5:42 | 10.0356 | -0.30336 | 0.58814
|  | 5:42 | 10.0367 | -0.34175 | 0.58814
|  | 5:42 | 10.0378 | -0.38967 | 0.58814
|  | 5:42 | 10.0389 | -0.42638 | 0.58813
|  | 5:42 | 10.04 | -0.42948 | 0.58813
|  | 5:42 | 10.0411 | -0.43258 | 0.58813
|  | 5:42 | 10.0422 | -0.44921 | 0.58813
|  | 5:42 | 10.0433 | -0.47935 | 0.58812
|  | 5:42 | 10.0444 | -0.5095 | 0.58812
|  | 5:42 | 10.0456 | -0.53188 | 0.58812
|  | 5:42 | 10.0467 | -0.55427 | 0.58812
|  | 5:42 | 10.0478 | -0.57911 | 0.58812
|  | 5:42 | 10.0489 | -0.60641 | 0.58811
|  | 5:42 | 10.05 | -0.63371 | 0.58811
|  | 5:42 | 10.0511 | -0.64927 | 0.58811
|  | 5:43 | 10.0522 | -0.66484 | 0.58811
|  | 5:43 | 10.0533 | -0.6804 | 0.5881
|  | 5:43 | 10.0544 | -0.69596 | 0.5881
|  | 5:43 | 10.0556 | -0.71153 | 0.5881
|  | 5:43 | 10.0567 | -0.72418 | 0.5881
|  | 5:43 | 10.0578 | -0.73684 | 0.58809
|  | 5:43 | 10.0589 | -0.73522 | 0.58809
|  | 5:43 | 10.06 | -0.71932 | 0.58809
|  | 5:43 | 10.0611 | -0.70341 | 0.58809
|  | 5:43 | 10.0622 | -0.67074 | 0.58809
|  | 5:43 | 10.0633 | -0.63806 | 0.58808
|  | 5:43 | 10.0644 | -0.60994 | 0.58808
|  | 5:43 | 10.0656 | -0.58635 | 0.58808
|  | 5:43 | 10.0667 | -0.56277 | 0.58808
|  | 5:43 | 10.0678 | -0.53527 | 0.58807
|  | 5:44 | 10.0689 | -0.50776 | 0.58807
|  | 5:44 | 10.07 | -0.48763 | 0.58807
|  | 5:44 | 10.0711 | -0.48964 | 0.58807
|  | 5:44 | 10.0722 | -0.49165 | 0.58806
|  | 5:44 | 10.0733 | -0.49001 | 0.58806
|  | 5:44 | 10.0744 | -0.48837 | 0.58806
|  | 5:44 | 10.0756 | -0.48899 | 0.58806
|  | 5:44 | 10.0767 | -0.49188 | 0.58806
|  | 5:44 | 10.0778 | -0.49352 | 0.58805
|  | 5:44 | 10.0789 | -0.49142 | 0.58805
|  | 5:44 | 10.08 | -0.48932 | 0.58805
|  | 5:44 | 10.0811 | -0.49175 | 0.58805
|  | 5:44 | 10.0822 | -0.4987 | 0.58804
|  | 5:44 | 10.0833 | -0.50565 | 0.58804
|  | 5:44 | 10.0844 | -0.50288 | 0.58804
|  | 5:45 | 10.0856 | -0.50011 | 0.58804
|  | 5:45 | 10.0867 | -0.48826 | 0.58803
|  | 5:45 | 10.0878 | -0.46731 | 0.58803
|  | 5:45 | 10.0889 | -0.44636 | 0.58803
|  | 5:45 | 10.09 | -0.413 | 0.58803
|  | 5:45 | 10.0911 | -0.37965 | 0.58803
|  | 5:45 | 10.0922 | -0.35026 | 0.58802
|  | 5:45 | 10.0933 | -0.32485 | 0.58802
|  | 5:45 | 10.0944 | -0.29944 | 0.58802
|  | 5:45 | 10.0956 | -0.27642 | 0.58802
|  | 5:45 | 10.0967 | -0.2534 | 0.58801
|  | 5:45 | 10.0978 | -0.236 | 0.58801
|  | 5:45 | 10.0989 | -0.22421 | 0.58801
|  | 5:45 | 10.1 | -0.21242 | 0.58801
|  | 5:45 | 10.1011 | -0.18995 | 0.588
|  | 5:46 | 10.1022 | -0.16749 | 0.588
|  | 5:46 | 10.1033 | -0.14283 | 0.588
|  | 5:46 | 10.1044 | -0.11597 | 0.588
|  | 5:46 | 10.1056 | -0.089118 | 0.588
|  | 5:46 | 10.1067 | -0.051508 | 0.58799
|  | 5:46 | 10.1078 | -0.013898 | 0.58799
|  | 5:46 | 10.1089 | 0.024607 | 0.58799
|  | 5:46 | 10.11 | 0.064006 | 0.58799
|  | 5:46 | 10.1111 | 0.1034 | 0.58798
|  | 5:46 | 10.1122 | 0.12872 | 0.58798
|  | 5:46 | 10.1133 | 0.15403 | 0.58798
|  | 5:46 | 10.1144 | 0.16833 | 0.58798
|  | 5:46 | 10.1156 | 0.17161 | 0.58797
|  | 5:46 | 10.1167 | 0.1749 | 0.58797
|  | 5:46 | 10.1178 | 0.19225 | 0.58797
|  | 5:47 | 10.1189 | 0.2096 | 0.58797
|  | 5:47 | 10.12 | 0.23125 | 0.58797
|  | 5:47 | 10.1211 | 0.25433 | 0.58796
|  | 5:47 | 10.1222 | 0.28118 | 0.58796
|  | 5:47 | 10.1233 | 0.3193 | 0.58796
|  | 5:47 | 10.1244 | 0.35742 | 0.58796
|  | 5:47 | 10.1256 | 0.37481 | 0.58795
|  | 5:47 | 10.1267 | 0.37146 | 0.58795
|  | 5:47 | 10.1278 | 0.36812 | 0.58795
|  | 5:47 | 10.1289 | 0.36814 | 0.58795
|  | 5:47 | 10.13 | 0.36817 | 0.58794
|  | 5:47 | 10.1311 | 0.36493 | 0.58794
|  | 5:47 | 10.1322 | 0.35842 | 0.58794
|  | 5:47 | 10.1333 | 0.35192 | 0.58794
|  | 5:47 | 10.1344 | 0.35745 | 0.58794
|  | 5:48 | 10.1356 | 0.36298 | 0.58793
|  | 5:48 | 10.1367 | 0.38439 | 0.58793
|  | 5:48 | 10.1378 | 0.42166 | 0.58793
|  | 5:48 | 10.1389 | 0.45893 | 0.58793
|  | 5:48 | 10.14 | 0.50834 | 0.58792
|  | 5:48 | 10.1411 | 0.55774 | 0.58792
|  | 5:48 | 10.1422 | 0.59714 | 0.58792
|  | 5:48 | 10.1433 | 0.62655 | 0.58792
|  | 5:48 | 10.1444 | 0.65595 | 0.58791
|  | 5:48 | 10.1456 | 0.68535 | 0.58791
|  | 5:48 | 10.1467 | 0.71475 | 0.58791
|  | 5:48 | 10.1478 | 0.7405 | 0.58791
|  | 5:48 | 10.1489 | 0.7626 | 0.58791
|  | 5:48 | 10.15 | 0.7847 | 0.5879
|  | 5:48 | 10.1511 | 0.78996 | 0.5879
|  | 5:49 | 10.1522 | 0.79522 | 0.5879
|  | 5:49 | 10.1533 | 0.80048 | 0.5879
|  | 5:49 | 10.1544 | 0.80574 | 0.58789
|  | 5:49 | 10.1556 | 0.811 | 0.58789
|  | 5:49 | 10.1567 | 0.80302 | 0.58789
|  | 5:49 | 10.1578 | 0.79504 | 0.58789
|  | 5:49 | 10.1589 | 0.78335 | 0.58788
|  | 5:49 | 10.16 | 0.76794 | 0.58788
|  | 5:49 | 10.1611 | 0.75254 | 0.58788
|  | 5:49 | 10.1622 | 0.73713 | 0.58788
|  | 5:49 | 10.1633 | 0.72173 | 0.58787
|  | 5:49 | 10.1644 | 0.70357 | 0.58787
|  | 5:49 | 10.1656 | 0.68266 | 0.58787
|  | 5:49 | 10.1667 | 0.66175 | 0.58787
|  | 5:49 | 10.1678 | 0.62242 | 0.58787
|  | 5:50 | 10.1689 | 0.58309 | 0.58786
|  | 5:50 | 10.17 | 0.54171 | 0.58786
|  | 5:50 | 10.1711 | 0.49829 | 0.58786
|  | 5:50 | 10.1722 | 0.45486 | 0.58786
|  | 5:50 | 10.1733 | 0.42925 | 0.58785
|  | 5:50 | 10.1744 | 0.40363 | 0.58785
|  | 5:50 | 10.1756 | 0.37379 | 0.58785
|  | 5:50 | 10.1767 | 0.33971 | 0.58785
|  | 5:50 | 10.1778 | 0.30564 | 0.58784
|  | 5:50 | 10.1789 | 0.27379 | 0.58784
|  | 5:50 | 10.18 | 0.24194 | 0.58784
|  | 5:50 | 10.1811 | 0.22435 | 0.58784
|  | 5:50 | 10.1822 | 0.22102 | 0.58784
|  | 5:50 | 10.1833 | 0.21769 | 0.58783
|  | 5:50 | 10.1844 | 0.20566 | 0.58783
|  | 5:51 | 10.1856 | 0.19362 | 0.58783
|  | 5:51 | 10.1867 | 0.18466 | 0.58783
|  | 5:51 | 10.1878 | 0.17879 | 0.58782
|  | 5:51 | 10.1889 | 0.17291 | 0.58782
|  | 5:51 | 10.19 | 0.16918 | 0.58782
|  | 5:51 | 10.1911 | 0.16545 | 0.58782
|  | 5:51 | 10.1922 | 0.15742 | 0.58781
|  | 5:51 | 10.1933 | 0.14511 | 0.58781
|  | 5:51 | 10.1944 | 0.13279 | 0.58781
|  | 5:51 | 10.1956 | 0.11944 | 0.58781
|  | 5:51 | 10.1967 | 0.10609 | 0.58781
|  | 5:51 | 10.1978 | 0.093734 | 0.5878
|  | 5:51 | 10.1989 | 0.082374 | 0.5878
|  | 5:51 | 10.2 | 0.071013 | 0.5878
|  | 5:51 | 10.2011 | 0.066403 | 0.5878
|  | 5:52 | 10.2022 | 0.061792 | 0.58779
|  | 5:52 | 10.2033 | 0.057755 | 0.58779
|  | 5:52 | 10.2044 | 0.05429 | 0.58779
|  | 5:52 | 10.2056 | 0.050825 | 0.58779
|  | 5:52 | 10.2067 | 0.032276 | 0.58778
|  | 5:52 | 10.2078 | 0.013726 | 0.58778
|  | 5:52 | 10.2089 | -0.0155 | 0.58778
|  | 5:52 | 10.21 | -0.055402 | 0.58778
|  | 5:52 | 10.2111 | -0.095305 | 0.58778
|  | 5:52 | 10.2122 | -0.1476 | 0.58777
|  | 5:52 | 10.2133 | -0.19989 | 0.58777
|  | 5:52 | 10.2144 | -0.25319 | 0.58777
|  | 5:52 | 10.2156 | -0.30752 | 0.58777
|  | 5:52 | 10.2167 | -0.36184 | 0.58776
|  | 5:52 | 10.2178 | -0.40614 | 0.58776
|  | 5:53 | 10.2189 | -0.45044 | 0.58776
|  | 5:53 | 10.22 | -0.48112 | 0.58776
|  | 5:53 | 10.2211 | -0.49819 | 0.58775
|  | 5:53 | 10.2222 | -0.51526 | 0.58775
|  | 5:53 | 10.2233 | -0.54146 | 0.58775
|  | 5:53 | 10.2244 | -0.56767 | 0.58775
|  | 5:53 | 10.2256 | -0.58665 | 0.58775
|  | 5:53 | 10.2267 | -0.59843 | 0.58774
|  | 5:53 | 10.2278 | -0.6102 | 0.58774
|  | 5:53 | 10.2289 | -0.60745 | 0.58774
|  | 5:53 | 10.23 | -0.6047 | 0.58774
|  | 5:53 | 10.2311 | -0.60347 | 0.58773
|  | 5:53 | 10.2322 | -0.60376 | 0.58773
|  | 5:53 | 10.2333 | -0.60405 | 0.58773
|  | 5:53 | 10.2344 | -0.60336 | 0.58773
|  | 5:54 | 10.2356 | -0.60266 | 0.58772
|  | 5:54 | 10.2367 | -0.60291 | 0.58772
|  | 5:54 | 10.2378 | -0.60599 | 0.58772
|  | 5:54 | 10.2389 | -0.60906 | 0.58772
|  | 5:54 | 10.24 | -0.61077 | 0.58772
|  | 5:54 | 10.2411 | -0.61248 | 0.58771
|  | 5:54 | 10.2422 | -0.6045 | 0.58771
|  | 5:54 | 10.2433 | -0.58685 | 0.58771
|  | 5:54 | 10.2444 | -0.56919 | 0.58771
|  | 5:54 | 10.2456 | -0.55636 | 0.5877
|  | 5:54 | 10.2467 | -0.54352 | 0.5877
|  | 5:54 | 10.2478 | -0.53564 | 0.5877
|  | 5:54 | 10.2489 | -0.53272 | 0.5877
|  | 5:54 | 10.25 | -0.5298 | 0.58769
|  | 5:54 | 10.2511 | -0.529 | 0.58769
|  | 5:55 | 10.2522 | -0.52819 | 0.58769
|  | 5:55 | 10.2533 | -0.53152 | 0.58769
|  | 5:55 | 10.2544 | -0.539 | 0.58769
|  | 5:55 | 10.2556 | -0.54647 | 0.58768
|  | 5:55 | 10.2567 | -0.54635 | 0.58768
|  | 5:55 | 10.2578 | -0.54623 | 0.58768
|  | 5:55 | 10.2589 | -0.54252 | 0.58768
|  | 5:55 | 10.26 | -0.53522 | 0.58767
|  | 5:55 | 10.2611 | -0.52791 | 0.58767
|  | 5:55 | 10.2622 | -0.51653 | 0.58767
|  | 5:55 | 10.2633 | -0.50516 | 0.58767
|  | 5:55 | 10.2644 | -0.47674 | 0.58766
|  | 5:55 | 10.2656 | -0.43128 | 0.58766
|  | 5:55 | 10.2667 | -0.38582 | 0.58766
|  | 5:55 | 10.2678 | -0.34134 | 0.58766
|  | 5:56 | 10.2689 | -0.29686 | 0.58766
|  | 5:56 | 10.27 | -0.25636 | 0.58765
|  | 5:56 | 10.2711 | -0.21982 | 0.58765
|  | 5:56 | 10.2722 | -0.18329 | 0.58765
|  | 5:56 | 10.2733 | -0.16697 | 0.58765
|  | 5:56 | 10.2744 | -0.15066 | 0.58764
|  | 5:56 | 10.2756 | -0.13059 | 0.58764
|  | 5:56 | 10.2767 | -0.10676 | 0.58764
|  | 5:56 | 10.2778 | -0.082929 | 0.58764
|  | 5:56 | 10.2789 | -0.064992 | 0.58763
|  | 5:56 | 10.28 | -0.047054 | 0.58763
|  | 5:56 | 10.2811 | -0.033677 | 0.58763
|  | 5:56 | 10.2822 | -0.024861 | 0.58763
|  | 5:56 | 10.2833 | -0.016045 | 0.58762
|  | 5:56 | 10.2844 | -0.015577 | 0.58762
|  | 5:57 | 10.2856 | -0.01511 | 0.58762
|  | 5:57 | 10.2867 | -0.032247 | 0.58762
|  | 5:57 | 10.2878 | -0.066986 | 0.58762
|  | 5:57 | 10.2889 | -0.10173 | 0.58761
|  | 5:57 | 10.29 | -0.11422 | 0.58761
|  | 5:57 | 10.2911 | -0.12672 | 0.58761
|  | 5:57 | 10.2922 | -0.14071 | 0.58761
|  | 5:57 | 10.2933 | -0.15619 | 0.5876
|  | 5:57 | 10.2944 | -0.17167 | 0.5876
|  | 5:57 | 10.2956 | -0.18715 | 0.5876
|  | 5:57 | 10.2967 | -0.20263 | 0.5876
|  | 5:57 | 10.2978 | -0.22463 | 0.58759
|  | 5:57 | 10.2989 | -0.25316 | 0.58759
|  | 5:57 | 10.3 | -0.28168 | 0.58759
|  | 5:57 | 10.3011 | -0.29777 | 0.58759
|  | 5:58 | 10.3022 | -0.31386 | 0.58759
|  | 5:58 | 10.3033 | -0.31394 | 0.58758
|  | 5:58 | 10.3044 | -0.298 | 0.58758
|  | 5:58 | 10.3056 | -0.28207 | 0.58758
|  | 5:58 | 10.3067 | -0.26097 | 0.58758
|  | 5:58 | 10.3078 | -0.23987 | 0.58757
|  | 5:58 | 10.3089 | -0.2201 | 0.58757
|  | 5:58 | 10.31 | -0.20168 | 0.58757
|  | 5:58 | 10.3111 | -0.18325 | 0.58757
|  | 5:58 | 10.3122 | -0.16685 | 0.58756
|  | 5:58 | 10.3133 | -0.15045 | 0.58756
|  | 5:58 | 10.3144 | -0.13497 | 0.58756
|  | 5:58 | 10.3156 | -0.1204 | 0.58756
|  | 5:58 | 10.3167 | -0.10583 | 0.58756
|  | 5:58 | 10.3178 | -0.085856 | 0.58755
|  | 5:59 | 10.3189 | -0.065882 | 0.58755
|  | 5:59 | 10.32 | -0.057483 | 0.58755
|  | 5:59 | 10.3211 | -0.060658 | 0.58755
|  | 5:59 | 10.3222 | -0.063833 | 0.58754
|  | 5:59 | 10.3233 | -0.042603 | 0.58754
|  | 5:59 | 10.3244 | -0.021374 | 0.58754
|  | 5:59 | 10.3256 | -0.0021204 | 0.58754
|  | 5:59 | 10.3267 | 0.015157 | 0.58753
|  | 5:59 | 10.3278 | 0.032435 | 0.58753
|  | 5:59 | 10.3289 | 0.024561 | 0.58753
|  | 5:59 | 10.33 | 0.016687 | 0.58753
|  | 5:59 | 10.3311 | 0.012389 | 0.58753
|  | 5:59 | 10.3322 | 0.011665 | 0.58752
|  | 5:59 | 10.3333 | 0.010942 | 0.58752
|  | 5:59 | 10.3344 | 0.002515 | 0.58752
|  | 6:00 | 10.3356 | -0.0059115 | 0.58752
|  | 6:00 | 10.3367 | -0.026255 | 0.58751
|  | 6:00 | 10.3378 | -0.058516 | 0.58751
|  | 6:00 | 10.3389 | -0.090777 | 0.58751
|  | 6:00 | 10.34 | -0.1219 | 0.58751
|  | 6:00 | 10.3411 | -0.15302 | 0.5875
|  | 6:00 | 10.3422 | -0.18289 | 0.5875
|  | 6:00 | 10.3433 | -0.2827 | 0.5875
|  | 6:00 | 10.3444 | -0.27395 | 0.5875
|  | 6:00 | 10.3456 | -0.26521 | 0.5875
|  | 6:00 | 10.3467 | -0.25647 | 0.58749
|  | 6:00 | 10.3478 | -0.24772 | 0.58749
|  | 6:00 | 10.3489 | -0.23835 | 0.58749
|  | 6:00 | 10.35 | -0.22836 | 0.58749
|  | 6:00 | 10.3511 | -0.21836 | 0.58748
|  | 6:01 | 10.3522 | -0.20836 | 0.58748
|  | 6:01 | 10.3533 | -0.19837 | 0.58748
|  | 6:01 | 10.3544 | -0.18873 | 0.58748
|  | 6:01 | 10.3556 | -0.17945 | 0.58747
|  | 6:01 | 10.3567 | -0.17017 | 0.58747
|  | 6:01 | 10.3578 | -0.16491 | 0.58747
|  | 6:01 | 10.3589 | -0.15964 | 0.58747
|  | 6:01 | 10.36 | -0.13943 | 0.58747
|  | 6:01 | 10.3611 | -0.1043 | 0.58746
|  | 6:01 | 10.3622 | -0.069166 | 0.58746
|  | 6:01 | 10.3633 | -0.025458 | 0.58746
|  | 6:01 | 10.3644 | 0.018251 | 0.58746
|  | 6:01 | 10.3656 | 0.050382 | 0.58745
|  | 6:01 | 10.3667 | 0.070937 | 0.58745
|  | 6:01 | 10.3678 | 0.091492 | 0.58745
|  | 6:02 | 10.3689 | 0.096229 | 0.58745
|  | 6:02 | 10.37 | 0.10097 | 0.58744
|  | 6:02 | 10.3711 | 0.10124 | 0.58744
|  | 6:02 | 10.3722 | 0.097046 | 0.58744
|  | 6:02 | 10.3733 | 0.092854 | 0.58744
|  | 6:02 | 10.3744 | 0.087061 | 0.58744
|  | 6:02 | 10.3756 | 0.081269 | 0.58743
|  | 6:02 | 10.3767 | 0.07728 | 0.58743
|  | 6:02 | 10.3778 | 0.075093 | 0.58743
|  | 6:02 | 10.3789 | 0.072907 | 0.58743
|  | 6:02 | 10.38 | 0.071547 | 0.58742
|  | 6:02 | 10.3811 | 0.070188 | 0.58742
|  | 6:02 | 10.3822 | 0.065275 | 0.58742
|  | 6:02 | 10.3833 | 0.05681 | 0.58742
|  | 6:02 | 10.3844 | 0.048345 | 0.58741
|  | 6:03 | 10.3856 | 0.04501 | 0.58741
|  | 6:03 | 10.3867 | 0.041676 | 0.58741
|  | 6:03 | 10.3878 | 0.041155 | 0.58741
|  | 6:03 | 10.3889 | 0.043449 | 0.58741
|  | 6:03 | 10.39 | 0.045743 | 0.5874
|  | 6:03 | 10.3911 | 0.053399 | 0.5874
|  | 6:03 | 10.3922 | 0.061055 | 0.5874
|  | 6:03 | 10.3933 | 0.07047 | 0.5874
|  | 6:03 | 10.3944 | 0.081644 | 0.58739
|  | 6:03 | 10.3956 | 0.092819 | 0.58739
|  | 6:03 | 10.3967 | 0.10541 | 0.58739
|  | 6:03 | 10.3978 | 0.11801 | 0.58739
|  | 6:03 | 10.3989 | 0.12946 | 0.58738
|  | 6:03 | 10.4 | 0.13978 | 0.58738
|  | 6:03 | 10.4011 | 0.15009 | 0.58738
|  | 6:04 | 10.4022 | 0.1558 | 0.58738
|  | 6:04 | 10.4033 | 0.1615 | 0.58737
|  | 6:04 | 10.4044 | 0.16624 | 0.58737
|  | 6:04 | 10.4056 | 0.17002 | 0.58737
|  | 6:04 | 10.4067 | 0.17379 | 0.58737
|  | 6:04 | 10.4078 | 0.25959 | 0.58737
|  | 6:04 | 10.4089 | 0.34539 | 0.58736
|  | 6:04 | 10.41 | 0.40906 | 0.58736
|  | 6:04 | 10.4111 | 0.45059 | 0.58736
|  | 6:04 | 10.4122 | 0.49213 | 0.58736
|  | 6:04 | 10.4133 | 0.4921 | 0.58735
|  | 6:04 | 10.4144 | 0.49208 | 0.58735
|  | 6:04 | 10.4156 | 0.49019 | 0.58735
|  | 6:04 | 10.4167 | 0.48643 | 0.58735
|  | 6:04 | 10.4178 | 0.48266 | 0.58734
|  | 6:05 | 10.4189 | 0.48082 | 0.58734
|  | 6:05 | 10.42 | 0.47897 | 0.58734
|  | 6:05 | 10.4211 | 0.48042 | 0.58734
|  | 6:05 | 10.4222 | 0.48518 | 0.58734
|  | 6:05 | 10.4233 | 0.48994 | 0.58733
|  | 6:05 | 10.4244 | 0.50082 | 0.58733
|  | 6:05 | 10.4256 | 0.5117 | 0.58733
|  | 6:05 | 10.4267 | 0.52447 | 0.58733
|  | 6:05 | 10.4278 | 0.53912 | 0.58732
|  | 6:05 | 10.4289 | 0.55378 | 0.58732
|  | 6:05 | 10.43 | 0.57058 | 0.58732
|  | 6:05 | 10.4311 | 0.58739 | 0.58732
|  | 6:05 | 10.4322 | 0.60419 | 0.58731
|  | 6:05 | 10.4333 | 0.621 | 0.58731
|  | 6:05 | 10.4344 | 0.63694 | 0.58731
|  | 6:06 | 10.4356 | 0.65031 | 0.58731
|  | 6:06 | 10.4367 | 0.66367 | 0.58731
|  | 6:06 | 10.4378 | 0.67734 | 0.5873
|  | 6:06 | 10.4389 | 0.69131 | 0.5873
|  | 6:06 | 10.44 | 0.70529 | 0.5873
|  | 6:06 | 10.4411 | 0.71926 | 0.5873
|  | 6:06 | 10.4422 | 0.73323 | 0.58729
|  | 6:06 | 10.4433 | 0.74576 | 0.58729
|  | 6:06 | 10.4444 | 0.75683 | 0.58729
|  | 6:06 | 10.4456 | 0.7679 | 0.58729
|  | 6:06 | 10.4467 | 0.77035 | 0.58728
|  | 6:06 | 10.4478 | 0.7728 | 0.58728
|  | 6:06 | 10.4489 | 0.77179 | 0.58728
|  | 6:06 | 10.45 | 0.76733 | 0.58728
|  | 6:06 | 10.4511 | 0.76286 | 0.58728
|  | 6:07 | 10.4522 | 0.75839 | 0.58727
|  | 6:07 | 10.4533 | 0.75393 | 0.58727
|  | 6:07 | 10.4544 | 0.74992 | 0.58727
|  | 6:07 | 10.4556 | 0.74636 | 0.58727
|  | 6:07 | 10.4567 | 0.74281 | 0.58726
|  | 6:07 | 10.4578 | 0.77247 | 0.58726
|  | 6:07 | 10.4589 | 0.80213 | 0.58726
|  | 6:07 | 10.46 | 0.80874 | 0.58726
|  | 6:07 | 10.4611 | 0.79229 | 0.58725
|  | 6:07 | 10.4622 | 0.77585 | 0.58725
|  | 6:07 | 10.4633 | 0.77601 | 0.58725
|  | 6:07 | 10.4644 | 0.77617 | 0.58725
|  | 6:07 | 10.4656 | 0.7786 | 0.58725
|  | 6:07 | 10.4667 | 0.78332 | 0.58724
|  | 6:07 | 10.4678 | 0.78803 | 0.58724
|  | 6:08 | 10.4689 | 0.79275 | 0.58724
|  | 6:08 | 10.47 | 0.79747 | 0.58724
|  | 6:08 | 10.4711 | 0.80064 | 0.58723
|  | 6:08 | 10.4722 | 0.80226 | 0.58723
|  | 6:08 | 10.4733 | 0.80389 | 0.58723
|  | 6:08 | 10.4744 | 0.80251 | 0.58723
|  | 6:08 | 10.4756 | 0.80114 | 0.58722
|  | 6:08 | 10.4767 | 0.79676 | 0.58722
|  | 6:08 | 10.4778 | 0.78937 | 0.58722
|  | 6:08 | 10.4789 | 0.78199 | 0.58722
|  | 6:08 | 10.48 | 0.76838 | 0.58722
|  | 6:08 | 10.4811 | 0.75477 | 0.58721
|  | 6:08 | 10.4822 | 0.7376 | 0.58721
|  | 6:08 | 10.4833 | 0.71685 | 0.58721
|  | 6:08 | 10.4844 | 0.69611 | 0.58721
|  | 6:09 | 10.4856 | 0.67314 | 0.5872
|  | 6:09 | 10.4867 | 0.65017 | 0.5872
|  | 6:09 | 10.4878 | 0.62532 | 0.5872
|  | 6:09 | 10.4889 | 0.59857 | 0.5872
|  | 6:09 | 10.49 | 0.57182 | 0.58719
|  | 6:09 | 10.4911 | 0.54024 | 0.58719
|  | 6:09 | 10.4922 | 0.50865 | 0.58719
|  | 6:09 | 10.4933 | 0.47528 | 0.58719
|  | 6:09 | 10.4944 | 0.44013 | 0.58719
|  | 6:09 | 10.4956 | 0.40498 | 0.58718
|  | 6:09 | 10.4967 | 0.36805 | 0.58718
|  | 6:09 | 10.4978 | 0.33113 | 0.58718
|  | 6:09 | 10.4989 | 0.29421 | 0.58718
|  | 6:09 | 10.5 | 0.25728 | 0.58717
|  | 6:09 | 10.5011 | 0.22036 | 0.58717
|  | 6:10 | 10.5022 | 0.18481 | 0.58717
|  | 6:10 | 10.5033 | 0.14927 | 0.58717
|  | 6:10 | 10.5044 | 0.11508 | 0.58716
|  | 6:10 | 10.5056 | 0.082226 | 0.58716
|  | 6:10 | 10.5067 | 0.049376 | 0.58716
|  | 6:10 | 10.5078 | -0.037982 | 0.58716
|  | 6:10 | 10.5089 | -0.12534 | 0.58716
|  | 6:10 | 10.51 | -0.25535 | 0.58715
|  | 6:10 | 10.5111 | -0.42801 | 0.58715
|  | 6:10 | 10.5122 | -0.60067 | 0.58715
|  | 6:10 | 10.5133 | -0.70218 | 0.58715
|  | 6:10 | 10.5144 | -0.80368 | 0.58714
|  | 6:10 | 10.5156 | -0.87558 | 0.58714
|  | 6:10 | 10.5167 | -0.91788 | 0.58714
|  | 6:10 | 10.5178 | -0.96018 | 0.58714
|  | 6:11 | 10.5189 | -0.96528 | 0.58713
|  | 6:11 | 10.52 | -0.97039 | 0.58713
|  | 6:11 | 10.5211 | -0.96714 | 0.58713
|  | 6:11 | 10.5222 | -0.95555 | 0.58713
|  | 6:11 | 10.5233 | -0.94395 | 0.58712
|  | 6:11 | 10.5244 | -0.92406 | 0.58712
|  | 6:11 | 10.5256 | -0.90417 | 0.58712
|  | 6:11 | 10.5267 | -0.88211 | 0.58712
|  | 6:11 | 10.5278 | -0.8579 | 0.58712
|  | 6:11 | 10.5289 | -0.83368 | 0.58711
|  | 6:11 | 10.53 | -0.80947 | 0.58711
|  | 6:11 | 10.5311 | -0.78525 | 0.58711
|  | 6:11 | 10.5322 | -0.7614 | 0.58711
|  | 6:11 | 10.5333 | -0.73791 | 0.5871
|  | 6:11 | 10.5344 | -0.71441 | 0.5871
|  | 6:12 | 10.5356 | -0.69092 | 0.5871
|  | 6:12 | 10.5367 | -0.66743 | 0.5871
|  | 6:12 | 10.5378 | -0.64491 | 0.58709
|  | 6:12 | 10.5389 | -0.62337 | 0.58709
|  | 6:12 | 10.54 | -0.60182 | 0.58709
|  | 6:12 | 10.5411 | -0.5858 | 0.58709
|  | 6:12 | 10.5422 | -0.56977 | 0.58709
|  | 6:12 | 10.5433 | -0.5558 | 0.58708
|  | 6:12 | 10.5444 | -0.54388 | 0.58708
|  | 6:12 | 10.5456 | -0.53196 | 0.58708
|  | 6:12 | 10.5467 | -0.52258 | 0.58708
|  | 6:12 | 10.5478 | -0.51321 | 0.58707
|  | 6:12 | 10.5489 | -0.50383 | 0.58707
|  | 6:12 | 10.55 | -0.49445 | 0.58707
|  | 6:12 | 10.5511 | -0.48508 | 0.58707
|  | 6:13 | 10.5522 | -0.47904 | 0.58706
|  | 6:13 | 10.5533 | -0.473 | 0.58706
|  | 6:13 | 10.5544 | -0.4684 | 0.58706
|  | 6:13 | 10.5556 | -0.46524 | 0.58706
|  | 6:13 | 10.5567 | -0.46208 | 0.58706
|  | 6:13 | 10.5578 | -0.519 | 0.58705
|  | 6:13 | 10.5589 | -0.57592 | 0.58705
|  | 6:13 | 10.56 | -0.61498 | 0.58705
|  | 6:13 | 10.5611 | -0.63619 | 0.58705
|  | 6:13 | 10.5622 | -0.6574 | 0.58704
|  | 6:13 | 10.5633 | -0.64013 | 0.58704
|  | 6:13 | 10.5644 | -0.62286 | 0.58704
|  | 6:13 | 10.5656 | -0.60193 | 0.58704
|  | 6:13 | 10.5667 | -0.57735 | 0.58703
|  | 6:13 | 10.5678 | -0.55276 | 0.58703
|  | 6:14 | 10.5689 | -0.52231 | 0.58703
|  | 6:14 | 10.57 | -0.49185 | 0.58703
|  | 6:14 | 10.5711 | -0.45848 | 0.58703
|  | 6:14 | 10.5722 | -0.42219 | 0.58702
|  | 6:14 | 10.5733 | -0.3859 | 0.58702
|  | 6:14 | 10.5744 | -0.3496 | 0.58702
|  | 6:14 | 10.5756 | -0.31331 | 0.58702
|  | 6:14 | 10.5767 | -0.27812 | 0.58701
|  | 6:14 | 10.5778 | -0.24404 | 0.58701
|  | 6:14 | 10.5789 | -0.20995 | 0.58701
|  | 6:14 | 10.58 | -0.17858 | 0.58701
|  | 6:14 | 10.5811 | -0.14721 | 0.587
|  | 6:14 | 10.5822 | -0.11655 | 0.587
|  | 6:14 | 10.5833 | -0.086588 | 0.587
|  | 6:14 | 10.5844 | -0.056628 | 0.587
|  | 6:15 | 10.5856 | -0.029615 | 0.587
|  | 6:15 | 10.5867 | -0.002601 | 0.58699
|  | 6:15 | 10.5878 | 0.021431 | 0.58699
|  | 6:15 | 10.5889 | 0.042482 | 0.58699
|  | 6:15 | 10.59 | 0.063533 | 0.58699
|  | 6:15 | 10.5911 | 0.079306 | 0.58698
|  | 6:15 | 10.5922 | 0.09508 | 0.58698
|  | 6:15 | 10.5933 | 0.10812 | 0.58698
|  | 6:15 | 10.5944 | 0.11841 | 0.58698
|  | 6:15 | 10.5956 | 0.12871 | 0.58697
|  | 6:15 | 10.5967 | 0.13544 | 0.58697
|  | 6:15 | 10.5978 | 0.14218 | 0.58697
|  | 6:15 | 10.5989 | 0.14891 | 0.58697
|  | 6:15 | 10.6 | 0.15564 | 0.58697
|  | 6:15 | 10.6011 | 0.16238 | 0.58696
|  | 6:16 | 10.6022 | 0.16911 | 0.58696
|  | 6:16 | 10.6033 | 0.17585 | 0.58696
|  | 6:16 | 10.6044 | 0.18168 | 0.58696
|  | 6:16 | 10.6056 | 0.18662 | 0.58695
|  | 6:16 | 10.6067 | 0.19157 | 0.58695
|  | 6:16 | 10.6078 | 0.1792 | 0.58695
|  | 6:16 | 10.6089 | 0.16683 | 0.58695
|  | 6:16 | 10.61 | 0.16802 | 0.58694
|  | 6:16 | 10.6111 | 0.18276 | 0.58694
|  | 6:16 | 10.6122 | 0.19751 | 0.58694
|  | 6:16 | 10.6133 | 0.2079 | 0.58694
|  | 6:16 | 10.6144 | 0.2183 | 0.58694
|  | 6:16 | 10.6156 | 0.22249 | 0.58693
|  | 6:16 | 10.6167 | 0.22048 | 0.58693
|  | 6:16 | 10.6178 | 0.21846 | 0.58693
|  | 6:17 | 10.6189 | 0.21104 | 0.58693
|  | 6:17 | 10.62 | 0.20361 | 0.58692
|  | 6:17 | 10.6211 | 0.19619 | 0.58692
|  | 6:17 | 10.6222 | 0.18876 | 0.58692
|  | 6:17 | 10.6233 | 0.18134 | 0.58692
|  | 6:17 | 10.6244 | 0.17929 | 0.58691
|  | 6:17 | 10.6256 | 0.17725 | 0.58691
|  | 6:17 | 10.6267 | 0.17861 | 0.58691
|  | 6:17 | 10.6278 | 0.18337 | 0.58691
|  | 6:17 | 10.6289 | 0.18813 | 0.58691
|  | 6:17 | 10.63 | 0.19536 | 0.5869
|  | 6:17 | 10.6311 | 0.20258 | 0.5869
|  | 6:17 | 10.6322 | 0.20918 | 0.5869
|  | 6:17 | 10.6333 | 0.21514 | 0.5869
|  | 6:17 | 10.6344 | 0.22111 | 0.58689
|  | 6:18 | 10.6356 | 0.22708 | 0.58689
|  | 6:18 | 10.6367 | 0.23304 | 0.58689
|  | 6:18 | 10.6378 | 0.24099 | 0.58689
|  | 6:18 | 10.6389 | 0.25091 | 0.58688
|  | 6:18 | 10.64 | 0.26082 | 0.58688
|  | 6:18 | 10.6411 | 0.27279 | 0.58688
|  | 6:18 | 10.6422 | 0.28475 | 0.58688
|  | 6:18 | 10.6433 | 0.29671 | 0.58687
|  | 6:18 | 10.6444 | 0.30867 | 0.58687
|  | 6:18 | 10.6456 | 0.32063 | 0.58687
|  | 6:18 | 10.6467 | 0.33175 | 0.58687
|  | 6:18 | 10.6478 | 0.34287 | 0.58687
|  | 6:18 | 10.6489 | 0.35398 | 0.58686
|  | 6:18 | 10.65 | 0.3651 | 0.58686
|  | 6:18 | 10.6511 | 0.37621 | 0.58686
|  | 6:19 | 10.6522 | 0.386 | 0.58686
|  | 6:19 | 10.6533 | 0.39579 | 0.58685
|  | 6:19 | 10.6544 | 0.40415 | 0.58685
|  | 6:19 | 10.6556 | 0.41109 | 0.58685
|  | 6:19 | 10.6567 | 0.41804 | 0.58685
|  | 6:19 | 10.6578 | 0.40223 | 0.58684
|  | 6:19 | 10.6589 | 0.38643 | 0.58684
|  | 6:19 | 10.66 | 0.38904 | 0.58684
|  | 6:19 | 10.6611 | 0.41007 | 0.58684
|  | 6:19 | 10.6622 | 0.43109 | 0.58684
|  | 6:19 | 10.6633 | 0.4384 | 0.58683
|  | 6:19 | 10.6644 | 0.44571 | 0.58683
|  | 6:19 | 10.6656 | 0.44633 | 0.58683
|  | 6:19 | 10.6667 | 0.44025 | 0.58683
|  | 6:19 | 10.6678 | 0.43418 | 0.58682
|  | 6:20 | 10.6689 | 0.42033 | 0.58682
|  | 6:20 | 10.67 | 0.40647 | 0.58682
|  | 6:20 | 10.6711 | 0.38991 | 0.58682
|  | 6:20 | 10.6722 | 0.37065 | 0.58681
|  | 6:20 | 10.6733 | 0.35139 | 0.58681
|  | 6:20 | 10.6744 | 0.32967 | 0.58681
|  | 6:20 | 10.6756 | 0.30795 | 0.58681
|  | 6:20 | 10.6767 | 0.28516 | 0.58681
|  | 6:20 | 10.6778 | 0.26129 | 0.5868
|  | 6:20 | 10.6789 | 0.23742 | 0.5868
|  | 6:20 | 10.68 | 0.20945 | 0.5868
|  | 6:20 | 10.6811 | 0.18148 | 0.5868
|  | 6:20 | 10.6822 | 0.15241 | 0.58679
|  | 6:20 | 10.6833 | 0.12226 | 0.58679
|  | 6:20 | 10.6844 | 0.092098 | 0.58679
|  | 6:21 | 10.6856 | 0.064983 | 0.58679
|  | 6:21 | 10.6867 | 0.037867 | 0.58678
|  | 6:21 | 10.6878 | 0.011722 | 0.58678
|  | 6:21 | 10.6889 | -0.013454 | 0.58678
|  | 6:21 | 10.69 | -0.038629 | 0.58678
|  | 6:21 | 10.6911 | -0.060119 | 0.58678
|  | 6:21 | 10.6922 | -0.081609 | 0.58677
|  | 6:21 | 10.6933 | -0.1004 | 0.58677
|  | 6:21 | 10.6944 | -0.11651 | 0.58677
|  | 6:21 | 10.6956 | -0.13261 | 0.58677
|  | 6:21 | 10.6967 | -0.14433 | 0.58676
|  | 6:21 | 10.6978 | -0.15606 | 0.58676
|  | 6:21 | 10.6989 | -0.16648 | 0.58676
|  | 6:21 | 10.7 | -0.17558 | 0.58676
|  | 6:21 | 10.7011 | -0.18468 | 0.58675
|  | 6:22 | 10.7022 | -0.19153 | 0.58675
|  | 6:22 | 10.7033 | -0.19838 | 0.58675
|  | 6:22 | 10.7044 | -0.20412 | 0.58675
|  | 6:22 | 10.7056 | -0.20875 | 0.58675
|  | 6:22 | 10.7067 | -0.21339 | 0.58674
|  | 6:22 | 10.7078 | -0.27673 | 0.58674
|  | 6:22 | 10.7089 | -0.34008 | 0.58674
|  | 6:22 | 10.71 | -0.41007 | 0.58674
|  | 6:22 | 10.7111 | -0.4867 | 0.58673
|  | 6:22 | 10.7122 | -0.56334 | 0.58673
|  | 6:22 | 10.7133 | -0.59367 | 0.58673
|  | 6:22 | 10.7144 | -0.62399 | 0.58673
|  | 6:22 | 10.7156 | -0.64309 | 0.58672
|  | 6:22 | 10.7167 | -0.65095 | 0.58672
|  | 6:22 | 10.7178 | -0.65881 | 0.58672
|  | 6:23 | 10.7189 | -0.6572 | 0.58672
|  | 6:23 | 10.72 | -0.65559 | 0.58672
|  | 6:23 | 10.7211 | -0.65201 | 0.58671
|  | 6:23 | 10.7222 | -0.64644 | 0.58671
|  | 6:23 | 10.7233 | -0.64087 | 0.58671
|  | 6:23 | 10.7244 | -0.6353 | 0.58671
|  | 6:23 | 10.7256 | -0.62973 | 0.5867
|  | 6:23 | 10.7267 | -0.62416 | 0.5867
|  | 6:23 | 10.7278 | -0.61859 | 0.5867
|  | 6:23 | 10.7289 | -0.61302 | 0.5867
|  | 6:23 | 10.73 | -0.60745 | 0.58669
|  | 6:23 | 10.7311 | -0.60188 | 0.58669
|  | 6:23 | 10.7322 | -0.59692 | 0.58669
|  | 6:23 | 10.7333 | -0.59255 | 0.58669
|  | 6:23 | 10.7344 | -0.58819 | 0.58669
|  | 6:24 | 10.7356 | -0.58697 | 0.58668
|  | 6:24 | 10.7367 | -0.58575 | 0.58668
|  | 6:24 | 10.7378 | -0.58651 | 0.58668
|  | 6:24 | 10.7389 | -0.58927 | 0.58668
|  | 6:24 | 10.74 | -0.59202 | 0.58667
|  | 6:24 | 10.7411 | -0.59622 | 0.58667
|  | 6:24 | 10.7422 | -0.60042 | 0.58667
|  | 6:24 | 10.7433 | -0.60463 | 0.58667
|  | 6:24 | 10.7444 | -0.60883 | 0.58666
|  | 6:24 | 10.7456 | -0.61303 | 0.58666
|  | 6:24 | 10.7467 | -0.61489 | 0.58666
|  | 6:24 | 10.7478 | -0.61674 | 0.58666
|  | 6:24 | 10.7489 | -0.61696 | 0.58666
|  | 6:24 | 10.75 | -0.61554 | 0.58665
|  | 6:24 | 10.7511 | -0.61412 | 0.58665
|  | 6:25 | 10.7522 | -0.60966 | 0.58665
|  | 6:25 | 10.7533 | -0.6052 | 0.58665
|  | 6:25 | 10.7544 | -0.59955 | 0.58664
|  | 6:25 | 10.7556 | -0.59272 | 0.58664
|  | 6:25 | 10.7567 | -0.58588 | 0.58664
|  | 6:25 | 10.7578 | -0.57414 | 0.58664
|  | 6:25 | 10.7589 | -0.56241 | 0.58663
|  | 6:25 | 10.76 | -0.55708 | 0.58663
|  | 6:25 | 10.7611 | -0.55816 | 0.58663
|  | 6:25 | 10.7622 | -0.55925 | 0.58663
|  | 6:25 | 10.7633 | -0.55809 | 0.58662
|  | 6:25 | 10.7644 | -0.55693 | 0.58662
|  | 6:25 | 10.7656 | -0.55379 | 0.58662
|  | 6:25 | 10.7667 | -0.54867 | 0.58662
|  | 6:25 | 10.7678 | -0.54355 | 0.58662
|  | 6:26 | 10.7689 | -0.53414 | 0.58661
|  | 6:26 | 10.77 | -0.52473 | 0.58661
|  | 6:26 | 10.7711 | -0.51434 | 0.58661
|  | 6:26 | 10.7722 | -0.50295 | 0.58661
|  | 6:26 | 10.7733 | -0.49157 | 0.5866
|  | 6:26 | 10.7744 | -0.47934 | 0.5866
|  | 6:26 | 10.7756 | -0.46711 | 0.5866
|  | 6:26 | 10.7767 | -0.4533 | 0.5866
|  | 6:26 | 10.7778 | -0.43792 | 0.58659
|  | 6:26 | 10.7789 | -0.42253 | 0.58659
|  | 6:26 | 10.78 | -0.40304 | 0.58659
|  | 6:26 | 10.7811 | -0.38356 | 0.58659
|  | 6:26 | 10.7822 | -0.36407 | 0.58659
|  | 6:26 | 10.7833 | -0.34458 | 0.58658
|  | 6:26 | 10.7844 | -0.3251 | 0.58658
|  | 6:27 | 10.7856 | -0.30561 | 0.58658
|  | 6:27 | 10.7867 | -0.28612 | 0.58658
|  | 6:27 | 10.7878 | -0.26563 | 0.58657
|  | 6:27 | 10.7889 | -0.24414 | 0.58657
|  | 6:27 | 10.79 | -0.22265 | 0.58657
|  | 6:27 | 10.7911 | -0.19861 | 0.58657
|  | 6:27 | 10.7922 | -0.17456 | 0.58656
|  | 6:27 | 10.7933 | -0.15137 | 0.58656
|  | 6:27 | 10.7944 | -0.12903 | 0.58656
|  | 6:27 | 10.7956 | -0.10669 | 0.58656
|  | 6:27 | 10.7967 | -0.087153 | 0.58656
|  | 6:27 | 10.7978 | -0.067612 | 0.58655
|  | 6:27 | 10.7989 | -0.049331 | 0.58655
|  | 6:27 | 10.8 | -0.032308 | 0.58655
|  | 6:27 | 10.8011 | -0.015285 | 0.58655
|  | 6:28 | 10.8022 | 0.0017385 | 0.58654
|  | 6:28 | 10.8033 | 0.018762 | 0.58654
|  | 6:28 | 10.8044 | 0.036672 | 0.58654
|  | 6:28 | 10.8056 | 0.055471 | 0.58654
|  | 6:28 | 10.8067 | 0.074269 | 0.58653
|  | 6:28 | 10.8078 | 0.13185 | 0.58653
|  | 6:28 | 10.8089 | 0.18944 | 0.58653
|  | 6:28 | 10.81 | 0.25458 | 0.58653
|  | 6:28 | 10.8111 | 0.32727 | 0.58653
|  | 6:28 | 10.8122 | 0.39996 | 0.58652
|  | 6:28 | 10.8133 | 0.42709 | 0.58652
|  | 6:28 | 10.8144 | 0.45422 | 0.58652
|  | 6:28 | 10.8156 | 0.47301 | 0.58652
|  | 6:28 | 10.8167 | 0.48346 | 0.58651
|  | 6:28 | 10.8178 | 0.49391 | 0.58651
|  | 6:29 | 10.8189 | 0.4989 | 0.58651
|  | 6:29 | 10.82 | 0.50389 | 0.58651
|  | 6:29 | 10.8211 | 0.50888 | 0.5865
|  | 6:29 | 10.8222 | 0.51386 | 0.5865
|  | 6:29 | 10.8233 | 0.51885 | 0.5865
|  | 6:29 | 10.8244 | 0.52352 | 0.5865
|  | 6:29 | 10.8256 | 0.52819 | 0.5865
|  | 6:29 | 10.8267 | 0.53072 | 0.58649
|  | 6:29 | 10.8278 | 0.53111 | 0.58649
|  | 6:29 | 10.8289 | 0.53149 | 0.58649
|  | 6:29 | 10.83 | 0.51394 | 0.58649
|  | 6:29 | 10.8311 | 0.4964 | 0.58648
|  | 6:29 | 10.8322 | 0.47974 | 0.58648
|  | 6:29 | 10.8333 | 0.46397 | 0.58648
|  | 6:29 | 10.8344 | 0.4482 | 0.58648
|  | 6:30 | 10.8356 | 0.44225 | 0.58647
|  | 6:30 | 10.8367 | 0.4363 | 0.58647
|  | 6:30 | 10.8378 | 0.43462 | 0.58647
|  | 6:30 | 10.8389 | 0.43722 | 0.58647
|  | 6:30 | 10.84 | 0.43981 | 0.58647
|  | 6:30 | 10.8411 | 0.44706 | 0.58646
|  | 6:30 | 10.8422 | 0.45432 | 0.58646
|  | 6:30 | 10.8433 | 0.46249 | 0.58646
|  | 6:30 | 10.8444 | 0.47159 | 0.58646
|  | 6:30 | 10.8456 | 0.48068 | 0.58645
|  | 6:30 | 10.8467 | 0.48567 | 0.58645
|  | 6:30 | 10.8478 | 0.49065 | 0.58645
|  | 6:30 | 10.8489 | 0.49461 | 0.58645
|  | 6:30 | 10.85 | 0.49755 | 0.58644
|  | 6:30 | 10.8511 | 0.50048 | 0.58644
|  | 6:31 | 10.8522 | 0.50341 | 0.58644
|  | 6:31 | 10.8533 | 0.50635 | 0.58644
|  | 6:31 | 10.8544 | 0.5096 | 0.58644
|  | 6:31 | 10.8556 | 0.51318 | 0.58643
|  | 6:31 | 10.8567 | 0.51676 | 0.58643
|  | 6:31 | 10.8578 | 0.5342 | 0.58643
|  | 6:31 | 10.8589 | 0.55164 | 0.58643
|  | 6:31 | 10.86 | 0.57136 | 0.58642
|  | 6:31 | 10.8611 | 0.59336 | 0.58642
|  | 6:31 | 10.8622 | 0.61535 | 0.58642
|  | 6:31 | 10.8633 | 0.61621 | 0.58642
|  | 6:31 | 10.8644 | 0.61707 | 0.58641
|  | 6:31 | 10.8656 | 0.55278 | 0.58641
|  | 6:31 | 10.8667 | 0.42336 | 0.58641
|  | 6:31 | 10.8678 | 0.29393 | 0.58641
|  | 6:32 | 10.8689 | 0.12168 | 0.58641
|  | 6:32 | 10.87 | -0.050575 | 0.5864
|  | 6:32 | 10.8711 | -0.18932 | 0.5864
|  | 6:32 | 10.8722 | -0.29455 | 0.5864
|  | 6:32 | 10.8733 | -0.39978 | 0.5864
|  | 6:32 | 10.8744 | -0.46036 | 0.58639
|  | 6:32 | 10.8756 | -0.52094 | 0.58639
|  | 6:32 | 10.8767 | -0.55285 | 0.58639
|  | 6:32 | 10.8778 | -0.57519 | 0.58639
|  | 6:32 | 10.8789 | -0.59753 | 0.58638
|  | 6:32 | 10.88 | -0.60515 | 0.58638
|  | 6:32 | 10.8811 | -0.61277 | 0.58638
|  | 6:32 | 10.8822 | -0.61922 | 0.58638
|  | 6:32 | 10.8833 | -0.62451 | 0.58637
|  | 6:32 | 10.8844 | -0.62981 | 0.58637
|  | 6:33 | 10.8856 | -0.62618 | 0.58637
|  | 6:33 | 10.8867 | -0.62256 | 0.58637
|  | 6:33 | 10.8878 | -0.61603 | 0.58637
|  | 6:33 | 10.8889 | -0.6066 | 0.58636
|  | 6:33 | 10.89 | -0.59717 | 0.58636
|  | 6:33 | 10.8911 | -0.58535 | 0.58636
|  | 6:33 | 10.8922 | -0.57353 | 0.58636
|  | 6:33 | 10.8933 | -0.56172 | 0.58635
|  | 6:33 | 10.8944 | -0.5499 | 0.58635
|  | 6:33 | 10.8956 | -0.53808 | 0.58635
|  | 6:33 | 10.8967 | -0.52758 | 0.58635
|  | 6:33 | 10.8978 | -0.51707 | 0.58634
|  | 6:33 | 10.8989 | -0.50726 | 0.58634
|  | 6:33 | 10.9 | -0.49814 | 0.58634
|  | 6:33 | 10.9011 | -0.48903 | 0.58634
|  | 6:34 | 10.9022 | -0.47846 | 0.58634
|  | 6:34 | 10.9033 | -0.46788 | 0.58633
|  | 6:34 | 10.9044 | -0.45626 | 0.58633
|  | 6:34 | 10.9056 | -0.44358 | 0.58633
|  | 6:34 | 10.9067 | -0.43089 | 0.58633
|  | 6:34 | 10.9078 | -0.47422 | 0.58632
|  | 6:34 | 10.9089 | -0.51755 | 0.58632
|  | 6:34 | 10.91 | -0.51794 | 0.58632
|  | 6:34 | 10.9111 | -0.4754 | 0.58632
|  | 6:34 | 10.9122 | -0.43286 | 0.58631
|  | 6:34 | 10.9133 | -0.39032 | 0.58631
|  | 6:34 | 10.9144 | -0.34779 | 0.58631
|  | 6:34 | 10.9156 | -0.31047 | 0.58631
|  | 6:34 | 10.9167 | -0.27839 | 0.58631
|  | 6:34 | 10.9178 | -0.2463 | 0.5863
|  | 6:35 | 10.9189 | -0.2209 | 0.5863
|  | 6:35 | 10.92 | -0.1955 | 0.5863
|  | 6:35 | 10.9211 | -0.174 | 0.5863
|  | 6:35 | 10.9222 | -0.1564 | 0.58629
|  | 6:35 | 10.9233 | -0.1388 | 0.58629
|  | 6:35 | 10.9244 | -0.12894 | 0.58629
|  | 6:35 | 10.9256 | -0.11907 | 0.58629
|  | 6:35 | 10.9267 | -0.1123 | 0.58628
|  | 6:35 | 10.9278 | -0.10863 | 0.58628
|  | 6:35 | 10.9289 | -0.10495 | 0.58628
|  | 6:35 | 10.93 | -0.10455 | 0.58628
|  | 6:35 | 10.9311 | -0.10416 | 0.58628
|  | 6:35 | 10.9322 | -0.10523 | 0.58627
|  | 6:35 | 10.9333 | -0.10777 | 0.58627
|  | 6:35 | 10.9344 | -0.11032 | 0.58627
|  | 6:36 | 10.9356 | -0.11594 | 0.58627
|  | 6:36 | 10.9367 | -0.12156 | 0.58626
|  | 6:36 | 10.9378 | -0.12811 | 0.58626
|  | 6:36 | 10.9389 | -0.1356 | 0.58626
|  | 6:36 | 10.94 | -0.14309 | 0.58626
|  | 6:36 | 10.9411 | -0.15173 | 0.58625
|  | 6:36 | 10.9422 | -0.16038 | 0.58625
|  | 6:36 | 10.9433 | -0.16719 | 0.58625
|  | 6:36 | 10.9444 | -0.17218 | 0.58625
|  | 6:36 | 10.9456 | -0.17717 | 0.58625
|  | 6:36 | 10.9467 | -0.17308 | 0.58624
|  | 6:36 | 10.9478 | -0.16899 | 0.58624
|  | 6:36 | 10.9489 | -0.16106 | 0.58624
|  | 6:36 | 10.95 | -0.14928 | 0.58624
|  | 6:36 | 10.9511 | -0.13749 | 0.58623
|  | 6:37 | 10.9522 | -0.12391 | 0.58623
|  | 6:37 | 10.9533 | -0.11032 | 0.58623
|  | 6:37 | 10.9544 | -0.098166 | 0.58623
|  | 6:37 | 10.9556 | -0.087453 | 0.58622
|  | 6:37 | 10.9567 | -0.07674 | 0.58622
|  | 6:37 | 10.9578 | -0.10069 | 0.58622
|  | 6:37 | 10.9589 | -0.12464 | 0.58622
|  | 6:37 | 10.96 | -0.17172 | 0.58622
|  | 6:37 | 10.9611 | -0.24193 | 0.58621
|  | 6:37 | 10.9622 | -0.31214 | 0.58621
|  | 6:37 | 10.9633 | -0.34213 | 0.58621
|  | 6:37 | 10.9644 | -0.37211 | 0.58621
|  | 6:37 | 10.9656 | -0.38781 | 0.5862
|  | 6:37 | 10.9667 | -0.38921 | 0.5862
|  | 6:37 | 10.9678 | -0.39061 | 0.5862
|  | 6:38 | 10.9689 | -0.37881 | 0.5862
|  | 6:38 | 10.97 | -0.36701 | 0.58619
|  | 6:38 | 10.9711 | -0.35222 | 0.58619
|  | 6:38 | 10.9722 | -0.33444 | 0.58619
|  | 6:38 | 10.9733 | -0.31667 | 0.58619
|  | 6:38 | 10.9744 | -0.2936 | 0.58619
|  | 6:38 | 10.9756 | -0.27053 | 0.58618
|  | 6:38 | 10.9767 | -0.24822 | 0.58618
|  | 6:38 | 10.9778 | -0.22668 | 0.58618
|  | 6:38 | 10.9789 | -0.20514 | 0.58618
|  | 6:38 | 10.98 | -0.1852 | 0.58617
|  | 6:38 | 10.9811 | -0.16526 | 0.58617
|  | 6:38 | 10.9822 | -0.14664 | 0.58617
|  | 6:38 | 10.9833 | -0.12934 | 0.58617
|  | 6:38 | 10.9844 | -0.11205 | 0.58616
|  | 6:39 | 10.9856 | -0.099948 | 0.58616
|  | 6:39 | 10.9867 | -0.087851 | 0.58616
|  | 6:39 | 10.9878 | -0.078508 | 0.58616
|  | 6:39 | 10.9889 | -0.07192 | 0.58616
|  | 6:39 | 10.99 | -0.065332 | 0.58615
|  | 6:39 | 10.9911 | -0.064053 | 0.58615
|  | 6:39 | 10.9922 | -0.062775 | 0.58615
|  | 6:39 | 10.9933 | -0.063185 | 0.58615
|  | 6:39 | 10.9944 | -0.065284 | 0.58614
|  | 6:39 | 10.9956 | -0.067382 | 0.58614
|  | 6:39 | 10.9967 | -0.069481 | 0.58614
|  | 6:39 | 10.9978 | -0.071579 | 0.58614
|  | 6:39 | 10.9989 | -0.074878 | 0.58613
|  | 6:39 | 11 | -0.079378 | 0.58613
|  | 6:39 | 11.0011 | -0.083878 | 0.58613
|  | 6:40 | 11.0022 | -0.088377 | 0.58613
|  | 6:40 | 11.0033 | -0.092877 | 0.58612
|  | 6:40 | 11.0044 | -0.098095 | 0.58612
|  | 6:40 | 11.0056 | -0.10403 | 0.58612
|  | 6:40 | 11.0067 | -0.10997 | 0.58612
|  | 6:40 | 11.0078 | -0.13946 | 0.58612
|  | 6:40 | 11.0089 | -0.16895 | 0.58611
|  | 6:40 | 11.01 | -0.18787 | 0.58611
|  | 6:40 | 11.0111 | -0.1962 | 0.58611
|  | 6:40 | 11.0122 | -0.20453 | 0.58611
|  | 6:40 | 11.0133 | -0.21203 | 0.5861
|  | 6:40 | 11.0144 | -0.21952 | 0.5861
|  | 6:40 | 11.0156 | -0.22564 | 0.5861
|  | 6:40 | 11.0167 | -0.23039 | 0.5861
|  | 6:40 | 11.0178 | -0.23513 | 0.58609
|  | 6:41 | 11.0189 | -0.23519 | 0.58609
|  | 6:41 | 11.02 | -0.23525 | 0.58609
|  | 6:41 | 11.0211 | -0.23093 | 0.58609
|  | 6:41 | 11.0222 | -0.22224 | 0.58609
|  | 6:41 | 11.0233 | -0.21354 | 0.58608
|  | 6:41 | 11.0244 | -0.19231 | 0.58608
|  | 6:41 | 11.0256 | -0.17108 | 0.58608
|  | 6:41 | 11.0267 | -0.14533 | 0.58608
|  | 6:41 | 11.0278 | -0.11506 | 0.58607
|  | 6:41 | 11.0289 | -0.084793 | 0.58607
|  | 6:41 | 11.03 | -0.052965 | 0.58607
|  | 6:41 | 11.0311 | -0.021138 | 0.58607
|  | 6:41 | 11.0322 | 0.0086022 | 0.58606
|  | 6:41 | 11.0333 | 0.036255 | 0.58606
|  | 6:41 | 11.0344 | 0.063909 | 0.58606
|  | 6:42 | 11.0356 | 0.08698 | 0.58606
|  | 6:42 | 11.0367 | 0.11005 | 0.58606
|  | 6:42 | 11.0378 | 0.12944 | 0.58605
|  | 6:42 | 11.0389 | 0.14515 | 0.58605
|  | 6:42 | 11.04 | 0.16086 | 0.58605
|  | 6:42 | 11.0411 | 0.16811 | 0.58605
|  | 6:42 | 11.0422 | 0.17535 | 0.58604
|  | 6:42 | 11.0433 | 0.17838 | 0.58604
|  | 6:42 | 11.0444 | 0.17718 | 0.58604
|  | 6:42 | 11.0456 | 0.17598 | 0.58604
|  | 6:42 | 11.0467 | 0.16966 | 0.58603
|  | 6:42 | 11.0478 | 0.16334 | 0.58603
|  | 6:42 | 11.0489 | 0.15506 | 0.58603
|  | 6:42 | 11.05 | 0.14482 | 0.58603
|  | 6:42 | 11.0511 | 0.13458 | 0.58603
|  | 6:43 | 11.0522 | 0.12037 | 0.58602
|  | 6:43 | 11.0533 | 0.10616 | 0.58602
|  | 6:43 | 11.0544 | 0.088851 | 0.58602
|  | 6:43 | 11.0556 | 0.068439 | 0.58602
|  | 6:43 | 11.0567 | 0.048027 | 0.58601
|  | 6:43 | 11.0578 | -0.029392 | 0.58601
|  | 6:43 | 11.0589 | -0.10681 | 0.58601
|  | 6:43 | 11.06 | -0.17328 | 0.58601
|  | 6:43 | 11.0611 | -0.22881 | 0.586
|  | 6:43 | 11.0622 | -0.28434 | 0.586
|  | 6:43 | 11.0633 | -0.30227 | 0.586
|  | 6:43 | 11.0644 | -0.3202 | 0.586
|  | 6:43 | 11.0656 | -0.32944 | 0.586
|  | 6:43 | 11.0667 | -0.33 | 0.58599
|  | 6:43 | 11.0678 | -0.33056 | 0.58599
|  | 6:44 | 11.0689 | -0.32176 | 0.58599
|  | 6:44 | 11.07 | -0.31296 | 0.58599
|  | 6:44 | 11.0711 | -0.3027 | 0.58598
|  | 6:44 | 11.0722 | -0.29098 | 0.58598
|  | 6:44 | 11.0733 | -0.27926 | 0.58598
|  | 6:44 | 11.0744 | -0.27189 | 0.58598
|  | 6:44 | 11.0756 | -0.26452 | 0.58597
|  | 6:44 | 11.0767 | -0.25715 | 0.58597
|  | 6:44 | 11.0778 | -0.24978 | 0.58597
|  | 6:44 | 11.0789 | -0.24241 | 0.58597
|  | 6:44 | 11.08 | -0.23608 | 0.58597
|  | 6:44 | 11.0811 | -0.22976 | 0.58596
|  | 6:44 | 11.0822 | -0.22516 | 0.58596
|  | 6:44 | 11.0833 | -0.22229 | 0.58596
|  | 6:44 | 11.0844 | -0.21941 | 0.58596
|  | 6:45 | 11.0856 | -0.22159 | 0.58595
|  | 6:45 | 11.0867 | -0.22376 | 0.58595
|  | 6:45 | 11.0878 | -0.2289 | 0.58595
|  | 6:45 | 11.0889 | -0.23701 | 0.58595
|  | 6:45 | 11.09 | -0.24512 | 0.58594
|  | 6:45 | 11.0911 | -0.25691 | 0.58594
|  | 6:45 | 11.0922 | -0.2687 | 0.58594
|  | 6:45 | 11.0933 | -0.27247 | 0.58594
|  | 6:45 | 11.0944 | -0.26823 | 0.58594
|  | 6:45 | 11.0956 | -0.264 | 0.58593
|  | 6:45 | 11.0967 | -0.28778 | 0.58593
|  | 6:45 | 11.0978 | -0.31157 | 0.58593
|  | 6:45 | 11.0989 | -0.33649 | 0.58593
|  | 6:45 | 11.1 | -0.36254 | 0.58592
|  | 6:45 | 11.1011 | -0.38859 | 0.58592
|  | 6:46 | 11.1022 | -0.40738 | 0.58592
|  | 6:46 | 11.1033 | -0.42617 | 0.58592
|  | 6:46 | 11.1044 | -0.44056 | 0.58591
|  | 6:46 | 11.1056 | -0.45055 | 0.58591
|  | 6:46 | 11.1067 | -0.46053 | 0.58591
|  | 6:46 | 11.1078 | -0.47051 | 0.58591
|  | 6:46 | 11.1089 | -0.4805 | 0.58591
|  | 6:46 | 11.11 | -0.50984 | 0.5859
|  | 6:46 | 11.1111 | -0.55854 | 0.5859
|  | 6:46 | 11.1122 | -0.60724 | 0.5859
|  | 6:46 | 11.1133 | -0.64314 | 0.5859
|  | 6:46 | 11.1144 | -0.67905 | 0.58589
|  | 6:46 | 11.1156 | -0.70179 | 0.58589
|  | 6:46 | 11.1167 | -0.71135 | 0.58589
|  | 6:46 | 11.1178 | -0.72092 | 0.58589
|  | 6:47 | 11.1189 | -0.70949 | 0.58588
|  | 6:47 | 11.12 | -0.69806 | 0.58588
|  | 6:47 | 11.1211 | -0.68135 | 0.58588
|  | 6:47 | 11.1222 | -0.65935 | 0.58588
|  | 6:47 | 11.1233 | -0.63736 | 0.58587
|  | 6:47 | 11.1244 | -0.61193 | 0.58587
|  | 6:47 | 11.1256 | -0.5865 | 0.58587
|  | 6:47 | 11.1267 | -0.56 | 0.58587
|  | 6:47 | 11.1278 | -0.53241 | 0.58587
|  | 6:47 | 11.1289 | -0.50482 | 0.58586
|  | 6:47 | 11.13 | -0.4782 | 0.58586
|  | 6:47 | 11.1311 | -0.45157 | 0.58586
|  | 6:47 | 11.1322 | -0.42824 | 0.58586
|  | 6:47 | 11.1333 | -0.40819 | 0.58585
|  | 6:47 | 11.1344 | -0.38814 | 0.58585
|  | 6:48 | 11.1356 | -0.36917 | 0.58585
|  | 6:48 | 11.1367 | -0.3502 | 0.58585
|  | 6:48 | 11.1378 | -0.3273 | 0.58584
|  | 6:48 | 11.1389 | -0.30045 | 0.58584
|  | 6:48 | 11.14 | -0.2736 | 0.58584
|  | 6:48 | 11.1411 | -0.23893 | 0.58584
|  | 6:48 | 11.1422 | -0.20425 | 0.58584
|  | 6:48 | 11.1433 | -0.16716 | 0.58583
|  | 6:48 | 11.1444 | -0.12764 | 0.58583
|  | 6:48 | 11.1456 | -0.088128 | 0.58583
|  | 6:48 | 11.1467 | -0.045627 | 0.58583
|  | 6:48 | 11.1478 | -0.0031259 | 0.58582
|  | 6:48 | 11.1489 | 0.039375 | 0.58582
|  | 6:48 | 11.15 | 0.081876 | 0.58582
|  | 6:48 | 11.1511 | 0.12438 | 0.58582
|  | 6:49 | 11.1522 | 0.16368 | 0.58581
|  | 6:49 | 11.1533 | 0.20299 | 0.58581
|  | 6:49 | 11.1544 | 0.23915 | 0.58581
|  | 6:49 | 11.1556 | 0.27216 | 0.58581
|  | 6:49 | 11.1567 | 0.30517 | 0.58581
|  | 6:49 | 11.1578 | 0.39575 | 0.5858
|  | 6:49 | 11.1589 | 0.48633 | 0.5858
|  | 6:49 | 11.16 | 0.5914 | 0.5858
|  | 6:49 | 11.1611 | 0.71096 | 0.5858
|  | 6:49 | 11.1622 | 0.83052 | 0.58579
|  | 6:49 | 11.1633 | 0.89732 | 0.58579
|  | 6:49 | 11.1644 | 0.96412 | 0.58579
|  | 6:49 | 11.1656 | 0.99801 | 0.58579
|  | 6:49 | 11.1667 | 0.99901 | 0.58578
|  | 6:49 | 11.1678 | 1 | 0.58578
|  | 6:50 | 11.1689 | 1 | 0.58578
|  | 6:50 | 11.17 | 1 | 0.58578
|  | 6:50 | 11.1711 | 1 | 0.58578
|  | 6:50 | 11.1722 | 1 | 0.58577
|  | 6:50 | 11.1733 | 1 | 0.58577
|  | 6:50 | 11.1744 | 1 | 0.58577
|  | 6:50 | 11.1756 | 1 | 0.58577
|  | 6:50 | 11.1767 | 1 | 0.58576
|  | 6:50 | 11.1778 | 1 | 0.58576
|  | 6:50 | 11.1789 | 1 | 0.58576
|  | 6:50 | 11.18 | 1 | 0.58576
|  | 6:50 | 11.1811 | 1 | 0.58575
|  | 6:50 | 11.1822 | 0.99275 | 0.58575
|  | 6:50 | 11.1833 | 0.97826 | 0.58575
|  | 6:50 | 11.1844 | 0.96377 | 0.58575
|  | 6:51 | 11.1856 | 0.94229 | 0.58575
|  | 6:51 | 11.1867 | 0.92081 | 0.58574
|  | 6:51 | 11.1878 | 0.89821 | 0.58574
|  | 6:51 | 11.1889 | 0.87449 | 0.58574
|  | 6:51 | 11.19 | 0.85076 | 0.58574
|  | 6:51 | 11.1911 | 0.82703 | 0.58573
|  | 6:51 | 11.1922 | 0.80331 | 0.58573
|  | 6:51 | 11.1933 | 0.78197 | 0.58573
|  | 6:51 | 11.1944 | 0.76302 | 0.58573
|  | 6:51 | 11.1956 | 0.74407 | 0.58572
|  | 6:51 | 11.1967 | 0.72773 | 0.58572
|  | 6:51 | 11.1978 | 0.71138 | 0.58572
|  | 6:51 | 11.1989 | 0.69565 | 0.58572
|  | 6:51 | 11.2 | 0.68054 | 0.58572
|  | 6:51 | 11.2011 | 0.66542 | 0.58571
|  | 6:52 | 11.2022 | 0.65113 | 0.58571
|  | 6:52 | 11.2033 | 0.63684 | 0.58571
|  | 6:52 | 11.2044 | 0.62134 | 0.58571
|  | 6:52 | 11.2056 | 0.60462 | 0.5857
|  | 6:52 | 11.2067 | 0.5879 | 0.5857
|  | 6:52 | 11.2078 | 0.52662 | 0.5857
|  | 6:52 | 11.2089 | 0.46533 | 0.5857
|  | 6:52 | 11.21 | 0.37083 | 0.58569
|  | 6:52 | 11.2111 | 0.24312 | 0.58569
|  | 6:52 | 11.2122 | 0.1154 | 0.58569
|  | 6:52 | 11.2133 | 0.030582 | 0.58569
|  | 6:52 | 11.2144 | -0.054235 | 0.58569
|  | 6:52 | 11.2156 | -0.11882 | 0.58568
|  | 6:52 | 11.2167 | -0.16317 | 0.58568
|  | 6:52 | 11.2178 | -0.20752 | 0.58568
|  | 6:53 | 11.2189 | -0.22771 | 0.58568
|  | 6:53 | 11.22 | -0.2479 | 0.58567
|  | 6:53 | 11.2211 | -0.2616 | 0.58567
|  | 6:53 | 11.2222 | -0.26882 | 0.58567
|  | 6:53 | 11.2233 | -0.27603 | 0.58567
|  | 6:53 | 11.2244 | -0.2752 | 0.58566
|  | 6:53 | 11.2256 | -0.27437 | 0.58566
|  | 6:53 | 11.2267 | -0.2712 | 0.58566
|  | 6:53 | 11.2278 | -0.26568 | 0.58566
|  | 6:53 | 11.2289 | -0.26016 | 0.58566
|  | 6:53 | 11.23 | -0.25279 | 0.58565
|  | 6:53 | 11.2311 | -0.24542 | 0.58565
|  | 6:53 | 11.2322 | -0.23917 | 0.58565
|  | 6:53 | 11.2333 | -0.23404 | 0.58565
|  | 6:53 | 11.2344 | -0.2289 | 0.58564
|  | 6:54 | 11.2356 | -0.2277 | 0.58564
|  | 6:54 | 11.2367 | -0.2265 | 0.58564
|  | 6:54 | 11.2378 | -0.22731 | 0.58564
|  | 6:54 | 11.2389 | -0.23014 | 0.58563
|  | 6:54 | 11.24 | -0.23298 | 0.58563
|  | 6:54 | 11.2411 | -0.23816 | 0.58563
|  | 6:54 | 11.2422 | -0.24335 | 0.58563
|  | 6:54 | 11.2433 | -0.24752 | 0.58562
|  | 6:54 | 11.2444 | -0.25066 | 0.58562
|  | 6:54 | 11.2456 | -0.25381 | 0.58562
|  | 6:54 | 11.2467 | -0.25289 | 0.58562
|  | 6:54 | 11.2478 | -0.25197 | 0.58562
|  | 6:54 | 11.2489 | -0.25105 | 0.58561
|  | 6:54 | 11.25 | -0.25012 | 0.58561
|  | 6:54 | 11.2511 | -0.2492 | 0.58561
|  | 6:55 | 11.2522 | -0.25441 | 0.58561
|  | 6:55 | 11.2533 | -0.25961 | 0.5856
|  | 6:55 | 11.2544 | -0.26755 | 0.5856
|  | 6:55 | 11.2556 | -0.27821 | 0.5856
|  | 6:55 | 11.2567 | -0.28888 | 0.5856
|  | 6:55 | 11.2578 | -0.33983 | 0.58559
|  | 6:55 | 11.2589 | -0.39078 | 0.58559
|  | 6:55 | 11.26 | -0.44965 | 0.58559
|  | 6:55 | 11.2611 | -0.51643 | 0.58559
|  | 6:55 | 11.2622 | -0.58322 | 0.58559
|  | 6:55 | 11.2633 | -0.60397 | 0.58558
|  | 6:55 | 11.2644 | -0.62473 | 0.58558
|  | 6:55 | 11.2656 | -0.64777 | 0.58558
|  | 6:55 | 11.2667 | -0.6731 | 0.58558
|  | 6:55 | 11.2678 | -0.69843 | 0.58557
|  | 6:56 | 11.2689 | -0.71074 | 0.58557
|  | 6:56 | 11.27 | -0.72304 | 0.58557
|  | 6:56 | 11.2711 | -0.73135 | 0.58557
|  | 6:56 | 11.2722 | -0.73565 | 0.58556
|  | 6:56 | 11.2733 | -0.73995 | 0.58556
|  | 6:56 | 11.2744 | -0.74053 | 0.58556
|  | 6:56 | 11.2756 | -0.74112 | 0.58556
|  | 6:56 | 11.2767 | -0.74171 | 0.58556
|  | 6:56 | 11.2778 | -0.74229 | 0.58555
|  | 6:56 | 11.2789 | -0.74288 | 0.58555
|  | 6:56 | 11.28 | -0.74671 | 0.58555
|  | 6:56 | 11.2811 | -0.75054 | 0.58555
|  | 6:56 | 11.2822 | -0.75487 | 0.58554
|  | 6:56 | 11.2833 | -0.7597 | 0.58554
|  | 6:56 | 11.2844 | -0.76454 | 0.58554
|  | 6:57 | 11.2856 | -0.76619 | 0.58554
|  | 6:57 | 11.2867 | -0.76784 | 0.58553
|  | 6:57 | 11.2878 | -0.765 | 0.58553
|  | 6:57 | 11.2889 | -0.75767 | 0.58553
|  | 6:57 | 11.29 | -0.75034 | 0.58553
|  | 6:57 | 11.2911 | -0.73281 | 0.58553
|  | 6:57 | 11.2922 | -0.71528 | 0.58552
|  | 6:57 | 11.2933 | -0.69493 | 0.58552
|  | 6:57 | 11.2944 | -0.67176 | 0.58552
|  | 6:57 | 11.2956 | -0.64859 | 0.58552
|  | 6:57 | 11.2967 | -0.62707 | 0.58551
|  | 6:57 | 11.2978 | -0.60555 | 0.58551
|  | 6:57 | 11.2989 | -0.5828 | 0.58551
|  | 6:57 | 11.3 | -0.55881 | 0.58551
|  | 6:57 | 11.3011 | -0.53482 | 0.5855
|  | 6:58 | 11.3022 | -0.50617 | 0.5855
|  | 6:58 | 11.3033 | -0.47752 | 0.5855
|  | 6:58 | 11.3044 | -0.44746 | 0.5855
|  | 6:58 | 11.3056 | -0.41599 | 0.5855
|  | 6:58 | 11.3067 | -0.38452 | 0.58549
|  | 6:58 | 11.3078 | -0.273 | 0.58549
|  | 6:58 | 11.3089 | -0.16148 | 0.58549
|  | 6:58 | 11.31 | -0.081884 | 0.58549
|  | 6:58 | 11.3111 | -0.034206 | 0.58548
|  | 6:58 | 11.3122 | 0.013472 | 0.58548
|  | 6:58 | 11.3133 | 0.017901 | 0.58548
|  | 6:58 | 11.3144 | 0.02233 | 0.58548
|  | 6:58 | 11.3156 | 0.029769 | 0.58547
|  | 6:58 | 11.3167 | 0.040218 | 0.58547
|  | 6:58 | 11.3178 | 0.050667 | 0.58547
|  | 6:59 | 11.3189 | 0.069809 | 0.58547
|  | 6:59 | 11.32 | 0.088951 | 0.58547
|  | 6:59 | 11.3211 | 0.10936 | 0.58546
|  | 6:59 | 11.3222 | 0.13104 | 0.58546
|  | 6:59 | 11.3233 | 0.15272 | 0.58546
|  | 6:59 | 11.3244 | 0.1744 | 0.58546
|  | 6:59 | 11.3256 | 0.19608 | 0.58545
|  | 6:59 | 11.3267 | 0.21617 | 0.58545
|  | 6:59 | 11.3278 | 0.23468 | 0.58545
|  | 6:59 | 11.3289 | 0.25318 | 0.58545
|  | 6:59 | 11.33 | 0.25374 | 0.58544
|  | 6:59 | 11.3311 | 0.25429 | 0.58544
|  | 6:59 | 11.3322 | 0.25072 | 0.58544
|  | 6:59 | 11.3333 | 0.24301 | 0.58544
|  | 6:59 | 11.3344 | 0.2353 | 0.58544
|  | 7:00 | 11.3356 | 0.22758 | 0.58543
|  | 7:00 | 11.3367 | 0.21987 | 0.58543
|  | 7:00 | 11.3378 | 0.21216 | 0.58543
|  | 7:00 | 11.3389 | 0.20445 | 0.58543
|  | 7:00 | 11.34 | 0.19724 | 0.58542
|  | 7:00 | 11.3411 | 0.19151 | 0.58542
|  | 7:00 | 11.3422 | 0.18578 | 0.58542
|  | 7:00 | 11.3433 | 0.17437 | 0.58542
|  | 7:00 | 11.3444 | 0.1573 | 0.58541
|  | 7:00 | 11.3456 | 0.14022 | 0.58541
|  | 7:00 | 11.3467 | 0.12315 | 0.58541
|  | 7:00 | 11.3478 | 0.10608 | 0.58541
|  | 7:00 | 11.3489 | 0.090442 | 0.58541
|  | 7:00 | 11.35 | 0.07625 | 0.5854
|  | 7:00 | 11.3511 | 0.062058 | 0.5854
|  | 7:01 | 11.3522 | 0.055419 | 0.5854
|  | 7:01 | 11.3533 | 0.04878 | 0.5854
|  | 7:01 | 11.3544 | 0.044606 | 0.58539
|  | 7:01 | 11.3556 | 0.042897 | 0.58539
|  | 7:01 | 11.3567 | 0.041188 | 0.58539
|  | 7:01 | 11.3578 | 0.063227 | 0.58539
|  | 7:01 | 11.3589 | 0.085266 | 0.58538
|  | 7:01 | 11.36 | 0.10193 | 0.58538
|  | 7:01 | 11.3611 | 0.11321 | 0.58538
|  | 7:01 | 11.3622 | 0.12449 | 0.58538
|  | 7:01 | 11.3633 | 0.12296 | 0.58537
|  | 7:01 | 11.3644 | 0.12144 | 0.58537
|  | 7:01 | 11.3656 | 0.11876 | 0.58537
|  | 7:01 | 11.3667 | 0.11493 | 0.58537
|  | 7:01 | 11.3678 | 0.1111 | 0.58537
|  | 7:02 | 11.3689 | 0.11423 | 0.58536
|  | 7:02 | 11.37 | 0.11735 | 0.58536
|  | 7:02 | 11.3711 | 0.12048 | 0.58536
|  | 7:02 | 11.3722 | 0.1236 | 0.58536
|  | 7:02 | 11.3733 | 0.12673 | 0.58535
|  | 7:02 | 11.3744 | 0.12325 | 0.58535
|  | 7:02 | 11.3756 | 0.11977 | 0.58535
|  | 7:02 | 11.3767 | 0.11537 | 0.58535
|  | 7:02 | 11.3778 | 0.11004 | 0.58534
|  | 7:02 | 11.3789 | 0.10472 | 0.58534
|  | 7:02 | 11.38 | 0.10111 | 0.58534
|  | 7:02 | 11.3811 | 0.097508 | 0.58534
|  | 7:02 | 11.3822 | 0.088062 | 0.58534
|  | 7:02 | 11.3833 | 0.072776 | 0.58533
|  | 7:02 | 11.3844 | 0.057489 | 0.58533
|  | 7:03 | 11.3856 | 0.055737 | 0.58533
|  | 7:03 | 11.3867 | 0.053985 | 0.58533
|  | 7:03 | 11.3878 | 0.052233 | 0.58532
|  | 7:03 | 11.3889 | 0.050482 | 0.58532
|  | 7:03 | 11.39 | 0.04873 | 0.58532
|  | 7:03 | 11.3911 | 0.040214 | 0.58532
|  | 7:03 | 11.3922 | 0.031698 | 0.58531
|  | 7:03 | 11.3933 | 0.023997 | 0.58531
|  | 7:03 | 11.3944 | 0.017112 | 0.58531
|  | 7:03 | 11.3956 | 0.010227 | 0.58531
|  | 7:03 | 11.3967 | 0.0042347 | 0.58531
|  | 7:03 | 11.3978 | -0.0017577 | 0.5853
|  | 7:03 | 11.3989 | -0.006581 | 0.5853
|  | 7:03 | 11.4 | -0.010235 | 0.5853
|  | 7:03 | 11.4011 | -0.01389 | 0.5853
|  | 7:04 | 11.4022 | -0.020872 | 0.58529
|  | 7:04 | 11.4033 | -0.027855 | 0.58529
|  | 7:04 | 11.4044 | -0.037131 | 0.58529
|  | 7:04 | 11.4056 | -0.0487 | 0.58529
|  | 7:04 | 11.4067 | -0.060269 | 0.58528
|  | 7:04 | 11.4078 | -0.091023 | 0.58528
|  | 7:04 | 11.4089 | -0.12178 | 0.58528
|  | 7:04 | 11.41 | -0.14208 | 0.58528
|  | 7:04 | 11.4111 | -0.15192 | 0.58528
|  | 7:04 | 11.4122 | -0.16176 | 0.58527
|  | 7:04 | 11.4133 | -0.13817 | 0.58527
|  | 7:04 | 11.4144 | -0.11457 | 0.58527
|  | 7:04 | 11.4156 | -0.092907 | 0.58527
|  | 7:04 | 11.4167 | -0.073168 | 0.58526
|  | 7:04 | 11.4178 | -0.05343 | 0.58526
|  | 7:05 | 11.4189 | -0.033691 | 0.58526
|  | 7:05 | 11.42 | -0.013953 | 0.58526
|  | 7:05 | 11.4211 | 0.0092327 | 0.58525
|  | 7:05 | 11.4222 | 0.035866 | 0.58525
|  | 7:05 | 11.4233 | 0.062499 | 0.58525
|  | 7:05 | 11.4244 | 0.070131 | 0.58525
|  | 7:05 | 11.4256 | 0.077764 | 0.58525
|  | 7:05 | 11.4267 | 0.09189 | 0.58524
|  | 7:05 | 11.4278 | 0.11251 | 0.58524
|  | 7:05 | 11.4289 | 0.13313 | 0.58524
|  | 7:05 | 11.43 | 0.1587 | 0.58524
|  | 7:05 | 11.4311 | 0.18427 | 0.58523
|  | 7:05 | 11.4322 | 0.20728 | 0.58523
|  | 7:05 | 11.4333 | 0.22772 | 0.58523
|  | 7:05 | 11.4344 | 0.24817 | 0.58523
|  | 7:06 | 11.4356 | 0.26466 | 0.58522
|  | 7:06 | 11.4367 | 0.28116 | 0.58522
|  | 7:06 | 11.4378 | 0.29597 | 0.58522
|  | 7:06 | 11.4389 | 0.30908 | 0.58522
|  | 7:06 | 11.44 | 0.3222 | 0.58522
|  | 7:06 | 11.4411 | 0.33311 | 0.58521
|  | 7:06 | 11.4422 | 0.34402 | 0.58521
|  | 7:06 | 11.4433 | 0.35327 | 0.58521
|  | 7:06 | 11.4444 | 0.36086 | 0.58521
|  | 7:06 | 11.4456 | 0.36845 | 0.5852
|  | 7:06 | 11.4467 | 0.38068 | 0.5852
|  | 7:06 | 11.4478 | 0.39291 | 0.5852
|  | 7:06 | 11.4489 | 0.40661 | 0.5852
|  | 7:06 | 11.45 | 0.42179 | 0.58519
|  | 7:06 | 11.4511 | 0.43696 | 0.58519
|  | 7:07 | 11.4522 | 0.45213 | 0.58519
|  | 7:07 | 11.4533 | 0.4673 | 0.58519
|  | 7:07 | 11.4544 | 0.48281 | 0.58519
|  | 7:07 | 11.4556 | 0.49865 | 0.58518
|  | 7:07 | 11.4567 | 0.51449 | 0.58518
|  | 7:07 | 11.4578 | 0.45424 | 0.58518
|  | 7:07 | 11.4589 | 0.39399 | 0.58518
|  | 7:07 | 11.46 | 0.35648 | 0.58517
|  | 7:07 | 11.4611 | 0.3417 | 0.58517
|  | 7:07 | 11.4622 | 0.32693 | 0.58517
|  | 7:07 | 11.4633 | 0.32757 | 0.58517
|  | 7:07 | 11.4644 | 0.32822 | 0.58516
|  | 7:07 | 11.4656 | 0.33101 | 0.58516
|  | 7:07 | 11.4667 | 0.33595 | 0.58516
|  | 7:07 | 11.4678 | 0.34088 | 0.58516
|  | 7:08 | 11.4689 | 0.34346 | 0.58516
|  | 7:08 | 11.47 | 0.34603 | 0.58515
|  | 7:08 | 11.4711 | 0.3471 | 0.58515
|  | 7:08 | 11.4722 | 0.34666 | 0.58515
|  | 7:08 | 11.4733 | 0.34622 | 0.58515
|  | 7:08 | 11.4744 | 0.34578 | 0.58514
|  | 7:08 | 11.4756 | 0.34535 | 0.58514
|  | 7:08 | 11.4767 | 0.34491 | 0.58514
|  | 7:08 | 11.4778 | 0.34447 | 0.58514
|  | 7:08 | 11.4789 | 0.34403 | 0.58513
|  | 7:08 | 11.48 | 0.34283 | 0.58513
|  | 7:08 | 11.4811 | 0.34164 | 0.58513
|  | 7:08 | 11.4822 | 0.33898 | 0.58513
|  | 7:08 | 11.4833 | 0.33485 | 0.58512
|  | 7:08 | 11.4844 | 0.33073 | 0.58512
|  | 7:09 | 11.4856 | 0.32296 | 0.58512
|  | 7:09 | 11.4867 | 0.31518 | 0.58512
|  | 7:09 | 11.4878 | 0.3066 | 0.58512
|  | 7:09 | 11.4889 | 0.29721 | 0.58511
|  | 7:09 | 11.49 | 0.28783 | 0.58511
|  | 7:09 | 11.4911 | 0.27844 | 0.58511
|  | 7:09 | 11.4922 | 0.26905 | 0.58511
|  | 7:09 | 11.4933 | 0.26023 | 0.5851
|  | 7:09 | 11.4944 | 0.25197 | 0.5851
|  | 7:09 | 11.4956 | 0.24371 | 0.5851
|  | 7:09 | 11.4967 | 0.23856 | 0.5851
|  | 7:09 | 11.4978 | 0.23342 | 0.58509
|  | 7:09 | 11.4989 | 0.23487 | 0.58509
|  | 7:09 | 11.5 | 0.24292 | 0.58509
|  | 7:09 | 11.5011 | 0.25097 | 0.58509
|  | 7:10 | 11.5022 | 0.25557 | 0.58509
|  | 7:10 | 11.5033 | 0.26016 | 0.58508
|  | 7:10 | 11.5044 | 0.26126 | 0.58508
|  | 7:10 | 11.5056 | 0.25887 | 0.58508
|  | 7:10 | 11.5067 | 0.25649 | 0.58508
|  | 7:10 | 11.5078 | 0.18397 | 0.58507
|  | 7:10 | 11.5089 | 0.11145 | 0.58507
|  | 7:10 | 11.51 | 0.059998 | 0.58507
|  | 7:10 | 11.5111 | 0.029607 | 0.58507
|  | 7:10 | 11.5122 | -0.00078433 | 0.58506
|  | 7:10 | 11.5133 | -0.019188 | 0.58506
|  | 7:10 | 11.5144 | -0.025604 | 0.58506
|  | 7:10 | 11.5156 | -0.027446 | 0.58506
|  | 7:10 | 11.5167 | -0.024714 | 0.58506
|  | 7:10 | 11.5178 | -0.021982 | 0.58505
|  | 7:11 | 11.5189 | -0.012935 | 0.58505
|  | 7:11 | 11.52 | -0.0038869 | 0.58505
|  | 7:11 | 11.5211 | 0.0051607 | 0.58505
|  | 7:11 | 11.5222 | 0.014208 | 0.58504
|  | 7:11 | 11.5233 | 0.023256 | 0.58504
|  | 7:11 | 11.5244 | 0.030227 | 0.58504
|  | 7:11 | 11.5256 | 0.037198 | 0.58504
|  | 7:11 | 11.5267 | 0.043009 | 0.58503
|  | 7:11 | 11.5278 | 0.047662 | 0.58503
|  | 7:11 | 11.5289 | 0.052315 | 0.58503
|  | 7:11 | 11.53 | 0.05224 | 0.58503
|  | 7:11 | 11.5311 | 0.052165 | 0.58503
|  | 7:11 | 11.5322 | 0.049087 | 0.58502
|  | 7:11 | 11.5333 | 0.043007 | 0.58502
|  | 7:11 | 11.5344 | 0.036927 | 0.58502
|  | 7:12 | 11.5356 | 0.026022 | 0.58502
|  | 7:12 | 11.5367 | 0.015117 | 0.58501
|  | 7:12 | 11.5378 | 0.0042125 | 0.58501
|  | 7:12 | 11.5389 | -0.0066922 | 0.58501
|  | 7:12 | 11.54 | -0.017597 | 0.58501
|  | 7:12 | 11.5411 | -0.023325 | 0.585
|  | 7:12 | 11.5422 | -0.029052 | 0.585
|  | 7:12 | 11.5433 | -0.03146 | 0.585
|  | 7:12 | 11.5444 | -0.030549 | 0.585
|  | 7:12 | 11.5456 | -0.029637 | 0.585
|  | 7:12 | 11.5467 | -0.023457 | 0.58499
|  | 7:12 | 11.5478 | -0.017276 | 0.58499
|  | 7:12 | 11.5489 | -0.0099999 | 0.58499
|  | 7:12 | 11.55 | -0.0016275 | 0.58499
|  | 7:12 | 11.5511 | 0.006745 | 0.58498
|  | 7:13 | 11.5522 | 0.013546 | 0.58498
|  | 7:13 | 11.5533 | 0.020348 | 0.58498
|  | 7:13 | 11.5544 | 0.026047 | 0.58498
|  | 7:13 | 11.5556 | 0.030645 | 0.58497
|  | 7:13 | 11.5567 | 0.035243 | 0.58497
|  | 7:13 | 11.5578 | -0.055773 | 0.58497
|  | 7:13 | 11.5589 | -0.14679 | 0.58497
|  | 7:13 | 11.56 | -0.2078 | 0.58497
|  | 7:13 | 11.5611 | -0.2388 | 0.58496
|  | 7:13 | 11.5622 | -0.26981 | 0.58496
|  | 7:13 | 11.5633 | -0.26367 | 0.58496
|  | 7:13 | 11.5644 | -0.25753 | 0.58496
|  | 7:13 | 11.5656 | -0.24763 | 0.58495
|  | 7:13 | 11.5667 | -0.23398 | 0.58495
|  | 7:13 | 11.5678 | -0.22032 | 0.58495
|  | 7:14 | 11.5689 | -0.20121 | 0.58495
|  | 7:14 | 11.57 | -0.1821 | 0.58494
|  | 7:14 | 11.5711 | -0.16395 | 0.58494
|  | 7:14 | 11.5722 | -0.14675 | 0.58494
|  | 7:14 | 11.5733 | -0.12955 | 0.58494
|  | 7:14 | 11.5744 | -0.11778 | 0.58494
|  | 7:14 | 11.5756 | -0.10601 | 0.58493
|  | 7:14 | 11.5767 | -0.097725 | 0.58493
|  | 7:14 | 11.5778 | -0.092925 | 0.58493
|  | 7:14 | 11.5789 | -0.088125 | 0.58493
|  | 7:14 | 11.58 | -0.089633 | 0.58492
|  | 7:14 | 11.5811 | -0.091142 | 0.58492
|  | 7:14 | 11.5822 | -0.095574 | 0.58492
|  | 7:14 | 11.5833 | -0.10293 | 0.58492
|  | 7:14 | 11.5844 | -0.11029 | 0.58491
|  | 7:15 | 11.5856 | -0.12483 | 0.58491
|  | 7:15 | 11.5867 | -0.13936 | 0.58491
|  | 7:15 | 11.5878 | -0.15726 | 0.58491
|  | 7:15 | 11.5889 | -0.17852 | 0.58491
|  | 7:15 | 11.59 | -0.19978 | 0.5849
|  | 7:15 | 11.5911 | -0.22103 | 0.5849
|  | 7:15 | 11.5922 | -0.24229 | 0.5849
|  | 7:15 | 11.5933 | -0.26218 | 0.5849
|  | 7:15 | 11.5944 | -0.28069 | 0.58489
|  | 7:15 | 11.5956 | -0.2992 | 0.58489
|  | 7:15 | 11.5967 | -0.31909 | 0.58489
|  | 7:15 | 11.5978 | -0.33898 | 0.58489
|  | 7:15 | 11.5989 | -0.35888 | 0.58488
|  | 7:15 | 11.6 | -0.37877 | 0.58488
|  | 7:15 | 11.6011 | -0.39866 | 0.58488
|  | 7:16 | 11.6022 | -0.40602 | 0.58488
|  | 7:16 | 11.6033 | -0.41337 | 0.58487
|  | 7:16 | 11.6044 | -0.41972 | 0.58487
|  | 7:16 | 11.6056 | -0.42506 | 0.58487
|  | 7:16 | 11.6067 | -0.43039 | 0.58487
|  | 7:16 | 11.6078 | -0.48458 | 0.58487
|  | 7:16 | 11.6089 | -0.53876 | 0.58486
|  | 7:16 | 11.61 | -0.5795 | 0.58486
|  | 7:16 | 11.6111 | -0.6068 | 0.58486
|  | 7:16 | 11.6122 | -0.63409 | 0.58486
|  | 7:16 | 11.6133 | -0.63528 | 0.58485
|  | 7:16 | 11.6144 | -0.63646 | 0.58485
|  | 7:16 | 11.6156 | -0.63504 | 0.58485
|  | 7:16 | 11.6167 | -0.631 | 0.58485
|  | 7:16 | 11.6178 | -0.62697 | 0.58484
|  | 7:17 | 11.6189 | -0.62293 | 0.58484
|  | 7:17 | 11.62 | -0.6189 | 0.58484
|  | 7:17 | 11.6211 | -0.61544 | 0.58484
|  | 7:17 | 11.6222 | -0.61256 | 0.58484
|  | 7:17 | 11.6233 | -0.60968 | 0.58483
|  | 7:17 | 11.6244 | -0.60679 | 0.58483
|  | 7:17 | 11.6256 | -0.60391 | 0.58483
|  | 7:17 | 11.6267 | -0.60054 | 0.58483
|  | 7:17 | 11.6278 | -0.59667 | 0.58482
|  | 7:17 | 11.6289 | -0.5928 | 0.58482
|  | 7:17 | 11.63 | -0.59102 | 0.58482
|  | 7:17 | 11.6311 | -0.58924 | 0.58482
|  | 7:17 | 11.6322 | -0.58896 | 0.58481
|  | 7:17 | 11.6333 | -0.5902 | 0.58481
|  | 7:17 | 11.6344 | -0.59144 | 0.58481
|  | 7:18 | 11.6356 | -0.59664 | 0.58481
|  | 7:18 | 11.6367 | -0.60185 | 0.58481
|  | 7:18 | 11.6378 | -0.61065 | 0.5848
|  | 7:18 | 11.6389 | -0.62304 | 0.5848
|  | 7:18 | 11.64 | -0.63542 | 0.5848
|  | 7:18 | 11.6411 | -0.64891 | 0.5848
|  | 7:18 | 11.6422 | -0.6624 | 0.58479
|  | 7:18 | 11.6433 | -0.6732 | 0.58479
|  | 7:18 | 11.6444 | -0.6813 | 0.58479
|  | 7:18 | 11.6456 | -0.68941 | 0.58479
|  | 7:18 | 11.6467 | -0.68981 | 0.58478
|  | 7:18 | 11.6478 | -0.69022 | 0.58478
|  | 7:18 | 11.6489 | -0.68727 | 0.58478
|  | 7:18 | 11.65 | -0.68098 | 0.58478
|  | 7:18 | 11.6511 | -0.67468 | 0.58478
|  | 7:19 | 11.6522 | -0.66251 | 0.58477
|  | 7:19 | 11.6533 | -0.65035 | 0.58477
|  | 7:19 | 11.6544 | -0.63818 | 0.58477
|  | 7:19 | 11.6556 | -0.62602 | 0.58477
|  | 7:19 | 11.6567 | -0.61385 | 0.58476
|  | 7:19 | 11.6578 | -0.5082 | 0.58476
|  | 7:19 | 11.6589 | -0.40255 | 0.58476
|  | 7:19 | 11.66 | -0.3128 | 0.58476
|  | 7:19 | 11.6611 | -0.23894 | 0.58475
|  | 7:19 | 11.6622 | -0.16508 | 0.58475
|  | 7:19 | 11.6633 | -0.13192 | 0.58475
|  | 7:19 | 11.6644 | -0.098767 | 0.58475
|  | 7:19 | 11.6656 | -0.076011 | 0.58475
|  | 7:19 | 11.6667 | -0.063653 | 0.58474
|  | 7:19 | 11.6678 | -0.051295 | 0.58474
|  | 7:20 | 11.6689 | -0.049098 | 0.58474
|  | 7:20 | 11.67 | -0.046901 | 0.58474
|  | 7:20 | 11.6711 | -0.047764 | 0.58473
|  | 7:20 | 11.6722 | -0.051687 | 0.58473
|  | 7:20 | 11.6733 | -0.05561 | 0.58473
|  | 7:20 | 11.6744 | -0.058509 | 0.58473
|  | 7:20 | 11.6756 | -0.061409 | 0.58472
|  | 7:20 | 11.6767 | -0.063271 | 0.58472
|  | 7:20 | 11.6778 | -0.064096 | 0.58472
|  | 7:20 | 11.6789 | -0.064921 | 0.58472
|  | 7:20 | 11.68 | -0.060995 | 0.58472
|  | 7:20 | 11.6811 | -0.057069 | 0.58471
|  | 7:20 | 11.6822 | -0.049778 | 0.58471
|  | 7:20 | 11.6833 | -0.03912 | 0.58471
|  | 7:20 | 11.6844 | -0.028462 | 0.58471
|  | 7:21 | 11.6856 | -0.012842 | 0.5847
|  | 7:21 | 11.6867 | 0.0027775 | 0.5847
|  | 7:21 | 11.6878 | 0.020036 | 0.5847
|  | 7:21 | 11.6889 | 0.038934 | 0.5847
|  | 7:21 | 11.69 | 0.057832 | 0.58469
|  | 7:21 | 11.6911 | 0.081885 | 0.58469
|  | 7:21 | 11.6922 | 0.10594 | 0.58469
|  | 7:21 | 11.6933 | 0.13145 | 0.58469
|  | 7:21 | 11.6944 | 0.15841 | 0.58469
|  | 7:21 | 11.6956 | 0.18538 | 0.58468
|  | 7:21 | 11.6967 | 0.21235 | 0.58468
|  | 7:21 | 11.6978 | 0.23931 | 0.58468
|  | 7:21 | 11.6989 | 0.26555 | 0.58468
|  | 7:21 | 11.7 | 0.29105 | 0.58467
|  | 7:21 | 11.7011 | 0.31656 | 0.58467
|  | 7:22 | 11.7022 | 0.33831 | 0.58467
|  | 7:22 | 11.7033 | 0.36005 | 0.58467
|  | 7:22 | 11.7044 | 0.38041 | 0.58466
|  | 7:22 | 11.7056 | 0.39939 | 0.58466
|  | 7:22 | 11.7067 | 0.41836 | 0.58466
|  | 7:22 | 11.7078 | 0.49252 | 0.58466
|  | 7:22 | 11.7089 | 0.56668 | 0.58466
|  | 7:22 | 11.71 | 0.6571 | 0.58465
|  | 7:22 | 11.7111 | 0.76377 | 0.58465
|  | 7:22 | 11.7122 | 0.87045 | 0.58465
|  | 7:22 | 11.7133 | 0.92227 | 0.58465
|  | 7:22 | 11.7144 | 0.97409 | 0.58464
|  | 7:22 | 11.7156 | 1 | 0.58464
|  | 7:22 | 11.7167 | 1 | 0.58464
|  | 7:22 | 11.7178 | 1 | 0.58464
|  | 7:23 | 11.7189 | 1 | 0.58463
|  | 7:23 | 11.72 | 1 | 0.58463
|  | 7:23 | 11.7211 | 1 | 0.58463
|  | 7:23 | 11.7222 | 1 | 0.58463
|  | 7:23 | 11.7233 | 1 | 0.58462
|  | 7:23 | 11.7244 | 1 | 0.58462
|  | 7:23 | 11.7256 | 1 | 0.58462
|  | 7:23 | 11.7267 | 0.98954 | 0.58462
|  | 7:23 | 11.7278 | 0.96861 | 0.58462
|  | 7:23 | 11.7289 | 0.94769 | 0.58461
|  | 7:23 | 11.73 | 0.92676 | 0.58461
|  | 7:23 | 11.7311 | 0.90583 | 0.58461
|  | 7:23 | 11.7322 | 0.8864 | 0.58461
|  | 7:23 | 11.7333 | 0.86847 | 0.5846
|  | 7:23 | 11.7344 | 0.85053 | 0.5846
|  | 7:24 | 11.7356 | 0.83122 | 0.5846
|  | 7:24 | 11.7367 | 0.81191 | 0.5846
|  | 7:24 | 11.7378 | 0.79135 | 0.58459
|  | 7:24 | 11.7389 | 0.76954 | 0.58459
|  | 7:24 | 11.74 | 0.74773 | 0.58459
|  | 7:24 | 11.7411 | 0.72292 | 0.58459
|  | 7:24 | 11.7422 | 0.69812 | 0.58459
|  | 7:24 | 11.7433 | 0.67131 | 0.58458
|  | 7:24 | 11.7444 | 0.64249 | 0.58458
|  | 7:24 | 11.7456 | 0.61367 | 0.58458
|  | 7:24 | 11.7467 | 0.57951 | 0.58458
|  | 7:24 | 11.7478 | 0.54534 | 0.58457
|  | 7:24 | 11.7489 | 0.50935 | 0.58457
|  | 7:24 | 11.75 | 0.47155 | 0.58457
|  | 7:24 | 11.7511 | 0.43375 | 0.58457
|  | 7:25 | 11.7522 | 0.39595 | 0.58456
|  | 7:25 | 11.7533 | 0.35815 | 0.58456
|  | 7:25 | 11.7544 | 0.31997 | 0.58456
|  | 7:25 | 11.7556 | 0.28142 | 0.58456
|  | 7:25 | 11.7567 | 0.24286 | 0.58456
|  | 7:25 | 11.7578 | 0.24479 | 0.58455
|  | 7:25 | 11.7589 | 0.24671 | 0.58455
|  | 7:25 | 11.76 | 0.25085 | 0.58455
|  | 7:25 | 11.7611 | 0.2572 | 0.58455
|  | 7:25 | 11.7622 | 0.26356 | 0.58454
|  | 7:25 | 11.7633 | 0.27313 | 0.58454
|  | 7:25 | 11.7644 | 0.28271 | 0.58454
|  | 7:25 | 11.7656 | 0.28495 | 0.58454
|  | 7:25 | 11.7667 | 0.27985 | 0.58453
|  | 7:25 | 11.7678 | 0.27475 | 0.58453
|  | 7:26 | 11.7689 | 0.26163 | 0.58453
|  | 7:26 | 11.77 | 0.24851 | 0.58453
|  | 7:26 | 11.7711 | 0.23428 | 0.58453
|  | 7:26 | 11.7722 | 0.21894 | 0.58452
|  | 7:26 | 11.7733 | 0.20359 | 0.58452
|  | 7:26 | 11.7744 | 0.18825 | 0.58452
|  | 7:26 | 11.7756 | 0.1729 | 0.58452
|  | 7:26 | 11.7767 | 0.1591 | 0.58451
|  | 7:26 | 11.7778 | 0.14684 | 0.58451
|  | 7:26 | 11.7789 | 0.13458 | 0.58451
|  | 7:26 | 11.78 | 0.12808 | 0.58451
|  | 7:26 | 11.7811 | 0.12157 | 0.5845
|  | 7:26 | 11.7822 | 0.11705 | 0.5845
|  | 7:26 | 11.7833 | 0.1145 | 0.5845
|  | 7:26 | 11.7844 | 0.11195 | 0.5845
|  | 7:27 | 11.7856 | 0.1094 | 0.5845
|  | 7:27 | 11.7867 | 0.10685 | 0.58449
|  | 7:27 | 11.7878 | 0.10092 | 0.58449
|  | 7:27 | 11.7889 | 0.091628 | 0.58449
|  | 7:27 | 11.79 | 0.082333 | 0.58449
|  | 7:27 | 11.7911 | 0.065356 | 0.58448
|  | 7:27 | 11.7922 | 0.04838 | 0.58448
|  | 7:27 | 11.7933 | 0.028627 | 0.58448
|  | 7:27 | 11.7944 | 0.0060996 | 0.58448
|  | 7:27 | 11.7956 | -0.016428 | 0.58447
|  | 7:27 | 11.7967 | -0.041192 | 0.58447
|  | 7:27 | 11.7978 | -0.065955 | 0.58447
|  | 7:27 | 11.7989 | -0.089502 | 0.58447
|  | 7:27 | 11.8 | -0.11183 | 0.58447
|  | 7:27 | 11.8011 | -0.13416 | 0.58446
|  | 7:28 | 11.8022 | -0.15307 | 0.58446
|  | 7:28 | 11.8033 | -0.17199 | 0.58446
|  | 7:28 | 11.8044 | -0.18978 | 0.58446
|  | 7:28 | 11.8056 | -0.20644 | 0.58445
|  | 7:28 | 11.8067 | -0.2231 | 0.58445
|  | 7:28 | 11.8078 | -0.307 | 0.58445
|  | 7:28 | 11.8089 | -0.39091 | 0.58445
|  | 7:28 | 11.81 | -0.48385 | 0.58444
|  | 7:28 | 11.8111 | -0.58583 | 0.58444
|  | 7:28 | 11.8122 | -0.68781 | 0.58444
|  | 7:28 | 11.8133 | -0.73052 | 0.58444
|  | 7:28 | 11.8144 | -0.77322 | 0.58444
|  | 7:28 | 11.8156 | -0.81093 | 0.58443
|  | 7:28 | 11.8167 | -0.84365 | 0.58443
|  | 7:28 | 11.8178 | -0.87637 | 0.58443
|  | 7:29 | 11.8189 | -0.88153 | 0.58443
|  | 7:29 | 11.82 | -0.88668 | 0.58442
|  | 7:29 | 11.8211 | -0.88243 | 0.58442
|  | 7:29 | 11.8222 | -0.86877 | 0.58442
|  | 7:29 | 11.8233 | -0.85511 | 0.58442
|  | 7:29 | 11.8244 | -0.82921 | 0.58441
|  | 7:29 | 11.8256 | -0.80332 | 0.58441
|  | 7:29 | 11.8267 | -0.77541 | 0.58441
|  | 7:29 | 11.8278 | -0.74551 | 0.58441
|  | 7:29 | 11.8289 | -0.7156 | 0.58441
|  | 7:29 | 11.83 | -0.6914 | 0.5844
|  | 7:29 | 11.8311 | -0.6672 | 0.5844
|  | 7:29 | 11.8322 | -0.64581 | 0.5844
|  | 7:29 | 11.8333 | -0.62723 | 0.5844
|  | 7:29 | 11.8344 | -0.60865 | 0.58439
|  | 7:30 | 11.8356 | -0.59007 | 0.58439
|  | 7:30 | 11.8367 | -0.57149 | 0.58439
|  | 7:30 | 11.8378 | -0.55114 | 0.58439
|  | 7:30 | 11.8389 | -0.52902 | 0.58438
|  | 7:30 | 11.84 | -0.5069 | 0.58438
|  | 7:30 | 11.8411 | -0.48242 | 0.58438
|  | 7:30 | 11.8422 | -0.45793 | 0.58438
|  | 7:30 | 11.8433 | -0.43491 | 0.58437
|  | 7:30 | 11.8444 | -0.41335 | 0.58437
|  | 7:30 | 11.8456 | -0.39178 | 0.58437
|  | 7:30 | 11.8467 | -0.375 | 0.58437
|  | 7:30 | 11.8478 | -0.35821 | 0.58437
|  | 7:30 | 11.8489 | -0.34235 | 0.58436
|  | 7:30 | 11.85 | -0.3274 | 0.58436
|  | 7:30 | 11.8511 | -0.31245 | 0.58436
|  | 7:31 | 11.8522 | -0.29852 | 0.58436
|  | 7:31 | 11.8533 | -0.28459 | 0.58435
|  | 7:31 | 11.8544 | -0.27125 | 0.58435
|  | 7:31 | 11.8556 | -0.25849 | 0.58435
|  | 7:31 | 11.8567 | -0.24574 | 0.58435
|  | 7:31 | 11.8578 | -0.20166 | 0.58434
|  | 7:31 | 11.8589 | -0.15758 | 0.58434
|  | 7:31 | 11.86 | -0.11851 | 0.58434
|  | 7:31 | 11.8611 | -0.084442 | 0.58434
|  | 7:31 | 11.8622 | -0.050377 | 0.58434
|  | 7:31 | 11.8633 | -0.022386 | 0.58433
|  | 7:31 | 11.8644 | 0.0056038 | 0.58433
|  | 7:31 | 11.8656 | 0.030365 | 0.58433
|  | 7:31 | 11.8667 | 0.051896 | 0.58433
|  | 7:31 | 11.8678 | 0.073427 | 0.58432
|  | 7:32 | 11.8689 | 0.080815 | 0.58432
|  | 7:32 | 11.87 | 0.088202 | 0.58432
|  | 7:32 | 11.8711 | 0.090438 | 0.58432
|  | 7:32 | 11.8722 | 0.087522 | 0.58431
|  | 7:32 | 11.8733 | 0.084606 | 0.58431
|  | 7:32 | 11.8744 | 0.094047 | 0.58431
|  | 7:32 | 11.8756 | 0.10349 | 0.58431
|  | 7:32 | 11.8767 | 0.11293 | 0.58431
|  | 7:32 | 11.8778 | 0.12237 | 0.5843
|  | 7:32 | 11.8789 | 0.13181 | 0.5843
|  | 7:32 | 11.88 | 0.14249 | 0.5843
|  | 7:32 | 11.8811 | 0.15317 | 0.5843
|  | 7:32 | 11.8822 | 0.15848 | 0.58429
|  | 7:32 | 11.8833 | 0.15841 | 0.58429
|  | 7:32 | 11.8844 | 0.15835 | 0.58429
|  | 7:33 | 11.8856 | 0.16065 | 0.58429
|  | 7:33 | 11.8867 | 0.16295 | 0.58428
|  | 7:33 | 11.8878 | 0.16769 | 0.58428
|  | 7:33 | 11.8889 | 0.17489 | 0.58428
|  | 7:33 | 11.89 | 0.18208 | 0.58428
|  | 7:33 | 11.8911 | 0.18927 | 0.58428
|  | 7:33 | 11.8922 | 0.19647 | 0.58427
|  | 7:33 | 11.8933 | 0.20156 | 0.58427
|  | 7:33 | 11.8944 | 0.20456 | 0.58427
|  | 7:33 | 11.8956 | 0.20755 | 0.58427
|  | 7:33 | 11.8967 | 0.20601 | 0.58426
|  | 7:33 | 11.8978 | 0.20447 | 0.58426
|  | 7:33 | 11.8989 | 0.20292 | 0.58426
|  | 7:33 | 11.9 | 0.20138 | 0.58426
|  | 7:33 | 11.9011 | 0.19984 | 0.58425
|  | 7:34 | 11.9022 | 0.19624 | 0.58425
|  | 7:34 | 11.9033 | 0.19265 | 0.58425
|  | 7:34 | 11.9044 | 0.18905 | 0.58425
|  | 7:34 | 11.9056 | 0.18546 | 0.58425
|  | 7:34 | 11.9067 | 0.18186 | 0.58424
|  | 7:34 | 11.9078 | 0.20655 | 0.58424
|  | 7:34 | 11.9089 | 0.23125 | 0.58424
|  | 7:34 | 11.91 | 0.27878 | 0.58424
|  | 7:34 | 11.9111 | 0.34917 | 0.58423
|  | 7:34 | 11.9122 | 0.41955 | 0.58423
|  | 7:34 | 11.9133 | 0.46532 | 0.58423
|  | 7:34 | 11.9144 | 0.51109 | 0.58423
|  | 7:34 | 11.9156 | 0.54332 | 0.58422
|  | 7:34 | 11.9167 | 0.562 | 0.58422
|  | 7:34 | 11.9178 | 0.58068 | 0.58422
|  | 7:35 | 11.9189 | 0.57944 | 0.58422
|  | 7:35 | 11.92 | 0.57819 | 0.58422
|  | 7:35 | 11.9211 | 0.56968 | 0.58421
|  | 7:35 | 11.9222 | 0.55389 | 0.58421
|  | 7:35 | 11.9233 | 0.53811 | 0.58421
|  | 7:35 | 11.9244 | 0.5166 | 0.58421
|  | 7:35 | 11.9256 | 0.49509 | 0.5842
|  | 7:35 | 11.9267 | 0.47205 | 0.5842
|  | 7:35 | 11.9278 | 0.44748 | 0.5842
|  | 7:35 | 11.9289 | 0.4229 | 0.5842
|  | 7:35 | 11.93 | 0.39623 | 0.58419
|  | 7:35 | 11.9311 | 0.36956 | 0.58419
|  | 7:35 | 11.9322 | 0.34288 | 0.58419
|  | 7:35 | 11.9333 | 0.31621 | 0.58419
|  | 7:35 | 11.9344 | 0.28954 | 0.58419
|  | 7:36 | 11.9356 | 0.26391 | 0.58418
|  | 7:36 | 11.9367 | 0.23828 | 0.58418
|  | 7:36 | 11.9378 | 0.21539 | 0.58418
|  | 7:36 | 11.9389 | 0.19522 | 0.58418
|  | 7:36 | 11.94 | 0.17506 | 0.58417
|  | 7:36 | 11.9411 | 0.16063 | 0.58417
|  | 7:36 | 11.9422 | 0.1462 | 0.58417
|  | 7:36 | 11.9433 | 0.13361 | 0.58417
|  | 7:36 | 11.9444 | 0.12286 | 0.58416
|  | 7:36 | 11.9456 | 0.11211 | 0.58416
|  | 7:36 | 11.9467 | 0.10243 | 0.58416
|  | 7:36 | 11.9478 | 0.092755 | 0.58416
|  | 7:36 | 11.9489 | 0.083078 | 0.58416
|  | 7:36 | 11.95 | 0.073402 | 0.58415
|  | 7:36 | 11.9511 | 0.063725 | 0.58415
|  | 7:37 | 11.9522 | 0.052588 | 0.58415
|  | 7:37 | 11.9533 | 0.041452 | 0.58415
|  | 7:37 | 11.9544 | 0.029734 | 0.58414
|  | 7:37 | 11.9556 | 0.017436 | 0.58414
|  | 7:37 | 11.9567 | 0.0051383 | 0.58414
|  | 7:37 | 11.9578 | -0.047343 | 0.58414
|  | 7:37 | 11.9589 | -0.099824 | 0.58413
|  | 7:37 | 11.96 | -0.16798 | 0.58413
|  | 7:37 | 11.9611 | -0.25181 | 0.58413
|  | 7:37 | 11.9622 | -0.33565 | 0.58413
|  | 7:37 | 11.9633 | -0.38735 | 0.58412
|  | 7:37 | 11.9644 | -0.43905 | 0.58412
|  | 7:37 | 11.9656 | -0.46146 | 0.58412
|  | 7:37 | 11.9667 | -0.4546 | 0.58412
|  | 7:37 | 11.9678 | -0.44773 | 0.58412
|  | 7:38 | 11.9689 | -0.4553 | 0.58411
|  | 7:38 | 11.97 | -0.46287 | 0.58411
|  | 7:38 | 11.9711 | -0.46802 | 0.58411
|  | 7:38 | 11.9722 | -0.47074 | 0.58411
|  | 7:38 | 11.9733 | -0.47346 | 0.5841
|  | 7:38 | 11.9744 | -0.46975 | 0.5841
|  | 7:38 | 11.9756 | -0.46605 | 0.5841
|  | 7:38 | 11.9767 | -0.45952 | 0.5841
|  | 7:38 | 11.9778 | -0.45017 | 0.58409
|  | 7:38 | 11.9789 | -0.44081 | 0.58409
|  | 7:38 | 11.98 | -0.43146 | 0.58409
|  | 7:38 | 11.9811 | -0.42211 | 0.58409
|  | 7:38 | 11.9822 | -0.41339 | 0.58409
|  | 7:38 | 11.9833 | -0.4053 | 0.58408
|  | 7:38 | 11.9844 | -0.39721 | 0.58408
|  | 7:39 | 11.9856 | -0.39273 | 0.58408
|  | 7:39 | 11.9867 | -0.38824 | 0.58408
|  | 7:39 | 11.9878 | -0.38311 | 0.58407
|  | 7:39 | 11.9889 | -0.37733 | 0.58407
|  | 7:39 | 11.99 | -0.37154 | 0.58407
|  | 7:39 | 11.9911 | -0.36405 | 0.58407
|  | 7:39 | 11.9922 | -0.35655 | 0.58406
|  | 7:39 | 11.9933 | -0.34838 | 0.58406
|  | 7:39 | 11.9944 | -0.33951 | 0.58406
|  | 7:39 | 11.9956 | -0.33065 | 0.58406
|  | 7:39 | 11.9967 | -0.31883 | 0.58406
|  | 7:39 | 11.9978 | -0.307 | 0.58405
|  | 7:39 | 11.9989 | -0.29517 | 0.58405
|  | 7:39 | 12 | -0.28334 | 0.58405
|  | 7:39 | 12.0011 | -0.27152 | 0.58405
|  | 7:40 | 12.0022 | -0.26255 | 0.58404
|  | 7:40 | 12.0033 | -0.25357 | 0.58404
|  | 7:40 | 12.0044 | -0.2446 | 0.58404
|  | 7:40 | 12.0056 | -0.23563 | 0.58404
|  | 7:40 | 12.0067 | -0.22666 | 0.58403
|  | 7:40 | 12.0078 | -0.16623 | 0.58403
|  | 7:40 | 12.0089 | -0.1058 | 0.58403
|  | 7:40 | 12.01 | -0.07499 | 0.58403
|  | 7:40 | 12.0111 | -0.073793 | 0.58403
|  | 7:40 | 12.0122 | -0.072596 | 0.58402
|  | 7:40 | 12.0133 | -0.090676 | 0.58402
|  | 7:40 | 12.0144 | -0.10876 | 0.58402
|  | 7:40 | 12.0156 | -0.11992 | 0.58402
|  | 7:40 | 12.0167 | -0.12415 | 0.58401
|  | 7:40 | 12.0178 | -0.12839 | 0.58401
|  | 7:41 | 12.0189 | -0.12273 | 0.58401
|  | 7:41 | 12.02 | -0.11707 | 0.58401
|  | 7:41 | 12.0211 | -0.10836 | 0.584
|  | 7:41 | 12.0222 | -0.096607 | 0.584
|  | 7:41 | 12.0233 | -0.084855 | 0.584
|  | 7:41 | 12.0244 | -0.073102 | 0.584
|  | 7:41 | 12.0256 | -0.06135 | 0.584
|  | 7:41 | 12.0267 | -0.048189 | 0.58399
|  | 7:41 | 12.0278 | -0.033621 | 0.58399
|  | 7:41 | 12.0289 | -0.019053 | 0.58399
|  | 7:41 | 12.03 | 0.00090471 | 0.58399
|  | 7:41 | 12.0311 | 0.020862 | 0.58398
|  | 7:41 | 12.0322 | 0.037016 | 0.58398
|  | 7:41 | 12.0333 | 0.049365 | 0.58398
|  | 7:41 | 12.0344 | 0.061714 | 0.58398
|  | 7:42 | 12.0356 | 0.066209 | 0.58397
|  | 7:42 | 12.0367 | 0.070704 | 0.58397
|  | 7:42 | 12.0378 | 0.084585 | 0.58397
|  | 7:42 | 12.0389 | 0.10785 | 0.58397
|  | 7:42 | 12.04 | 0.13112 | 0.58397
|  | 7:42 | 12.0411 | 0.15088 | 0.58396
|  | 7:42 | 12.0422 | 0.17065 | 0.58396
|  | 7:42 | 12.0433 | 0.18854 | 0.58396
|  | 7:42 | 12.0444 | 0.20455 | 0.58396
|  | 7:42 | 12.0456 | 0.22055 | 0.58395
|  | 7:42 | 12.0467 | 0.23139 | 0.58395
|  | 7:42 | 12.0478 | 0.24222 | 0.58395
|  | 7:42 | 12.0489 | 0.25077 | 0.58395
|  | 7:42 | 12.05 | 0.25703 | 0.58394
|  | 7:42 | 12.0511 | 0.2633 | 0.58394
|  | 7:43 | 12.0522 | 0.26956 | 0.58394
|  | 7:43 | 12.0533 | 0.27582 | 0.58394
|  | 7:43 | 12.0544 | 0.28117 | 0.58394
|  | 7:43 | 12.0556 | 0.28561 | 0.58393
|  | 7:43 | 12.0567 | 0.29004 | 0.58393
|  | 7:43 | 12.0578 | 0.43182 | 0.58393
|  | 7:43 | 12.0589 | 0.5736 | 0.58393
|  | 7:43 | 12.06 | 0.70993 | 0.58392
|  | 7:43 | 12.0611 | 0.8408 | 0.58392
|  | 7:43 | 12.0622 | 0.97168 | 0.58392
|  | 7:43 | 12.0633 | 0.98301 | 0.58392
|  | 7:43 | 12.0644 | 0.99434 | 0.58391
|  | 7:43 | 12.0656 | 1 | 0.58391
|  | 7:43 | 12.0667 | 1 | 0.58391
|  | 7:43 | 12.0678 | 1 | 0.58391
|  | 7:44 | 12.0689 | 1 | 0.58391
|  | 7:44 | 12.07 | 1 | 0.5839
|  | 7:44 | 12.0711 | 1 | 0.5839
|  | 7:44 | 12.0722 | 1 | 0.5839
|  | 7:44 | 12.0733 | 1 | 0.5839
|  | 7:44 | 12.0744 | 1 | 0.58389
|  | 7:44 | 12.0756 | 1 | 0.58389
|  | 7:44 | 12.0767 | 0.98087 | 0.58389
|  | 7:44 | 12.0778 | 0.9426 | 0.58389
|  | 7:44 | 12.0789 | 0.90433 | 0.58388
|  | 7:44 | 12.08 | 0.86072 | 0.58388
|  | 7:44 | 12.0811 | 0.81711 | 0.58388
|  | 7:44 | 12.0822 | 0.7735 | 0.58388
|  | 7:44 | 12.0833 | 0.72989 | 0.58387
|  | 7:44 | 12.0844 | 0.68628 | 0.58387
|  | 7:45 | 12.0856 | 0.64501 | 0.58387
|  | 7:45 | 12.0867 | 0.60374 | 0.58387
|  | 7:45 | 12.0878 | 0.56015 | 0.58387
|  | 7:45 | 12.0889 | 0.51423 | 0.58386
|  | 7:45 | 12.09 | 0.46832 | 0.58386
|  | 7:45 | 12.0911 | 0.415 | 0.58386
|  | 7:45 | 12.0922 | 0.36168 | 0.58386
|  | 7:45 | 12.0933 | 0.30515 | 0.58385
|  | 7:45 | 12.0944 | 0.24542 | 0.58385
|  | 7:45 | 12.0956 | 0.18569 | 0.58385
|  | 7:45 | 12.0967 | 0.1229 | 0.58385
|  | 7:45 | 12.0978 | 0.060104 | 0.58384
|  | 7:45 | 12.0989 | -0.0026872 | 0.58384
|  | 7:45 | 12.1 | -0.065478 | 0.58384
|  | 7:45 | 12.1011 | -0.12827 | 0.58384
|  | 7:46 | 12.1022 | -0.18722 | 0.58384
|  | 7:46 | 12.1033 | -0.24617 | 0.58383
|  | 7:46 | 12.1044 | -0.30138 | 0.58383
|  | 7:46 | 12.1056 | -0.35284 | 0.58383
|  | 7:46 | 12.1067 | -0.4043 | 0.58383
|  | 7:46 | 12.1078 | -0.50607 | 0.58382
|  | 7:46 | 12.1089 | -0.60784 | 0.58382
|  | 7:46 | 12.11 | -0.72698 | 0.58382
|  | 7:46 | 12.1111 | -0.86349 | 0.58382
|  | 7:46 | 12.1122 | -1 | 0.58381
|  | 7:46 | 12.1133 | -1 | 0.58381
|  | 7:46 | 12.1144 | -1 | 0.58381
|  | 7:46 | 12.1156 | -1 | 0.58381
|  | 7:46 | 12.1167 | -1 | 0.58381
|  | 7:46 | 12.1178 | -1 | 0.5838
|  | 7:47 | 12.1189 | -1 | 0.5838
|  | 7:47 | 12.12 | -1 | 0.5838
|  | 7:47 | 12.1211 | -1 | 0.5838
|  | 7:47 | 12.1222 | -1 | 0.58379
|  | 7:47 | 12.1233 | -1 | 0.58379
|  | 7:47 | 12.1244 | -1 | 0.58379
|  | 7:47 | 12.1256 | -1 | 0.58379
|  | 7:47 | 12.1267 | -1 | 0.58378
|  | 7:47 | 12.1278 | -1 | 0.58378
|  | 7:47 | 12.1289 | -1 | 0.58378
|  | 7:47 | 12.13 | -1 | 0.58378
|  | 7:47 | 12.1311 | -1 | 0.58378
|  | 7:47 | 12.1322 | -1 | 0.58377
|  | 7:47 | 12.1333 | -1 | 0.58377
|  | 7:47 | 12.1344 | -1 | 0.58377
|  | 7:48 | 12.1356 | -1 | 0.58377
|  | 7:48 | 12.1367 | -1 | 0.58376
|  | 7:48 | 12.1378 | -1 | 0.58376
|  | 7:48 | 12.1389 | -1 | 0.58376
|  | 7:48 | 12.14 | -1 | 0.58376
|  | 7:48 | 12.1411 | -1 | 0.58375
|  | 7:48 | 12.1422 | -1 | 0.58375
|  | 7:48 | 12.1433 | -1 | 0.58375
|  | 7:48 | 12.1444 | -1 | 0.58375
|  | 7:48 | 12.1456 | -1 | 0.58375
|  | 7:48 | 12.1467 | -1 | 0.58374
|  | 7:48 | 12.1478 | -1 | 0.58374
|  | 7:48 | 12.1489 | -0.97871 | 0.58374
|  | 7:48 | 12.15 | -0.93612 | 0.58374
|  | 7:48 | 12.1511 | -0.89353 | 0.58373
|  | 7:49 | 12.1522 | -0.82905 | 0.58373
|  | 7:49 | 12.1533 | -0.76457 | 0.58373
|  | 7:49 | 12.1544 | -0.70261 | 0.58373
|  | 7:49 | 12.1556 | -0.64317 | 0.58372
|  | 7:49 | 12.1567 | -0.58372 | 0.58372
|  | 7:49 | 12.1578 | -0.38857 | 0.58372
|  | 7:49 | 12.1589 | -0.19341 | 0.58372
|  | 7:49 | 12.16 | 0.014714 | 0.58372
|  | 7:49 | 12.1611 | 0.23582 | 0.58371
|  | 7:49 | 12.1622 | 0.45692 | 0.58371
|  | 7:49 | 12.1633 | 0.62776 | 0.58371
|  | 7:49 | 12.1644 | 0.79861 | 0.58371
|  | 7:49 | 12.1656 | 0.90723 | 0.5837
|  | 7:49 | 12.1667 | 0.95361 | 0.5837
|  | 7:49 | 12.1678 | 1 | 0.5837
|  | 7:50 | 12.1689 | 1 | 0.5837
|  | 7:50 | 12.17 | 1 | 0.58369
|  | 7:50 | 12.1711 | 1 | 0.58369
|  | 7:50 | 12.1722 | 1 | 0.58369
|  | 7:50 | 12.1733 | 1 | 0.58369
|  | 7:50 | 12.1744 | 1 | 0.58369
|  | 7:50 | 12.1756 | 1 | 0.58368
|  | 7:50 | 12.1767 | 0.98722 | 0.58368
|  | 7:50 | 12.1778 | 0.96167 | 0.58368
|  | 7:50 | 12.1789 | 0.93612 | 0.58368
|  | 7:50 | 12.18 | 0.90241 | 0.58367
|  | 7:50 | 12.1811 | 0.8687 | 0.58367
|  | 7:50 | 12.1822 | 0.83718 | 0.58367
|  | 7:50 | 12.1833 | 0.80786 | 0.58367
|  | 7:50 | 12.1844 | 0.77854 | 0.58366
|  | 7:51 | 12.1856 | 0.7506 | 0.58366
|  | 7:51 | 12.1867 | 0.72267 | 0.58366
|  | 7:51 | 12.1878 | 0.69439 | 0.58366
|  | 7:51 | 12.1889 | 0.66577 | 0.58366
|  | 7:51 | 12.19 | 0.63714 | 0.58365
|  | 7:51 | 12.1911 | 0.60852 | 0.58365
|  | 7:51 | 12.1922 | 0.57989 | 0.58365
|  | 7:51 | 12.1933 | 0.55235 | 0.58365
|  | 7:51 | 12.1944 | 0.52591 | 0.58364
|  | 7:51 | 12.1956 | 0.49946 | 0.58364
|  | 7:51 | 12.1967 | 0.47076 | 0.58364
|  | 7:51 | 12.1978 | 0.44206 | 0.58364
|  | 7:51 | 12.1989 | 0.41336 | 0.58363
|  | 7:51 | 12.2 | 0.38465 | 0.58363
|  | 7:51 | 12.2011 | 0.35595 | 0.58363
|  | 7:52 | 12.2022 | 0.32262 | 0.58363
|  | 7:52 | 12.2033 | 0.28929 | 0.58362
|  | 7:52 | 12.2044 | 0.25344 | 0.58362
|  | 7:52 | 12.2056 | 0.21507 | 0.58362
|  | 7:52 | 12.2067 | 0.1767 | 0.58362
|  | 7:52 | 12.2078 | 0.24757 | 0.58362
|  | 7:52 | 12.2089 | 0.31844 | 0.58361
|  | 7:52 | 12.21 | 0.37238 | 0.58361
|  | 7:52 | 12.2111 | 0.40939 | 0.58361
|  | 7:52 | 12.2122 | 0.4464 | 0.58361
|  | 7:52 | 12.2133 | 0.45446 | 0.5836
|  | 7:52 | 12.2144 | 0.46253 | 0.5836
|  | 7:52 | 12.2156 | 0.45695 | 0.5836
|  | 7:52 | 12.2167 | 0.43773 | 0.5836
|  | 7:52 | 12.2178 | 0.4185 | 0.58359
|  | 7:53 | 12.2189 | 0.38503 | 0.58359
|  | 7:53 | 12.22 | 0.35155 | 0.58359
|  | 7:53 | 12.2211 | 0.31506 | 0.58359
|  | 7:53 | 12.2222 | 0.27554 | 0.58359
|  | 7:53 | 12.2233 | 0.23602 | 0.58358
|  | 7:53 | 12.2244 | 0.19841 | 0.58358
|  | 7:53 | 12.2256 | 0.1608 | 0.58358
|  | 7:53 | 12.2267 | 0.12102 | 0.58358
|  | 7:53 | 12.2278 | 0.080516 | 0.58357
|  | 7:53 | 12.2289 | 0.041959 | 0.58357
|  | 7:53 | 12.23 | 0.0092477 | 0.58357
|  | 7:53 | 12.2311 | -0.023463 | 0.58357
|  | 7:53 | 12.2322 | -0.045612 | 0.58356
|  | 7:53 | 12.2333 | -0.06424 | 0.58356
|  | 7:53 | 12.2344 | -0.080306 | 0.58356
|  | 7:54 | 12.2356 | -0.088686 | 0.58356
|  | 7:54 | 12.2367 | -0.097065 | 0.58356
|  | 7:54 | 12.2378 | -0.10018 | 0.58355
|  | 7:54 | 12.2389 | -0.10153 | 0.58355
|  | 7:54 | 12.24 | -0.10262 | 0.58355
|  | 7:54 | 12.2411 | -0.10291 | 0.58355
|  | 7:54 | 12.2422 | -0.10321 | 0.58354
|  | 7:54 | 12.2433 | -0.10502 | 0.58354
|  | 7:54 | 12.2444 | -0.10735 | 0.58354
|  | 7:54 | 12.2456 | -0.10967 | 0.58354
|  | 7:54 | 12.2467 | -0.11199 | 0.58353
|  | 7:54 | 12.2478 | -0.11432 | 0.58353
|  | 7:54 | 12.2489 | -0.11297 | 0.58353
|  | 7:54 | 12.25 | -0.1104 | 0.58353
|  | 7:54 | 12.2511 | -0.10631 | 0.58353
|  | 7:55 | 12.2522 | -0.097698 | 0.58352
|  | 7:55 | 12.2533 | -0.089082 | 0.58352
|  | 7:55 | 12.2544 | -0.077714 | 0.58352
|  | 7:55 | 12.2556 | -0.065428 | 0.58352
|  | 7:55 | 12.2567 | -0.058191 | 0.58351
|  | 7:55 | 12.2578 | -0.066102 | 0.58351
|  | 7:55 | 12.2589 | -0.074013 | 0.58351
|  | 7:55 | 12.26 | -0.081924 | 0.58351
|  | 7:55 | 12.2611 | -0.089834 | 0.5835
|  | 7:55 | 12.2622 | -0.095008 | 0.5835
|  | 7:55 | 12.2633 | -0.091969 | 0.5835
|  | 7:55 | 12.2644 | -0.08893 | 0.5835
|  | 7:55 | 12.2656 | -0.082126 | 0.5835
|  | 7:55 | 12.2667 | -0.074067 | 0.58349
|  | 7:55 | 12.2678 | -0.062682 | 0.58349
|  | 7:56 | 12.2689 | -0.041321 | 0.58349
|  | 7:56 | 12.27 | -0.01996 | 0.58349
|  | 7:56 | 12.2711 | 0.00025003 | 0.58348
|  | 7:56 | 12.2722 | 0.020076 | 0.58348
|  | 7:56 | 12.2733 | 0.038548 | 0.58348
|  | 7:56 | 12.2744 | 0.052958 | 0.58348
|  | 7:56 | 12.2756 | 0.067367 | 0.58347
|  | 7:56 | 12.2767 | 0.075013 | 0.58347
|  | 7:56 | 12.2778 | 0.080404 | 0.58347
|  | 7:56 | 12.2789 | 0.083676 | 0.58347
|  | 7:56 | 12.28 | 0.080591 | 0.58347
|  | 7:56 | 12.2811 | 0.077506 | 0.58346
|  | 7:56 | 12.2822 | 0.073421 | 0.58346
|  | 7:56 | 12.2833 | 0.069002 | 0.58346
|  | 7:56 | 12.2844 | 0.065085 | 0.58346
|  | 7:57 | 12.2856 | 0.062669 | 0.58345
|  | 7:57 | 12.2867 | 0.060253 | 0.58345
|  | 7:57 | 12.2878 | 0.056999 | 0.58345
|  | 7:57 | 12.2889 | 0.053465 | 0.58345
|  | 7:57 | 12.29 | 0.049646 | 0.58344
|  | 7:57 | 12.2911 | 0.044971 | 0.58344
|  | 7:57 | 12.2922 | 0.040297 | 0.58344
|  | 7:57 | 12.2933 | 0.036583 | 0.58344
|  | 7:57 | 12.2944 | 0.033188 | 0.58344
|  | 7:57 | 12.2956 | 0.02929 | 0.58343
|  | 7:57 | 12.2967 | 0.02388 | 0.58343
|  | 7:57 | 12.2978 | 0.018471 | 0.58343
|  | 7:57 | 12.2989 | 0.013062 | 0.58343
|  | 7:57 | 12.3 | 0.0076527 | 0.58342
|  | 7:57 | 12.3011 | 0.003055 | 0.58342
|  | 7:58 | 12.3022 | 0.00089172 | 0.58342
|  | 7:58 | 12.3033 | -0.0012716 | 0.58342
|  | 7:58 | 12.3044 | 0.0015097 | 0.58341
|  | 7:58 | 12.3056 | 0.0059392 | 0.58341
|  | 7:58 | 12.3067 | 0.016653 | 0.58341
|  | 7:58 | 12.3078 | 0.04622 | 0.58341
|  | 7:58 | 12.3089 | 0.075788 | 0.58341
|  | 7:58 | 12.31 | 0.17855 | 0.5834
|  | 7:58 | 12.3111 | 0.30572 | 0.5834
|  | 7:58 | 12.3122 | 0.4228 | 0.5834
|  | 7:58 | 12.3133 | 0.50962 | 0.5834
|  | 7:58 | 12.3144 | 0.59644 | 0.58339
|  | 7:58 | 12.3156 | 0.64934 | 0.58339
|  | 7:58 | 12.3167 | 0.69095 | 0.58339
|  | 7:58 | 12.3178 | 0.72519 | 0.58339
|  | 7:59 | 12.3189 | 0.73735 | 0.58338
|  | 7:59 | 12.32 | 0.74951 | 0.58338
|  | 7:59 | 12.3211 | 0.74882 | 0.58338
|  | 7:59 | 12.3222 | 0.74385 | 0.58338
|  | 7:59 | 12.3233 | 0.73645 | 0.58337
|  | 7:59 | 12.3244 | 0.72177 | 0.58337
|  | 7:59 | 12.3256 | 0.70709 | 0.58337
|  | 7:59 | 12.3267 | 0.68715 | 0.58337
|  | 7:59 | 12.3278 | 0.66545 | 0.58337
|  | 7:59 | 12.3289 | 0.64111 | 0.58336
|  | 7:59 | 12.33 | 0.60884 | 0.58336
|  | 7:59 | 12.3311 | 0.57657 | 0.58336
|  | 7:59 | 12.3322 | 0.54106 | 0.58336
|  | 7:59 | 12.3333 | 0.50447 | 0.58335
|  | 7:59 | 12.3344 | 0.47098 | 0.58335
|  | 8:00 | 12.3356 | 0.44679 | 0.58335
|  | 8:00 | 12.3367 | 0.4226 | 0.58335
|  | 8:00 | 12.3378 | 0.40427 | 0.58334
|  | 8:00 | 12.3389 | 0.3879 | 0.58334
|  | 8:00 | 12.34 | 0.37223 | 0.58334
|  | 8:00 | 12.3411 | 0.35868 | 0.58334
|  | 8:00 | 12.3422 | 0.34514 | 0.58334
|  | 8:00 | 12.3433 | -0.14425 | 0.58333
|  | 8:00 | 12.3444 | -0.12965 | 0.58333
|  | 8:00 | 12.3456 | -0.13601 | 0.58333
|  | 8:00 | 12.3467 | -0.14238 | 0.58333
|  | 8:00 | 12.3478 | -0.14874 | 0.58332
|  | 8:00 | 12.3489 | -0.15511 | 0.58332
|  | 8:00 | 12.35 | -0.16147 | 0.58332
|  | 8:00 | 12.3511 | -0.15001 | 0.58332
|  | 8:01 | 12.3522 | -0.13855 | 0.58331
|  | 8:01 | 12.3533 | -0.11353 | 0.58331
|  | 8:01 | 12.3544 | -0.083978 | 0.58331
|  | 8:01 | 12.3556 | -0.05443 | 0.58331
|  | 8:01 | 12.3567 | -0.032121 | 0.58331
|  | 8:01 | 12.3578 | -0.0098121 | 0.5833
|  | 8:01 | 12.3589 | 0.0050135 | 0.5833
|  | 8:01 | 12.36 | 0.012356 | 0.5833
|  | 8:01 | 12.3611 | 0.019698 | 0.5833
|  | 8:01 | 12.3622 | 0.0056427 | 0.58329
|  | 8:01 | 12.3633 | -0.0084124 | 0.58329
|  | 8:01 | 12.3644 | -0.016135 | 0.58329
|  | 8:01 | 12.3656 | -0.017526 | 0.58329
|  | 8:01 | 12.3667 | -0.018917 | 0.58328
|  | 8:01 | 12.3678 | -0.0074832 | 0.58328
|  | 8:02 | 12.3689 | 0.0039504 | 0.58328
|  | 8:02 | 12.37 | 0.016937 | 0.58328
|  | 8:02 | 12.3711 | 0.030441 | 0.58328
|  | 8:02 | 12.3722 | 0.043946 | 0.58327
|  | 8:02 | 12.3733 | 0.065859 | 0.58327
|  | 8:02 | 12.3744 | 0.087772 | 0.58327
|  | 8:02 | 12.3756 | 0.10268 | 0.58327
|  | 8:02 | 12.3767 | 0.11526 | 0.58326
|  | 8:02 | 12.3778 | 0.12783 | 0.58326
|  | 8:02 | 12.3789 | 0.13629 | 0.58326
|  | 8:02 | 12.38 | 0.14474 | 0.58326
|  | 8:02 | 12.3811 | 0.1681 | 0.58325
|  | 8:02 | 12.3822 | 0.20635 | 0.58325
|  | 8:02 | 12.3833 | 0.2446 | 0.58325
|  | 8:02 | 12.3844 | 0.28614 | 0.58325
|  | 8:03 | 12.3856 | 0.32769 | 0.58325
|  | 8:03 | 12.3867 | 0.37177 | 0.58324
|  | 8:03 | 12.3878 | 0.41839 | 0.58324
|  | 8:03 | 12.3889 | 0.4646 | 0.58324
|  | 8:03 | 12.39 | 0.50955 | 0.58324
|  | 8:03 | 12.3911 | 0.55451 | 0.58323
|  | 8:03 | 12.3922 | 0.60292 | 0.58323
|  | 8:03 | 12.3933 | 0.65481 | 0.58323
|  | 8:03 | 12.3944 | 0.70669 | 0.58323
|  | 8:03 | 12.3956 | 0.72091 | 0.58322
|  | 8:03 | 12.3967 | 0.73513 | 0.58322
|  | 8:03 | 12.3978 | 0.73769 | 0.58322
|  | 8:03 | 12.3989 | 0.7286 | 0.58322
|  | 8:03 | 12.4 | 0.71951 | 0.58322
|  | 8:03 | 12.4011 | 0.69733 | 0.58321
|  | 8:04 | 12.4022 | 0.66208 | 0.58321
|  | 8:04 | 12.4033 | 0.6161 | 0.58321
|  | 8:04 | 12.4044 | 0.5594 | 0.58321
|  | 8:04 | 12.4056 | 0.50271 | 0.5832
|  | 8:04 | 12.4067 | 0.43484 | 0.5832
|  | 8:04 | 12.4078 | 0.36696 | 0.5832
|  | 8:04 | 12.4089 | 0.2997 | 0.5832
|  | 8:04 | 12.41 | 0.23306 | 0.58319
|  | 8:04 | 12.4111 | 0.16641 | 0.58319
|  | 8:04 | 12.4122 | 0.1269 | 0.58319
|  | 8:04 | 12.4133 | 0.087393 | 0.58319
|  | 8:04 | 12.4144 | 0.062752 | 0.58319
|  | 8:04 | 12.4156 | 0.052981 | 0.58318
|  | 8:04 | 12.4167 | 0.04321 | 0.58318
|  | 8:04 | 12.4178 | 0.031374 | 0.58318
|  | 8:05 | 12.4189 | 0.019538 | 0.58318
|  | 8:05 | 12.42 | 0.0014623 | 0.58317
|  | 8:05 | 12.4211 | -0.022852 | 0.58317
|  | 8:05 | 12.4222 | -0.047167 | 0.58317
|  | 8:05 | 12.4233 | -0.057435 | 0.58317
|  | 8:05 | 12.4244 | -0.067703 | 0.58316
|  | 8:05 | 12.4256 | -0.080728 | 0.58316
|  | 8:05 | 12.4267 | -0.096511 | 0.58316
|  | 8:05 | 12.4278 | -0.11229 | 0.58316
|  | 8:05 | 12.4289 | -0.14181 | 0.58316
|  | 8:05 | 12.43 | -0.17133 | 0.58315
|  | 8:05 | 12.4311 | -0.19213 | 0.58315
|  | 8:05 | 12.4322 | -0.21003 | 0.58315
|  | 8:05 | 12.4333 | -0.22794 | 0.58315
|  | 8:05 | 12.4344 | -0.25217 | 0.58314
|  | 8:06 | 12.4356 | -0.2764 | 0.58314
|  | 8:06 | 12.4367 | -0.29614 | 0.58314
|  | 8:06 | 12.4378 | -0.31141 | 0.58314
|  | 8:06 | 12.4389 | -0.32668 | 0.58313
|  | 8:06 | 12.44 | -0.33634 | 0.58313
|  | 8:06 | 12.4411 | -0.346 | 0.58313
|  | 8:06 | 12.4422 | -0.35417 | 0.58313
|  | 8:06 | 12.4433 | -0.36184 | 0.58312
|  | 8:06 | 12.4444 | -0.3695 | 0.58312
|  | 8:06 | 12.4456 | -0.38223 | 0.58312
|  | 8:06 | 12.4467 | -0.39495 | 0.58312
|  | 8:06 | 12.4478 | -0.41366 | 0.58312
|  | 8:06 | 12.4489 | -0.43836 | 0.58311
|  | 8:06 | 12.45 | -0.46307 | 0.58311
|  | 8:06 | 12.4511 | -0.49142 | 0.58311
|  | 8:07 | 12.4522 | -0.51976 | 0.58311
|  | 8:07 | 12.4533 | -0.53557 | 0.5831
|  | 8:07 | 12.4544 | -0.53885 | 0.5831
|  | 8:07 | 12.4556 | -0.54212 | 0.5831
|  | 8:07 | 12.4567 | -0.52588 | 0.5831
|  | 8:07 | 12.4578 | -0.50964 | 0.58309
|  | 8:07 | 12.4589 | -0.48512 | 0.58309
|  | 8:07 | 12.46 | -0.45232 | 0.58309
|  | 8:07 | 12.4611 | -0.41952 | 0.58309
|  | 8:07 | 12.4622 | -0.39896 | 0.58309
|  | 8:07 | 12.4633 | -0.3784 | 0.58308
|  | 8:07 | 12.4644 | -0.36069 | 0.58308
|  | 8:07 | 12.4656 | -0.34581 | 0.58308
|  | 8:07 | 12.4667 | -0.33094 | 0.58308
|  | 8:07 | 12.4678 | -0.31151 | 0.58307
|  | 8:08 | 12.4689 | -0.29208 | 0.58307
|  | 8:08 | 12.47 | -0.26401 | 0.58307
|  | 8:08 | 12.4711 | -0.2273 | 0.58307
|  | 8:08 | 12.4722 | -0.1906 | 0.58306
|  | 8:08 | 12.4733 | -0.15165 | 0.58306
|  | 8:08 | 12.4744 | -0.1127 | 0.58306
|  | 8:08 | 12.4756 | -0.070709 | 0.58306
|  | 8:08 | 12.4767 | -0.025681 | 0.58306
|  | 8:08 | 12.4778 | 0.019348 | 0.58305
|  | 8:08 | 12.4789 | 0.066808 | 0.58305
|  | 8:08 | 12.48 | 0.11427 | 0.58305
|  | 8:08 | 12.4811 | 0.14906 | 0.58305
|  | 8:08 | 12.4822 | 0.17962 | 0.58304
|  | 8:08 | 12.4833 | 0.21018 | 0.58304
|  | 8:08 | 12.4844 | 0.22659 | 0.58304
|  | 8:09 | 12.4856 | 0.243 | 0.58304
|  | 8:09 | 12.4867 | 0.26015 | 0.58303
|  | 8:09 | 12.4878 | 0.27804 | 0.58303
|  | 8:09 | 12.4889 | 0.29593 | 0.58303
|  | 8:09 | 12.49 | 0.34579 | 0.58303
|  | 8:09 | 12.4911 | 0.39566 | 0.58303
|  | 8:09 | 12.4922 | 0.41648 | 0.58302
|  | 8:09 | 12.4933 | 0.42761 | 0.58302
|  | 8:09 | 12.4944 | 0.43875 | 0.58302
|  | 8:09 | 12.4956 | 0.48488 | 0.58302
|  | 8:09 | 12.4967 | 0.53101 | 0.58301
|  | 8:09 | 12.4978 | 0.56431 | 0.58301
|  | 8:09 | 12.4989 | 0.58479 | 0.58301
|  | 8:09 | 12.5 | 0.60527 | 0.58301
|  | 8:09 | 12.5011 | 0.62576 | 0.583
|  | 8:10 | 12.5022 | 0.64624 | 0.583
|  | 8:10 | 12.5033 | 0.65386 | 0.583
|  | 8:10 | 12.5044 | 0.64862 | 0.583
|  | 8:10 | 12.5056 | 0.64337 | 0.583
|  | 8:10 | 12.5067 | 0.61858 | 0.58299
|  | 8:10 | 12.5078 | 0.59379 | 0.58299
|  | 8:10 | 12.5089 | 0.57945 | 0.58299
|  | 8:10 | 12.51 | 0.5686 | 0.58299
|  | 8:10 | 12.5111 | 0.55774 | 0.58298
|  | 8:10 | 12.5122 | 0.53406 | 0.58298
|  | 8:10 | 12.5133 | 0.51037 | 0.58298
|  | 8:10 | 12.5144 | 0.48484 | 0.58298
|  | 8:10 | 12.5156 | 0.45747 | 0.58297
|  | 8:10 | 12.5167 | 0.43009 | 0.58297
|  | 8:10 | 12.5178 | 0.40661 | 0.58297
|  | 8:11 | 12.5189 | 0.38313 | 0.58297
|  | 8:11 | 12.52 | 0.35578 | 0.58297
|  | 8:11 | 12.5211 | 0.32455 | 0.58296
|  | 8:11 | 12.5222 | 0.29332 | 0.58296
|  | 8:11 | 12.5233 | 0.24981 | 0.58296
|  | 8:11 | 12.5244 | 0.20629 | 0.58296
|  | 8:11 | 12.5256 | 0.16355 | 0.58295
|  | 8:11 | 12.5267 | 0.12106 | 0.58295
|  | 8:11 | 12.5278 | 0.078582 | 0.58295
|  | 8:11 | 12.5289 | 0.031632 | 0.58295
|  | 8:11 | 12.53 | -0.015318 | 0.58294
|  | 8:11 | 12.5311 | -0.035845 | 0.58294
|  | 8:11 | 12.5322 | -0.047565 | 0.58294
|  | 8:11 | 12.5333 | -0.059285 | 0.58294
|  | 8:11 | 12.5344 | -0.081598 | 0.58294
|  | 8:12 | 12.5356 | -0.10391 | 0.58293
|  | 8:12 | 12.5367 | -0.13323 | 0.58293
|  | 8:12 | 12.5378 | -0.16956 | 0.58293
|  | 8:12 | 12.5389 | -0.20588 | 0.58293
|  | 8:12 | 12.54 | -0.24997 | 0.58292
|  | 8:12 | 12.5411 | -0.29406 | 0.58292
|  | 8:12 | 12.5422 | -0.33234 | 0.58292
|  | 8:12 | 12.5433 | -0.3648 | 0.58292
|  | 8:12 | 12.5444 | -0.39726 | 0.58291
|  | 8:12 | 12.5456 | -0.42357 | 0.58291
|  | 8:12 | 12.5467 | -0.44987 | 0.58291
|  | 8:12 | 12.5478 | -0.46847 | 0.58291
|  | 8:12 | 12.5489 | -0.47935 | 0.58291
|  | 8:12 | 12.55 | -0.49023 | 0.5829
|  | 8:12 | 12.5511 | -0.5088 | 0.5829
|  | 8:13 | 12.5522 | -0.52738 | 0.5829
|  | 8:13 | 12.5533 | -0.54595 | 0.5829
|  | 8:13 | 12.5544 | -0.56452 | 0.58289
|  | 8:13 | 12.5556 | -0.58056 | 0.58289
|  | 8:13 | 12.5567 | -0.58899 | 0.58289
|  | 8:13 | 12.5578 | -0.59741 | 0.58289
|  | 8:13 | 12.5589 | -0.60464 | 0.58288
|  | 8:13 | 12.56 | -0.61068 | 0.58288
|  | 8:13 | 12.5611 | -0.61671 | 0.58288
|  | 8:13 | 12.5622 | -0.62274 | 0.58288
|  | 8:13 | 12.5633 | -0.62878 | 0.58287
|  | 8:13 | 12.5644 | -0.64556 | 0.58287
|  | 8:13 | 12.5656 | -0.67309 | 0.58287
|  | 8:13 | 12.5667 | -0.70062 | 0.58287
|  | 8:13 | 12.5678 | -0.7259 | 0.58287
|  | 8:14 | 12.5689 | -0.75118 | 0.58286
|  | 8:14 | 12.57 | -0.76373 | 0.58286
|  | 8:14 | 12.5711 | -0.76355 | 0.58286
|  | 8:14 | 12.5722 | -0.76336 | 0.58286
|  | 8:14 | 12.5733 | -0.74165 | 0.58285
|  | 8:14 | 12.5744 | -0.71995 | 0.58285
|  | 8:14 | 12.5756 | -0.69328 | 0.58285
|  | 8:14 | 12.5767 | -0.66166 | 0.58285
|  | 8:14 | 12.5778 | -0.63004 | 0.58284
|  | 8:14 | 12.5789 | -0.60123 | 0.58284
|  | 8:14 | 12.58 | -0.57243 | 0.58284
|  | 8:14 | 12.5811 | -0.55891 | 0.58284
|  | 8:14 | 12.5822 | -0.56068 | 0.58284
|  | 8:14 | 12.5833 | -0.56245 | 0.58283
|  | 8:14 | 12.5844 | -0.54412 | 0.58283
|  | 8:15 | 12.5856 | -0.52578 | 0.58283
|  | 8:15 | 12.5867 | -0.51626 | 0.58283
|  | 8:15 | 12.5878 | -0.51554 | 0.58282
|  | 8:15 | 12.5889 | -0.51483 | 0.58282
|  | 8:15 | 12.59 | -0.51658 | 0.58282
|  | 8:15 | 12.5911 | -0.51832 | 0.58282
|  | 8:15 | 12.5922 | -0.51742 | 0.58281
|  | 8:15 | 12.5933 | -0.51387 | 0.58281
|  | 8:15 | 12.5944 | -0.51032 | 0.58281
|  | 8:15 | 12.5956 | -0.49265 | 0.58281
|  | 8:15 | 12.5967 | -0.47497 | 0.58281
|  | 8:15 | 12.5978 | -0.4573 | 0.5828
|  | 8:15 | 12.5989 | -0.43963 | 0.5828
|  | 8:15 | 12.6 | -0.42195 | 0.5828
|  | 8:15 | 12.6011 | -0.40033 | 0.5828
|  | 8:16 | 12.6022 | -0.3787 | 0.58279
|  | 8:16 | 12.6033 | -0.35755 | 0.58279
|  | 8:16 | 12.6044 | -0.33687 | 0.58279
|  | 8:16 | 12.6056 | -0.31619 | 0.58279
|  | 8:16 | 12.6067 | -0.27026 | 0.58278
|  | 8:16 | 12.6078 | -0.22432 | 0.58278
|  | 8:16 | 12.6089 | -0.18079 | 0.58278
|  | 8:16 | 12.61 | -0.13806 | 0.58278
|  | 8:16 | 12.6111 | -0.095326 | 0.58278
|  | 8:16 | 12.6122 | -0.056057 | 0.58277
|  | 8:16 | 12.6133 | -0.016788 | 0.58277
|  | 8:16 | 12.6144 | 0.015659 | 0.58277
|  | 8:16 | 12.6156 | 0.041284 | 0.58277
|  | 8:16 | 12.6167 | 0.066908 | 0.58276
|  | 8:16 | 12.6178 | 0.067889 | 0.58276
|  | 8:17 | 12.6189 | 0.06887 | 0.58276
|  | 8:17 | 12.62 | 0.077604 | 0.58276
|  | 8:17 | 12.6211 | 0.094089 | 0.58275
|  | 8:17 | 12.6222 | 0.11057 | 0.58275
|  | 8:17 | 12.6233 | 0.13697 | 0.58275
|  | 8:17 | 12.6244 | 0.16337 | 0.58275
|  | 8:17 | 12.6256 | 0.18555 | 0.58275
|  | 8:17 | 12.6267 | 0.2035 | 0.58274
|  | 8:17 | 12.6278 | 0.22146 | 0.58274
|  | 8:17 | 12.6289 | 0.25483 | 0.58274
|  | 8:17 | 12.63 | 0.2882 | 0.58274
|  | 8:17 | 12.6311 | 0.30837 | 0.58273
|  | 8:17 | 12.6322 | 0.31533 | 0.58273
|  | 8:17 | 12.6333 | 0.32229 | 0.58273
|  | 8:17 | 12.6344 | 0.34371 | 0.58273
|  | 8:18 | 12.6356 | 0.36513 | 0.58272
|  | 8:18 | 12.6367 | 0.39495 | 0.58272
|  | 8:18 | 12.6378 | 0.43316 | 0.58272
|  | 8:18 | 12.6389 | 0.47137 | 0.58272
|  | 8:18 | 12.64 | 0.50421 | 0.58272
|  | 8:18 | 12.6411 | 0.53705 | 0.58271
|  | 8:18 | 12.6422 | 0.56677 | 0.58271
|  | 8:18 | 12.6433 | 0.59337 | 0.58271
|  | 8:18 | 12.6444 | 0.61996 | 0.58271
|  | 8:18 | 12.6456 | 0.63533 | 0.5827
|  | 8:18 | 12.6467 | 0.6507 | 0.5827
|  | 8:18 | 12.6478 | 0.67478 | 0.5827
|  | 8:18 | 12.6489 | 0.70756 | 0.5827
|  | 8:18 | 12.65 | 0.74033 | 0.58269
|  | 8:18 | 12.6511 | 0.7188 | 0.58269
|  | 8:19 | 12.6522 | 0.69726 | 0.58269
|  | 8:19 | 12.6533 | 0.69924 | 0.58269
|  | 8:19 | 12.6544 | 0.72473 | 0.58269
|  | 8:19 | 12.6556 | 0.75023 | 0.58268
|  | 8:19 | 12.6567 | 0.75876 | 0.58268
|  | 8:19 | 12.6578 | 0.76729 | 0.58268
|  | 8:19 | 12.6589 | 0.77299 | 0.58268
|  | 8:19 | 12.66 | 0.77774 | 0.58267
|  | 8:19 | 12.6611 | 0.7825 | 0.58267
|  | 8:19 | 12.6622 | 0.76741 | 0.58267
|  | 8:19 | 12.6633 | 0.75232 | 0.58267
|  | 8:19 | 12.6644 | 0.7296 | 0.58266
|  | 8:19 | 12.6656 | 0.69925 | 0.58266
|  | 8:19 | 12.6667 | 0.6689 | 0.58266
|  | 8:19 | 12.6678 | 0.62576 | 0.58266
|  | 8:20 | 12.6689 | 0.58261 | 0.58266
|  | 8:20 | 12.67 | 0.54949 | 0.58265
|  | 8:20 | 12.6711 | 0.5264 | 0.58265
|  | 8:20 | 12.6722 | 0.50331 | 0.58265
|  | 8:20 | 12.6733 | 0.4765 | 0.58265
|  | 8:20 | 12.6744 | 0.44968 | 0.58264
|  | 8:20 | 12.6756 | 0.4167 | 0.58264
|  | 8:20 | 12.6767 | 0.37755 | 0.58264
|  | 8:20 | 12.6778 | 0.33841 | 0.58264
|  | 8:20 | 12.6789 | 0.29386 | 0.58263
|  | 8:20 | 12.68 | 0.24932 | 0.58263
|  | 8:20 | 12.6811 | 0.21533 | 0.58263
|  | 8:20 | 12.6822 | 0.19189 | 0.58263
|  | 8:20 | 12.6833 | 0.16844 | 0.58262
|  | 8:20 | 12.6844 | 0.16499 | 0.58262
|  | 8:21 | 12.6856 | 0.16153 | 0.58262
|  | 8:21 | 12.6867 | 0.15986 | 0.58262
|  | 8:21 | 12.6878 | 0.15996 | 0.58262
|  | 8:21 | 12.6889 | 0.16005 | 0.58261
|  | 8:21 | 12.69 | 0.14796 | 0.58261
|  | 8:21 | 12.6911 | 0.13587 | 0.58261
|  | 8:21 | 12.6922 | 0.12378 | 0.58261
|  | 8:21 | 12.6933 | 0.1117 | 0.5826
|  | 8:21 | 12.6944 | 0.099605 | 0.5826
|  | 8:21 | 12.6956 | 0.079349 | 0.5826
|  | 8:21 | 12.6967 | 0.059092 | 0.5826
|  | 8:21 | 12.6978 | 0.042185 | 0.58259
|  | 8:21 | 12.6989 | 0.028626 | 0.58259
|  | 8:21 | 12.7 | 0.015067 | 0.58259
|  | 8:21 | 12.7011 | 0.017848 | 0.58259
|  | 8:22 | 12.7022 | 0.020629 | 0.58259
|  | 8:22 | 12.7033 | 0.02341 | 0.58258
|  | 8:22 | 12.7044 | 0.02619 | 0.58258
|  | 8:22 | 12.7056 | 0.028971 | 0.58258
|  | 8:22 | 12.7067 | 0.040168 | 0.58258
|  | 8:22 | 12.7078 | 0.051364 | 0.58257
|  | 8:22 | 12.7089 | 0.060832 | 0.58257
|  | 8:22 | 12.71 | 0.068571 | 0.58257
|  | 8:22 | 12.7111 | 0.076309 | 0.58257
|  | 8:22 | 12.7122 | 0.077437 | 0.58256
|  | 8:22 | 12.7133 | 0.078564 | 0.58256
|  | 8:22 | 12.7144 | 0.080322 | 0.58256
|  | 8:22 | 12.7156 | 0.082711 | 0.58256
|  | 8:22 | 12.7167 | 0.085099 | 0.58256
|  | 8:22 | 12.7178 | 0.082506 | 0.58255
|  | 8:23 | 12.7189 | 0.079913 | 0.58255
|  | 8:23 | 12.72 | 0.07732 | 0.58255
|  | 8:23 | 12.7211 | 0.074727 | 0.58255
|  | 8:23 | 12.7222 | 0.072134 | 0.58254
|  | 8:23 | 12.7233 | 0.05751 | 0.58254
|  | 8:23 | 12.7244 | 0.042887 | 0.58254
|  | 8:23 | 12.7256 | 0.041184 | 0.58254
|  | 8:23 | 12.7267 | 0.052402 | 0.58253
|  | 8:23 | 12.7278 | 0.063621 | 0.58253
|  | 8:23 | 12.7289 | 0.059618 | 0.58253
|  | 8:23 | 12.73 | 0.055615 | 0.58253
|  | 8:23 | 12.7311 | 0.053782 | 0.58253
|  | 8:23 | 12.7322 | 0.054119 | 0.58252
|  | 8:23 | 12.7333 | 0.054456 | 0.58252
|  | 8:23 | 12.7344 | 0.052728 | 0.58252
|  | 8:24 | 12.7356 | 0.051 | 0.58252
|  | 8:24 | 12.7367 | 0.053232 | 0.58251
|  | 8:24 | 12.7378 | 0.059425 | 0.58251
|  | 8:24 | 12.7389 | 0.065617 | 0.58251
|  | 8:24 | 12.74 | 0.089973 | 0.58251
|  | 8:24 | 12.7411 | 0.11433 | 0.5825
|  | 8:24 | 12.7422 | 0.13104 | 0.5825
|  | 8:24 | 12.7433 | 0.14009 | 0.5825
|  | 8:24 | 12.7444 | 0.14915 | 0.5825
|  | 8:24 | 12.7456 | 0.14294 | 0.5825
|  | 8:24 | 12.7467 | 0.13674 | 0.58249
|  | 8:24 | 12.7478 | 0.13903 | 0.58249
|  | 8:24 | 12.7489 | 0.14981 | 0.58249
|  | 8:24 | 12.75 | 0.16059 | 0.58249
|  | 8:24 | 12.7511 | 0.17604 | 0.58248
|  | 8:25 | 12.7522 | 0.1915 | 0.58248
|  | 8:25 | 12.7533 | 0.20614 | 0.58248
|  | 8:25 | 12.7544 | 0.21996 | 0.58248
|  | 8:25 | 12.7556 | 0.23378 | 0.58247
|  | 8:25 | 12.7567 | 0.22649 | 0.58247
|  | 8:25 | 12.7578 | 0.2192 | 0.58247
|  | 8:25 | 12.7589 | 0.2103 | 0.58247
|  | 8:25 | 12.76 | 0.1998 | 0.58247
|  | 8:25 | 12.7611 | 0.18929 | 0.58246
|  | 8:25 | 12.7622 | 0.16969 | 0.58246
|  | 8:25 | 12.7633 | 0.15009 | 0.58246
|  | 8:25 | 12.7644 | 0.12595 | 0.58246
|  | 8:25 | 12.7656 | 0.09729 | 0.58245
|  | 8:25 | 12.7667 | 0.068625 | 0.58245
|  | 8:25 | 12.7678 | 0.07361 | 0.58245
|  | 8:26 | 12.7689 | 0.078594 | 0.58245
|  | 8:26 | 12.77 | 0.072993 | 0.58244
|  | 8:26 | 12.7711 | 0.056805 | 0.58244
|  | 8:26 | 12.7722 | 0.040617 | 0.58244
|  | 8:26 | 12.7733 | 0.014632 | 0.58244
|  | 8:26 | 12.7744 | -0.011353 | 0.58244
|  | 8:26 | 12.7756 | -0.035552 | 0.58243
|  | 8:26 | 12.7767 | -0.057963 | 0.58243
|  | 8:26 | 12.7778 | -0.080375 | 0.58243
|  | 8:26 | 12.7789 | -0.065543 | 0.58243
|  | 8:26 | 12.78 | -0.050712 | 0.58242
|  | 8:26 | 12.7811 | -0.031837 | 0.58242
|  | 8:26 | 12.7822 | -0.0089175 | 0.58242
|  | 8:26 | 12.7833 | 0.014002 | 0.58242
|  | 8:26 | 12.7844 | 0.0028253 | 0.58241
|  | 8:27 | 12.7856 | -0.0083511 | 0.58241
|  | 8:27 | 12.7867 | -0.022928 | 0.58241
|  | 8:27 | 12.7878 | -0.040906 | 0.58241
|  | 8:27 | 12.7889 | -0.058884 | 0.58241
|  | 8:27 | 12.79 | -0.068746 | 0.5824
|  | 8:27 | 12.7911 | -0.078609 | 0.5824
|  | 8:27 | 12.7922 | -0.07932 | 0.5824
|  | 8:27 | 12.7933 | -0.076982 | 0.5824
|  | 8:27 | 12.7944 | -0.074643 | 0.58239
|  | 8:27 | 12.7956 | -0.075455 | 0.58239
|  | 8:27 | 12.7967 | -0.076267 | 0.58239
|  | 8:27 | 12.7978 | -0.073963 | 0.58239
|  | 8:27 | 12.7989 | -0.07062 | 0.58238
|  | 8:27 | 12.8 | -0.067277 | 0.58238
|  | 8:27 | 12.8011 | -0.087801 | 0.58238
|  | 8:28 | 12.8022 | -0.10832 | 0.58238
|  | 8:28 | 12.8033 | -0.11242 | 0.58237
|  | 8:28 | 12.8044 | -0.10009 | 0.58237
|  | 8:28 | 12.8056 | -0.087763 | 0.58237
|  | 8:28 | 12.8067 | -0.068639 | 0.58237
|  | 8:28 | 12.8078 | -0.049516 | 0.58237
|  | 8:28 | 12.8089 | -0.015747 | 0.58236
|  | 8:28 | 12.81 | 0.032669 | 0.58236
|  | 8:28 | 12.8111 | 0.076313 | 0.58236
|  | 8:28 | 12.8122 | 0.10565 | 0.58236
|  | 8:28 | 12.8133 | 0.13498 | 0.58235
|  | 8:28 | 12.8144 | 0.14996 | 0.58235
|  | 8:28 | 12.8156 | 0.1506 | 0.58235
|  | 8:28 | 12.8167 | 0.15123 | 0.58235
|  | 8:28 | 12.8178 | 0.15947 | 0.58234
|  | 8:29 | 12.8189 | 0.1677 | 0.58234
|  | 8:29 | 12.82 | 0.16361 | 0.58234
|  | 8:29 | 12.8211 | 0.14719 | 0.58234
|  | 8:29 | 12.8222 | 0.13078 | 0.58234
|  | 8:29 | 12.8233 | 0.11437 | 0.58233
|  | 8:29 | 12.8244 | 0.097961 | 0.58233
|  | 8:29 | 12.8256 | 0.077558 | 0.58233
|  | 8:29 | 12.8267 | 0.055824 | 0.58233
|  | 8:29 | 12.8278 | 0.034089 | 0.58232
|  | 8:29 | 12.8289 | 0.018564 | 0.58232
|  | 8:29 | 12.83 | 0.0030393 | 0.58232
|  | 8:29 | 12.8311 | -0.016027 | 0.58232
|  | 8:29 | 12.8322 | -0.038635 | 0.58231
|  | 8:29 | 12.8333 | -0.061243 | 0.58231
|  | 8:29 | 12.8344 | -0.068344 | 0.58231
|  | 8:30 | 12.8356 | -0.075445 | 0.58231
|  | 8:30 | 12.8367 | -0.080764 | 0.58231
|  | 8:30 | 12.8378 | -0.0843 | 0.5823
|  | 8:30 | 12.8389 | -0.087836 | 0.5823
|  | 8:30 | 12.84 | -0.08516 | 0.5823
|  | 8:30 | 12.8411 | -0.082483 | 0.5823
|  | 8:30 | 12.8422 | -0.079807 | 0.58229
|  | 8:30 | 12.8433 | -0.07713 | 0.58229
|  | 8:30 | 12.8444 | -0.074454 | 0.58229
|  | 8:30 | 12.8456 | -0.076025 | 0.58229
|  | 8:30 | 12.8467 | -0.077597 | 0.58228
|  | 8:30 | 12.8478 | -0.085439 | 0.58228
|  | 8:30 | 12.8489 | -0.09955 | 0.58228
|  | 8:30 | 12.85 | -0.11366 | 0.58228
|  | 8:30 | 12.8511 | -0.11441 | 0.58228
|  | 8:31 | 12.8522 | -0.11516 | 0.58227
|  | 8:31 | 12.8533 | -0.10971 | 0.58227
|  | 8:31 | 12.8544 | -0.09806 | 0.58227
|  | 8:31 | 12.8556 | -0.084509 | 0.58227
|  | 8:31 | 12.8567 | -0.065244 | 0.58226
|  | 8:31 | 12.8578 | -0.045979 | 0.58226
|  | 8:31 | 12.8589 | -0.029559 | 0.58226
|  | 8:31 | 12.86 | -0.015984 | 0.58226
|  | 8:31 | 12.8611 | -0.0024094 | 0.58225
|  | 8:31 | 12.8622 | 0.022238 | 0.58225
|  | 8:31 | 12.8633 | 0.046885 | 0.58225
|  | 8:31 | 12.8644 | 0.074314 | 0.58225
|  | 8:31 | 12.8656 | 0.10453 | 0.58225
|  | 8:31 | 12.8667 | 0.13474 | 0.58224
|  | 8:31 | 12.8678 | 0.15843 | 0.58224
|  | 8:32 | 12.8689 | 0.18212 | 0.58224
|  | 8:32 | 12.87 | 0.20365 | 0.58224
|  | 8:32 | 12.8711 | 0.22304 | 0.58223
|  | 8:32 | 12.8722 | 0.24243 | 0.58223
|  | 8:32 | 12.8733 | 0.2467 | 0.58223
|  | 8:32 | 12.8744 | 0.25097 | 0.58223
|  | 8:32 | 12.8756 | 0.25524 | 0.58222
|  | 8:32 | 12.8767 | 0.25952 | 0.58222
|  | 8:32 | 12.8778 | 0.26379 | 0.58222
|  | 8:32 | 12.8789 | 0.26806 | 0.58222
|  | 8:32 | 12.88 | 0.27234 | 0.58222
|  | 8:32 | 12.8811 | 0.27055 | 0.58221
|  | 8:32 | 12.8822 | 0.26272 | 0.58221
|  | 8:32 | 12.8833 | 0.25488 | 0.58221
|  | 8:32 | 12.8844 | 0.23498 | 0.58221
|  | 8:33 | 12.8856 | 0.21507 | 0.5822
|  | 8:33 | 12.8867 | 0.20228 | 0.5822
|  | 8:33 | 12.8878 | 0.1966 | 0.5822
|  | 8:33 | 12.8889 | 0.19092 | 0.5822
|  | 8:33 | 12.89 | 0.17374 | 0.58219
|  | 8:33 | 12.8911 | 0.15656 | 0.58219
|  | 8:33 | 12.8922 | 0.14737 | 0.58219
|  | 8:33 | 12.8933 | 0.14617 | 0.58219
|  | 8:33 | 12.8944 | 0.14096 | 0.58219
|  | 8:33 | 12.8956 | 0.1237 | 0.58218
|  | 8:33 | 12.8967 | 0.10644 | 0.58218
|  | 8:33 | 12.8978 | 0.091813 | 0.58218
|  | 8:33 | 12.8989 | 0.079822 | 0.58218
|  | 8:33 | 12.9 | 0.067831 | 0.58217
|  | 8:33 | 12.9011 | 0.075896 | 0.58217
|  | 8:34 | 12.9022 | 0.083961 | 0.58217
|  | 8:34 | 12.9033 | 0.086463 | 0.58217
|  | 8:34 | 12.9044 | 0.083403 | 0.58216
|  | 8:34 | 12.9056 | 0.080342 | 0.58216
|  | 8:34 | 12.9067 | 0.086139 | 0.58216
|  | 8:34 | 12.9078 | 0.091936 | 0.58216
|  | 8:34 | 12.9089 | 0.086932 | 0.58216
|  | 8:34 | 12.91 | 0.071129 | 0.58215
|  | 8:34 | 12.9111 | 0.055325 | 0.58215
|  | 8:34 | 12.9122 | 0.058039 | 0.58215
|  | 8:34 | 12.9133 | 0.060754 | 0.58215
|  | 8:34 | 12.9144 | 0.053289 | 0.58214
|  | 8:34 | 12.9156 | 0.035644 | 0.58214
|  | 8:34 | 12.9167 | 0.018 | 0.58214
|  | 8:34 | 12.9178 | -0.013065 | 0.58214
|  | 8:35 | 12.9189 | -0.04413 | 0.58213
|  | 8:35 | 12.92 | -0.070275 | 0.58213
|  | 8:35 | 12.9211 | -0.091499 | 0.58213
|  | 8:35 | 12.9222 | -0.11272 | 0.58213
|  | 8:35 | 12.9233 | -0.1153 | 0.58212
|  | 8:35 | 12.9244 | -0.11788 | 0.58212
|  | 8:35 | 12.9256 | -0.11783 | 0.58212
|  | 8:35 | 12.9267 | -0.11514 | 0.58212
|  | 8:35 | 12.9278 | -0.11272 | 0.58212
|  | 8:35 | 12.9289 | -0.11108 | 0.58211
|  | 8:35 | 12.93 | -0.10944 | 0.58211
|  | 8:35 | 12.9311 | -0.1078 | 0.58211
|  | 8:35 | 12.9322 | -0.12031 | 0.58211
|  | 8:35 | 12.9333 | -0.13283 | 0.5821
|  | 8:35 | 12.9344 | -0.13556 | 0.5821
|  | 8:36 | 12.9356 | -0.1383 | 0.5821
|  | 8:36 | 12.9367 | -0.13564 | 0.5821
|  | 8:36 | 12.9378 | -0.13119 | 0.58209
|  | 8:36 | 12.9389 | -0.1251 | 0.58209
|  | 8:36 | 12.94 | -0.11411 | 0.58209
|  | 8:36 | 12.9411 | -0.10312 | 0.58209
|  | 8:36 | 12.9422 | -0.087127 | 0.58209
|  | 8:36 | 12.9433 | -0.06947 | 0.58208
|  | 8:36 | 12.9444 | -0.057029 | 0.58208
|  | 8:36 | 12.9456 | -0.060235 | 0.58208
|  | 8:36 | 12.9467 | -0.06344 | 0.58208
|  | 8:36 | 12.9478 | -0.059529 | 0.58207
|  | 8:36 | 12.9489 | -0.053247 | 0.58207
|  | 8:36 | 12.95 | -0.048412 | 0.58207
|  | 8:36 | 12.9511 | -0.047923 | 0.58207
|  | 8:37 | 12.9522 | -0.047434 | 0.58206
|  | 8:37 | 12.9533 | -0.052124 | 0.58206
|  | 8:37 | 12.9544 | -0.05854 | 0.58206
|  | 8:37 | 12.9556 | -0.068618 | 0.58206
|  | 8:37 | 12.9567 | -0.08968 | 0.58206
|  | 8:37 | 12.9578 | -0.11074 | 0.58205
|  | 8:37 | 12.9589 | -0.12803 | 0.58205
|  | 8:37 | 12.96 | -0.14405 | 0.58205
|  | 8:37 | 12.9611 | -0.15587 | 0.58205
|  | 8:37 | 12.9622 | -0.15507 | 0.58204
|  | 8:37 | 12.9633 | -0.15427 | 0.58204
|  | 8:37 | 12.9644 | -0.1689 | 0.58204
|  | 8:37 | 12.9656 | -0.18867 | 0.58204
|  | 8:37 | 12.9667 | -0.19879 | 0.58203
|  | 8:37 | 12.9678 | -0.17995 | 0.58203
|  | 8:38 | 12.9689 | -0.16112 | 0.58203
|  | 8:38 | 12.97 | -0.14042 | 0.58203
|  | 8:38 | 12.9711 | -0.1191 | 0.58203
|  | 8:38 | 12.9722 | -0.087246 | 0.58202
|  | 8:38 | 12.9733 | -0.023777 | 0.58202
|  | 8:38 | 12.9744 | 0.039692 | 0.58202
|  | 8:38 | 12.9756 | 0.084628 | 0.58202
|  | 8:38 | 12.9767 | 0.12956 | 0.58201
|  | 8:38 | 12.9778 | 0.17372 | 0.58201
|  | 8:38 | 12.9789 | 0.21556 | 0.58201
|  | 8:38 | 12.98 | 0.2574 | 0.58201
|  | 8:38 | 12.9811 | 0.26371 | 0.582
|  | 8:38 | 12.9822 | 0.25818 | 0.582
|  | 8:38 | 12.9833 | 0.25264 | 0.582
|  | 8:38 | 12.9844 | 0.24711 | 0.582
|  | 8:39 | 12.9856 | 0.24157 | 0.582
|  | 8:39 | 12.9867 | 0.24404 | 0.58199
|  | 8:39 | 12.9878 | 0.24918 | 0.58199
|  | 8:39 | 12.9889 | 0.25653 | 0.58199
|  | 8:39 | 12.99 | 0.27053 | 0.58199
|  | 8:39 | 12.9911 | 0.28454 | 0.58198
|  | 8:39 | 12.9922 | 0.28643 | 0.58198
|  | 8:39 | 12.9933 | 0.28428 | 0.58198
|  | 8:39 | 12.9944 | 0.28637 | 0.58198
|  | 8:39 | 12.9956 | 0.30114 | 0.58197
|  | 8:39 | 12.9967 | 0.31592 | 0.58197
|  | 8:39 | 12.9978 | 0.32289 | 0.58197
|  | 8:39 | 12.9989 | 0.32726 | 0.58197
|  | 8:39 | 13 | 0.32399 | 0.58197
|  | 8:39 | 13.0011 | 0.3131 | 0.58196
|  | 8:40 | 13.0022 | 0.3022 | 0.58196
|  | 8:40 | 13.0033 | 0.28574 | 0.58196
|  | 8:40 | 13.0044 | 0.26742 | 0.58196
|  | 8:40 | 13.0056 | 0.24996 | 0.58195
|  | 8:40 | 13.0067 | 0.23337 | 0.58195
|  | 8:40 | 13.0078 | 0.21678 | 0.58195
|  | 8:40 | 13.0089 | 0.18735 | 0.58195
|  | 8:40 | 13.01 | 0.15364 | 0.58194
|  | 8:40 | 13.0111 | 0.13899 | 0.58194
|  | 8:40 | 13.0122 | 0.1434 | 0.58194
|  | 8:40 | 13.0133 | 0.1478 | 0.58194
|  | 8:40 | 13.0144 | 0.16101 | 0.58194
|  | 8:40 | 13.0156 | 0.17715 | 0.58193
|  | 8:40 | 13.0167 | 0.1784 | 0.58193
|  | 8:40 | 13.0178 | 0.16474 | 0.58193
|  | 8:41 | 13.0189 | 0.15109 | 0.58193
|  | 8:41 | 13.02 | 0.12306 | 0.58192
|  | 8:41 | 13.0211 | 0.090241 | 0.58192
|  | 8:41 | 13.0222 | 0.056587 | 0.58192
|  | 8:41 | 13.0233 | 0.020429 | 0.58192
|  | 8:41 | 13.0244 | -0.015729 | 0.58191
|  | 8:41 | 13.0256 | -0.042232 | 0.58191
|  | 8:41 | 13.0267 | -0.065516 | 0.58191
|  | 8:41 | 13.0278 | -0.087599 | 0.58191
|  | 8:41 | 13.0289 | -0.10608 | 0.58191
|  | 8:41 | 13.03 | -0.12456 | 0.5819
|  | 8:41 | 13.0311 | -0.13921 | 0.5819
|  | 8:41 | 13.0322 | -0.15259 | 0.5819
|  | 8:41 | 13.0333 | -0.16354 | 0.5819
|  | 8:41 | 13.0344 | -0.16719 | 0.58189
|  | 8:42 | 13.0356 | -0.17083 | 0.58189
|  | 8:42 | 13.0367 | -0.19514 | 0.58189
|  | 8:42 | 13.0378 | -0.22632 | 0.58189
|  | 8:42 | 13.0389 | -0.24783 | 0.58188
|  | 8:42 | 13.04 | -0.24028 | 0.58188
|  | 8:42 | 13.0411 | -0.23273 | 0.58188
|  | 8:42 | 13.0422 | -0.22091 | 0.58188
|  | 8:42 | 13.0433 | -0.20767 | 0.58187
|  | 8:42 | 13.0444 | -0.19169 | 0.58187
|  | 8:42 | 13.0456 | -0.1675 | 0.58187
|  | 8:42 | 13.0467 | -0.14331 | 0.58187
|  | 8:42 | 13.0478 | -0.12658 | 0.58187
|  | 8:42 | 13.0489 | -0.11235 | 0.58186
|  | 8:42 | 13.05 | -0.099041 | 0.58186
|  | 8:42 | 13.0511 | -0.088485 | 0.58186
|  | 8:43 | 13.0522 | -0.077929 | 0.58186
|  | 8:43 | 13.0533 | -0.06405 | 0.58185
|  | 8:43 | 13.0544 | -0.049063 | 0.58185
|  | 8:43 | 13.0556 | -0.032325 | 0.58185
|  | 8:43 | 13.0567 | -0.01033 | 0.58185
|  | 8:43 | 13.0578 | 0.011664 | 0.58184
|  | 8:43 | 13.0589 | 0.025807 | 0.58184
|  | 8:43 | 13.06 | 0.037333 | 0.58184
|  | 8:43 | 13.0611 | 0.049144 | 0.58184
|  | 8:43 | 13.0622 | 0.06181 | 0.58184
|  | 8:43 | 13.0633 | 0.074475 | 0.58183
|  | 8:43 | 13.0644 | 0.088406 | 0.58183
|  | 8:43 | 13.0656 | 0.10276 | 0.58183
|  | 8:43 | 13.0667 | 0.11637 | 0.58183
|  | 8:43 | 13.0678 | 0.12776 | 0.58182
|  | 8:44 | 13.0689 | 0.13916 | 0.58182
|  | 8:44 | 13.07 | 0.15333 | 0.58182
|  | 8:44 | 13.0711 | 0.16843 | 0.58182
|  | 8:44 | 13.0722 | 0.18226 | 0.58181
|  | 8:44 | 13.0733 | 0.19228 | 0.58181
|  | 8:44 | 13.0744 | 0.20229 | 0.58181
|  | 8:44 | 13.0756 | 0.18703 | 0.58181
|  | 8:44 | 13.0767 | 0.17176 | 0.58181
|  | 8:44 | 13.0778 | 0.15361 | 0.5818
|  | 8:44 | 13.0789 | 0.12677 | 0.5818
|  | 8:44 | 13.08 | 0.099932 | 0.5818
|  | 8:44 | 13.0811 | 0.080254 | 0.5818
|  | 8:44 | 13.0822 | 0.062962 | 0.58179
|  | 8:44 | 13.0833 | 0.049071 | 0.58179
|  | 8:44 | 13.0844 | 0.045383 | 0.58179
|  | 8:45 | 13.0856 | 0.041695 | 0.58179
|  | 8:45 | 13.0867 | 0.032198 | 0.58178
|  | 8:45 | 13.0878 | 0.020765 | 0.58178
|  | 8:45 | 13.0889 | 0.010218 | 0.58178
|  | 8:45 | 13.09 | 0.0023298 | 0.58178
|  | 8:45 | 13.0911 | -0.0055582 | 0.58178
|  | 8:45 | 13.0922 | -0.023576 | 0.58177
|  | 8:45 | 13.0933 | -0.04497 | 0.58177
|  | 8:45 | 13.0944 | -0.063236 | 0.58177
|  | 8:45 | 13.0956 | -0.072119 | 0.58177
|  | 8:45 | 13.0967 | -0.081002 | 0.58176
|  | 8:45 | 13.0978 | -0.091497 | 0.58176
|  | 8:45 | 13.0989 | -0.10253 | 0.58176
|  | 8:45 | 13.1 | -0.11184 | 0.58176
|  | 8:45 | 13.1011 | -0.11599 | 0.58175
|  | 8:46 | 13.1022 | -0.12014 | 0.58175
|  | 8:46 | 13.1033 | -0.12608 | 0.58175
|  | 8:46 | 13.1044 | -0.13383 | 0.58175
|  | 8:46 | 13.1056 | -0.14157 | 0.58175
|  | 8:46 | 13.1067 | -0.14002 | 0.58174
|  | 8:46 | 13.1078 | -0.13847 | 0.58174
|  | 8:46 | 13.1089 | -0.14396 | 0.58174
|  | 8:46 | 13.11 | -0.1565 | 0.58174
|  | 8:46 | 13.1111 | -0.16904 | 0.58173
|  | 8:46 | 13.1122 | -0.18405 | 0.58173
|  | 8:46 | 13.1133 | -0.19905 | 0.58173
|  | 8:46 | 13.1144 | -0.20539 | 0.58173
|  | 8:46 | 13.1156 | -0.20306 | 0.58172
|  | 8:46 | 13.1167 | -0.20073 | 0.58172
|  | 8:46 | 13.1178 | -0.17283 | 0.58172
|  | 8:47 | 13.1189 | -0.14493 | 0.58172
|  | 8:47 | 13.12 | -0.1155 | 0.58172
|  | 8:47 | 13.1211 | -0.084542 | 0.58171
|  | 8:47 | 13.1222 | -0.053583 | 0.58171
|  | 8:47 | 13.1233 | -0.01823 | 0.58171
|  | 8:47 | 13.1244 | 0.017124 | 0.58171
|  | 8:47 | 13.1256 | 0.042132 | 0.5817
|  | 8:47 | 13.1267 | 0.056796 | 0.5817
|  | 8:47 | 13.1278 | 0.07146 | 0.5817
|  | 8:47 | 13.1289 | 0.069582 | 0.5817
|  | 8:47 | 13.13 | 0.067705 | 0.58169
|  | 8:47 | 13.1311 | 0.068706 | 0.58169
|  | 8:47 | 13.1322 | 0.072586 | 0.58169
|  | 8:47 | 13.1333 | 0.076467 | 0.58169
|  | 8:47 | 13.1344 | 0.08665 | 0.58169
|  | 8:48 | 13.1356 | 0.096832 | 0.58168
|  | 8:48 | 13.1367 | 0.097433 | 0.58168
|  | 8:48 | 13.1378 | 0.088452 | 0.58168
|  | 8:48 | 13.1389 | 0.079471 | 0.58168
|  | 8:48 | 13.14 | 0.07049 | 0.58167
|  | 8:48 | 13.1411 | 0.061509 | 0.58167
|  | 8:48 | 13.1422 | 0.044761 | 0.58167
|  | 8:48 | 13.1433 | 0.020245 | 0.58167
|  | 8:48 | 13.1444 | -0.0042709 | 0.58166
|  | 8:48 | 13.1456 | -0.0071686 | 0.58166
|  | 8:48 | 13.1467 | -0.010066 | 0.58166
|  | 8:48 | 13.1478 | -0.015785 | 0.58166
|  | 8:48 | 13.1489 | -0.024325 | 0.58166
|  | 8:48 | 13.15 | -0.032865 | 0.58165
|  | 8:48 | 13.1511 | -0.041405 | 0.58165
|  | 8:49 | 13.1522 | -0.049945 | 0.58165
|  | 8:49 | 13.1533 | -0.061732 | 0.58165
|  | 8:49 | 13.1544 | -0.076764 | 0.58164
|  | 8:49 | 13.1556 | -0.091797 | 0.58164
|  | 8:49 | 13.1567 | -0.081949 | 0.58164
|  | 8:49 | 13.1578 | -0.072101 | 0.58164
|  | 8:49 | 13.1589 | -0.069993 | 0.58163
|  | 8:49 | 13.16 | -0.075625 | 0.58163
|  | 8:49 | 13.1611 | -0.081256 | 0.58163
|  | 8:49 | 13.1622 | -0.10398 | 0.58163
|  | 8:49 | 13.1633 | -0.12671 | 0.58162
|  | 8:49 | 13.1644 | -0.13424 | 0.58162
|  | 8:49 | 13.1656 | -0.13671 | 0.58162
|  | 8:49 | 13.1667 | -0.13917 | 0.58162
|  | 8:49 | 13.1678 | -0.13967 | 0.58162
|  | 8:50 | 13.1689 | -0.14016 | 0.58161
|  | 8:50 | 13.17 | -0.13967 | 0.58161
|  | 8:50 | 13.1711 | -0.1382 | 0.58161
|  | 8:50 | 13.1722 | -0.13672 | 0.58161
|  | 8:50 | 13.1733 | -0.13986 | 0.5816
|  | 8:50 | 13.1744 | -0.143 | 0.5816
|  | 8:50 | 13.1756 | -0.15783 | 0.5816
|  | 8:50 | 13.1767 | -0.18435 | 0.5816
|  | 8:50 | 13.1778 | -0.21088 | 0.58159
|  | 8:50 | 13.1789 | -0.23015 | 0.58159
|  | 8:50 | 13.18 | -0.24943 | 0.58159
|  | 8:50 | 13.1811 | -0.27026 | 0.58159
|  | 8:50 | 13.1822 | -0.29265 | 0.58159
|  | 8:50 | 13.1833 | -0.31503 | 0.58158
|  | 8:50 | 13.1844 | -0.32195 | 0.58158
|  | 8:51 | 13.1856 | -0.32886 | 0.58158
|  | 8:51 | 13.1867 | -0.34119 | 0.58158
|  | 8:51 | 13.1878 | -0.35894 | 0.58157
|  | 8:51 | 13.1889 | -0.37669 | 0.58157
|  | 8:51 | 13.19 | -0.40678 | 0.58157
|  | 8:51 | 13.1911 | -0.43687 | 0.58157
|  | 8:51 | 13.1922 | -0.47126 | 0.58156
|  | 8:51 | 13.1933 | -0.50996 | 0.58156
|  | 8:51 | 13.1944 | -0.54865 | 0.58156
|  | 8:51 | 13.1956 | -0.56956 | 0.58156
|  | 8:51 | 13.1967 | -0.59046 | 0.58156
|  | 8:51 | 13.1978 | -0.60099 | 0.58155
|  | 8:51 | 13.1989 | -0.60114 | 0.58155
|  | 8:51 | 13.2 | -0.60129 | 0.58155
|  | 8:51 | 13.2011 | -0.60725 | 0.58155
|  | 8:52 | 13.2022 | -0.6132 | 0.58154
|  | 8:52 | 13.2033 | -0.61495 | 0.58154
|  | 8:52 | 13.2044 | -0.6125 | 0.58154
|  | 8:52 | 13.2056 | -0.61004 | 0.58154
|  | 8:52 | 13.2067 | -0.60192 | 0.58153
|  | 8:52 | 13.2078 | -0.59379 | 0.58153
|  | 8:52 | 13.2089 | -0.57338 | 0.58153
|  | 8:52 | 13.21 | -0.54068 | 0.58153
|  | 8:52 | 13.2111 | -0.50798 | 0.58153
|  | 8:52 | 13.2122 | -0.44948 | 0.58152
|  | 8:52 | 13.2133 | -0.39097 | 0.58152
|  | 8:52 | 13.2144 | -0.34491 | 0.58152
|  | 8:52 | 13.2156 | -0.30298 | 0.58152
|  | 8:52 | 13.2167 | -0.26106 | 0.58151
|  | 8:52 | 13.2178 | -0.21372 | 0.58151
|  | 8:53 | 13.2189 | -0.16637 | 0.58151
|  | 8:53 | 13.22 | -0.13138 | 0.58151
|  | 8:53 | 13.2211 | -0.10875 | 0.5815
|  | 8:53 | 13.2222 | -0.086123 | 0.5815
|  | 8:53 | 13.2233 | -0.059309 | 0.5815
|  | 8:53 | 13.2244 | -0.032495 | 0.5815
|  | 8:53 | 13.2256 | -0.0085625 | 0.5815
|  | 8:53 | 13.2267 | 0.01441 | 0.58149
|  | 8:53 | 13.2278 | 0.037382 | 0.58149
|  | 8:53 | 13.2289 | 0.066252 | 0.58149
|  | 8:53 | 13.23 | 0.095122 | 0.58149
|  | 8:53 | 13.2311 | 0.10872 | 0.58148
|  | 8:53 | 13.2322 | 0.10704 | 0.58148
|  | 8:53 | 13.2333 | 0.10536 | 0.58148
|  | 8:53 | 13.2344 | 0.10089 | 0.58148
|  | 8:54 | 13.2356 | 0.088038 | 0.58147
|  | 8:54 | 13.2367 | 0.080428 | 0.58147
|  | 8:54 | 13.2378 | 0.078054 | 0.58147
|  | 8:54 | 13.2389 | 0.07568 | 0.58147
|  | 8:54 | 13.24 | 0.060873 | 0.58147
|  | 8:54 | 13.2411 | 0.046067 | 0.58146
|  | 8:54 | 13.2422 | 0.032489 | 0.58146
|  | 8:54 | 13.2433 | 0.02014 | 0.58146
|  | 8:54 | 13.2444 | 0.0077913 | 0.58146
|  | 8:54 | 13.2456 | 0.0089382 | 0.58145
|  | 8:54 | 13.2467 | 0.010085 | 0.58145
|  | 8:54 | 13.2478 | 0.017944 | 0.58145
|  | 8:54 | 13.2489 | 0.032514 | 0.58145
|  | 8:54 | 13.25 | 0.047085 | 0.58144
|  | 8:54 | 13.2511 | 0.076109 | 0.58144
|  | 8:55 | 13.2522 | 0.10513 | 0.58144
|  | 8:55 | 13.2533 | 0.13867 | 0.58144
|  | 8:55 | 13.2544 | 0.17371 | 0.58144
|  | 8:55 | 13.2556 | 0.20875 | 0.58143
|  | 8:55 | 13.2567 | 0.23334 | 0.58143
|  | 8:55 | 13.2578 | 0.25792 | 0.58143
|  | 8:55 | 13.2589 | 0.27615 | 0.58143
|  | 8:55 | 13.26 | 0.28804 | 0.58142
|  | 8:55 | 13.2611 | 0.29992 | 0.58142
|  | 8:55 | 13.2622 | 0.31798 | 0.58142
|  | 8:55 | 13.2633 | 0.33605 | 0.58142
|  | 8:55 | 13.2644 | 0.36385 | 0.58141
|  | 8:55 | 13.2656 | 0.40137 | 0.58141
|  | 8:55 | 13.2667 | 0.4389 | 0.58141
|  | 8:55 | 13.2678 | 0.47837 | 0.58141
|  | 8:56 | 13.2689 | 0.51784 | 0.58141
|  | 8:56 | 13.27 | 0.54605 | 0.5814
|  | 8:56 | 13.2711 | 0.57051 | 0.5814
|  | 8:56 | 13.2722 | 0.59043 | 0.5814
|  | 8:56 | 13.2733 | 0.59672 | 0.5814
|  | 8:56 | 13.2744 | 0.60301 | 0.58139
|  | 8:56 | 13.2756 | 0.61476 | 0.58139
|  | 8:56 | 13.2767 | 0.62833 | 0.58139
|  | 8:56 | 13.2778 | 0.63908 | 0.58139
|  | 8:56 | 13.2789 | 0.64134 | 0.58138
|  | 8:56 | 13.28 | 0.6436 | 0.58138
|  | 8:56 | 13.2811 | 0.64966 | 0.58138
|  | 8:56 | 13.2822 | 0.65699 | 0.58138
|  | 8:56 | 13.2833 | 0.66861 | 0.58137
|  | 8:56 | 13.2844 | 0.69311 | 0.58137
|  | 8:57 | 13.2856 | 0.71761 | 0.58137
|  | 8:57 | 13.2867 | 0.72431 | 0.58137
|  | 8:57 | 13.2878 | 0.72507 | 0.58137
|  | 8:57 | 13.2889 | 0.72324 | 0.58136
|  | 8:57 | 13.29 | 0.71361 | 0.58136
|  | 8:57 | 13.2911 | 0.70399 | 0.58136
|  | 8:57 | 13.2922 | 0.68391 | 0.58136
|  | 8:57 | 13.2933 | 0.66036 | 0.58135
|  | 8:57 | 13.2944 | 0.63042 | 0.58135
|  | 8:57 | 13.2956 | 0.58134 | 0.58135
|  | 8:57 | 13.2967 | 0.53226 | 0.58135
|  | 8:57 | 13.2978 | 0.48119 | 0.58134
|  | 8:57 | 13.2989 | 0.42944 | 0.58134
|  | 8:57 | 13.3 | 0.38903 | 0.58134
|  | 8:57 | 13.3011 | 0.35995 | 0.58134
|  | 8:58 | 13.3022 | 0.33088 | 0.58134
|  | 8:58 | 13.3033 | 0.2821 | 0.58133
|  | 8:58 | 13.3044 | 0.22676 | 0.58133
|  | 8:58 | 13.3056 | 0.17658 | 0.58133
|  | 8:58 | 13.3067 | 0.1419 | 0.58133
|  | 8:58 | 13.3078 | 0.10722 | 0.58132
|  | 8:58 | 13.3089 | 0.081901 | 0.58132
|  | 8:58 | 13.31 | 0.056586 | 0.58132
|  | 8:58 | 13.3111 | 0.030142 | 0.58132
|  | 8:58 | 13.3122 | 0.00031549 | 0.58131
|  | 8:58 | 13.3133 | -0.029511 | 0.58131
|  | 8:58 | 13.3144 | -0.058698 | 0.58131
|  | 8:58 | 13.3156 | -0.087671 | 0.58131
|  | 8:58 | 13.3167 | -0.11306 | 0.58131
|  | 8:58 | 13.3178 | -0.12771 | 0.5813
|  | 8:59 | 13.3189 | -0.14236 | 0.5813
|  | 8:59 | 13.32 | -0.16624 | 0.5813
|  | 8:59 | 13.3211 | -0.1932 | 0.5813
|  | 8:59 | 13.3222 | -0.22575 | 0.58129
|  | 8:59 | 13.3233 | -0.2751 | 0.58129
|  | 8:59 | 13.3244 | -0.32445 | 0.58129
|  | 8:59 | 13.3256 | -0.35449 | 0.58129
|  | 8:59 | 13.3267 | -0.37809 | 0.58128
|  | 8:59 | 13.3278 | -0.39723 | 0.58128
|  | 8:59 | 13.3289 | -0.40298 | 0.58128
|  | 8:59 | 13.33 | -0.40874 | 0.58128
|  | 8:59 | 13.3311 | -0.41121 | 0.58128
|  | 8:59 | 13.3322 | -0.41258 | 0.58127
|  | 8:59 | 13.3333 | -0.4191 | 0.58127
|  | 8:59 | 13.3344 | -0.44105 | 0.58127
|  | 9:00 | 13.3356 | -0.46301 | 0.58127
|  | 9:00 | 13.3367 | -0.4794 | 0.58126
|  | 9:00 | 13.3378 | -0.49394 | 0.58126
|  | 9:00 | 13.3389 | -0.50803 | 0.58126
|  | 9:00 | 13.34 | -0.52082 | 0.58126
|  | 9:00 | 13.3411 | -0.53361 | 0.58125
|  | 9:00 | 13.3422 | -0.57167 | 0.58125
|  | 9:00 | 13.3433 | -0.61817 | 0.58125
|  | 9:00 | 13.3444 | -0.65686 | 0.58125
|  | 9:00 | 13.3456 | -0.67212 | 0.58125
|  | 9:00 | 13.3467 | -0.68739 | 0.58124
|  | 9:00 | 13.3478 | -0.69862 | 0.58124
|  | 9:00 | 13.3489 | -0.7085 | 0.58124
|  | 9:00 | 13.35 | -0.7136 | 0.58124
|  | 9:00 | 13.3511 | -0.70432 | 0.58123
|  | 9:01 | 13.3522 | -0.69505 | 0.58123
|  | 9:01 | 13.3533 | -0.67207 | 0.58123
|  | 9:01 | 13.3544 | -0.64451 | 0.58123
|  | 9:01 | 13.3556 | -0.61836 | 0.58122
|  | 9:01 | 13.3567 | -0.59644 | 0.58122
|  | 9:01 | 13.3578 | -0.57451 | 0.58122
|  | 9:01 | 13.3589 | -0.55325 | 0.58122
|  | 9:01 | 13.36 | -0.53222 | 0.58122
|  | 9:01 | 13.3611 | -0.51696 | 0.58121
|  | 9:01 | 13.3622 | -0.51903 | 0.58121
|  | 9:01 | 13.3633 | -0.5211 | 0.58121
|  | 9:01 | 13.3644 | -0.52402 | 0.58121
|  | 9:01 | 13.3656 | -0.52724 | 0.5812
|  | 9:01 | 13.3667 | -0.52781 | 0.5812
|  | 9:01 | 13.3678 | -0.52046 | 0.5812
|  | 9:02 | 13.3689 | -0.51311 | 0.5812
|  | 9:02 | 13.37 | -0.49295 | 0.58119
|  | 9:02 | 13.3711 | -0.46852 | 0.58119
|  | 9:02 | 13.3722 | -0.44277 | 0.58119
|  | 9:02 | 13.3733 | -0.41302 | 0.58119
|  | 9:02 | 13.3744 | -0.38327 | 0.58119
|  | 9:02 | 13.3756 | -0.36219 | 0.58118
|  | 9:02 | 13.3767 | -0.34399 | 0.58118
|  | 9:02 | 13.3778 | -0.32331 | 0.58118
|  | 9:02 | 13.3789 | -0.29521 | 0.58118
|  | 9:02 | 13.38 | -0.26711 | 0.58117
|  | 9:02 | 13.3811 | -0.22818 | 0.58117
|  | 9:02 | 13.3822 | -0.18565 | 0.58117
|  | 9:02 | 13.3833 | -0.14681 | 0.58117
|  | 9:02 | 13.3844 | -0.11909 | 0.58116
|  | 9:03 | 13.3856 | -0.091362 | 0.58116
|  | 9:03 | 13.3867 | -0.063635 | 0.58116
|  | 9:03 | 13.3878 | -0.035909 | 0.58116
|  | 9:03 | 13.3889 | -0.010399 | 0.58116
|  | 9:03 | 13.39 | 0.008462 | 0.58115
|  | 9:03 | 13.3911 | 0.027323 | 0.58115
|  | 9:03 | 13.3922 | 0.034398 | 0.58115
|  | 9:03 | 13.3933 | 0.037546 | 0.58115
|  | 9:03 | 13.3944 | 0.043552 | 0.58114
|  | 9:03 | 13.3956 | 0.058133 | 0.58114
|  | 9:03 | 13.3967 | 0.072714 | 0.58114
|  | 9:03 | 13.3978 | 0.058027 | 0.58114
|  | 9:03 | 13.3989 | 0.033585 | 0.58113
|  | 9:03 | 13.4 | 0.0091424 | 0.58113
|  | 9:03 | 13.4011 | -0.0069915 | 0.58113
|  | 9:04 | 13.4022 | -0.014817 | 0.58113
|  | 9:04 | 13.4033 | -0.013008 | 0.58112
|  | 9:04 | 13.4044 | -0.0079873 | 0.58112
|  | 9:04 | 13.4056 | -0.0032145 | 0.58112
|  | 9:04 | 13.4067 | 0.00081442 | 0.58112
|  | 9:04 | 13.4078 | 0.0048433 | 0.58112
|  | 9:04 | 13.4089 | -0.011699 | 0.58111
|  | 9:04 | 13.41 | -0.035099 | 0.58111
|  | 9:04 | 13.4111 | -0.062149 | 0.58111
|  | 9:04 | 13.4122 | -0.10015 | 0.58111
|  | 9:04 | 13.4133 | -0.13814 | 0.5811
|  | 9:04 | 13.4144 | -0.15922 | 0.5811
|  | 9:04 | 13.4156 | -0.17466 | 0.5811
|  | 9:04 | 13.4167 | -0.18651 | 0.5811
|  | 9:04 | 13.4178 | -0.18759 | 0.58109
|  | 9:05 | 13.4189 | -0.18868 | 0.58109
|  | 9:05 | 13.42 | -0.16432 | 0.58109
|  | 9:05 | 13.4211 | -0.13147 | 0.58109
|  | 9:05 | 13.4222 | -0.097254 | 0.58109
|  | 9:05 | 13.4233 | -0.058911 | 0.58108
|  | 9:05 | 13.4244 | -0.020569 | 0.58108
|  | 9:05 | 13.4256 | 0.017096 | 0.58108
|  | 9:05 | 13.4267 | 0.054534 | 0.58108
|  | 9:05 | 13.4278 | 0.085579 | 0.58107
|  | 9:05 | 13.4289 | 0.097447 | 0.58107
|  | 9:05 | 13.43 | 0.10931 | 0.58107
|  | 9:05 | 13.4311 | 0.11074 | 0.58107
|  | 9:05 | 13.4322 | 0.10868 | 0.58106
|  | 9:05 | 13.4333 | 0.10522 | 0.58106
|  | 9:05 | 13.4344 | 0.097578 | 0.58106
|  | 9:06 | 13.4356 | 0.089932 | 0.58106
|  | 9:06 | 13.4367 | 0.073569 | 0.58106
|  | 9:06 | 13.4378 | 0.048491 | 0.58105
|  | 9:06 | 13.4389 | 0.023412 | 0.58105
|  | 9:06 | 13.44 | 0.0095454 | 0.58105
|  | 9:06 | 13.4411 | -0.0043213 | 0.58105
|  | 9:06 | 13.4422 | -0.0022857 | 0.58104
|  | 9:06 | 13.4433 | 0.015652 | 0.58104
|  | 9:06 | 13.4444 | 0.03359 | 0.58104
|  | 9:06 | 13.4456 | 0.10038 | 0.58104
|  | 9:06 | 13.4467 | 0.16717 | 0.58103
|  | 9:06 | 13.4478 | 0.23184 | 0.58103
|  | 9:06 | 13.4489 | 0.29437 | 0.58103
|  | 9:06 | 13.45 | 0.35691 | 0.58103
|  | 9:06 | 13.4511 | 0.38203 | 0.58103
|  | 9:07 | 13.4522 | 0.40715 | 0.58102
|  | 9:07 | 13.4533 | 0.43669 | 0.58102
|  | 9:07 | 13.4544 | 0.47067 | 0.58102
|  | 9:07 | 13.4556 | 0.50464 | 0.58102
|  | 9:07 | 13.4567 | 0.51512 | 0.58101
|  | 9:07 | 13.4578 | 0.52559 | 0.58101
|  | 9:07 | 13.4589 | 0.54013 | 0.58101
|  | 9:07 | 13.46 | 0.55874 | 0.58101
|  | 9:07 | 13.4611 | 0.57735 | 0.581
|  | 9:07 | 13.4622 | 0.57414 | 0.581
|  | 9:07 | 13.4633 | 0.57092 | 0.581
|  | 9:07 | 13.4644 | 0.57038 | 0.581
|  | 9:07 | 13.4656 | 0.57251 | 0.581
|  | 9:07 | 13.4667 | 0.57464 | 0.58099
|  | 9:07 | 13.4678 | 0.57446 | 0.58099
|  | 9:08 | 13.4689 | 0.57428 | 0.58099
|  | 9:08 | 13.47 | 0.56794 | 0.58099
|  | 9:08 | 13.4711 | 0.55544 | 0.58098
|  | 9:08 | 13.4722 | 0.54294 | 0.58098
|  | 9:08 | 13.4733 | 0.53362 | 0.58098
|  | 9:08 | 13.4744 | 0.52431 | 0.58098
|  | 9:08 | 13.4756 | 0.51346 | 0.58097
|  | 9:08 | 13.4767 | 0.50109 | 0.58097
|  | 9:08 | 13.4778 | 0.48871 | 0.58097
|  | 9:08 | 13.4789 | 0.46532 | 0.58097
|  | 9:08 | 13.48 | 0.44193 | 0.58097
|  | 9:08 | 13.4811 | 0.41736 | 0.58096
|  | 9:08 | 13.4822 | 0.39241 | 0.58096
|  | 9:08 | 13.4833 | 0.36745 | 0.58096
|  | 9:08 | 13.4844 | 0.32955 | 0.58096
|  | 9:09 | 13.4856 | 0.29165 | 0.58095
|  | 9:09 | 13.4867 | 0.25312 | 0.58095
|  | 9:09 | 13.4878 | 0.21396 | 0.58095
|  | 9:09 | 13.4889 | 0.1748 | 0.58095
|  | 9:09 | 13.49 | 0.11481 | 0.58094
|  | 9:09 | 13.4911 | 0.054818 | 0.58094
|  | 9:09 | 13.4922 | -0.0065868 | 0.58094
|  | 9:09 | 13.4933 | -0.068462 | 0.58094
|  | 9:09 | 13.4944 | -0.13034 | 0.58094
|  | 9:09 | 13.4956 | -0.17611 | 0.58093
|  | 9:09 | 13.4967 | -0.22189 | 0.58093
|  | 9:09 | 13.4978 | -0.26715 | 0.58093
|  | 9:09 | 13.4989 | -0.3119 | 0.58093
|  | 9:09 | 13.5 | -0.35665 | 0.58092
|  | 9:09 | 13.5011 | -0.39577 | 0.58092
|  | 9:10 | 13.5022 | -0.43489 | 0.58092
|  | 9:10 | 13.5033 | -0.45765 | 0.58092
|  | 9:10 | 13.5044 | -0.46406 | 0.58091
|  | 9:10 | 13.5056 | -0.47047 | 0.58091
|  | 9:10 | 13.5067 | -0.45239 | 0.58091
|  | 9:10 | 13.5078 | -0.4343 | 0.58091
|  | 9:10 | 13.5089 | -0.42879 | 0.58091
|  | 9:10 | 13.51 | -0.43588 | 0.5809
|  | 9:10 | 13.5111 | -0.44296 | 0.5809
|  | 9:10 | 13.5122 | -0.44646 | 0.5809
|  | 9:10 | 13.5133 | -0.44997 | 0.5809
|  | 9:10 | 13.5144 | -0.44712 | 0.58089
|  | 9:10 | 13.5156 | -0.43794 | 0.58089
|  | 9:10 | 13.5167 | -0.42875 | 0.58089
|  | 9:10 | 13.5178 | -0.42518 | 0.58089
|  | 9:11 | 13.5189 | -0.42161 | 0.58088
|  | 9:11 | 13.52 | -0.42556 | 0.58088
|  | 9:11 | 13.5211 | -0.43704 | 0.58088
|  | 9:11 | 13.5222 | -0.44852 | 0.58088
|  | 9:11 | 13.5233 | -0.44164 | 0.58087
|  | 9:11 | 13.5244 | -0.43475 | 0.58087
|  | 9:11 | 13.5256 | -0.42925 | 0.58087
|  | 9:11 | 13.5267 | -0.42513 | 0.58087
|  | 9:11 | 13.5278 | -0.421 | 0.58087
|  | 9:11 | 13.5289 | -0.40086 | 0.58086
|  | 9:11 | 13.53 | -0.38072 | 0.58086
|  | 9:11 | 13.5311 | -0.36457 | 0.58086
|  | 9:11 | 13.5322 | -0.35242 | 0.58086
|  | 9:11 | 13.5333 | -0.34187 | 0.58085
|  | 9:11 | 13.5344 | -0.33616 | 0.58085
|  | 9:12 | 13.5356 | -0.33044 | 0.58085
|  | 9:12 | 13.5367 | -0.31632 | 0.58085
|  | 9:12 | 13.5378 | -0.29381 | 0.58084
|  | 9:12 | 13.5389 | -0.2713 | 0.58084
|  | 9:12 | 13.54 | -0.25262 | 0.58084
|  | 9:12 | 13.5411 | -0.23394 | 0.58084
|  | 9:12 | 13.5422 | -0.21066 | 0.58084
|  | 9:12 | 13.5433 | -0.18278 | 0.58083
|  | 9:12 | 13.5444 | -0.1549 | 0.58083
|  | 9:12 | 13.5456 | -0.1598 | 0.58083
|  | 9:12 | 13.5467 | -0.1647 | 0.58083
|  | 9:12 | 13.5478 | -0.16862 | 0.58082
|  | 9:12 | 13.5489 | -0.17156 | 0.58082
|  | 9:12 | 13.55 | -0.17451 | 0.58082
|  | 9:12 | 13.5511 | -0.16854 | 0.58082
|  | 9:13 | 13.5522 | -0.16258 | 0.58081
|  | 9:13 | 13.5533 | -0.16124 | 0.58081
|  | 9:13 | 13.5544 | -0.16454 | 0.58081
|  | 9:13 | 13.5556 | -0.16783 | 0.58081
|  | 9:13 | 13.5567 | -0.15843 | 0.58081
|  | 9:13 | 13.5578 | -0.14903 | 0.5808
|  | 9:13 | 13.5589 | -0.12965 | 0.5808
|  | 9:13 | 13.56 | -0.10029 | 0.5808
|  | 9:13 | 13.5611 | -0.070943 | 0.5808
|  | 9:13 | 13.5622 | -0.066805 | 0.58079
|  | 9:13 | 13.5633 | -0.062667 | 0.58079
|  | 9:13 | 13.5644 | -0.054492 | 0.58079
|  | 9:13 | 13.5656 | -0.042281 | 0.58079
|  | 9:13 | 13.5667 | -0.030069 | 0.58078
|  | 9:13 | 13.5678 | -0.017858 | 0.58078
|  | 9:14 | 13.5689 | 0.0074794 | 0.58078
|  | 9:14 | 13.57 | 0.030449 | 0.58078
|  | 9:14 | 13.5711 | 0.046317 | 0.58078
|  | 9:14 | 13.5722 | 0.062185 | 0.58077
|  | 9:14 | 13.5733 | 0.082672 | 0.58077
|  | 9:14 | 13.5744 | 0.10316 | 0.58077
|  | 9:14 | 13.5756 | 0.12318 | 0.58077
|  | 9:14 | 13.5767 | 0.14273 | 0.58076
|  | 9:14 | 13.5778 | 0.16229 | 0.58076
|  | 9:14 | 13.5789 | 0.17597 | 0.58076
|  | 9:14 | 13.58 | 0.18965 | 0.58076
|  | 9:14 | 13.5811 | 0.21106 | 0.58075
|  | 9:14 | 13.5822 | 0.24018 | 0.58075
|  | 9:14 | 13.5833 | 0.2693 | 0.58075
|  | 9:14 | 13.5844 | 0.28985 | 0.58075
|  | 9:15 | 13.5856 | 0.3104 | 0.58075
|  | 9:15 | 13.5867 | 0.32411 | 0.58074
|  | 9:15 | 13.5878 | 0.33098 | 0.58074
|  | 9:15 | 13.5889 | 0.33785 | 0.58074
|  | 9:15 | 13.59 | 0.3406 | 0.58074
|  | 9:15 | 13.5911 | 0.34335 | 0.58073
|  | 9:15 | 13.5922 | 0.34433 | 0.58073
|  | 9:15 | 13.5933 | 0.34356 | 0.58073
|  | 9:15 | 13.5944 | 0.34278 | 0.58073
|  | 9:15 | 13.5956 | 0.3594 | 0.58072
|  | 9:15 | 13.5967 | 0.37602 | 0.58072
|  | 9:15 | 13.5978 | 0.39263 | 0.58072
|  | 9:15 | 13.5989 | 0.40925 | 0.58072
|  | 9:15 | 13.6 | 0.42587 | 0.58072
|  | 9:15 | 13.6011 | 0.4182 | 0.58071
|  | 9:16 | 13.6022 | 0.41053 | 0.58071
|  | 9:16 | 13.6033 | 0.39842 | 0.58071
|  | 9:16 | 13.6044 | 0.38187 | 0.58071
|  | 9:16 | 13.6056 | 0.36532 | 0.5807
|  | 9:16 | 13.6067 | 0.33087 | 0.5807
|  | 9:16 | 13.6078 | 0.29642 | 0.5807
|  | 9:16 | 13.6089 | 0.28083 | 0.5807
|  | 9:16 | 13.61 | 0.28412 | 0.58069
|  | 9:16 | 13.6111 | 0.2874 | 0.58069
|  | 9:16 | 13.6122 | 0.2724 | 0.58069
|  | 9:16 | 13.6133 | 0.2574 | 0.58069
|  | 9:16 | 13.6144 | 0.2361 | 0.58069
|  | 9:16 | 13.6156 | 0.2085 | 0.58068
|  | 9:16 | 13.6167 | 0.18089 | 0.58068
|  | 9:16 | 13.6178 | 0.14929 | 0.58068
|  | 9:17 | 13.6189 | 0.11769 | 0.58068
|  | 9:17 | 13.62 | 0.10424 | 0.58067
|  | 9:17 | 13.6211 | 0.096831 | 0.58067
|  | 9:17 | 13.6222 | 0.089426 | 0.58067
|  | 9:17 | 13.6233 | 0.072852 | 0.58067
|  | 9:17 | 13.6244 | 0.056277 | 0.58066
|  | 9:17 | 13.6256 | 0.041294 | 0.58066
|  | 9:17 | 13.6267 | 0.027902 | 0.58066
|  | 9:17 | 13.6278 | 0.01451 | 0.58066
|  | 9:17 | 13.6289 | -0.0091688 | 0.58066
|  | 9:17 | 13.63 | -0.032848 | 0.58065
|  | 9:17 | 13.6311 | -0.066966 | 0.58065
|  | 9:17 | 13.6322 | -0.11152 | 0.58065
|  | 9:17 | 13.6333 | -0.15608 | 0.58065
|  | 9:17 | 13.6344 | -0.17782 | 0.58064
|  | 9:18 | 13.6356 | -0.19956 | 0.58064
|  | 9:18 | 13.6367 | -0.21505 | 0.58064
|  | 9:18 | 13.6378 | -0.2243 | 0.58064
|  | 9:18 | 13.6389 | -0.23485 | 0.58063
|  | 9:18 | 13.64 | -0.24933 | 0.58063
|  | 9:18 | 13.6411 | -0.26381 | 0.58063
|  | 9:18 | 13.6422 | -0.28585 | 0.58063
|  | 9:18 | 13.6433 | -0.31041 | 0.58062
|  | 9:18 | 13.6444 | -0.33498 | 0.58062
|  | 9:18 | 13.6456 | -0.35433 | 0.58062
|  | 9:18 | 13.6467 | -0.37369 | 0.58062
|  | 9:18 | 13.6478 | -0.38334 | 0.58062
|  | 9:18 | 13.6489 | -0.38329 | 0.58061
|  | 9:18 | 13.65 | -0.38325 | 0.58061
|  | 9:18 | 13.6511 | -0.37177 | 0.58061
|  | 9:19 | 13.6522 | -0.36028 | 0.58061
|  | 9:19 | 13.6533 | -0.34955 | 0.5806
|  | 9:19 | 13.6544 | -0.33956 | 0.5806
|  | 9:19 | 13.6556 | -0.32957 | 0.5806
|  | 9:19 | 13.6567 | -0.32282 | 0.5806
|  | 9:19 | 13.6578 | -0.31608 | 0.58059
|  | 9:19 | 13.6589 | -0.30933 | 0.58059
|  | 9:19 | 13.66 | -0.30258 | 0.58059
|  | 9:19 | 13.6611 | -0.2977 | 0.58059
|  | 9:19 | 13.6622 | -0.29843 | 0.58059
|  | 9:19 | 13.6633 | -0.29916 | 0.58058
|  | 9:19 | 13.6644 | -0.3059 | 0.58058
|  | 9:19 | 13.6656 | -0.31865 | 0.58058
|  | 9:19 | 13.6667 | -0.33141 | 0.58058
|  | 9:19 | 13.6678 | -0.34928 | 0.58057
|  | 9:20 | 13.6689 | -0.36715 | 0.58057
|  | 9:20 | 13.67 | -0.36743 | 0.58057
|  | 9:20 | 13.6711 | -0.35014 | 0.58057
|  | 9:20 | 13.6722 | -0.33284 | 0.58056
|  | 9:20 | 13.6733 | -0.32614 | 0.58056
|  | 9:20 | 13.6744 | -0.31945 | 0.58056
|  | 9:20 | 13.6756 | -0.32347 | 0.58056
|  | 9:20 | 13.6767 | -0.33105 | 0.58056
|  | 9:20 | 13.6778 | -0.33863 | 0.58055
|  | 9:20 | 13.6789 | -0.34742 | 0.58055
|  | 9:20 | 13.68 | -0.35621 | 0.58055
|  | 9:20 | 13.6811 | -0.35525 | 0.58055
|  | 9:20 | 13.6822 | -0.34453 | 0.58054
|  | 9:20 | 13.6833 | -0.33382 | 0.58054
|  | 9:20 | 13.6844 | -0.32408 | 0.58054
|  | 9:21 | 13.6856 | -0.31435 | 0.58054
|  | 9:21 | 13.6867 | -0.29629 | 0.58053
|  | 9:21 | 13.6878 | -0.2699 | 0.58053
|  | 9:21 | 13.6889 | -0.24351 | 0.58053
|  | 9:21 | 13.69 | -0.22981 | 0.58053
|  | 9:21 | 13.6911 | -0.21611 | 0.58053
|  | 9:21 | 13.6922 | -0.19988 | 0.58052
|  | 9:21 | 13.6933 | -0.18112 | 0.58052
|  | 9:21 | 13.6944 | -0.16235 | 0.58052
|  | 9:21 | 13.6956 | -0.16142 | 0.58052
|  | 9:21 | 13.6967 | -0.16049 | 0.58051
|  | 9:21 | 13.6978 | -0.15389 | 0.58051
|  | 9:21 | 13.6989 | -0.14164 | 0.58051
|  | 9:21 | 13.7 | -0.12939 | 0.58051
|  | 9:21 | 13.7011 | -0.12526 | 0.5805
|  | 9:22 | 13.7022 | -0.12113 | 0.5805
|  | 9:22 | 13.7033 | -0.12313 | 0.5805
|  | 9:22 | 13.7044 | -0.13125 | 0.5805
|  | 9:22 | 13.7056 | -0.13938 | 0.5805
|  | 9:22 | 13.7067 | -0.13197 | 0.58049
|  | 9:22 | 13.7078 | -0.12456 | 0.58049
|  | 9:22 | 13.7089 | -0.11274 | 0.58049
|  | 9:22 | 13.71 | -0.096521 | 0.58049
|  | 9:22 | 13.7111 | -0.080302 | 0.58048
|  | 9:22 | 13.7122 | -0.054155 | 0.58048
|  | 9:22 | 13.7133 | -0.028008 | 0.58048
|  | 9:22 | 13.7144 | -0.0045076 | 0.58048
|  | 9:22 | 13.7156 | 0.016347 | 0.58047
|  | 9:22 | 13.7167 | 0.037201 | 0.58047
|  | 9:22 | 13.7178 | 0.038561 | 0.58047
|  | 9:23 | 13.7189 | 0.039921 | 0.58047
|  | 9:23 | 13.72 | 0.04462 | 0.58047
|  | 9:23 | 13.7211 | 0.052657 | 0.58046
|  | 9:23 | 13.7222 | 0.060695 | 0.58046
|  | 9:23 | 13.7233 | 0.062016 | 0.58046
|  | 9:23 | 13.7244 | 0.063337 | 0.58046
|  | 9:23 | 13.7256 | 0.059152 | 0.58045
|  | 9:23 | 13.7267 | 0.049461 | 0.58045
|  | 9:23 | 13.7278 | 0.039771 | 0.58045
|  | 9:23 | 13.7289 | 0.03008 | 0.58045
|  | 9:23 | 13.73 | 0.02039 | 0.58044
|  | 9:23 | 13.7311 | 0.012533 | 0.58044
|  | 9:23 | 13.7322 | 0.00651 | 0.58044
|  | 9:23 | 13.7333 | 0.00048686 | 0.58044
|  | 9:23 | 13.7344 | -0.0055363 | 0.58044
|  | 9:24 | 13.7356 | -0.028667 | 0.58043
|  | 9:24 | 13.7367 | -0.055754 | 0.58043
|  | 9:24 | 13.7378 | -0.094714 | 0.58043
|  | 9:24 | 13.7389 | -0.13367 | 0.58043
|  | 9:24 | 13.74 | -0.1564 | 0.58042
|  | 9:24 | 13.7411 | -0.17912 | 0.58042
|  | 9:24 | 13.7422 | -0.20465 | 0.58042
|  | 9:24 | 13.7433 | -0.23296 | 0.58042
|  | 9:24 | 13.7444 | -0.26128 | 0.58041
|  | 9:24 | 13.7456 | -0.28713 | 0.58041
|  | 9:24 | 13.7467 | -0.31299 | 0.58041
|  | 9:24 | 13.7478 | -0.3269 | 0.58041
|  | 9:24 | 13.7489 | -0.32887 | 0.58041
|  | 9:24 | 13.75 | -0.33084 | 0.5804
|  | 9:24 | 13.7511 | -0.34417 | 0.5804
|  | 9:25 | 13.7522 | -0.35749 | 0.5804
|  | 9:25 | 13.7533 | -0.36829 | 0.5804
|  | 9:25 | 13.7544 | -0.37657 | 0.58039
|  | 9:25 | 13.7556 | -0.38484 | 0.58039
|  | 9:25 | 13.7567 | -0.39763 | 0.58039
|  | 9:25 | 13.7578 | -0.41043 | 0.58039
|  | 9:25 | 13.7589 | -0.42784 | 0.58038
|  | 9:25 | 13.76 | -0.44987 | 0.58038
|  | 9:25 | 13.7611 | -0.4719 | 0.58038
|  | 9:25 | 13.7622 | -0.49075 | 0.58038
|  | 9:25 | 13.7633 | -0.50959 | 0.58037
|  | 9:25 | 13.7644 | -0.5272 | 0.58037
|  | 9:25 | 13.7656 | -0.54355 | 0.58037
|  | 9:25 | 13.7667 | -0.5599 | 0.58037
|  | 9:25 | 13.7678 | -0.58263 | 0.58037
|  | 9:26 | 13.7689 | -0.60537 | 0.58036
|  | 9:26 | 13.77 | -0.62365 | 0.58036
|  | 9:26 | 13.7711 | -0.63747 | 0.58036
|  | 9:26 | 13.7722 | -0.65129 | 0.58036
|  | 9:26 | 13.7733 | -0.65879 | 0.58035
|  | 9:26 | 13.7744 | -0.66629 | 0.58035
|  | 9:26 | 13.7756 | -0.67986 | 0.58035
|  | 9:26 | 13.7767 | -0.6995 | 0.58035
|  | 9:26 | 13.7778 | -0.71913 | 0.58034
|  | 9:26 | 13.7789 | -0.73168 | 0.58034
|  | 9:26 | 13.78 | -0.74423 | 0.58034
|  | 9:26 | 13.7811 | -0.7505 | 0.58034
|  | 9:26 | 13.7822 | -0.75049 | 0.58034
|  | 9:26 | 13.7833 | -0.75048 | 0.58033
|  | 9:26 | 13.7844 | -0.73916 | 0.58033
|  | 9:27 | 13.7856 | -0.72783 | 0.58033
|  | 9:27 | 13.7867 | -0.70987 | 0.58033
|  | 9:27 | 13.7878 | -0.68526 | 0.58032
|  | 9:27 | 13.7889 | -0.66066 | 0.58032
|  | 9:27 | 13.79 | -0.6495 | 0.58032
|  | 9:27 | 13.7911 | -0.63834 | 0.58032
|  | 9:27 | 13.7922 | -0.61665 | 0.58031
|  | 9:27 | 13.7933 | -0.58443 | 0.58031
|  | 9:27 | 13.7944 | -0.55221 | 0.58031
|  | 9:27 | 13.7956 | -0.51541 | 0.58031
|  | 9:27 | 13.7967 | -0.47861 | 0.58031
|  | 9:27 | 13.7978 | -0.44523 | 0.5803
|  | 9:27 | 13.7989 | -0.41524 | 0.5803
|  | 9:27 | 13.8 | -0.38526 | 0.5803
|  | 9:27 | 13.8011 | -0.37899 | 0.5803
|  | 9:28 | 13.8022 | -0.37271 | 0.58029
|  | 9:28 | 13.8033 | -0.37159 | 0.58029
|  | 9:28 | 13.8044 | -0.37563 | 0.58029
|  | 9:28 | 13.8056 | -0.37966 | 0.58029
|  | 9:28 | 13.8067 | -0.36377 | 0.58028
|  | 9:28 | 13.8078 | -0.34788 | 0.58028
|  | 9:28 | 13.8089 | -0.32774 | 0.58028
|  | 9:28 | 13.81 | -0.30335 | 0.58028
|  | 9:28 | 13.8111 | -0.27896 | 0.58028
|  | 9:28 | 13.8122 | -0.25074 | 0.58027
|  | 9:28 | 13.8133 | -0.22252 | 0.58027
|  | 9:28 | 13.8144 | -0.19509 | 0.58027
|  | 9:28 | 13.8156 | -0.16792 | 0.58027
|  | 9:28 | 13.8167 | -0.14272 | 0.58026
|  | 9:28 | 13.8178 | -0.12345 | 0.58026
|  | 9:29 | 13.8189 | -0.10417 | 0.58026
|  | 9:29 | 13.82 | -0.087397 | 0.58026
|  | 9:29 | 13.8211 | -0.07313 | 0.58025
|  | 9:29 | 13.8222 | -0.058863 | 0.58025
|  | 9:29 | 13.8233 | -0.061269 | 0.58025
|  | 9:29 | 13.8244 | -0.063676 | 0.58025
|  | 9:29 | 13.8256 | -0.065522 | 0.58025
|  | 9:29 | 13.8267 | -0.066808 | 0.58024
|  | 9:29 | 13.8278 | -0.068094 | 0.58024
|  | 9:29 | 13.8289 | -0.075492 | 0.58024
|  | 9:29 | 13.83 | -0.08289 | 0.58024
|  | 9:29 | 13.8311 | -0.09073 | 0.58023
|  | 9:29 | 13.8322 | -0.099014 | 0.58023
|  | 9:29 | 13.8333 | -0.1073 | 0.58023
|  | 9:29 | 13.8344 | -0.089359 | 0.58023
|  | 9:30 | 13.8356 | -0.071421 | 0.58022
|  | 9:30 | 13.8367 | -0.049309 | 0.58022
|  | 9:30 | 13.8378 | -0.023023 | 0.58022
|  | 9:30 | 13.8389 | 0.0032623 | 0.58022
|  | 9:30 | 13.84 | 0.016532 | 0.58022
|  | 9:30 | 13.8411 | 0.029801 | 0.58021
|  | 9:30 | 13.8422 | 0.036497 | 0.58021
|  | 9:30 | 13.8433 | 0.03662 | 0.58021
|  | 9:30 | 13.8444 | 0.036742 | 0.58021
|  | 9:30 | 13.8456 | 0.031934 | 0.5802
|  | 9:30 | 13.8467 | 0.027126 | 0.5802
|  | 9:30 | 13.8478 | 0.038487 | 0.5802
|  | 9:30 | 13.8489 | 0.06602 | 0.5802
|  | 9:30 | 13.85 | 0.093552 | 0.58019
|  | 9:30 | 13.8511 | 0.12924 | 0.58019
|  | 9:31 | 13.8522 | 0.16492 | 0.58019
|  | 9:31 | 13.8533 | 0.19135 | 0.58019
|  | 9:31 | 13.8544 | 0.20853 | 0.58019
|  | 9:31 | 13.8556 | 0.2257 | 0.58018
|  | 9:31 | 13.8567 | 0.2251 | 0.58018
|  | 9:31 | 13.8578 | 0.22449 | 0.58018
|  | 9:31 | 13.8589 | 0.21902 | 0.58018
|  | 9:31 | 13.86 | 0.2087 | 0.58017
|  | 9:31 | 13.8611 | 0.19838 | 0.58017
|  | 9:31 | 13.8622 | 0.17104 | 0.58017
|  | 9:31 | 13.8633 | 0.14371 | 0.58017
|  | 9:31 | 13.8644 | 0.12041 | 0.58016
|  | 9:31 | 13.8656 | 0.10116 | 0.58016
|  | 9:31 | 13.8667 | 0.081902 | 0.58016
|  | 9:31 | 13.8678 | 0.099815 | 0.58016
|  | 9:32 | 13.8689 | 0.11773 | 0.58016
|  | 9:32 | 13.87 | 0.13342 | 0.58015
|  | 9:32 | 13.8711 | 0.14689 | 0.58015
|  | 9:32 | 13.8722 | 0.16036 | 0.58015
|  | 9:32 | 13.8733 | 0.17384 | 0.58015
|  | 9:32 | 13.8744 | 0.18731 | 0.58014
|  | 9:32 | 13.8756 | 0.20476 | 0.58014
|  | 9:32 | 13.8767 | 0.22619 | 0.58014
|  | 9:32 | 13.8778 | 0.24763 | 0.58014
|  | 9:32 | 13.8789 | 0.26643 | 0.58013
|  | 9:32 | 13.88 | 0.28523 | 0.58013
|  | 9:32 | 13.8811 | 0.29984 | 0.58013
|  | 9:32 | 13.8822 | 0.31025 | 0.58013
|  | 9:32 | 13.8833 | 0.32066 | 0.58012
|  | 9:32 | 13.8844 | 0.33434 | 0.58012
|  | 9:33 | 13.8856 | 0.34802 | 0.58012
|  | 9:33 | 13.8867 | 0.36502 | 0.58012
|  | 9:33 | 13.8878 | 0.38533 | 0.58012
|  | 9:33 | 13.8889 | 0.40565 | 0.58011
|  | 9:33 | 13.89 | 0.42159 | 0.58011
|  | 9:33 | 13.8911 | 0.43753 | 0.58011
|  | 9:33 | 13.8922 | 0.45058 | 0.58011
|  | 9:33 | 13.8933 | 0.46075 | 0.5801
|  | 9:33 | 13.8944 | 0.47091 | 0.5801
|  | 9:33 | 13.8956 | 0.47039 | 0.5801
|  | 9:33 | 13.8967 | 0.46987 | 0.5801
|  | 9:33 | 13.8978 | 0.46317 | 0.58009
|  | 9:33 | 13.8989 | 0.45441 | 0.58009
|  | 9:33 | 13.9 | 0.44565 | 0.58009
|  | 9:33 | 13.9011 | 0.42328 | 0.58009
|  | 9:34 | 13.9022 | 0.4009 | 0.58009
|  | 9:34 | 13.9033 | 0.38572 | 0.58008
|  | 9:34 | 13.9044 | 0.39211 | 0.58008
|  | 9:34 | 13.9056 | 0.3985 | 0.58008
|  | 9:34 | 13.9067 | 0.4237 | 0.58008
|  | 9:34 | 13.9078 | 0.4489 | 0.58007
|  | 9:34 | 13.9089 | 0.46088 | 0.58007
|  | 9:34 | 13.91 | 0.45964 | 0.58007
|  | 9:34 | 13.9111 | 0.45841 | 0.58007
|  | 9:34 | 13.9122 | 0.4475 | 0.58006
|  | 9:34 | 13.9133 | 0.43659 | 0.58006
|  | 9:34 | 13.9144 | 0.42325 | 0.58006
|  | 9:34 | 13.9156 | 0.40749 | 0.58006
|  | 9:34 | 13.9167 | 0.39172 | 0.58006
|  | 9:34 | 13.9178 | 0.40531 | 0.58005
|  | 9:35 | 13.9189 | 0.4189 | 0.58005
|  | 9:35 | 13.92 | 0.43151 | 0.58005
|  | 9:35 | 13.9211 | 0.44314 | 0.58005
|  | 9:35 | 13.9222 | 0.45477 | 0.58004
|  | 9:35 | 13.9233 | 0.4521 | 0.58004
|  | 9:35 | 13.9244 | 0.44943 | 0.58004
|  | 9:35 | 13.9256 | 0.43991 | 0.58004
|  | 9:35 | 13.9267 | 0.42354 | 0.58003
|  | 9:35 | 13.9278 | 0.40717 | 0.58003
|  | 9:35 | 13.9289 | 0.40518 | 0.58003
|  | 9:35 | 13.93 | 0.40319 | 0.58003
|  | 9:35 | 13.9311 | 0.41374 | 0.58003
|  | 9:35 | 13.9322 | 0.43682 | 0.58002
|  | 9:35 | 13.9333 | 0.45991 | 0.58002
|  | 9:35 | 13.9344 | 0.48429 | 0.58002
|  | 9:36 | 13.9356 | 0.50867 | 0.58002
|  | 9:36 | 13.9367 | 0.52763 | 0.58001
|  | 9:36 | 13.9378 | 0.54478 | 0.58001
|  | 9:36 | 13.9389 | 0.56194 | 0.58001
|  | 9:36 | 13.94 | 0.57207 | 0.58001
|  | 9:36 | 13.9411 | 0.58221 | 0.58
|  | 9:36 | 13.9422 | 0.58718 | 0.58
|  | 9:36 | 13.9433 | 0.58698 | 0.58
|  | 9:36 | 13.9444 | 0.58678 | 0.58
|  | 9:36 | 13.9456 | 0.60128 | 0.58
|  | 9:36 | 13.9467 | 0.61578 | 0.57999
|  | 9:36 | 13.9478 | 0.62143 | 0.57999
|  | 9:36 | 13.9489 | 0.61825 | 0.57999
|  | 9:36 | 13.95 | 0.61506 | 0.57999
|  | 9:36 | 13.9511 | 0.62239 | 0.57998
|  | 9:37 | 13.9522 | 0.62971 | 0.57998
|  | 9:37 | 13.9533 | 0.63355 | 0.57998
|  | 9:37 | 13.9544 | 0.6339 | 0.57998
|  | 9:37 | 13.9556 | 0.63907 | 0.57997
|  | 9:37 | 13.9567 | 0.65868 | 0.57997
|  | 9:37 | 13.9578 | 0.6783 | 0.57997
|  | 9:37 | 13.9589 | 0.69792 | 0.57997
|  | 9:37 | 13.96 | 0.71754 | 0.57997
|  | 9:37 | 13.9611 | 0.73715 | 0.57996
|  | 9:37 | 13.9622 | 0.75945 | 0.57996
|  | 9:37 | 13.9633 | 0.78175 | 0.57996
|  | 9:37 | 13.9644 | 0.79371 | 0.57996
|  | 9:37 | 13.9656 | 0.79532 | 0.57995
|  | 9:37 | 13.9667 | 0.79693 | 0.57995
|  | 9:37 | 13.9678 | 0.81251 | 0.57995
|  | 9:38 | 13.9689 | 0.82809 | 0.57995
|  | 9:38 | 13.97 | 0.83863 | 0.57994
|  | 9:38 | 13.9711 | 0.84413 | 0.57994
|  | 9:38 | 13.9722 | 0.84963 | 0.57994
|  | 9:38 | 13.9733 | 0.82497 | 0.57994
|  | 9:38 | 13.9744 | 0.8003 | 0.57994
|  | 9:38 | 13.9756 | 0.77953 | 0.57993
|  | 9:38 | 13.9767 | 0.76265 | 0.57993
|  | 9:38 | 13.9778 | 0.74578 | 0.57993
|  | 9:38 | 13.9789 | 0.7289 | 0.57993
|  | 9:38 | 13.98 | 0.71203 | 0.57992
|  | 9:38 | 13.9811 | 0.69599 | 0.57992
|  | 9:38 | 13.9822 | 0.68079 | 0.57992
|  | 9:38 | 13.9833 | 0.66559 | 0.57992
|  | 9:38 | 13.9844 | 0.65039 | 0.57991
|  | 9:39 | 13.9856 | 0.63519 | 0.57991
|  | 9:39 | 13.9867 | 0.6287 | 0.57991
|  | 9:39 | 13.9878 | 0.62511 | 0.57991
|  | 9:39 | 13.9889 | 0.62152 | 0.57991
|  | 9:39 | 13.99 | 0.60905 | 0.5799
|  | 9:39 | 13.9911 | 0.59658 | 0.5799
|  | 9:39 | 13.9922 | 0.59451 | 0.5799
|  | 9:39 | 13.9933 | 0.60285 | 0.5799
|  | 9:39 | 13.9944 | 0.61119 | 0.57989
|  | 9:39 | 13.9956 | 0.62747 | 0.57989
|  | 9:39 | 13.9967 | 0.64374 | 0.57989
|  | 9:39 | 13.9978 | 0.64699 | 0.57989
|  | 9:39 | 13.9989 | 0.6372 | 0.57988
|  | 9:39 | 14 | 0.62494 | 0.57988
|  | 9:39 | 14.0011 | 0.60529 | 0.57988
|  | 9:40 | 14.0022 | 0.58564 | 0.57988
|  | 9:40 | 14.0033 | 0.56408 | 0.57987
|  | 9:40 | 14.0044 | 0.54061 | 0.57987
|  | 9:40 | 14.0056 | 0.51713 | 0.57987
|  | 9:40 | 14.0067 | 0.50205 | 0.57987
|  | 9:40 | 14.0078 | 0.48696 | 0.57987
|  | 9:40 | 14.0089 | 0.46771 | 0.57986
|  | 9:40 | 14.01 | 0.4443 | 0.57986
|  | 9:40 | 14.0111 | 0.4209 | 0.57986
|  | 9:40 | 14.0122 | 0.38558 | 0.57986
|  | 9:40 | 14.0133 | 0.35026 | 0.57985
|  | 9:40 | 14.0144 | 0.31233 | 0.57985
|  | 9:40 | 14.0156 | 0.27179 | 0.57985
|  | 9:40 | 14.0167 | 0.23124 | 0.57985
|  | 9:40 | 14.0178 | 0.20065 | 0.57984
|  | 9:41 | 14.0189 | 0.17005 | 0.57984
|  | 9:41 | 14.02 | 0.14077 | 0.57984
|  | 9:41 | 14.0211 | 0.11281 | 0.57984
|  | 9:41 | 14.0222 | 0.084842 | 0.57984
|  | 9:41 | 14.0233 | 0.038603 | 0.57983
|  | 9:41 | 14.0244 | -0.0076366 | 0.57983
|  | 9:41 | 14.0256 | -0.047739 | 0.57983
|  | 9:41 | 14.0267 | -0.081703 | 0.57983
|  | 9:41 | 14.0278 | -0.11567 | 0.57982
|  | 9:41 | 14.0289 | -0.13646 | 0.57982
|  | 9:41 | 14.03 | -0.15725 | 0.57982
|  | 9:41 | 14.0311 | -0.18325 | 0.57982
|  | 9:41 | 14.0322 | -0.21444 | 0.57981
|  | 9:41 | 14.0333 | -0.24563 | 0.57981
|  | 9:41 | 14.0344 | -0.2745 | 0.57981
|  | 9:42 | 14.0356 | -0.30336 | 0.57981
|  | 9:42 | 14.0367 | -0.34175 | 0.57981
|  | 9:42 | 14.0378 | -0.38967 | 0.5798
|  | 9:42 | 14.0389 | -0.42638 | 0.5798
|  | 9:42 | 14.04 | -0.42948 | 0.5798
|  | 9:42 | 14.0411 | -0.43258 | 0.5798
|  | 9:42 | 14.0422 | -0.44921 | 0.57979
|  | 9:42 | 14.0433 | -0.47935 | 0.57979
|  | 9:42 | 14.0444 | -0.5095 | 0.57979
|  | 9:42 | 14.0456 | -0.53188 | 0.57979
|  | 9:42 | 14.0467 | -0.55427 | 0.57978
|  | 9:42 | 14.0478 | -0.57911 | 0.57978
|  | 9:42 | 14.0489 | -0.60641 | 0.57978
|  | 9:42 | 14.05 | -0.63371 | 0.57978
|  | 9:42 | 14.0511 | -0.64927 | 0.57978
|  | 9:43 | 14.0522 | -0.66484 | 0.57977
|  | 9:43 | 14.0533 | -0.6804 | 0.57977
|  | 9:43 | 14.0544 | -0.69596 | 0.57977
|  | 9:43 | 14.0556 | -0.71153 | 0.57977
|  | 9:43 | 14.0567 | -0.72418 | 0.57976
|  | 9:43 | 14.0578 | -0.73684 | 0.57976
|  | 9:43 | 14.0589 | -0.73522 | 0.57976
|  | 9:43 | 14.06 | -0.71932 | 0.57976
|  | 9:43 | 14.0611 | -0.70341 | 0.57975
|  | 9:43 | 14.0622 | -0.67074 | 0.57975
|  | 9:43 | 14.0633 | -0.63806 | 0.57975
|  | 9:43 | 14.0644 | -0.60994 | 0.57975
|  | 9:43 | 14.0656 | -0.58635 | 0.57975
|  | 9:43 | 14.0667 | -0.56277 | 0.57974
|  | 9:43 | 14.0678 | -0.53527 | 0.57974
|  | 9:44 | 14.0689 | -0.50776 | 0.57974
|  | 9:44 | 14.07 | -0.48763 | 0.57974
|  | 9:44 | 14.0711 | -0.48964 | 0.57973
|  | 9:44 | 14.0722 | -0.49165 | 0.57973
|  | 9:44 | 14.0733 | -0.49001 | 0.57973
|  | 9:44 | 14.0744 | -0.48837 | 0.57973
|  | 9:44 | 14.0756 | -0.48899 | 0.57972
|  | 9:44 | 14.0767 | -0.49188 | 0.57972
|  | 9:44 | 14.0778 | -0.49352 | 0.57972
|  | 9:44 | 14.0789 | -0.49142 | 0.57972
|  | 9:44 | 14.08 | -0.48932 | 0.57972
|  | 9:44 | 14.0811 | -0.49175 | 0.57971
|  | 9:44 | 14.0822 | -0.4987 | 0.57971
|  | 9:44 | 14.0833 | -0.50565 | 0.57971
|  | 9:44 | 14.0844 | -0.50288 | 0.57971
|  | 9:45 | 14.0856 | -0.50011 | 0.5797
|  | 9:45 | 14.0867 | -0.48826 | 0.5797
|  | 9:45 | 14.0878 | -0.46731 | 0.5797
|  | 9:45 | 14.0889 | -0.44636 | 0.5797
|  | 9:45 | 14.09 | -0.413 | 0.57969
|  | 9:45 | 14.0911 | -0.37965 | 0.57969
|  | 9:45 | 14.0922 | -0.35026 | 0.57969
|  | 9:45 | 14.0933 | -0.32485 | 0.57969
|  | 9:45 | 14.0944 | -0.29944 | 0.57969
|  | 9:45 | 14.0956 | -0.27642 | 0.57968
|  | 9:45 | 14.0967 | -0.2534 | 0.57968
|  | 9:45 | 14.0978 | -0.236 | 0.57968
|  | 9:45 | 14.0989 | -0.22421 | 0.57968
|  | 9:45 | 14.1 | -0.21242 | 0.57967
|  | 9:45 | 14.1011 | -0.18995 | 0.57967
|  | 9:46 | 14.1022 | -0.16749 | 0.57967
|  | 9:46 | 14.1033 | -0.14283 | 0.57967
|  | 9:46 | 14.1044 | -0.11597 | 0.57966
|  | 9:46 | 14.1056 | -0.089118 | 0.57966
|  | 9:46 | 14.1067 | -0.051508 | 0.57966
|  | 9:46 | 14.1078 | -0.013898 | 0.57966
|  | 9:46 | 14.1089 | 0.024607 | 0.57966
|  | 9:46 | 14.11 | 0.064006 | 0.57965
|  | 9:46 | 14.1111 | 0.1034 | 0.57965
|  | 9:46 | 14.1122 | 0.12872 | 0.57965
|  | 9:46 | 14.1133 | 0.15403 | 0.57965
|  | 9:46 | 14.1144 | 0.16833 | 0.57964
|  | 9:46 | 14.1156 | 0.17161 | 0.57964
|  | 9:46 | 14.1167 | 0.1749 | 0.57964
|  | 9:46 | 14.1178 | 0.19225 | 0.57964
|  | 9:47 | 14.1189 | 0.2096 | 0.57963
|  | 9:47 | 14.12 | 0.23125 | 0.57963
|  | 9:47 | 14.1211 | 0.25433 | 0.57963
|  | 9:47 | 14.1222 | 0.28118 | 0.57963
|  | 9:47 | 14.1233 | 0.3193 | 0.57962
|  | 9:47 | 14.1244 | 0.35742 | 0.57962
|  | 9:47 | 14.1256 | 0.37481 | 0.57962
|  | 9:47 | 14.1267 | 0.37146 | 0.57962
|  | 9:47 | 14.1278 | 0.36812 | 0.57962
|  | 9:47 | 14.1289 | 0.36814 | 0.57961
|  | 9:47 | 14.13 | 0.36817 | 0.57961
|  | 9:47 | 14.1311 | 0.36493 | 0.57961
|  | 9:47 | 14.1322 | 0.35842 | 0.57961
|  | 9:47 | 14.1333 | 0.35192 | 0.5796
|  | 9:47 | 14.1344 | 0.35745 | 0.5796
|  | 9:48 | 14.1356 | 0.36298 | 0.5796
|  | 9:48 | 14.1367 | 0.38439 | 0.5796
|  | 9:48 | 14.1378 | 0.42166 | 0.57959
|  | 9:48 | 14.1389 | 0.45893 | 0.57959
|  | 9:48 | 14.14 | 0.50834 | 0.57959
|  | 9:48 | 14.1411 | 0.55774 | 0.57959
|  | 9:48 | 14.1422 | 0.59714 | 0.57959
|  | 9:48 | 14.1433 | 0.62655 | 0.57958
|  | 9:48 | 14.1444 | 0.65595 | 0.57958
|  | 9:48 | 14.1456 | 0.68535 | 0.57958
|  | 9:48 | 14.1467 | 0.71475 | 0.57958
|  | 9:48 | 14.1478 | 0.7405 | 0.57957
|  | 9:48 | 14.1489 | 0.7626 | 0.57957
|  | 9:48 | 14.15 | 0.7847 | 0.57957
|  | 9:48 | 14.1511 | 0.78996 | 0.57957
|  | 9:49 | 14.1522 | 0.79522 | 0.57956
|  | 9:49 | 14.1533 | 0.80048 | 0.57956
|  | 9:49 | 14.1544 | 0.80574 | 0.57956
|  | 9:49 | 14.1556 | 0.811 | 0.57956
|  | 9:49 | 14.1567 | 0.80302 | 0.57956
|  | 9:49 | 14.1578 | 0.79504 | 0.57955
|  | 9:49 | 14.1589 | 0.78335 | 0.57955
|  | 9:49 | 14.16 | 0.76794 | 0.57955
|  | 9:49 | 14.1611 | 0.75254 | 0.57955
|  | 9:49 | 14.1622 | 0.73713 | 0.57954
|  | 9:49 | 14.1633 | 0.72173 | 0.57954
|  | 9:49 | 14.1644 | 0.70357 | 0.57954
|  | 9:49 | 14.1656 | 0.68266 | 0.57954
|  | 9:49 | 14.1667 | 0.66175 | 0.57953
|  | 9:49 | 14.1678 | 0.62242 | 0.57953
|  | 9:50 | 14.1689 | 0.58309 | 0.57953
|  | 9:50 | 14.17 | 0.54171 | 0.57953
|  | 9:50 | 14.1711 | 0.49829 | 0.57953
|  | 9:50 | 14.1722 | 0.45486 | 0.57952
|  | 9:50 | 14.1733 | 0.42925 | 0.57952
|  | 9:50 | 14.1744 | 0.40363 | 0.57952
|  | 9:50 | 14.1756 | 0.37379 | 0.57952
|  | 9:50 | 14.1767 | 0.33971 | 0.57951
|  | 9:50 | 14.1778 | 0.30564 | 0.57951
|  | 9:50 | 14.1789 | 0.27379 | 0.57951
|  | 9:50 | 14.18 | 0.24194 | 0.57951
|  | 9:50 | 14.1811 | 0.22435 | 0.5795
|  | 9:50 | 14.1822 | 0.22102 | 0.5795
|  | 9:50 | 14.1833 | 0.21769 | 0.5795
|  | 9:50 | 14.1844 | 0.20566 | 0.5795
|  | 9:51 | 14.1856 | 0.19362 | 0.5795
|  | 9:51 | 14.1867 | 0.18466 | 0.57949
|  | 9:51 | 14.1878 | 0.17879 | 0.57949
|  | 9:51 | 14.1889 | 0.17291 | 0.57949
|  | 9:51 | 14.19 | 0.16918 | 0.57949
|  | 9:51 | 14.1911 | 0.16545 | 0.57948
|  | 9:51 | 14.1922 | 0.15742 | 0.57948
|  | 9:51 | 14.1933 | 0.14511 | 0.57948
|  | 9:51 | 14.1944 | 0.13279 | 0.57948
|  | 9:51 | 14.1956 | 0.11944 | 0.57947
|  | 9:51 | 14.1967 | 0.10609 | 0.57947
|  | 9:51 | 14.1978 | 0.093734 | 0.57947
|  | 9:51 | 14.1989 | 0.082374 | 0.57947
|  | 9:51 | 14.2 | 0.071013 | 0.57947
|  | 9:51 | 14.2011 | 0.066403 | 0.57946
|  | 9:52 | 14.2022 | 0.061792 | 0.57946
|  | 9:52 | 14.2033 | 0.057755 | 0.57946
|  | 9:52 | 14.2044 | 0.05429 | 0.57946
|  | 9:52 | 14.2056 | 0.050825 | 0.57945
|  | 9:52 | 14.2067 | 0.032276 | 0.57945
|  | 9:52 | 14.2078 | 0.013726 | 0.57945
|  | 9:52 | 14.2089 | -0.0155 | 0.57945
|  | 9:52 | 14.21 | -0.055402 | 0.57944
|  | 9:52 | 14.2111 | -0.095305 | 0.57944
|  | 9:52 | 14.2122 | -0.1476 | 0.57944
|  | 9:52 | 14.2133 | -0.19989 | 0.57944
|  | 9:52 | 14.2144 | -0.25319 | 0.57944
|  | 9:52 | 14.2156 | -0.30752 | 0.57943
|  | 9:52 | 14.2167 | -0.36184 | 0.57943
|  | 9:52 | 14.2178 | -0.40614 | 0.57943
|  | 9:53 | 14.2189 | -0.45044 | 0.57943
|  | 9:53 | 14.22 | -0.48112 | 0.57942
|  | 9:53 | 14.2211 | -0.49819 | 0.57942
|  | 9:53 | 14.2222 | -0.51526 | 0.57942
|  | 9:53 | 14.2233 | -0.54146 | 0.57942
|  | 9:53 | 14.2244 | -0.56767 | 0.57941
|  | 9:53 | 14.2256 | -0.58665 | 0.57941
|  | 9:53 | 14.2267 | -0.59843 | 0.57941
|  | 9:53 | 14.2278 | -0.6102 | 0.57941
|  | 9:53 | 14.2289 | -0.60745 | 0.57941
|  | 9:53 | 14.23 | -0.6047 | 0.5794
|  | 9:53 | 14.2311 | -0.60347 | 0.5794
|  | 9:53 | 14.2322 | -0.60376 | 0.5794
|  | 9:53 | 14.2333 | -0.60405 | 0.5794
|  | 9:53 | 14.2344 | -0.60336 | 0.57939
|  | 9:54 | 14.2356 | -0.60266 | 0.57939
|  | 9:54 | 14.2367 | -0.60291 | 0.57939
|  | 9:54 | 14.2378 | -0.60599 | 0.57939
|  | 9:54 | 14.2389 | -0.60906 | 0.57938
|  | 9:54 | 14.24 | -0.61077 | 0.57938
|  | 9:54 | 14.2411 | -0.61248 | 0.57938
|  | 9:54 | 14.2422 | -0.6045 | 0.57938
|  | 9:54 | 14.2433 | -0.58685 | 0.57937
|  | 9:54 | 14.2444 | -0.56919 | 0.57937
|  | 9:54 | 14.2456 | -0.55636 | 0.57937
|  | 9:54 | 14.2467 | -0.54352 | 0.57937
|  | 9:54 | 14.2478 | -0.53564 | 0.57937
|  | 9:54 | 14.2489 | -0.53272 | 0.57936
|  | 9:54 | 14.25 | -0.5298 | 0.57936
|  | 9:54 | 14.2511 | -0.529 | 0.57936
|  | 9:55 | 14.2522 | -0.52819 | 0.57936
|  | 9:55 | 14.2533 | -0.53152 | 0.57935
|  | 9:55 | 14.2544 | -0.539 | 0.57935
|  | 9:55 | 14.2556 | -0.54647 | 0.57935
|  | 9:55 | 14.2567 | -0.54635 | 0.57935
|  | 9:55 | 14.2578 | -0.54623 | 0.57934
|  | 9:55 | 14.2589 | -0.54252 | 0.57934
|  | 9:55 | 14.26 | -0.53522 | 0.57934
|  | 9:55 | 14.2611 | -0.52791 | 0.57934
|  | 9:55 | 14.2622 | -0.51653 | 0.57934
|  | 9:55 | 14.2633 | -0.50516 | 0.57933
|  | 9:55 | 14.2644 | -0.47674 | 0.57933
|  | 9:55 | 14.2656 | -0.43128 | 0.57933
|  | 9:55 | 14.2667 | -0.38582 | 0.57933
|  | 9:55 | 14.2678 | -0.34134 | 0.57932
|  | 9:56 | 14.2689 | -0.29686 | 0.57932
|  | 9:56 | 14.27 | -0.25636 | 0.57932
|  | 9:56 | 14.2711 | -0.21982 | 0.57932
|  | 9:56 | 14.2722 | -0.18329 | 0.57931
|  | 9:56 | 14.2733 | -0.16697 | 0.57931
|  | 9:56 | 14.2744 | -0.15066 | 0.57931
|  | 9:56 | 14.2756 | -0.13059 | 0.57931
|  | 9:56 | 14.2767 | -0.10676 | 0.57931
|  | 9:56 | 14.2778 | -0.082929 | 0.5793
|  | 9:56 | 14.2789 | -0.064992 | 0.5793
|  | 9:56 | 14.28 | -0.047054 | 0.5793
|  | 9:56 | 14.2811 | -0.033677 | 0.5793
|  | 9:56 | 14.2822 | -0.024861 | 0.57929
|  | 9:56 | 14.2833 | -0.016045 | 0.57929
|  | 9:56 | 14.2844 | -0.015577 | 0.57929
|  | 9:57 | 14.2856 | -0.01511 | 0.57929
|  | 9:57 | 14.2867 | -0.032247 | 0.57928
|  | 9:57 | 14.2878 | -0.066986 | 0.57928
|  | 9:57 | 14.2889 | -0.10173 | 0.57928
|  | 9:57 | 14.29 | -0.11422 | 0.57928
|  | 9:57 | 14.2911 | -0.12672 | 0.57928
|  | 9:57 | 14.2922 | -0.14071 | 0.57927
|  | 9:57 | 14.2933 | -0.15619 | 0.57927
|  | 9:57 | 14.2944 | -0.17167 | 0.57927
|  | 9:57 | 14.2956 | -0.18715 | 0.57927
|  | 9:57 | 14.2967 | -0.20263 | 0.57926
|  | 9:57 | 14.2978 | -0.22463 | 0.57926
|  | 9:57 | 14.2989 | -0.25316 | 0.57926
|  | 9:57 | 14.3 | -0.28168 | 0.57926
|  | 9:57 | 14.3011 | -0.29777 | 0.57925
|  | 9:58 | 14.3022 | -0.31386 | 0.57925
|  | 9:58 | 14.3033 | -0.31394 | 0.57925
|  | 9:58 | 14.3044 | -0.298 | 0.57925
|  | 9:58 | 14.3056 | -0.28207 | 0.57925
|  | 9:58 | 14.3067 | -0.26097 | 0.57924
|  | 9:58 | 14.3078 | -0.23987 | 0.57924
|  | 9:58 | 14.3089 | -0.2201 | 0.57924
|  | 9:58 | 14.31 | -0.20168 | 0.57924
|  | 9:58 | 14.3111 | -0.18325 | 0.57923
|  | 9:58 | 14.3122 | -0.16685 | 0.57923
|  | 9:58 | 14.3133 | -0.15045 | 0.57923
|  | 9:58 | 14.3144 | -0.13497 | 0.57923
|  | 9:58 | 14.3156 | -0.1204 | 0.57922
|  | 9:58 | 14.3167 | -0.10583 | 0.57922
|  | 9:58 | 14.3178 | -0.085856 | 0.57922
|  | 9:59 | 14.3189 | -0.065882 | 0.57922
|  | 9:59 | 14.32 | -0.057483 | 0.57922
|  | 9:59 | 14.3211 | -0.060658 | 0.57921
|  | 9:59 | 14.3222 | -0.063833 | 0.57921
|  | 9:59 | 14.3233 | -0.042603 | 0.57921
|  | 9:59 | 14.3244 | -0.021374 | 0.57921
|  | 9:59 | 14.3256 | -0.0021204 | 0.5792
|  | 9:59 | 14.3267 | 0.015157 | 0.5792
|  | 9:59 | 14.3278 | 0.032435 | 0.5792
|  | 9:59 | 14.3289 | 0.024561 | 0.5792
|  | 9:59 | 14.33 | 0.016687 | 0.57919
|  | 9:59 | 14.3311 | 0.012389 | 0.57919
|  | 9:59 | 14.3322 | 0.011665 | 0.57919
|  | 9:59 | 14.3333 | 0.010942 | 0.57919
|  | 9:59 | 14.3344 | 0.002515 | 0.57919
|  | 10:00 | 14.3356 | -0.0059115 | 0.57918
|  | 10:00 | 14.3367 | -0.026255 | 0.57918
|  | 10:00 | 14.3378 | -0.058516 | 0.57918
|  | 10:00 | 14.3389 | -0.090777 | 0.57918
|  | 10:00 | 14.34 | -0.1219 | 0.57917
|  | 10:00 | 14.3411 | -0.15302 | 0.57917
|  | 10:00 | 14.3422 | -0.18289 | 0.57917
|  | 10:00 | 14.3433 | -0.14425 | 0.57917
|  | 10:00 | 14.3444 | -0.12965 | 0.57916
|  | 10:00 | 14.3456 | -0.13601 | 0.57916
|  | 10:00 | 14.3467 | -0.14238 | 0.57916
|  | 10:00 | 14.3478 | -0.14874 | 0.57916
|  | 10:00 | 14.3489 | -0.15511 | 0.57916
|  | 10:00 | 14.35 | -0.16147 | 0.57915
|  | 10:00 | 14.3511 | -0.15001 | 0.57915
|  | 10:01 | 14.3522 | -0.13855 | 0.57915
|  | 10:01 | 14.3533 | -0.11353 | 0.57915
|  | 10:01 | 14.3544 | -0.083978 | 0.57914
|  | 10:01 | 14.3556 | -0.05443 | 0.57914
|  | 10:01 | 14.3567 | -0.032121 | 0.57914
|  | 10:01 | 14.3578 | -0.0098121 | 0.57914
|  | 10:01 | 14.3589 | 0.0050135 | 0.57913
|  | 10:01 | 14.36 | 0.012356 | 0.57913
|  | 10:01 | 14.3611 | 0.019698 | 0.57913
|  | 10:01 | 14.3622 | 0.0056427 | 0.57913
|  | 10:01 | 14.3633 | -0.0084124 | 0.57912
|  | 10:01 | 14.3644 | -0.016135 | 0.57912
|  | 10:01 | 14.3656 | -0.017526 | 0.57912
|  | 10:01 | 14.3667 | -0.018917 | 0.57912
|  | 10:01 | 14.3678 | -0.0074832 | 0.57912
|  | 10:02 | 14.3689 | 0.0039504 | 0.57911
|  | 10:02 | 14.37 | 0.016937 | 0.57911
|  | 10:02 | 14.3711 | 0.030441 | 0.57911
|  | 10:02 | 14.3722 | 0.043946 | 0.57911
|  | 10:02 | 14.3733 | 0.065859 | 0.5791
|  | 10:02 | 14.3744 | 0.087772 | 0.5791
|  | 10:02 | 14.3756 | 0.10268 | 0.5791
|  | 10:02 | 14.3767 | 0.11526 | 0.5791
|  | 10:02 | 14.3778 | 0.12783 | 0.57909
|  | 10:02 | 14.3789 | 0.13629 | 0.57909
|  | 10:02 | 14.38 | 0.14474 | 0.57909
|  | 10:02 | 14.3811 | 0.1681 | 0.57909
|  | 10:02 | 14.3822 | 0.20635 | 0.57909
|  | 10:02 | 14.3833 | 0.2446 | 0.57908
|  | 10:02 | 14.3844 | 0.28614 | 0.57908
|  | 10:03 | 14.3856 | 0.32769 | 0.57908
|  | 10:03 | 14.3867 | 0.37177 | 0.57908
|  | 10:03 | 14.3878 | 0.41839 | 0.57907
|  | 10:03 | 14.3889 | 0.4646 | 0.57907
|  | 10:03 | 14.39 | 0.50955 | 0.57907
|  | 10:03 | 14.3911 | 0.55451 | 0.57907
|  | 10:03 | 14.3922 | 0.60292 | 0.57906
|  | 10:03 | 14.3933 | 0.65481 | 0.57906
|  | 10:03 | 14.3944 | 0.70669 | 0.57906
|  | 10:03 | 14.3956 | 0.72091 | 0.57906
|  | 10:03 | 14.3967 | 0.73513 | 0.57906
|  | 10:03 | 14.3978 | 0.73769 | 0.57905
|  | 10:03 | 14.3989 | 0.7286 | 0.57905
|  | 10:03 | 14.4 | 0.71951 | 0.57905
|  | 10:03 | 14.4011 | 0.69733 | 0.57905
|  | 10:04 | 14.4022 | 0.66208 | 0.57904
|  | 10:04 | 14.4033 | 0.6161 | 0.57904
|  | 10:04 | 14.4044 | 0.5594 | 0.57904
|  | 10:04 | 14.4056 | 0.50271 | 0.57904
|  | 10:04 | 14.4067 | 0.43484 | 0.57903
|  | 10:04 | 14.4078 | 0.36696 | 0.57903
|  | 10:04 | 14.4089 | 0.2997 | 0.57903
|  | 10:04 | 14.41 | 0.23306 | 0.57903
|  | 10:04 | 14.4111 | 0.16641 | 0.57903
|  | 10:04 | 14.4122 | 0.1269 | 0.57902
|  | 10:04 | 14.4133 | 0.087393 | 0.57902
|  | 10:04 | 14.4144 | 0.062752 | 0.57902
|  | 10:04 | 14.4156 | 0.052981 | 0.57902
|  | 10:04 | 14.4167 | 0.04321 | 0.57901
|  | 10:04 | 14.4178 | 0.031374 | 0.57901
|  | 10:05 | 14.4189 | 0.019538 | 0.57901
|  | 10:05 | 14.42 | 0.0014623 | 0.57901
|  | 10:05 | 14.4211 | -0.022852 | 0.579
|  | 10:05 | 14.4222 | -0.047167 | 0.579
|  | 10:05 | 14.4233 | -0.057435 | 0.579
|  | 10:05 | 14.4244 | -0.067703 | 0.579
|  | 10:05 | 14.4256 | -0.080728 | 0.579
|  | 10:05 | 14.4267 | -0.096511 | 0.57899
|  | 10:05 | 14.4278 | -0.11229 | 0.57899
|  | 10:05 | 14.4289 | -0.14181 | 0.57899
|  | 10:05 | 14.43 | -0.17133 | 0.57899
|  | 10:05 | 14.4311 | -0.19213 | 0.57898
|  | 10:05 | 14.4322 | -0.21003 | 0.57898
|  | 10:05 | 14.4333 | -0.22794 | 0.57898
|  | 10:05 | 14.4344 | -0.25217 | 0.57898
|  | 10:06 | 14.4356 | -0.2764 | 0.57897
|  | 10:06 | 14.4367 | -0.29614 | 0.57897
|  | 10:06 | 14.4378 | -0.31141 | 0.57897
|  | 10:06 | 14.4389 | -0.32668 | 0.57897
|  | 10:06 | 14.44 | -0.33634 | 0.57897
|  | 10:06 | 14.4411 | -0.346 | 0.57896
|  | 10:06 | 14.4422 | -0.35417 | 0.57896
|  | 10:06 | 14.4433 | -0.36184 | 0.57896
|  | 10:06 | 14.4444 | -0.3695 | 0.57896
|  | 10:06 | 14.4456 | -0.38223 | 0.57895
|  | 10:06 | 14.4467 | -0.39495 | 0.57895
|  | 10:06 | 14.4478 | -0.41366 | 0.57895
|  | 10:06 | 14.4489 | -0.43836 | 0.57895
|  | 10:06 | 14.45 | -0.46307 | 0.57894
|  | 10:06 | 14.4511 | -0.49142 | 0.57894
|  | 10:07 | 14.4522 | -0.51976 | 0.57894
|  | 10:07 | 14.4533 | -0.53557 | 0.57894
|  | 10:07 | 14.4544 | -0.53885 | 0.57894
|  | 10:07 | 14.4556 | -0.54212 | 0.57893
|  | 10:07 | 14.4567 | -0.52588 | 0.57893
|  | 10:07 | 14.4578 | -0.50964 | 0.57893
|  | 10:07 | 14.4589 | -0.48512 | 0.57893
|  | 10:07 | 14.46 | -0.45232 | 0.57892
|  | 10:07 | 14.4611 | -0.41952 | 0.57892
|  | 10:07 | 14.4622 | -0.39896 | 0.57892
|  | 10:07 | 14.4633 | -0.3784 | 0.57892
|  | 10:07 | 14.4644 | -0.36069 | 0.57891
|  | 10:07 | 14.4656 | -0.34581 | 0.57891
|  | 10:07 | 14.4667 | -0.33094 | 0.57891
|  | 10:07 | 14.4678 | -0.31151 | 0.57891
|  | 10:08 | 14.4689 | -0.29208 | 0.57891
|  | 10:08 | 14.47 | -0.26401 | 0.5789
|  | 10:08 | 14.4711 | -0.2273 | 0.5789
|  | 10:08 | 14.4722 | -0.1906 | 0.5789
|  | 10:08 | 14.4733 | -0.15165 | 0.5789
|  | 10:08 | 14.4744 | -0.1127 | 0.57889
|  | 10:08 | 14.4756 | -0.070709 | 0.57889
|  | 10:08 | 14.4767 | -0.025681 | 0.57889
|  | 10:08 | 14.4778 | 0.019348 | 0.57889
|  | 10:08 | 14.4789 | 0.066808 | 0.57888
|  | 10:08 | 14.48 | 0.11427 | 0.57888
|  | 10:08 | 14.4811 | 0.14906 | 0.57888
|  | 10:08 | 14.4822 | 0.17962 | 0.57888
|  | 10:08 | 14.4833 | 0.21018 | 0.57887
|  | 10:08 | 14.4844 | 0.22659 | 0.57887
|  | 10:09 | 14.4856 | 0.243 | 0.57887
|  | 10:09 | 14.4867 | 0.26015 | 0.57887
|  | 10:09 | 14.4878 | 0.27804 | 0.57887
|  | 10:09 | 14.4889 | 0.29593 | 0.57886
|  | 10:09 | 14.49 | 0.34579 | 0.57886
|  | 10:09 | 14.4911 | 0.39566 | 0.57886
|  | 10:09 | 14.4922 | 0.41648 | 0.57886
|  | 10:09 | 14.4933 | 0.42761 | 0.57885
|  | 10:09 | 14.4944 | 0.43875 | 0.57885
|  | 10:09 | 14.4956 | 0.48488 | 0.57885
|  | 10:09 | 14.4967 | 0.53101 | 0.57885
|  | 10:09 | 14.4978 | 0.56431 | 0.57884
|  | 10:09 | 14.4989 | 0.58479 | 0.57884
|  | 10:09 | 14.5 | 0.60527 | 0.57884
|  | 10:09 | 14.5011 | 0.62576 | 0.57884
|  | 10:10 | 14.5022 | 0.64624 | 0.57884
|  | 10:10 | 14.5033 | 0.65386 | 0.57883
|  | 10:10 | 14.5044 | 0.64862 | 0.57883
|  | 10:10 | 14.5056 | 0.64337 | 0.57883
|  | 10:10 | 14.5067 | 0.61858 | 0.57883
|  | 10:10 | 14.5078 | 0.59379 | 0.57882
|  | 10:10 | 14.5089 | 0.57945 | 0.57882
|  | 10:10 | 14.51 | 0.5686 | 0.57882
|  | 10:10 | 14.5111 | 0.55774 | 0.57882
|  | 10:10 | 14.5122 | 0.53406 | 0.57881
|  | 10:10 | 14.5133 | 0.51037 | 0.57881
|  | 10:10 | 14.5144 | 0.48484 | 0.57881
|  | 10:10 | 14.5156 | 0.45747 | 0.57881
|  | 10:10 | 14.5167 | 0.43009 | 0.57881
|  | 10:10 | 14.5178 | 0.40661 | 0.5788
|  | 10:11 | 14.5189 | 0.38313 | 0.5788
|  | 10:11 | 14.52 | 0.35578 | 0.5788
|  | 10:11 | 14.5211 | 0.32455 | 0.5788
|  | 10:11 | 14.5222 | 0.29332 | 0.57879
|  | 10:11 | 14.5233 | 0.24981 | 0.57879
|  | 10:11 | 14.5244 | 0.20629 | 0.57879
|  | 10:11 | 14.5256 | 0.16355 | 0.57879
|  | 10:11 | 14.5267 | 0.12106 | 0.57878
|  | 10:11 | 14.5278 | 0.078582 | 0.57878
|  | 10:11 | 14.5289 | 0.031632 | 0.57878
|  | 10:11 | 14.53 | -0.015318 | 0.57878
|  | 10:11 | 14.5311 | -0.035845 | 0.57878
|  | 10:11 | 14.5322 | -0.047565 | 0.57877
|  | 10:11 | 14.5333 | -0.059285 | 0.57877
|  | 10:11 | 14.5344 | -0.081598 | 0.57877
|  | 10:12 | 14.5356 | -0.10391 | 0.57877
|  | 10:12 | 14.5367 | -0.13323 | 0.57876
|  | 10:12 | 14.5378 | -0.16956 | 0.57876
|  | 10:12 | 14.5389 | -0.20588 | 0.57876
|  | 10:12 | 14.54 | -0.24997 | 0.57876
|  | 10:12 | 14.5411 | -0.29406 | 0.57875
|  | 10:12 | 14.5422 | -0.33234 | 0.57875
|  | 10:12 | 14.5433 | -0.3648 | 0.57875
|  | 10:12 | 14.5444 | -0.39726 | 0.57875
|  | 10:12 | 14.5456 | -0.42357 | 0.57875
|  | 10:12 | 14.5467 | -0.44987 | 0.57874
|  | 10:12 | 14.5478 | -0.46847 | 0.57874
|  | 10:12 | 14.5489 | -0.47935 | 0.57874
|  | 10:12 | 14.55 | -0.49023 | 0.57874
|  | 10:12 | 14.5511 | -0.5088 | 0.57873
|  | 10:13 | 14.5522 | -0.52738 | 0.57873
|  | 10:13 | 14.5533 | -0.54595 | 0.57873
|  | 10:13 | 14.5544 | -0.56452 | 0.57873
|  | 10:13 | 14.5556 | -0.58056 | 0.57872
|  | 10:13 | 14.5567 | -0.58899 | 0.57872
|  | 10:13 | 14.5578 | -0.59741 | 0.57872
|  | 10:13 | 14.5589 | -0.60464 | 0.57872
|  | 10:13 | 14.56 | -0.61068 | 0.57872
|  | 10:13 | 14.5611 | -0.61671 | 0.57871
|  | 10:13 | 14.5622 | -0.62274 | 0.57871
|  | 10:13 | 14.5633 | -0.62878 | 0.57871
|  | 10:13 | 14.5644 | -0.64556 | 0.57871
|  | 10:13 | 14.5656 | -0.67309 | 0.5787
|  | 10:13 | 14.5667 | -0.70062 | 0.5787
|  | 10:13 | 14.5678 | -0.7259 | 0.5787
|  | 10:14 | 14.5689 | -0.75118 | 0.5787
|  | 10:14 | 14.57 | -0.76373 | 0.57869
|  | 10:14 | 14.5711 | -0.76355 | 0.57869
|  | 10:14 | 14.5722 | -0.76336 | 0.57869
|  | 10:14 | 14.5733 | -0.74165 | 0.57869
|  | 10:14 | 14.5744 | -0.71995 | 0.57869
|  | 10:14 | 14.5756 | -0.69328 | 0.57868
|  | 10:14 | 14.5767 | -0.66166 | 0.57868
|  | 10:14 | 14.5778 | -0.63004 | 0.57868
|  | 10:14 | 14.5789 | -0.60123 | 0.57868
|  | 10:14 | 14.58 | -0.57243 | 0.57867
|  | 10:14 | 14.5811 | -0.55891 | 0.57867
|  | 10:14 | 14.5822 | -0.56068 | 0.57867
|  | 10:14 | 14.5833 | -0.56245 | 0.57867
|  | 10:14 | 14.5844 | -0.54412 | 0.57866
|  | 10:15 | 14.5856 | -0.52578 | 0.57866
|  | 10:15 | 14.5867 | -0.51626 | 0.57866
|  | 10:15 | 14.5878 | -0.51554 | 0.57866
|  | 10:15 | 14.5889 | -0.51483 | 0.57866
|  | 10:15 | 14.59 | -0.51658 | 0.57865
|  | 10:15 | 14.5911 | -0.51832 | 0.57865
|  | 10:15 | 14.5922 | -0.51742 | 0.57865
|  | 10:15 | 14.5933 | -0.51387 | 0.57865
|  | 10:15 | 14.5944 | -0.51032 | 0.57864
|  | 10:15 | 14.5956 | -0.49265 | 0.57864
|  | 10:15 | 14.5967 | -0.47497 | 0.57864
|  | 10:15 | 14.5978 | -0.4573 | 0.57864
|  | 10:15 | 14.5989 | -0.43963 | 0.57863
|  | 10:15 | 14.6 | -0.42195 | 0.57863
|  | 10:15 | 14.6011 | -0.40033 | 0.57863
|  | 10:16 | 14.6022 | -0.3787 | 0.57863
|  | 10:16 | 14.6033 | -0.35755 | 0.57862
|  | 10:16 | 14.6044 | -0.33687 | 0.57862
|  | 10:16 | 14.6056 | -0.31619 | 0.57862
|  | 10:16 | 14.6067 | -0.27026 | 0.57862
|  | 10:16 | 14.6078 | -0.22432 | 0.57862
|  | 10:16 | 14.6089 | -0.18079 | 0.57861
|  | 10:16 | 14.61 | -0.13806 | 0.57861
|  | 10:16 | 14.6111 | -0.095326 | 0.57861
|  | 10:16 | 14.6122 | -0.056057 | 0.57861
|  | 10:16 | 14.6133 | -0.016788 | 0.5786
|  | 10:16 | 14.6144 | 0.015659 | 0.5786
|  | 10:16 | 14.6156 | 0.041284 | 0.5786
|  | 10:16 | 14.6167 | 0.066908 | 0.5786
|  | 10:16 | 14.6178 | 0.067889 | 0.57859
|  | 10:17 | 14.6189 | 0.06887 | 0.57859
|  | 10:17 | 14.62 | 0.077604 | 0.57859
|  | 10:17 | 14.6211 | 0.094089 | 0.57859
|  | 10:17 | 14.6222 | 0.11057 | 0.57859
|  | 10:17 | 14.6233 | 0.13697 | 0.57858
|  | 10:17 | 14.6244 | 0.16337 | 0.57858
|  | 10:17 | 14.6256 | 0.18555 | 0.57858
|  | 10:17 | 14.6267 | 0.2035 | 0.57858
|  | 10:17 | 14.6278 | 0.22146 | 0.57857
|  | 10:17 | 14.6289 | 0.25483 | 0.57857
|  | 10:17 | 14.63 | 0.2882 | 0.57857
|  | 10:17 | 14.6311 | 0.30837 | 0.57857
|  | 10:17 | 14.6322 | 0.31533 | 0.57856
|  | 10:17 | 14.6333 | 0.32229 | 0.57856
|  | 10:17 | 14.6344 | 0.34371 | 0.57856
|  | 10:18 | 14.6356 | 0.36513 | 0.57856
|  | 10:18 | 14.6367 | 0.39495 | 0.57856
|  | 10:18 | 14.6378 | 0.43316 | 0.57855
|  | 10:18 | 14.6389 | 0.47137 | 0.57855
|  | 10:18 | 14.64 | 0.50421 | 0.57855
|  | 10:18 | 14.6411 | 0.53705 | 0.57855
|  | 10:18 | 14.6422 | 0.56677 | 0.57854
|  | 10:18 | 14.6433 | 0.59337 | 0.57854
|  | 10:18 | 14.6444 | 0.61996 | 0.57854
|  | 10:18 | 14.6456 | 0.63533 | 0.57854
|  | 10:18 | 14.6467 | 0.6507 | 0.57853
|  | 10:18 | 14.6478 | 0.67478 | 0.57853
|  | 10:18 | 14.6489 | 0.70756 | 0.57853
|  | 10:18 | 14.65 | 0.74033 | 0.57853
|  | 10:18 | 14.6511 | 0.7188 | 0.57853
|  | 10:19 | 14.6522 | 0.69726 | 0.57852
|  | 10:19 | 14.6533 | 0.69924 | 0.57852
|  | 10:19 | 14.6544 | 0.72473 | 0.57852
|  | 10:19 | 14.6556 | 0.75023 | 0.57852
|  | 10:19 | 14.6567 | 0.75876 | 0.57851
|  | 10:19 | 14.6578 | 0.76729 | 0.57851
|  | 10:19 | 14.6589 | 0.77299 | 0.57851
|  | 10:19 | 14.66 | 0.77774 | 0.57851
|  | 10:19 | 14.6611 | 0.7825 | 0.5785
|  | 10:19 | 14.6622 | 0.76741 | 0.5785
|  | 10:19 | 14.6633 | 0.75232 | 0.5785
|  | 10:19 | 14.6644 | 0.7296 | 0.5785
|  | 10:19 | 14.6656 | 0.69925 | 0.5785
|  | 10:19 | 14.6667 | 0.6689 | 0.57849
|  | 10:19 | 14.6678 | 0.62576 | 0.57849
|  | 10:20 | 14.6689 | 0.58261 | 0.57849
|  | 10:20 | 14.67 | 0.54949 | 0.57849
|  | 10:20 | 14.6711 | 0.5264 | 0.57848
|  | 10:20 | 14.6722 | 0.50331 | 0.57848
|  | 10:20 | 14.6733 | 0.4765 | 0.57848
|  | 10:20 | 14.6744 | 0.44968 | 0.57848
|  | 10:20 | 14.6756 | 0.4167 | 0.57847
|  | 10:20 | 14.6767 | 0.37755 | 0.57847
|  | 10:20 | 14.6778 | 0.33841 | 0.57847
|  | 10:20 | 14.6789 | 0.29386 | 0.57847
|  | 10:20 | 14.68 | 0.24932 | 0.57847
|  | 10:20 | 14.6811 | 0.21533 | 0.57846
|  | 10:20 | 14.6822 | 0.19189 | 0.57846
|  | 10:20 | 14.6833 | 0.16844 | 0.57846
|  | 10:20 | 14.6844 | 0.16499 | 0.57846
|  | 10:21 | 14.6856 | 0.16153 | 0.57845
|  | 10:21 | 14.6867 | 0.15986 | 0.57845
|  | 10:21 | 14.6878 | 0.15996 | 0.57845
|  | 10:21 | 14.6889 | 0.16005 | 0.57845
|  | 10:21 | 14.69 | 0.14796 | 0.57844
|  | 10:21 | 14.6911 | 0.13587 | 0.57844
|  | 10:21 | 14.6922 | 0.12378 | 0.57844
|  | 10:21 | 14.6933 | 0.1117 | 0.57844
|  | 10:21 | 14.6944 | 0.099605 | 0.57844
|  | 10:21 | 14.6956 | 0.079349 | 0.57843
|  | 10:21 | 14.6967 | 0.059092 | 0.57843
|  | 10:21 | 14.6978 | 0.042185 | 0.57843
|  | 10:21 | 14.6989 | 0.028626 | 0.57843
|  | 10:21 | 14.7 | 0.015067 | 0.57842
|  | 10:21 | 14.7011 | 0.017848 | 0.57842
|  | 10:22 | 14.7022 | 0.020629 | 0.57842
|  | 10:22 | 14.7033 | 0.02341 | 0.57842
|  | 10:22 | 14.7044 | 0.02619 | 0.57841
|  | 10:22 | 14.7056 | 0.028971 | 0.57841
|  | 10:22 | 14.7067 | 0.040168 | 0.57841
|  | 10:22 | 14.7078 | 0.051364 | 0.57841
|  | 10:22 | 14.7089 | 0.060832 | 0.57841
|  | 10:22 | 14.71 | 0.068571 | 0.5784
|  | 10:22 | 14.7111 | 0.076309 | 0.5784
|  | 10:22 | 14.7122 | 0.077437 | 0.5784
|  | 10:22 | 14.7133 | 0.078564 | 0.5784
|  | 10:22 | 14.7144 | 0.080322 | 0.57839
|  | 10:22 | 14.7156 | 0.082711 | 0.57839
|  | 10:22 | 14.7167 | 0.085099 | 0.57839
|  | 10:22 | 14.7178 | 0.082506 | 0.57839
|  | 10:23 | 14.7189 | 0.079913 | 0.57838
|  | 10:23 | 14.72 | 0.07732 | 0.57838
|  | 10:23 | 14.7211 | 0.074727 | 0.57838
|  | 10:23 | 14.7222 | 0.072134 | 0.57838
|  | 10:23 | 14.7233 | 0.05751 | 0.57837
|  | 10:23 | 14.7244 | 0.042887 | 0.57837
|  | 10:23 | 14.7256 | 0.041184 | 0.57837
|  | 10:23 | 14.7267 | 0.052402 | 0.57837
|  | 10:23 | 14.7278 | 0.063621 | 0.57837
|  | 10:23 | 14.7289 | 0.059618 | 0.57836
|  | 10:23 | 14.73 | 0.055615 | 0.57836
|  | 10:23 | 14.7311 | 0.053782 | 0.57836
|  | 10:23 | 14.7322 | 0.054119 | 0.57836
|  | 10:23 | 14.7333 | 0.054456 | 0.57835
|  | 10:23 | 14.7344 | 0.052728 | 0.57835
|  | 10:24 | 14.7356 | 0.051 | 0.57835
|  | 10:24 | 14.7367 | 0.053232 | 0.57835
|  | 10:24 | 14.7378 | 0.059425 | 0.57834
|  | 10:24 | 14.7389 | 0.065617 | 0.57834
|  | 10:24 | 14.74 | 0.089973 | 0.57834
|  | 10:24 | 14.7411 | 0.11433 | 0.57834
|  | 10:24 | 14.7422 | 0.13104 | 0.57834
|  | 10:24 | 14.7433 | 0.14009 | 0.57833
|  | 10:24 | 14.7444 | 0.14915 | 0.57833
|  | 10:24 | 14.7456 | 0.14294 | 0.57833
|  | 10:24 | 14.7467 | 0.13674 | 0.57833
|  | 10:24 | 14.7478 | 0.13903 | 0.57832
|  | 10:24 | 14.7489 | 0.14981 | 0.57832
|  | 10:24 | 14.75 | 0.16059 | 0.57832
|  | 10:24 | 14.7511 | 0.17604 | 0.57832
|  | 10:25 | 14.7522 | 0.1915 | 0.57831
|  | 10:25 | 14.7533 | 0.20614 | 0.57831
|  | 10:25 | 14.7544 | 0.21996 | 0.57831
|  | 10:25 | 14.7556 | 0.23378 | 0.57831
|  | 10:25 | 14.7567 | 0.22649 | 0.57831
|  | 10:25 | 14.7578 | 0.2192 | 0.5783
|  | 10:25 | 14.7589 | 0.2103 | 0.5783
|  | 10:25 | 14.76 | 0.1998 | 0.5783
|  | 10:25 | 14.7611 | 0.18929 | 0.5783
|  | 10:25 | 14.7622 | 0.16969 | 0.57829
|  | 10:25 | 14.7633 | 0.15009 | 0.57829
|  | 10:25 | 14.7644 | 0.12595 | 0.57829
|  | 10:25 | 14.7656 | 0.09729 | 0.57829
|  | 10:25 | 14.7667 | 0.068625 | 0.57828
|  | 10:25 | 14.7678 | 0.07361 | 0.57828
|  | 10:26 | 14.7689 | 0.078594 | 0.57828
|  | 10:26 | 14.77 | 0.072993 | 0.57828
|  | 10:26 | 14.7711 | 0.056805 | 0.57828
|  | 10:26 | 14.7722 | 0.040617 | 0.57827
|  | 10:26 | 14.7733 | 0.014632 | 0.57827
|  | 10:26 | 14.7744 | -0.011353 | 0.57827
|  | 10:26 | 14.7756 | -0.035552 | 0.57827
|  | 10:26 | 14.7767 | -0.057963 | 0.57826
|  | 10:26 | 14.7778 | -0.080375 | 0.57826
|  | 10:26 | 14.7789 | -0.065543 | 0.57826
|  | 10:26 | 14.78 | -0.050712 | 0.57826
|  | 10:26 | 14.7811 | -0.031837 | 0.57825
|  | 10:26 | 14.7822 | -0.0089175 | 0.57825
|  | 10:26 | 14.7833 | 0.014002 | 0.57825
|  | 10:26 | 14.7844 | 0.0028253 | 0.57825
|  | 10:27 | 14.7856 | -0.0083511 | 0.57825
|  | 10:27 | 14.7867 | -0.022928 | 0.57824
|  | 10:27 | 14.7878 | -0.040906 | 0.57824
|  | 10:27 | 14.7889 | -0.058884 | 0.57824
|  | 10:27 | 14.79 | -0.068746 | 0.57824
|  | 10:27 | 14.7911 | -0.078609 | 0.57823
|  | 10:27 | 14.7922 | -0.07932 | 0.57823
|  | 10:27 | 14.7933 | -0.076982 | 0.57823
|  | 10:27 | 14.7944 | -0.074643 | 0.57823
|  | 10:27 | 14.7956 | -0.075455 | 0.57822
|  | 10:27 | 14.7967 | -0.076267 | 0.57822
|  | 10:27 | 14.7978 | -0.073963 | 0.57822
|  | 10:27 | 14.7989 | -0.07062 | 0.57822
|  | 10:27 | 14.8 | -0.067277 | 0.57822
|  | 10:27 | 14.8011 | -0.087801 | 0.57821
|  | 10:28 | 14.8022 | -0.10832 | 0.57821
|  | 10:28 | 14.8033 | -0.11242 | 0.57821
|  | 10:28 | 14.8044 | -0.10009 | 0.57821
|  | 10:28 | 14.8056 | -0.087763 | 0.5782
|  | 10:28 | 14.8067 | -0.068639 | 0.5782
|  | 10:28 | 14.8078 | -0.049516 | 0.5782
|  | 10:28 | 14.8089 | -0.015747 | 0.5782
|  | 10:28 | 14.81 | 0.032669 | 0.57819
|  | 10:28 | 14.8111 | 0.076313 | 0.57819
|  | 10:28 | 14.8122 | 0.10565 | 0.57819
|  | 10:28 | 14.8133 | 0.13498 | 0.57819
|  | 10:28 | 14.8144 | 0.14996 | 0.57819
|  | 10:28 | 14.8156 | 0.1506 | 0.57818
|  | 10:28 | 14.8167 | 0.15123 | 0.57818
|  | 10:28 | 14.8178 | 0.15947 | 0.57818
|  | 10:29 | 14.8189 | 0.1677 | 0.57818
|  | 10:29 | 14.82 | 0.16361 | 0.57817
|  | 10:29 | 14.8211 | 0.14719 | 0.57817
|  | 10:29 | 14.8222 | 0.13078 | 0.57817
|  | 10:29 | 14.8233 | 0.11437 | 0.57817
|  | 10:29 | 14.8244 | 0.097961 | 0.57816
|  | 10:29 | 14.8256 | 0.077558 | 0.57816
|  | 10:29 | 14.8267 | 0.055824 | 0.57816
|  | 10:29 | 14.8278 | 0.034089 | 0.57816
|  | 10:29 | 14.8289 | 0.018564 | 0.57816
|  | 10:29 | 14.83 | 0.0030393 | 0.57815
|  | 10:29 | 14.8311 | -0.016027 | 0.57815
|  | 10:29 | 14.8322 | -0.038635 | 0.57815
|  | 10:29 | 14.8333 | -0.061243 | 0.57815
|  | 10:29 | 14.8344 | -0.068344 | 0.57814
|  | 10:30 | 14.8356 | -0.075445 | 0.57814
|  | 10:30 | 14.8367 | -0.080764 | 0.57814
|  | 10:30 | 14.8378 | -0.0843 | 0.57814
|  | 10:30 | 14.8389 | -0.087836 | 0.57813
|  | 10:30 | 14.84 | -0.08516 | 0.57813
|  | 10:30 | 14.8411 | -0.082483 | 0.57813
|  | 10:30 | 14.8422 | -0.079807 | 0.57813
|  | 10:30 | 14.8433 | -0.07713 | 0.57812
|  | 10:30 | 14.8444 | -0.074454 | 0.57812
|  | 10:30 | 14.8456 | -0.076025 | 0.57812
|  | 10:30 | 14.8467 | -0.077597 | 0.57812
|  | 10:30 | 14.8478 | -0.085439 | 0.57812
|  | 10:30 | 14.8489 | -0.09955 | 0.57811
|  | 10:30 | 14.85 | -0.11366 | 0.57811
|  | 10:30 | 14.8511 | -0.11441 | 0.57811
|  | 10:31 | 14.8522 | -0.11516 | 0.57811
|  | 10:31 | 14.8533 | -0.10971 | 0.5781
|  | 10:31 | 14.8544 | -0.09806 | 0.5781
|  | 10:31 | 14.8556 | -0.084509 | 0.5781
|  | 10:31 | 14.8567 | -0.065244 | 0.5781
|  | 10:31 | 14.8578 | -0.045979 | 0.57809
|  | 10:31 | 14.8589 | -0.029559 | 0.57809
|  | 10:31 | 14.86 | -0.015984 | 0.57809
|  | 10:31 | 14.8611 | -0.0024094 | 0.57809
|  | 10:31 | 14.8622 | 0.022238 | 0.57809
|  | 10:31 | 14.8633 | 0.046885 | 0.57808
|  | 10:31 | 14.8644 | 0.074314 | 0.57808
|  | 10:31 | 14.8656 | 0.10453 | 0.57808
|  | 10:31 | 14.8667 | 0.13474 | 0.57808
|  | 10:31 | 14.8678 | 0.15843 | 0.57807
|  | 10:32 | 14.8689 | 0.18212 | 0.57807
|  | 10:32 | 14.87 | 0.20365 | 0.57807
|  | 10:32 | 14.8711 | 0.22304 | 0.57807
|  | 10:32 | 14.8722 | 0.24243 | 0.57806
|  | 10:32 | 14.8733 | 0.2467 | 0.57806
|  | 10:32 | 14.8744 | 0.25097 | 0.57806
|  | 10:32 | 14.8756 | 0.25524 | 0.57806
|  | 10:32 | 14.8767 | 0.25952 | 0.57806
|  | 10:32 | 14.8778 | 0.26379 | 0.57805
|  | 10:32 | 14.8789 | 0.26806 | 0.57805
|  | 10:32 | 14.88 | 0.27234 | 0.57805
|  | 10:32 | 14.8811 | 0.27055 | 0.57805
|  | 10:32 | 14.8822 | 0.26272 | 0.57804
|  | 10:32 | 14.8833 | 0.25488 | 0.57804
|  | 10:32 | 14.8844 | 0.23498 | 0.57804
|  | 10:33 | 14.8856 | 0.21507 | 0.57804
|  | 10:33 | 14.8867 | 0.20228 | 0.57803
|  | 10:33 | 14.8878 | 0.1966 | 0.57803
|  | 10:33 | 14.8889 | 0.19092 | 0.57803
|  | 10:33 | 14.89 | 0.17374 | 0.57803
|  | 10:33 | 14.8911 | 0.15656 | 0.57803
|  | 10:33 | 14.8922 | 0.14737 | 0.57802
|  | 10:33 | 14.8933 | 0.14617 | 0.57802
|  | 10:33 | 14.8944 | 0.14096 | 0.57802
|  | 10:33 | 14.8956 | 0.1237 | 0.57802
|  | 10:33 | 14.8967 | 0.10644 | 0.57801
|  | 10:33 | 14.8978 | 0.091813 | 0.57801
|  | 10:33 | 14.8989 | 0.079822 | 0.57801
|  | 10:33 | 14.9 | 0.067831 | 0.57801
|  | 10:33 | 14.9011 | 0.075896 | 0.578
|  | 10:34 | 14.9022 | 0.083961 | 0.578
|  | 10:34 | 14.9033 | 0.086463 | 0.578
|  | 10:34 | 14.9044 | 0.083403 | 0.578
|  | 10:34 | 14.9056 | 0.080342 | 0.578
|  | 10:34 | 14.9067 | 0.086139 | 0.57799
|  | 10:34 | 14.9078 | 0.091936 | 0.57799
|  | 10:34 | 14.9089 | 0.086932 | 0.57799
|  | 10:34 | 14.91 | 0.071129 | 0.57799
|  | 10:34 | 14.9111 | 0.055325 | 0.57798
|  | 10:34 | 14.9122 | 0.058039 | 0.57798
|  | 10:34 | 14.9133 | 0.060754 | 0.57798
|  | 10:34 | 14.9144 | 0.053289 | 0.57798
|  | 10:34 | 14.9156 | 0.035644 | 0.57797
|  | 10:34 | 14.9167 | 0.018 | 0.57797
|  | 10:34 | 14.9178 | -0.013065 | 0.57797
|  | 10:35 | 14.9189 | -0.04413 | 0.57797
|  | 10:35 | 14.92 | -0.070275 | 0.57797
|  | 10:35 | 14.9211 | -0.091499 | 0.57796
|  | 10:35 | 14.9222 | -0.11272 | 0.57796
|  | 10:35 | 14.9233 | -0.1153 | 0.57796
|  | 10:35 | 14.9244 | -0.11788 | 0.57796
|  | 10:35 | 14.9256 | -0.11783 | 0.57795
|  | 10:35 | 14.9267 | -0.11514 | 0.57795
|  | 10:35 | 14.9278 | -0.11272 | 0.57795
|  | 10:35 | 14.9289 | -0.11108 | 0.57795
|  | 10:35 | 14.93 | -0.10944 | 0.57794
|  | 10:35 | 14.9311 | -0.1078 | 0.57794
|  | 10:35 | 14.9322 | -0.12031 | 0.57794
|  | 10:35 | 14.9333 | -0.13283 | 0.57794
|  | 10:35 | 14.9344 | -0.13556 | 0.57794
|  | 10:36 | 14.9356 | -0.1383 | 0.57793
|  | 10:36 | 14.9367 | -0.13564 | 0.57793
|  | 10:36 | 14.9378 | -0.13119 | 0.57793
|  | 10:36 | 14.9389 | -0.1251 | 0.57793
|  | 10:36 | 14.94 | -0.11411 | 0.57792
|  | 10:36 | 14.9411 | -0.10312 | 0.57792
|  | 10:36 | 14.9422 | -0.087127 | 0.57792
|  | 10:36 | 14.9433 | -0.06947 | 0.57792
|  | 10:36 | 14.9444 | -0.057029 | 0.57791
|  | 10:36 | 14.9456 | -0.060235 | 0.57791
|  | 10:36 | 14.9467 | -0.06344 | 0.57791
|  | 10:36 | 14.9478 | -0.059529 | 0.57791
|  | 10:36 | 14.9489 | -0.053247 | 0.57791
|  | 10:36 | 14.95 | -0.048412 | 0.5779
|  | 10:36 | 14.9511 | -0.047923 | 0.5779
|  | 10:37 | 14.9522 | -0.047434 | 0.5779
|  | 10:37 | 14.9533 | -0.052124 | 0.5779
|  | 10:37 | 14.9544 | -0.05854 | 0.57789
|  | 10:37 | 14.9556 | -0.068618 | 0.57789
|  | 10:37 | 14.9567 | -0.08968 | 0.57789
|  | 10:37 | 14.9578 | -0.11074 | 0.57789
|  | 10:37 | 14.9589 | -0.12803 | 0.57788
|  | 10:37 | 14.96 | -0.14405 | 0.57788
|  | 10:37 | 14.9611 | -0.15587 | 0.57788
|  | 10:37 | 14.9622 | -0.15507 | 0.57788
|  | 10:37 | 14.9633 | -0.15427 | 0.57787
|  | 10:37 | 14.9644 | -0.1689 | 0.57787
|  | 10:37 | 14.9656 | -0.18867 | 0.57787
|  | 10:37 | 14.9667 | -0.19879 | 0.57787
|  | 10:37 | 14.9678 | -0.17995 | 0.57787
|  | 10:38 | 14.9689 | -0.16112 | 0.57786
|  | 10:38 | 14.97 | -0.14042 | 0.57786
|  | 10:38 | 14.9711 | -0.1191 | 0.57786
|  | 10:38 | 14.9722 | -0.087246 | 0.57786
|  | 10:38 | 14.9733 | -0.023777 | 0.57785
|  | 10:38 | 14.9744 | 0.039692 | 0.57785
|  | 10:38 | 14.9756 | 0.084628 | 0.57785
|  | 10:38 | 14.9767 | 0.12956 | 0.57785
|  | 10:38 | 14.9778 | 0.17372 | 0.57784
|  | 10:38 | 14.9789 | 0.21556 | 0.57784
|  | 10:38 | 14.98 | 0.2574 | 0.57784
|  | 10:38 | 14.9811 | 0.26371 | 0.57784
|  | 10:38 | 14.9822 | 0.25818 | 0.57784
|  | 10:38 | 14.9833 | 0.25264 | 0.57783
|  | 10:38 | 14.9844 | 0.24711 | 0.57783
|  | 10:39 | 14.9856 | 0.24157 | 0.57783
|  | 10:39 | 14.9867 | 0.24404 | 0.57783
|  | 10:39 | 14.9878 | 0.24918 | 0.57782
|  | 10:39 | 14.9889 | 0.25653 | 0.57782
|  | 10:39 | 14.99 | 0.27053 | 0.57782
|  | 10:39 | 14.9911 | 0.28454 | 0.57782
|  | 10:39 | 14.9922 | 0.28643 | 0.57781
|  | 10:39 | 14.9933 | 0.28428 | 0.57781
|  | 10:39 | 14.9944 | 0.28637 | 0.57781
|  | 10:39 | 14.9956 | 0.30114 | 0.57781
|  | 10:39 | 14.9967 | 0.31592 | 0.57781
|  | 10:39 | 14.9978 | 0.32289 | 0.5778
|  | 10:39 | 14.9989 | 0.32726 | 0.5778
|  | 10:39 | 15 | 0.32399 | 0.5778
|  | 10:39 | 15.0011 | 0.3131 | 0.5778
|  | 10:40 | 15.0022 | 0.3022 | 0.57779
|  | 10:40 | 15.0033 | 0.28574 | 0.57779
|  | 10:40 | 15.0044 | 0.26742 | 0.57779
|  | 10:40 | 15.0056 | 0.24996 | 0.57779
|  | 10:40 | 15.0067 | 0.23337 | 0.57778
|  | 10:40 | 15.0078 | 0.21678 | 0.57778
|  | 10:40 | 15.0089 | 0.18735 | 0.57778
|  | 10:40 | 15.01 | 0.15364 | 0.57778
|  | 10:40 | 15.0111 | 0.13899 | 0.57778
|  | 10:40 | 15.0122 | 0.1434 | 0.57777
|  | 10:40 | 15.0133 | 0.1478 | 0.57777
|  | 10:40 | 15.0144 | 0.16101 | 0.57777
|  | 10:40 | 15.0156 | 0.17715 | 0.57777
|  | 10:40 | 15.0167 | 0.1784 | 0.57776
|  | 10:40 | 15.0178 | 0.16474 | 0.57776
|  | 10:41 | 15.0189 | 0.15109 | 0.57776
|  | 10:41 | 15.02 | 0.12306 | 0.57776
|  | 10:41 | 15.0211 | 0.090241 | 0.57775
|  | 10:41 | 15.0222 | 0.056587 | 0.57775
|  | 10:41 | 15.0233 | 0.020429 | 0.57775
|  | 10:41 | 15.0244 | -0.015729 | 0.57775
|  | 10:41 | 15.0256 | -0.042232 | 0.57775
|  | 10:41 | 15.0267 | -0.065516 | 0.57774
|  | 10:41 | 15.0278 | -0.087599 | 0.57774
|  | 10:41 | 15.0289 | -0.10608 | 0.57774
|  | 10:41 | 15.03 | -0.12456 | 0.57774
|  | 10:41 | 15.0311 | -0.13921 | 0.57773
|  | 10:41 | 15.0322 | -0.15259 | 0.57773
|  | 10:41 | 15.0333 | -0.16354 | 0.57773
|  | 10:41 | 15.0344 | -0.16719 | 0.57773
|  | 10:42 | 15.0356 | -0.17083 | 0.57772
|  | 10:42 | 15.0367 | -0.19514 | 0.57772
|  | 10:42 | 15.0378 | -0.22632 | 0.57772
|  | 10:42 | 15.0389 | -0.24783 | 0.57772
|  | 10:42 | 15.04 | -0.24028 | 0.57772
|  | 10:42 | 15.0411 | -0.23273 | 0.57771
|  | 10:42 | 15.0422 | -0.22091 | 0.57771
|  | 10:42 | 15.0433 | -0.20767 | 0.57771
|  | 10:42 | 15.0444 | -0.19169 | 0.57771
|  | 10:42 | 15.0456 | -0.1675 | 0.5777
|  | 10:42 | 15.0467 | -0.14331 | 0.5777
|  | 10:42 | 15.0478 | -0.12658 | 0.5777
|  | 10:42 | 15.0489 | -0.11235 | 0.5777
|  | 10:42 | 15.05 | -0.099041 | 0.57769
|  | 10:42 | 15.0511 | -0.088485 | 0.57769
|  | 10:43 | 15.0522 | -0.077929 | 0.57769
|  | 10:43 | 15.0533 | -0.06405 | 0.57769
|  | 10:43 | 15.0544 | -0.049063 | 0.57769
|  | 10:43 | 15.0556 | -0.032325 | 0.57768
|  | 10:43 | 15.0567 | -0.01033 | 0.57768
|  | 10:43 | 15.0578 | 0.011664 | 0.57768
|  | 10:43 | 15.0589 | 0.025807 | 0.57768
|  | 10:43 | 15.06 | 0.037333 | 0.57767
|  | 10:43 | 15.0611 | 0.049144 | 0.57767
|  | 10:43 | 15.0622 | 0.06181 | 0.57767
|  | 10:43 | 15.0633 | 0.074475 | 0.57767
|  | 10:43 | 15.0644 | 0.088406 | 0.57766
|  | 10:43 | 15.0656 | 0.10276 | 0.57766
|  | 10:43 | 15.0667 | 0.11637 | 0.57766
|  | 10:43 | 15.0678 | 0.12776 | 0.57766
|  | 10:44 | 15.0689 | 0.13916 | 0.57766
|  | 10:44 | 15.07 | 0.15333 | 0.57765
|  | 10:44 | 15.0711 | 0.16843 | 0.57765
|  | 10:44 | 15.0722 | 0.18226 | 0.57765
|  | 10:44 | 15.0733 | 0.19228 | 0.57765
|  | 10:44 | 15.0744 | 0.20229 | 0.57764
|  | 10:44 | 15.0756 | 0.18703 | 0.57764
|  | 10:44 | 15.0767 | 0.17176 | 0.57764
|  | 10:44 | 15.0778 | 0.15361 | 0.57764
|  | 10:44 | 15.0789 | 0.12677 | 0.57763
|  | 10:44 | 15.08 | 0.099932 | 0.57763
|  | 10:44 | 15.0811 | 0.080254 | 0.57763
|  | 10:44 | 15.0822 | 0.062962 | 0.57763
|  | 10:44 | 15.0833 | 0.049071 | 0.57762
|  | 10:44 | 15.0844 | 0.045383 | 0.57762
|  | 10:45 | 15.0856 | 0.041695 | 0.57762
|  | 10:45 | 15.0867 | 0.032198 | 0.57762
|  | 10:45 | 15.0878 | 0.020765 | 0.57762
|  | 10:45 | 15.0889 | 0.010218 | 0.57761
|  | 10:45 | 15.09 | 0.0023298 | 0.57761
|  | 10:45 | 15.0911 | -0.0055582 | 0.57761
|  | 10:45 | 15.0922 | -0.023576 | 0.57761
|  | 10:45 | 15.0933 | -0.04497 | 0.5776
|  | 10:45 | 15.0944 | -0.063236 | 0.5776
|  | 10:45 | 15.0956 | -0.072119 | 0.5776
|  | 10:45 | 15.0967 | -0.081002 | 0.5776
|  | 10:45 | 15.0978 | -0.091497 | 0.57759
|  | 10:45 | 15.0989 | -0.10253 | 0.57759
|  | 10:45 | 15.1 | -0.11184 | 0.57759
|  | 10:45 | 15.1011 | -0.11599 | 0.57759
|  | 10:46 | 15.1022 | -0.12014 | 0.57759
|  | 10:46 | 15.1033 | -0.12608 | 0.57758
|  | 10:46 | 15.1044 | -0.13383 | 0.57758
|  | 10:46 | 15.1056 | -0.14157 | 0.57758
|  | 10:46 | 15.1067 | -0.14002 | 0.57758
|  | 10:46 | 15.1078 | -0.13847 | 0.57757
|  | 10:46 | 15.1089 | -0.14396 | 0.57757
|  | 10:46 | 15.11 | -0.1565 | 0.57757
|  | 10:46 | 15.1111 | -0.16904 | 0.57757
|  | 10:46 | 15.1122 | -0.18405 | 0.57756
|  | 10:46 | 15.1133 | -0.19905 | 0.57756
|  | 10:46 | 15.1144 | -0.20539 | 0.57756
|  | 10:46 | 15.1156 | -0.20306 | 0.57756
|  | 10:46 | 15.1167 | -0.20073 | 0.57756
|  | 10:46 | 15.1178 | -0.17283 | 0.57755
|  | 10:47 | 15.1189 | -0.14493 | 0.57755
|  | 10:47 | 15.12 | -0.1155 | 0.57755
|  | 10:47 | 15.1211 | -0.084542 | 0.57755
|  | 10:47 | 15.1222 | -0.053583 | 0.57754
|  | 10:47 | 15.1233 | -0.01823 | 0.57754
|  | 10:47 | 15.1244 | 0.017124 | 0.57754
|  | 10:47 | 15.1256 | 0.042132 | 0.57754
|  | 10:47 | 15.1267 | 0.056796 | 0.57753
|  | 10:47 | 15.1278 | 0.07146 | 0.57753
|  | 10:47 | 15.1289 | 0.069582 | 0.57753
|  | 10:47 | 15.13 | 0.067705 | 0.57753
|  | 10:47 | 15.1311 | 0.068706 | 0.57753
|  | 10:47 | 15.1322 | 0.072586 | 0.57752
|  | 10:47 | 15.1333 | 0.076467 | 0.57752
|  | 10:47 | 15.1344 | 0.08665 | 0.57752
|  | 10:48 | 15.1356 | 0.096832 | 0.57752
|  | 10:48 | 15.1367 | 0.097433 | 0.57751
|  | 10:48 | 15.1378 | 0.088452 | 0.57751
|  | 10:48 | 15.1389 | 0.079471 | 0.57751
|  | 10:48 | 15.14 | 0.07049 | 0.57751
|  | 10:48 | 15.1411 | 0.061509 | 0.5775
|  | 10:48 | 15.1422 | 0.044761 | 0.5775
|  | 10:48 | 15.1433 | 0.020245 | 0.5775
|  | 10:48 | 15.1444 | -0.0042709 | 0.5775
|  | 10:48 | 15.1456 | -0.0071686 | 0.5775
|  | 10:48 | 15.1467 | -0.010066 | 0.57749
|  | 10:48 | 15.1478 | -0.015785 | 0.57749
|  | 10:48 | 15.1489 | -0.024325 | 0.57749
|  | 10:48 | 15.15 | -0.032865 | 0.57749
|  | 10:48 | 15.1511 | -0.041405 | 0.57748
|  | 10:49 | 15.1522 | -0.049945 | 0.57748
|  | 10:49 | 15.1533 | -0.061732 | 0.57748
|  | 10:49 | 15.1544 | -0.076764 | 0.57748
|  | 10:49 | 15.1556 | -0.091797 | 0.57747
|  | 10:49 | 15.1567 | -0.081949 | 0.57747
|  | 10:49 | 15.1578 | -0.072101 | 0.57747
|  | 10:49 | 15.1589 | -0.069993 | 0.57747
|  | 10:49 | 15.16 | -0.075625 | 0.57747
|  | 10:49 | 15.1611 | -0.081256 | 0.57746
|  | 10:49 | 15.1622 | -0.10398 | 0.57746
|  | 10:49 | 15.1633 | -0.12671 | 0.57746
|  | 10:49 | 15.1644 | -0.13424 | 0.57746
|  | 10:49 | 15.1656 | -0.13671 | 0.57745
|  | 10:49 | 15.1667 | -0.13917 | 0.57745
|  | 10:49 | 15.1678 | -0.13967 | 0.57745
|  | 10:50 | 15.1689 | -0.14016 | 0.57745
|  | 10:50 | 15.17 | -0.13967 | 0.57744
|  | 10:50 | 15.1711 | -0.1382 | 0.57744
|  | 10:50 | 15.1722 | -0.13672 | 0.57744
|  | 10:50 | 15.1733 | -0.13986 | 0.57744
|  | 10:50 | 15.1744 | -0.143 | 0.57744
|  | 10:50 | 15.1756 | -0.15783 | 0.57743
|  | 10:50 | 15.1767 | -0.18435 | 0.57743
|  | 10:50 | 15.1778 | -0.21088 | 0.57743
|  | 10:50 | 15.1789 | -0.23015 | 0.57743
|  | 10:50 | 15.18 | -0.24943 | 0.57742
|  | 10:50 | 15.1811 | -0.27026 | 0.57742
|  | 10:50 | 15.1822 | -0.29265 | 0.57742
|  | 10:50 | 15.1833 | -0.31503 | 0.57742
|  | 10:50 | 15.1844 | -0.32195 | 0.57741
|  | 10:51 | 15.1856 | -0.32886 | 0.57741
|  | 10:51 | 15.1867 | -0.34119 | 0.57741
|  | 10:51 | 15.1878 | -0.35894 | 0.57741
|  | 10:51 | 15.1889 | -0.37669 | 0.57741
|  | 10:51 | 15.19 | -0.40678 | 0.5774
|  | 10:51 | 15.1911 | -0.43687 | 0.5774
|  | 10:51 | 15.1922 | -0.47126 | 0.5774
|  | 10:51 | 15.1933 | -0.50996 | 0.5774
|  | 10:51 | 15.1944 | -0.54865 | 0.57739
|  | 10:51 | 15.1956 | -0.56956 | 0.57739
|  | 10:51 | 15.1967 | -0.59046 | 0.57739
|  | 10:51 | 15.1978 | -0.60099 | 0.57739
|  | 10:51 | 15.1989 | -0.60114 | 0.57738
|  | 10:51 | 15.2 | -0.60129 | 0.57738
|  | 10:51 | 15.2011 | -0.60725 | 0.57738
|  | 10:52 | 15.2022 | -0.6132 | 0.57738
|  | 10:52 | 15.2033 | -0.61495 | 0.57737
|  | 10:52 | 15.2044 | -0.6125 | 0.57737
|  | 10:52 | 15.2056 | -0.61004 | 0.57737
|  | 10:52 | 15.2067 | -0.60192 | 0.57737
|  | 10:52 | 15.2078 | -0.59379 | 0.57737
|  | 10:52 | 15.2089 | -0.57338 | 0.57736
|  | 10:52 | 15.21 | -0.54068 | 0.57736
|  | 10:52 | 15.2111 | -0.50798 | 0.57736
|  | 10:52 | 15.2122 | -0.44948 | 0.57736
|  | 10:52 | 15.2133 | -0.39097 | 0.57735
|  | 10:52 | 15.2144 | -0.34491 | 0.57735
|  | 10:52 | 15.2156 | -0.30298 | 0.57735
|  | 10:52 | 15.2167 | -0.26106 | 0.57735
|  | 10:52 | 15.2178 | -0.21372 | 0.57734
|  | 10:53 | 15.2189 | -0.16637 | 0.57734
|  | 10:53 | 15.22 | -0.13138 | 0.57734
|  | 10:53 | 15.2211 | -0.10875 | 0.57734
|  | 10:53 | 15.2222 | -0.086123 | 0.57734
|  | 10:53 | 15.2233 | -0.059309 | 0.57733
|  | 10:53 | 15.2244 | -0.032495 | 0.57733
|  | 10:53 | 15.2256 | -0.0085625 | 0.57733
|  | 10:53 | 15.2267 | 0.01441 | 0.57733
|  | 10:53 | 15.2278 | 0.037382 | 0.57732
|  | 10:53 | 15.2289 | 0.066252 | 0.57732
|  | 10:53 | 15.23 | 0.095122 | 0.57732
|  | 10:53 | 15.2311 | 0.10872 | 0.57732
|  | 10:53 | 15.2322 | 0.10704 | 0.57731
|  | 10:53 | 15.2333 | 0.10536 | 0.57731
|  | 10:53 | 15.2344 | 0.10089 | 0.57731
|  | 10:54 | 15.2356 | 0.088038 | 0.57731
|  | 10:54 | 15.2367 | 0.080428 | 0.57731
|  | 10:54 | 15.2378 | 0.078054 | 0.5773
|  | 10:54 | 15.2389 | 0.07568 | 0.5773
|  | 10:54 | 15.24 | 0.060873 | 0.5773
|  | 10:54 | 15.2411 | 0.046067 | 0.5773
|  | 10:54 | 15.2422 | 0.032489 | 0.57729
|  | 10:54 | 15.2433 | 0.02014 | 0.57729
|  | 10:54 | 15.2444 | 0.0077913 | 0.57729
|  | 10:54 | 15.2456 | 0.0089382 | 0.57729
|  | 10:54 | 15.2467 | 0.010085 | 0.57728
|  | 10:54 | 15.2478 | 0.017944 | 0.57728
|  | 10:54 | 15.2489 | 0.032514 | 0.57728
|  | 10:54 | 15.25 | 0.047085 | 0.57728
|  | 10:54 | 15.2511 | 0.076109 | 0.57728
|  | 10:55 | 15.2522 | 0.10513 | 0.57727
|  | 10:55 | 15.2533 | 0.13867 | 0.57727
|  | 10:55 | 15.2544 | 0.17371 | 0.57727
|  | 10:55 | 15.2556 | 0.20875 | 0.57727
|  | 10:55 | 15.2567 | 0.23334 | 0.57726
|  | 10:55 | 15.2578 | 0.25792 | 0.57726
|  | 10:55 | 15.2589 | 0.27615 | 0.57726
|  | 10:55 | 15.26 | 0.28804 | 0.57726
|  | 10:55 | 15.2611 | 0.29992 | 0.57725
|  | 10:55 | 15.2622 | 0.31798 | 0.57725
|  | 10:55 | 15.2633 | 0.33605 | 0.57725
|  | 10:55 | 15.2644 | 0.36385 | 0.57725
|  | 10:55 | 15.2656 | 0.40137 | 0.57725
|  | 10:55 | 15.2667 | 0.4389 | 0.57724
|  | 10:55 | 15.2678 | 0.47837 | 0.57724
|  | 10:56 | 15.2689 | 0.51784 | 0.57724
|  | 10:56 | 15.27 | 0.54605 | 0.57724
|  | 10:56 | 15.2711 | 0.57051 | 0.57723
|  | 10:56 | 15.2722 | 0.59043 | 0.57723
|  | 10:56 | 15.2733 | 0.59672 | 0.57723
|  | 10:56 | 15.2744 | 0.60301 | 0.57723
|  | 10:56 | 15.2756 | 0.61476 | 0.57722
|  | 10:56 | 15.2767 | 0.62833 | 0.57722
|  | 10:56 | 15.2778 | 0.63908 | 0.57722
|  | 10:56 | 15.2789 | 0.64134 | 0.57722
|  | 10:56 | 15.28 | 0.6436 | 0.57722
|  | 10:56 | 15.2811 | 0.64966 | 0.57721
|  | 10:56 | 15.2822 | 0.65699 | 0.57721
|  | 10:56 | 15.2833 | 0.66861 | 0.57721
|  | 10:56 | 15.2844 | 0.69311 | 0.57721
|  | 10:57 | 15.2856 | 0.71761 | 0.5772
|  | 10:57 | 15.2867 | 0.72431 | 0.5772
|  | 10:57 | 15.2878 | 0.72507 | 0.5772
|  | 10:57 | 15.2889 | 0.72324 | 0.5772
|  | 10:57 | 15.29 | 0.71361 | 0.57719
|  | 10:57 | 15.2911 | 0.70399 | 0.57719
|  | 10:57 | 15.2922 | 0.68391 | 0.57719
|  | 10:57 | 15.2933 | 0.66036 | 0.57719
|  | 10:57 | 15.2944 | 0.63042 | 0.57719
|  | 10:57 | 15.2956 | 0.58134 | 0.57718
|  | 10:57 | 15.2967 | 0.53226 | 0.57718
|  | 10:57 | 15.2978 | 0.48119 | 0.57718
|  | 10:57 | 15.2989 | 0.42944 | 0.57718
|  | 10:57 | 15.3 | 0.38903 | 0.57717
|  | 10:57 | 15.3011 | 0.35995 | 0.57717
|  | 10:58 | 15.3022 | 0.33088 | 0.57717
|  | 10:58 | 15.3033 | 0.2821 | 0.57717
|  | 10:58 | 15.3044 | 0.22676 | 0.57716
|  | 10:58 | 15.3056 | 0.17658 | 0.57716
|  | 10:58 | 15.3067 | 0.1419 | 0.57716
|  | 10:58 | 15.3078 | 0.10722 | 0.57716
|  | 10:58 | 15.3089 | 0.081901 | 0.57716
|  | 10:58 | 15.31 | 0.056586 | 0.57715
|  | 10:58 | 15.3111 | 0.030142 | 0.57715
|  | 10:58 | 15.3122 | 0.00031549 | 0.57715
|  | 10:58 | 15.3133 | -0.029511 | 0.57715
|  | 10:58 | 15.3144 | -0.058698 | 0.57714
|  | 10:58 | 15.3156 | -0.087671 | 0.57714
|  | 10:58 | 15.3167 | -0.11306 | 0.57714
|  | 10:58 | 15.3178 | -0.12771 | 0.57714
|  | 10:59 | 15.3189 | -0.14236 | 0.57713
|  | 10:59 | 15.32 | -0.16624 | 0.57713
|  | 10:59 | 15.3211 | -0.1932 | 0.57713
|  | 10:59 | 15.3222 | -0.22575 | 0.57713
|  | 10:59 | 15.3233 | -0.2751 | 0.57712
|  | 10:59 | 15.3244 | -0.32445 | 0.57712
|  | 10:59 | 15.3256 | -0.35449 | 0.57712
|  | 10:59 | 15.3267 | -0.37809 | 0.57712
|  | 10:59 | 15.3278 | -0.39723 | 0.57712
|  | 10:59 | 15.3289 | -0.40298 | 0.57711
|  | 10:59 | 15.33 | -0.40874 | 0.57711
|  | 10:59 | 15.3311 | -0.41121 | 0.57711
|  | 10:59 | 15.3322 | -0.41258 | 0.57711
|  | 10:59 | 15.3333 | -0.4191 | 0.5771
|  | 10:59 | 15.3344 | -0.44105 | 0.5771
|  | 11:00 | 15.3356 | -0.46301 | 0.5771
|  | 11:00 | 15.3367 | -0.4794 | 0.5771
|  | 11:00 | 15.3378 | -0.49394 | 0.57709
|  | 11:00 | 15.3389 | -0.50803 | 0.57709
|  | 11:00 | 15.34 | -0.52082 | 0.57709
|  | 11:00 | 15.3411 | -0.53361 | 0.57709
|  | 11:00 | 15.3422 | -0.57167 | 0.57709
|  | 11:00 | 15.3433 | -0.61817 | 0.57708
|  | 11:00 | 15.3444 | -0.65686 | 0.57708
|  | 11:00 | 15.3456 | -0.67212 | 0.57708
|  | 11:00 | 15.3467 | -0.68739 | 0.57708
|  | 11:00 | 15.3478 | -0.69862 | 0.57707
|  | 11:00 | 15.3489 | -0.7085 | 0.57707
|  | 11:00 | 15.35 | -0.7136 | 0.57707
|  | 11:00 | 15.3511 | -0.70432 | 0.57707
|  | 11:01 | 15.3522 | -0.69505 | 0.57706
|  | 11:01 | 15.3533 | -0.67207 | 0.57706
|  | 11:01 | 15.3544 | -0.64451 | 0.57706
|  | 11:01 | 15.3556 | -0.61836 | 0.57706
|  | 11:01 | 15.3567 | -0.59644 | 0.57706
|  | 11:01 | 15.3578 | -0.57451 | 0.57705
|  | 11:01 | 15.3589 | -0.55325 | 0.57705
|  | 11:01 | 15.36 | -0.53222 | 0.57705
|  | 11:01 | 15.3611 | -0.51696 | 0.57705
|  | 11:01 | 15.3622 | -0.51903 | 0.57704
|  | 11:01 | 15.3633 | -0.5211 | 0.57704
|  | 11:01 | 15.3644 | -0.52402 | 0.57704
|  | 11:01 | 15.3656 | -0.52724 | 0.57704
|  | 11:01 | 15.3667 | -0.52781 | 0.57703
|  | 11:01 | 15.3678 | -0.52046 | 0.57703
|  | 11:02 | 15.3689 | -0.51311 | 0.57703
|  | 11:02 | 15.37 | -0.49295 | 0.57703
|  | 11:02 | 15.3711 | -0.46852 | 0.57703
|  | 11:02 | 15.3722 | -0.44277 | 0.57702
|  | 11:02 | 15.3733 | -0.41302 | 0.57702
|  | 11:02 | 15.3744 | -0.38327 | 0.57702
|  | 11:02 | 15.3756 | -0.36219 | 0.57702
|  | 11:02 | 15.3767 | -0.34399 | 0.57701
|  | 11:02 | 15.3778 | -0.32331 | 0.57701
|  | 11:02 | 15.3789 | -0.29521 | 0.57701
|  | 11:02 | 15.38 | -0.26711 | 0.57701
|  | 11:02 | 15.3811 | -0.22818 | 0.577
|  | 11:02 | 15.3822 | -0.18565 | 0.577
|  | 11:02 | 15.3833 | -0.14681 | 0.577
|  | 11:02 | 15.3844 | -0.11909 | 0.577
|  | 11:03 | 15.3856 | -0.091362 | 0.577
|  | 11:03 | 15.3867 | -0.063635 | 0.57699
|  | 11:03 | 15.3878 | -0.035909 | 0.57699
|  | 11:03 | 15.3889 | -0.010399 | 0.57699
|  | 11:03 | 15.39 | 0.008462 | 0.57699
|  | 11:03 | 15.3911 | 0.027323 | 0.57698
|  | 11:03 | 15.3922 | 0.034398 | 0.57698
|  | 11:03 | 15.3933 | 0.037546 | 0.57698
|  | 11:03 | 15.3944 | 0.043552 | 0.57698
|  | 11:03 | 15.3956 | 0.058133 | 0.57697
|  | 11:03 | 15.3967 | 0.072714 | 0.57697
|  | 11:03 | 15.3978 | 0.058027 | 0.57697
|  | 11:03 | 15.3989 | 0.033585 | 0.57697
|  | 11:03 | 15.4 | 0.0091424 | 0.57697
|  | 11:03 | 15.4011 | -0.0069915 | 0.57696
|  | 11:04 | 15.4022 | -0.014817 | 0.57696
|  | 11:04 | 15.4033 | -0.013008 | 0.57696
|  | 11:04 | 15.4044 | -0.0079873 | 0.57696
|  | 11:04 | 15.4056 | -0.0032145 | 0.57695
|  | 11:04 | 15.4067 | 0.00081442 | 0.57695
|  | 11:04 | 15.4078 | 0.0048433 | 0.57695
|  | 11:04 | 15.4089 | -0.011699 | 0.57695
|  | 11:04 | 15.41 | -0.035099 | 0.57694
|  | 11:04 | 15.4111 | -0.062149 | 0.57694
|  | 11:04 | 15.4122 | -0.10015 | 0.57694
|  | 11:04 | 15.4133 | -0.13814 | 0.57694
|  | 11:04 | 15.4144 | -0.15922 | 0.57694
|  | 11:04 | 15.4156 | -0.17466 | 0.57693
|  | 11:04 | 15.4167 | -0.18651 | 0.57693
|  | 11:04 | 15.4178 | -0.18759 | 0.57693
|  | 11:05 | 15.4189 | -0.18868 | 0.57693
|  | 11:05 | 15.42 | -0.16432 | 0.57692
|  | 11:05 | 15.4211 | -0.13147 | 0.57692
|  | 11:05 | 15.4222 | -0.097254 | 0.57692
|  | 11:05 | 15.4233 | -0.058911 | 0.57692
|  | 11:05 | 15.4244 | -0.020569 | 0.57691
|  | 11:05 | 15.4256 | 0.017096 | 0.57691
|  | 11:05 | 15.4267 | 0.054534 | 0.57691
|  | 11:05 | 15.4278 | 0.085579 | 0.57691
|  | 11:05 | 15.4289 | 0.097447 | 0.57691
|  | 11:05 | 15.43 | 0.10931 | 0.5769
|  | 11:05 | 15.4311 | 0.11074 | 0.5769
|  | 11:05 | 15.4322 | 0.10868 | 0.5769
|  | 11:05 | 15.4333 | 0.10522 | 0.5769
|  | 11:05 | 15.4344 | 0.097578 | 0.57689
|  | 11:06 | 15.4356 | 0.089932 | 0.57689
|  | 11:06 | 15.4367 | 0.073569 | 0.57689
|  | 11:06 | 15.4378 | 0.048491 | 0.57689
|  | 11:06 | 15.4389 | 0.023412 | 0.57688
|  | 11:06 | 15.44 | 0.0095454 | 0.57688
|  | 11:06 | 15.4411 | -0.0043213 | 0.57688
|  | 11:06 | 15.4422 | -0.0022857 | 0.57688
|  | 11:06 | 15.4433 | 0.015652 | 0.57687
|  | 11:06 | 15.4444 | 0.03359 | 0.57687
|  | 11:06 | 15.4456 | 0.10038 | 0.57687
|  | 11:06 | 15.4467 | 0.16717 | 0.57687
|  | 11:06 | 15.4478 | 0.23184 | 0.57687
|  | 11:06 | 15.4489 | 0.29437 | 0.57686
|  | 11:06 | 15.45 | 0.35691 | 0.57686
|  | 11:06 | 15.4511 | 0.38203 | 0.57686
|  | 11:07 | 15.4522 | 0.40715 | 0.57686
|  | 11:07 | 15.4533 | 0.43669 | 0.57685
|  | 11:07 | 15.4544 | 0.47067 | 0.57685
|  | 11:07 | 15.4556 | 0.50464 | 0.57685
|  | 11:07 | 15.4567 | 0.51512 | 0.57685
|  | 11:07 | 15.4578 | 0.52559 | 0.57684
|  | 11:07 | 15.4589 | 0.54013 | 0.57684
|  | 11:07 | 15.46 | 0.55874 | 0.57684
|  | 11:07 | 15.4611 | 0.57735 | 0.57684
|  | 11:07 | 15.4622 | 0.57414 | 0.57684
|  | 11:07 | 15.4633 | 0.57092 | 0.57683
|  | 11:07 | 15.4644 | 0.57038 | 0.57683
|  | 11:07 | 15.4656 | 0.57251 | 0.57683
|  | 11:07 | 15.4667 | 0.57464 | 0.57683
|  | 11:07 | 15.4678 | 0.57446 | 0.57682
|  | 11:08 | 15.4689 | 0.57428 | 0.57682
|  | 11:08 | 15.47 | 0.56794 | 0.57682
|  | 11:08 | 15.4711 | 0.55544 | 0.57682
|  | 11:08 | 15.4722 | 0.54294 | 0.57681
|  | 11:08 | 15.4733 | 0.53362 | 0.57681
|  | 11:08 | 15.4744 | 0.52431 | 0.57681
|  | 11:08 | 15.4756 | 0.51346 | 0.57681
|  | 11:08 | 15.4767 | 0.50109 | 0.57681
|  | 11:08 | 15.4778 | 0.48871 | 0.5768
|  | 11:08 | 15.4789 | 0.46532 | 0.5768
|  | 11:08 | 15.48 | 0.44193 | 0.5768
|  | 11:08 | 15.4811 | 0.41736 | 0.5768
|  | 11:08 | 15.4822 | 0.39241 | 0.57679
|  | 11:08 | 15.4833 | 0.36745 | 0.57679
|  | 11:08 | 15.4844 | 0.32955 | 0.57679
|  | 11:09 | 15.4856 | 0.29165 | 0.57679
|  | 11:09 | 15.4867 | 0.25312 | 0.57678
|  | 11:09 | 15.4878 | 0.21396 | 0.57678
|  | 11:09 | 15.4889 | 0.1748 | 0.57678
|  | 11:09 | 15.49 | 0.11481 | 0.57678
|  | 11:09 | 15.4911 | 0.054818 | 0.57678
|  | 11:09 | 15.4922 | -0.0065868 | 0.57677
|  | 11:09 | 15.4933 | -0.068462 | 0.57677
|  | 11:09 | 15.4944 | -0.13034 | 0.57677
|  | 11:09 | 15.4956 | -0.17611 | 0.57677
|  | 11:09 | 15.4967 | -0.22189 | 0.57676
|  | 11:09 | 15.4978 | -0.26715 | 0.57676
|  | 11:09 | 15.4989 | -0.3119 | 0.57676
|  | 11:09 | 15.5 | -0.35665 | 0.57676
|  | 11:09 | 15.5011 | -0.39577 | 0.57675
|  | 11:10 | 15.5022 | -0.43489 | 0.57675
|  | 11:10 | 15.5033 | -0.45765 | 0.57675
|  | 11:10 | 15.5044 | -0.46406 | 0.57675
|  | 11:10 | 15.5056 | -0.47047 | 0.57675
|  | 11:10 | 15.5067 | -0.45239 | 0.57674
|  | 11:10 | 15.5078 | -0.4343 | 0.57674
|  | 11:10 | 15.5089 | -0.42879 | 0.57674
|  | 11:10 | 15.51 | -0.43588 | 0.57674
|  | 11:10 | 15.5111 | -0.44296 | 0.57673
|  | 11:10 | 15.5122 | -0.44646 | 0.57673
|  | 11:10 | 15.5133 | -0.44997 | 0.57673
|  | 11:10 | 15.5144 | -0.44712 | 0.57673
|  | 11:10 | 15.5156 | -0.43794 | 0.57672
|  | 11:10 | 15.5167 | -0.42875 | 0.57672
|  | 11:10 | 15.5178 | -0.42518 | 0.57672
|  | 11:11 | 15.5189 | -0.42161 | 0.57672
|  | 11:11 | 15.52 | -0.42556 | 0.57672
|  | 11:11 | 15.5211 | -0.43704 | 0.57671
|  | 11:11 | 15.5222 | -0.44852 | 0.57671
|  | 11:11 | 15.5233 | -0.44164 | 0.57671
|  | 11:11 | 15.5244 | -0.43475 | 0.57671
|  | 11:11 | 15.5256 | -0.42925 | 0.5767
|  | 11:11 | 15.5267 | -0.42513 | 0.5767
|  | 11:11 | 15.5278 | -0.421 | 0.5767
|  | 11:11 | 15.5289 | -0.40086 | 0.5767
|  | 11:11 | 15.53 | -0.38072 | 0.57669
|  | 11:11 | 15.5311 | -0.36457 | 0.57669
|  | 11:11 | 15.5322 | -0.35242 | 0.57669
|  | 11:11 | 15.5333 | -0.34187 | 0.57669
|  | 11:11 | 15.5344 | -0.33616 | 0.57669
|  | 11:12 | 15.5356 | -0.33044 | 0.57668
|  | 11:12 | 15.5367 | -0.31632 | 0.57668
|  | 11:12 | 15.5378 | -0.29381 | 0.57668
|  | 11:12 | 15.5389 | -0.2713 | 0.57668
|  | 11:12 | 15.54 | -0.25262 | 0.57667
|  | 11:12 | 15.5411 | -0.23394 | 0.57667
|  | 11:12 | 15.5422 | -0.21066 | 0.57667
|  | 11:12 | 15.5433 | -0.18278 | 0.57667
|  | 11:12 | 15.5444 | -0.1549 | 0.57666
|  | 11:12 | 15.5456 | -0.1598 | 0.57666
|  | 11:12 | 15.5467 | -0.1647 | 0.57666
|  | 11:12 | 15.5478 | -0.16862 | 0.57666
|  | 11:12 | 15.5489 | -0.17156 | 0.57666
|  | 11:12 | 15.55 | -0.17451 | 0.57665
|  | 11:12 | 15.5511 | -0.16854 | 0.57665
|  | 11:13 | 15.5522 | -0.16258 | 0.57665
|  | 11:13 | 15.5533 | -0.16124 | 0.57665
|  | 11:13 | 15.5544 | -0.16454 | 0.57664
|  | 11:13 | 15.5556 | -0.16783 | 0.57664
|  | 11:13 | 15.5567 | -0.15843 | 0.57664
|  | 11:13 | 15.5578 | -0.14903 | 0.57664
|  | 11:13 | 15.5589 | -0.12965 | 0.57663
|  | 11:13 | 15.56 | -0.10029 | 0.57663
|  | 11:13 | 15.5611 | -0.070943 | 0.57663
|  | 11:13 | 15.5622 | -0.066805 | 0.57663
|  | 11:13 | 15.5633 | -0.062667 | 0.57662
|  | 11:13 | 15.5644 | -0.054492 | 0.57662
|  | 11:13 | 15.5656 | -0.042281 | 0.57662
|  | 11:13 | 15.5667 | -0.030069 | 0.57662
|  | 11:13 | 15.5678 | -0.017858 | 0.57662
|  | 11:14 | 15.5689 | 0.0074794 | 0.57661
|  | 11:14 | 15.57 | 0.030449 | 0.57661
|  | 11:14 | 15.5711 | 0.046317 | 0.57661
|  | 11:14 | 15.5722 | 0.062185 | 0.57661
|  | 11:14 | 15.5733 | 0.082672 | 0.5766
|  | 11:14 | 15.5744 | 0.10316 | 0.5766
|  | 11:14 | 15.5756 | 0.12318 | 0.5766
|  | 11:14 | 15.5767 | 0.14273 | 0.5766
|  | 11:14 | 15.5778 | 0.16229 | 0.57659
|  | 11:14 | 15.5789 | 0.17597 | 0.57659
|  | 11:14 | 15.58 | 0.18965 | 0.57659
|  | 11:14 | 15.5811 | 0.21106 | 0.57659
|  | 11:14 | 15.5822 | 0.24018 | 0.57659
|  | 11:14 | 15.5833 | 0.2693 | 0.57658
|  | 11:14 | 15.5844 | 0.28985 | 0.57658
|  | 11:15 | 15.5856 | 0.3104 | 0.57658
|  | 11:15 | 15.5867 | 0.32411 | 0.57658
|  | 11:15 | 15.5878 | 0.33098 | 0.57657
|  | 11:15 | 15.5889 | 0.33785 | 0.57657
|  | 11:15 | 15.59 | 0.3406 | 0.57657
|  | 11:15 | 15.5911 | 0.34335 | 0.57657
|  | 11:15 | 15.5922 | 0.34433 | 0.57656
|  | 11:15 | 15.5933 | 0.34356 | 0.57656
|  | 11:15 | 15.5944 | 0.34278 | 0.57656
|  | 11:15 | 15.5956 | 0.3594 | 0.57656
|  | 11:15 | 15.5967 | 0.37602 | 0.57656
|  | 11:15 | 15.5978 | 0.39263 | 0.57655
|  | 11:15 | 15.5989 | 0.40925 | 0.57655
|  | 11:15 | 15.6 | 0.42587 | 0.57655
|  | 11:15 | 15.6011 | 0.4182 | 0.57655
|  | 11:16 | 15.6022 | 0.41053 | 0.57654
|  | 11:16 | 15.6033 | 0.39842 | 0.57654
|  | 11:16 | 15.6044 | 0.38187 | 0.57654
|  | 11:16 | 15.6056 | 0.36532 | 0.57654
|  | 11:16 | 15.6067 | 0.33087 | 0.57653
|  | 11:16 | 15.6078 | 0.29642 | 0.57653
|  | 11:16 | 15.6089 | 0.28083 | 0.57653
|  | 11:16 | 15.61 | 0.28412 | 0.57653
|  | 11:16 | 15.6111 | 0.2874 | 0.57653
|  | 11:16 | 15.6122 | 0.2724 | 0.57652
|  | 11:16 | 15.6133 | 0.2574 | 0.57652
|  | 11:16 | 15.6144 | 0.2361 | 0.57652
|  | 11:16 | 15.6156 | 0.2085 | 0.57652
|  | 11:16 | 15.6167 | 0.18089 | 0.57651
|  | 11:16 | 15.6178 | 0.14929 | 0.57651
|  | 11:17 | 15.6189 | 0.11769 | 0.57651
|  | 11:17 | 15.62 | 0.10424 | 0.57651
|  | 11:17 | 15.6211 | 0.096831 | 0.5765
|  | 11:17 | 15.6222 | 0.089426 | 0.5765
|  | 11:17 | 15.6233 | 0.072852 | 0.5765
|  | 11:17 | 15.6244 | 0.056277 | 0.5765
|  | 11:17 | 15.6256 | 0.041294 | 0.5765
|  | 11:17 | 15.6267 | 0.027902 | 0.57649
|  | 11:17 | 15.6278 | 0.01451 | 0.57649
|  | 11:17 | 15.6289 | -0.0091688 | 0.57649
|  | 11:17 | 15.63 | -0.032848 | 0.57649
|  | 11:17 | 15.6311 | -0.066966 | 0.57648
|  | 11:17 | 15.6322 | -0.11152 | 0.57648
|  | 11:17 | 15.6333 | -0.15608 | 0.57648
|  | 11:17 | 15.6344 | -0.17782 | 0.57648
|  | 11:18 | 15.6356 | -0.19956 | 0.57647
|  | 11:18 | 15.6367 | -0.21505 | 0.57647
|  | 11:18 | 15.6378 | -0.2243 | 0.57647
|  | 11:18 | 15.6389 | -0.23485 | 0.57647
|  | 11:18 | 15.64 | -0.24933 | 0.57647
|  | 11:18 | 15.6411 | -0.26381 | 0.57646
|  | 11:18 | 15.6422 | -0.28585 | 0.57646
|  | 11:18 | 15.6433 | -0.31041 | 0.57646
|  | 11:18 | 15.6444 | -0.33498 | 0.57646
|  | 11:18 | 15.6456 | -0.35433 | 0.57645
|  | 11:18 | 15.6467 | -0.37369 | 0.57645
|  | 11:18 | 15.6478 | -0.38334 | 0.57645
|  | 11:18 | 15.6489 | -0.38329 | 0.57645
|  | 11:18 | 15.65 | -0.38325 | 0.57644
|  | 11:18 | 15.6511 | -0.37177 | 0.57644
|  | 11:19 | 15.6522 | -0.36028 | 0.57644
|  | 11:19 | 15.6533 | -0.34955 | 0.57644
|  | 11:19 | 15.6544 | -0.33956 | 0.57644
|  | 11:19 | 15.6556 | -0.32957 | 0.57643
|  | 11:19 | 15.6567 | -0.32282 | 0.57643
|  | 11:19 | 15.6578 | -0.31608 | 0.57643
|  | 11:19 | 15.6589 | -0.30933 | 0.57643
|  | 11:19 | 15.66 | -0.30258 | 0.57642
|  | 11:19 | 15.6611 | -0.2977 | 0.57642
|  | 11:19 | 15.6622 | -0.29843 | 0.57642
|  | 11:19 | 15.6633 | -0.29916 | 0.57642
|  | 11:19 | 15.6644 | -0.3059 | 0.57641
|  | 11:19 | 15.6656 | -0.31865 | 0.57641
|  | 11:19 | 15.6667 | -0.33141 | 0.57641
|  | 11:19 | 15.6678 | -0.34928 | 0.57641
|  | 11:20 | 15.6689 | -0.36715 | 0.57641
|  | 11:20 | 15.67 | -0.36743 | 0.5764
|  | 11:20 | 15.6711 | -0.35014 | 0.5764
|  | 11:20 | 15.6722 | -0.33284 | 0.5764
|  | 11:20 | 15.6733 | -0.32614 | 0.5764
|  | 11:20 | 15.6744 | -0.31945 | 0.57639
|  | 11:20 | 15.6756 | -0.32347 | 0.57639
|  | 11:20 | 15.6767 | -0.33105 | 0.57639
|  | 11:20 | 15.6778 | -0.33863 | 0.57639
|  | 11:20 | 15.6789 | -0.34742 | 0.57638
|  | 11:20 | 15.68 | -0.35621 | 0.57638
|  | 11:20 | 15.6811 | -0.35525 | 0.57638
|  | 11:20 | 15.6822 | -0.34453 | 0.57638
|  | 11:20 | 15.6833 | -0.33382 | 0.57637
|  | 11:20 | 15.6844 | -0.32408 | 0.57637
|  | 11:21 | 15.6856 | -0.31435 | 0.57637
|  | 11:21 | 15.6867 | -0.29629 | 0.57637
|  | 11:21 | 15.6878 | -0.2699 | 0.57637
|  | 11:21 | 15.6889 | -0.24351 | 0.57636
|  | 11:21 | 15.69 | -0.22981 | 0.57636
|  | 11:21 | 15.6911 | -0.21611 | 0.57636
|  | 11:21 | 15.6922 | -0.19988 | 0.57636
|  | 11:21 | 15.6933 | -0.18112 | 0.57635
|  | 11:21 | 15.6944 | -0.16235 | 0.57635
|  | 11:21 | 15.6956 | -0.16142 | 0.57635
|  | 11:21 | 15.6967 | -0.16049 | 0.57635
|  | 11:21 | 15.6978 | -0.15389 | 0.57634
|  | 11:21 | 15.6989 | -0.14164 | 0.57634
|  | 11:21 | 15.7 | -0.12939 | 0.57634
|  | 11:21 | 15.7011 | -0.12526 | 0.57634
|  | 11:22 | 15.7022 | -0.12113 | 0.57634
|  | 11:22 | 15.7033 | -0.12313 | 0.57633
|  | 11:22 | 15.7044 | -0.13125 | 0.57633
|  | 11:22 | 15.7056 | -0.13938 | 0.57633
|  | 11:22 | 15.7067 | -0.13197 | 0.57633
|  | 11:22 | 15.7078 | -0.12456 | 0.57632
|  | 11:22 | 15.7089 | -0.11274 | 0.57632
|  | 11:22 | 15.71 | -0.096521 | 0.57632
|  | 11:22 | 15.7111 | -0.080302 | 0.57632
|  | 11:22 | 15.7122 | -0.054155 | 0.57631
|  | 11:22 | 15.7133 | -0.028008 | 0.57631
|  | 11:22 | 15.7144 | -0.0045076 | 0.57631
|  | 11:22 | 15.7156 | 0.016347 | 0.57631
|  | 11:22 | 15.7167 | 0.037201 | 0.57631
|  | 11:22 | 15.7178 | 0.038561 | 0.5763
|  | 11:23 | 15.7189 | 0.039921 | 0.5763
|  | 11:23 | 15.72 | 0.04462 | 0.5763
|  | 11:23 | 15.7211 | 0.052657 | 0.5763
|  | 11:23 | 15.7222 | 0.060695 | 0.57629
|  | 11:23 | 15.7233 | 0.062016 | 0.57629
|  | 11:23 | 15.7244 | 0.063337 | 0.57629
|  | 11:23 | 15.7256 | 0.059152 | 0.57629
|  | 11:23 | 15.7267 | 0.049461 | 0.57628
|  | 11:23 | 15.7278 | 0.039771 | 0.57628
|  | 11:23 | 15.7289 | 0.03008 | 0.57628
|  | 11:23 | 15.73 | 0.02039 | 0.57628
|  | 11:23 | 15.7311 | 0.012533 | 0.57628
|  | 11:23 | 15.7322 | 0.00651 | 0.57627
|  | 11:23 | 15.7333 | 0.00048686 | 0.57627
|  | 11:23 | 15.7344 | -0.0055363 | 0.57627
|  | 11:24 | 15.7356 | -0.028667 | 0.57627
|  | 11:24 | 15.7367 | -0.055754 | 0.57626
|  | 11:24 | 15.7378 | -0.094714 | 0.57626
|  | 11:24 | 15.7389 | -0.13367 | 0.57626
|  | 11:24 | 15.74 | -0.1564 | 0.57626
|  | 11:24 | 15.7411 | -0.17912 | 0.57625
|  | 11:24 | 15.7422 | -0.20465 | 0.57625
|  | 11:24 | 15.7433 | -0.23296 | 0.57625
|  | 11:24 | 15.7444 | -0.26128 | 0.57625
|  | 11:24 | 15.7456 | -0.28713 | 0.57625
|  | 11:24 | 15.7467 | -0.31299 | 0.57624
|  | 11:24 | 15.7478 | -0.3269 | 0.57624
|  | 11:24 | 15.7489 | -0.32887 | 0.57624
|  | 11:24 | 15.75 | -0.33084 | 0.57624
|  | 11:24 | 15.7511 | -0.34417 | 0.57623
|  | 11:25 | 15.7522 | -0.35749 | 0.57623
|  | 11:25 | 15.7533 | -0.36829 | 0.57623
|  | 11:25 | 15.7544 | -0.37657 | 0.57623
|  | 11:25 | 15.7556 | -0.38484 | 0.57622
|  | 11:25 | 15.7567 | -0.39763 | 0.57622
|  | 11:25 | 15.7578 | -0.41043 | 0.57622
|  | 11:25 | 15.7589 | -0.42784 | 0.57622
|  | 11:25 | 15.76 | -0.44987 | 0.57622
|  | 11:25 | 15.7611 | -0.4719 | 0.57621
|  | 11:25 | 15.7622 | -0.49075 | 0.57621
|  | 11:25 | 15.7633 | -0.50959 | 0.57621
|  | 11:25 | 15.7644 | -0.5272 | 0.57621
|  | 11:25 | 15.7656 | -0.54355 | 0.5762
|  | 11:25 | 15.7667 | -0.5599 | 0.5762
|  | 11:25 | 15.7678 | -0.58263 | 0.5762
|  | 11:26 | 15.7689 | -0.60537 | 0.5762
|  | 11:26 | 15.77 | -0.62365 | 0.57619
|  | 11:26 | 15.7711 | -0.63747 | 0.57619
|  | 11:26 | 15.7722 | -0.65129 | 0.57619
|  | 11:26 | 15.7733 | -0.65879 | 0.57619
|  | 11:26 | 15.7744 | -0.66629 | 0.57619
|  | 11:26 | 15.7756 | -0.67986 | 0.57618
|  | 11:26 | 15.7767 | -0.6995 | 0.57618
|  | 11:26 | 15.7778 | -0.71913 | 0.57618
|  | 11:26 | 15.7789 | -0.73168 | 0.57618
|  | 11:26 | 15.78 | -0.74423 | 0.57617
|  | 11:26 | 15.7811 | -0.7505 | 0.57617
|  | 11:26 | 15.7822 | -0.75049 | 0.57617
|  | 11:26 | 15.7833 | -0.75048 | 0.57617
|  | 11:26 | 15.7844 | -0.73916 | 0.57616
|  | 11:27 | 15.7856 | -0.72783 | 0.57616
|  | 11:27 | 15.7867 | -0.70987 | 0.57616
|  | 11:27 | 15.7878 | -0.68526 | 0.57616
|  | 11:27 | 15.7889 | -0.66066 | 0.57616
|  | 11:27 | 15.79 | -0.6495 | 0.57615
|  | 11:27 | 15.7911 | -0.63834 | 0.57615
|  | 11:27 | 15.7922 | -0.61665 | 0.57615
|  | 11:27 | 15.7933 | -0.58443 | 0.57615
|  | 11:27 | 15.7944 | -0.55221 | 0.57614
|  | 11:27 | 15.7956 | -0.51541 | 0.57614
|  | 11:27 | 15.7967 | -0.47861 | 0.57614
|  | 11:27 | 15.7978 | -0.44523 | 0.57614
|  | 11:27 | 15.7989 | -0.41524 | 0.57613
|  | 11:27 | 15.8 | -0.38526 | 0.57613
|  | 11:27 | 15.8011 | -0.37899 | 0.57613
|  | 11:28 | 15.8022 | -0.37271 | 0.57613
|  | 11:28 | 15.8033 | -0.37159 | 0.57612
|  | 11:28 | 15.8044 | -0.37563 | 0.57612
|  | 11:28 | 15.8056 | -0.37966 | 0.57612
|  | 11:28 | 15.8067 | -0.36377 | 0.57612
|  | 11:28 | 15.8078 | -0.34788 | 0.57612
|  | 11:28 | 15.8089 | -0.32774 | 0.57611
|  | 11:28 | 15.81 | -0.30335 | 0.57611
|  | 11:28 | 15.8111 | -0.27896 | 0.57611
|  | 11:28 | 15.8122 | -0.25074 | 0.57611
|  | 11:28 | 15.8133 | -0.22252 | 0.5761
|  | 11:28 | 15.8144 | -0.19509 | 0.5761
|  | 11:28 | 15.8156 | -0.16792 | 0.5761
|  | 11:28 | 15.8167 | -0.14272 | 0.5761
|  | 11:28 | 15.8178 | -0.12345 | 0.57609
|  | 11:29 | 15.8189 | -0.10417 | 0.57609
|  | 11:29 | 15.82 | -0.087397 | 0.57609
|  | 11:29 | 15.8211 | -0.07313 | 0.57609
|  | 11:29 | 15.8222 | -0.058863 | 0.57609
|  | 11:29 | 15.8233 | -0.061269 | 0.57608
|  | 11:29 | 15.8244 | -0.063676 | 0.57608
|  | 11:29 | 15.8256 | -0.065522 | 0.57608
|  | 11:29 | 15.8267 | -0.066808 | 0.57608
|  | 11:29 | 15.8278 | -0.068094 | 0.57607
|  | 11:29 | 15.8289 | -0.075492 | 0.57607
|  | 11:29 | 15.83 | -0.08289 | 0.57607
|  | 11:29 | 15.8311 | -0.09073 | 0.57607
|  | 11:29 | 15.8322 | -0.099014 | 0.57606
|  | 11:29 | 15.8333 | -0.1073 | 0.57606
|  | 11:29 | 15.8344 | -0.089359 | 0.57606
|  | 11:30 | 15.8356 | -0.071421 | 0.57606
|  | 11:30 | 15.8367 | -0.049309 | 0.57606
|  | 11:30 | 15.8378 | -0.023023 | 0.57605
|  | 11:30 | 15.8389 | 0.0032623 | 0.57605
|  | 11:30 | 15.84 | 0.016532 | 0.57605
|  | 11:30 | 15.8411 | 0.029801 | 0.57605
|  | 11:30 | 15.8422 | 0.036497 | 0.57604
|  | 11:30 | 15.8433 | 0.03662 | 0.57604
|  | 11:30 | 15.8444 | 0.036742 | 0.57604
|  | 11:30 | 15.8456 | 0.031934 | 0.57604
|  | 11:30 | 15.8467 | 0.027126 | 0.57603
|  | 11:30 | 15.8478 | 0.038487 | 0.57603
|  | 11:30 | 15.8489 | 0.06602 | 0.57603
|  | 11:30 | 15.85 | 0.093552 | 0.57603
|  | 11:30 | 15.8511 | 0.12924 | 0.57603
|  | 11:31 | 15.8522 | 0.16492 | 0.57602
|  | 11:31 | 15.8533 | 0.19135 | 0.57602
|  | 11:31 | 15.8544 | 0.20853 | 0.57602
|  | 11:31 | 15.8556 | 0.2257 | 0.57602
|  | 11:31 | 15.8567 | 0.2251 | 0.57601
|  | 11:31 | 15.8578 | 0.22449 | 0.57601
|  | 11:31 | 15.8589 | 0.21902 | 0.57601
|  | 11:31 | 15.86 | 0.2087 | 0.57601
|  | 11:31 | 15.8611 | 0.19838 | 0.576
|  | 11:31 | 15.8622 | 0.17104 | 0.576
|  | 11:31 | 15.8633 | 0.14371 | 0.576
|  | 11:31 | 15.8644 | 0.12041 | 0.576
|  | 11:31 | 15.8656 | 0.10116 | 0.576
|  | 11:31 | 15.8667 | 0.081902 | 0.57599
|  | 11:31 | 15.8678 | 0.099815 | 0.57599
|  | 11:32 | 15.8689 | 0.11773 | 0.57599
|  | 11:32 | 15.87 | 0.13342 | 0.57599
|  | 11:32 | 15.8711 | 0.14689 | 0.57598
|  | 11:32 | 15.8722 | 0.16036 | 0.57598
|  | 11:32 | 15.8733 | 0.17384 | 0.57598
|  | 11:32 | 15.8744 | 0.18731 | 0.57598
|  | 11:32 | 15.8756 | 0.20476 | 0.57597
|  | 11:32 | 15.8767 | 0.22619 | 0.57597
|  | 11:32 | 15.8778 | 0.24763 | 0.57597
|  | 11:32 | 15.8789 | 0.26643 | 0.57597
|  | 11:32 | 15.88 | 0.28523 | 0.57597
|  | 11:32 | 15.8811 | 0.29984 | 0.57596
|  | 11:32 | 15.8822 | 0.31025 | 0.57596
|  | 11:32 | 15.8833 | 0.32066 | 0.57596
|  | 11:32 | 15.8844 | 0.33434 | 0.57596
|  | 11:33 | 15.8856 | 0.34802 | 0.57595
|  | 11:33 | 15.8867 | 0.36502 | 0.57595
|  | 11:33 | 15.8878 | 0.38533 | 0.57595
|  | 11:33 | 15.8889 | 0.40565 | 0.57595
|  | 11:33 | 15.89 | 0.42159 | 0.57594
|  | 11:33 | 15.8911 | 0.43753 | 0.57594
|  | 11:33 | 15.8922 | 0.45058 | 0.57594
|  | 11:33 | 15.8933 | 0.46075 | 0.57594
|  | 11:33 | 15.8944 | 0.47091 | 0.57594
|  | 11:33 | 15.8956 | 0.47039 | 0.57593
|  | 11:33 | 15.8967 | 0.46987 | 0.57593
|  | 11:33 | 15.8978 | 0.46317 | 0.57593
|  | 11:33 | 15.8989 | 0.45441 | 0.57593
|  | 11:33 | 15.9 | 0.44565 | 0.57592
|  | 11:33 | 15.9011 | 0.42328 | 0.57592
|  | 11:34 | 15.9022 | 0.4009 | 0.57592
|  | 11:34 | 15.9033 | 0.38572 | 0.57592
|  | 11:34 | 15.9044 | 0.39211 | 0.57591
|  | 11:34 | 15.9056 | 0.3985 | 0.57591
|  | 11:34 | 15.9067 | 0.4237 | 0.57591
|  | 11:34 | 15.9078 | 0.4489 | 0.57591
|  | 11:34 | 15.9089 | 0.46088 | 0.57591
|  | 11:34 | 15.91 | 0.45964 | 0.5759
|  | 11:34 | 15.9111 | 0.45841 | 0.5759
|  | 11:34 | 15.9122 | 0.4475 | 0.5759
|  | 11:34 | 15.9133 | 0.43659 | 0.5759
|  | 11:34 | 15.9144 | 0.42325 | 0.57589
|  | 11:34 | 15.9156 | 0.40749 | 0.57589
|  | 11:34 | 15.9167 | 0.39172 | 0.57589
|  | 11:34 | 15.9178 | 0.40531 | 0.57589
|  | 11:35 | 15.9189 | 0.4189 | 0.57588
|  | 11:35 | 15.92 | 0.43151 | 0.57588
|  | 11:35 | 15.9211 | 0.44314 | 0.57588
|  | 11:35 | 15.9222 | 0.45477 | 0.57588
|  | 11:35 | 15.9233 | 0.4521 | 0.57587
|  | 11:35 | 15.9244 | 0.44943 | 0.57587
|  | 11:35 | 15.9256 | 0.43991 | 0.57587
|  | 11:35 | 15.9267 | 0.42354 | 0.57587
|  | 11:35 | 15.9278 | 0.40717 | 0.57587
|  | 11:35 | 15.9289 | 0.40518 | 0.57586
|  | 11:35 | 15.93 | 0.40319 | 0.57586
|  | 11:35 | 15.9311 | 0.41374 | 0.57586
|  | 11:35 | 15.9322 | 0.43682 | 0.57586
|  | 11:35 | 15.9333 | 0.45991 | 0.57585
|  | 11:35 | 15.9344 | 0.48429 | 0.57585
|  | 11:36 | 15.9356 | 0.50867 | 0.57585
|  | 11:36 | 15.9367 | 0.52763 | 0.57585
|  | 11:36 | 15.9378 | 0.54478 | 0.57584
|  | 11:36 | 15.9389 | 0.56194 | 0.57584
|  | 11:36 | 15.94 | 0.57207 | 0.57584
|  | 11:36 | 15.9411 | 0.58221 | 0.57584
|  | 11:36 | 15.9422 | 0.58718 | 0.57584
|  | 11:36 | 15.9433 | 0.58698 | 0.57583
|  | 11:36 | 15.9444 | 0.58678 | 0.57583
|  | 11:36 | 15.9456 | 0.60128 | 0.57583
|  | 11:36 | 15.9467 | 0.61578 | 0.57583
|  | 11:36 | 15.9478 | 0.62143 | 0.57582
|  | 11:36 | 15.9489 | 0.61825 | 0.57582
|  | 11:36 | 15.95 | 0.61506 | 0.57582
|  | 11:36 | 15.9511 | 0.62239 | 0.57582
|  | 11:37 | 15.9522 | 0.62971 | 0.57581
|  | 11:37 | 15.9533 | 0.63355 | 0.57581
|  | 11:37 | 15.9544 | 0.6339 | 0.57581
|  | 11:37 | 15.9556 | 0.63907 | 0.57581
|  | 11:37 | 15.9567 | 0.65868 | 0.57581
|  | 11:37 | 15.9578 | 0.6783 | 0.5758
|  | 11:37 | 15.9589 | 0.69792 | 0.5758
|  | 11:37 | 15.96 | 0.71754 | 0.5758
|  | 11:37 | 15.9611 | 0.73715 | 0.5758
|  | 11:37 | 15.9622 | 0.75945 | 0.57579
|  | 11:37 | 15.9633 | 0.78175 | 0.57579
|  | 11:37 | 15.9644 | 0.79371 | 0.57579
|  | 11:37 | 15.9656 | 0.79532 | 0.57579
|  | 11:37 | 15.9667 | 0.79693 | 0.57578
|  | 11:37 | 15.9678 | 0.81251 | 0.57578
|  | 11:38 | 15.9689 | 0.82809 | 0.57578
|  | 11:38 | 15.97 | 0.83863 | 0.57578
|  | 11:38 | 15.9711 | 0.84413 | 0.57578
|  | 11:38 | 15.9722 | 0.84963 | 0.57577
|  | 11:38 | 15.9733 | 0.82497 | 0.57577
|  | 11:38 | 15.9744 | 0.8003 | 0.57577
|  | 11:38 | 15.9756 | 0.77953 | 0.57577
|  | 11:38 | 15.9767 | 0.76265 | 0.57576
|  | 11:38 | 15.9778 | 0.74578 | 0.57576
|  | 11:38 | 15.9789 | 0.7289 | 0.57576
|  | 11:38 | 15.98 | 0.71203 | 0.57576
|  | 11:38 | 15.9811 | 0.69599 | 0.57575
|  | 11:38 | 15.9822 | 0.68079 | 0.57575
|  | 11:38 | 15.9833 | 0.66559 | 0.57575
|  | 11:38 | 15.9844 | 0.65039 | 0.57575
|  | 11:39 | 15.9856 | 0.63519 | 0.57575
|  | 11:39 | 15.9867 | 0.6287 | 0.57574
|  | 11:39 | 15.9878 | 0.62511 | 0.57574
|  | 11:39 | 15.9889 | 0.62152 | 0.57574
|  | 11:39 | 15.99 | 0.60905 | 0.57574
|  | 11:39 | 15.9911 | 0.59658 | 0.57573
|  | 11:39 | 15.9922 | 0.59451 | 0.57573
|  | 11:39 | 15.9933 | 0.60285 | 0.57573
|  | 11:39 | 15.9944 | 0.61119 | 0.57573
|  | 11:39 | 15.9956 | 0.62747 | 0.57572
|  | 11:39 | 15.9967 | 0.64374 | 0.57572
|  | 11:39 | 15.9978 | 0.64699 | 0.57572
|  | 11:39 | 15.9989 | 0.6372 | 0.57572
|  | 11:39 | 16 | 0.62494 | 0.57572
|  | 11:39 | 16.0011 | 0.60529 | 0.57571
|  | 11:40 | 16.0022 | 0.58564 | 0.57571
|  | 11:40 | 16.0033 | 0.56408 | 0.57571
|  | 11:40 | 16.0044 | 0.54061 | 0.57571
|  | 11:40 | 16.0056 | 0.51713 | 0.5757
|  | 11:40 | 16.0067 | 0.50205 | 0.5757
|  | 11:40 | 16.0078 | 0.48696 | 0.5757
|  | 11:40 | 16.0089 | 0.46771 | 0.5757
|  | 11:40 | 16.01 | 0.4443 | 0.57569
|  | 11:40 | 16.0111 | 0.4209 | 0.57569
|  | 11:40 | 16.0122 | 0.38558 | 0.57569
|  | 11:40 | 16.0133 | 0.35026 | 0.57569
|  | 11:40 | 16.0144 | 0.31233 | 0.57569
|  | 11:40 | 16.0156 | 0.27179 | 0.57568
|  | 11:40 | 16.0167 | 0.23124 | 0.57568
|  | 11:40 | 16.0178 | 0.20065 | 0.57568
|  | 11:41 | 16.0189 | 0.17005 | 0.57568
|  | 11:41 | 16.02 | 0.14077 | 0.57567
|  | 11:41 | 16.0211 | 0.11281 | 0.57567
|  | 11:41 | 16.0222 | 0.084842 | 0.57567
|  | 11:41 | 16.0233 | 0.038603 | 0.57567
|  | 11:41 | 16.0244 | -0.0076366 | 0.57566
|  | 11:41 | 16.0256 | -0.047739 | 0.57566
|  | 11:41 | 16.0267 | -0.081703 | 0.57566
|  | 11:41 | 16.0278 | -0.11567 | 0.57566
|  | 11:41 | 16.0289 | -0.13646 | 0.57566
|  | 11:41 | 16.03 | -0.15725 | 0.57565
|  | 11:41 | 16.0311 | -0.18325 | 0.57565
|  | 11:41 | 16.0322 | -0.21444 | 0.57565
|  | 11:41 | 16.0333 | -0.24563 | 0.57565
|  | 11:41 | 16.0344 | -0.2745 | 0.57564
|  | 11:42 | 16.0356 | -0.30336 | 0.57564
|  | 11:42 | 16.0367 | -0.34175 | 0.57564
|  | 11:42 | 16.0378 | -0.38967 | 0.57564
|  | 11:42 | 16.0389 | -0.42638 | 0.57563
|  | 11:42 | 16.04 | -0.42948 | 0.57563
|  | 11:42 | 16.0411 | -0.43258 | 0.57563
|  | 11:42 | 16.0422 | -0.44921 | 0.57563
|  | 11:42 | 16.0433 | -0.47935 | 0.57562
|  | 11:42 | 16.0444 | -0.5095 | 0.57562
|  | 11:42 | 16.0456 | -0.53188 | 0.57562
|  | 11:42 | 16.0467 | -0.55427 | 0.57562
|  | 11:42 | 16.0478 | -0.57911 | 0.57562
|  | 11:42 | 16.0489 | -0.60641 | 0.57561
|  | 11:42 | 16.05 | -0.63371 | 0.57561
|  | 11:42 | 16.0511 | -0.64927 | 0.57561
|  | 11:43 | 16.0522 | -0.66484 | 0.57561
|  | 11:43 | 16.0533 | -0.6804 | 0.5756
|  | 11:43 | 16.0544 | -0.69596 | 0.5756
|  | 11:43 | 16.0556 | -0.71153 | 0.5756
|  | 11:43 | 16.0567 | -0.72418 | 0.5756
|  | 11:43 | 16.0578 | -0.73684 | 0.57559
|  | 11:43 | 16.0589 | -0.73522 | 0.57559
|  | 11:43 | 16.06 | -0.71932 | 0.57559
|  | 11:43 | 16.0611 | -0.70341 | 0.57559
|  | 11:43 | 16.0622 | -0.67074 | 0.57559
|  | 11:43 | 16.0633 | -0.63806 | 0.57558
|  | 11:43 | 16.0644 | -0.60994 | 0.57558
|  | 11:43 | 16.0656 | -0.58635 | 0.57558
|  | 11:43 | 16.0667 | -0.56277 | 0.57558
|  | 11:43 | 16.0678 | -0.53527 | 0.57557
|  | 11:44 | 16.0689 | -0.50776 | 0.57557
|  | 11:44 | 16.07 | -0.48763 | 0.57557
|  | 11:44 | 16.0711 | -0.48964 | 0.57557
|  | 11:44 | 16.0722 | -0.49165 | 0.57556
|  | 11:44 | 16.0733 | -0.49001 | 0.57556
|  | 11:44 | 16.0744 | -0.48837 | 0.57556
|  | 11:44 | 16.0756 | -0.48899 | 0.57556
|  | 11:44 | 16.0767 | -0.49188 | 0.57556
|  | 11:44 | 16.0778 | -0.49352 | 0.57555
|  | 11:44 | 16.0789 | -0.49142 | 0.57555
|  | 11:44 | 16.08 | -0.48932 | 0.57555
|  | 11:44 | 16.0811 | -0.49175 | 0.57555
|  | 11:44 | 16.0822 | -0.4987 | 0.57554
|  | 11:44 | 16.0833 | -0.50565 | 0.57554
|  | 11:44 | 16.0844 | -0.50288 | 0.57554
|  | 11:45 | 16.0856 | -0.50011 | 0.57554
|  | 11:45 | 16.0867 | -0.48826 | 0.57553
|  | 11:45 | 16.0878 | -0.46731 | 0.57553
|  | 11:45 | 16.0889 | -0.44636 | 0.57553
|  | 11:45 | 16.09 | -0.413 | 0.57553
|  | 11:45 | 16.0911 | -0.37965 | 0.57553
|  | 11:45 | 16.0922 | -0.35026 | 0.57552
|  | 11:45 | 16.0933 | -0.32485 | 0.57552
|  | 11:45 | 16.0944 | -0.29944 | 0.57552
|  | 11:45 | 16.0956 | -0.27642 | 0.57552
|  | 11:45 | 16.0967 | -0.2534 | 0.57551
|  | 11:45 | 16.0978 | -0.236 | 0.57551
|  | 11:45 | 16.0989 | -0.22421 | 0.57551
|  | 11:45 | 16.1 | -0.21242 | 0.57551
|  | 11:45 | 16.1011 | -0.18995 | 0.5755
|  | 11:46 | 16.1022 | -0.16749 | 0.5755
|  | 11:46 | 16.1033 | -0.14283 | 0.5755
|  | 11:46 | 16.1044 | -0.11597 | 0.5755
|  | 11:46 | 16.1056 | -0.089118 | 0.5755
|  | 11:46 | 16.1067 | -0.051508 | 0.57549
|  | 11:46 | 16.1078 | -0.013898 | 0.57549
|  | 11:46 | 16.1089 | 0.024607 | 0.57549
|  | 11:46 | 16.11 | 0.064006 | 0.57549
|  | 11:46 | 16.1111 | 0.1034 | 0.57548
|  | 11:46 | 16.1122 | 0.12872 | 0.57548
|  | 11:46 | 16.1133 | 0.15403 | 0.57548
|  | 11:46 | 16.1144 | 0.16833 | 0.57548
|  | 11:46 | 16.1156 | 0.17161 | 0.57547
|  | 11:46 | 16.1167 | 0.1749 | 0.57547
|  | 11:46 | 16.1178 | 0.19225 | 0.57547
|  | 11:47 | 16.1189 | 0.2096 | 0.57547
|  | 11:47 | 16.12 | 0.23125 | 0.57547
|  | 11:47 | 16.1211 | 0.25433 | 0.57546
|  | 11:47 | 16.1222 | 0.28118 | 0.57546
|  | 11:47 | 16.1233 | 0.3193 | 0.57546
|  | 11:47 | 16.1244 | 0.35742 | 0.57546
|  | 11:47 | 16.1256 | 0.37481 | 0.57545
|  | 11:47 | 16.1267 | 0.37146 | 0.57545
|  | 11:47 | 16.1278 | 0.36812 | 0.57545
|  | 11:47 | 16.1289 | 0.36814 | 0.57545
|  | 11:47 | 16.13 | 0.36817 | 0.57544
|  | 11:47 | 16.1311 | 0.36493 | 0.57544
|  | 11:47 | 16.1322 | 0.35842 | 0.57544
|  | 11:47 | 16.1333 | 0.35192 | 0.57544
|  | 11:47 | 16.1344 | 0.35745 | 0.57544
|  | 11:48 | 16.1356 | 0.36298 | 0.57543
|  | 11:48 | 16.1367 | 0.38439 | 0.57543
|  | 11:48 | 16.1378 | 0.42166 | 0.57543
|  | 11:48 | 16.1389 | 0.45893 | 0.57543
|  | 11:48 | 16.14 | 0.50834 | 0.57542
|  | 11:48 | 16.1411 | 0.55774 | 0.57542
|  | 11:48 | 16.1422 | 0.59714 | 0.57542
|  | 11:48 | 16.1433 | 0.62655 | 0.57542
|  | 11:48 | 16.1444 | 0.65595 | 0.57541
|  | 11:48 | 16.1456 | 0.68535 | 0.57541
|  | 11:48 | 16.1467 | 0.71475 | 0.57541
|  | 11:48 | 16.1478 | 0.7405 | 0.57541
|  | 11:48 | 16.1489 | 0.7626 | 0.57541
|  | 11:48 | 16.15 | 0.7847 | 0.5754
|  | 11:48 | 16.1511 | 0.78996 | 0.5754
|  | 11:49 | 16.1522 | 0.79522 | 0.5754
|  | 11:49 | 16.1533 | 0.80048 | 0.5754
|  | 11:49 | 16.1544 | 0.80574 | 0.57539
|  | 11:49 | 16.1556 | 0.811 | 0.57539
|  | 11:49 | 16.1567 | 0.80302 | 0.57539
|  | 11:49 | 16.1578 | 0.79504 | 0.57539
|  | 11:49 | 16.1589 | 0.78335 | 0.57538
|  | 11:49 | 16.16 | 0.76794 | 0.57538
|  | 11:49 | 16.1611 | 0.75254 | 0.57538
|  | 11:49 | 16.1622 | 0.73713 | 0.57538
|  | 11:49 | 16.1633 | 0.72173 | 0.57537
|  | 11:49 | 16.1644 | 0.70357 | 0.57537
|  | 11:49 | 16.1656 | 0.68266 | 0.57537
|  | 11:49 | 16.1667 | 0.66175 | 0.57537
|  | 11:49 | 16.1678 | 0.62242 | 0.57537
|  | 11:50 | 16.1689 | 0.58309 | 0.57536
|  | 11:50 | 16.17 | 0.54171 | 0.57536
|  | 11:50 | 16.1711 | 0.49829 | 0.57536
|  | 11:50 | 16.1722 | 0.45486 | 0.57536
|  | 11:50 | 16.1733 | 0.42925 | 0.57535
|  | 11:50 | 16.1744 | 0.40363 | 0.57535
|  | 11:50 | 16.1756 | 0.37379 | 0.57535
|  | 11:50 | 16.1767 | 0.33971 | 0.57535
|  | 11:50 | 16.1778 | 0.30564 | 0.57534
|  | 11:50 | 16.1789 | 0.27379 | 0.57534
|  | 11:50 | 16.18 | 0.24194 | 0.57534
|  | 11:50 | 16.1811 | 0.22435 | 0.57534
|  | 11:50 | 16.1822 | 0.22102 | 0.57534
|  | 11:50 | 16.1833 | 0.21769 | 0.57533
|  | 11:50 | 16.1844 | 0.20566 | 0.57533
|  | 11:51 | 16.1856 | 0.19362 | 0.57533
|  | 11:51 | 16.1867 | 0.18466 | 0.57533
|  | 11:51 | 16.1878 | 0.17879 | 0.57532
|  | 11:51 | 16.1889 | 0.17291 | 0.57532
|  | 11:51 | 16.19 | 0.16918 | 0.57532
|  | 11:51 | 16.1911 | 0.16545 | 0.57532
|  | 11:51 | 16.1922 | 0.15742 | 0.57531
|  | 11:51 | 16.1933 | 0.14511 | 0.57531
|  | 11:51 | 16.1944 | 0.13279 | 0.57531
|  | 11:51 | 16.1956 | 0.11944 | 0.57531
|  | 11:51 | 16.1967 | 0.10609 | 0.57531
|  | 11:51 | 16.1978 | 0.093734 | 0.5753
|  | 11:51 | 16.1989 | 0.082374 | 0.5753
|  | 11:51 | 16.2 | 0.071013 | 0.5753
|  | 11:51 | 16.2011 | 0.066403 | 0.5753
|  | 11:52 | 16.2022 | 0.061792 | 0.57529
|  | 11:52 | 16.2033 | 0.057755 | 0.57529
|  | 11:52 | 16.2044 | 0.05429 | 0.57529
|  | 11:52 | 16.2056 | 0.050825 | 0.57529
|  | 11:52 | 16.2067 | 0.032276 | 0.57528
|  | 11:52 | 16.2078 | 0.013726 | 0.57528
|  | 11:52 | 16.2089 | -0.0155 | 0.57528
|  | 11:52 | 16.21 | -0.055402 | 0.57528
|  | 11:52 | 16.2111 | -0.095305 | 0.57528
|  | 11:52 | 16.2122 | -0.1476 | 0.57527
|  | 11:52 | 16.2133 | -0.19989 | 0.57527
|  | 11:52 | 16.2144 | -0.25319 | 0.57527
|  | 11:52 | 16.2156 | -0.30752 | 0.57527
|  | 11:52 | 16.2167 | -0.36184 | 0.57526
|  | 11:52 | 16.2178 | -0.40614 | 0.57526
|  | 11:53 | 16.2189 | -0.45044 | 0.57526
|  | 11:53 | 16.22 | -0.48112 | 0.57526
|  | 11:53 | 16.2211 | -0.49819 | 0.57525
|  | 11:53 | 16.2222 | -0.51526 | 0.57525
|  | 11:53 | 16.2233 | -0.54146 | 0.57525
|  | 11:53 | 16.2244 | -0.56767 | 0.57525
|  | 11:53 | 16.2256 | -0.58665 | 0.57525
|  | 11:53 | 16.2267 | -0.59843 | 0.57524
|  | 11:53 | 16.2278 | -0.6102 | 0.57524
|  | 11:53 | 16.2289 | -0.60745 | 0.57524
|  | 11:53 | 16.23 | -0.6047 | 0.57524
|  | 11:53 | 16.2311 | -0.60347 | 0.57523
|  | 11:53 | 16.2322 | -0.60376 | 0.57523
|  | 11:53 | 16.2333 | -0.60405 | 0.57523
|  | 11:53 | 16.2344 | -0.60336 | 0.57523
|  | 11:54 | 16.2356 | -0.60266 | 0.57522
|  | 11:54 | 16.2367 | -0.60291 | 0.57522
|  | 11:54 | 16.2378 | -0.60599 | 0.57522
|  | 11:54 | 16.2389 | -0.60906 | 0.57522
|  | 11:54 | 16.24 | -0.61077 | 0.57522
|  | 11:54 | 16.2411 | -0.61248 | 0.57521
|  | 11:54 | 16.2422 | -0.6045 | 0.57521
|  | 11:54 | 16.2433 | -0.58685 | 0.57521
|  | 11:54 | 16.2444 | -0.56919 | 0.57521
|  | 11:54 | 16.2456 | -0.55636 | 0.5752
|  | 11:54 | 16.2467 | -0.54352 | 0.5752
|  | 11:54 | 16.2478 | -0.53564 | 0.5752
|  | 11:54 | 16.2489 | -0.53272 | 0.5752
|  | 11:54 | 16.25 | -0.5298 | 0.57519
|  | 11:54 | 16.2511 | -0.529 | 0.57519
|  | 11:55 | 16.2522 | -0.52819 | 0.57519
|  | 11:55 | 16.2533 | -0.53152 | 0.57519
|  | 11:55 | 16.2544 | -0.539 | 0.57519
|  | 11:55 | 16.2556 | -0.54647 | 0.57518
|  | 11:55 | 16.2567 | -0.54635 | 0.57518
|  | 11:55 | 16.2578 | -0.54623 | 0.57518
|  | 11:55 | 16.2589 | -0.54252 | 0.57518
|  | 11:55 | 16.26 | -0.53522 | 0.57517
|  | 11:55 | 16.2611 | -0.52791 | 0.57517
|  | 11:55 | 16.2622 | -0.51653 | 0.57517
|  | 11:55 | 16.2633 | -0.50516 | 0.57517
|  | 11:55 | 16.2644 | -0.47674 | 0.57516
|  | 11:55 | 16.2656 | -0.43128 | 0.57516
|  | 11:55 | 16.2667 | -0.38582 | 0.57516
|  | 11:55 | 16.2678 | -0.34134 | 0.57516
|  | 11:56 | 16.2689 | -0.29686 | 0.57516
|  | 11:56 | 16.27 | -0.25636 | 0.57515
|  | 11:56 | 16.2711 | -0.21982 | 0.57515
|  | 11:56 | 16.2722 | -0.18329 | 0.57515
|  | 11:56 | 16.2733 | -0.16697 | 0.57515
|  | 11:56 | 16.2744 | -0.15066 | 0.57514
|  | 11:56 | 16.2756 | -0.13059 | 0.57514
|  | 11:56 | 16.2767 | -0.10676 | 0.57514
|  | 11:56 | 16.2778 | -0.082929 | 0.57514
|  | 11:56 | 16.2789 | -0.064992 | 0.57513
|  | 11:56 | 16.28 | -0.047054 | 0.57513
|  | 11:56 | 16.2811 | -0.033677 | 0.57513
|  | 11:56 | 16.2822 | -0.024861 | 0.57513
|  | 11:56 | 16.2833 | -0.016045 | 0.57512
|  | 11:56 | 16.2844 | -0.015577 | 0.57512
|  | 11:57 | 16.2856 | -0.01511 | 0.57512
|  | 11:57 | 16.2867 | -0.032247 | 0.57512
|  | 11:57 | 16.2878 | -0.066986 | 0.57512
|  | 11:57 | 16.2889 | -0.10173 | 0.57511
|  | 11:57 | 16.29 | -0.11422 | 0.57511
|  | 11:57 | 16.2911 | -0.12672 | 0.57511
|  | 11:57 | 16.2922 | -0.14071 | 0.57511
|  | 11:57 | 16.2933 | -0.15619 | 0.5751
|  | 11:57 | 16.2944 | -0.17167 | 0.5751
|  | 11:57 | 16.2956 | -0.18715 | 0.5751
|  | 11:57 | 16.2967 | -0.20263 | 0.5751
|  | 11:57 | 16.2978 | -0.22463 | 0.57509
|  | 11:57 | 16.2989 | -0.25316 | 0.57509
|  | 11:57 | 16.3 | -0.28168 | 0.57509
|  | 11:57 | 16.3011 | -0.29777 | 0.57509
|  | 11:58 | 16.3022 | -0.31386 | 0.57509
|  | 11:58 | 16.3033 | -0.31394 | 0.57508
|  | 11:58 | 16.3044 | -0.298 | 0.57508
|  | 11:58 | 16.3056 | -0.28207 | 0.57508
|  | 11:58 | 16.3067 | -0.26097 | 0.57508
|  | 11:58 | 16.3078 | -0.23987 | 0.57507
|  | 11:58 | 16.3089 | -0.2201 | 0.57507
|  | 11:58 | 16.31 | -0.20168 | 0.57507
|  | 11:58 | 16.3111 | -0.18325 | 0.57507
|  | 11:58 | 16.3122 | -0.16685 | 0.57506
|  | 11:58 | 16.3133 | -0.15045 | 0.57506
|  | 11:58 | 16.3144 | -0.13497 | 0.57506
|  | 11:58 | 16.3156 | -0.1204 | 0.57506
|  | 11:58 | 16.3167 | -0.10583 | 0.57506
|  | 11:58 | 16.3178 | -0.085856 | 0.57505
|  | 11:59 | 16.3189 | -0.065882 | 0.57505
|  | 11:59 | 16.32 | -0.057483 | 0.57505
|  | 11:59 | 16.3211 | -0.060658 | 0.57505
|  | 11:59 | 16.3222 | -0.063833 | 0.57504
|  | 11:59 | 16.3233 | -0.042603 | 0.57504
|  | 11:59 | 16.3244 | -0.021374 | 0.57504
|  | 11:59 | 16.3256 | -0.0021204 | 0.57504
|  | 11:59 | 16.3267 | 0.015157 | 0.57503
|  | 11:59 | 16.3278 | 0.032435 | 0.57503
|  | 11:59 | 16.3289 | 0.024561 | 0.57503
|  | 11:59 | 16.33 | 0.016687 | 0.57503
|  | 11:59 | 16.3311 | 0.012389 | 0.57503
|  | 11:59 | 16.3322 | 0.011665 | 0.57502
|  | 11:59 | 16.3333 | 0.010942 | 0.57502
|  | 11:59 | 16.3344 | 0.002515 | 0.57502
|  | 12:00 | 16.3356 | -0.0059115 | 0.57502
|  | 12:00 | 16.3367 | -0.026255 | 0.57501
|  | 12:00 | 16.3378 | -0.058516 | 0.57501
|  | 12:00 | 16.3389 | -0.090777 | 0.57501
|  | 12:00 | 16.34 | -0.1219 | 0.57501
|  | 12:00 | 16.3411 | -0.15302 | 0.575
|  | 12:00 | 16.3422 | -0.18289 | 0.575
|  | 12:00 | 16.3433 | -0.14425 | 0.575
|  | 12:00 | 16.3444 | -0.12965 | 0.575
|  | 12:00 | 16.3456 | -0.13601 | 0.575
|  | 12:00 | 16.3467 | -0.14238 | 0.57499
|  | 12:00 | 16.3478 | -0.14874 | 0.57499
|  | 12:00 | 16.3489 | -0.15511 | 0.57499
|  | 12:00 | 16.35 | -0.16147 | 0.57499
|  | 12:00 | 16.3511 | -0.15001 | 0.57498
|  | 12:01 | 16.3522 | -0.13855 | 0.57498
|  | 12:01 | 16.3533 | -0.11353 | 0.57498
|  | 12:01 | 16.3544 | -0.083978 | 0.57498
|  | 12:01 | 16.3556 | -0.05443 | 0.57497
|  | 12:01 | 16.3567 | -0.032121 | 0.57497
|  | 12:01 | 16.3578 | -0.0098121 | 0.57497
|  | 12:01 | 16.3589 | 0.0050135 | 0.57497
|  | 12:01 | 16.36 | 0.012356 | 0.57497
|  | 12:01 | 16.3611 | 0.019698 | 0.57496
|  | 12:01 | 16.3622 | 0.0056427 | 0.57496
|  | 12:01 | 16.3633 | -0.0084124 | 0.57496
|  | 12:01 | 16.3644 | -0.016135 | 0.57496
|  | 12:01 | 16.3656 | -0.017526 | 0.57495
|  | 12:01 | 16.3667 | -0.018917 | 0.57495
|  | 12:01 | 16.3678 | -0.0074832 | 0.57495
|  | 12:02 | 16.3689 | 0.0039504 | 0.57495
|  | 12:02 | 16.37 | 0.016937 | 0.57494
|  | 12:02 | 16.3711 | 0.030441 | 0.57494
|  | 12:02 | 16.3722 | 0.043946 | 0.57494
|  | 12:02 | 16.3733 | 0.065859 | 0.57494
|  | 12:02 | 16.3744 | 0.087772 | 0.57494
|  | 12:02 | 16.3756 | 0.10268 | 0.57493
|  | 12:02 | 16.3767 | 0.11526 | 0.57493
|  | 12:02 | 16.3778 | 0.12783 | 0.57493
|  | 12:02 | 16.3789 | 0.13629 | 0.57493
|  | 12:02 | 16.38 | 0.14474 | 0.57492
|  | 12:02 | 16.3811 | 0.1681 | 0.57492
|  | 12:02 | 16.3822 | 0.20635 | 0.57492
|  | 12:02 | 16.3833 | 0.2446 | 0.57492
|  | 12:02 | 16.3844 | 0.28614 | 0.57491
|  | 12:03 | 16.3856 | 0.32769 | 0.57491
|  | 12:03 | 16.3867 | 0.37177 | 0.57491
|  | 12:03 | 16.3878 | 0.41839 | 0.57491
|  | 12:03 | 16.3889 | 0.4646 | 0.57491
|  | 12:03 | 16.39 | 0.50955 | 0.5749
|  | 12:03 | 16.3911 | 0.55451 | 0.5749
|  | 12:03 | 16.3922 | 0.60292 | 0.5749
|  | 12:03 | 16.3933 | 0.65481 | 0.5749
|  | 12:03 | 16.3944 | 0.70669 | 0.57489
|  | 12:03 | 16.3956 | 0.72091 | 0.57489
|  | 12:03 | 16.3967 | 0.73513 | 0.57489
|  | 12:03 | 16.3978 | 0.73769 | 0.57489
|  | 12:03 | 16.3989 | 0.7286 | 0.57488
|  | 12:03 | 16.4 | 0.71951 | 0.57488
|  | 12:03 | 16.4011 | 0.69733 | 0.57488
|  | 12:04 | 16.4022 | 0.66208 | 0.57488
|  | 12:04 | 16.4033 | 0.6161 | 0.57487
|  | 12:04 | 16.4044 | 0.5594 | 0.57487
|  | 12:04 | 16.4056 | 0.50271 | 0.57487
|  | 12:04 | 16.4067 | 0.43484 | 0.57487
|  | 12:04 | 16.4078 | 0.36696 | 0.57487
|  | 12:04 | 16.4089 | 0.2997 | 0.57486
|  | 12:04 | 16.41 | 0.23306 | 0.57486
|  | 12:04 | 16.4111 | 0.16641 | 0.57486
|  | 12:04 | 16.4122 | 0.1269 | 0.57486
|  | 12:04 | 16.4133 | 0.087393 | 0.57485
|  | 12:04 | 16.4144 | 0.062752 | 0.57485
|  | 12:04 | 16.4156 | 0.052981 | 0.57485
|  | 12:04 | 16.4167 | 0.04321 | 0.57485
|  | 12:04 | 16.4178 | 0.031374 | 0.57484
|  | 12:05 | 16.4189 | 0.019538 | 0.57484
|  | 12:05 | 16.42 | 0.0014623 | 0.57484
|  | 12:05 | 16.4211 | -0.022852 | 0.57484
|  | 12:05 | 16.4222 | -0.047167 | 0.57484
|  | 12:05 | 16.4233 | -0.057435 | 0.57483
|  | 12:05 | 16.4244 | -0.067703 | 0.57483
|  | 12:05 | 16.4256 | -0.080728 | 0.57483
|  | 12:05 | 16.4267 | -0.096511 | 0.57483
|  | 12:05 | 16.4278 | -0.11229 | 0.57482
|  | 12:05 | 16.4289 | -0.14181 | 0.57482
|  | 12:05 | 16.43 | -0.17133 | 0.57482
|  | 12:05 | 16.4311 | -0.19213 | 0.57482
|  | 12:05 | 16.4322 | -0.21003 | 0.57481
|  | 12:05 | 16.4333 | -0.22794 | 0.57481
|  | 12:05 | 16.4344 | -0.25217 | 0.57481
|  | 12:06 | 16.4356 | -0.2764 | 0.57481
|  | 12:06 | 16.4367 | -0.29614 | 0.57481
|  | 12:06 | 16.4378 | -0.31141 | 0.5748
|  | 12:06 | 16.4389 | -0.32668 | 0.5748
|  | 12:06 | 16.44 | -0.33634 | 0.5748
|  | 12:06 | 16.4411 | -0.346 | 0.5748
|  | 12:06 | 16.4422 | -0.35417 | 0.57479
|  | 12:06 | 16.4433 | -0.36184 | 0.57479
|  | 12:06 | 16.4444 | -0.3695 | 0.57479
|  | 12:06 | 16.4456 | -0.38223 | 0.57479
|  | 12:06 | 16.4467 | -0.39495 | 0.57478
|  | 12:06 | 16.4478 | -0.41366 | 0.57478
|  | 12:06 | 16.4489 | -0.43836 | 0.57478
|  | 12:06 | 16.45 | -0.46307 | 0.57478
|  | 12:06 | 16.4511 | -0.49142 | 0.57478
|  | 12:07 | 16.4522 | -0.51976 | 0.57477
|  | 12:07 | 16.4533 | -0.53557 | 0.57477
|  | 12:07 | 16.4544 | -0.53885 | 0.57477
|  | 12:07 | 16.4556 | -0.54212 | 0.57477
|  | 12:07 | 16.4567 | -0.52588 | 0.57476
|  | 12:07 | 16.4578 | -0.50964 | 0.57476
|  | 12:07 | 16.4589 | -0.48512 | 0.57476
|  | 12:07 | 16.46 | -0.45232 | 0.57476
|  | 12:07 | 16.4611 | -0.41952 | 0.57475
|  | 12:07 | 16.4622 | -0.39896 | 0.57475
|  | 12:07 | 16.4633 | -0.3784 | 0.57475
|  | 12:07 | 16.4644 | -0.36069 | 0.57475
|  | 12:07 | 16.4656 | -0.34581 | 0.57475
|  | 12:07 | 16.4667 | -0.33094 | 0.57474
|  | 12:07 | 16.4678 | -0.31151 | 0.57474
|  | 12:08 | 16.4689 | -0.29208 | 0.57474
|  | 12:08 | 16.47 | -0.26401 | 0.57474
|  | 12:08 | 16.4711 | -0.2273 | 0.57473
|  | 12:08 | 16.4722 | -0.1906 | 0.57473
|  | 12:08 | 16.4733 | -0.15165 | 0.57473
|  | 12:08 | 16.4744 | -0.1127 | 0.57473
|  | 12:08 | 16.4756 | -0.070709 | 0.57472
|  | 12:08 | 16.4767 | -0.025681 | 0.57472
|  | 12:08 | 16.4778 | 0.019348 | 0.57472
|  | 12:08 | 16.4789 | 0.066808 | 0.57472
|  | 12:08 | 16.48 | 0.11427 | 0.57472
|  | 12:08 | 16.4811 | 0.14906 | 0.57471
|  | 12:08 | 16.4822 | 0.17962 | 0.57471
|  | 12:08 | 16.4833 | 0.21018 | 0.57471
|  | 12:08 | 16.4844 | 0.22659 | 0.57471
|  | 12:09 | 16.4856 | 0.243 | 0.5747
|  | 12:09 | 16.4867 | 0.26015 | 0.5747
|  | 12:09 | 16.4878 | 0.27804 | 0.5747
|  | 12:09 | 16.4889 | 0.29593 | 0.5747
|  | 12:09 | 16.49 | 0.34579 | 0.57469
|  | 12:09 | 16.4911 | 0.39566 | 0.57469
|  | 12:09 | 16.4922 | 0.41648 | 0.57469
|  | 12:09 | 16.4933 | 0.42761 | 0.57469
|  | 12:09 | 16.4944 | 0.43875 | 0.57469
|  | 12:09 | 16.4956 | 0.48488 | 0.57468
|  | 12:09 | 16.4967 | 0.53101 | 0.57468
|  | 12:09 | 16.4978 | 0.56431 | 0.57468
|  | 12:09 | 16.4989 | 0.58479 | 0.57468
|  | 12:09 | 16.5 | 0.60527 | 0.57467
|  | 12:09 | 16.5011 | 0.62576 | 0.57467
|  | 12:10 | 16.5022 | 0.64624 | 0.57467
|  | 12:10 | 16.5033 | 0.65386 | 0.57467
|  | 12:10 | 16.5044 | 0.64862 | 0.57466
|  | 12:10 | 16.5056 | 0.64337 | 0.57466
|  | 12:10 | 16.5067 | 0.61858 | 0.57466
|  | 12:10 | 16.5078 | 0.59379 | 0.57466
|  | 12:10 | 16.5089 | 0.57945 | 0.57466
|  | 12:10 | 16.51 | 0.5686 | 0.57465
|  | 12:10 | 16.5111 | 0.55774 | 0.57465
|  | 12:10 | 16.5122 | 0.53406 | 0.57465
|  | 12:10 | 16.5133 | 0.51037 | 0.57465
|  | 12:10 | 16.5144 | 0.48484 | 0.57464
|  | 12:10 | 16.5156 | 0.45747 | 0.57464
|  | 12:10 | 16.5167 | 0.43009 | 0.57464
|  | 12:10 | 16.5178 | 0.40661 | 0.57464
|  | 12:11 | 16.5189 | 0.38313 | 0.57463
|  | 12:11 | 16.52 | 0.35578 | 0.57463
|  | 12:11 | 16.5211 | 0.32455 | 0.57463
|  | 12:11 | 16.5222 | 0.29332 | 0.57463
|  | 12:11 | 16.5233 | 0.24981 | 0.57462
|  | 12:11 | 16.5244 | 0.20629 | 0.57462
|  | 12:11 | 16.5256 | 0.16355 | 0.57462
|  | 12:11 | 16.5267 | 0.12106 | 0.57462
|  | 12:11 | 16.5278 | 0.078582 | 0.57462
|  | 12:11 | 16.5289 | 0.031632 | 0.57461
|  | 12:11 | 16.53 | -0.015318 | 0.57461
|  | 12:11 | 16.5311 | -0.035845 | 0.57461
|  | 12:11 | 16.5322 | -0.047565 | 0.57461
|  | 12:11 | 16.5333 | -0.059285 | 0.5746
|  | 12:11 | 16.5344 | -0.081598 | 0.5746
|  | 12:12 | 16.5356 | -0.10391 | 0.5746
|  | 12:12 | 16.5367 | -0.13323 | 0.5746
|  | 12:12 | 16.5378 | -0.16956 | 0.57459
|  | 12:12 | 16.5389 | -0.20588 | 0.57459
|  | 12:12 | 16.54 | -0.24997 | 0.57459
|  | 12:12 | 16.5411 | -0.29406 | 0.57459
|  | 12:12 | 16.5422 | -0.33234 | 0.57459
|  | 12:12 | 16.5433 | -0.3648 | 0.57458
|  | 12:12 | 16.5444 | -0.39726 | 0.57458
|  | 12:12 | 16.5456 | -0.42357 | 0.57458
|  | 12:12 | 16.5467 | -0.44987 | 0.57458
|  | 12:12 | 16.5478 | -0.46847 | 0.57457
|  | 12:12 | 16.5489 | -0.47935 | 0.57457
|  | 12:12 | 16.55 | -0.49023 | 0.57457
|  | 12:12 | 16.5511 | -0.5088 | 0.57457
|  | 12:13 | 16.5522 | -0.52738 | 0.57456
|  | 12:13 | 16.5533 | -0.54595 | 0.57456
|  | 12:13 | 16.5544 | -0.56452 | 0.57456
|  | 12:13 | 16.5556 | -0.58056 | 0.57456
|  | 12:13 | 16.5567 | -0.58899 | 0.57456
|  | 12:13 | 16.5578 | -0.59741 | 0.57455
|  | 12:13 | 16.5589 | -0.60464 | 0.57455
|  | 12:13 | 16.56 | -0.61068 | 0.57455
|  | 12:13 | 16.5611 | -0.61671 | 0.57455
|  | 12:13 | 16.5622 | -0.62274 | 0.57454
|  | 12:13 | 16.5633 | -0.62878 | 0.57454
|  | 12:13 | 16.5644 | -0.64556 | 0.57454
|  | 12:13 | 16.5656 | -0.67309 | 0.57454
|  | 12:13 | 16.5667 | -0.70062 | 0.57453
|  | 12:13 | 16.5678 | -0.7259 | 0.57453
|  | 12:14 | 16.5689 | -0.75118 | 0.57453
|  | 12:14 | 16.57 | -0.76373 | 0.57453
|  | 12:14 | 16.5711 | -0.76355 | 0.57453
|  | 12:14 | 16.5722 | -0.76336 | 0.57452
|  | 12:14 | 16.5733 | -0.74165 | 0.57452
|  | 12:14 | 16.5744 | -0.71995 | 0.57452
|  | 12:14 | 16.5756 | -0.69328 | 0.57452
|  | 12:14 | 16.5767 | -0.66166 | 0.57451
|  | 12:14 | 16.5778 | -0.63004 | 0.57451
|  | 12:14 | 16.5789 | -0.60123 | 0.57451
|  | 12:14 | 16.58 | -0.57243 | 0.57451
|  | 12:14 | 16.5811 | -0.55891 | 0.5745
|  | 12:14 | 16.5822 | -0.56068 | 0.5745
|  | 12:14 | 16.5833 | -0.56245 | 0.5745
|  | 12:14 | 16.5844 | -0.54412 | 0.5745
|  | 12:15 | 16.5856 | -0.52578 | 0.5745
|  | 12:15 | 16.5867 | -0.51626 | 0.57449
|  | 12:15 | 16.5878 | -0.51554 | 0.57449
|  | 12:15 | 16.5889 | -0.51483 | 0.57449
|  | 12:15 | 16.59 | -0.51658 | 0.57449
|  | 12:15 | 16.5911 | -0.51832 | 0.57448
|  | 12:15 | 16.5922 | -0.51742 | 0.57448
|  | 12:15 | 16.5933 | -0.51387 | 0.57448
|  | 12:15 | 16.5944 | -0.51032 | 0.57448
|  | 12:15 | 16.5956 | -0.49265 | 0.57447
|  | 12:15 | 16.5967 | -0.47497 | 0.57447
|  | 12:15 | 16.5978 | -0.4573 | 0.57447
|  | 12:15 | 16.5989 | -0.43963 | 0.57447
|  | 12:15 | 16.6 | -0.42195 | 0.57447
|  | 12:15 | 16.6011 | -0.40033 | 0.57446
|  | 12:16 | 16.6022 | -0.3787 | 0.57446
|  | 12:16 | 16.6033 | -0.35755 | 0.57446
|  | 12:16 | 16.6044 | -0.33687 | 0.57446
|  | 12:16 | 16.6056 | -0.31619 | 0.57445
|  | 12:16 | 16.6067 | -0.27026 | 0.57445
|  | 12:16 | 16.6078 | -0.22432 | 0.57445
|  | 12:16 | 16.6089 | -0.18079 | 0.57445
|  | 12:16 | 16.61 | -0.13806 | 0.57444
|  | 12:16 | 16.6111 | -0.095326 | 0.57444
|  | 12:16 | 16.6122 | -0.056057 | 0.57444
|  | 12:16 | 16.6133 | -0.016788 | 0.57444
|  | 12:16 | 16.6144 | 0.015659 | 0.57444
|  | 12:16 | 16.6156 | 0.041284 | 0.57443
|  | 12:16 | 16.6167 | 0.066908 | 0.57443
|  | 12:16 | 16.6178 | 0.067889 | 0.57443
|  | 12:17 | 16.6189 | 0.06887 | 0.57443
|  | 12:17 | 16.62 | 0.077604 | 0.57442
|  | 12:17 | 16.6211 | 0.094089 | 0.57442
|  | 12:17 | 16.6222 | 0.11057 | 0.57442
|  | 12:17 | 16.6233 | 0.13697 | 0.57442
|  | 12:17 | 16.6244 | 0.16337 | 0.57441
|  | 12:17 | 16.6256 | 0.18555 | 0.57441
|  | 12:17 | 16.6267 | 0.2035 | 0.57441
|  | 12:17 | 16.6278 | 0.22146 | 0.57441
|  | 12:17 | 16.6289 | 0.25483 | 0.57441
|  | 12:17 | 16.63 | 0.2882 | 0.5744
|  | 12:17 | 16.6311 | 0.30837 | 0.5744
|  | 12:17 | 16.6322 | 0.31533 | 0.5744
|  | 12:17 | 16.6333 | 0.32229 | 0.5744
|  | 12:17 | 16.6344 | 0.34371 | 0.57439
|  | 12:18 | 16.6356 | 0.36513 | 0.57439
|  | 12:18 | 16.6367 | 0.39495 | 0.57439
|  | 12:18 | 16.6378 | 0.43316 | 0.57439
|  | 12:18 | 16.6389 | 0.47137 | 0.57438
|  | 12:18 | 16.64 | 0.50421 | 0.57438
|  | 12:18 | 16.6411 | 0.53705 | 0.57438
|  | 12:18 | 16.6422 | 0.56677 | 0.57438
|  | 12:18 | 16.6433 | 0.59337 | 0.57437
|  | 12:18 | 16.6444 | 0.61996 | 0.57437
|  | 12:18 | 16.6456 | 0.63533 | 0.57437
|  | 12:18 | 16.6467 | 0.6507 | 0.57437
|  | 12:18 | 16.6478 | 0.67478 | 0.57437
|  | 12:18 | 16.6489 | 0.70756 | 0.57436
|  | 12:18 | 16.65 | 0.74033 | 0.57436
|  | 12:18 | 16.6511 | 0.7188 | 0.57436
|  | 12:19 | 16.6522 | 0.69726 | 0.57436
|  | 12:19 | 16.6533 | 0.69924 | 0.57435
|  | 12:19 | 16.6544 | 0.72473 | 0.57435
|  | 12:19 | 16.6556 | 0.75023 | 0.57435
|  | 12:19 | 16.6567 | 0.75876 | 0.57435
|  | 12:19 | 16.6578 | 0.76729 | 0.57434
|  | 12:19 | 16.6589 | 0.77299 | 0.57434
|  | 12:19 | 16.66 | 0.77774 | 0.57434
|  | 12:19 | 16.6611 | 0.7825 | 0.57434
|  | 12:19 | 16.6622 | 0.76741 | 0.57434
|  | 12:19 | 16.6633 | 0.75232 | 0.57433
|  | 12:19 | 16.6644 | 0.7296 | 0.57433
|  | 12:19 | 16.6656 | 0.69925 | 0.57433
|  | 12:19 | 16.6667 | 0.6689 | 0.57433
|  | 12:19 | 16.6678 | 0.62576 | 0.57432
|  | 12:20 | 16.6689 | 0.58261 | 0.57432
|  | 12:20 | 16.67 | 0.54949 | 0.57432
|  | 12:20 | 16.6711 | 0.5264 | 0.57432
|  | 12:20 | 16.6722 | 0.50331 | 0.57431
|  | 12:20 | 16.6733 | 0.4765 | 0.57431
|  | 12:20 | 16.6744 | 0.44968 | 0.57431
|  | 12:20 | 16.6756 | 0.4167 | 0.57431
|  | 12:20 | 16.6767 | 0.37755 | 0.57431
|  | 12:20 | 16.6778 | 0.33841 | 0.5743
|  | 12:20 | 16.6789 | 0.29386 | 0.5743
|  | 12:20 | 16.68 | 0.24932 | 0.5743
|  | 12:20 | 16.6811 | 0.21533 | 0.5743
|  | 12:20 | 16.6822 | 0.19189 | 0.57429
|  | 12:20 | 16.6833 | 0.16844 | 0.57429
|  | 12:20 | 16.6844 | 0.16499 | 0.57429
|  | 12:21 | 16.6856 | 0.16153 | 0.57429
|  | 12:21 | 16.6867 | 0.15986 | 0.57428
|  | 12:21 | 16.6878 | 0.15996 | 0.57428
|  | 12:21 | 16.6889 | 0.16005 | 0.57428
|  | 12:21 | 16.69 | 0.14796 | 0.57428
|  | 12:21 | 16.6911 | 0.13587 | 0.57428
|  | 12:21 | 16.6922 | 0.12378 | 0.57427
|  | 12:21 | 16.6933 | 0.1117 | 0.57427
|  | 12:21 | 16.6944 | 0.099605 | 0.57427
|  | 12:21 | 16.6956 | 0.079349 | 0.57427
|  | 12:21 | 16.6967 | 0.059092 | 0.57426
|  | 12:21 | 16.6978 | 0.042185 | 0.57426
|  | 12:21 | 16.6989 | 0.028626 | 0.57426
|  | 12:21 | 16.7 | 0.015067 | 0.57426
|  | 12:21 | 16.7011 | 0.017848 | 0.57425
|  | 12:22 | 16.7022 | 0.020629 | 0.57425
|  | 12:22 | 16.7033 | 0.02341 | 0.57425
|  | 12:22 | 16.7044 | 0.02619 | 0.57425
|  | 12:22 | 16.7056 | 0.028971 | 0.57425
|  | 12:22 | 16.7067 | 0.040168 | 0.57424
|  | 12:22 | 16.7078 | 0.051364 | 0.57424
|  | 12:22 | 16.7089 | 0.060832 | 0.57424
|  | 12:22 | 16.71 | 0.068571 | 0.57424
|  | 12:22 | 16.7111 | 0.076309 | 0.57423
|  | 12:22 | 16.7122 | 0.077437 | 0.57423
|  | 12:22 | 16.7133 | 0.078564 | 0.57423
|  | 12:22 | 16.7144 | 0.080322 | 0.57423
|  | 12:22 | 16.7156 | 0.082711 | 0.57422
|  | 12:22 | 16.7167 | 0.085099 | 0.57422
|  | 12:22 | 16.7178 | 0.082506 | 0.57422
|  | 12:23 | 16.7189 | 0.079913 | 0.57422
|  | 12:23 | 16.72 | 0.07732 | 0.57422
|  | 12:23 | 16.7211 | 0.074727 | 0.57421
|  | 12:23 | 16.7222 | 0.072134 | 0.57421
|  | 12:23 | 16.7233 | 0.05751 | 0.57421
|  | 12:23 | 16.7244 | 0.042887 | 0.57421
|  | 12:23 | 16.7256 | 0.041184 | 0.5742
|  | 12:23 | 16.7267 | 0.052402 | 0.5742
|  | 12:23 | 16.7278 | 0.063621 | 0.5742
|  | 12:23 | 16.7289 | 0.059618 | 0.5742
|  | 12:23 | 16.73 | 0.055615 | 0.57419
|  | 12:23 | 16.7311 | 0.053782 | 0.57419
|  | 12:23 | 16.7322 | 0.054119 | 0.57419
|  | 12:23 | 16.7333 | 0.054456 | 0.57419
|  | 12:23 | 16.7344 | 0.052728 | 0.57419
|  | 12:24 | 16.7356 | 0.051 | 0.57418
|  | 12:24 | 16.7367 | 0.053232 | 0.57418
|  | 12:24 | 16.7378 | 0.059425 | 0.57418
|  | 12:24 | 16.7389 | 0.065617 | 0.57418
|  | 12:24 | 16.74 | 0.089973 | 0.57417
|  | 12:24 | 16.7411 | 0.11433 | 0.57417
|  | 12:24 | 16.7422 | 0.13104 | 0.57417
|  | 12:24 | 16.7433 | 0.14009 | 0.57417
|  | 12:24 | 16.7444 | 0.14915 | 0.57416
|  | 12:24 | 16.7456 | 0.14294 | 0.57416
|  | 12:24 | 16.7467 | 0.13674 | 0.57416
|  | 12:24 | 16.7478 | 0.13903 | 0.57416
|  | 12:24 | 16.7489 | 0.14981 | 0.57416
|  | 12:24 | 16.75 | 0.16059 | 0.57415
|  | 12:24 | 16.7511 | 0.17604 | 0.57415
|  | 12:25 | 16.7522 | 0.1915 | 0.57415
|  | 12:25 | 16.7533 | 0.20614 | 0.57415
|  | 12:25 | 16.7544 | 0.21996 | 0.57414
|  | 12:25 | 16.7556 | 0.23378 | 0.57414
|  | 12:25 | 16.7567 | 0.22649 | 0.57414
|  | 12:25 | 16.7578 | 0.2192 | 0.57414
|  | 12:25 | 16.7589 | 0.2103 | 0.57413
|  | 12:25 | 16.76 | 0.1998 | 0.57413
|  | 12:25 | 16.7611 | 0.18929 | 0.57413
|  | 12:25 | 16.7622 | 0.16969 | 0.57413
|  | 12:25 | 16.7633 | 0.15009 | 0.57412
|  | 12:25 | 16.7644 | 0.12595 | 0.57412
|  | 12:25 | 16.7656 | 0.09729 | 0.57412
|  | 12:25 | 16.7667 | 0.068625 | 0.57412
|  | 12:25 | 16.7678 | 0.07361 | 0.57412
|  | 12:26 | 16.7689 | 0.078594 | 0.57411
|  | 12:26 | 16.77 | 0.072993 | 0.57411
|  | 12:26 | 16.7711 | 0.056805 | 0.57411
|  | 12:26 | 16.7722 | 0.040617 | 0.57411
|  | 12:26 | 16.7733 | 0.014632 | 0.5741
|  | 12:26 | 16.7744 | -0.011353 | 0.5741
|  | 12:26 | 16.7756 | -0.035552 | 0.5741
|  | 12:26 | 16.7767 | -0.057963 | 0.5741
|  | 12:26 | 16.7778 | -0.080375 | 0.57409
|  | 12:26 | 16.7789 | -0.065543 | 0.57409
|  | 12:26 | 16.78 | -0.050712 | 0.57409
|  | 12:26 | 16.7811 | -0.031837 | 0.57409
|  | 12:26 | 16.7822 | -0.0089175 | 0.57409
|  | 12:26 | 16.7833 | 0.014002 | 0.57408
|  | 12:26 | 16.7844 | 0.0028253 | 0.57408
|  | 12:27 | 16.7856 | -0.0083511 | 0.57408
|  | 12:27 | 16.7867 | -0.022928 | 0.57408
|  | 12:27 | 16.7878 | -0.040906 | 0.57407
|  | 12:27 | 16.7889 | -0.058884 | 0.57407
|  | 12:27 | 16.79 | -0.068746 | 0.57407
|  | 12:27 | 16.7911 | -0.078609 | 0.57407
|  | 12:27 | 16.7922 | -0.07932 | 0.57406
|  | 12:27 | 16.7933 | -0.076982 | 0.57406
|  | 12:27 | 16.7944 | -0.074643 | 0.57406
|  | 12:27 | 16.7956 | -0.075455 | 0.57406
|  | 12:27 | 16.7967 | -0.076267 | 0.57406
|  | 12:27 | 16.7978 | -0.073963 | 0.57405
|  | 12:27 | 16.7989 | -0.07062 | 0.57405
|  | 12:27 | 16.8 | -0.067277 | 0.57405
|  | 12:27 | 16.8011 | -0.087801 | 0.57405
|  | 12:28 | 16.8022 | -0.10832 | 0.57404
|  | 12:28 | 16.8033 | -0.11242 | 0.57404
|  | 12:28 | 16.8044 | -0.10009 | 0.57404
|  | 12:28 | 16.8056 | -0.087763 | 0.57404
|  | 12:28 | 16.8067 | -0.068639 | 0.57403
|  | 12:28 | 16.8078 | -0.049516 | 0.57403
|  | 12:28 | 16.8089 | -0.015747 | 0.57403
|  | 12:28 | 16.81 | 0.032669 | 0.57403
|  | 12:28 | 16.8111 | 0.076313 | 0.57403
|  | 12:28 | 16.8122 | 0.10565 | 0.57402
|  | 12:28 | 16.8133 | 0.13498 | 0.57402
|  | 12:28 | 16.8144 | 0.14996 | 0.57402
|  | 12:28 | 16.8156 | 0.1506 | 0.57402
|  | 12:28 | 16.8167 | 0.15123 | 0.57401
|  | 12:28 | 16.8178 | 0.15947 | 0.57401
|  | 12:29 | 16.8189 | 0.1677 | 0.57401
|  | 12:29 | 16.82 | 0.16361 | 0.57401
|  | 12:29 | 16.8211 | 0.14719 | 0.574
|  | 12:29 | 16.8222 | 0.13078 | 0.574
|  | 12:29 | 16.8233 | 0.11437 | 0.574
|  | 12:29 | 16.8244 | 0.097961 | 0.574
|  | 12:29 | 16.8256 | 0.077558 | 0.574
|  | 12:29 | 16.8267 | 0.055824 | 0.57399
|  | 12:29 | 16.8278 | 0.034089 | 0.57399
|  | 12:29 | 16.8289 | 0.018564 | 0.57399
|  | 12:29 | 16.83 | 0.0030393 | 0.57399
|  | 12:29 | 16.8311 | -0.016027 | 0.57398
|  | 12:29 | 16.8322 | -0.038635 | 0.57398
|  | 12:29 | 16.8333 | -0.061243 | 0.57398
|  | 12:29 | 16.8344 | -0.068344 | 0.57398
|  | 12:30 | 16.8356 | -0.075445 | 0.57397
|  | 12:30 | 16.8367 | -0.080764 | 0.57397
|  | 12:30 | 16.8378 | -0.0843 | 0.57397
|  | 12:30 | 16.8389 | -0.087836 | 0.57397
|  | 12:30 | 16.84 | -0.08516 | 0.57397
|  | 12:30 | 16.8411 | -0.082483 | 0.57396
|  | 12:30 | 16.8422 | -0.079807 | 0.57396
|  | 12:30 | 16.8433 | -0.07713 | 0.57396
|  | 12:30 | 16.8444 | -0.074454 | 0.57396
|  | 12:30 | 16.8456 | -0.076025 | 0.57395
|  | 12:30 | 16.8467 | -0.077597 | 0.57395
|  | 12:30 | 16.8478 | -0.085439 | 0.57395
|  | 12:30 | 16.8489 | -0.09955 | 0.57395
|  | 12:30 | 16.85 | -0.11366 | 0.57394
|  | 12:30 | 16.8511 | -0.11441 | 0.57394
|  | 12:31 | 16.8522 | -0.11516 | 0.57394
|  | 12:31 | 16.8533 | -0.10971 | 0.57394
|  | 12:31 | 16.8544 | -0.09806 | 0.57394
|  | 12:31 | 16.8556 | -0.084509 | 0.57393
|  | 12:31 | 16.8567 | -0.065244 | 0.57393
|  | 12:31 | 16.8578 | -0.045979 | 0.57393
|  | 12:31 | 16.8589 | -0.029559 | 0.57393
|  | 12:31 | 16.86 | -0.015984 | 0.57392
|  | 12:31 | 16.8611 | -0.0024094 | 0.57392
|  | 12:31 | 16.8622 | 0.022238 | 0.57392
|  | 12:31 | 16.8633 | 0.046885 | 0.57392
|  | 12:31 | 16.8644 | 0.074314 | 0.57391
|  | 12:31 | 16.8656 | 0.10453 | 0.57391
|  | 12:31 | 16.8667 | 0.13474 | 0.57391
|  | 12:31 | 16.8678 | 0.15843 | 0.57391
|  | 12:32 | 16.8689 | 0.18212 | 0.57391
|  | 12:32 | 16.87 | 0.20365 | 0.5739
|  | 12:32 | 16.8711 | 0.22304 | 0.5739
|  | 12:32 | 16.8722 | 0.24243 | 0.5739
|  | 12:32 | 16.8733 | 0.2467 | 0.5739
|  | 12:32 | 16.8744 | 0.25097 | 0.57389
|  | 12:32 | 16.8756 | 0.25524 | 0.57389
|  | 12:32 | 16.8767 | 0.25952 | 0.57389
|  | 12:32 | 16.8778 | 0.26379 | 0.57389
|  | 12:32 | 16.8789 | 0.26806 | 0.57388
|  | 12:32 | 16.88 | 0.27234 | 0.57388
|  | 12:32 | 16.8811 | 0.27055 | 0.57388
|  | 12:32 | 16.8822 | 0.26272 | 0.57388
|  | 12:32 | 16.8833 | 0.25488 | 0.57387
|  | 12:32 | 16.8844 | 0.23498 | 0.57387
|  | 12:33 | 16.8856 | 0.21507 | 0.57387
|  | 12:33 | 16.8867 | 0.20228 | 0.57387
|  | 12:33 | 16.8878 | 0.1966 | 0.57387
|  | 12:33 | 16.8889 | 0.19092 | 0.57386
|  | 12:33 | 16.89 | 0.17374 | 0.57386
|  | 12:33 | 16.8911 | 0.15656 | 0.57386
|  | 12:33 | 16.8922 | 0.14737 | 0.57386
|  | 12:33 | 16.8933 | 0.14617 | 0.57385
|  | 12:33 | 16.8944 | 0.14096 | 0.57385
|  | 12:33 | 16.8956 | 0.1237 | 0.57385
|  | 12:33 | 16.8967 | 0.10644 | 0.57385
|  | 12:33 | 16.8978 | 0.091813 | 0.57384
|  | 12:33 | 16.8989 | 0.079822 | 0.57384
|  | 12:33 | 16.9 | 0.067831 | 0.57384
|  | 12:33 | 16.9011 | 0.075896 | 0.57384
|  | 12:34 | 16.9022 | 0.083961 | 0.57384
|  | 12:34 | 16.9033 | 0.086463 | 0.57383
|  | 12:34 | 16.9044 | 0.083403 | 0.57383
|  | 12:34 | 16.9056 | 0.080342 | 0.57383
|  | 12:34 | 16.9067 | 0.086139 | 0.57383
|  | 12:34 | 16.9078 | 0.091936 | 0.57382
|  | 12:34 | 16.9089 | 0.086932 | 0.57382
|  | 12:34 | 16.91 | 0.071129 | 0.57382
|  | 12:34 | 16.9111 | 0.055325 | 0.57382
|  | 12:34 | 16.9122 | 0.058039 | 0.57381
|  | 12:34 | 16.9133 | 0.060754 | 0.57381
|  | 12:34 | 16.9144 | 0.053289 | 0.57381
|  | 12:34 | 16.9156 | 0.035644 | 0.57381
|  | 12:34 | 16.9167 | 0.018 | 0.57381
|  | 12:34 | 16.9178 | -0.013065 | 0.5738
|  | 12:35 | 16.9189 | -0.04413 | 0.5738
|  | 12:35 | 16.92 | -0.070275 | 0.5738
|  | 12:35 | 16.9211 | -0.091499 | 0.5738
|  | 12:35 | 16.9222 | -0.11272 | 0.57379
|  | 12:35 | 16.9233 | -0.1153 | 0.57379
|  | 12:35 | 16.9244 | -0.11788 | 0.57379
|  | 12:35 | 16.9256 | -0.11783 | 0.57379
|  | 12:35 | 16.9267 | -0.11514 | 0.57378
|  | 12:35 | 16.9278 | -0.11272 | 0.57378
|  | 12:35 | 16.9289 | -0.11108 | 0.57378
|  | 12:35 | 16.93 | -0.10944 | 0.57378
|  | 12:35 | 16.9311 | -0.1078 | 0.57378
|  | 12:35 | 16.9322 | -0.12031 | 0.57377
|  | 12:35 | 16.9333 | -0.13283 | 0.57377
|  | 12:35 | 16.9344 | -0.13556 | 0.57377
|  | 12:36 | 16.9356 | -0.1383 | 0.57377
|  | 12:36 | 16.9367 | -0.13564 | 0.57376
|  | 12:36 | 16.9378 | -0.13119 | 0.57376
|  | 12:36 | 16.9389 | -0.1251 | 0.57376
|  | 12:36 | 16.94 | -0.11411 | 0.57376
|  | 12:36 | 16.9411 | -0.10312 | 0.57375
|  | 12:36 | 16.9422 | -0.087127 | 0.57375
|  | 12:36 | 16.9433 | -0.06947 | 0.57375
|  | 12:36 | 16.9444 | -0.057029 | 0.57375
|  | 12:36 | 16.9456 | -0.060235 | 0.57375
|  | 12:36 | 16.9467 | -0.06344 | 0.57374
|  | 12:36 | 16.9478 | -0.059529 | 0.57374
|  | 12:36 | 16.9489 | -0.053247 | 0.57374
|  | 12:36 | 16.95 | -0.048412 | 0.57374
|  | 12:36 | 16.9511 | -0.047923 | 0.57373
|  | 12:37 | 16.9522 | -0.047434 | 0.57373
|  | 12:37 | 16.9533 | -0.052124 | 0.57373
|  | 12:37 | 16.9544 | -0.05854 | 0.57373
|  | 12:37 | 16.9556 | -0.068618 | 0.57372
|  | 12:37 | 16.9567 | -0.08968 | 0.57372
|  | 12:37 | 16.9578 | -0.11074 | 0.57372
|  | 12:37 | 16.9589 | -0.12803 | 0.57372
|  | 12:37 | 16.96 | -0.14405 | 0.57372
|  | 12:37 | 16.9611 | -0.15587 | 0.57371
|  | 12:37 | 16.9622 | -0.15507 | 0.57371
|  | 12:37 | 16.9633 | -0.15427 | 0.57371
|  | 12:37 | 16.9644 | -0.1689 | 0.57371
|  | 12:37 | 16.9656 | -0.18867 | 0.5737
|  | 12:37 | 16.9667 | -0.19879 | 0.5737
|  | 12:37 | 16.9678 | -0.17995 | 0.5737
|  | 12:38 | 16.9689 | -0.16112 | 0.5737
|  | 12:38 | 16.97 | -0.14042 | 0.57369
|  | 12:38 | 16.9711 | -0.1191 | 0.57369
|  | 12:38 | 16.9722 | -0.087246 | 0.57369
|  | 12:38 | 16.9733 | -0.023777 | 0.57369
|  | 12:38 | 16.9744 | 0.039692 | 0.57369
|  | 12:38 | 16.9756 | 0.084628 | 0.57368
|  | 12:38 | 16.9767 | 0.12956 | 0.57368
|  | 12:38 | 16.9778 | 0.17372 | 0.57368
|  | 12:38 | 16.9789 | 0.21556 | 0.57368
|  | 12:38 | 16.98 | 0.2574 | 0.57367
|  | 12:38 | 16.9811 | 0.26371 | 0.57367
|  | 12:38 | 16.9822 | 0.25818 | 0.57367
|  | 12:38 | 16.9833 | 0.25264 | 0.57367
|  | 12:38 | 16.9844 | 0.24711 | 0.57366
|  | 12:39 | 16.9856 | 0.24157 | 0.57366
|  | 12:39 | 16.9867 | 0.24404 | 0.57366
|  | 12:39 | 16.9878 | 0.24918 | 0.57366
|  | 12:39 | 16.9889 | 0.25653 | 0.57366
|  | 12:39 | 16.99 | 0.27053 | 0.57365
|  | 12:39 | 16.9911 | 0.28454 | 0.57365
|  | 12:39 | 16.9922 | 0.28643 | 0.57365
|  | 12:39 | 16.9933 | 0.28428 | 0.57365
|  | 12:39 | 16.9944 | 0.28637 | 0.57364
|  | 12:39 | 16.9956 | 0.30114 | 0.57364
|  | 12:39 | 16.9967 | 0.31592 | 0.57364
|  | 12:39 | 16.9978 | 0.32289 | 0.57364
|  | 12:39 | 16.9989 | 0.32726 | 0.57363
|  | 12:39 | 17 | 0.32399 | 0.57363
|  | 12:39 | 17.0011 | 0.3131 | 0.57363
|  | 12:40 | 17.0022 | 0.3022 | 0.57363
|  | 12:40 | 17.0033 | 0.28574 | 0.57362
|  | 12:40 | 17.0044 | 0.26742 | 0.57362
|  | 12:40 | 17.0056 | 0.24996 | 0.57362
|  | 12:40 | 17.0067 | 0.23337 | 0.57362
|  | 12:40 | 17.0078 | 0.21678 | 0.57362
|  | 12:40 | 17.0089 | 0.18735 | 0.57361
|  | 12:40 | 17.01 | 0.15364 | 0.57361
|  | 12:40 | 17.0111 | 0.13899 | 0.57361
|  | 12:40 | 17.0122 | 0.1434 | 0.57361
|  | 12:40 | 17.0133 | 0.1478 | 0.5736
|  | 12:40 | 17.0144 | 0.16101 | 0.5736
|  | 12:40 | 17.0156 | 0.17715 | 0.5736
|  | 12:40 | 17.0167 | 0.1784 | 0.5736
|  | 12:40 | 17.0178 | 0.16474 | 0.57359
|  | 12:41 | 17.0189 | 0.15109 | 0.57359
|  | 12:41 | 17.02 | 0.12306 | 0.57359
|  | 12:41 | 17.0211 | 0.090241 | 0.57359
|  | 12:41 | 17.0222 | 0.056587 | 0.57359
|  | 12:41 | 17.0233 | 0.020429 | 0.57358
|  | 12:41 | 17.0244 | -0.015729 | 0.57358
|  | 12:41 | 17.0256 | -0.042232 | 0.57358
|  | 12:41 | 17.0267 | -0.065516 | 0.57358
|  | 12:41 | 17.0278 | -0.087599 | 0.57357
|  | 12:41 | 17.0289 | -0.10608 | 0.57357
|  | 12:41 | 17.03 | -0.12456 | 0.57357
|  | 12:41 | 17.0311 | -0.13921 | 0.57357
|  | 12:41 | 17.0322 | -0.15259 | 0.57356
|  | 12:41 | 17.0333 | -0.16354 | 0.57356
|  | 12:41 | 17.0344 | -0.16719 | 0.57356
|  | 12:42 | 17.0356 | -0.17083 | 0.57356
|  | 12:42 | 17.0367 | -0.19514 | 0.57356
|  | 12:42 | 17.0378 | -0.22632 | 0.57355
|  | 12:42 | 17.0389 | -0.24783 | 0.57355
|  | 12:42 | 17.04 | -0.24028 | 0.57355
|  | 12:42 | 17.0411 | -0.23273 | 0.57355
|  | 12:42 | 17.0422 | -0.22091 | 0.57354
|  | 12:42 | 17.0433 | -0.20767 | 0.57354
|  | 12:42 | 17.0444 | -0.19169 | 0.57354
|  | 12:42 | 17.0456 | -0.1675 | 0.57354
|  | 12:42 | 17.0467 | -0.14331 | 0.57353
|  | 12:42 | 17.0478 | -0.12658 | 0.57353
|  | 12:42 | 17.0489 | -0.11235 | 0.57353
|  | 12:42 | 17.05 | -0.099041 | 0.57353
|  | 12:42 | 17.0511 | -0.088485 | 0.57353
|  | 12:43 | 17.0522 | -0.077929 | 0.57352
|  | 12:43 | 17.0533 | -0.06405 | 0.57352
|  | 12:43 | 17.0544 | -0.049063 | 0.57352
|  | 12:43 | 17.0556 | -0.032325 | 0.57352
|  | 12:43 | 17.0567 | -0.01033 | 0.57351
|  | 12:43 | 17.0578 | 0.011664 | 0.57351
|  | 12:43 | 17.0589 | 0.025807 | 0.57351
|  | 12:43 | 17.06 | 0.037333 | 0.57351
|  | 12:43 | 17.0611 | 0.049144 | 0.5735
|  | 12:43 | 17.0622 | 0.06181 | 0.5735
|  | 12:43 | 17.0633 | 0.074475 | 0.5735
|  | 12:43 | 17.0644 | 0.088406 | 0.5735
|  | 12:43 | 17.0656 | 0.10276 | 0.5735
|  | 12:43 | 17.0667 | 0.11637 | 0.57349
|  | 12:43 | 17.0678 | 0.12776 | 0.57349
|  | 12:44 | 17.0689 | 0.13916 | 0.57349
|  | 12:44 | 17.07 | 0.15333 | 0.57349
|  | 12:44 | 17.0711 | 0.16843 | 0.57348
|  | 12:44 | 17.0722 | 0.18226 | 0.57348
|  | 12:44 | 17.0733 | 0.19228 | 0.57348
|  | 12:44 | 17.0744 | 0.20229 | 0.57348
|  | 12:44 | 17.0756 | 0.18703 | 0.57347
|  | 12:44 | 17.0767 | 0.17176 | 0.57347
|  | 12:44 | 17.0778 | 0.15361 | 0.57347
|  | 12:44 | 17.0789 | 0.12677 | 0.57347
|  | 12:44 | 17.08 | 0.099932 | 0.57347
|  | 12:44 | 17.0811 | 0.080254 | 0.57346
|  | 12:44 | 17.0822 | 0.062962 | 0.57346
|  | 12:44 | 17.0833 | 0.049071 | 0.57346
|  | 12:44 | 17.0844 | 0.045383 | 0.57346
|  | 12:45 | 17.0856 | 0.041695 | 0.57345
|  | 12:45 | 17.0867 | 0.032198 | 0.57345
|  | 12:45 | 17.0878 | 0.020765 | 0.57345
|  | 12:45 | 17.0889 | 0.010218 | 0.57345
|  | 12:45 | 17.09 | 0.0023298 | 0.57344
|  | 12:45 | 17.0911 | -0.0055582 | 0.57344
|  | 12:45 | 17.0922 | -0.023576 | 0.57344
|  | 12:45 | 17.0933 | -0.04497 | 0.57344
|  | 12:45 | 17.0944 | -0.063236 | 0.57344
|  | 12:45 | 17.0956 | -0.072119 | 0.57343
|  | 12:45 | 17.0967 | -0.081002 | 0.57343
|  | 12:45 | 17.0978 | -0.091497 | 0.57343
|  | 12:45 | 17.0989 | -0.10253 | 0.57343
|  | 12:45 | 17.1 | -0.11184 | 0.57342
|  | 12:45 | 17.1011 | -0.11599 | 0.57342
|  | 12:46 | 17.1022 | -0.12014 | 0.57342
|  | 12:46 | 17.1033 | -0.12608 | 0.57342
|  | 12:46 | 17.1044 | -0.13383 | 0.57341
|  | 12:46 | 17.1056 | -0.14157 | 0.57341
|  | 12:46 | 17.1067 | -0.14002 | 0.57341
|  | 12:46 | 17.1078 | -0.13847 | 0.57341
|  | 12:46 | 17.1089 | -0.14396 | 0.57341
|  | 12:46 | 17.11 | -0.1565 | 0.5734
|  | 12:46 | 17.1111 | -0.16904 | 0.5734
|  | 12:46 | 17.1122 | -0.18405 | 0.5734
|  | 12:46 | 17.1133 | -0.19905 | 0.5734
|  | 12:46 | 17.1144 | -0.20539 | 0.57339
|  | 12:46 | 17.1156 | -0.20306 | 0.57339
|  | 12:46 | 17.1167 | -0.20073 | 0.57339
|  | 12:46 | 17.1178 | -0.17283 | 0.57339
|  | 12:47 | 17.1189 | -0.14493 | 0.57338
|  | 12:47 | 17.12 | -0.1155 | 0.57338
|  | 12:47 | 17.1211 | -0.084542 | 0.57338
|  | 12:47 | 17.1222 | -0.053583 | 0.57338
|  | 12:47 | 17.1233 | -0.01823 | 0.57337
|  | 12:47 | 17.1244 | 0.017124 | 0.57337
|  | 12:47 | 17.1256 | 0.042132 | 0.57337
|  | 12:47 | 17.1267 | 0.056796 | 0.57337
|  | 12:47 | 17.1278 | 0.07146 | 0.57337
|  | 12:47 | 17.1289 | 0.069582 | 0.57336
|  | 12:47 | 17.13 | 0.067705 | 0.57336
|  | 12:47 | 17.1311 | 0.068706 | 0.57336
|  | 12:47 | 17.1322 | 0.072586 | 0.57336
|  | 12:47 | 17.1333 | 0.076467 | 0.57335
|  | 12:47 | 17.1344 | 0.08665 | 0.57335
|  | 12:48 | 17.1356 | 0.096832 | 0.57335
|  | 12:48 | 17.1367 | 0.097433 | 0.57335
|  | 12:48 | 17.1378 | 0.088452 | 0.57334
|  | 12:48 | 17.1389 | 0.079471 | 0.57334
|  | 12:48 | 17.14 | 0.07049 | 0.57334
|  | 12:48 | 17.1411 | 0.061509 | 0.57334
|  | 12:48 | 17.1422 | 0.044761 | 0.57334
|  | 12:48 | 17.1433 | 0.020245 | 0.57333
|  | 12:48 | 17.1444 | -0.0042709 | 0.57333
|  | 12:48 | 17.1456 | -0.0071686 | 0.57333
|  | 12:48 | 17.1467 | -0.010066 | 0.57333
|  | 12:48 | 17.1478 | -0.015785 | 0.57332
|  | 12:48 | 17.1489 | -0.024325 | 0.57332
|  | 12:48 | 17.15 | -0.032865 | 0.57332
|  | 12:48 | 17.1511 | -0.041405 | 0.57332
|  | 12:49 | 17.1522 | -0.049945 | 0.57331
|  | 12:49 | 17.1533 | -0.061732 | 0.57331
|  | 12:49 | 17.1544 | -0.076764 | 0.57331
|  | 12:49 | 17.1556 | -0.091797 | 0.57331
|  | 12:49 | 17.1567 | -0.081949 | 0.57331
|  | 12:49 | 17.1578 | -0.072101 | 0.5733
|  | 12:49 | 17.1589 | -0.069993 | 0.5733
|  | 12:49 | 17.16 | -0.075625 | 0.5733
|  | 12:49 | 17.1611 | -0.081256 | 0.5733
|  | 12:49 | 17.1622 | -0.10398 | 0.57329
|  | 12:49 | 17.1633 | -0.12671 | 0.57329
|  | 12:49 | 17.1644 | -0.13424 | 0.57329
|  | 12:49 | 17.1656 | -0.13671 | 0.57329
|  | 12:49 | 17.1667 | -0.13917 | 0.57328
|  | 12:49 | 17.1678 | -0.13967 | 0.57328
|  | 12:50 | 17.1689 | -0.14016 | 0.57328
|  | 12:50 | 17.17 | -0.13967 | 0.57328
|  | 12:50 | 17.1711 | -0.1382 | 0.57328
|  | 12:50 | 17.1722 | -0.13672 | 0.57327
|  | 12:50 | 17.1733 | -0.13986 | 0.57327
|  | 12:50 | 17.1744 | -0.143 | 0.57327
|  | 12:50 | 17.1756 | -0.15783 | 0.57327
|  | 12:50 | 17.1767 | -0.18435 | 0.57326
|  | 12:50 | 17.1778 | -0.21088 | 0.57326
|  | 12:50 | 17.1789 | -0.23015 | 0.57326
|  | 12:50 | 17.18 | -0.24943 | 0.57326
|  | 12:50 | 17.1811 | -0.27026 | 0.57325
|  | 12:50 | 17.1822 | -0.29265 | 0.57325
|  | 12:50 | 17.1833 | -0.31503 | 0.57325
|  | 12:50 | 17.1844 | -0.32195 | 0.57325
|  | 12:51 | 17.1856 | -0.32886 | 0.57325
|  | 12:51 | 17.1867 | -0.34119 | 0.57324
|  | 12:51 | 17.1878 | -0.35894 | 0.57324
|  | 12:51 | 17.1889 | -0.37669 | 0.57324
|  | 12:51 | 17.19 | -0.40678 | 0.57324
|  | 12:51 | 17.1911 | -0.43687 | 0.57323
|  | 12:51 | 17.1922 | -0.47126 | 0.57323
|  | 12:51 | 17.1933 | -0.50996 | 0.57323
|  | 12:51 | 17.1944 | -0.54865 | 0.57323
|  | 12:51 | 17.1956 | -0.56956 | 0.57322
|  | 12:51 | 17.1967 | -0.59046 | 0.57322
|  | 12:51 | 17.1978 | -0.60099 | 0.57322
|  | 12:51 | 17.1989 | -0.60114 | 0.57322
|  | 12:51 | 17.2 | -0.60129 | 0.57322
|  | 12:51 | 17.2011 | -0.60725 | 0.57321
|  | 12:52 | 17.2022 | -0.6132 | 0.57321
|  | 12:52 | 17.2033 | -0.61495 | 0.57321
|  | 12:52 | 17.2044 | -0.6125 | 0.57321
|  | 12:52 | 17.2056 | -0.61004 | 0.5732
|  | 12:52 | 17.2067 | -0.60192 | 0.5732
|  | 12:52 | 17.2078 | -0.59379 | 0.5732
|  | 12:52 | 17.2089 | -0.57338 | 0.5732
|  | 12:52 | 17.21 | -0.54068 | 0.57319
|  | 12:52 | 17.2111 | -0.50798 | 0.57319
|  | 12:52 | 17.2122 | -0.44948 | 0.57319
|  | 12:52 | 17.2133 | -0.39097 | 0.57319
|  | 12:52 | 17.2144 | -0.34491 | 0.57319
|  | 12:52 | 17.2156 | -0.30298 | 0.57318
|  | 12:52 | 17.2167 | -0.26106 | 0.57318
|  | 12:52 | 17.2178 | -0.21372 | 0.57318
|  | 12:53 | 17.2189 | -0.16637 | 0.57318
|  | 12:53 | 17.22 | -0.13138 | 0.57317
|  | 12:53 | 17.2211 | -0.10875 | 0.57317
|  | 12:53 | 17.2222 | -0.086123 | 0.57317
|  | 12:53 | 17.2233 | -0.059309 | 0.57317
|  | 12:53 | 17.2244 | -0.032495 | 0.57316
|  | 12:53 | 17.2256 | -0.0085625 | 0.57316
|  | 12:53 | 17.2267 | 0.01441 | 0.57316
|  | 12:53 | 17.2278 | 0.037382 | 0.57316
|  | 12:53 | 17.2289 | 0.066252 | 0.57316
|  | 12:53 | 17.23 | 0.095122 | 0.57315
|  | 12:53 | 17.2311 | 0.10872 | 0.57315
|  | 12:53 | 17.2322 | 0.10704 | 0.57315
|  | 12:53 | 17.2333 | 0.10536 | 0.57315
|  | 12:53 | 17.2344 | 0.10089 | 0.57314
|  | 12:54 | 17.2356 | 0.088038 | 0.57314
|  | 12:54 | 17.2367 | 0.080428 | 0.57314
|  | 12:54 | 17.2378 | 0.078054 | 0.57314
|  | 12:54 | 17.2389 | 0.07568 | 0.57313
|  | 12:54 | 17.24 | 0.060873 | 0.57313
|  | 12:54 | 17.2411 | 0.046067 | 0.57313
|  | 12:54 | 17.2422 | 0.032489 | 0.57313
|  | 12:54 | 17.2433 | 0.02014 | 0.57312
|  | 12:54 | 17.2444 | 0.0077913 | 0.57312
|  | 12:54 | 17.2456 | 0.0089382 | 0.57312
|  | 12:54 | 17.2467 | 0.010085 | 0.57312
|  | 12:54 | 17.2478 | 0.017944 | 0.57312
|  | 12:54 | 17.2489 | 0.032514 | 0.57311
|  | 12:54 | 17.25 | 0.047085 | 0.57311
|  | 12:54 | 17.2511 | 0.076109 | 0.57311
|  | 12:55 | 17.2522 | 0.10513 | 0.57311
|  | 12:55 | 17.2533 | 0.13867 | 0.5731
|  | 12:55 | 17.2544 | 0.17371 | 0.5731
|  | 12:55 | 17.2556 | 0.20875 | 0.5731
|  | 12:55 | 17.2567 | 0.23334 | 0.5731
|  | 12:55 | 17.2578 | 0.25792 | 0.57309
|  | 12:55 | 17.2589 | 0.27615 | 0.57309
|  | 12:55 | 17.26 | 0.28804 | 0.57309
|  | 12:55 | 17.2611 | 0.29992 | 0.57309
|  | 12:55 | 17.2622 | 0.31798 | 0.57309
|  | 12:55 | 17.2633 | 0.33605 | 0.57308
|  | 12:55 | 17.2644 | 0.36385 | 0.57308
|  | 12:55 | 17.2656 | 0.40137 | 0.57308
|  | 12:55 | 17.2667 | 0.4389 | 0.57308
|  | 12:55 | 17.2678 | 0.47837 | 0.57307
|  | 12:56 | 17.2689 | 0.51784 | 0.57307
|  | 12:56 | 17.27 | 0.54605 | 0.57307
|  | 12:56 | 17.2711 | 0.57051 | 0.57307
|  | 12:56 | 17.2722 | 0.59043 | 0.57306
|  | 12:56 | 17.2733 | 0.59672 | 0.57306
|  | 12:56 | 17.2744 | 0.60301 | 0.57306
|  | 12:56 | 17.2756 | 0.61476 | 0.57306
|  | 12:56 | 17.2767 | 0.62833 | 0.57306
|  | 12:56 | 17.2778 | 0.63908 | 0.57305
|  | 12:56 | 17.2789 | 0.64134 | 0.57305
|  | 12:56 | 17.28 | 0.6436 | 0.57305
|  | 12:56 | 17.2811 | 0.64966 | 0.57305
|  | 12:56 | 17.2822 | 0.65699 | 0.57304
|  | 12:56 | 17.2833 | 0.66861 | 0.57304
|  | 12:56 | 17.2844 | 0.69311 | 0.57304
|  | 12:57 | 17.2856 | 0.71761 | 0.57304
|  | 12:57 | 17.2867 | 0.72431 | 0.57303
|  | 12:57 | 17.2878 | 0.72507 | 0.57303
|  | 12:57 | 17.2889 | 0.72324 | 0.57303
|  | 12:57 | 17.29 | 0.71361 | 0.57303
|  | 12:57 | 17.2911 | 0.70399 | 0.57303
|  | 12:57 | 17.2922 | 0.68391 | 0.57302
|  | 12:57 | 17.2933 | 0.66036 | 0.57302
|  | 12:57 | 17.2944 | 0.63042 | 0.57302
|  | 12:57 | 17.2956 | 0.58134 | 0.57302
|  | 12:57 | 17.2967 | 0.53226 | 0.57301
|  | 12:57 | 17.2978 | 0.48119 | 0.57301
|  | 12:57 | 17.2989 | 0.42944 | 0.57301
|  | 12:57 | 17.3 | 0.38903 | 0.57301
|  | 12:57 | 17.3011 | 0.35995 | 0.573
|  | 12:58 | 17.3022 | 0.33088 | 0.573
|  | 12:58 | 17.3033 | 0.2821 | 0.573
|  | 12:58 | 17.3044 | 0.22676 | 0.573
|  | 12:58 | 17.3056 | 0.17658 | 0.573
|  | 12:58 | 17.3067 | 0.1419 | 0.57299
|  | 12:58 | 17.3078 | 0.10722 | 0.57299
|  | 12:58 | 17.3089 | 0.081901 | 0.57299
|  | 12:58 | 17.31 | 0.056586 | 0.57299
|  | 12:58 | 17.3111 | 0.030142 | 0.57298
|  | 12:58 | 17.3122 | 0.00031549 | 0.57298
|  | 12:58 | 17.3133 | -0.029511 | 0.57298
|  | 12:58 | 17.3144 | -0.058698 | 0.57298
|  | 12:58 | 17.3156 | -0.087671 | 0.57297
|  | 12:58 | 17.3167 | -0.11306 | 0.57297
|  | 12:58 | 17.3178 | -0.12771 | 0.57297
|  | 12:59 | 17.3189 | -0.14236 | 0.57297
|  | 12:59 | 17.32 | -0.16624 | 0.57297
|  | 12:59 | 17.3211 | -0.1932 | 0.57296
|  | 12:59 | 17.3222 | -0.22575 | 0.57296
|  | 12:59 | 17.3233 | -0.2751 | 0.57296
|  | 12:59 | 17.3244 | -0.32445 | 0.57296
|  | 12:59 | 17.3256 | -0.35449 | 0.57295
|  | 12:59 | 17.3267 | -0.37809 | 0.57295
|  | 12:59 | 17.3278 | -0.39723 | 0.57295
|  | 12:59 | 17.3289 | -0.40298 | 0.57295
|  | 12:59 | 17.33 | -0.40874 | 0.57294
|  | 12:59 | 17.3311 | -0.41121 | 0.57294
|  | 12:59 | 17.3322 | -0.41258 | 0.57294
|  | 12:59 | 17.3333 | -0.4191 | 0.57294
|  | 12:59 | 17.3344 | -0.44105 | 0.57294
|  | 13:00 | 17.3356 | -0.46301 | 0.57293
|  | 13:00 | 17.3367 | -0.4794 | 0.57293
|  | 13:00 | 17.3378 | -0.49394 | 0.57293
|  | 13:00 | 17.3389 | -0.50803 | 0.57293
|  | 13:00 | 17.34 | -0.52082 | 0.57292
|  | 13:00 | 17.3411 | -0.53361 | 0.57292
|  | 13:00 | 17.3422 | -0.57167 | 0.57292
|  | 13:00 | 17.3433 | -0.61817 | 0.57292
|  | 13:00 | 17.3444 | -0.65686 | 0.57291
|  | 13:00 | 17.3456 | -0.67212 | 0.57291
|  | 13:00 | 17.3467 | -0.68739 | 0.57291
|  | 13:00 | 17.3478 | -0.69862 | 0.57291
|  | 13:00 | 17.3489 | -0.7085 | 0.57291
|  | 13:00 | 17.35 | -0.7136 | 0.5729
|  | 13:00 | 17.3511 | -0.70432 | 0.5729
|  | 13:01 | 17.3522 | -0.69505 | 0.5729
|  | 13:01 | 17.3533 | -0.67207 | 0.5729
|  | 13:01 | 17.3544 | -0.64451 | 0.57289
|  | 13:01 | 17.3556 | -0.61836 | 0.57289
|  | 13:01 | 17.3567 | -0.59644 | 0.57289
|  | 13:01 | 17.3578 | -0.57451 | 0.57289
|  | 13:01 | 17.3589 | -0.55325 | 0.57288
|  | 13:01 | 17.36 | -0.53222 | 0.57288
|  | 13:01 | 17.3611 | -0.51696 | 0.57288
|  | 13:01 | 17.3622 | -0.51903 | 0.57288
|  | 13:01 | 17.3633 | -0.5211 | 0.57287
|  | 13:01 | 17.3644 | -0.52402 | 0.57287
|  | 13:01 | 17.3656 | -0.52724 | 0.57287
|  | 13:01 | 17.3667 | -0.52781 | 0.57287
|  | 13:01 | 17.3678 | -0.52046 | 0.57287
|  | 13:02 | 17.3689 | -0.51311 | 0.57286
|  | 13:02 | 17.37 | -0.49295 | 0.57286
|  | 13:02 | 17.3711 | -0.46852 | 0.57286
|  | 13:02 | 17.3722 | -0.44277 | 0.57286
|  | 13:02 | 17.3733 | -0.41302 | 0.57285
|  | 13:02 | 17.3744 | -0.38327 | 0.57285
|  | 13:02 | 17.3756 | -0.36219 | 0.57285
|  | 13:02 | 17.3767 | -0.34399 | 0.57285
|  | 13:02 | 17.3778 | -0.32331 | 0.57284
|  | 13:02 | 17.3789 | -0.29521 | 0.57284
|  | 13:02 | 17.38 | -0.26711 | 0.57284
|  | 13:02 | 17.3811 | -0.22818 | 0.57284
|  | 13:02 | 17.3822 | -0.18565 | 0.57284
|  | 13:02 | 17.3833 | -0.14681 | 0.57283
|  | 13:02 | 17.3844 | -0.11909 | 0.57283
|  | 13:03 | 17.3856 | -0.091362 | 0.57283
|  | 13:03 | 17.3867 | -0.063635 | 0.57283
|  | 13:03 | 17.3878 | -0.035909 | 0.57282
|  | 13:03 | 17.3889 | -0.010399 | 0.57282
|  | 13:03 | 17.39 | 0.008462 | 0.57282
|  | 13:03 | 17.3911 | 0.027323 | 0.57282
|  | 13:03 | 17.3922 | 0.034398 | 0.57281
|  | 13:03 | 17.3933 | 0.037546 | 0.57281
|  | 13:03 | 17.3944 | 0.043552 | 0.57281
|  | 13:03 | 17.3956 | 0.058133 | 0.57281
|  | 13:03 | 17.3967 | 0.072714 | 0.57281
|  | 13:03 | 17.3978 | 0.058027 | 0.5728
|  | 13:03 | 17.3989 | 0.033585 | 0.5728
|  | 13:03 | 17.4 | 0.0091424 | 0.5728
|  | 13:03 | 17.4011 | -0.0069915 | 0.5728
|  | 13:04 | 17.4022 | -0.014817 | 0.57279
|  | 13:04 | 17.4033 | -0.013008 | 0.57279
|  | 13:04 | 17.4044 | -0.0079873 | 0.57279
|  | 13:04 | 17.4056 | -0.0032145 | 0.57279
|  | 13:04 | 17.4067 | 0.00081442 | 0.57278
|  | 13:04 | 17.4078 | 0.0048433 | 0.57278
|  | 13:04 | 17.4089 | -0.011699 | 0.57278
|  | 13:04 | 17.41 | -0.035099 | 0.57278
|  | 13:04 | 17.4111 | -0.062149 | 0.57278
|  | 13:04 | 17.4122 | -0.10015 | 0.57277
|  | 13:04 | 17.4133 | -0.13814 | 0.57277
|  | 13:04 | 17.4144 | -0.15922 | 0.57277
|  | 13:04 | 17.4156 | -0.17466 | 0.57277
|  | 13:04 | 17.4167 | -0.18651 | 0.57276
|  | 13:04 | 17.4178 | -0.18759 | 0.57276
|  | 13:05 | 17.4189 | -0.18868 | 0.57276
|  | 13:05 | 17.42 | -0.16432 | 0.57276
|  | 13:05 | 17.4211 | -0.13147 | 0.57275
|  | 13:05 | 17.4222 | -0.097254 | 0.57275
|  | 13:05 | 17.4233 | -0.058911 | 0.57275
|  | 13:05 | 17.4244 | -0.020569 | 0.57275
|  | 13:05 | 17.4256 | 0.017096 | 0.57275
|  | 13:05 | 17.4267 | 0.054534 | 0.57274
|  | 13:05 | 17.4278 | 0.085579 | 0.57274
|  | 13:05 | 17.4289 | 0.097447 | 0.57274
|  | 13:05 | 17.43 | 0.10931 | 0.57274
|  | 13:05 | 17.4311 | 0.11074 | 0.57273
|  | 13:05 | 17.4322 | 0.10868 | 0.57273
|  | 13:05 | 17.4333 | 0.10522 | 0.57273
|  | 13:05 | 17.4344 | 0.097578 | 0.57273
|  | 13:06 | 17.4356 | 0.089932 | 0.57272
|  | 13:06 | 17.4367 | 0.073569 | 0.57272
|  | 13:06 | 17.4378 | 0.048491 | 0.57272
|  | 13:06 | 17.4389 | 0.023412 | 0.57272
|  | 13:06 | 17.44 | 0.0095454 | 0.57272
|  | 13:06 | 17.4411 | -0.0043213 | 0.57271
|  | 13:06 | 17.4422 | -0.0022857 | 0.57271
|  | 13:06 | 17.4433 | 0.015652 | 0.57271
|  | 13:06 | 17.4444 | 0.03359 | 0.57271
|  | 13:06 | 17.4456 | 0.10038 | 0.5727
|  | 13:06 | 17.4467 | 0.16717 | 0.5727
|  | 13:06 | 17.4478 | 0.23184 | 0.5727
|  | 13:06 | 17.4489 | 0.29437 | 0.5727
|  | 13:06 | 17.45 | 0.35691 | 0.57269
|  | 13:06 | 17.4511 | 0.38203 | 0.57269
|  | 13:07 | 17.4522 | 0.40715 | 0.57269
|  | 13:07 | 17.4533 | 0.43669 | 0.57269
|  | 13:07 | 17.4544 | 0.47067 | 0.57269
|  | 13:07 | 17.4556 | 0.50464 | 0.57268
|  | 13:07 | 17.4567 | 0.51512 | 0.57268
|  | 13:07 | 17.4578 | 0.52559 | 0.57268
|  | 13:07 | 17.4589 | 0.54013 | 0.57268
|  | 13:07 | 17.46 | 0.55874 | 0.57267
|  | 13:07 | 17.4611 | 0.57735 | 0.57267
|  | 13:07 | 17.4622 | 0.57414 | 0.57267
|  | 13:07 | 17.4633 | 0.57092 | 0.57267
|  | 13:07 | 17.4644 | 0.57038 | 0.57266
|  | 13:07 | 17.4656 | 0.57251 | 0.57266
|  | 13:07 | 17.4667 | 0.57464 | 0.57266
|  | 13:07 | 17.4678 | 0.57446 | 0.57266
|  | 13:08 | 17.4689 | 0.57428 | 0.57266
|  | 13:08 | 17.47 | 0.56794 | 0.57265
|  | 13:08 | 17.4711 | 0.55544 | 0.57265
|  | 13:08 | 17.4722 | 0.54294 | 0.57265
|  | 13:08 | 17.4733 | 0.53362 | 0.57265
|  | 13:08 | 17.4744 | 0.52431 | 0.57264
|  | 13:08 | 17.4756 | 0.51346 | 0.57264
|  | 13:08 | 17.4767 | 0.50109 | 0.57264
|  | 13:08 | 17.4778 | 0.48871 | 0.57264
|  | 13:08 | 17.4789 | 0.46532 | 0.57263
|  | 13:08 | 17.48 | 0.44193 | 0.57263
|  | 13:08 | 17.4811 | 0.41736 | 0.57263
|  | 13:08 | 17.4822 | 0.39241 | 0.57263
|  | 13:08 | 17.4833 | 0.36745 | 0.57262
|  | 13:08 | 17.4844 | 0.32955 | 0.57262
|  | 13:09 | 17.4856 | 0.29165 | 0.57262
|  | 13:09 | 17.4867 | 0.25312 | 0.57262
|  | 13:09 | 17.4878 | 0.21396 | 0.57262
|  | 13:09 | 17.4889 | 0.1748 | 0.57261
|  | 13:09 | 17.49 | 0.11481 | 0.57261
|  | 13:09 | 17.4911 | 0.054818 | 0.57261
|  | 13:09 | 17.4922 | -0.0065868 | 0.57261
|  | 13:09 | 17.4933 | -0.068462 | 0.5726
|  | 13:09 | 17.4944 | -0.13034 | 0.5726
|  | 13:09 | 17.4956 | -0.17611 | 0.5726
|  | 13:09 | 17.4967 | -0.22189 | 0.5726
|  | 13:09 | 17.4978 | -0.26715 | 0.57259
|  | 13:09 | 17.4989 | -0.3119 | 0.57259
|  | 13:09 | 17.5 | -0.35665 | 0.57259
|  | 13:09 | 17.5011 | -0.39577 | 0.57259
|  | 13:10 | 17.5022 | -0.43489 | 0.57259
|  | 13:10 | 17.5033 | -0.45765 | 0.57258
|  | 13:10 | 17.5044 | -0.46406 | 0.57258
|  | 13:10 | 17.5056 | -0.47047 | 0.57258
|  | 13:10 | 17.5067 | -0.45239 | 0.57258
|  | 13:10 | 17.5078 | -0.4343 | 0.57257
|  | 13:10 | 17.5089 | -0.42879 | 0.57257
|  | 13:10 | 17.51 | -0.43588 | 0.57257
|  | 13:10 | 17.5111 | -0.44296 | 0.57257
|  | 13:10 | 17.5122 | -0.44646 | 0.57256
|  | 13:10 | 17.5133 | -0.44997 | 0.57256
|  | 13:10 | 17.5144 | -0.44712 | 0.57256
|  | 13:10 | 17.5156 | -0.43794 | 0.57256
|  | 13:10 | 17.5167 | -0.42875 | 0.57256
|  | 13:10 | 17.5178 | -0.42518 | 0.57255
|  | 13:11 | 17.5189 | -0.42161 | 0.57255
|  | 13:11 | 17.52 | -0.42556 | 0.57255
|  | 13:11 | 17.5211 | -0.43704 | 0.57255
|  | 13:11 | 17.5222 | -0.44852 | 0.57254
|  | 13:11 | 17.5233 | -0.44164 | 0.57254
|  | 13:11 | 17.5244 | -0.43475 | 0.57254
|  | 13:11 | 17.5256 | -0.42925 | 0.57254
|  | 13:11 | 17.5267 | -0.42513 | 0.57253
|  | 13:11 | 17.5278 | -0.421 | 0.57253
|  | 13:11 | 17.5289 | -0.40086 | 0.57253
|  | 13:11 | 17.53 | -0.38072 | 0.57253
|  | 13:11 | 17.5311 | -0.36457 | 0.57253
|  | 13:11 | 17.5322 | -0.35242 | 0.57252
|  | 13:11 | 17.5333 | -0.34187 | 0.57252
|  | 13:11 | 17.5344 | -0.33616 | 0.57252
|  | 13:12 | 17.5356 | -0.33044 | 0.57252
|  | 13:12 | 17.5367 | -0.31632 | 0.57251
|  | 13:12 | 17.5378 | -0.29381 | 0.57251
|  | 13:12 | 17.5389 | -0.2713 | 0.57251
|  | 13:12 | 17.54 | -0.25262 | 0.57251
|  | 13:12 | 17.5411 | -0.23394 | 0.5725
|  | 13:12 | 17.5422 | -0.21066 | 0.5725
|  | 13:12 | 17.5433 | -0.18278 | 0.5725
|  | 13:12 | 17.5444 | -0.1549 | 0.5725
|  | 13:12 | 17.5456 | -0.1598 | 0.5725
|  | 13:12 | 17.5467 | -0.1647 | 0.57249
|  | 13:12 | 17.5478 | -0.16862 | 0.57249
|  | 13:12 | 17.5489 | -0.17156 | 0.57249
|  | 13:12 | 17.55 | -0.17451 | 0.57249
|  | 13:12 | 17.5511 | -0.16854 | 0.57248
|  | 13:13 | 17.5522 | -0.16258 | 0.57248
|  | 13:13 | 17.5533 | -0.16124 | 0.57248
|  | 13:13 | 17.5544 | -0.16454 | 0.57248
|  | 13:13 | 17.5556 | -0.16783 | 0.57247
|  | 13:13 | 17.5567 | -0.15843 | 0.57247
|  | 13:13 | 17.5578 | -0.14903 | 0.57247
|  | 13:13 | 17.5589 | -0.12965 | 0.57247
|  | 13:13 | 17.56 | -0.10029 | 0.57247
|  | 13:13 | 17.5611 | -0.070943 | 0.57246
|  | 13:13 | 17.5622 | -0.066805 | 0.57246
|  | 13:13 | 17.5633 | -0.062667 | 0.57246
|  | 13:13 | 17.5644 | -0.054492 | 0.57246
|  | 13:13 | 17.5656 | -0.042281 | 0.57245
|  | 13:13 | 17.5667 | -0.030069 | 0.57245
|  | 13:13 | 17.5678 | -0.017858 | 0.57245
|  | 13:14 | 17.5689 | 0.0074794 | 0.57245
|  | 13:14 | 17.57 | 0.030449 | 0.57244
|  | 13:14 | 17.5711 | 0.046317 | 0.57244
|  | 13:14 | 17.5722 | 0.062185 | 0.57244
|  | 13:14 | 17.5733 | 0.082672 | 0.57244
|  | 13:14 | 17.5744 | 0.10316 | 0.57244
|  | 13:14 | 17.5756 | 0.12318 | 0.57243
|  | 13:14 | 17.5767 | 0.14273 | 0.57243
|  | 13:14 | 17.5778 | 0.16229 | 0.57243
|  | 13:14 | 17.5789 | 0.17597 | 0.57243
|  | 13:14 | 17.58 | 0.18965 | 0.57242
|  | 13:14 | 17.5811 | 0.21106 | 0.57242
|  | 13:14 | 17.5822 | 0.24018 | 0.57242
|  | 13:14 | 17.5833 | 0.2693 | 0.57242
|  | 13:14 | 17.5844 | 0.28985 | 0.57241
|  | 13:15 | 17.5856 | 0.3104 | 0.57241
|  | 13:15 | 17.5867 | 0.32411 | 0.57241
|  | 13:15 | 17.5878 | 0.33098 | 0.57241
|  | 13:15 | 17.5889 | 0.33785 | 0.57241
|  | 13:15 | 17.59 | 0.3406 | 0.5724
|  | 13:15 | 17.5911 | 0.34335 | 0.5724
|  | 13:15 | 17.5922 | 0.34433 | 0.5724
|  | 13:15 | 17.5933 | 0.34356 | 0.5724
|  | 13:15 | 17.5944 | 0.34278 | 0.57239
|  | 13:15 | 17.5956 | 0.3594 | 0.57239
|  | 13:15 | 17.5967 | 0.37602 | 0.57239
|  | 13:15 | 17.5978 | 0.39263 | 0.57239
|  | 13:15 | 17.5989 | 0.40925 | 0.57238
|  | 13:15 | 17.6 | 0.42587 | 0.57238
|  | 13:15 | 17.6011 | 0.4182 | 0.57238
|  | 13:16 | 17.6022 | 0.41053 | 0.57238
|  | 13:16 | 17.6033 | 0.39842 | 0.57237
|  | 13:16 | 17.6044 | 0.38187 | 0.57237
|  | 13:16 | 17.6056 | 0.36532 | 0.57237
|  | 13:16 | 17.6067 | 0.33087 | 0.57237
|  | 13:16 | 17.6078 | 0.29642 | 0.57237
|  | 13:16 | 17.6089 | 0.28083 | 0.57236
|  | 13:16 | 17.61 | 0.28412 | 0.57236
|  | 13:16 | 17.6111 | 0.2874 | 0.57236
|  | 13:16 | 17.6122 | 0.2724 | 0.57236
|  | 13:16 | 17.6133 | 0.2574 | 0.57235
|  | 13:16 | 17.6144 | 0.2361 | 0.57235
|  | 13:16 | 17.6156 | 0.2085 | 0.57235
|  | 13:16 | 17.6167 | 0.18089 | 0.57235
|  | 13:16 | 17.6178 | 0.14929 | 0.57234
|  | 13:17 | 17.6189 | 0.11769 | 0.57234
|  | 13:17 | 17.62 | 0.10424 | 0.57234
|  | 13:17 | 17.6211 | 0.096831 | 0.57234
|  | 13:17 | 17.6222 | 0.089426 | 0.57234
|  | 13:17 | 17.6233 | 0.072852 | 0.57233
|  | 13:17 | 17.6244 | 0.056277 | 0.57233
|  | 13:17 | 17.6256 | 0.041294 | 0.57233
|  | 13:17 | 17.6267 | 0.027902 | 0.57233
|  | 13:17 | 17.6278 | 0.01451 | 0.57232
|  | 13:17 | 17.6289 | -0.0091688 | 0.57232
|  | 13:17 | 17.63 | -0.032848 | 0.57232
|  | 13:17 | 17.6311 | -0.066966 | 0.57232
|  | 13:17 | 17.6322 | -0.11152 | 0.57231
|  | 13:17 | 17.6333 | -0.15608 | 0.57231
|  | 13:17 | 17.6344 | -0.17782 | 0.57231
|  | 13:18 | 17.6356 | -0.19956 | 0.57231
|  | 13:18 | 17.6367 | -0.21505 | 0.57231
|  | 13:18 | 17.6378 | -0.2243 | 0.5723
|  | 13:18 | 17.6389 | -0.23485 | 0.5723
|  | 13:18 | 17.64 | -0.24933 | 0.5723
|  | 13:18 | 17.6411 | -0.26381 | 0.5723
|  | 13:18 | 17.6422 | -0.28585 | 0.57229
|  | 13:18 | 17.6433 | -0.31041 | 0.57229
|  | 13:18 | 17.6444 | -0.33498 | 0.57229
|  | 13:18 | 17.6456 | -0.35433 | 0.57229
|  | 13:18 | 17.6467 | -0.37369 | 0.57228
|  | 13:18 | 17.6478 | -0.38334 | 0.57228
|  | 13:18 | 17.6489 | -0.38329 | 0.57228
|  | 13:18 | 17.65 | -0.38325 | 0.57228
|  | 13:18 | 17.6511 | -0.37177 | 0.57228
|  | 13:19 | 17.6522 | -0.36028 | 0.57227
|  | 13:19 | 17.6533 | -0.34955 | 0.57227
|  | 13:19 | 17.6544 | -0.33956 | 0.57227
|  | 13:19 | 17.6556 | -0.32957 | 0.57227
|  | 13:19 | 17.6567 | -0.32282 | 0.57226
|  | 13:19 | 17.6578 | -0.31608 | 0.57226
|  | 13:19 | 17.6589 | -0.30933 | 0.57226
|  | 13:19 | 17.66 | -0.30258 | 0.57226
|  | 13:19 | 17.6611 | -0.2977 | 0.57225
|  | 13:19 | 17.6622 | -0.29843 | 0.57225
|  | 13:19 | 17.6633 | -0.29916 | 0.57225
|  | 13:19 | 17.6644 | -0.3059 | 0.57225
|  | 13:19 | 17.6656 | -0.31865 | 0.57225
|  | 13:19 | 17.6667 | -0.33141 | 0.57224
|  | 13:19 | 17.6678 | -0.34928 | 0.57224
|  | 13:20 | 17.6689 | -0.36715 | 0.57224
|  | 13:20 | 17.67 | -0.36743 | 0.57224
|  | 13:20 | 17.6711 | -0.35014 | 0.57223
|  | 13:20 | 17.6722 | -0.33284 | 0.57223
|  | 13:20 | 17.6733 | -0.32614 | 0.57223
|  | 13:20 | 17.6744 | -0.31945 | 0.57223
|  | 13:20 | 17.6756 | -0.32347 | 0.57222
|  | 13:20 | 17.6767 | -0.33105 | 0.57222
|  | 13:20 | 17.6778 | -0.33863 | 0.57222
|  | 13:20 | 17.6789 | -0.34742 | 0.57222
|  | 13:20 | 17.68 | -0.35621 | 0.57222
|  | 13:20 | 17.6811 | -0.35525 | 0.57221
|  | 13:20 | 17.6822 | -0.34453 | 0.57221
|  | 13:20 | 17.6833 | -0.33382 | 0.57221
|  | 13:20 | 17.6844 | -0.32408 | 0.57221
|  | 13:21 | 17.6856 | -0.31435 | 0.5722
|  | 13:21 | 17.6867 | -0.29629 | 0.5722
|  | 13:21 | 17.6878 | -0.2699 | 0.5722
|  | 13:21 | 17.6889 | -0.24351 | 0.5722
|  | 13:21 | 17.69 | -0.22981 | 0.57219
|  | 13:21 | 17.6911 | -0.21611 | 0.57219
|  | 13:21 | 17.6922 | -0.19988 | 0.57219
|  | 13:21 | 17.6933 | -0.18112 | 0.57219
|  | 13:21 | 17.6944 | -0.16235 | 0.57219
|  | 13:21 | 17.6956 | -0.16142 | 0.57218
|  | 13:21 | 17.6967 | -0.16049 | 0.57218
|  | 13:21 | 17.6978 | -0.15389 | 0.57218
|  | 13:21 | 17.6989 | -0.14164 | 0.57218
|  | 13:21 | 17.7 | -0.12939 | 0.57217
|  | 13:21 | 17.7011 | -0.12526 | 0.57217
|  | 13:22 | 17.7022 | -0.12113 | 0.57217
|  | 13:22 | 17.7033 | -0.12313 | 0.57217
|  | 13:22 | 17.7044 | -0.13125 | 0.57216
|  | 13:22 | 17.7056 | -0.13938 | 0.57216
|  | 13:22 | 17.7067 | -0.13197 | 0.57216
|  | 13:22 | 17.7078 | -0.12456 | 0.57216
|  | 13:22 | 17.7089 | -0.11274 | 0.57216
|  | 13:22 | 17.71 | -0.096521 | 0.57215
|  | 13:22 | 17.7111 | -0.080302 | 0.57215
|  | 13:22 | 17.7122 | -0.054155 | 0.57215
|  | 13:22 | 17.7133 | -0.028008 | 0.57215
|  | 13:22 | 17.7144 | -0.0045076 | 0.57214
|  | 13:22 | 17.7156 | 0.016347 | 0.57214
|  | 13:22 | 17.7167 | 0.037201 | 0.57214
|  | 13:22 | 17.7178 | 0.038561 | 0.57214
|  | 13:23 | 17.7189 | 0.039921 | 0.57213
|  | 13:23 | 17.72 | 0.04462 | 0.57213
|  | 13:23 | 17.7211 | 0.052657 | 0.57213
|  | 13:23 | 17.7222 | 0.060695 | 0.57213
|  | 13:23 | 17.7233 | 0.062016 | 0.57212
|  | 13:23 | 17.7244 | 0.063337 | 0.57212
|  | 13:23 | 17.7256 | 0.059152 | 0.57212
|  | 13:23 | 17.7267 | 0.049461 | 0.57212
|  | 13:23 | 17.7278 | 0.039771 | 0.57212
|  | 13:23 | 17.7289 | 0.03008 | 0.57211
|  | 13:23 | 17.73 | 0.02039 | 0.57211
|  | 13:23 | 17.7311 | 0.012533 | 0.57211
|  | 13:23 | 17.7322 | 0.00651 | 0.57211
|  | 13:23 | 17.7333 | 0.00048686 | 0.5721
|  | 13:23 | 17.7344 | -0.0055363 | 0.5721
|  | 13:24 | 17.7356 | -0.028667 | 0.5721
|  | 13:24 | 17.7367 | -0.055754 | 0.5721
|  | 13:24 | 17.7378 | -0.094714 | 0.57209
|  | 13:24 | 17.7389 | -0.13367 | 0.57209
|  | 13:24 | 17.74 | -0.1564 | 0.57209
|  | 13:24 | 17.7411 | -0.17912 | 0.57209
|  | 13:24 | 17.7422 | -0.20465 | 0.57209
|  | 13:24 | 17.7433 | -0.23296 | 0.57208
|  | 13:24 | 17.7444 | -0.26128 | 0.57208
|  | 13:24 | 17.7456 | -0.28713 | 0.57208
|  | 13:24 | 17.7467 | -0.31299 | 0.57208
|  | 13:24 | 17.7478 | -0.3269 | 0.57207
|  | 13:24 | 17.7489 | -0.32887 | 0.57207
|  | 13:24 | 17.75 | -0.33084 | 0.57207
|  | 13:24 | 17.7511 | -0.34417 | 0.57207
|  | 13:25 | 17.7522 | -0.35749 | 0.57206
|  | 13:25 | 17.7533 | -0.36829 | 0.57206
|  | 13:25 | 17.7544 | -0.37657 | 0.57206
|  | 13:25 | 17.7556 | -0.38484 | 0.57206
|  | 13:25 | 17.7567 | -0.39763 | 0.57206
|  | 13:25 | 17.7578 | -0.41043 | 0.57205
|  | 13:25 | 17.7589 | -0.42784 | 0.57205
|  | 13:25 | 17.76 | -0.44987 | 0.57205
|  | 13:25 | 17.7611 | -0.4719 | 0.57205
|  | 13:25 | 17.7622 | -0.49075 | 0.57204
|  | 13:25 | 17.7633 | -0.50959 | 0.57204
|  | 13:25 | 17.7644 | -0.5272 | 0.57204
|  | 13:25 | 17.7656 | -0.54355 | 0.57204
|  | 13:25 | 17.7667 | -0.5599 | 0.57203
|  | 13:25 | 17.7678 | -0.58263 | 0.57203
|  | 13:26 | 17.7689 | -0.60537 | 0.57203
|  | 13:26 | 17.77 | -0.62365 | 0.57203
|  | 13:26 | 17.7711 | -0.63747 | 0.57203
|  | 13:26 | 17.7722 | -0.65129 | 0.57202
|  | 13:26 | 17.7733 | -0.65879 | 0.57202
|  | 13:26 | 17.7744 | -0.66629 | 0.57202
|  | 13:26 | 17.7756 | -0.67986 | 0.57202
|  | 13:26 | 17.7767 | -0.6995 | 0.57201
|  | 13:26 | 17.7778 | -0.71913 | 0.57201
|  | 13:26 | 17.7789 | -0.73168 | 0.57201
|  | 13:26 | 17.78 | -0.74423 | 0.57201
|  | 13:26 | 17.7811 | -0.7505 | 0.572
|  | 13:26 | 17.7822 | -0.75049 | 0.572
|  | 13:26 | 17.7833 | -0.75048 | 0.572
|  | 13:26 | 17.7844 | -0.73916 | 0.572
|  | 13:27 | 17.7856 | -0.72783 | 0.572
|  | 13:27 | 17.7867 | -0.70987 | 0.57199
|  | 13:27 | 17.7878 | -0.68526 | 0.57199
|  | 13:27 | 17.7889 | -0.66066 | 0.57199
|  | 13:27 | 17.79 | -0.6495 | 0.57199
|  | 13:27 | 17.7911 | -0.63834 | 0.57198
|  | 13:27 | 17.7922 | -0.61665 | 0.57198
|  | 13:27 | 17.7933 | -0.58443 | 0.57198
|  | 13:27 | 17.7944 | -0.55221 | 0.57198
|  | 13:27 | 17.7956 | -0.51541 | 0.57197
|  | 13:27 | 17.7967 | -0.47861 | 0.57197
|  | 13:27 | 17.7978 | -0.44523 | 0.57197
|  | 13:27 | 17.7989 | -0.41524 | 0.57197
|  | 13:27 | 17.8 | -0.38526 | 0.57197
|  | 13:27 | 17.8011 | -0.37899 | 0.57196
|  | 13:28 | 17.8022 | -0.37271 | 0.57196
|  | 13:28 | 17.8033 | -0.37159 | 0.57196
|  | 13:28 | 17.8044 | -0.37563 | 0.57196
|  | 13:28 | 17.8056 | -0.37966 | 0.57195
|  | 13:28 | 17.8067 | -0.36377 | 0.57195
|  | 13:28 | 17.8078 | -0.34788 | 0.57195
|  | 13:28 | 17.8089 | -0.32774 | 0.57195
|  | 13:28 | 17.81 | -0.30335 | 0.57194
|  | 13:28 | 17.8111 | -0.27896 | 0.57194
|  | 13:28 | 17.8122 | -0.25074 | 0.57194
|  | 13:28 | 17.8133 | -0.22252 | 0.57194
|  | 13:28 | 17.8144 | -0.19509 | 0.57194
|  | 13:28 | 17.8156 | -0.16792 | 0.57193
|  | 13:28 | 17.8167 | -0.14272 | 0.57193
|  | 13:28 | 17.8178 | -0.12345 | 0.57193
|  | 13:29 | 17.8189 | -0.10417 | 0.57193
|  | 13:29 | 17.82 | -0.087397 | 0.57192
|  | 13:29 | 17.8211 | -0.07313 | 0.57192
|  | 13:29 | 17.8222 | -0.058863 | 0.57192
|  | 13:29 | 17.8233 | -0.061269 | 0.57192
|  | 13:29 | 17.8244 | -0.063676 | 0.57191
|  | 13:29 | 17.8256 | -0.065522 | 0.57191
|  | 13:29 | 17.8267 | -0.066808 | 0.57191
|  | 13:29 | 17.8278 | -0.068094 | 0.57191
|  | 13:29 | 17.8289 | -0.075492 | 0.57191
|  | 13:29 | 17.83 | -0.08289 | 0.5719
|  | 13:29 | 17.8311 | -0.09073 | 0.5719
|  | 13:29 | 17.8322 | -0.099014 | 0.5719
|  | 13:29 | 17.8333 | -0.1073 | 0.5719
|  | 13:29 | 17.8344 | -0.089359 | 0.57189
|  | 13:30 | 17.8356 | -0.071421 | 0.57189
|  | 13:30 | 17.8367 | -0.049309 | 0.57189
|  | 13:30 | 17.8378 | -0.023023 | 0.57189
|  | 13:30 | 17.8389 | 0.0032623 | 0.57188
|  | 13:30 | 17.84 | 0.016532 | 0.57188
|  | 13:30 | 17.8411 | 0.029801 | 0.57188
|  | 13:30 | 17.8422 | 0.036497 | 0.57188
|  | 13:30 | 17.8433 | 0.03662 | 0.57187
|  | 13:30 | 17.8444 | 0.036742 | 0.57187
|  | 13:30 | 17.8456 | 0.031934 | 0.57187
|  | 13:30 | 17.8467 | 0.027126 | 0.57187
|  | 13:30 | 17.8478 | 0.038487 | 0.57187
|  | 13:30 | 17.8489 | 0.06602 | 0.57186
|  | 13:30 | 17.85 | 0.093552 | 0.57186
|  | 13:30 | 17.8511 | 0.12924 | 0.57186
|  | 13:31 | 17.8522 | 0.16492 | 0.57186
|  | 13:31 | 17.8533 | 0.19135 | 0.57185
|  | 13:31 | 17.8544 | 0.20853 | 0.57185
|  | 13:31 | 17.8556 | 0.2257 | 0.57185
|  | 13:31 | 17.8567 | 0.2251 | 0.57185
|  | 13:31 | 17.8578 | 0.22449 | 0.57184
|  | 13:31 | 17.8589 | 0.21902 | 0.57184
|  | 13:31 | 17.86 | 0.2087 | 0.57184
|  | 13:31 | 17.8611 | 0.19838 | 0.57184
|  | 13:31 | 17.8622 | 0.17104 | 0.57184
|  | 13:31 | 17.8633 | 0.14371 | 0.57183
|  | 13:31 | 17.8644 | 0.12041 | 0.57183
|  | 13:31 | 17.8656 | 0.10116 | 0.57183
|  | 13:31 | 17.8667 | 0.081902 | 0.57183
|  | 13:31 | 17.8678 | 0.099815 | 0.57182
|  | 13:32 | 17.8689 | 0.11773 | 0.57182
|  | 13:32 | 17.87 | 0.13342 | 0.57182
|  | 13:32 | 17.8711 | 0.14689 | 0.57182
|  | 13:32 | 17.8722 | 0.16036 | 0.57181
|  | 13:32 | 17.8733 | 0.17384 | 0.57181
|  | 13:32 | 17.8744 | 0.18731 | 0.57181
|  | 13:32 | 17.8756 | 0.20476 | 0.57181
|  | 13:32 | 17.8767 | 0.22619 | 0.57181
|  | 13:32 | 17.8778 | 0.24763 | 0.5718
|  | 13:32 | 17.8789 | 0.26643 | 0.5718
|  | 13:32 | 17.88 | 0.28523 | 0.5718
|  | 13:32 | 17.8811 | 0.29984 | 0.5718
|  | 13:32 | 17.8822 | 0.31025 | 0.57179
|  | 13:32 | 17.8833 | 0.32066 | 0.57179
|  | 13:32 | 17.8844 | 0.33434 | 0.57179
|  | 13:33 | 17.8856 | 0.34802 | 0.57179
|  | 13:33 | 17.8867 | 0.36502 | 0.57178
|  | 13:33 | 17.8878 | 0.38533 | 0.57178
|  | 13:33 | 17.8889 | 0.40565 | 0.57178
|  | 13:33 | 17.89 | 0.42159 | 0.57178
|  | 13:33 | 17.8911 | 0.43753 | 0.57178
|  | 13:33 | 17.8922 | 0.45058 | 0.57177
|  | 13:33 | 17.8933 | 0.46075 | 0.57177
|  | 13:33 | 17.8944 | 0.47091 | 0.57177
|  | 13:33 | 17.8956 | 0.47039 | 0.57177
|  | 13:33 | 17.8967 | 0.46987 | 0.57176
|  | 13:33 | 17.8978 | 0.46317 | 0.57176
|  | 13:33 | 17.8989 | 0.45441 | 0.57176
|  | 13:33 | 17.9 | 0.44565 | 0.57176
|  | 13:33 | 17.9011 | 0.42328 | 0.57175
|  | 13:34 | 17.9022 | 0.4009 | 0.57175
|  | 13:34 | 17.9033 | 0.38572 | 0.57175
|  | 13:34 | 17.9044 | 0.39211 | 0.57175
|  | 13:34 | 17.9056 | 0.3985 | 0.57175
|  | 13:34 | 17.9067 | 0.4237 | 0.57174
|  | 13:34 | 17.9078 | 0.4489 | 0.57174
|  | 13:34 | 17.9089 | 0.46088 | 0.57174
|  | 13:34 | 17.91 | 0.45964 | 0.57174
|  | 13:34 | 17.9111 | 0.45841 | 0.57173
|  | 13:34 | 17.9122 | 0.4475 | 0.57173
|  | 13:34 | 17.9133 | 0.43659 | 0.57173
|  | 13:34 | 17.9144 | 0.42325 | 0.57173
|  | 13:34 | 17.9156 | 0.40749 | 0.57172
|  | 13:34 | 17.9167 | 0.39172 | 0.57172
|  | 13:34 | 17.9178 | 0.40531 | 0.57172
|  | 13:35 | 17.9189 | 0.4189 | 0.57172
|  | 13:35 | 17.92 | 0.43151 | 0.57172
|  | 13:35 | 17.9211 | 0.44314 | 0.57171
|  | 13:35 | 17.9222 | 0.45477 | 0.57171
|  | 13:35 | 17.9233 | 0.4521 | 0.57171
|  | 13:35 | 17.9244 | 0.44943 | 0.57171
|  | 13:35 | 17.9256 | 0.43991 | 0.5717
|  | 13:35 | 17.9267 | 0.42354 | 0.5717
|  | 13:35 | 17.9278 | 0.40717 | 0.5717
|  | 13:35 | 17.9289 | 0.40518 | 0.5717
|  | 13:35 | 17.93 | 0.40319 | 0.57169
|  | 13:35 | 17.9311 | 0.41374 | 0.57169
|  | 13:35 | 17.9322 | 0.43682 | 0.57169
|  | 13:35 | 17.9333 | 0.45991 | 0.57169
|  | 13:35 | 17.9344 | 0.48429 | 0.57169
|  | 13:36 | 17.9356 | 0.50867 | 0.57168
|  | 13:36 | 17.9367 | 0.52763 | 0.57168
|  | 13:36 | 17.9378 | 0.54478 | 0.57168
|  | 13:36 | 17.9389 | 0.56194 | 0.57168
|  | 13:36 | 17.94 | 0.57207 | 0.57167
|  | 13:36 | 17.9411 | 0.58221 | 0.57167
|  | 13:36 | 17.9422 | 0.58718 | 0.57167
|  | 13:36 | 17.9433 | 0.58698 | 0.57167
|  | 13:36 | 17.9444 | 0.58678 | 0.57166
|  | 13:36 | 17.9456 | 0.60128 | 0.57166
|  | 13:36 | 17.9467 | 0.61578 | 0.57166
|  | 13:36 | 17.9478 | 0.62143 | 0.57166
|  | 13:36 | 17.9489 | 0.61825 | 0.57166
|  | 13:36 | 17.95 | 0.61506 | 0.57165
|  | 13:36 | 17.9511 | 0.62239 | 0.57165
|  | 13:37 | 17.9522 | 0.62971 | 0.57165
|  | 13:37 | 17.9533 | 0.63355 | 0.57165
|  | 13:37 | 17.9544 | 0.6339 | 0.57164
|  | 13:37 | 17.9556 | 0.63907 | 0.57164
|  | 13:37 | 17.9567 | 0.65868 | 0.57164
|  | 13:37 | 17.9578 | 0.6783 | 0.57164
|  | 13:37 | 17.9589 | 0.69792 | 0.57163
|  | 13:37 | 17.96 | 0.71754 | 0.57163
|  | 13:37 | 17.9611 | 0.73715 | 0.57163
|  | 13:37 | 17.9622 | 0.75945 | 0.57163
|  | 13:37 | 17.9633 | 0.78175 | 0.57162
|  | 13:37 | 17.9644 | 0.79371 | 0.57162
|  | 13:37 | 17.9656 | 0.79532 | 0.57162
|  | 13:37 | 17.9667 | 0.79693 | 0.57162
|  | 13:37 | 17.9678 | 0.81251 | 0.57162
|  | 13:38 | 17.9689 | 0.82809 | 0.57161
|  | 13:38 | 17.97 | 0.83863 | 0.57161
|  | 13:38 | 17.9711 | 0.84413 | 0.57161
|  | 13:38 | 17.9722 | 0.84963 | 0.57161
|  | 13:38 | 17.9733 | 0.82497 | 0.5716
|  | 13:38 | 17.9744 | 0.8003 | 0.5716
|  | 13:38 | 17.9756 | 0.77953 | 0.5716
|  | 13:38 | 17.9767 | 0.76265 | 0.5716
|  | 13:38 | 17.9778 | 0.74578 | 0.57159
|  | 13:38 | 17.9789 | 0.7289 | 0.57159
|  | 13:38 | 17.98 | 0.71203 | 0.57159
|  | 13:38 | 17.9811 | 0.69599 | 0.57159
|  | 13:38 | 17.9822 | 0.68079 | 0.57159
|  | 13:38 | 17.9833 | 0.66559 | 0.57158
|  | 13:38 | 17.9844 | 0.65039 | 0.57158
|  | 13:39 | 17.9856 | 0.63519 | 0.57158
|  | 13:39 | 17.9867 | 0.6287 | 0.57158
|  | 13:39 | 17.9878 | 0.62511 | 0.57157
|  | 13:39 | 17.9889 | 0.62152 | 0.57157
|  | 13:39 | 17.99 | 0.60905 | 0.57157
|  | 13:39 | 17.9911 | 0.59658 | 0.57157
|  | 13:39 | 17.9922 | 0.59451 | 0.57156
|  | 13:39 | 17.9933 | 0.60285 | 0.57156
|  | 13:39 | 17.9944 | 0.61119 | 0.57156
|  | 13:39 | 17.9956 | 0.62747 | 0.57156
|  | 13:39 | 17.9967 | 0.64374 | 0.57156
|  | 13:39 | 17.9978 | 0.64699 | 0.57155
|  | 13:39 | 17.9989 | 0.6372 | 0.57155
|  | 13:39 | 18 | 0.62494 | 0.57155
|  | 13:39 | 18.0011 | 0.60529 | 0.57155
|  | 13:40 | 18.0022 | 0.58564 | 0.57154
|  | 13:40 | 18.0033 | 0.56408 | 0.57154
|  | 13:40 | 18.0044 | 0.54061 | 0.57154
|  | 13:40 | 18.0056 | 0.51713 | 0.57154
|  | 13:40 | 18.0067 | 0.50205 | 0.57153
|  | 13:40 | 18.0078 | 0.48696 | 0.57153
|  | 13:40 | 18.0089 | 0.46771 | 0.57153
|  | 13:40 | 18.01 | 0.4443 | 0.57153
|  | 13:40 | 18.0111 | 0.4209 | 0.57153
|  | 13:40 | 18.0122 | 0.38558 | 0.57152
|  | 13:40 | 18.0133 | 0.35026 | 0.57152
|  | 13:40 | 18.0144 | 0.31233 | 0.57152
|  | 13:40 | 18.0156 | 0.27179 | 0.57152
|  | 13:40 | 18.0167 | 0.23124 | 0.57151
|  | 13:40 | 18.0178 | 0.20065 | 0.57151
|  | 13:41 | 18.0189 | 0.17005 | 0.57151
|  | 13:41 | 18.02 | 0.14077 | 0.57151
|  | 13:41 | 18.0211 | 0.11281 | 0.5715
|  | 13:41 | 18.0222 | 0.084842 | 0.5715
|  | 13:41 | 18.0233 | 0.038603 | 0.5715
|  | 13:41 | 18.0244 | -0.0076366 | 0.5715
|  | 13:41 | 18.0256 | -0.047739 | 0.5715
|  | 13:41 | 18.0267 | -0.081703 | 0.57149
|  | 13:41 | 18.0278 | -0.11567 | 0.57149
|  | 13:41 | 18.0289 | -0.13646 | 0.57149
|  | 13:41 | 18.03 | -0.15725 | 0.57149
|  | 13:41 | 18.0311 | -0.18325 | 0.57148
|  | 13:41 | 18.0322 | -0.21444 | 0.57148
|  | 13:41 | 18.0333 | -0.24563 | 0.57148
|  | 13:41 | 18.0344 | -0.2745 | 0.57148
|  | 13:42 | 18.0356 | -0.30336 | 0.57147
|  | 13:42 | 18.0367 | -0.34175 | 0.57147
|  | 13:42 | 18.0378 | -0.38967 | 0.57147
|  | 13:42 | 18.0389 | -0.42638 | 0.57147
|  | 13:42 | 18.04 | -0.42948 | 0.57147
|  | 13:42 | 18.0411 | -0.43258 | 0.57146
|  | 13:42 | 18.0422 | -0.44921 | 0.57146
|  | 13:42 | 18.0433 | -0.47935 | 0.57146
|  | 13:42 | 18.0444 | -0.5095 | 0.57146
|  | 13:42 | 18.0456 | -0.53188 | 0.57145
|  | 13:42 | 18.0467 | -0.55427 | 0.57145
|  | 13:42 | 18.0478 | -0.57911 | 0.57145
|  | 13:42 | 18.0489 | -0.60641 | 0.57145
|  | 13:42 | 18.05 | -0.63371 | 0.57144
|  | 13:42 | 18.0511 | -0.64927 | 0.57144
|  | 13:43 | 18.0522 | -0.66484 | 0.57144
|  | 13:43 | 18.0533 | -0.6804 | 0.57144
|  | 13:43 | 18.0544 | -0.69596 | 0.57144
|  | 13:43 | 18.0556 | -0.71153 | 0.57143
|  | 13:43 | 18.0567 | -0.72418 | 0.57143
|  | 13:43 | 18.0578 | -0.73684 | 0.57143
|  | 13:43 | 18.0589 | -0.73522 | 0.57143
|  | 13:43 | 18.06 | -0.71932 | 0.57142
|  | 13:43 | 18.0611 | -0.70341 | 0.57142
|  | 13:43 | 18.0622 | -0.67074 | 0.57142
|  | 13:43 | 18.0633 | -0.63806 | 0.57142
|  | 13:43 | 18.0644 | -0.60994 | 0.57141
|  | 13:43 | 18.0656 | -0.58635 | 0.57141
|  | 13:43 | 18.0667 | -0.56277 | 0.57141
|  | 13:43 | 18.0678 | -0.53527 | 0.57141
|  | 13:44 | 18.0689 | -0.50776 | 0.57141
|  | 13:44 | 18.07 | -0.48763 | 0.5714
|  | 13:44 | 18.0711 | -0.48964 | 0.5714
|  | 13:44 | 18.0722 | -0.49165 | 0.5714
|  | 13:44 | 18.0733 | -0.49001 | 0.5714
|  | 13:44 | 18.0744 | -0.48837 | 0.57139
|  | 13:44 | 18.0756 | -0.48899 | 0.57139
|  | 13:44 | 18.0767 | -0.49188 | 0.57139
|  | 13:44 | 18.0778 | -0.49352 | 0.57139
|  | 13:44 | 18.0789 | -0.49142 | 0.57138
|  | 13:44 | 18.08 | -0.48932 | 0.57138
|  | 13:44 | 18.0811 | -0.49175 | 0.57138
|  | 13:44 | 18.0822 | -0.4987 | 0.57138
|  | 13:44 | 18.0833 | -0.50565 | 0.57137
|  | 13:44 | 18.0844 | -0.50288 | 0.57137
|  | 13:45 | 18.0856 | -0.50011 | 0.57137
|  | 13:45 | 18.0867 | -0.48826 | 0.57137
|  | 13:45 | 18.0878 | -0.46731 | 0.57137
|  | 13:45 | 18.0889 | -0.44636 | 0.57136
|  | 13:45 | 18.09 | -0.413 | 0.57136
|  | 13:45 | 18.0911 | -0.37965 | 0.57136
|  | 13:45 | 18.0922 | -0.35026 | 0.57136
|  | 13:45 | 18.0933 | -0.32485 | 0.57135
|  | 13:45 | 18.0944 | -0.29944 | 0.57135
|  | 13:45 | 18.0956 | -0.27642 | 0.57135
|  | 13:45 | 18.0967 | -0.2534 | 0.57135
|  | 13:45 | 18.0978 | -0.236 | 0.57134
|  | 13:45 | 18.0989 | -0.22421 | 0.57134
|  | 13:45 | 18.1 | -0.21242 | 0.57134
|  | 13:45 | 18.1011 | -0.18995 | 0.57134
|  | 13:46 | 18.1022 | -0.16749 | 0.57134
|  | 13:46 | 18.1033 | -0.14283 | 0.57133
|  | 13:46 | 18.1044 | -0.11597 | 0.57133
|  | 13:46 | 18.1056 | -0.089118 | 0.57133
|  | 13:46 | 18.1067 | -0.051508 | 0.57133
|  | 13:46 | 18.1078 | -0.013898 | 0.57132
|  | 13:46 | 18.1089 | 0.024607 | 0.57132
|  | 13:46 | 18.11 | 0.064006 | 0.57132
|  | 13:46 | 18.1111 | 0.1034 | 0.57132
|  | 13:46 | 18.1122 | 0.12872 | 0.57131
|  | 13:46 | 18.1133 | 0.15403 | 0.57131
|  | 13:46 | 18.1144 | 0.16833 | 0.57131
|  | 13:46 | 18.1156 | 0.17161 | 0.57131
|  | 13:46 | 18.1167 | 0.1749 | 0.57131
|  | 13:46 | 18.1178 | 0.19225 | 0.5713
|  | 13:47 | 18.1189 | 0.2096 | 0.5713
|  | 13:47 | 18.12 | 0.23125 | 0.5713
|  | 13:47 | 18.1211 | 0.25433 | 0.5713
|  | 13:47 | 18.1222 | 0.28118 | 0.57129
|  | 13:47 | 18.1233 | 0.3193 | 0.57129
|  | 13:47 | 18.1244 | 0.35742 | 0.57129
|  | 13:47 | 18.1256 | 0.37481 | 0.57129
|  | 13:47 | 18.1267 | 0.37146 | 0.57128
|  | 13:47 | 18.1278 | 0.36812 | 0.57128
|  | 13:47 | 18.1289 | 0.36814 | 0.57128
|  | 13:47 | 18.13 | 0.36817 | 0.57128
|  | 13:47 | 18.1311 | 0.36493 | 0.57128
|  | 13:47 | 18.1322 | 0.35842 | 0.57127
|  | 13:47 | 18.1333 | 0.35192 | 0.57127
|  | 13:47 | 18.1344 | 0.35745 | 0.57127
|  | 13:48 | 18.1356 | 0.36298 | 0.57127
|  | 13:48 | 18.1367 | 0.38439 | 0.57126
|  | 13:48 | 18.1378 | 0.42166 | 0.57126
|  | 13:48 | 18.1389 | 0.45893 | 0.57126
|  | 13:48 | 18.14 | 0.50834 | 0.57126
|  | 13:48 | 18.1411 | 0.55774 | 0.57125
|  | 13:48 | 18.1422 | 0.59714 | 0.57125
|  | 13:48 | 18.1433 | 0.62655 | 0.57125
|  | 13:48 | 18.1444 | 0.65595 | 0.57125
|  | 13:48 | 18.1456 | 0.68535 | 0.57125
|  | 13:48 | 18.1467 | 0.71475 | 0.57124
|  | 13:48 | 18.1478 | 0.7405 | 0.57124
|  | 13:48 | 18.1489 | 0.7626 | 0.57124
|  | 13:48 | 18.15 | 0.7847 | 0.57124
|  | 13:48 | 18.1511 | 0.78996 | 0.57123
|  | 13:49 | 18.1522 | 0.79522 | 0.57123
|  | 13:49 | 18.1533 | 0.80048 | 0.57123
|  | 13:49 | 18.1544 | 0.80574 | 0.57123
|  | 13:49 | 18.1556 | 0.811 | 0.57122
|  | 13:49 | 18.1567 | 0.80302 | 0.57122
|  | 13:49 | 18.1578 | 0.79504 | 0.57122
|  | 13:49 | 18.1589 | 0.78335 | 0.57122
|  | 13:49 | 18.16 | 0.76794 | 0.57122
|  | 13:49 | 18.1611 | 0.75254 | 0.57121
|  | 13:49 | 18.1622 | 0.73713 | 0.57121
|  | 13:49 | 18.1633 | 0.72173 | 0.57121
|  | 13:49 | 18.1644 | 0.70357 | 0.57121
|  | 13:49 | 18.1656 | 0.68266 | 0.5712
|  | 13:49 | 18.1667 | 0.66175 | 0.5712
|  | 13:49 | 18.1678 | 0.62242 | 0.5712
|  | 13:50 | 18.1689 | 0.58309 | 0.5712
|  | 13:50 | 18.17 | 0.54171 | 0.57119
|  | 13:50 | 18.1711 | 0.49829 | 0.57119
|  | 13:50 | 18.1722 | 0.45486 | 0.57119
|  | 13:50 | 18.1733 | 0.42925 | 0.57119
|  | 13:50 | 18.1744 | 0.40363 | 0.57119
|  | 13:50 | 18.1756 | 0.37379 | 0.57118
|  | 13:50 | 18.1767 | 0.33971 | 0.57118
|  | 13:50 | 18.1778 | 0.30564 | 0.57118
|  | 13:50 | 18.1789 | 0.27379 | 0.57118
|  | 13:50 | 18.18 | 0.24194 | 0.57117
|  | 13:50 | 18.1811 | 0.22435 | 0.57117
|  | 13:50 | 18.1822 | 0.22102 | 0.57117
|  | 13:50 | 18.1833 | 0.21769 | 0.57117
|  | 13:50 | 18.1844 | 0.20566 | 0.57116
|  | 13:51 | 18.1856 | 0.19362 | 0.57116
|  | 13:51 | 18.1867 | 0.18466 | 0.57116
|  | 13:51 | 18.1878 | 0.17879 | 0.57116
|  | 13:51 | 18.1889 | 0.17291 | 0.57116
|  | 13:51 | 18.19 | 0.16918 | 0.57115
|  | 13:51 | 18.1911 | 0.16545 | 0.57115
|  | 13:51 | 18.1922 | 0.15742 | 0.57115
|  | 13:51 | 18.1933 | 0.14511 | 0.57115
|  | 13:51 | 18.1944 | 0.13279 | 0.57114
|  | 13:51 | 18.1956 | 0.11944 | 0.57114
|  | 13:51 | 18.1967 | 0.10609 | 0.57114
|  | 13:51 | 18.1978 | 0.093734 | 0.57114
|  | 13:51 | 18.1989 | 0.082374 | 0.57113
|  | 13:51 | 18.2 | 0.071013 | 0.57113
|  | 13:51 | 18.2011 | 0.066403 | 0.57113
|  | 13:52 | 18.2022 | 0.061792 | 0.57113
|  | 13:52 | 18.2033 | 0.057755 | 0.57112
|  | 13:52 | 18.2044 | 0.05429 | 0.57112
|  | 13:52 | 18.2056 | 0.050825 | 0.57112
|  | 13:52 | 18.2067 | 0.032276 | 0.57112
|  | 13:52 | 18.2078 | 0.013726 | 0.57112
|  | 13:52 | 18.2089 | -0.0155 | 0.57111
|  | 13:52 | 18.21 | -0.055402 | 0.57111
|  | 13:52 | 18.2111 | -0.095305 | 0.57111
|  | 13:52 | 18.2122 | -0.1476 | 0.57111
|  | 13:52 | 18.2133 | -0.19989 | 0.5711
|  | 13:52 | 18.2144 | -0.25319 | 0.5711
|  | 13:52 | 18.2156 | -0.30752 | 0.5711
|  | 13:52 | 18.2167 | -0.36184 | 0.5711
|  | 13:52 | 18.2178 | -0.40614 | 0.57109
|  | 13:53 | 18.2189 | -0.45044 | 0.57109
|  | 13:53 | 18.22 | -0.48112 | 0.57109
|  | 13:53 | 18.2211 | -0.49819 | 0.57109
|  | 13:53 | 18.2222 | -0.51526 | 0.57109
|  | 13:53 | 18.2233 | -0.54146 | 0.57108
|  | 13:53 | 18.2244 | -0.56767 | 0.57108
|  | 13:53 | 18.2256 | -0.58665 | 0.57108
|  | 13:53 | 18.2267 | -0.59843 | 0.57108
|  | 13:53 | 18.2278 | -0.6102 | 0.57107
|  | 13:53 | 18.2289 | -0.60745 | 0.57107
|  | 13:53 | 18.23 | -0.6047 | 0.57107
|  | 13:53 | 18.2311 | -0.60347 | 0.57107
|  | 13:53 | 18.2322 | -0.60376 | 0.57106
|  | 13:53 | 18.2333 | -0.60405 | 0.57106
|  | 13:53 | 18.2344 | -0.60336 | 0.57106
|  | 13:54 | 18.2356 | -0.60266 | 0.57106
|  | 13:54 | 18.2367 | -0.60291 | 0.57106
|  | 13:54 | 18.2378 | -0.60599 | 0.57105
|  | 13:54 | 18.2389 | -0.60906 | 0.57105
|  | 13:54 | 18.24 | -0.61077 | 0.57105
|  | 13:54 | 18.2411 | -0.61248 | 0.57105
|  | 13:54 | 18.2422 | -0.6045 | 0.57104
|  | 13:54 | 18.2433 | -0.58685 | 0.57104
|  | 13:54 | 18.2444 | -0.56919 | 0.57104
|  | 13:54 | 18.2456 | -0.55636 | 0.57104
|  | 13:54 | 18.2467 | -0.54352 | 0.57103
|  | 13:54 | 18.2478 | -0.53564 | 0.57103
|  | 13:54 | 18.2489 | -0.53272 | 0.57103
|  | 13:54 | 18.25 | -0.5298 | 0.57103
|  | 13:54 | 18.2511 | -0.529 | 0.57103
|  | 13:55 | 18.2522 | -0.52819 | 0.57102
|  | 13:55 | 18.2533 | -0.53152 | 0.57102
|  | 13:55 | 18.2544 | -0.539 | 0.57102
|  | 13:55 | 18.2556 | -0.54647 | 0.57102
|  | 13:55 | 18.2567 | -0.54635 | 0.57101
|  | 13:55 | 18.2578 | -0.54623 | 0.57101
|  | 13:55 | 18.2589 | -0.54252 | 0.57101
|  | 13:55 | 18.26 | -0.53522 | 0.57101
|  | 13:55 | 18.2611 | -0.52791 | 0.571
|  | 13:55 | 18.2622 | -0.51653 | 0.571
|  | 13:55 | 18.2633 | -0.50516 | 0.571
|  | 13:55 | 18.2644 | -0.47674 | 0.571
|  | 13:55 | 18.2656 | -0.43128 | 0.571
|  | 13:55 | 18.2667 | -0.38582 | 0.57099
|  | 13:55 | 18.2678 | -0.34134 | 0.57099
|  | 13:56 | 18.2689 | -0.29686 | 0.57099
|  | 13:56 | 18.27 | -0.25636 | 0.57099
|  | 13:56 | 18.2711 | -0.21982 | 0.57098
|  | 13:56 | 18.2722 | -0.18329 | 0.57098
|  | 13:56 | 18.2733 | -0.16697 | 0.57098
|  | 13:56 | 18.2744 | -0.15066 | 0.57098
|  | 13:56 | 18.2756 | -0.13059 | 0.57097
|  | 13:56 | 18.2767 | -0.10676 | 0.57097
|  | 13:56 | 18.2778 | -0.082929 | 0.57097
|  | 13:56 | 18.2789 | -0.064992 | 0.57097
|  | 13:56 | 18.28 | -0.047054 | 0.57097
|  | 13:56 | 18.2811 | -0.033677 | 0.57096
|  | 13:56 | 18.2822 | -0.024861 | 0.57096
|  | 13:56 | 18.2833 | -0.016045 | 0.57096
|  | 13:56 | 18.2844 | -0.015577 | 0.57096
|  | 13:57 | 18.2856 | -0.01511 | 0.57095
|  | 13:57 | 18.2867 | -0.032247 | 0.57095
|  | 13:57 | 18.2878 | -0.066986 | 0.57095
|  | 13:57 | 18.2889 | -0.10173 | 0.57095
|  | 13:57 | 18.29 | -0.11422 | 0.57094
|  | 13:57 | 18.2911 | -0.12672 | 0.57094
|  | 13:57 | 18.2922 | -0.14071 | 0.57094
|  | 13:57 | 18.2933 | -0.15619 | 0.57094
|  | 13:57 | 18.2944 | -0.17167 | 0.57094
|  | 13:57 | 18.2956 | -0.18715 | 0.57093
|  | 13:57 | 18.2967 | -0.20263 | 0.57093
|  | 13:57 | 18.2978 | -0.22463 | 0.57093
|  | 13:57 | 18.2989 | -0.25316 | 0.57093
|  | 13:57 | 18.3 | -0.28168 | 0.57092
|  | 13:57 | 18.3011 | -0.29777 | 0.57092
|  | 13:58 | 18.3022 | -0.31386 | 0.57092
|  | 13:58 | 18.3033 | -0.31394 | 0.57092
|  | 13:58 | 18.3044 | -0.298 | 0.57091
|  | 13:58 | 18.3056 | -0.28207 | 0.57091
|  | 13:58 | 18.3067 | -0.26097 | 0.57091
|  | 13:58 | 18.3078 | -0.23987 | 0.57091
|  | 13:58 | 18.3089 | -0.2201 | 0.57091
|  | 13:58 | 18.31 | -0.20168 | 0.5709
|  | 13:58 | 18.3111 | -0.18325 | 0.5709
|  | 13:58 | 18.3122 | -0.16685 | 0.5709
|  | 13:58 | 18.3133 | -0.15045 | 0.5709
|  | 13:58 | 18.3144 | -0.13497 | 0.57089
|  | 13:58 | 18.3156 | -0.1204 | 0.57089
|  | 13:58 | 18.3167 | -0.10583 | 0.57089
|  | 13:58 | 18.3178 | -0.085856 | 0.57089
|  | 13:59 | 18.3189 | -0.065882 | 0.57088
|  | 13:59 | 18.32 | -0.057483 | 0.57088
|  | 13:59 | 18.3211 | -0.060658 | 0.57088
|  | 13:59 | 18.3222 | -0.063833 | 0.57088
|  | 13:59 | 18.3233 | -0.042603 | 0.57087
|  | 13:59 | 18.3244 | -0.021374 | 0.57087
|  | 13:59 | 18.3256 | -0.0021204 | 0.57087
|  | 13:59 | 18.3267 | 0.015157 | 0.57087
|  | 13:59 | 18.3278 | 0.032435 | 0.57087
|  | 13:59 | 18.3289 | 0.024561 | 0.57086
|  | 13:59 | 18.33 | 0.016687 | 0.57086
|  | 13:59 | 18.3311 | 0.012389 | 0.57086
|  | 13:59 | 18.3322 | 0.011665 | 0.57086
|  | 13:59 | 18.3333 | 0.010942 | 0.57085
|  | 13:59 | 18.3344 | 0.002515 | 0.57085
|  | 14:00 | 18.3356 | -0.0059115 | 0.57085
|  | 14:00 | 18.3367 | -0.026255 | 0.57085
|  | 14:00 | 18.3378 | -0.058516 | 0.57084
|  | 14:00 | 18.3389 | -0.090777 | 0.57084
|  | 14:00 | 18.34 | -0.1219 | 0.57084
|  | 14:00 | 18.3411 | -0.15302 | 0.57084
|  | 14:00 | 18.3422 | -0.18289 | 0.57084
|  | 14:00 | 18.3433 | -0.2827 | 0.57083
|  | 14:00 | 18.3444 | -0.27395 | 0.57083
|  | 14:00 | 18.3456 | -0.26521 | 0.57083
|  | 14:00 | 18.3467 | -0.25647 | 0.57083
|  | 14:00 | 18.3478 | -0.24772 | 0.57082
|  | 14:00 | 18.3489 | -0.23835 | 0.57082
|  | 14:00 | 18.35 | -0.22836 | 0.57082
|  | 14:00 | 18.3511 | -0.21836 | 0.57082
|  | 14:01 | 18.3522 | -0.20836 | 0.57081
|  | 14:01 | 18.3533 | -0.19837 | 0.57081
|  | 14:01 | 18.3544 | -0.18873 | 0.57081
|  | 14:01 | 18.3556 | -0.17945 | 0.57081
|  | 14:01 | 18.3567 | -0.17017 | 0.57081
|  | 14:01 | 18.3578 | -0.16491 | 0.5708
|  | 14:01 | 18.3589 | -0.15964 | 0.5708
|  | 14:01 | 18.36 | -0.13943 | 0.5708
|  | 14:01 | 18.3611 | -0.1043 | 0.5708
|  | 14:01 | 18.3622 | -0.069166 | 0.57079
|  | 14:01 | 18.3633 | -0.025458 | 0.57079
|  | 14:01 | 18.3644 | 0.018251 | 0.57079
|  | 14:01 | 18.3656 | 0.050382 | 0.57079
|  | 14:01 | 18.3667 | 0.070937 | 0.57078
|  | 14:01 | 18.3678 | 0.091492 | 0.57078
|  | 14:02 | 18.3689 | 0.096229 | 0.57078
|  | 14:02 | 18.37 | 0.10097 | 0.57078
|  | 14:02 | 18.3711 | 0.10124 | 0.57078
|  | 14:02 | 18.3722 | 0.097046 | 0.57077
|  | 14:02 | 18.3733 | 0.092854 | 0.57077
|  | 14:02 | 18.3744 | 0.087061 | 0.57077
|  | 14:02 | 18.3756 | 0.081269 | 0.57077
|  | 14:02 | 18.3767 | 0.07728 | 0.57076
|  | 14:02 | 18.3778 | 0.075093 | 0.57076
|  | 14:02 | 18.3789 | 0.072907 | 0.57076
|  | 14:02 | 18.38 | 0.071547 | 0.57076
|  | 14:02 | 18.3811 | 0.070188 | 0.57075
|  | 14:02 | 18.3822 | 0.065275 | 0.57075
|  | 14:02 | 18.3833 | 0.05681 | 0.57075
|  | 14:02 | 18.3844 | 0.048345 | 0.57075
|  | 14:03 | 18.3856 | 0.04501 | 0.57075
|  | 14:03 | 18.3867 | 0.041676 | 0.57074
|  | 14:03 | 18.3878 | 0.041155 | 0.57074
|  | 14:03 | 18.3889 | 0.043449 | 0.57074
|  | 14:03 | 18.39 | 0.045743 | 0.57074
|  | 14:03 | 18.3911 | 0.053399 | 0.57073
|  | 14:03 | 18.3922 | 0.061055 | 0.57073
|  | 14:03 | 18.3933 | 0.07047 | 0.57073
|  | 14:03 | 18.3944 | 0.081644 | 0.57073
|  | 14:03 | 18.3956 | 0.092819 | 0.57072
|  | 14:03 | 18.3967 | 0.10541 | 0.57072
|  | 14:03 | 18.3978 | 0.11801 | 0.57072
|  | 14:03 | 18.3989 | 0.12946 | 0.57072
|  | 14:03 | 18.4 | 0.13978 | 0.57072
|  | 14:03 | 18.4011 | 0.15009 | 0.57071
|  | 14:04 | 18.4022 | 0.1558 | 0.57071
|  | 14:04 | 18.4033 | 0.1615 | 0.57071
|  | 14:04 | 18.4044 | 0.16624 | 0.57071
|  | 14:04 | 18.4056 | 0.17002 | 0.5707
|  | 14:04 | 18.4067 | 0.17379 | 0.5707
|  | 14:04 | 18.4078 | 0.25959 | 0.5707
|  | 14:04 | 18.4089 | 0.34539 | 0.5707
|  | 14:04 | 18.41 | 0.40906 | 0.57069
|  | 14:04 | 18.4111 | 0.45059 | 0.57069
|  | 14:04 | 18.4122 | 0.49213 | 0.57069
|  | 14:04 | 18.4133 | 0.4921 | 0.57069
|  | 14:04 | 18.4144 | 0.49208 | 0.57069
|  | 14:04 | 18.4156 | 0.49019 | 0.57068
|  | 14:04 | 18.4167 | 0.48643 | 0.57068
|  | 14:04 | 18.4178 | 0.48266 | 0.57068
|  | 14:05 | 18.4189 | 0.48082 | 0.57068
|  | 14:05 | 18.42 | 0.47897 | 0.57067
|  | 14:05 | 18.4211 | 0.48042 | 0.57067
|  | 14:05 | 18.4222 | 0.48518 | 0.57067
|  | 14:05 | 18.4233 | 0.48994 | 0.57067
|  | 14:05 | 18.4244 | 0.50082 | 0.57066
|  | 14:05 | 18.4256 | 0.5117 | 0.57066
|  | 14:05 | 18.4267 | 0.52447 | 0.57066
|  | 14:05 | 18.4278 | 0.53912 | 0.57066
|  | 14:05 | 18.4289 | 0.55378 | 0.57066
|  | 14:05 | 18.43 | 0.57058 | 0.57065
|  | 14:05 | 18.4311 | 0.58739 | 0.57065
|  | 14:05 | 18.4322 | 0.60419 | 0.57065
|  | 14:05 | 18.4333 | 0.621 | 0.57065
|  | 14:05 | 18.4344 | 0.63694 | 0.57064
|  | 14:06 | 18.4356 | 0.65031 | 0.57064
|  | 14:06 | 18.4367 | 0.66367 | 0.57064
|  | 14:06 | 18.4378 | 0.67734 | 0.57064
|  | 14:06 | 18.4389 | 0.69131 | 0.57063
|  | 14:06 | 18.44 | 0.70529 | 0.57063
|  | 14:06 | 18.4411 | 0.71926 | 0.57063
|  | 14:06 | 18.4422 | 0.73323 | 0.57063
|  | 14:06 | 18.4433 | 0.74576 | 0.57062
|  | 14:06 | 18.4444 | 0.75683 | 0.57062
|  | 14:06 | 18.4456 | 0.7679 | 0.57062
|  | 14:06 | 18.4467 | 0.77035 | 0.57062
|  | 14:06 | 18.4478 | 0.7728 | 0.57062
|  | 14:06 | 18.4489 | 0.77179 | 0.57061
|  | 14:06 | 18.45 | 0.76733 | 0.57061
|  | 14:06 | 18.4511 | 0.76286 | 0.57061
|  | 14:07 | 18.4522 | 0.75839 | 0.57061
|  | 14:07 | 18.4533 | 0.75393 | 0.5706
|  | 14:07 | 18.4544 | 0.74992 | 0.5706
|  | 14:07 | 18.4556 | 0.74636 | 0.5706
|  | 14:07 | 18.4567 | 0.74281 | 0.5706
|  | 14:07 | 18.4578 | 0.77247 | 0.57059
|  | 14:07 | 18.4589 | 0.80213 | 0.57059
|  | 14:07 | 18.46 | 0.80874 | 0.57059
|  | 14:07 | 18.4611 | 0.79229 | 0.57059
|  | 14:07 | 18.4622 | 0.77585 | 0.57059
|  | 14:07 | 18.4633 | 0.77601 | 0.57058
|  | 14:07 | 18.4644 | 0.77617 | 0.57058
|  | 14:07 | 18.4656 | 0.7786 | 0.57058
|  | 14:07 | 18.4667 | 0.78332 | 0.57058
|  | 14:07 | 18.4678 | 0.78803 | 0.57057
|  | 14:08 | 18.4689 | 0.79275 | 0.57057
|  | 14:08 | 18.47 | 0.79747 | 0.57057
|  | 14:08 | 18.4711 | 0.80064 | 0.57057
|  | 14:08 | 18.4722 | 0.80226 | 0.57056
|  | 14:08 | 18.4733 | 0.80389 | 0.57056
|  | 14:08 | 18.4744 | 0.80251 | 0.57056
|  | 14:08 | 18.4756 | 0.80114 | 0.57056
|  | 14:08 | 18.4767 | 0.79676 | 0.57056
|  | 14:08 | 18.4778 | 0.78937 | 0.57055
|  | 14:08 | 18.4789 | 0.78199 | 0.57055
|  | 14:08 | 18.48 | 0.76838 | 0.57055
|  | 14:08 | 18.4811 | 0.75477 | 0.57055
|  | 14:08 | 18.4822 | 0.7376 | 0.57054
|  | 14:08 | 18.4833 | 0.71685 | 0.57054
|  | 14:08 | 18.4844 | 0.69611 | 0.57054
|  | 14:09 | 18.4856 | 0.67314 | 0.57054
|  | 14:09 | 18.4867 | 0.65017 | 0.57053
|  | 14:09 | 18.4878 | 0.62532 | 0.57053
|  | 14:09 | 18.4889 | 0.59857 | 0.57053
|  | 14:09 | 18.49 | 0.57182 | 0.57053
|  | 14:09 | 18.4911 | 0.54024 | 0.57053
|  | 14:09 | 18.4922 | 0.50865 | 0.57052
|  | 14:09 | 18.4933 | 0.47528 | 0.57052
|  | 14:09 | 18.4944 | 0.44013 | 0.57052
|  | 14:09 | 18.4956 | 0.40498 | 0.57052
|  | 14:09 | 18.4967 | 0.36805 | 0.57051
|  | 14:09 | 18.4978 | 0.33113 | 0.57051
|  | 14:09 | 18.4989 | 0.29421 | 0.57051
|  | 14:09 | 18.5 | 0.25728 | 0.57051
|  | 14:09 | 18.5011 | 0.22036 | 0.5705
|  | 14:10 | 18.5022 | 0.18481 | 0.5705
|  | 14:10 | 18.5033 | 0.14927 | 0.5705
|  | 14:10 | 18.5044 | 0.11508 | 0.5705
|  | 14:10 | 18.5056 | 0.082226 | 0.5705
|  | 14:10 | 18.5067 | 0.049376 | 0.57049
|  | 14:10 | 18.5078 | -0.037982 | 0.57049
|  | 14:10 | 18.5089 | -0.12534 | 0.57049
|  | 14:10 | 18.51 | -0.25535 | 0.57049
|  | 14:10 | 18.5111 | -0.42801 | 0.57048
|  | 14:10 | 18.5122 | -0.60067 | 0.57048
|  | 14:10 | 18.5133 | -0.70218 | 0.57048
|  | 14:10 | 18.5144 | -0.80368 | 0.57048
|  | 14:10 | 18.5156 | -0.87558 | 0.57047
|  | 14:10 | 18.5167 | -0.91788 | 0.57047
|  | 14:10 | 18.5178 | -0.96018 | 0.57047
|  | 14:11 | 18.5189 | -0.96528 | 0.57047
|  | 14:11 | 18.52 | -0.97039 | 0.57047
|  | 14:11 | 18.5211 | -0.96714 | 0.57046
|  | 14:11 | 18.5222 | -0.95555 | 0.57046
|  | 14:11 | 18.5233 | -0.94395 | 0.57046
|  | 14:11 | 18.5244 | -0.92406 | 0.57046
|  | 14:11 | 18.5256 | -0.90417 | 0.57045
|  | 14:11 | 18.5267 | -0.88211 | 0.57045
|  | 14:11 | 18.5278 | -0.8579 | 0.57045
|  | 14:11 | 18.5289 | -0.83368 | 0.57045
|  | 14:11 | 18.53 | -0.80947 | 0.57044
|  | 14:11 | 18.5311 | -0.78525 | 0.57044
|  | 14:11 | 18.5322 | -0.7614 | 0.57044
|  | 14:11 | 18.5333 | -0.73791 | 0.57044
|  | 14:11 | 18.5344 | -0.71441 | 0.57044
|  | 14:12 | 18.5356 | -0.69092 | 0.57043
|  | 14:12 | 18.5367 | -0.66743 | 0.57043
|  | 14:12 | 18.5378 | -0.64491 | 0.57043
|  | 14:12 | 18.5389 | -0.62337 | 0.57043
|  | 14:12 | 18.54 | -0.60182 | 0.57042
|  | 14:12 | 18.5411 | -0.5858 | 0.57042
|  | 14:12 | 18.5422 | -0.56977 | 0.57042
|  | 14:12 | 18.5433 | -0.5558 | 0.57042
|  | 14:12 | 18.5444 | -0.54388 | 0.57041
|  | 14:12 | 18.5456 | -0.53196 | 0.57041
|  | 14:12 | 18.5467 | -0.52258 | 0.57041
|  | 14:12 | 18.5478 | -0.51321 | 0.57041
|  | 14:12 | 18.5489 | -0.50383 | 0.57041
|  | 14:12 | 18.55 | -0.49445 | 0.5704
|  | 14:12 | 18.5511 | -0.48508 | 0.5704
|  | 14:13 | 18.5522 | -0.47904 | 0.5704
|  | 14:13 | 18.5533 | -0.473 | 0.5704
|  | 14:13 | 18.5544 | -0.4684 | 0.57039
|  | 14:13 | 18.5556 | -0.46524 | 0.57039
|  | 14:13 | 18.5567 | -0.46208 | 0.57039
|  | 14:13 | 18.5578 | -0.519 | 0.57039
|  | 14:13 | 18.5589 | -0.57592 | 0.57038
|  | 14:13 | 18.56 | -0.61498 | 0.57038
|  | 14:13 | 18.5611 | -0.63619 | 0.57038
|  | 14:13 | 18.5622 | -0.6574 | 0.57038
|  | 14:13 | 18.5633 | -0.64013 | 0.57037
|  | 14:13 | 18.5644 | -0.62286 | 0.57037
|  | 14:13 | 18.5656 | -0.60193 | 0.57037
|  | 14:13 | 18.5667 | -0.57735 | 0.57037
|  | 14:13 | 18.5678 | -0.55276 | 0.57037
|  | 14:14 | 18.5689 | -0.52231 | 0.57036
|  | 14:14 | 18.57 | -0.49185 | 0.57036
|  | 14:14 | 18.5711 | -0.45848 | 0.57036
|  | 14:14 | 18.5722 | -0.42219 | 0.57036
|  | 14:14 | 18.5733 | -0.3859 | 0.57035
|  | 14:14 | 18.5744 | -0.3496 | 0.57035
|  | 14:14 | 18.5756 | -0.31331 | 0.57035
|  | 14:14 | 18.5767 | -0.27812 | 0.57035
|  | 14:14 | 18.5778 | -0.24404 | 0.57034
|  | 14:14 | 18.5789 | -0.20995 | 0.57034
|  | 14:14 | 18.58 | -0.17858 | 0.57034
|  | 14:14 | 18.5811 | -0.14721 | 0.57034
|  | 14:14 | 18.5822 | -0.11655 | 0.57034
|  | 14:14 | 18.5833 | -0.086588 | 0.57033
|  | 14:14 | 18.5844 | -0.056628 | 0.57033
|  | 14:15 | 18.5856 | -0.029615 | 0.57033
|  | 14:15 | 18.5867 | -0.002601 | 0.57033
|  | 14:15 | 18.5878 | 0.021431 | 0.57032
|  | 14:15 | 18.5889 | 0.042482 | 0.57032
|  | 14:15 | 18.59 | 0.063533 | 0.57032
|  | 14:15 | 18.5911 | 0.079306 | 0.57032
|  | 14:15 | 18.5922 | 0.09508 | 0.57031
|  | 14:15 | 18.5933 | 0.10812 | 0.57031
|  | 14:15 | 18.5944 | 0.11841 | 0.57031
|  | 14:15 | 18.5956 | 0.12871 | 0.57031
|  | 14:15 | 18.5967 | 0.13544 | 0.57031
|  | 14:15 | 18.5978 | 0.14218 | 0.5703
|  | 14:15 | 18.5989 | 0.14891 | 0.5703
|  | 14:15 | 18.6 | 0.15564 | 0.5703
|  | 14:15 | 18.6011 | 0.16238 | 0.5703
|  | 14:16 | 18.6022 | 0.16911 | 0.57029
|  | 14:16 | 18.6033 | 0.17585 | 0.57029
|  | 14:16 | 18.6044 | 0.18168 | 0.57029
|  | 14:16 | 18.6056 | 0.18662 | 0.57029
|  | 14:16 | 18.6067 | 0.19157 | 0.57028
|  | 14:16 | 18.6078 | 0.1792 | 0.57028
|  | 14:16 | 18.6089 | 0.16683 | 0.57028
|  | 14:16 | 18.61 | 0.16802 | 0.57028
|  | 14:16 | 18.6111 | 0.18276 | 0.57028
|  | 14:16 | 18.6122 | 0.19751 | 0.57027
|  | 14:16 | 18.6133 | 0.2079 | 0.57027
|  | 14:16 | 18.6144 | 0.2183 | 0.57027
|  | 14:16 | 18.6156 | 0.22249 | 0.57027
|  | 14:16 | 18.6167 | 0.22048 | 0.57026
|  | 14:16 | 18.6178 | 0.21846 | 0.57026
|  | 14:17 | 18.6189 | 0.21104 | 0.57026
|  | 14:17 | 18.62 | 0.20361 | 0.57026
|  | 14:17 | 18.6211 | 0.19619 | 0.57025
|  | 14:17 | 18.6222 | 0.18876 | 0.57025
|  | 14:17 | 18.6233 | 0.18134 | 0.57025
|  | 14:17 | 18.6244 | 0.17929 | 0.57025
|  | 14:17 | 18.6256 | 0.17725 | 0.57025
|  | 14:17 | 18.6267 | 0.17861 | 0.57024
|  | 14:17 | 18.6278 | 0.18337 | 0.57024
|  | 14:17 | 18.6289 | 0.18813 | 0.57024
|  | 14:17 | 18.63 | 0.19536 | 0.57024
|  | 14:17 | 18.6311 | 0.20258 | 0.57023
|  | 14:17 | 18.6322 | 0.20918 | 0.57023
|  | 14:17 | 18.6333 | 0.21514 | 0.57023
|  | 14:17 | 18.6344 | 0.22111 | 0.57023
|  | 14:18 | 18.6356 | 0.22708 | 0.57022
|  | 14:18 | 18.6367 | 0.23304 | 0.57022
|  | 14:18 | 18.6378 | 0.24099 | 0.57022
|  | 14:18 | 18.6389 | 0.25091 | 0.57022
|  | 14:18 | 18.64 | 0.26082 | 0.57022
|  | 14:18 | 18.6411 | 0.27279 | 0.57021
|  | 14:18 | 18.6422 | 0.28475 | 0.57021
|  | 14:18 | 18.6433 | 0.29671 | 0.57021
|  | 14:18 | 18.6444 | 0.30867 | 0.57021
|  | 14:18 | 18.6456 | 0.32063 | 0.5702
|  | 14:18 | 18.6467 | 0.33175 | 0.5702
|  | 14:18 | 18.6478 | 0.34287 | 0.5702
|  | 14:18 | 18.6489 | 0.35398 | 0.5702
|  | 14:18 | 18.65 | 0.3651 | 0.57019
|  | 14:18 | 18.6511 | 0.37621 | 0.57019
|  | 14:19 | 18.6522 | 0.386 | 0.57019
|  | 14:19 | 18.6533 | 0.39579 | 0.57019
|  | 14:19 | 18.6544 | 0.40415 | 0.57019
|  | 14:19 | 18.6556 | 0.41109 | 0.57018
|  | 14:19 | 18.6567 | 0.41804 | 0.57018
|  | 14:19 | 18.6578 | 0.40223 | 0.57018
|  | 14:19 | 18.6589 | 0.38643 | 0.57018
|  | 14:19 | 18.66 | 0.38904 | 0.57017
|  | 14:19 | 18.6611 | 0.41007 | 0.57017
|  | 14:19 | 18.6622 | 0.43109 | 0.57017
|  | 14:19 | 18.6633 | 0.4384 | 0.57017
|  | 14:19 | 18.6644 | 0.44571 | 0.57016
|  | 14:19 | 18.6656 | 0.44633 | 0.57016
|  | 14:19 | 18.6667 | 0.44025 | 0.57016
|  | 14:19 | 18.6678 | 0.43418 | 0.57016
|  | 14:20 | 18.6689 | 0.42033 | 0.57016
|  | 14:20 | 18.67 | 0.40647 | 0.57015
|  | 14:20 | 18.6711 | 0.38991 | 0.57015
|  | 14:20 | 18.6722 | 0.37065 | 0.57015
|  | 14:20 | 18.6733 | 0.35139 | 0.57015
|  | 14:20 | 18.6744 | 0.32967 | 0.57014
|  | 14:20 | 18.6756 | 0.30795 | 0.57014
|  | 14:20 | 18.6767 | 0.28516 | 0.57014
|  | 14:20 | 18.6778 | 0.26129 | 0.57014
|  | 14:20 | 18.6789 | 0.23742 | 0.57013
|  | 14:20 | 18.68 | 0.20945 | 0.57013
|  | 14:20 | 18.6811 | 0.18148 | 0.57013
|  | 14:20 | 18.6822 | 0.15241 | 0.57013
|  | 14:20 | 18.6833 | 0.12226 | 0.57012
|  | 14:20 | 18.6844 | 0.092098 | 0.57012
|  | 14:21 | 18.6856 | 0.064983 | 0.57012
|  | 14:21 | 18.6867 | 0.037867 | 0.57012
|  | 14:21 | 18.6878 | 0.011722 | 0.57012
|  | 14:21 | 18.6889 | -0.013454 | 0.57011
|  | 14:21 | 18.69 | -0.038629 | 0.57011
|  | 14:21 | 18.6911 | -0.060119 | 0.57011
|  | 14:21 | 18.6922 | -0.081609 | 0.57011
|  | 14:21 | 18.6933 | -0.1004 | 0.5701
|  | 14:21 | 18.6944 | -0.11651 | 0.5701
|  | 14:21 | 18.6956 | -0.13261 | 0.5701
|  | 14:21 | 18.6967 | -0.14433 | 0.5701
|  | 14:21 | 18.6978 | -0.15606 | 0.57009
|  | 14:21 | 18.6989 | -0.16648 | 0.57009
|  | 14:21 | 18.7 | -0.17558 | 0.57009
|  | 14:21 | 18.7011 | -0.18468 | 0.57009
|  | 14:22 | 18.7022 | -0.19153 | 0.57009
|  | 14:22 | 18.7033 | -0.19838 | 0.57008
|  | 14:22 | 18.7044 | -0.20412 | 0.57008
|  | 14:22 | 18.7056 | -0.20875 | 0.57008
|  | 14:22 | 18.7067 | -0.21339 | 0.57008
|  | 14:22 | 18.7078 | -0.27673 | 0.57007
|  | 14:22 | 18.7089 | -0.34008 | 0.57007
|  | 14:22 | 18.71 | -0.41007 | 0.57007
|  | 14:22 | 18.7111 | -0.4867 | 0.57007
|  | 14:22 | 18.7122 | -0.56334 | 0.57006
|  | 14:22 | 18.7133 | -0.59367 | 0.57006
|  | 14:22 | 18.7144 | -0.62399 | 0.57006
|  | 14:22 | 18.7156 | -0.64309 | 0.57006
|  | 14:22 | 18.7167 | -0.65095 | 0.57006
|  | 14:22 | 18.7178 | -0.65881 | 0.57005
|  | 14:23 | 18.7189 | -0.6572 | 0.57005
|  | 14:23 | 18.72 | -0.65559 | 0.57005
|  | 14:23 | 18.7211 | -0.65201 | 0.57005
|  | 14:23 | 18.7222 | -0.64644 | 0.57004
|  | 14:23 | 18.7233 | -0.64087 | 0.57004
|  | 14:23 | 18.7244 | -0.6353 | 0.57004
|  | 14:23 | 18.7256 | -0.62973 | 0.57004
|  | 14:23 | 18.7267 | -0.62416 | 0.57003
|  | 14:23 | 18.7278 | -0.61859 | 0.57003
|  | 14:23 | 18.7289 | -0.61302 | 0.57003
|  | 14:23 | 18.73 | -0.60745 | 0.57003
|  | 14:23 | 18.7311 | -0.60188 | 0.57003
|  | 14:23 | 18.7322 | -0.59692 | 0.57002
|  | 14:23 | 18.7333 | -0.59255 | 0.57002
|  | 14:23 | 18.7344 | -0.58819 | 0.57002
|  | 14:24 | 18.7356 | -0.58697 | 0.57002
|  | 14:24 | 18.7367 | -0.58575 | 0.57001
|  | 14:24 | 18.7378 | -0.58651 | 0.57001
|  | 14:24 | 18.7389 | -0.58927 | 0.57001
|  | 14:24 | 18.74 | -0.59202 | 0.57001
|  | 14:24 | 18.7411 | -0.59622 | 0.57
|  | 14:24 | 18.7422 | -0.60042 | 0.57
|  | 14:24 | 18.7433 | -0.60463 | 0.57
|  | 14:24 | 18.7444 | -0.60883 | 0.57
|  | 14:24 | 18.7456 | -0.61303 | 0.57
|  | 14:24 | 18.7467 | -0.61489 | 0.56999
|  | 14:24 | 18.7478 | -0.61674 | 0.56999
|  | 14:24 | 18.7489 | -0.61696 | 0.56999
|  | 14:24 | 18.75 | -0.61554 | 0.56999
|  | 14:24 | 18.7511 | -0.61412 | 0.56998
|  | 14:25 | 18.7522 | -0.60966 | 0.56998
|  | 14:25 | 18.7533 | -0.6052 | 0.56998
|  | 14:25 | 18.7544 | -0.59955 | 0.56998
|  | 14:25 | 18.7556 | -0.59272 | 0.56997
|  | 14:25 | 18.7567 | -0.58588 | 0.56997
|  | 14:25 | 18.7578 | -0.57414 | 0.56997
|  | 14:25 | 18.7589 | -0.56241 | 0.56997
|  | 14:25 | 18.76 | -0.55708 | 0.56997
|  | 14:25 | 18.7611 | -0.55816 | 0.56996
|  | 14:25 | 18.7622 | -0.55925 | 0.56996
|  | 14:25 | 18.7633 | -0.55809 | 0.56996
|  | 14:25 | 18.7644 | -0.55693 | 0.56996
|  | 14:25 | 18.7656 | -0.55379 | 0.56995
|  | 14:25 | 18.7667 | -0.54867 | 0.56995
|  | 14:25 | 18.7678 | -0.54355 | 0.56995
|  | 14:26 | 18.7689 | -0.53414 | 0.56995
|  | 14:26 | 18.77 | -0.52473 | 0.56994
|  | 14:26 | 18.7711 | -0.51434 | 0.56994
|  | 14:26 | 18.7722 | -0.50295 | 0.56994
|  | 14:26 | 18.7733 | -0.49157 | 0.56994
|  | 14:26 | 18.7744 | -0.47934 | 0.56994
|  | 14:26 | 18.7756 | -0.46711 | 0.56993
|  | 14:26 | 18.7767 | -0.4533 | 0.56993
|  | 14:26 | 18.7778 | -0.43792 | 0.56993
|  | 14:26 | 18.7789 | -0.42253 | 0.56993
|  | 14:26 | 18.78 | -0.40304 | 0.56992
|  | 14:26 | 18.7811 | -0.38356 | 0.56992
|  | 14:26 | 18.7822 | -0.36407 | 0.56992
|  | 14:26 | 18.7833 | -0.34458 | 0.56992
|  | 14:26 | 18.7844 | -0.3251 | 0.56991
|  | 14:27 | 18.7856 | -0.30561 | 0.56991
|  | 14:27 | 18.7867 | -0.28612 | 0.56991
|  | 14:27 | 18.7878 | -0.26563 | 0.56991
|  | 14:27 | 18.7889 | -0.24414 | 0.56991
|  | 14:27 | 18.79 | -0.22265 | 0.5699
|  | 14:27 | 18.7911 | -0.19861 | 0.5699
|  | 14:27 | 18.7922 | -0.17456 | 0.5699
|  | 14:27 | 18.7933 | -0.15137 | 0.5699
|  | 14:27 | 18.7944 | -0.12903 | 0.56989
|  | 14:27 | 18.7956 | -0.10669 | 0.56989
|  | 14:27 | 18.7967 | -0.087153 | 0.56989
|  | 14:27 | 18.7978 | -0.067612 | 0.56989
|  | 14:27 | 18.7989 | -0.049331 | 0.56988
|  | 14:27 | 18.8 | -0.032308 | 0.56988
|  | 14:27 | 18.8011 | -0.015285 | 0.56988
|  | 14:28 | 18.8022 | 0.0017385 | 0.56988
|  | 14:28 | 18.8033 | 0.018762 | 0.56987
|  | 14:28 | 18.8044 | 0.036672 | 0.56987
|  | 14:28 | 18.8056 | 0.055471 | 0.56987
|  | 14:28 | 18.8067 | 0.074269 | 0.56987
|  | 14:28 | 18.8078 | 0.13185 | 0.56987
|  | 14:28 | 18.8089 | 0.18944 | 0.56986
|  | 14:28 | 18.81 | 0.25458 | 0.56986
|  | 14:28 | 18.8111 | 0.32727 | 0.56986
|  | 14:28 | 18.8122 | 0.39996 | 0.56986
|  | 14:28 | 18.8133 | 0.42709 | 0.56985
|  | 14:28 | 18.8144 | 0.45422 | 0.56985
|  | 14:28 | 18.8156 | 0.47301 | 0.56985
|  | 14:28 | 18.8167 | 0.48346 | 0.56985
|  | 14:28 | 18.8178 | 0.49391 | 0.56984
|  | 14:29 | 18.8189 | 0.4989 | 0.56984
|  | 14:29 | 18.82 | 0.50389 | 0.56984
|  | 14:29 | 18.8211 | 0.50888 | 0.56984
|  | 14:29 | 18.8222 | 0.51386 | 0.56984
|  | 14:29 | 18.8233 | 0.51885 | 0.56983
|  | 14:29 | 18.8244 | 0.52352 | 0.56983
|  | 14:29 | 18.8256 | 0.52819 | 0.56983
|  | 14:29 | 18.8267 | 0.53072 | 0.56983
|  | 14:29 | 18.8278 | 0.53111 | 0.56982
|  | 14:29 | 18.8289 | 0.53149 | 0.56982
|  | 14:29 | 18.83 | 0.51394 | 0.56982
|  | 14:29 | 18.8311 | 0.4964 | 0.56982
|  | 14:29 | 18.8322 | 0.47974 | 0.56981
|  | 14:29 | 18.8333 | 0.46397 | 0.56981
|  | 14:29 | 18.8344 | 0.4482 | 0.56981
|  | 14:30 | 18.8356 | 0.44225 | 0.56981
|  | 14:30 | 18.8367 | 0.4363 | 0.56981
|  | 14:30 | 18.8378 | 0.43462 | 0.5698
|  | 14:30 | 18.8389 | 0.43722 | 0.5698
|  | 14:30 | 18.84 | 0.43981 | 0.5698
|  | 14:30 | 18.8411 | 0.44706 | 0.5698
|  | 14:30 | 18.8422 | 0.45432 | 0.56979
|  | 14:30 | 18.8433 | 0.46249 | 0.56979
|  | 14:30 | 18.8444 | 0.47159 | 0.56979
|  | 14:30 | 18.8456 | 0.48068 | 0.56979
|  | 14:30 | 18.8467 | 0.48567 | 0.56978
|  | 14:30 | 18.8478 | 0.49065 | 0.56978
|  | 14:30 | 18.8489 | 0.49461 | 0.56978
|  | 14:30 | 18.85 | 0.49755 | 0.56978
|  | 14:30 | 18.8511 | 0.50048 | 0.56978
|  | 14:31 | 18.8522 | 0.50341 | 0.56977
|  | 14:31 | 18.8533 | 0.50635 | 0.56977
|  | 14:31 | 18.8544 | 0.5096 | 0.56977
|  | 14:31 | 18.8556 | 0.51318 | 0.56977
|  | 14:31 | 18.8567 | 0.51676 | 0.56976
|  | 14:31 | 18.8578 | 0.5342 | 0.56976
|  | 14:31 | 18.8589 | 0.55164 | 0.56976
|  | 14:31 | 18.86 | 0.57136 | 0.56976
|  | 14:31 | 18.8611 | 0.59336 | 0.56975
|  | 14:31 | 18.8622 | 0.61535 | 0.56975
|  | 14:31 | 18.8633 | 0.61621 | 0.56975
|  | 14:31 | 18.8644 | 0.61707 | 0.56975
|  | 14:31 | 18.8656 | 0.55278 | 0.56975
|  | 14:31 | 18.8667 | 0.42336 | 0.56974
|  | 14:31 | 18.8678 | 0.29393 | 0.56974
|  | 14:32 | 18.8689 | 0.12168 | 0.56974
|  | 14:32 | 18.87 | -0.050575 | 0.56974
|  | 14:32 | 18.8711 | -0.18932 | 0.56973
|  | 14:32 | 18.8722 | -0.29455 | 0.56973
|  | 14:32 | 18.8733 | -0.39978 | 0.56973
|  | 14:32 | 18.8744 | -0.46036 | 0.56973
|  | 14:32 | 18.8756 | -0.52094 | 0.56972
|  | 14:32 | 18.8767 | -0.55285 | 0.56972
|  | 14:32 | 18.8778 | -0.57519 | 0.56972
|  | 14:32 | 18.8789 | -0.59753 | 0.56972
|  | 14:32 | 18.88 | -0.60515 | 0.56972
|  | 14:32 | 18.8811 | -0.61277 | 0.56971
|  | 14:32 | 18.8822 | -0.61922 | 0.56971
|  | 14:32 | 18.8833 | -0.62451 | 0.56971
|  | 14:32 | 18.8844 | -0.62981 | 0.56971
|  | 14:33 | 18.8856 | -0.62618 | 0.5697
|  | 14:33 | 18.8867 | -0.62256 | 0.5697
|  | 14:33 | 18.8878 | -0.61603 | 0.5697
|  | 14:33 | 18.8889 | -0.6066 | 0.5697
|  | 14:33 | 18.89 | -0.59717 | 0.56969
|  | 14:33 | 18.8911 | -0.58535 | 0.56969
|  | 14:33 | 18.8922 | -0.57353 | 0.56969
|  | 14:33 | 18.8933 | -0.56172 | 0.56969
|  | 14:33 | 18.8944 | -0.5499 | 0.56969
|  | 14:33 | 18.8956 | -0.53808 | 0.56968
|  | 14:33 | 18.8967 | -0.52758 | 0.56968
|  | 14:33 | 18.8978 | -0.51707 | 0.56968
|  | 14:33 | 18.8989 | -0.50726 | 0.56968
|  | 14:33 | 18.9 | -0.49814 | 0.56967
|  | 14:33 | 18.9011 | -0.48903 | 0.56967
|  | 14:34 | 18.9022 | -0.47846 | 0.56967
|  | 14:34 | 18.9033 | -0.46788 | 0.56967
|  | 14:34 | 18.9044 | -0.45626 | 0.56966
|  | 14:34 | 18.9056 | -0.44358 | 0.56966
|  | 14:34 | 18.9067 | -0.43089 | 0.56966
|  | 14:34 | 18.9078 | -0.47422 | 0.56966
|  | 14:34 | 18.9089 | -0.51755 | 0.56966
|  | 14:34 | 18.91 | -0.51794 | 0.56965
|  | 14:34 | 18.9111 | -0.4754 | 0.56965
|  | 14:34 | 18.9122 | -0.43286 | 0.56965
|  | 14:34 | 18.9133 | -0.39032 | 0.56965
|  | 14:34 | 18.9144 | -0.34779 | 0.56964
|  | 14:34 | 18.9156 | -0.31047 | 0.56964
|  | 14:34 | 18.9167 | -0.27839 | 0.56964
|  | 14:34 | 18.9178 | -0.2463 | 0.56964
|  | 14:35 | 18.9189 | -0.2209 | 0.56963
|  | 14:35 | 18.92 | -0.1955 | 0.56963
|  | 14:35 | 18.9211 | -0.174 | 0.56963
|  | 14:35 | 18.9222 | -0.1564 | 0.56963
|  | 14:35 | 18.9233 | -0.1388 | 0.56962
|  | 14:35 | 18.9244 | -0.12894 | 0.56962
|  | 14:35 | 18.9256 | -0.11907 | 0.56962
|  | 14:35 | 18.9267 | -0.1123 | 0.56962
|  | 14:35 | 18.9278 | -0.10863 | 0.56962
|  | 14:35 | 18.9289 | -0.10495 | 0.56961
|  | 14:35 | 18.93 | -0.10455 | 0.56961
|  | 14:35 | 18.9311 | -0.10416 | 0.56961
|  | 14:35 | 18.9322 | -0.10523 | 0.56961
|  | 14:35 | 18.9333 | -0.10777 | 0.5696
|  | 14:35 | 18.9344 | -0.11032 | 0.5696
|  | 14:36 | 18.9356 | -0.11594 | 0.5696
|  | 14:36 | 18.9367 | -0.12156 | 0.5696
|  | 14:36 | 18.9378 | -0.12811 | 0.56959
|  | 14:36 | 18.9389 | -0.1356 | 0.56959
|  | 14:36 | 18.94 | -0.14309 | 0.56959
|  | 14:36 | 18.9411 | -0.15173 | 0.56959
|  | 14:36 | 18.9422 | -0.16038 | 0.56959
|  | 14:36 | 18.9433 | -0.16719 | 0.56958
|  | 14:36 | 18.9444 | -0.17218 | 0.56958
|  | 14:36 | 18.9456 | -0.17717 | 0.56958
|  | 14:36 | 18.9467 | -0.17308 | 0.56958
|  | 14:36 | 18.9478 | -0.16899 | 0.56957
|  | 14:36 | 18.9489 | -0.16106 | 0.56957
|  | 14:36 | 18.95 | -0.14928 | 0.56957
|  | 14:36 | 18.9511 | -0.13749 | 0.56957
|  | 14:37 | 18.9522 | -0.12391 | 0.56956
|  | 14:37 | 18.9533 | -0.11032 | 0.56956
|  | 14:37 | 18.9544 | -0.098166 | 0.56956
|  | 14:37 | 18.9556 | -0.087453 | 0.56956
|  | 14:37 | 18.9567 | -0.07674 | 0.56956
|  | 14:37 | 18.9578 | -0.10069 | 0.56955
|  | 14:37 | 18.9589 | -0.12464 | 0.56955
|  | 14:37 | 18.96 | -0.17172 | 0.56955
|  | 14:37 | 18.9611 | -0.24193 | 0.56955
|  | 14:37 | 18.9622 | -0.31214 | 0.56954
|  | 14:37 | 18.9633 | -0.34213 | 0.56954
|  | 14:37 | 18.9644 | -0.37211 | 0.56954
|  | 14:37 | 18.9656 | -0.38781 | 0.56954
|  | 14:37 | 18.9667 | -0.38921 | 0.56953
|  | 14:37 | 18.9678 | -0.39061 | 0.56953
|  | 14:38 | 18.9689 | -0.37881 | 0.56953
|  | 14:38 | 18.97 | -0.36701 | 0.56953
|  | 14:38 | 18.9711 | -0.35222 | 0.56953
|  | 14:38 | 18.9722 | -0.33444 | 0.56952
|  | 14:38 | 18.9733 | -0.31667 | 0.56952
|  | 14:38 | 18.9744 | -0.2936 | 0.56952
|  | 14:38 | 18.9756 | -0.27053 | 0.56952
|  | 14:38 | 18.9767 | -0.24822 | 0.56951
|  | 14:38 | 18.9778 | -0.22668 | 0.56951
|  | 14:38 | 18.9789 | -0.20514 | 0.56951
|  | 14:38 | 18.98 | -0.1852 | 0.56951
|  | 14:38 | 18.9811 | -0.16526 | 0.5695
|  | 14:38 | 18.9822 | -0.14664 | 0.5695
|  | 14:38 | 18.9833 | -0.12934 | 0.5695
|  | 14:38 | 18.9844 | -0.11205 | 0.5695
|  | 14:39 | 18.9856 | -0.099948 | 0.5695
|  | 14:39 | 18.9867 | -0.087851 | 0.56949
|  | 14:39 | 18.9878 | -0.078508 | 0.56949
|  | 14:39 | 18.9889 | -0.07192 | 0.56949
|  | 14:39 | 18.99 | -0.065332 | 0.56949
|  | 14:39 | 18.9911 | -0.064053 | 0.56948
|  | 14:39 | 18.9922 | -0.062775 | 0.56948
|  | 14:39 | 18.9933 | -0.063185 | 0.56948
|  | 14:39 | 18.9944 | -0.065284 | 0.56948
|  | 14:39 | 18.9956 | -0.067382 | 0.56947
|  | 14:39 | 18.9967 | -0.069481 | 0.56947
|  | 14:39 | 18.9978 | -0.071579 | 0.56947
|  | 14:39 | 18.9989 | -0.074878 | 0.56947
|  | 14:39 | 19 | -0.079378 | 0.56947
|  | 14:39 | 19.0011 | -0.083878 | 0.56946
|  | 14:40 | 19.0022 | -0.088377 | 0.56946
|  | 14:40 | 19.0033 | -0.092877 | 0.56946
|  | 14:40 | 19.0044 | -0.098095 | 0.56946
|  | 14:40 | 19.0056 | -0.10403 | 0.56945
|  | 14:40 | 19.0067 | -0.10997 | 0.56945
|  | 14:40 | 19.0078 | -0.13946 | 0.56945
|  | 14:40 | 19.0089 | -0.16895 | 0.56945
|  | 14:40 | 19.01 | -0.18787 | 0.56944
|  | 14:40 | 19.0111 | -0.1962 | 0.56944
|  | 14:40 | 19.0122 | -0.20453 | 0.56944
|  | 14:40 | 19.0133 | -0.21203 | 0.56944
|  | 14:40 | 19.0144 | -0.21952 | 0.56944
|  | 14:40 | 19.0156 | -0.22564 | 0.56943
|  | 14:40 | 19.0167 | -0.23039 | 0.56943
|  | 14:40 | 19.0178 | -0.23513 | 0.56943
|  | 14:41 | 19.0189 | -0.23519 | 0.56943
|  | 14:41 | 19.02 | -0.23525 | 0.56942
|  | 14:41 | 19.0211 | -0.23093 | 0.56942
|  | 14:41 | 19.0222 | -0.22224 | 0.56942
|  | 14:41 | 19.0233 | -0.21354 | 0.56942
|  | 14:41 | 19.0244 | -0.19231 | 0.56941
|  | 14:41 | 19.0256 | -0.17108 | 0.56941
|  | 14:41 | 19.0267 | -0.14533 | 0.56941
|  | 14:41 | 19.0278 | -0.11506 | 0.56941
|  | 14:41 | 19.0289 | -0.084793 | 0.56941
|  | 14:41 | 19.03 | -0.052965 | 0.5694
|  | 14:41 | 19.0311 | -0.021138 | 0.5694
|  | 14:41 | 19.0322 | 0.0086022 | 0.5694
|  | 14:41 | 19.0333 | 0.036255 | 0.5694
|  | 14:41 | 19.0344 | 0.063909 | 0.56939
|  | 14:42 | 19.0356 | 0.08698 | 0.56939
|  | 14:42 | 19.0367 | 0.11005 | 0.56939
|  | 14:42 | 19.0378 | 0.12944 | 0.56939
|  | 14:42 | 19.0389 | 0.14515 | 0.56938
|  | 14:42 | 19.04 | 0.16086 | 0.56938
|  | 14:42 | 19.0411 | 0.16811 | 0.56938
|  | 14:42 | 19.0422 | 0.17535 | 0.56938
|  | 14:42 | 19.0433 | 0.17838 | 0.56937
|  | 14:42 | 19.0444 | 0.17718 | 0.56937
|  | 14:42 | 19.0456 | 0.17598 | 0.56937
|  | 14:42 | 19.0467 | 0.16966 | 0.56937
|  | 14:42 | 19.0478 | 0.16334 | 0.56937
|  | 14:42 | 19.0489 | 0.15506 | 0.56936
|  | 14:42 | 19.05 | 0.14482 | 0.56936
|  | 14:42 | 19.0511 | 0.13458 | 0.56936
|  | 14:43 | 19.0522 | 0.12037 | 0.56936
|  | 14:43 | 19.0533 | 0.10616 | 0.56935
|  | 14:43 | 19.0544 | 0.088851 | 0.56935
|  | 14:43 | 19.0556 | 0.068439 | 0.56935
|  | 14:43 | 19.0567 | 0.048027 | 0.56935
|  | 14:43 | 19.0578 | -0.029392 | 0.56934
|  | 14:43 | 19.0589 | -0.10681 | 0.56934
|  | 14:43 | 19.06 | -0.17328 | 0.56934
|  | 14:43 | 19.0611 | -0.22881 | 0.56934
|  | 14:43 | 19.0622 | -0.28434 | 0.56934
|  | 14:43 | 19.0633 | -0.30227 | 0.56933
|  | 14:43 | 19.0644 | -0.3202 | 0.56933
|  | 14:43 | 19.0656 | -0.32944 | 0.56933
|  | 14:43 | 19.0667 | -0.33 | 0.56933
|  | 14:43 | 19.0678 | -0.33056 | 0.56932
|  | 14:44 | 19.0689 | -0.32176 | 0.56932
|  | 14:44 | 19.07 | -0.31296 | 0.56932
|  | 14:44 | 19.0711 | -0.3027 | 0.56932
|  | 14:44 | 19.0722 | -0.29098 | 0.56931
|  | 14:44 | 19.0733 | -0.27926 | 0.56931
|  | 14:44 | 19.0744 | -0.27189 | 0.56931
|  | 14:44 | 19.0756 | -0.26452 | 0.56931
|  | 14:44 | 19.0767 | -0.25715 | 0.56931
|  | 14:44 | 19.0778 | -0.24978 | 0.5693
|  | 14:44 | 19.0789 | -0.24241 | 0.5693
|  | 14:44 | 19.08 | -0.23608 | 0.5693
|  | 14:44 | 19.0811 | -0.22976 | 0.5693
|  | 14:44 | 19.0822 | -0.22516 | 0.56929
|  | 14:44 | 19.0833 | -0.22229 | 0.56929
|  | 14:44 | 19.0844 | -0.21941 | 0.56929
|  | 14:45 | 19.0856 | -0.22159 | 0.56929
|  | 14:45 | 19.0867 | -0.22376 | 0.56928
|  | 14:45 | 19.0878 | -0.2289 | 0.56928
|  | 14:45 | 19.0889 | -0.23701 | 0.56928
|  | 14:45 | 19.09 | -0.24512 | 0.56928
|  | 14:45 | 19.0911 | -0.25691 | 0.56928
|  | 14:45 | 19.0922 | -0.2687 | 0.56927
|  | 14:45 | 19.0933 | -0.27247 | 0.56927
|  | 14:45 | 19.0944 | -0.26823 | 0.56927
|  | 14:45 | 19.0956 | -0.264 | 0.56927
|  | 14:45 | 19.0967 | -0.28778 | 0.56926
|  | 14:45 | 19.0978 | -0.31157 | 0.56926
|  | 14:45 | 19.0989 | -0.33649 | 0.56926
|  | 14:45 | 19.1 | -0.36254 | 0.56926
|  | 14:45 | 19.1011 | -0.38859 | 0.56925
|  | 14:46 | 19.1022 | -0.40738 | 0.56925
|  | 14:46 | 19.1033 | -0.42617 | 0.56925
|  | 14:46 | 19.1044 | -0.44056 | 0.56925
|  | 14:46 | 19.1056 | -0.45055 | 0.56925
|  | 14:46 | 19.1067 | -0.46053 | 0.56924
|  | 14:46 | 19.1078 | -0.47051 | 0.56924
|  | 14:46 | 19.1089 | -0.4805 | 0.56924
|  | 14:46 | 19.11 | -0.50984 | 0.56924
|  | 14:46 | 19.1111 | -0.55854 | 0.56923
|  | 14:46 | 19.1122 | -0.60724 | 0.56923
|  | 14:46 | 19.1133 | -0.64314 | 0.56923
|  | 14:46 | 19.1144 | -0.67905 | 0.56923
|  | 14:46 | 19.1156 | -0.70179 | 0.56922
|  | 14:46 | 19.1167 | -0.71135 | 0.56922
|  | 14:46 | 19.1178 | -0.72092 | 0.56922
|  | 14:47 | 19.1189 | -0.70949 | 0.56922
|  | 14:47 | 19.12 | -0.69806 | 0.56922
|  | 14:47 | 19.1211 | -0.68135 | 0.56921
|  | 14:47 | 19.1222 | -0.65935 | 0.56921
|  | 14:47 | 19.1233 | -0.63736 | 0.56921
|  | 14:47 | 19.1244 | -0.61193 | 0.56921
|  | 14:47 | 19.1256 | -0.5865 | 0.5692
|  | 14:47 | 19.1267 | -0.56 | 0.5692
|  | 14:47 | 19.1278 | -0.53241 | 0.5692
|  | 14:47 | 19.1289 | -0.50482 | 0.5692
|  | 14:47 | 19.13 | -0.4782 | 0.56919
|  | 14:47 | 19.1311 | -0.45157 | 0.56919
|  | 14:47 | 19.1322 | -0.42824 | 0.56919
|  | 14:47 | 19.1333 | -0.40819 | 0.56919
|  | 14:47 | 19.1344 | -0.38814 | 0.56919
|  | 14:48 | 19.1356 | -0.36917 | 0.56918
|  | 14:48 | 19.1367 | -0.3502 | 0.56918
|  | 14:48 | 19.1378 | -0.3273 | 0.56918
|  | 14:48 | 19.1389 | -0.30045 | 0.56918
|  | 14:48 | 19.14 | -0.2736 | 0.56917
|  | 14:48 | 19.1411 | -0.23893 | 0.56917
|  | 14:48 | 19.1422 | -0.20425 | 0.56917
|  | 14:48 | 19.1433 | -0.16716 | 0.56917
|  | 14:48 | 19.1444 | -0.12764 | 0.56916
|  | 14:48 | 19.1456 | -0.088128 | 0.56916
|  | 14:48 | 19.1467 | -0.045627 | 0.56916
|  | 14:48 | 19.1478 | -0.0031259 | 0.56916
|  | 14:48 | 19.1489 | 0.039375 | 0.56916
|  | 14:48 | 19.15 | 0.081876 | 0.56915
|  | 14:48 | 19.1511 | 0.12438 | 0.56915
|  | 14:49 | 19.1522 | 0.16368 | 0.56915
|  | 14:49 | 19.1533 | 0.20299 | 0.56915
|  | 14:49 | 19.1544 | 0.23915 | 0.56914
|  | 14:49 | 19.1556 | 0.27216 | 0.56914
|  | 14:49 | 19.1567 | 0.30517 | 0.56914
|  | 14:49 | 19.1578 | 0.39575 | 0.56914
|  | 14:49 | 19.1589 | 0.48633 | 0.56913
|  | 14:49 | 19.16 | 0.5914 | 0.56913
|  | 14:49 | 19.1611 | 0.71096 | 0.56913
|  | 14:49 | 19.1622 | 0.83052 | 0.56913
|  | 14:49 | 19.1633 | 0.89732 | 0.56912
|  | 14:49 | 19.1644 | 0.96412 | 0.56912
|  | 14:49 | 19.1656 | 0.99801 | 0.56912
|  | 14:49 | 19.1667 | 0.99901 | 0.56912
|  | 14:49 | 19.1678 | 1 | 0.56912
|  | 14:50 | 19.1689 | 1 | 0.56911
|  | 14:50 | 19.17 | 1 | 0.56911
|  | 14:50 | 19.1711 | 1 | 0.56911
|  | 14:50 | 19.1722 | 1 | 0.56911
|  | 14:50 | 19.1733 | 1 | 0.5691
|  | 14:50 | 19.1744 | 1 | 0.5691
|  | 14:50 | 19.1756 | 1 | 0.5691
|  | 14:50 | 19.1767 | 1 | 0.5691
|  | 14:50 | 19.1778 | 1 | 0.56909
|  | 14:50 | 19.1789 | 1 | 0.56909
|  | 14:50 | 19.18 | 1 | 0.56909
|  | 14:50 | 19.1811 | 1 | 0.56909
|  | 14:50 | 19.1822 | 0.99275 | 0.56909
|  | 14:50 | 19.1833 | 0.97826 | 0.56908
|  | 14:50 | 19.1844 | 0.96377 | 0.56908
|  | 14:51 | 19.1856 | 0.94229 | 0.56908
|  | 14:51 | 19.1867 | 0.92081 | 0.56908
|  | 14:51 | 19.1878 | 0.89821 | 0.56907
|  | 14:51 | 19.1889 | 0.87449 | 0.56907
|  | 14:51 | 19.19 | 0.85076 | 0.56907
|  | 14:51 | 19.1911 | 0.82703 | 0.56907
|  | 14:51 | 19.1922 | 0.80331 | 0.56906
|  | 14:51 | 19.1933 | 0.78197 | 0.56906
|  | 14:51 | 19.1944 | 0.76302 | 0.56906
|  | 14:51 | 19.1956 | 0.74407 | 0.56906
|  | 14:51 | 19.1967 | 0.72773 | 0.56906
|  | 14:51 | 19.1978 | 0.71138 | 0.56905
|  | 14:51 | 19.1989 | 0.69565 | 0.56905
|  | 14:51 | 19.2 | 0.68054 | 0.56905
|  | 14:51 | 19.2011 | 0.66542 | 0.56905
|  | 14:52 | 19.2022 | 0.65113 | 0.56904
|  | 14:52 | 19.2033 | 0.63684 | 0.56904
|  | 14:52 | 19.2044 | 0.62134 | 0.56904
|  | 14:52 | 19.2056 | 0.60462 | 0.56904
|  | 14:52 | 19.2067 | 0.5879 | 0.56903
|  | 14:52 | 19.2078 | 0.52662 | 0.56903
|  | 14:52 | 19.2089 | 0.46533 | 0.56903
|  | 14:52 | 19.21 | 0.37083 | 0.56903
|  | 14:52 | 19.2111 | 0.24312 | 0.56903
|  | 14:52 | 19.2122 | 0.1154 | 0.56902
|  | 14:52 | 19.2133 | 0.030582 | 0.56902
|  | 14:52 | 19.2144 | -0.054235 | 0.56902
|  | 14:52 | 19.2156 | -0.11882 | 0.56902
|  | 14:52 | 19.2167 | -0.16317 | 0.56901
|  | 14:52 | 19.2178 | -0.20752 | 0.56901
|  | 14:53 | 19.2189 | -0.22771 | 0.56901
|  | 14:53 | 19.22 | -0.2479 | 0.56901
|  | 14:53 | 19.2211 | -0.2616 | 0.569
|  | 14:53 | 19.2222 | -0.26882 | 0.569
|  | 14:53 | 19.2233 | -0.27603 | 0.569
|  | 14:53 | 19.2244 | -0.2752 | 0.569
|  | 14:53 | 19.2256 | -0.27437 | 0.569
|  | 14:53 | 19.2267 | -0.2712 | 0.56899
|  | 14:53 | 19.2278 | -0.26568 | 0.56899
|  | 14:53 | 19.2289 | -0.26016 | 0.56899
|  | 14:53 | 19.23 | -0.25279 | 0.56899
|  | 14:53 | 19.2311 | -0.24542 | 0.56898
|  | 14:53 | 19.2322 | -0.23917 | 0.56898
|  | 14:53 | 19.2333 | -0.23404 | 0.56898
|  | 14:53 | 19.2344 | -0.2289 | 0.56898
|  | 14:54 | 19.2356 | -0.2277 | 0.56897
|  | 14:54 | 19.2367 | -0.2265 | 0.56897
|  | 14:54 | 19.2378 | -0.22731 | 0.56897
|  | 14:54 | 19.2389 | -0.23014 | 0.56897
|  | 14:54 | 19.24 | -0.23298 | 0.56897
|  | 14:54 | 19.2411 | -0.23816 | 0.56896
|  | 14:54 | 19.2422 | -0.24335 | 0.56896
|  | 14:54 | 19.2433 | -0.24752 | 0.56896
|  | 14:54 | 19.2444 | -0.25066 | 0.56896
|  | 14:54 | 19.2456 | -0.25381 | 0.56895
|  | 14:54 | 19.2467 | -0.25289 | 0.56895
|  | 14:54 | 19.2478 | -0.25197 | 0.56895
|  | 14:54 | 19.2489 | -0.25105 | 0.56895
|  | 14:54 | 19.25 | -0.25012 | 0.56894
|  | 14:54 | 19.2511 | -0.2492 | 0.56894
|  | 14:55 | 19.2522 | -0.25441 | 0.56894
|  | 14:55 | 19.2533 | -0.25961 | 0.56894
|  | 14:55 | 19.2544 | -0.26755 | 0.56894
|  | 14:55 | 19.2556 | -0.27821 | 0.56893
|  | 14:55 | 19.2567 | -0.28888 | 0.56893
|  | 14:55 | 19.2578 | -0.33983 | 0.56893
|  | 14:55 | 19.2589 | -0.39078 | 0.56893
|  | 14:55 | 19.26 | -0.44965 | 0.56892
|  | 14:55 | 19.2611 | -0.51643 | 0.56892
|  | 14:55 | 19.2622 | -0.58322 | 0.56892
|  | 14:55 | 19.2633 | -0.60397 | 0.56892
|  | 14:55 | 19.2644 | -0.62473 | 0.56891
|  | 14:55 | 19.2656 | -0.64777 | 0.56891
|  | 14:55 | 19.2667 | -0.6731 | 0.56891
|  | 14:55 | 19.2678 | -0.69843 | 0.56891
|  | 14:56 | 19.2689 | -0.71074 | 0.56891
|  | 14:56 | 19.27 | -0.72304 | 0.5689
|  | 14:56 | 19.2711 | -0.73135 | 0.5689
|  | 14:56 | 19.2722 | -0.73565 | 0.5689
|  | 14:56 | 19.2733 | -0.73995 | 0.5689
|  | 14:56 | 19.2744 | -0.74053 | 0.56889
|  | 14:56 | 19.2756 | -0.74112 | 0.56889
|  | 14:56 | 19.2767 | -0.74171 | 0.56889
|  | 14:56 | 19.2778 | -0.74229 | 0.56889
|  | 14:56 | 19.2789 | -0.74288 | 0.56888
|  | 14:56 | 19.28 | -0.74671 | 0.56888
|  | 14:56 | 19.2811 | -0.75054 | 0.56888
|  | 14:56 | 19.2822 | -0.75487 | 0.56888
|  | 14:56 | 19.2833 | -0.7597 | 0.56887
|  | 14:56 | 19.2844 | -0.76454 | 0.56887
|  | 14:57 | 19.2856 | -0.76619 | 0.56887
|  | 14:57 | 19.2867 | -0.76784 | 0.56887
|  | 14:57 | 19.2878 | -0.765 | 0.56887
|  | 14:57 | 19.2889 | -0.75767 | 0.56886
|  | 14:57 | 19.29 | -0.75034 | 0.56886
|  | 14:57 | 19.2911 | -0.73281 | 0.56886
|  | 14:57 | 19.2922 | -0.71528 | 0.56886
|  | 14:57 | 19.2933 | -0.69493 | 0.56885
|  | 14:57 | 19.2944 | -0.67176 | 0.56885
|  | 14:57 | 19.2956 | -0.64859 | 0.56885
|  | 14:57 | 19.2967 | -0.62707 | 0.56885
|  | 14:57 | 19.2978 | -0.60555 | 0.56884
|  | 14:57 | 19.2989 | -0.5828 | 0.56884
|  | 14:57 | 19.3 | -0.55881 | 0.56884
|  | 14:57 | 19.3011 | -0.53482 | 0.56884
|  | 14:58 | 19.3022 | -0.50617 | 0.56884
|  | 14:58 | 19.3033 | -0.47752 | 0.56883
|  | 14:58 | 19.3044 | -0.44746 | 0.56883
|  | 14:58 | 19.3056 | -0.41599 | 0.56883
|  | 14:58 | 19.3067 | -0.38452 | 0.56883
|  | 14:58 | 19.3078 | -0.273 | 0.56882
|  | 14:58 | 19.3089 | -0.16148 | 0.56882
|  | 14:58 | 19.31 | -0.081884 | 0.56882
|  | 14:58 | 19.3111 | -0.034206 | 0.56882
|  | 14:58 | 19.3122 | 0.013472 | 0.56881
|  | 14:58 | 19.3133 | 0.017901 | 0.56881
|  | 14:58 | 19.3144 | 0.02233 | 0.56881
|  | 14:58 | 19.3156 | 0.029769 | 0.56881
|  | 14:58 | 19.3167 | 0.040218 | 0.56881
|  | 14:58 | 19.3178 | 0.050667 | 0.5688
|  | 14:59 | 19.3189 | 0.069809 | 0.5688
|  | 14:59 | 19.32 | 0.088951 | 0.5688
|  | 14:59 | 19.3211 | 0.10936 | 0.5688
|  | 14:59 | 19.3222 | 0.13104 | 0.56879
|  | 14:59 | 19.3233 | 0.15272 | 0.56879
|  | 14:59 | 19.3244 | 0.1744 | 0.56879
|  | 14:59 | 19.3256 | 0.19608 | 0.56879
|  | 14:59 | 19.3267 | 0.21617 | 0.56878
|  | 14:59 | 19.3278 | 0.23468 | 0.56878
|  | 14:59 | 19.3289 | 0.25318 | 0.56878
|  | 14:59 | 19.33 | 0.25374 | 0.56878
|  | 14:59 | 19.3311 | 0.25429 | 0.56878
|  | 14:59 | 19.3322 | 0.25072 | 0.56877
|  | 14:59 | 19.3333 | 0.24301 | 0.56877
|  | 14:59 | 19.3344 | 0.2353 | 0.56877
|  | 15:00 | 19.3356 | 0.22758 | 0.56877
|  | 15:00 | 19.3367 | 0.21987 | 0.56876
|  | 15:00 | 19.3378 | 0.21216 | 0.56876
|  | 15:00 | 19.3389 | 0.20445 | 0.56876
|  | 15:00 | 19.34 | 0.19724 | 0.56876
|  | 15:00 | 19.3411 | 0.19151 | 0.56875
|  | 15:00 | 19.3422 | 0.18578 | 0.56875
|  | 15:00 | 19.3433 | 0.17437 | 0.56875
|  | 15:00 | 19.3444 | 0.1573 | 0.56875
|  | 15:00 | 19.3456 | 0.14022 | 0.56875
|  | 15:00 | 19.3467 | 0.12315 | 0.56874
|  | 15:00 | 19.3478 | 0.10608 | 0.56874
|  | 15:00 | 19.3489 | 0.090442 | 0.56874
|  | 15:00 | 19.35 | 0.07625 | 0.56874
|  | 15:00 | 19.3511 | 0.062058 | 0.56873
|  | 15:01 | 19.3522 | 0.055419 | 0.56873
|  | 15:01 | 19.3533 | 0.04878 | 0.56873
|  | 15:01 | 19.3544 | 0.044606 | 0.56873
|  | 15:01 | 19.3556 | 0.042897 | 0.56872
|  | 15:01 | 19.3567 | 0.041188 | 0.56872
|  | 15:01 | 19.3578 | 0.063227 | 0.56872
|  | 15:01 | 19.3589 | 0.085266 | 0.56872
|  | 15:01 | 19.36 | 0.10193 | 0.56872
|  | 15:01 | 19.3611 | 0.11321 | 0.56871
|  | 15:01 | 19.3622 | 0.12449 | 0.56871
|  | 15:01 | 19.3633 | 0.12296 | 0.56871
|  | 15:01 | 19.3644 | 0.12144 | 0.56871
|  | 15:01 | 19.3656 | 0.11876 | 0.5687
|  | 15:01 | 19.3667 | 0.11493 | 0.5687
|  | 15:01 | 19.3678 | 0.1111 | 0.5687
|  | 15:02 | 19.3689 | 0.11423 | 0.5687
|  | 15:02 | 19.37 | 0.11735 | 0.56869
|  | 15:02 | 19.3711 | 0.12048 | 0.56869
|  | 15:02 | 19.3722 | 0.1236 | 0.56869
|  | 15:02 | 19.3733 | 0.12673 | 0.56869
|  | 15:02 | 19.3744 | 0.12325 | 0.56869
|  | 15:02 | 19.3756 | 0.11977 | 0.56868
|  | 15:02 | 19.3767 | 0.11537 | 0.56868
|  | 15:02 | 19.3778 | 0.11004 | 0.56868
|  | 15:02 | 19.3789 | 0.10472 | 0.56868
|  | 15:02 | 19.38 | 0.10111 | 0.56867
|  | 15:02 | 19.3811 | 0.097508 | 0.56867
|  | 15:02 | 19.3822 | 0.088062 | 0.56867
|  | 15:02 | 19.3833 | 0.072776 | 0.56867
|  | 15:02 | 19.3844 | 0.057489 | 0.56866
|  | 15:03 | 19.3856 | 0.055737 | 0.56866
|  | 15:03 | 19.3867 | 0.053985 | 0.56866
|  | 15:03 | 19.3878 | 0.052233 | 0.56866
|  | 15:03 | 19.3889 | 0.050482 | 0.56866
|  | 15:03 | 19.39 | 0.04873 | 0.56865
|  | 15:03 | 19.3911 | 0.040214 | 0.56865
|  | 15:03 | 19.3922 | 0.031698 | 0.56865
|  | 15:03 | 19.3933 | 0.023997 | 0.56865
|  | 15:03 | 19.3944 | 0.017112 | 0.56864
|  | 15:03 | 19.3956 | 0.010227 | 0.56864
|  | 15:03 | 19.3967 | 0.0042347 | 0.56864
|  | 15:03 | 19.3978 | -0.0017577 | 0.56864
|  | 15:03 | 19.3989 | -0.006581 | 0.56863
|  | 15:03 | 19.4 | -0.010235 | 0.56863
|  | 15:03 | 19.4011 | -0.01389 | 0.56863
|  | 15:04 | 19.4022 | -0.020872 | 0.56863
|  | 15:04 | 19.4033 | -0.027855 | 0.56862
|  | 15:04 | 19.4044 | -0.037131 | 0.56862
|  | 15:04 | 19.4056 | -0.0487 | 0.56862
|  | 15:04 | 19.4067 | -0.060269 | 0.56862
|  | 15:04 | 19.4078 | -0.091023 | 0.56862
|  | 15:04 | 19.4089 | -0.12178 | 0.56861
|  | 15:04 | 19.41 | -0.14208 | 0.56861
|  | 15:04 | 19.4111 | -0.15192 | 0.56861
|  | 15:04 | 19.4122 | -0.16176 | 0.56861
|  | 15:04 | 19.4133 | -0.13817 | 0.5686
|  | 15:04 | 19.4144 | -0.11457 | 0.5686
|  | 15:04 | 19.4156 | -0.092907 | 0.5686
|  | 15:04 | 19.4167 | -0.073168 | 0.5686
|  | 15:04 | 19.4178 | -0.05343 | 0.56859
|  | 15:05 | 19.4189 | -0.033691 | 0.56859
|  | 15:05 | 19.42 | -0.013953 | 0.56859
|  | 15:05 | 19.4211 | 0.0092327 | 0.56859
|  | 15:05 | 19.4222 | 0.035866 | 0.56859
|  | 15:05 | 19.4233 | 0.062499 | 0.56858
|  | 15:05 | 19.4244 | 0.070131 | 0.56858
|  | 15:05 | 19.4256 | 0.077764 | 0.56858
|  | 15:05 | 19.4267 | 0.09189 | 0.56858
|  | 15:05 | 19.4278 | 0.11251 | 0.56857
|  | 15:05 | 19.4289 | 0.13313 | 0.56857
|  | 15:05 | 19.43 | 0.1587 | 0.56857
|  | 15:05 | 19.4311 | 0.18427 | 0.56857
|  | 15:05 | 19.4322 | 0.20728 | 0.56856
|  | 15:05 | 19.4333 | 0.22772 | 0.56856
|  | 15:05 | 19.4344 | 0.24817 | 0.56856
|  | 15:06 | 19.4356 | 0.26466 | 0.56856
|  | 15:06 | 19.4367 | 0.28116 | 0.56856
|  | 15:06 | 19.4378 | 0.29597 | 0.56855
|  | 15:06 | 19.4389 | 0.30908 | 0.56855
|  | 15:06 | 19.44 | 0.3222 | 0.56855
|  | 15:06 | 19.4411 | 0.33311 | 0.56855
|  | 15:06 | 19.4422 | 0.34402 | 0.56854
|  | 15:06 | 19.4433 | 0.35327 | 0.56854
|  | 15:06 | 19.4444 | 0.36086 | 0.56854
|  | 15:06 | 19.4456 | 0.36845 | 0.56854
|  | 15:06 | 19.4467 | 0.38068 | 0.56853
|  | 15:06 | 19.4478 | 0.39291 | 0.56853
|  | 15:06 | 19.4489 | 0.40661 | 0.56853
|  | 15:06 | 19.45 | 0.42179 | 0.56853
|  | 15:06 | 19.4511 | 0.43696 | 0.56853
|  | 15:07 | 19.4522 | 0.45213 | 0.56852
|  | 15:07 | 19.4533 | 0.4673 | 0.56852
|  | 15:07 | 19.4544 | 0.48281 | 0.56852
|  | 15:07 | 19.4556 | 0.49865 | 0.56852
|  | 15:07 | 19.4567 | 0.51449 | 0.56851
|  | 15:07 | 19.4578 | 0.45424 | 0.56851
|  | 15:07 | 19.4589 | 0.39399 | 0.56851
|  | 15:07 | 19.46 | 0.35648 | 0.56851
|  | 15:07 | 19.4611 | 0.3417 | 0.5685
|  | 15:07 | 19.4622 | 0.32693 | 0.5685
|  | 15:07 | 19.4633 | 0.32757 | 0.5685
|  | 15:07 | 19.4644 | 0.32822 | 0.5685
|  | 15:07 | 19.4656 | 0.33101 | 0.5685
|  | 15:07 | 19.4667 | 0.33595 | 0.56849
|  | 15:07 | 19.4678 | 0.34088 | 0.56849
|  | 15:08 | 19.4689 | 0.34346 | 0.56849
|  | 15:08 | 19.47 | 0.34603 | 0.56849
|  | 15:08 | 19.4711 | 0.3471 | 0.56848
|  | 15:08 | 19.4722 | 0.34666 | 0.56848
|  | 15:08 | 19.4733 | 0.34622 | 0.56848
|  | 15:08 | 19.4744 | 0.34578 | 0.56848
|  | 15:08 | 19.4756 | 0.34535 | 0.56847
|  | 15:08 | 19.4767 | 0.34491 | 0.56847
|  | 15:08 | 19.4778 | 0.34447 | 0.56847
|  | 15:08 | 19.4789 | 0.34403 | 0.56847
|  | 15:08 | 19.48 | 0.34283 | 0.56847
|  | 15:08 | 19.4811 | 0.34164 | 0.56846
|  | 15:08 | 19.4822 | 0.33898 | 0.56846
|  | 15:08 | 19.4833 | 0.33485 | 0.56846
|  | 15:08 | 19.4844 | 0.33073 | 0.56846
|  | 15:09 | 19.4856 | 0.32296 | 0.56845
|  | 15:09 | 19.4867 | 0.31518 | 0.56845
|  | 15:09 | 19.4878 | 0.3066 | 0.56845
|  | 15:09 | 19.4889 | 0.29721 | 0.56845
|  | 15:09 | 19.49 | 0.28783 | 0.56844
|  | 15:09 | 19.4911 | 0.27844 | 0.56844
|  | 15:09 | 19.4922 | 0.26905 | 0.56844
|  | 15:09 | 19.4933 | 0.26023 | 0.56844
|  | 15:09 | 19.4944 | 0.25197 | 0.56844
|  | 15:09 | 19.4956 | 0.24371 | 0.56843
|  | 15:09 | 19.4967 | 0.23856 | 0.56843
|  | 15:09 | 19.4978 | 0.23342 | 0.56843
|  | 15:09 | 19.4989 | 0.23487 | 0.56843
|  | 15:09 | 19.5 | 0.24292 | 0.56842
|  | 15:09 | 19.5011 | 0.25097 | 0.56842
|  | 15:10 | 19.5022 | 0.25557 | 0.56842
|  | 15:10 | 19.5033 | 0.26016 | 0.56842
|  | 15:10 | 19.5044 | 0.26126 | 0.56841
|  | 15:10 | 19.5056 | 0.25887 | 0.56841
|  | 15:10 | 19.5067 | 0.25649 | 0.56841
|  | 15:10 | 19.5078 | 0.18397 | 0.56841
|  | 15:10 | 19.5089 | 0.11145 | 0.56841
|  | 15:10 | 19.51 | 0.059998 | 0.5684
|  | 15:10 | 19.5111 | 0.029607 | 0.5684
|  | 15:10 | 19.5122 | -0.00078433 | 0.5684
|  | 15:10 | 19.5133 | -0.019188 | 0.5684
|  | 15:10 | 19.5144 | -0.025604 | 0.56839
|  | 15:10 | 19.5156 | -0.027446 | 0.56839
|  | 15:10 | 19.5167 | -0.024714 | 0.56839
|  | 15:10 | 19.5178 | -0.021982 | 0.56839
|  | 15:11 | 19.5189 | -0.012935 | 0.56838
|  | 15:11 | 19.52 | -0.0038869 | 0.56838
|  | 15:11 | 19.5211 | 0.0051607 | 0.56838
|  | 15:11 | 19.5222 | 0.014208 | 0.56838
|  | 15:11 | 19.5233 | 0.023256 | 0.56837
|  | 15:11 | 19.5244 | 0.030227 | 0.56837
|  | 15:11 | 19.5256 | 0.037198 | 0.56837
|  | 15:11 | 19.5267 | 0.043009 | 0.56837
|  | 15:11 | 19.5278 | 0.047662 | 0.56837
|  | 15:11 | 19.5289 | 0.052315 | 0.56836
|  | 15:11 | 19.53 | 0.05224 | 0.56836
|  | 15:11 | 19.5311 | 0.052165 | 0.56836
|  | 15:11 | 19.5322 | 0.049087 | 0.56836
|  | 15:11 | 19.5333 | 0.043007 | 0.56835
|  | 15:11 | 19.5344 | 0.036927 | 0.56835
|  | 15:12 | 19.5356 | 0.026022 | 0.56835
|  | 15:12 | 19.5367 | 0.015117 | 0.56835
|  | 15:12 | 19.5378 | 0.0042125 | 0.56834
|  | 15:12 | 19.5389 | -0.0066922 | 0.56834
|  | 15:12 | 19.54 | -0.017597 | 0.56834
|  | 15:12 | 19.5411 | -0.023325 | 0.56834
|  | 15:12 | 19.5422 | -0.029052 | 0.56834
|  | 15:12 | 19.5433 | -0.03146 | 0.56833
|  | 15:12 | 19.5444 | -0.030549 | 0.56833
|  | 15:12 | 19.5456 | -0.029637 | 0.56833
|  | 15:12 | 19.5467 | -0.023457 | 0.56833
|  | 15:12 | 19.5478 | -0.017276 | 0.56832
|  | 15:12 | 19.5489 | -0.0099999 | 0.56832
|  | 15:12 | 19.55 | -0.0016275 | 0.56832
|  | 15:12 | 19.5511 | 0.006745 | 0.56832
|  | 15:13 | 19.5522 | 0.013546 | 0.56831
|  | 15:13 | 19.5533 | 0.020348 | 0.56831
|  | 15:13 | 19.5544 | 0.026047 | 0.56831
|  | 15:13 | 19.5556 | 0.030645 | 0.56831
|  | 15:13 | 19.5567 | 0.035243 | 0.56831
|  | 15:13 | 19.5578 | -0.055773 | 0.5683
|  | 15:13 | 19.5589 | -0.14679 | 0.5683
|  | 15:13 | 19.56 | -0.2078 | 0.5683
|  | 15:13 | 19.5611 | -0.2388 | 0.5683
|  | 15:13 | 19.5622 | -0.26981 | 0.56829
|  | 15:13 | 19.5633 | -0.26367 | 0.56829
|  | 15:13 | 19.5644 | -0.25753 | 0.56829
|  | 15:13 | 19.5656 | -0.24763 | 0.56829
|  | 15:13 | 19.5667 | -0.23398 | 0.56828
|  | 15:13 | 19.5678 | -0.22032 | 0.56828
|  | 15:14 | 19.5689 | -0.20121 | 0.56828
|  | 15:14 | 19.57 | -0.1821 | 0.56828
|  | 15:14 | 19.5711 | -0.16395 | 0.56828
|  | 15:14 | 19.5722 | -0.14675 | 0.56827
|  | 15:14 | 19.5733 | -0.12955 | 0.56827
|  | 15:14 | 19.5744 | -0.11778 | 0.56827
|  | 15:14 | 19.5756 | -0.10601 | 0.56827
|  | 15:14 | 19.5767 | -0.097725 | 0.56826
|  | 15:14 | 19.5778 | -0.092925 | 0.56826
|  | 15:14 | 19.5789 | -0.088125 | 0.56826
|  | 15:14 | 19.58 | -0.089633 | 0.56826
|  | 15:14 | 19.5811 | -0.091142 | 0.56825
|  | 15:14 | 19.5822 | -0.095574 | 0.56825
|  | 15:14 | 19.5833 | -0.10293 | 0.56825
|  | 15:14 | 19.5844 | -0.11029 | 0.56825
|  | 15:15 | 19.5856 | -0.12483 | 0.56825
|  | 15:15 | 19.5867 | -0.13936 | 0.56824
|  | 15:15 | 19.5878 | -0.15726 | 0.56824
|  | 15:15 | 19.5889 | -0.17852 | 0.56824
|  | 15:15 | 19.59 | -0.19978 | 0.56824
|  | 15:15 | 19.5911 | -0.22103 | 0.56823
|  | 15:15 | 19.5922 | -0.24229 | 0.56823
|  | 15:15 | 19.5933 | -0.26218 | 0.56823
|  | 15:15 | 19.5944 | -0.28069 | 0.56823
|  | 15:15 | 19.5956 | -0.2992 | 0.56822
|  | 15:15 | 19.5967 | -0.31909 | 0.56822
|  | 15:15 | 19.5978 | -0.33898 | 0.56822
|  | 15:15 | 19.5989 | -0.35888 | 0.56822
|  | 15:15 | 19.6 | -0.37877 | 0.56822
|  | 15:15 | 19.6011 | -0.39866 | 0.56821
|  | 15:16 | 19.6022 | -0.40602 | 0.56821
|  | 15:16 | 19.6033 | -0.41337 | 0.56821
|  | 15:16 | 19.6044 | -0.41972 | 0.56821
|  | 15:16 | 19.6056 | -0.42506 | 0.5682
|  | 15:16 | 19.6067 | -0.43039 | 0.5682
|  | 15:16 | 19.6078 | -0.48458 | 0.5682
|  | 15:16 | 19.6089 | -0.53876 | 0.5682
|  | 15:16 | 19.61 | -0.5795 | 0.56819
|  | 15:16 | 19.6111 | -0.6068 | 0.56819
|  | 15:16 | 19.6122 | -0.63409 | 0.56819
|  | 15:16 | 19.6133 | -0.63528 | 0.56819
|  | 15:16 | 19.6144 | -0.63646 | 0.56819
|  | 15:16 | 19.6156 | -0.63504 | 0.56818
|  | 15:16 | 19.6167 | -0.631 | 0.56818
|  | 15:16 | 19.6178 | -0.62697 | 0.56818
|  | 15:17 | 19.6189 | -0.62293 | 0.56818
|  | 15:17 | 19.62 | -0.6189 | 0.56817
|  | 15:17 | 19.6211 | -0.61544 | 0.56817
|  | 15:17 | 19.6222 | -0.61256 | 0.56817
|  | 15:17 | 19.6233 | -0.60968 | 0.56817
|  | 15:17 | 19.6244 | -0.60679 | 0.56816
|  | 15:17 | 19.6256 | -0.60391 | 0.56816
|  | 15:17 | 19.6267 | -0.60054 | 0.56816
|  | 15:17 | 19.6278 | -0.59667 | 0.56816
|  | 15:17 | 19.6289 | -0.5928 | 0.56816
|  | 15:17 | 19.63 | -0.59102 | 0.56815
|  | 15:17 | 19.6311 | -0.58924 | 0.56815
|  | 15:17 | 19.6322 | -0.58896 | 0.56815
|  | 15:17 | 19.6333 | -0.5902 | 0.56815
|  | 15:17 | 19.6344 | -0.59144 | 0.56814
|  | 15:18 | 19.6356 | -0.59664 | 0.56814
|  | 15:18 | 19.6367 | -0.60185 | 0.56814
|  | 15:18 | 19.6378 | -0.61065 | 0.56814
|  | 15:18 | 19.6389 | -0.62304 | 0.56813
|  | 15:18 | 19.64 | -0.63542 | 0.56813
|  | 15:18 | 19.6411 | -0.64891 | 0.56813
|  | 15:18 | 19.6422 | -0.6624 | 0.56813
|  | 15:18 | 19.6433 | -0.6732 | 0.56812
|  | 15:18 | 19.6444 | -0.6813 | 0.56812
|  | 15:18 | 19.6456 | -0.68941 | 0.56812
|  | 15:18 | 19.6467 | -0.68981 | 0.56812
|  | 15:18 | 19.6478 | -0.69022 | 0.56812
|  | 15:18 | 19.6489 | -0.68727 | 0.56811
|  | 15:18 | 19.65 | -0.68098 | 0.56811
|  | 15:18 | 19.6511 | -0.67468 | 0.56811
|  | 15:19 | 19.6522 | -0.66251 | 0.56811
|  | 15:19 | 19.6533 | -0.65035 | 0.5681
|  | 15:19 | 19.6544 | -0.63818 | 0.5681
|  | 15:19 | 19.6556 | -0.62602 | 0.5681
|  | 15:19 | 19.6567 | -0.61385 | 0.5681
|  | 15:19 | 19.6578 | -0.5082 | 0.56809
|  | 15:19 | 19.6589 | -0.40255 | 0.56809
|  | 15:19 | 19.66 | -0.3128 | 0.56809
|  | 15:19 | 19.6611 | -0.23894 | 0.56809
|  | 15:19 | 19.6622 | -0.16508 | 0.56809
|  | 15:19 | 19.6633 | -0.13192 | 0.56808
|  | 15:19 | 19.6644 | -0.098767 | 0.56808
|  | 15:19 | 19.6656 | -0.076011 | 0.56808
|  | 15:19 | 19.6667 | -0.063653 | 0.56808
|  | 15:19 | 19.6678 | -0.051295 | 0.56807
|  | 15:20 | 19.6689 | -0.049098 | 0.56807
|  | 15:20 | 19.67 | -0.046901 | 0.56807
|  | 15:20 | 19.6711 | -0.047764 | 0.56807
|  | 15:20 | 19.6722 | -0.051687 | 0.56806
|  | 15:20 | 19.6733 | -0.05561 | 0.56806
|  | 15:20 | 19.6744 | -0.058509 | 0.56806
|  | 15:20 | 19.6756 | -0.061409 | 0.56806
|  | 15:20 | 19.6767 | -0.063271 | 0.56806
|  | 15:20 | 19.6778 | -0.064096 | 0.56805
|  | 15:20 | 19.6789 | -0.064921 | 0.56805
|  | 15:20 | 19.68 | -0.060995 | 0.56805
|  | 15:20 | 19.6811 | -0.057069 | 0.56805
|  | 15:20 | 19.6822 | -0.049778 | 0.56804
|  | 15:20 | 19.6833 | -0.03912 | 0.56804
|  | 15:20 | 19.6844 | -0.028462 | 0.56804
|  | 15:21 | 19.6856 | -0.012842 | 0.56804
|  | 15:21 | 19.6867 | 0.0027775 | 0.56803
|  | 15:21 | 19.6878 | 0.020036 | 0.56803
|  | 15:21 | 19.6889 | 0.038934 | 0.56803
|  | 15:21 | 19.69 | 0.057832 | 0.56803
|  | 15:21 | 19.6911 | 0.081885 | 0.56803
|  | 15:21 | 19.6922 | 0.10594 | 0.56802
|  | 15:21 | 19.6933 | 0.13145 | 0.56802
|  | 15:21 | 19.6944 | 0.15841 | 0.56802
|  | 15:21 | 19.6956 | 0.18538 | 0.56802
|  | 15:21 | 19.6967 | 0.21235 | 0.56801
|  | 15:21 | 19.6978 | 0.23931 | 0.56801
|  | 15:21 | 19.6989 | 0.26555 | 0.56801
|  | 15:21 | 19.7 | 0.29105 | 0.56801
|  | 15:21 | 19.7011 | 0.31656 | 0.568
|  | 15:22 | 19.7022 | 0.33831 | 0.568
|  | 15:22 | 19.7033 | 0.36005 | 0.568
|  | 15:22 | 19.7044 | 0.38041 | 0.568
|  | 15:22 | 19.7056 | 0.39939 | 0.568
|  | 15:22 | 19.7067 | 0.41836 | 0.56799
|  | 15:22 | 19.7078 | 0.49252 | 0.56799
|  | 15:22 | 19.7089 | 0.56668 | 0.56799
|  | 15:22 | 19.71 | 0.6571 | 0.56799
|  | 15:22 | 19.7111 | 0.76377 | 0.56798
|  | 15:22 | 19.7122 | 0.87045 | 0.56798
|  | 15:22 | 19.7133 | 0.92227 | 0.56798
|  | 15:22 | 19.7144 | 0.97409 | 0.56798
|  | 15:22 | 19.7156 | 1 | 0.56797
|  | 15:22 | 19.7167 | 1 | 0.56797
|  | 15:22 | 19.7178 | 1 | 0.56797
|  | 15:23 | 19.7189 | 1 | 0.56797
|  | 15:23 | 19.72 | 1 | 0.56797
|  | 15:23 | 19.7211 | 1 | 0.56796
|  | 15:23 | 19.7222 | 1 | 0.56796
|  | 15:23 | 19.7233 | 1 | 0.56796
|  | 15:23 | 19.7244 | 1 | 0.56796
|  | 15:23 | 19.7256 | 1 | 0.56795
|  | 15:23 | 19.7267 | 0.98954 | 0.56795
|  | 15:23 | 19.7278 | 0.96861 | 0.56795
|  | 15:23 | 19.7289 | 0.94769 | 0.56795
|  | 15:23 | 19.73 | 0.92676 | 0.56794
|  | 15:23 | 19.7311 | 0.90583 | 0.56794
|  | 15:23 | 19.7322 | 0.8864 | 0.56794
|  | 15:23 | 19.7333 | 0.86847 | 0.56794
|  | 15:23 | 19.7344 | 0.85053 | 0.56794
|  | 15:24 | 19.7356 | 0.83122 | 0.56793
|  | 15:24 | 19.7367 | 0.81191 | 0.56793
|  | 15:24 | 19.7378 | 0.79135 | 0.56793
|  | 15:24 | 19.7389 | 0.76954 | 0.56793
|  | 15:24 | 19.74 | 0.74773 | 0.56792
|  | 15:24 | 19.7411 | 0.72292 | 0.56792
|  | 15:24 | 19.7422 | 0.69812 | 0.56792
|  | 15:24 | 19.7433 | 0.67131 | 0.56792
|  | 15:24 | 19.7444 | 0.64249 | 0.56791
|  | 15:24 | 19.7456 | 0.61367 | 0.56791
|  | 15:24 | 19.7467 | 0.57951 | 0.56791
|  | 15:24 | 19.7478 | 0.54534 | 0.56791
|  | 15:24 | 19.7489 | 0.50935 | 0.56791
|  | 15:24 | 19.75 | 0.47155 | 0.5679
|  | 15:24 | 19.7511 | 0.43375 | 0.5679
|  | 15:25 | 19.7522 | 0.39595 | 0.5679
|  | 15:25 | 19.7533 | 0.35815 | 0.5679
|  | 15:25 | 19.7544 | 0.31997 | 0.56789
|  | 15:25 | 19.7556 | 0.28142 | 0.56789
|  | 15:25 | 19.7567 | 0.24286 | 0.56789
|  | 15:25 | 19.7578 | 0.24479 | 0.56789
|  | 15:25 | 19.7589 | 0.24671 | 0.56788
|  | 15:25 | 19.76 | 0.25085 | 0.56788
|  | 15:25 | 19.7611 | 0.2572 | 0.56788
|  | 15:25 | 19.7622 | 0.26356 | 0.56788
|  | 15:25 | 19.7633 | 0.27313 | 0.56787
|  | 15:25 | 19.7644 | 0.28271 | 0.56787
|  | 15:25 | 19.7656 | 0.28495 | 0.56787
|  | 15:25 | 19.7667 | 0.27985 | 0.56787
|  | 15:25 | 19.7678 | 0.27475 | 0.56787
|  | 15:26 | 19.7689 | 0.26163 | 0.56786
|  | 15:26 | 19.77 | 0.24851 | 0.56786
|  | 15:26 | 19.7711 | 0.23428 | 0.56786
|  | 15:26 | 19.7722 | 0.21894 | 0.56786
|  | 15:26 | 19.7733 | 0.20359 | 0.56785
|  | 15:26 | 19.7744 | 0.18825 | 0.56785
|  | 15:26 | 19.7756 | 0.1729 | 0.56785
|  | 15:26 | 19.7767 | 0.1591 | 0.56785
|  | 15:26 | 19.7778 | 0.14684 | 0.56784
|  | 15:26 | 19.7789 | 0.13458 | 0.56784
|  | 15:26 | 19.78 | 0.12808 | 0.56784
|  | 15:26 | 19.7811 | 0.12157 | 0.56784
|  | 15:26 | 19.7822 | 0.11705 | 0.56784
|  | 15:26 | 19.7833 | 0.1145 | 0.56783
|  | 15:26 | 19.7844 | 0.11195 | 0.56783
|  | 15:27 | 19.7856 | 0.1094 | 0.56783
|  | 15:27 | 19.7867 | 0.10685 | 0.56783
|  | 15:27 | 19.7878 | 0.10092 | 0.56782
|  | 15:27 | 19.7889 | 0.091628 | 0.56782
|  | 15:27 | 19.79 | 0.082333 | 0.56782
|  | 15:27 | 19.7911 | 0.065356 | 0.56782
|  | 15:27 | 19.7922 | 0.04838 | 0.56781
|  | 15:27 | 19.7933 | 0.028627 | 0.56781
|  | 15:27 | 19.7944 | 0.0060996 | 0.56781
|  | 15:27 | 19.7956 | -0.016428 | 0.56781
|  | 15:27 | 19.7967 | -0.041192 | 0.56781
|  | 15:27 | 19.7978 | -0.065955 | 0.5678
|  | 15:27 | 19.7989 | -0.089502 | 0.5678
|  | 15:27 | 19.8 | -0.11183 | 0.5678
|  | 15:27 | 19.8011 | -0.13416 | 0.5678
|  | 15:28 | 19.8022 | -0.15307 | 0.56779
|  | 15:28 | 19.8033 | -0.17199 | 0.56779
|  | 15:28 | 19.8044 | -0.18978 | 0.56779
|  | 15:28 | 19.8056 | -0.20644 | 0.56779
|  | 15:28 | 19.8067 | -0.2231 | 0.56778
|  | 15:28 | 19.8078 | -0.307 | 0.56778
|  | 15:28 | 19.8089 | -0.39091 | 0.56778
|  | 15:28 | 19.81 | -0.48385 | 0.56778
|  | 15:28 | 19.8111 | -0.58583 | 0.56778
|  | 15:28 | 19.8122 | -0.68781 | 0.56777
|  | 15:28 | 19.8133 | -0.73052 | 0.56777
|  | 15:28 | 19.8144 | -0.77322 | 0.56777
|  | 15:28 | 19.8156 | -0.81093 | 0.56777
|  | 15:28 | 19.8167 | -0.84365 | 0.56776
|  | 15:28 | 19.8178 | -0.87637 | 0.56776
|  | 15:29 | 19.8189 | -0.88153 | 0.56776
|  | 15:29 | 19.82 | -0.88668 | 0.56776
|  | 15:29 | 19.8211 | -0.88243 | 0.56775
|  | 15:29 | 19.8222 | -0.86877 | 0.56775
|  | 15:29 | 19.8233 | -0.85511 | 0.56775
|  | 15:29 | 19.8244 | -0.82921 | 0.56775
|  | 15:29 | 19.8256 | -0.80332 | 0.56775
|  | 15:29 | 19.8267 | -0.77541 | 0.56774
|  | 15:29 | 19.8278 | -0.74551 | 0.56774
|  | 15:29 | 19.8289 | -0.7156 | 0.56774
|  | 15:29 | 19.83 | -0.6914 | 0.56774
|  | 15:29 | 19.8311 | -0.6672 | 0.56773
|  | 15:29 | 19.8322 | -0.64581 | 0.56773
|  | 15:29 | 19.8333 | -0.62723 | 0.56773
|  | 15:29 | 19.8344 | -0.60865 | 0.56773
|  | 15:30 | 19.8356 | -0.59007 | 0.56772
|  | 15:30 | 19.8367 | -0.57149 | 0.56772
|  | 15:30 | 19.8378 | -0.55114 | 0.56772
|  | 15:30 | 19.8389 | -0.52902 | 0.56772
|  | 15:30 | 19.84 | -0.5069 | 0.56772
|  | 15:30 | 19.8411 | -0.48242 | 0.56771
|  | 15:30 | 19.8422 | -0.45793 | 0.56771
|  | 15:30 | 19.8433 | -0.43491 | 0.56771
|  | 15:30 | 19.8444 | -0.41335 | 0.56771
|  | 15:30 | 19.8456 | -0.39178 | 0.5677
|  | 15:30 | 19.8467 | -0.375 | 0.5677
|  | 15:30 | 19.8478 | -0.35821 | 0.5677
|  | 15:30 | 19.8489 | -0.34235 | 0.5677
|  | 15:30 | 19.85 | -0.3274 | 0.56769
|  | 15:30 | 19.8511 | -0.31245 | 0.56769
|  | 15:31 | 19.8522 | -0.29852 | 0.56769
|  | 15:31 | 19.8533 | -0.28459 | 0.56769
|  | 15:31 | 19.8544 | -0.27125 | 0.56769
|  | 15:31 | 19.8556 | -0.25849 | 0.56768
|  | 15:31 | 19.8567 | -0.24574 | 0.56768
|  | 15:31 | 19.8578 | -0.20166 | 0.56768
|  | 15:31 | 19.8589 | -0.15758 | 0.56768
|  | 15:31 | 19.86 | -0.11851 | 0.56767
|  | 15:31 | 19.8611 | -0.084442 | 0.56767
|  | 15:31 | 19.8622 | -0.050377 | 0.56767
|  | 15:31 | 19.8633 | -0.022386 | 0.56767
|  | 15:31 | 19.8644 | 0.0056038 | 0.56766
|  | 15:31 | 19.8656 | 0.030365 | 0.56766
|  | 15:31 | 19.8667 | 0.051896 | 0.56766
|  | 15:31 | 19.8678 | 0.073427 | 0.56766
|  | 15:32 | 19.8689 | 0.080815 | 0.56766
|  | 15:32 | 19.87 | 0.088202 | 0.56765
|  | 15:32 | 19.8711 | 0.090438 | 0.56765
|  | 15:32 | 19.8722 | 0.087522 | 0.56765
|  | 15:32 | 19.8733 | 0.084606 | 0.56765
|  | 15:32 | 19.8744 | 0.094047 | 0.56764
|  | 15:32 | 19.8756 | 0.10349 | 0.56764
|  | 15:32 | 19.8767 | 0.11293 | 0.56764
|  | 15:32 | 19.8778 | 0.12237 | 0.56764
|  | 15:32 | 19.8789 | 0.13181 | 0.56763
|  | 15:32 | 19.88 | 0.14249 | 0.56763
|  | 15:32 | 19.8811 | 0.15317 | 0.56763
|  | 15:32 | 19.8822 | 0.15848 | 0.56763
|  | 15:32 | 19.8833 | 0.15841 | 0.56762
|  | 15:32 | 19.8844 | 0.15835 | 0.56762
|  | 15:33 | 19.8856 | 0.16065 | 0.56762
|  | 15:33 | 19.8867 | 0.16295 | 0.56762
|  | 15:33 | 19.8878 | 0.16769 | 0.56762
|  | 15:33 | 19.8889 | 0.17489 | 0.56761
|  | 15:33 | 19.89 | 0.18208 | 0.56761
|  | 15:33 | 19.8911 | 0.18927 | 0.56761
|  | 15:33 | 19.8922 | 0.19647 | 0.56761
|  | 15:33 | 19.8933 | 0.20156 | 0.5676
|  | 15:33 | 19.8944 | 0.20456 | 0.5676
|  | 15:33 | 19.8956 | 0.20755 | 0.5676
|  | 15:33 | 19.8967 | 0.20601 | 0.5676
|  | 15:33 | 19.8978 | 0.20447 | 0.56759
|  | 15:33 | 19.8989 | 0.20292 | 0.56759
|  | 15:33 | 19.9 | 0.20138 | 0.56759
|  | 15:33 | 19.9011 | 0.19984 | 0.56759
|  | 15:34 | 19.9022 | 0.19624 | 0.56759
|  | 15:34 | 19.9033 | 0.19265 | 0.56758
|  | 15:34 | 19.9044 | 0.18905 | 0.56758
|  | 15:34 | 19.9056 | 0.18546 | 0.56758
|  | 15:34 | 19.9067 | 0.18186 | 0.56758
|  | 15:34 | 19.9078 | 0.20655 | 0.56757
|  | 15:34 | 19.9089 | 0.23125 | 0.56757
|  | 15:34 | 19.91 | 0.27878 | 0.56757
|  | 15:34 | 19.9111 | 0.34917 | 0.56757
|  | 15:34 | 19.9122 | 0.41955 | 0.56756
|  | 15:34 | 19.9133 | 0.46532 | 0.56756
|  | 15:34 | 19.9144 | 0.51109 | 0.56756
|  | 15:34 | 19.9156 | 0.54332 | 0.56756
|  | 15:34 | 19.9167 | 0.562 | 0.56756
|  | 15:34 | 19.9178 | 0.58068 | 0.56755
|  | 15:35 | 19.9189 | 0.57944 | 0.56755
|  | 15:35 | 19.92 | 0.57819 | 0.56755
|  | 15:35 | 19.9211 | 0.56968 | 0.56755
|  | 15:35 | 19.9222 | 0.55389 | 0.56754
|  | 15:35 | 19.9233 | 0.53811 | 0.56754
|  | 15:35 | 19.9244 | 0.5166 | 0.56754
|  | 15:35 | 19.9256 | 0.49509 | 0.56754
|  | 15:35 | 19.9267 | 0.47205 | 0.56753
|  | 15:35 | 19.9278 | 0.44748 | 0.56753
|  | 15:35 | 19.9289 | 0.4229 | 0.56753
|  | 15:35 | 19.93 | 0.39623 | 0.56753
|  | 15:35 | 19.9311 | 0.36956 | 0.56753
|  | 15:35 | 19.9322 | 0.34288 | 0.56752
|  | 15:35 | 19.9333 | 0.31621 | 0.56752
|  | 15:35 | 19.9344 | 0.28954 | 0.56752
|  | 15:36 | 19.9356 | 0.26391 | 0.56752
|  | 15:36 | 19.9367 | 0.23828 | 0.56751
|  | 15:36 | 19.9378 | 0.21539 | 0.56751
|  | 15:36 | 19.9389 | 0.19522 | 0.56751
|  | 15:36 | 19.94 | 0.17506 | 0.56751
|  | 15:36 | 19.9411 | 0.16063 | 0.5675
|  | 15:36 | 19.9422 | 0.1462 | 0.5675
|  | 15:36 | 19.9433 | 0.13361 | 0.5675
|  | 15:36 | 19.9444 | 0.12286 | 0.5675
|  | 15:36 | 19.9456 | 0.11211 | 0.5675
|  | 15:36 | 19.9467 | 0.10243 | 0.56749
|  | 15:36 | 19.9478 | 0.092755 | 0.56749
|  | 15:36 | 19.9489 | 0.083078 | 0.56749
|  | 15:36 | 19.95 | 0.073402 | 0.56749
|  | 15:36 | 19.9511 | 0.063725 | 0.56748
|  | 15:37 | 19.9522 | 0.052588 | 0.56748
|  | 15:37 | 19.9533 | 0.041452 | 0.56748
|  | 15:37 | 19.9544 | 0.029734 | 0.56748
|  | 15:37 | 19.9556 | 0.017436 | 0.56747
|  | 15:37 | 19.9567 | 0.0051383 | 0.56747
|  | 15:37 | 19.9578 | -0.047343 | 0.56747
|  | 15:37 | 19.9589 | -0.099824 | 0.56747
|  | 15:37 | 19.96 | -0.16798 | 0.56747
|  | 15:37 | 19.9611 | -0.25181 | 0.56746
|  | 15:37 | 19.9622 | -0.33565 | 0.56746
|  | 15:37 | 19.9633 | -0.38735 | 0.56746
|  | 15:37 | 19.9644 | -0.43905 | 0.56746
|  | 15:37 | 19.9656 | -0.46146 | 0.56745
|  | 15:37 | 19.9667 | -0.4546 | 0.56745
|  | 15:37 | 19.9678 | -0.44773 | 0.56745
|  | 15:38 | 19.9689 | -0.4553 | 0.56745
|  | 15:38 | 19.97 | -0.46287 | 0.56744
|  | 15:38 | 19.9711 | -0.46802 | 0.56744
|  | 15:38 | 19.9722 | -0.47074 | 0.56744
|  | 15:38 | 19.9733 | -0.47346 | 0.56744
|  | 15:38 | 19.9744 | -0.46975 | 0.56744
|  | 15:38 | 19.9756 | -0.46605 | 0.56743
|  | 15:38 | 19.9767 | -0.45952 | 0.56743
|  | 15:38 | 19.9778 | -0.45017 | 0.56743
|  | 15:38 | 19.9789 | -0.44081 | 0.56743
|  | 15:38 | 19.98 | -0.43146 | 0.56742
|  | 15:38 | 19.9811 | -0.42211 | 0.56742
|  | 15:38 | 19.9822 | -0.41339 | 0.56742
|  | 15:38 | 19.9833 | -0.4053 | 0.56742
|  | 15:38 | 19.9844 | -0.39721 | 0.56741
|  | 15:39 | 19.9856 | -0.39273 | 0.56741
|  | 15:39 | 19.9867 | -0.38824 | 0.56741
|  | 15:39 | 19.9878 | -0.38311 | 0.56741
|  | 15:39 | 19.9889 | -0.37733 | 0.56741
|  | 15:39 | 19.99 | -0.37154 | 0.5674
|  | 15:39 | 19.9911 | -0.36405 | 0.5674
|  | 15:39 | 19.9922 | -0.35655 | 0.5674
|  | 15:39 | 19.9933 | -0.34838 | 0.5674
|  | 15:39 | 19.9944 | -0.33951 | 0.56739
|  | 15:39 | 19.9956 | -0.33065 | 0.56739
|  | 15:39 | 19.9967 | -0.31883 | 0.56739
|  | 15:39 | 19.9978 | -0.307 | 0.56739
|  | 15:39 | 19.9989 | -0.29517 | 0.56738
|  | 15:39 | 20 | -0.28334 | 0.56738
|  | 15:39 | 20.0011 | -0.27152 | 0.56738
|  | 15:40 | 20.0022 | -0.26255 | 0.56738
|  | 15:40 | 20.0033 | -0.25357 | 0.56737
|  | 15:40 | 20.0044 | -0.2446 | 0.56737
|  | 15:40 | 20.0056 | -0.23563 | 0.56737
|  | 15:40 | 20.0067 | -0.22666 | 0.56737
|  | 15:40 | 20.0078 | -0.16623 | 0.56737
|  | 15:40 | 20.0089 | -0.1058 | 0.56736
|  | 15:40 | 20.01 | -0.07499 | 0.56736
|  | 15:40 | 20.0111 | -0.073793 | 0.56736
|  | 15:40 | 20.0122 | -0.072596 | 0.56736
|  | 15:40 | 20.0133 | -0.090676 | 0.56735
|  | 15:40 | 20.0144 | -0.10876 | 0.56735
|  | 15:40 | 20.0156 | -0.11992 | 0.56735
|  | 15:40 | 20.0167 | -0.12415 | 0.56735
|  | 15:40 | 20.0178 | -0.12839 | 0.56734
|  | 15:41 | 20.0189 | -0.12273 | 0.56734
|  | 15:41 | 20.02 | -0.11707 | 0.56734
|  | 15:41 | 20.0211 | -0.10836 | 0.56734
|  | 15:41 | 20.0222 | -0.096607 | 0.56734
|  | 15:41 | 20.0233 | -0.084855 | 0.56733
|  | 15:41 | 20.0244 | -0.073102 | 0.56733
|  | 15:41 | 20.0256 | -0.06135 | 0.56733
|  | 15:41 | 20.0267 | -0.048189 | 0.56733
|  | 15:41 | 20.0278 | -0.033621 | 0.56732
|  | 15:41 | 20.0289 | -0.019053 | 0.56732
|  | 15:41 | 20.03 | 0.00090471 | 0.56732
|  | 15:41 | 20.0311 | 0.020862 | 0.56732
|  | 15:41 | 20.0322 | 0.037016 | 0.56731
|  | 15:41 | 20.0333 | 0.049365 | 0.56731
|  | 15:41 | 20.0344 | 0.061714 | 0.56731
|  | 15:42 | 20.0356 | 0.066209 | 0.56731
|  | 15:42 | 20.0367 | 0.070704 | 0.56731
|  | 15:42 | 20.0378 | 0.084585 | 0.5673
|  | 15:42 | 20.0389 | 0.10785 | 0.5673
|  | 15:42 | 20.04 | 0.13112 | 0.5673
|  | 15:42 | 20.0411 | 0.15088 | 0.5673
|  | 15:42 | 20.0422 | 0.17065 | 0.56729
|  | 15:42 | 20.0433 | 0.18854 | 0.56729
|  | 15:42 | 20.0444 | 0.20455 | 0.56729
|  | 15:42 | 20.0456 | 0.22055 | 0.56729
|  | 15:42 | 20.0467 | 0.23139 | 0.56728
|  | 15:42 | 20.0478 | 0.24222 | 0.56728
|  | 15:42 | 20.0489 | 0.25077 | 0.56728
|  | 15:42 | 20.05 | 0.25703 | 0.56728
|  | 15:42 | 20.0511 | 0.2633 | 0.56728
|  | 15:43 | 20.0522 | 0.26956 | 0.56727
|  | 15:43 | 20.0533 | 0.27582 | 0.56727
|  | 15:43 | 20.0544 | 0.28117 | 0.56727
|  | 15:43 | 20.0556 | 0.28561 | 0.56727
|  | 15:43 | 20.0567 | 0.29004 | 0.56726
|  | 15:43 | 20.0578 | 0.43182 | 0.56726
|  | 15:43 | 20.0589 | 0.5736 | 0.56726
|  | 15:43 | 20.06 | 0.70993 | 0.56726
|  | 15:43 | 20.0611 | 0.8408 | 0.56725
|  | 15:43 | 20.0622 | 0.97168 | 0.56725
|  | 15:43 | 20.0633 | 0.98301 | 0.56725
|  | 15:43 | 20.0644 | 0.99434 | 0.56725
|  | 15:43 | 20.0656 | 1 | 0.56725
|  | 15:43 | 20.0667 | 1 | 0.56724
|  | 15:43 | 20.0678 | 1 | 0.56724
|  | 15:44 | 20.0689 | 1 | 0.56724
|  | 15:44 | 20.07 | 1 | 0.56724
|  | 15:44 | 20.0711 | 1 | 0.56723
|  | 15:44 | 20.0722 | 1 | 0.56723
|  | 15:44 | 20.0733 | 1 | 0.56723
|  | 15:44 | 20.0744 | 1 | 0.56723
|  | 15:44 | 20.0756 | 1 | 0.56722
|  | 15:44 | 20.0767 | 0.98087 | 0.56722
|  | 15:44 | 20.0778 | 0.9426 | 0.56722
|  | 15:44 | 20.0789 | 0.90433 | 0.56722
|  | 15:44 | 20.08 | 0.86072 | 0.56722
|  | 15:44 | 20.0811 | 0.81711 | 0.56721
|  | 15:44 | 20.0822 | 0.7735 | 0.56721
|  | 15:44 | 20.0833 | 0.72989 | 0.56721
|  | 15:44 | 20.0844 | 0.68628 | 0.56721
|  | 15:45 | 20.0856 | 0.64501 | 0.5672
|  | 15:45 | 20.0867 | 0.60374 | 0.5672
|  | 15:45 | 20.0878 | 0.56015 | 0.5672
|  | 15:45 | 20.0889 | 0.51423 | 0.5672
|  | 15:45 | 20.09 | 0.46832 | 0.56719
|  | 15:45 | 20.0911 | 0.415 | 0.56719
|  | 15:45 | 20.0922 | 0.36168 | 0.56719
|  | 15:45 | 20.0933 | 0.30515 | 0.56719
|  | 15:45 | 20.0944 | 0.24542 | 0.56719
|  | 15:45 | 20.0956 | 0.18569 | 0.56718
|  | 15:45 | 20.0967 | 0.1229 | 0.56718
|  | 15:45 | 20.0978 | 0.060104 | 0.56718
|  | 15:45 | 20.0989 | -0.0026872 | 0.56718
|  | 15:45 | 20.1 | -0.065478 | 0.56717
|  | 15:45 | 20.1011 | -0.12827 | 0.56717
|  | 15:46 | 20.1022 | -0.18722 | 0.56717
|  | 15:46 | 20.1033 | -0.24617 | 0.56717
|  | 15:46 | 20.1044 | -0.30138 | 0.56716
|  | 15:46 | 20.1056 | -0.35284 | 0.56716
|  | 15:46 | 20.1067 | -0.4043 | 0.56716
|  | 15:46 | 20.1078 | -0.50607 | 0.56716
|  | 15:46 | 20.1089 | -0.60784 | 0.56716
|  | 15:46 | 20.11 | -0.72698 | 0.56715
|  | 15:46 | 20.1111 | -0.86349 | 0.56715
|  | 15:46 | 20.1122 | -1 | 0.56715
|  | 15:46 | 20.1133 | -1 | 0.56715
|  | 15:46 | 20.1144 | -1 | 0.56714
|  | 15:46 | 20.1156 | -1 | 0.56714
|  | 15:46 | 20.1167 | -1 | 0.56714
|  | 15:46 | 20.1178 | -1 | 0.56714
|  | 15:47 | 20.1189 | -1 | 0.56713
|  | 15:47 | 20.12 | -1 | 0.56713
|  | 15:47 | 20.1211 | -1 | 0.56713
|  | 15:47 | 20.1222 | -1 | 0.56713
|  | 15:47 | 20.1233 | -1 | 0.56712
|  | 15:47 | 20.1244 | -1 | 0.56712
|  | 15:47 | 20.1256 | -1 | 0.56712
|  | 15:47 | 20.1267 | -1 | 0.56712
|  | 15:47 | 20.1278 | -1 | 0.56712
|  | 15:47 | 20.1289 | -1 | 0.56711
|  | 15:47 | 20.13 | -1 | 0.56711
|  | 15:47 | 20.1311 | -1 | 0.56711
|  | 15:47 | 20.1322 | -1 | 0.56711
|  | 15:47 | 20.1333 | -1 | 0.5671
|  | 15:47 | 20.1344 | -1 | 0.5671
|  | 15:48 | 20.1356 | -1 | 0.5671
|  | 15:48 | 20.1367 | -1 | 0.5671
|  | 15:48 | 20.1378 | -1 | 0.56709
|  | 15:48 | 20.1389 | -1 | 0.56709
|  | 15:48 | 20.14 | -1 | 0.56709
|  | 15:48 | 20.1411 | -1 | 0.56709
|  | 15:48 | 20.1422 | -1 | 0.56709
|  | 15:48 | 20.1433 | -1 | 0.56708
|  | 15:48 | 20.1444 | -1 | 0.56708
|  | 15:48 | 20.1456 | -1 | 0.56708
|  | 15:48 | 20.1467 | -1 | 0.56708
|  | 15:48 | 20.1478 | -1 | 0.56707
|  | 15:48 | 20.1489 | -0.97871 | 0.56707
|  | 15:48 | 20.15 | -0.93612 | 0.56707
|  | 15:48 | 20.1511 | -0.89353 | 0.56707
|  | 15:49 | 20.1522 | -0.82905 | 0.56706
|  | 15:49 | 20.1533 | -0.76457 | 0.56706
|  | 15:49 | 20.1544 | -0.70261 | 0.56706
|  | 15:49 | 20.1556 | -0.64317 | 0.56706
|  | 15:49 | 20.1567 | -0.58372 | 0.56706
|  | 15:49 | 20.1578 | -0.38857 | 0.56705
|  | 15:49 | 20.1589 | -0.19341 | 0.56705
|  | 15:49 | 20.16 | 0.014714 | 0.56705
|  | 15:49 | 20.1611 | 0.23582 | 0.56705
|  | 15:49 | 20.1622 | 0.45692 | 0.56704
|  | 15:49 | 20.1633 | 0.62776 | 0.56704
|  | 15:49 | 20.1644 | 0.79861 | 0.56704
|  | 15:49 | 20.1656 | 0.90723 | 0.56704
|  | 15:49 | 20.1667 | 0.95361 | 0.56703
|  | 15:49 | 20.1678 | 1 | 0.56703
|  | 15:50 | 20.1689 | 1 | 0.56703
|  | 15:50 | 20.17 | 1 | 0.56703
|  | 15:50 | 20.1711 | 1 | 0.56703
|  | 15:50 | 20.1722 | 1 | 0.56702
|  | 15:50 | 20.1733 | 1 | 0.56702
|  | 15:50 | 20.1744 | 1 | 0.56702
|  | 15:50 | 20.1756 | 1 | 0.56702
|  | 15:50 | 20.1767 | 0.98722 | 0.56701
|  | 15:50 | 20.1778 | 0.96167 | 0.56701
|  | 15:50 | 20.1789 | 0.93612 | 0.56701
|  | 15:50 | 20.18 | 0.90241 | 0.56701
|  | 15:50 | 20.1811 | 0.8687 | 0.567
|  | 15:50 | 20.1822 | 0.83718 | 0.567
|  | 15:50 | 20.1833 | 0.80786 | 0.567
|  | 15:50 | 20.1844 | 0.77854 | 0.567
|  | 15:51 | 20.1856 | 0.7506 | 0.567
|  | 15:51 | 20.1867 | 0.72267 | 0.56699
|  | 15:51 | 20.1878 | 0.69439 | 0.56699
|  | 15:51 | 20.1889 | 0.66577 | 0.56699
|  | 15:51 | 20.19 | 0.63714 | 0.56699
|  | 15:51 | 20.1911 | 0.60852 | 0.56698
|  | 15:51 | 20.1922 | 0.57989 | 0.56698
|  | 15:51 | 20.1933 | 0.55235 | 0.56698
|  | 15:51 | 20.1944 | 0.52591 | 0.56698
|  | 15:51 | 20.1956 | 0.49946 | 0.56697
|  | 15:51 | 20.1967 | 0.47076 | 0.56697
|  | 15:51 | 20.1978 | 0.44206 | 0.56697
|  | 15:51 | 20.1989 | 0.41336 | 0.56697
|  | 15:51 | 20.2 | 0.38465 | 0.56697
|  | 15:51 | 20.2011 | 0.35595 | 0.56696
|  | 15:52 | 20.2022 | 0.32262 | 0.56696
|  | 15:52 | 20.2033 | 0.28929 | 0.56696
|  | 15:52 | 20.2044 | 0.25344 | 0.56696
|  | 15:52 | 20.2056 | 0.21507 | 0.56695
|  | 15:52 | 20.2067 | 0.1767 | 0.56695
|  | 15:52 | 20.2078 | 0.24757 | 0.56695
|  | 15:52 | 20.2089 | 0.31844 | 0.56695
|  | 15:52 | 20.21 | 0.37238 | 0.56694
|  | 15:52 | 20.2111 | 0.40939 | 0.56694
|  | 15:52 | 20.2122 | 0.4464 | 0.56694
|  | 15:52 | 20.2133 | 0.45446 | 0.56694
|  | 15:52 | 20.2144 | 0.46253 | 0.56694
|  | 15:52 | 20.2156 | 0.45695 | 0.56693
|  | 15:52 | 20.2167 | 0.43773 | 0.56693
|  | 15:52 | 20.2178 | 0.4185 | 0.56693
|  | 15:53 | 20.2189 | 0.38503 | 0.56693
|  | 15:53 | 20.22 | 0.35155 | 0.56692
|  | 15:53 | 20.2211 | 0.31506 | 0.56692
|  | 15:53 | 20.2222 | 0.27554 | 0.56692
|  | 15:53 | 20.2233 | 0.23602 | 0.56692
|  | 15:53 | 20.2244 | 0.19841 | 0.56691
|  | 15:53 | 20.2256 | 0.1608 | 0.56691
|  | 15:53 | 20.2267 | 0.12102 | 0.56691
|  | 15:53 | 20.2278 | 0.080516 | 0.56691
|  | 15:53 | 20.2289 | 0.041959 | 0.56691
|  | 15:53 | 20.23 | 0.0092477 | 0.5669
|  | 15:53 | 20.2311 | -0.023463 | 0.5669
|  | 15:53 | 20.2322 | -0.045612 | 0.5669
|  | 15:53 | 20.2333 | -0.06424 | 0.5669
|  | 15:53 | 20.2344 | -0.080306 | 0.56689
|  | 15:54 | 20.2356 | -0.088686 | 0.56689
|  | 15:54 | 20.2367 | -0.097065 | 0.56689
|  | 15:54 | 20.2378 | -0.10018 | 0.56689
|  | 15:54 | 20.2389 | -0.10153 | 0.56688
|  | 15:54 | 20.24 | -0.10262 | 0.56688
|  | 15:54 | 20.2411 | -0.10291 | 0.56688
|  | 15:54 | 20.2422 | -0.10321 | 0.56688
|  | 15:54 | 20.2433 | -0.10502 | 0.56687
|  | 15:54 | 20.2444 | -0.10735 | 0.56687
|  | 15:54 | 20.2456 | -0.10967 | 0.56687
|  | 15:54 | 20.2467 | -0.11199 | 0.56687
|  | 15:54 | 20.2478 | -0.11432 | 0.56687
|  | 15:54 | 20.2489 | -0.11297 | 0.56686
|  | 15:54 | 20.25 | -0.1104 | 0.56686
|  | 15:54 | 20.2511 | -0.10631 | 0.56686
|  | 15:55 | 20.2522 | -0.097698 | 0.56686
|  | 15:55 | 20.2533 | -0.089082 | 0.56685
|  | 15:55 | 20.2544 | -0.077714 | 0.56685
|  | 15:55 | 20.2556 | -0.065428 | 0.56685
|  | 15:55 | 20.2567 | -0.058191 | 0.56685
|  | 15:55 | 20.2578 | -0.066102 | 0.56684
|  | 15:55 | 20.2589 | -0.074013 | 0.56684
|  | 15:55 | 20.26 | -0.081924 | 0.56684
|  | 15:55 | 20.2611 | -0.089834 | 0.56684
|  | 15:55 | 20.2622 | -0.095008 | 0.56684
|  | 15:55 | 20.2633 | -0.091969 | 0.56683
|  | 15:55 | 20.2644 | -0.08893 | 0.56683
|  | 15:55 | 20.2656 | -0.082126 | 0.56683
|  | 15:55 | 20.2667 | -0.074067 | 0.56683
|  | 15:55 | 20.2678 | -0.062682 | 0.56682
|  | 15:56 | 20.2689 | -0.041321 | 0.56682
|  | 15:56 | 20.27 | -0.01996 | 0.56682
|  | 15:56 | 20.2711 | 0.00025003 | 0.56682
|  | 15:56 | 20.2722 | 0.020076 | 0.56681
|  | 15:56 | 20.2733 | 0.038548 | 0.56681
|  | 15:56 | 20.2744 | 0.052958 | 0.56681
|  | 15:56 | 20.2756 | 0.067367 | 0.56681
|  | 15:56 | 20.2767 | 0.075013 | 0.56681
|  | 15:56 | 20.2778 | 0.080404 | 0.5668
|  | 15:56 | 20.2789 | 0.083676 | 0.5668
|  | 15:56 | 20.28 | 0.080591 | 0.5668
|  | 15:56 | 20.2811 | 0.077506 | 0.5668
|  | 15:56 | 20.2822 | 0.073421 | 0.56679
|  | 15:56 | 20.2833 | 0.069002 | 0.56679
|  | 15:56 | 20.2844 | 0.065085 | 0.56679
|  | 15:57 | 20.2856 | 0.062669 | 0.56679
|  | 15:57 | 20.2867 | 0.060253 | 0.56678
|  | 15:57 | 20.2878 | 0.056999 | 0.56678
|  | 15:57 | 20.2889 | 0.053465 | 0.56678
|  | 15:57 | 20.29 | 0.049646 | 0.56678
|  | 15:57 | 20.2911 | 0.044971 | 0.56678
|  | 15:57 | 20.2922 | 0.040297 | 0.56677
|  | 15:57 | 20.2933 | 0.036583 | 0.56677
|  | 15:57 | 20.2944 | 0.033188 | 0.56677
|  | 15:57 | 20.2956 | 0.02929 | 0.56677
|  | 15:57 | 20.2967 | 0.02388 | 0.56676
|  | 15:57 | 20.2978 | 0.018471 | 0.56676
|  | 15:57 | 20.2989 | 0.013062 | 0.56676
|  | 15:57 | 20.3 | 0.0076527 | 0.56676
|  | 15:57 | 20.3011 | 0.003055 | 0.56675
|  | 15:58 | 20.3022 | 0.00089172 | 0.56675
|  | 15:58 | 20.3033 | -0.0012716 | 0.56675
|  | 15:58 | 20.3044 | 0.0015097 | 0.56675
|  | 15:58 | 20.3056 | 0.0059392 | 0.56675
|  | 15:58 | 20.3067 | 0.016653 | 0.56674
|  | 15:58 | 20.3078 | 0.04622 | 0.56674
|  | 15:58 | 20.3089 | 0.075788 | 0.56674
|  | 15:58 | 20.31 | 0.17855 | 0.56674
|  | 15:58 | 20.3111 | 0.30572 | 0.56673
|  | 15:58 | 20.3122 | 0.4228 | 0.56673
|  | 15:58 | 20.3133 | 0.50962 | 0.56673
|  | 15:58 | 20.3144 | 0.59644 | 0.56673
|  | 15:58 | 20.3156 | 0.64934 | 0.56672
|  | 15:58 | 20.3167 | 0.69095 | 0.56672
|  | 15:58 | 20.3178 | 0.72519 | 0.56672
|  | 15:59 | 20.3189 | 0.73735 | 0.56672
|  | 15:59 | 20.32 | 0.74951 | 0.56672
|  | 15:59 | 20.3211 | 0.74882 | 0.56671
|  | 15:59 | 20.3222 | 0.74385 | 0.56671
|  | 15:59 | 20.3233 | 0.73645 | 0.56671
|  | 15:59 | 20.3244 | 0.72177 | 0.56671
|  | 15:59 | 20.3256 | 0.70709 | 0.5667
|  | 15:59 | 20.3267 | 0.68715 | 0.5667
|  | 15:59 | 20.3278 | 0.66545 | 0.5667
|  | 15:59 | 20.3289 | 0.64111 | 0.5667
|  | 15:59 | 20.33 | 0.60884 | 0.56669
|  | 15:59 | 20.3311 | 0.57657 | 0.56669
|  | 15:59 | 20.3322 | 0.54106 | 0.56669
|  | 15:59 | 20.3333 | 0.50447 | 0.56669
|  | 15:59 | 20.3344 | 0.47098 | 0.56669
|  | 16:00 | 20.3356 | 0.44679 | 0.56668
|  | 16:00 | 20.3367 | 0.4226 | 0.56668
|  | 16:00 | 20.3378 | 0.40427 | 0.56668
|  | 16:00 | 20.3389 | 0.3879 | 0.56668
|  | 16:00 | 20.34 | 0.37223 | 0.56667
|  | 16:00 | 20.3411 | 0.35868 | 0.56667
|  | 16:00 | 20.3422 | 0.34514 | 0.56667
|  | 16:00 | 20.3433 | -0.14425 | 0.56667
|  | 16:00 | 20.3444 | -0.12965 | 0.56666
|  | 16:00 | 20.3456 | -0.13601 | 0.56666
|  | 16:00 | 20.3467 | -0.14238 | 0.56666
|  | 16:00 | 20.3478 | -0.14874 | 0.56666
|  | 16:00 | 20.3489 | -0.15511 | 0.56666
|  | 16:00 | 20.35 | -0.16147 | 0.56665
|  | 16:00 | 20.3511 | -0.15001 | 0.56665
|  | 16:01 | 20.3522 | -0.13855 | 0.56665
|  | 16:01 | 20.3533 | -0.11353 | 0.56665
|  | 16:01 | 20.3544 | -0.083978 | 0.56664
|  | 16:01 | 20.3556 | -0.05443 | 0.56664
|  | 16:01 | 20.3567 | -0.032121 | 0.56664
|  | 16:01 | 20.3578 | -0.0098121 | 0.56664
|  | 16:01 | 20.3589 | 0.0050135 | 0.56663
|  | 16:01 | 20.36 | 0.012356 | 0.56663
|  | 16:01 | 20.3611 | 0.019698 | 0.56663
|  | 16:01 | 20.3622 | 0.0056427 | 0.56663
|  | 16:01 | 20.3633 | -0.0084124 | 0.56662
|  | 16:01 | 20.3644 | -0.016135 | 0.56662
|  | 16:01 | 20.3656 | -0.017526 | 0.56662
|  | 16:01 | 20.3667 | -0.018917 | 0.56662
|  | 16:01 | 20.3678 | -0.0074832 | 0.56662
|  | 16:02 | 20.3689 | 0.0039504 | 0.56661
|  | 16:02 | 20.37 | 0.016937 | 0.56661
|  | 16:02 | 20.3711 | 0.030441 | 0.56661
|  | 16:02 | 20.3722 | 0.043946 | 0.56661
|  | 16:02 | 20.3733 | 0.065859 | 0.5666
|  | 16:02 | 20.3744 | 0.087772 | 0.5666
|  | 16:02 | 20.3756 | 0.10268 | 0.5666
|  | 16:02 | 20.3767 | 0.11526 | 0.5666
|  | 16:02 | 20.3778 | 0.12783 | 0.56659
|  | 16:02 | 20.3789 | 0.13629 | 0.56659
|  | 16:02 | 20.38 | 0.14474 | 0.56659
|  | 16:02 | 20.3811 | 0.1681 | 0.56659
|  | 16:02 | 20.3822 | 0.20635 | 0.56659
|  | 16:02 | 20.3833 | 0.2446 | 0.56658
|  | 16:02 | 20.3844 | 0.28614 | 0.56658
|  | 16:03 | 20.3856 | 0.32769 | 0.56658
|  | 16:03 | 20.3867 | 0.37177 | 0.56658
|  | 16:03 | 20.3878 | 0.41839 | 0.56657
|  | 16:03 | 20.3889 | 0.4646 | 0.56657
|  | 16:03 | 20.39 | 0.50955 | 0.56657
|  | 16:03 | 20.3911 | 0.55451 | 0.56657
|  | 16:03 | 20.3922 | 0.60292 | 0.56656
|  | 16:03 | 20.3933 | 0.65481 | 0.56656
|  | 16:03 | 20.3944 | 0.70669 | 0.56656
|  | 16:03 | 20.3956 | 0.72091 | 0.56656
|  | 16:03 | 20.3967 | 0.73513 | 0.56656
|  | 16:03 | 20.3978 | 0.73769 | 0.56655
|  | 16:03 | 20.3989 | 0.7286 | 0.56655
|  | 16:03 | 20.4 | 0.71951 | 0.56655
|  | 16:03 | 20.4011 | 0.69733 | 0.56655
|  | 16:04 | 20.4022 | 0.66208 | 0.56654
|  | 16:04 | 20.4033 | 0.6161 | 0.56654
|  | 16:04 | 20.4044 | 0.5594 | 0.56654
|  | 16:04 | 20.4056 | 0.50271 | 0.56654
|  | 16:04 | 20.4067 | 0.43484 | 0.56653
|  | 16:04 | 20.4078 | 0.36696 | 0.56653
|  | 16:04 | 20.4089 | 0.2997 | 0.56653
|  | 16:04 | 20.41 | 0.23306 | 0.56653
|  | 16:04 | 20.4111 | 0.16641 | 0.56653
|  | 16:04 | 20.4122 | 0.1269 | 0.56652
|  | 16:04 | 20.4133 | 0.087393 | 0.56652
|  | 16:04 | 20.4144 | 0.062752 | 0.56652
|  | 16:04 | 20.4156 | 0.052981 | 0.56652
|  | 16:04 | 20.4167 | 0.04321 | 0.56651
|  | 16:04 | 20.4178 | 0.031374 | 0.56651
|  | 16:05 | 20.4189 | 0.019538 | 0.56651
|  | 16:05 | 20.42 | 0.0014623 | 0.56651
|  | 16:05 | 20.4211 | -0.022852 | 0.5665
|  | 16:05 | 20.4222 | -0.047167 | 0.5665
|  | 16:05 | 20.4233 | -0.057435 | 0.5665
|  | 16:05 | 20.4244 | -0.067703 | 0.5665
|  | 16:05 | 20.4256 | -0.080728 | 0.5665
|  | 16:05 | 20.4267 | -0.096511 | 0.56649
|  | 16:05 | 20.4278 | -0.11229 | 0.56649
|  | 16:05 | 20.4289 | -0.14181 | 0.56649
|  | 16:05 | 20.43 | -0.17133 | 0.56649
|  | 16:05 | 20.4311 | -0.19213 | 0.56648
|  | 16:05 | 20.4322 | -0.21003 | 0.56648
|  | 16:05 | 20.4333 | -0.22794 | 0.56648
|  | 16:05 | 20.4344 | -0.25217 | 0.56648
|  | 16:06 | 20.4356 | -0.2764 | 0.56647
|  | 16:06 | 20.4367 | -0.29614 | 0.56647
|  | 16:06 | 20.4378 | -0.31141 | 0.56647
|  | 16:06 | 20.4389 | -0.32668 | 0.56647
|  | 16:06 | 20.44 | -0.33634 | 0.56647
|  | 16:06 | 20.4411 | -0.346 | 0.56646
|  | 16:06 | 20.4422 | -0.35417 | 0.56646
|  | 16:06 | 20.4433 | -0.36184 | 0.56646
|  | 16:06 | 20.4444 | -0.3695 | 0.56646
|  | 16:06 | 20.4456 | -0.38223 | 0.56645
|  | 16:06 | 20.4467 | -0.39495 | 0.56645
|  | 16:06 | 20.4478 | -0.41366 | 0.56645
|  | 16:06 | 20.4489 | -0.43836 | 0.56645
|  | 16:06 | 20.45 | -0.46307 | 0.56644
|  | 16:06 | 20.4511 | -0.49142 | 0.56644
|  | 16:07 | 20.4522 | -0.51976 | 0.56644
|  | 16:07 | 20.4533 | -0.53557 | 0.56644
|  | 16:07 | 20.4544 | -0.53885 | 0.56644
|  | 16:07 | 20.4556 | -0.54212 | 0.56643
|  | 16:07 | 20.4567 | -0.52588 | 0.56643
|  | 16:07 | 20.4578 | -0.50964 | 0.56643
|  | 16:07 | 20.4589 | -0.48512 | 0.56643
|  | 16:07 | 20.46 | -0.45232 | 0.56642
|  | 16:07 | 20.4611 | -0.41952 | 0.56642
|  | 16:07 | 20.4622 | -0.39896 | 0.56642
|  | 16:07 | 20.4633 | -0.3784 | 0.56642
|  | 16:07 | 20.4644 | -0.36069 | 0.56641
|  | 16:07 | 20.4656 | -0.34581 | 0.56641
|  | 16:07 | 20.4667 | -0.33094 | 0.56641
|  | 16:07 | 20.4678 | -0.31151 | 0.56641
|  | 16:08 | 20.4689 | -0.29208 | 0.56641
|  | 16:08 | 20.47 | -0.26401 | 0.5664
|  | 16:08 | 20.4711 | -0.2273 | 0.5664
|  | 16:08 | 20.4722 | -0.1906 | 0.5664
|  | 16:08 | 20.4733 | -0.15165 | 0.5664
|  | 16:08 | 20.4744 | -0.1127 | 0.56639
|  | 16:08 | 20.4756 | -0.070709 | 0.56639
|  | 16:08 | 20.4767 | -0.025681 | 0.56639
|  | 16:08 | 20.4778 | 0.019348 | 0.56639
|  | 16:08 | 20.4789 | 0.066808 | 0.56638
|  | 16:08 | 20.48 | 0.11427 | 0.56638
|  | 16:08 | 20.4811 | 0.14906 | 0.56638
|  | 16:08 | 20.4822 | 0.17962 | 0.56638
|  | 16:08 | 20.4833 | 0.21018 | 0.56637
|  | 16:08 | 20.4844 | 0.22659 | 0.56637
|  | 16:09 | 20.4856 | 0.243 | 0.56637
|  | 16:09 | 20.4867 | 0.26015 | 0.56637
|  | 16:09 | 20.4878 | 0.27804 | 0.56637
|  | 16:09 | 20.4889 | 0.29593 | 0.56636
|  | 16:09 | 20.49 | 0.34579 | 0.56636
|  | 16:09 | 20.4911 | 0.39566 | 0.56636
|  | 16:09 | 20.4922 | 0.41648 | 0.56636
|  | 16:09 | 20.4933 | 0.42761 | 0.56635
|  | 16:09 | 20.4944 | 0.43875 | 0.56635
|  | 16:09 | 20.4956 | 0.48488 | 0.56635
|  | 16:09 | 20.4967 | 0.53101 | 0.56635
|  | 16:09 | 20.4978 | 0.56431 | 0.56634
|  | 16:09 | 20.4989 | 0.58479 | 0.56634
|  | 16:09 | 20.5 | 0.60527 | 0.56634
|  | 16:09 | 20.5011 | 0.62576 | 0.56634
|  | 16:10 | 20.5022 | 0.64624 | 0.56634
|  | 16:10 | 20.5033 | 0.65386 | 0.56633
|  | 16:10 | 20.5044 | 0.64862 | 0.56633
|  | 16:10 | 20.5056 | 0.64337 | 0.56633
|  | 16:10 | 20.5067 | 0.61858 | 0.56633
|  | 16:10 | 20.5078 | 0.59379 | 0.56632
|  | 16:10 | 20.5089 | 0.57945 | 0.56632
|  | 16:10 | 20.51 | 0.5686 | 0.56632
|  | 16:10 | 20.5111 | 0.55774 | 0.56632
|  | 16:10 | 20.5122 | 0.53406 | 0.56631
|  | 16:10 | 20.5133 | 0.51037 | 0.56631
|  | 16:10 | 20.5144 | 0.48484 | 0.56631
|  | 16:10 | 20.5156 | 0.45747 | 0.56631
|  | 16:10 | 20.5167 | 0.43009 | 0.56631
|  | 16:10 | 20.5178 | 0.40661 | 0.5663
|  | 16:11 | 20.5189 | 0.38313 | 0.5663
|  | 16:11 | 20.52 | 0.35578 | 0.5663
|  | 16:11 | 20.5211 | 0.32455 | 0.5663
|  | 16:11 | 20.5222 | 0.29332 | 0.56629
|  | 16:11 | 20.5233 | 0.24981 | 0.56629
|  | 16:11 | 20.5244 | 0.20629 | 0.56629
|  | 16:11 | 20.5256 | 0.16355 | 0.56629
|  | 16:11 | 20.5267 | 0.12106 | 0.56628
|  | 16:11 | 20.5278 | 0.078582 | 0.56628
|  | 16:11 | 20.5289 | 0.031632 | 0.56628
|  | 16:11 | 20.53 | -0.015318 | 0.56628
|  | 16:11 | 20.5311 | -0.035845 | 0.56628
|  | 16:11 | 20.5322 | -0.047565 | 0.56627
|  | 16:11 | 20.5333 | -0.059285 | 0.56627
|  | 16:11 | 20.5344 | -0.081598 | 0.56627
|  | 16:12 | 20.5356 | -0.10391 | 0.56627
|  | 16:12 | 20.5367 | -0.13323 | 0.56626
|  | 16:12 | 20.5378 | -0.16956 | 0.56626
|  | 16:12 | 20.5389 | -0.20588 | 0.56626
|  | 16:12 | 20.54 | -0.24997 | 0.56626
|  | 16:12 | 20.5411 | -0.29406 | 0.56625
|  | 16:12 | 20.5422 | -0.33234 | 0.56625
|  | 16:12 | 20.5433 | -0.3648 | 0.56625
|  | 16:12 | 20.5444 | -0.39726 | 0.56625
|  | 16:12 | 20.5456 | -0.42357 | 0.56625
|  | 16:12 | 20.5467 | -0.44987 | 0.56624
|  | 16:12 | 20.5478 | -0.46847 | 0.56624
|  | 16:12 | 20.5489 | -0.47935 | 0.56624
|  | 16:12 | 20.55 | -0.49023 | 0.56624
|  | 16:12 | 20.5511 | -0.5088 | 0.56623
|  | 16:13 | 20.5522 | -0.52738 | 0.56623
|  | 16:13 | 20.5533 | -0.54595 | 0.56623
|  | 16:13 | 20.5544 | -0.56452 | 0.56623
|  | 16:13 | 20.5556 | -0.58056 | 0.56622
|  | 16:13 | 20.5567 | -0.58899 | 0.56622
|  | 16:13 | 20.5578 | -0.59741 | 0.56622
|  | 16:13 | 20.5589 | -0.60464 | 0.56622
|  | 16:13 | 20.56 | -0.61068 | 0.56622
|  | 16:13 | 20.5611 | -0.61671 | 0.56621
|  | 16:13 | 20.5622 | -0.62274 | 0.56621
|  | 16:13 | 20.5633 | -0.62878 | 0.56621
|  | 16:13 | 20.5644 | -0.64556 | 0.56621
|  | 16:13 | 20.5656 | -0.67309 | 0.5662
|  | 16:13 | 20.5667 | -0.70062 | 0.5662
|  | 16:13 | 20.5678 | -0.7259 | 0.5662
|  | 16:14 | 20.5689 | -0.75118 | 0.5662
|  | 16:14 | 20.57 | -0.76373 | 0.56619
|  | 16:14 | 20.5711 | -0.76355 | 0.56619
|  | 16:14 | 20.5722 | -0.76336 | 0.56619
|  | 16:14 | 20.5733 | -0.74165 | 0.56619
|  | 16:14 | 20.5744 | -0.71995 | 0.56619
|  | 16:14 | 20.5756 | -0.69328 | 0.56618
|  | 16:14 | 20.5767 | -0.66166 | 0.56618
|  | 16:14 | 20.5778 | -0.63004 | 0.56618
|  | 16:14 | 20.5789 | -0.60123 | 0.56618
|  | 16:14 | 20.58 | -0.57243 | 0.56617
|  | 16:14 | 20.5811 | -0.55891 | 0.56617
|  | 16:14 | 20.5822 | -0.56068 | 0.56617
|  | 16:14 | 20.5833 | -0.56245 | 0.56617
|  | 16:14 | 20.5844 | -0.54412 | 0.56616
|  | 16:15 | 20.5856 | -0.52578 | 0.56616
|  | 16:15 | 20.5867 | -0.51626 | 0.56616
|  | 16:15 | 20.5878 | -0.51554 | 0.56616
|  | 16:15 | 20.5889 | -0.51483 | 0.56616
|  | 16:15 | 20.59 | -0.51658 | 0.56615
|  | 16:15 | 20.5911 | -0.51832 | 0.56615
|  | 16:15 | 20.5922 | -0.51742 | 0.56615
|  | 16:15 | 20.5933 | -0.51387 | 0.56615
|  | 16:15 | 20.5944 | -0.51032 | 0.56614
|  | 16:15 | 20.5956 | -0.49265 | 0.56614
|  | 16:15 | 20.5967 | -0.47497 | 0.56614
|  | 16:15 | 20.5978 | -0.4573 | 0.56614
|  | 16:15 | 20.5989 | -0.43963 | 0.56613
|  | 16:15 | 20.6 | -0.42195 | 0.56613
|  | 16:15 | 20.6011 | -0.40033 | 0.56613
|  | 16:16 | 20.6022 | -0.3787 | 0.56613
|  | 16:16 | 20.6033 | -0.35755 | 0.56612
|  | 16:16 | 20.6044 | -0.33687 | 0.56612
|  | 16:16 | 20.6056 | -0.31619 | 0.56612
|  | 16:16 | 20.6067 | -0.27026 | 0.56612
|  | 16:16 | 20.6078 | -0.22432 | 0.56612
|  | 16:16 | 20.6089 | -0.18079 | 0.56611
|  | 16:16 | 20.61 | -0.13806 | 0.56611
|  | 16:16 | 20.6111 | -0.095326 | 0.56611
|  | 16:16 | 20.6122 | -0.056057 | 0.56611
|  | 16:16 | 20.6133 | -0.016788 | 0.5661
|  | 16:16 | 20.6144 | 0.015659 | 0.5661
|  | 16:16 | 20.6156 | 0.041284 | 0.5661
|  | 16:16 | 20.6167 | 0.066908 | 0.5661
|  | 16:16 | 20.6178 | 0.067889 | 0.56609
|  | 16:17 | 20.6189 | 0.06887 | 0.56609
|  | 16:17 | 20.62 | 0.077604 | 0.56609
|  | 16:17 | 20.6211 | 0.094089 | 0.56609
|  | 16:17 | 20.6222 | 0.11057 | 0.56609
|  | 16:17 | 20.6233 | 0.13697 | 0.56608
|  | 16:17 | 20.6244 | 0.16337 | 0.56608
|  | 16:17 | 20.6256 | 0.18555 | 0.56608
|  | 16:17 | 20.6267 | 0.2035 | 0.56608
|  | 16:17 | 20.6278 | 0.22146 | 0.56607
|  | 16:17 | 20.6289 | 0.25483 | 0.56607
|  | 16:17 | 20.63 | 0.2882 | 0.56607
|  | 16:17 | 20.6311 | 0.30837 | 0.56607
|  | 16:17 | 20.6322 | 0.31533 | 0.56606
|  | 16:17 | 20.6333 | 0.32229 | 0.56606
|  | 16:17 | 20.6344 | 0.34371 | 0.56606
|  | 16:18 | 20.6356 | 0.36513 | 0.56606
|  | 16:18 | 20.6367 | 0.39495 | 0.56606
|  | 16:18 | 20.6378 | 0.43316 | 0.56605
|  | 16:18 | 20.6389 | 0.47137 | 0.56605
|  | 16:18 | 20.64 | 0.50421 | 0.56605
|  | 16:18 | 20.6411 | 0.53705 | 0.56605
|  | 16:18 | 20.6422 | 0.56677 | 0.56604
|  | 16:18 | 20.6433 | 0.59337 | 0.56604
|  | 16:18 | 20.6444 | 0.61996 | 0.56604
|  | 16:18 | 20.6456 | 0.63533 | 0.56604
|  | 16:18 | 20.6467 | 0.6507 | 0.56603
|  | 16:18 | 20.6478 | 0.67478 | 0.56603
|  | 16:18 | 20.6489 | 0.70756 | 0.56603
|  | 16:18 | 20.65 | 0.74033 | 0.56603
|  | 16:18 | 20.6511 | 0.7188 | 0.56603
|  | 16:19 | 20.6522 | 0.69726 | 0.56602
|  | 16:19 | 20.6533 | 0.69924 | 0.56602
|  | 16:19 | 20.6544 | 0.72473 | 0.56602
|  | 16:19 | 20.6556 | 0.75023 | 0.56602
|  | 16:19 | 20.6567 | 0.75876 | 0.56601
|  | 16:19 | 20.6578 | 0.76729 | 0.56601
|  | 16:19 | 20.6589 | 0.77299 | 0.56601
|  | 16:19 | 20.66 | 0.77774 | 0.56601
|  | 16:19 | 20.6611 | 0.7825 | 0.566
|  | 16:19 | 20.6622 | 0.76741 | 0.566
|  | 16:19 | 20.6633 | 0.75232 | 0.566
|  | 16:19 | 20.6644 | 0.7296 | 0.566
|  | 16:19 | 20.6656 | 0.69925 | 0.566
|  | 16:19 | 20.6667 | 0.6689 | 0.56599
|  | 16:19 | 20.6678 | 0.62576 | 0.56599
|  | 16:20 | 20.6689 | 0.58261 | 0.56599
|  | 16:20 | 20.67 | 0.54949 | 0.56599
|  | 16:20 | 20.6711 | 0.5264 | 0.56598
|  | 16:20 | 20.6722 | 0.50331 | 0.56598
|  | 16:20 | 20.6733 | 0.4765 | 0.56598
|  | 16:20 | 20.6744 | 0.44968 | 0.56598
|  | 16:20 | 20.6756 | 0.4167 | 0.56597
|  | 16:20 | 20.6767 | 0.37755 | 0.56597
|  | 16:20 | 20.6778 | 0.33841 | 0.56597
|  | 16:20 | 20.6789 | 0.29386 | 0.56597
|  | 16:20 | 20.68 | 0.24932 | 0.56597
|  | 16:20 | 20.6811 | 0.21533 | 0.56596
|  | 16:20 | 20.6822 | 0.19189 | 0.56596
|  | 16:20 | 20.6833 | 0.16844 | 0.56596
|  | 16:20 | 20.6844 | 0.16499 | 0.56596
|  | 16:21 | 20.6856 | 0.16153 | 0.56595
|  | 16:21 | 20.6867 | 0.15986 | 0.56595
|  | 16:21 | 20.6878 | 0.15996 | 0.56595
|  | 16:21 | 20.6889 | 0.16005 | 0.56595
|  | 16:21 | 20.69 | 0.14796 | 0.56594
|  | 16:21 | 20.6911 | 0.13587 | 0.56594
|  | 16:21 | 20.6922 | 0.12378 | 0.56594
|  | 16:21 | 20.6933 | 0.1117 | 0.56594
|  | 16:21 | 20.6944 | 0.099605 | 0.56594
|  | 16:21 | 20.6956 | 0.079349 | 0.56593
|  | 16:21 | 20.6967 | 0.059092 | 0.56593
|  | 16:21 | 20.6978 | 0.042185 | 0.56593
|  | 16:21 | 20.6989 | 0.028626 | 0.56593
|  | 16:21 | 20.7 | 0.015067 | 0.56592
|  | 16:21 | 20.7011 | 0.017848 | 0.56592
|  | 16:22 | 20.7022 | 0.020629 | 0.56592
|  | 16:22 | 20.7033 | 0.02341 | 0.56592
|  | 16:22 | 20.7044 | 0.02619 | 0.56591
|  | 16:22 | 20.7056 | 0.028971 | 0.56591
|  | 16:22 | 20.7067 | 0.040168 | 0.56591
|  | 16:22 | 20.7078 | 0.051364 | 0.56591
|  | 16:22 | 20.7089 | 0.060832 | 0.56591
|  | 16:22 | 20.71 | 0.068571 | 0.5659
|  | 16:22 | 20.7111 | 0.076309 | 0.5659
|  | 16:22 | 20.7122 | 0.077437 | 0.5659
|  | 16:22 | 20.7133 | 0.078564 | 0.5659
|  | 16:22 | 20.7144 | 0.080322 | 0.56589
|  | 16:22 | 20.7156 | 0.082711 | 0.56589
|  | 16:22 | 20.7167 | 0.085099 | 0.56589
|  | 16:22 | 20.7178 | 0.082506 | 0.56589
|  | 16:23 | 20.7189 | 0.079913 | 0.56588
|  | 16:23 | 20.72 | 0.07732 | 0.56588
|  | 16:23 | 20.7211 | 0.074727 | 0.56588
|  | 16:23 | 20.7222 | 0.072134 | 0.56588
|  | 16:23 | 20.7233 | 0.05751 | 0.56587
|  | 16:23 | 20.7244 | 0.042887 | 0.56587
|  | 16:23 | 20.7256 | 0.041184 | 0.56587
|  | 16:23 | 20.7267 | 0.052402 | 0.56587
|  | 16:23 | 20.7278 | 0.063621 | 0.56587
|  | 16:23 | 20.7289 | 0.059618 | 0.56586
|  | 16:23 | 20.73 | 0.055615 | 0.56586
|  | 16:23 | 20.7311 | 0.053782 | 0.56586
|  | 16:23 | 20.7322 | 0.054119 | 0.56586
|  | 16:23 | 20.7333 | 0.054456 | 0.56585
|  | 16:23 | 20.7344 | 0.052728 | 0.56585
|  | 16:24 | 20.7356 | 0.051 | 0.56585
|  | 16:24 | 20.7367 | 0.053232 | 0.56585
|  | 16:24 | 20.7378 | 0.059425 | 0.56584
|  | 16:24 | 20.7389 | 0.065617 | 0.56584
|  | 16:24 | 20.74 | 0.089973 | 0.56584
|  | 16:24 | 20.7411 | 0.11433 | 0.56584
|  | 16:24 | 20.7422 | 0.13104 | 0.56584
|  | 16:24 | 20.7433 | 0.14009 | 0.56583
|  | 16:24 | 20.7444 | 0.14915 | 0.56583
|  | 16:24 | 20.7456 | 0.14294 | 0.56583
|  | 16:24 | 20.7467 | 0.13674 | 0.56583
|  | 16:24 | 20.7478 | 0.13903 | 0.56582
|  | 16:24 | 20.7489 | 0.14981 | 0.56582
|  | 16:24 | 20.75 | 0.16059 | 0.56582
|  | 16:24 | 20.7511 | 0.17604 | 0.56582
|  | 16:25 | 20.7522 | 0.1915 | 0.56581
|  | 16:25 | 20.7533 | 0.20614 | 0.56581
|  | 16:25 | 20.7544 | 0.21996 | 0.56581
|  | 16:25 | 20.7556 | 0.23378 | 0.56581
|  | 16:25 | 20.7567 | 0.22649 | 0.56581
|  | 16:25 | 20.7578 | 0.2192 | 0.5658
|  | 16:25 | 20.7589 | 0.2103 | 0.5658
|  | 16:25 | 20.76 | 0.1998 | 0.5658
|  | 16:25 | 20.7611 | 0.18929 | 0.5658
|  | 16:25 | 20.7622 | 0.16969 | 0.56579
|  | 16:25 | 20.7633 | 0.15009 | 0.56579
|  | 16:25 | 20.7644 | 0.12595 | 0.56579
|  | 16:25 | 20.7656 | 0.09729 | 0.56579
|  | 16:25 | 20.7667 | 0.068625 | 0.56578
|  | 16:25 | 20.7678 | 0.07361 | 0.56578
|  | 16:26 | 20.7689 | 0.078594 | 0.56578
|  | 16:26 | 20.77 | 0.072993 | 0.56578
|  | 16:26 | 20.7711 | 0.056805 | 0.56578
|  | 16:26 | 20.7722 | 0.040617 | 0.56577
|  | 16:26 | 20.7733 | 0.014632 | 0.56577
|  | 16:26 | 20.7744 | -0.011353 | 0.56577
|  | 16:26 | 20.7756 | -0.035552 | 0.56577
|  | 16:26 | 20.7767 | -0.057963 | 0.56576
|  | 16:26 | 20.7778 | -0.080375 | 0.56576
|  | 16:26 | 20.7789 | -0.065543 | 0.56576
|  | 16:26 | 20.78 | -0.050712 | 0.56576
|  | 16:26 | 20.7811 | -0.031837 | 0.56575
|  | 16:26 | 20.7822 | -0.0089175 | 0.56575
|  | 16:26 | 20.7833 | 0.014002 | 0.56575
|  | 16:26 | 20.7844 | 0.0028253 | 0.56575
|  | 16:27 | 20.7856 | -0.0083511 | 0.56575
|  | 16:27 | 20.7867 | -0.022928 | 0.56574
|  | 16:27 | 20.7878 | -0.040906 | 0.56574
|  | 16:27 | 20.7889 | -0.058884 | 0.56574
|  | 16:27 | 20.79 | -0.068746 | 0.56574
|  | 16:27 | 20.7911 | -0.078609 | 0.56573
|  | 16:27 | 20.7922 | -0.07932 | 0.56573
|  | 16:27 | 20.7933 | -0.076982 | 0.56573
|  | 16:27 | 20.7944 | -0.074643 | 0.56573
|  | 16:27 | 20.7956 | -0.075455 | 0.56572
|  | 16:27 | 20.7967 | -0.076267 | 0.56572
|  | 16:27 | 20.7978 | -0.073963 | 0.56572
|  | 16:27 | 20.7989 | -0.07062 | 0.56572
|  | 16:27 | 20.8 | -0.067277 | 0.56572
|  | 16:27 | 20.8011 | -0.087801 | 0.56571
|  | 16:28 | 20.8022 | -0.10832 | 0.56571
|  | 16:28 | 20.8033 | -0.11242 | 0.56571
|  | 16:28 | 20.8044 | -0.10009 | 0.56571
|  | 16:28 | 20.8056 | -0.087763 | 0.5657
|  | 16:28 | 20.8067 | -0.068639 | 0.5657
|  | 16:28 | 20.8078 | -0.049516 | 0.5657
|  | 16:28 | 20.8089 | -0.015747 | 0.5657
|  | 16:28 | 20.81 | 0.032669 | 0.56569
|  | 16:28 | 20.8111 | 0.076313 | 0.56569
|  | 16:28 | 20.8122 | 0.10565 | 0.56569
|  | 16:28 | 20.8133 | 0.13498 | 0.56569
|  | 16:28 | 20.8144 | 0.14996 | 0.56569
|  | 16:28 | 20.8156 | 0.1506 | 0.56568
|  | 16:28 | 20.8167 | 0.15123 | 0.56568
|  | 16:28 | 20.8178 | 0.15947 | 0.56568
|  | 16:29 | 20.8189 | 0.1677 | 0.56568
|  | 16:29 | 20.82 | 0.16361 | 0.56567
|  | 16:29 | 20.8211 | 0.14719 | 0.56567
|  | 16:29 | 20.8222 | 0.13078 | 0.56567
|  | 16:29 | 20.8233 | 0.11437 | 0.56567
|  | 16:29 | 20.8244 | 0.097961 | 0.56566
|  | 16:29 | 20.8256 | 0.077558 | 0.56566
|  | 16:29 | 20.8267 | 0.055824 | 0.56566
|  | 16:29 | 20.8278 | 0.034089 | 0.56566
|  | 16:29 | 20.8289 | 0.018564 | 0.56566
|  | 16:29 | 20.83 | 0.0030393 | 0.56565
|  | 16:29 | 20.8311 | -0.016027 | 0.56565
|  | 16:29 | 20.8322 | -0.038635 | 0.56565
|  | 16:29 | 20.8333 | -0.061243 | 0.56565
|  | 16:29 | 20.8344 | -0.068344 | 0.56564
|  | 16:30 | 20.8356 | -0.075445 | 0.56564
|  | 16:30 | 20.8367 | -0.080764 | 0.56564
|  | 16:30 | 20.8378 | -0.0843 | 0.56564
|  | 16:30 | 20.8389 | -0.087836 | 0.56563
|  | 16:30 | 20.84 | -0.08516 | 0.56563
|  | 16:30 | 20.8411 | -0.082483 | 0.56563
|  | 16:30 | 20.8422 | -0.079807 | 0.56563
|  | 16:30 | 20.8433 | -0.07713 | 0.56562
|  | 16:30 | 20.8444 | -0.074454 | 0.56562
|  | 16:30 | 20.8456 | -0.076025 | 0.56562
|  | 16:30 | 20.8467 | -0.077597 | 0.56562
|  | 16:30 | 20.8478 | -0.085439 | 0.56562
|  | 16:30 | 20.8489 | -0.09955 | 0.56561
|  | 16:30 | 20.85 | -0.11366 | 0.56561
|  | 16:30 | 20.8511 | -0.11441 | 0.56561
|  | 16:31 | 20.8522 | -0.11516 | 0.56561
|  | 16:31 | 20.8533 | -0.10971 | 0.5656
|  | 16:31 | 20.8544 | -0.09806 | 0.5656
|  | 16:31 | 20.8556 | -0.084509 | 0.5656
|  | 16:31 | 20.8567 | -0.065244 | 0.5656
|  | 16:31 | 20.8578 | -0.045979 | 0.56559
|  | 16:31 | 20.8589 | -0.029559 | 0.56559
|  | 16:31 | 20.86 | -0.015984 | 0.56559
|  | 16:31 | 20.8611 | -0.0024094 | 0.56559
|  | 16:31 | 20.8622 | 0.022238 | 0.56559
|  | 16:31 | 20.8633 | 0.046885 | 0.56558
|  | 16:31 | 20.8644 | 0.074314 | 0.56558
|  | 16:31 | 20.8656 | 0.10453 | 0.56558
|  | 16:31 | 20.8667 | 0.13474 | 0.56558
|  | 16:31 | 20.8678 | 0.15843 | 0.56557
|  | 16:32 | 20.8689 | 0.18212 | 0.56557
|  | 16:32 | 20.87 | 0.20365 | 0.56557
|  | 16:32 | 20.8711 | 0.22304 | 0.56557
|  | 16:32 | 20.8722 | 0.24243 | 0.56556
|  | 16:32 | 20.8733 | 0.2467 | 0.56556
|  | 16:32 | 20.8744 | 0.25097 | 0.56556
|  | 16:32 | 20.8756 | 0.25524 | 0.56556
|  | 16:32 | 20.8767 | 0.25952 | 0.56556
|  | 16:32 | 20.8778 | 0.26379 | 0.56555
|  | 16:32 | 20.8789 | 0.26806 | 0.56555
|  | 16:32 | 20.88 | 0.27234 | 0.56555
|  | 16:32 | 20.8811 | 0.27055 | 0.56555
|  | 16:32 | 20.8822 | 0.26272 | 0.56554
|  | 16:32 | 20.8833 | 0.25488 | 0.56554
|  | 16:32 | 20.8844 | 0.23498 | 0.56554
|  | 16:33 | 20.8856 | 0.21507 | 0.56554
|  | 16:33 | 20.8867 | 0.20228 | 0.56553
|  | 16:33 | 20.8878 | 0.1966 | 0.56553
|  | 16:33 | 20.8889 | 0.19092 | 0.56553
|  | 16:33 | 20.89 | 0.17374 | 0.56553
|  | 16:33 | 20.8911 | 0.15656 | 0.56553
|  | 16:33 | 20.8922 | 0.14737 | 0.56552
|  | 16:33 | 20.8933 | 0.14617 | 0.56552
|  | 16:33 | 20.8944 | 0.14096 | 0.56552
|  | 16:33 | 20.8956 | 0.1237 | 0.56552
|  | 16:33 | 20.8967 | 0.10644 | 0.56551
|  | 16:33 | 20.8978 | 0.091813 | 0.56551
|  | 16:33 | 20.8989 | 0.079822 | 0.56551
|  | 16:33 | 20.9 | 0.067831 | 0.56551
|  | 16:33 | 20.9011 | 0.075896 | 0.5655
|  | 16:34 | 20.9022 | 0.083961 | 0.5655
|  | 16:34 | 20.9033 | 0.086463 | 0.5655
|  | 16:34 | 20.9044 | 0.083403 | 0.5655
|  | 16:34 | 20.9056 | 0.080342 | 0.5655
|  | 16:34 | 20.9067 | 0.086139 | 0.56549
|  | 16:34 | 20.9078 | 0.091936 | 0.56549
|  | 16:34 | 20.9089 | 0.086932 | 0.56549
|  | 16:34 | 20.91 | 0.071129 | 0.56549
|  | 16:34 | 20.9111 | 0.055325 | 0.56548
|  | 16:34 | 20.9122 | 0.058039 | 0.56548
|  | 16:34 | 20.9133 | 0.060754 | 0.56548
|  | 16:34 | 20.9144 | 0.053289 | 0.56548
|  | 16:34 | 20.9156 | 0.035644 | 0.56547
|  | 16:34 | 20.9167 | 0.018 | 0.56547
|  | 16:34 | 20.9178 | -0.013065 | 0.56547
|  | 16:35 | 20.9189 | -0.04413 | 0.56547
|  | 16:35 | 20.92 | -0.070275 | 0.56547
|  | 16:35 | 20.9211 | -0.091499 | 0.56546
|  | 16:35 | 20.9222 | -0.11272 | 0.56546
|  | 16:35 | 20.9233 | -0.1153 | 0.56546
|  | 16:35 | 20.9244 | -0.11788 | 0.56546
|  | 16:35 | 20.9256 | -0.11783 | 0.56545
|  | 16:35 | 20.9267 | -0.11514 | 0.56545
|  | 16:35 | 20.9278 | -0.11272 | 0.56545
|  | 16:35 | 20.9289 | -0.11108 | 0.56545
|  | 16:35 | 20.93 | -0.10944 | 0.56544
|  | 16:35 | 20.9311 | -0.1078 | 0.56544
|  | 16:35 | 20.9322 | -0.12031 | 0.56544
|  | 16:35 | 20.9333 | -0.13283 | 0.56544
|  | 16:35 | 20.9344 | -0.13556 | 0.56544
|  | 16:36 | 20.9356 | -0.1383 | 0.56543
|  | 16:36 | 20.9367 | -0.13564 | 0.56543
|  | 16:36 | 20.9378 | -0.13119 | 0.56543
|  | 16:36 | 20.9389 | -0.1251 | 0.56543
|  | 16:36 | 20.94 | -0.11411 | 0.56542
|  | 16:36 | 20.9411 | -0.10312 | 0.56542
|  | 16:36 | 20.9422 | -0.087127 | 0.56542
|  | 16:36 | 20.9433 | -0.06947 | 0.56542
|  | 16:36 | 20.9444 | -0.057029 | 0.56541
|  | 16:36 | 20.9456 | -0.060235 | 0.56541
|  | 16:36 | 20.9467 | -0.06344 | 0.56541
|  | 16:36 | 20.9478 | -0.059529 | 0.56541
|  | 16:36 | 20.9489 | -0.053247 | 0.56541
|  | 16:36 | 20.95 | -0.048412 | 0.5654
|  | 16:36 | 20.9511 | -0.047923 | 0.5654
|  | 16:37 | 20.9522 | -0.047434 | 0.5654
|  | 16:37 | 20.9533 | -0.052124 | 0.5654
|  | 16:37 | 20.9544 | -0.05854 | 0.56539
|  | 16:37 | 20.9556 | -0.068618 | 0.56539
|  | 16:37 | 20.9567 | -0.08968 | 0.56539
|  | 16:37 | 20.9578 | -0.11074 | 0.56539
|  | 16:37 | 20.9589 | -0.12803 | 0.56538
|  | 16:37 | 20.96 | -0.14405 | 0.56538
|  | 16:37 | 20.9611 | -0.15587 | 0.56538
|  | 16:37 | 20.9622 | -0.15507 | 0.56538
|  | 16:37 | 20.9633 | -0.15427 | 0.56537
|  | 16:37 | 20.9644 | -0.1689 | 0.56537
|  | 16:37 | 20.9656 | -0.18867 | 0.56537
|  | 16:37 | 20.9667 | -0.19879 | 0.56537
|  | 16:37 | 20.9678 | -0.17995 | 0.56537
|  | 16:38 | 20.9689 | -0.16112 | 0.56536
|  | 16:38 | 20.97 | -0.14042 | 0.56536
|  | 16:38 | 20.9711 | -0.1191 | 0.56536
|  | 16:38 | 20.9722 | -0.087246 | 0.56536
|  | 16:38 | 20.9733 | -0.023777 | 0.56535
|  | 16:38 | 20.9744 | 0.039692 | 0.56535
|  | 16:38 | 20.9756 | 0.084628 | 0.56535
|  | 16:38 | 20.9767 | 0.12956 | 0.56535
|  | 16:38 | 20.9778 | 0.17372 | 0.56534
|  | 16:38 | 20.9789 | 0.21556 | 0.56534
|  | 16:38 | 20.98 | 0.2574 | 0.56534
|  | 16:38 | 20.9811 | 0.26371 | 0.56534
|  | 16:38 | 20.9822 | 0.25818 | 0.56534
|  | 16:38 | 20.9833 | 0.25264 | 0.56533
|  | 16:38 | 20.9844 | 0.24711 | 0.56533
|  | 16:39 | 20.9856 | 0.24157 | 0.56533
|  | 16:39 | 20.9867 | 0.24404 | 0.56533
|  | 16:39 | 20.9878 | 0.24918 | 0.56532
|  | 16:39 | 20.9889 | 0.25653 | 0.56532
|  | 16:39 | 20.99 | 0.27053 | 0.56532
|  | 16:39 | 20.9911 | 0.28454 | 0.56532
|  | 16:39 | 20.9922 | 0.28643 | 0.56531
|  | 16:39 | 20.9933 | 0.28428 | 0.56531
|  | 16:39 | 20.9944 | 0.28637 | 0.56531
|  | 16:39 | 20.9956 | 0.30114 | 0.56531
|  | 16:39 | 20.9967 | 0.31592 | 0.56531
|  | 16:39 | 20.9978 | 0.32289 | 0.5653
|  | 16:39 | 20.9989 | 0.32726 | 0.5653
|  | 16:39 | 21 | 0.32399 | 0.5653
|  | 16:39 | 21.0011 | 0.3131 | 0.5653
|  | 16:40 | 21.0022 | 0.3022 | 0.56529
|  | 16:40 | 21.0033 | 0.28574 | 0.56529
|  | 16:40 | 21.0044 | 0.26742 | 0.56529
|  | 16:40 | 21.0056 | 0.24996 | 0.56529
|  | 16:40 | 21.0067 | 0.23337 | 0.56528
|  | 16:40 | 21.0078 | 0.21678 | 0.56528
|  | 16:40 | 21.0089 | 0.18735 | 0.56528
|  | 16:40 | 21.01 | 0.15364 | 0.56528
|  | 16:40 | 21.0111 | 0.13899 | 0.56528
|  | 16:40 | 21.0122 | 0.1434 | 0.56527
|  | 16:40 | 21.0133 | 0.1478 | 0.56527
|  | 16:40 | 21.0144 | 0.16101 | 0.56527
|  | 16:40 | 21.0156 | 0.17715 | 0.56527
|  | 16:40 | 21.0167 | 0.1784 | 0.56526
|  | 16:40 | 21.0178 | 0.16474 | 0.56526
|  | 16:41 | 21.0189 | 0.15109 | 0.56526
|  | 16:41 | 21.02 | 0.12306 | 0.56526
|  | 16:41 | 21.0211 | 0.090241 | 0.56525
|  | 16:41 | 21.0222 | 0.056587 | 0.56525
|  | 16:41 | 21.0233 | 0.020429 | 0.56525
|  | 16:41 | 21.0244 | -0.015729 | 0.56525
|  | 16:41 | 21.0256 | -0.042232 | 0.56525
|  | 16:41 | 21.0267 | -0.065516 | 0.56524
|  | 16:41 | 21.0278 | -0.087599 | 0.56524
|  | 16:41 | 21.0289 | -0.10608 | 0.56524
|  | 16:41 | 21.03 | -0.12456 | 0.56524
|  | 16:41 | 21.0311 | -0.13921 | 0.56523
|  | 16:41 | 21.0322 | -0.15259 | 0.56523
|  | 16:41 | 21.0333 | -0.16354 | 0.56523
|  | 16:41 | 21.0344 | -0.16719 | 0.56523
|  | 16:42 | 21.0356 | -0.17083 | 0.56522
|  | 16:42 | 21.0367 | -0.19514 | 0.56522
|  | 16:42 | 21.0378 | -0.22632 | 0.56522
|  | 16:42 | 21.0389 | -0.24783 | 0.56522
|  | 16:42 | 21.04 | -0.24028 | 0.56522
|  | 16:42 | 21.0411 | -0.23273 | 0.56521
|  | 16:42 | 21.0422 | -0.22091 | 0.56521
|  | 16:42 | 21.0433 | -0.20767 | 0.56521
|  | 16:42 | 21.0444 | -0.19169 | 0.56521
|  | 16:42 | 21.0456 | -0.1675 | 0.5652
|  | 16:42 | 21.0467 | -0.14331 | 0.5652
|  | 16:42 | 21.0478 | -0.12658 | 0.5652
|  | 16:42 | 21.0489 | -0.11235 | 0.5652
|  | 16:42 | 21.05 | -0.099041 | 0.56519
|  | 16:42 | 21.0511 | -0.088485 | 0.56519
|  | 16:43 | 21.0522 | -0.077929 | 0.56519
|  | 16:43 | 21.0533 | -0.06405 | 0.56519
|  | 16:43 | 21.0544 | -0.049063 | 0.56519
|  | 16:43 | 21.0556 | -0.032325 | 0.56518
|  | 16:43 | 21.0567 | -0.01033 | 0.56518
|  | 16:43 | 21.0578 | 0.011664 | 0.56518
|  | 16:43 | 21.0589 | 0.025807 | 0.56518
|  | 16:43 | 21.06 | 0.037333 | 0.56517
|  | 16:43 | 21.0611 | 0.049144 | 0.56517
|  | 16:43 | 21.0622 | 0.06181 | 0.56517
|  | 16:43 | 21.0633 | 0.074475 | 0.56517
|  | 16:43 | 21.0644 | 0.088406 | 0.56516
|  | 16:43 | 21.0656 | 0.10276 | 0.56516
|  | 16:43 | 21.0667 | 0.11637 | 0.56516
|  | 16:43 | 21.0678 | 0.12776 | 0.56516
|  | 16:44 | 21.0689 | 0.13916 | 0.56516
|  | 16:44 | 21.07 | 0.15333 | 0.56515
|  | 16:44 | 21.0711 | 0.16843 | 0.56515
|  | 16:44 | 21.0722 | 0.18226 | 0.56515
|  | 16:44 | 21.0733 | 0.19228 | 0.56515
|  | 16:44 | 21.0744 | 0.20229 | 0.56514
|  | 16:44 | 21.0756 | 0.18703 | 0.56514
|  | 16:44 | 21.0767 | 0.17176 | 0.56514
|  | 16:44 | 21.0778 | 0.15361 | 0.56514
|  | 16:44 | 21.0789 | 0.12677 | 0.56513
|  | 16:44 | 21.08 | 0.099932 | 0.56513
|  | 16:44 | 21.0811 | 0.080254 | 0.56513
|  | 16:44 | 21.0822 | 0.062962 | 0.56513
|  | 16:44 | 21.0833 | 0.049071 | 0.56512
|  | 16:44 | 21.0844 | 0.045383 | 0.56512
|  | 16:45 | 21.0856 | 0.041695 | 0.56512
|  | 16:45 | 21.0867 | 0.032198 | 0.56512
|  | 16:45 | 21.0878 | 0.020765 | 0.56512
|  | 16:45 | 21.0889 | 0.010218 | 0.56511
|  | 16:45 | 21.09 | 0.0023298 | 0.56511
|  | 16:45 | 21.0911 | -0.0055582 | 0.56511
|  | 16:45 | 21.0922 | -0.023576 | 0.56511
|  | 16:45 | 21.0933 | -0.04497 | 0.5651
|  | 16:45 | 21.0944 | -0.063236 | 0.5651
|  | 16:45 | 21.0956 | -0.072119 | 0.5651
|  | 16:45 | 21.0967 | -0.081002 | 0.5651
|  | 16:45 | 21.0978 | -0.091497 | 0.56509
|  | 16:45 | 21.0989 | -0.10253 | 0.56509
|  | 16:45 | 21.1 | -0.11184 | 0.56509
|  | 16:45 | 21.1011 | -0.11599 | 0.56509
|  | 16:46 | 21.1022 | -0.12014 | 0.56509
|  | 16:46 | 21.1033 | -0.12608 | 0.56508
|  | 16:46 | 21.1044 | -0.13383 | 0.56508
|  | 16:46 | 21.1056 | -0.14157 | 0.56508
|  | 16:46 | 21.1067 | -0.14002 | 0.56508
|  | 16:46 | 21.1078 | -0.13847 | 0.56507
|  | 16:46 | 21.1089 | -0.14396 | 0.56507
|  | 16:46 | 21.11 | -0.1565 | 0.56507
|  | 16:46 | 21.1111 | -0.16904 | 0.56507
|  | 16:46 | 21.1122 | -0.18405 | 0.56506
|  | 16:46 | 21.1133 | -0.19905 | 0.56506
|  | 16:46 | 21.1144 | -0.20539 | 0.56506
|  | 16:46 | 21.1156 | -0.20306 | 0.56506
|  | 16:46 | 21.1167 | -0.20073 | 0.56506
|  | 16:46 | 21.1178 | -0.17283 | 0.56505
|  | 16:47 | 21.1189 | -0.14493 | 0.56505
|  | 16:47 | 21.12 | -0.1155 | 0.56505
|  | 16:47 | 21.1211 | -0.084542 | 0.56505
|  | 16:47 | 21.1222 | -0.053583 | 0.56504
|  | 16:47 | 21.1233 | -0.01823 | 0.56504
|  | 16:47 | 21.1244 | 0.017124 | 0.56504
|  | 16:47 | 21.1256 | 0.042132 | 0.56504
|  | 16:47 | 21.1267 | 0.056796 | 0.56503
|  | 16:47 | 21.1278 | 0.07146 | 0.56503
|  | 16:47 | 21.1289 | 0.069582 | 0.56503
|  | 16:47 | 21.13 | 0.067705 | 0.56503
|  | 16:47 | 21.1311 | 0.068706 | 0.56503
|  | 16:47 | 21.1322 | 0.072586 | 0.56502
|  | 16:47 | 21.1333 | 0.076467 | 0.56502
|  | 16:47 | 21.1344 | 0.08665 | 0.56502
|  | 16:48 | 21.1356 | 0.096832 | 0.56502
|  | 16:48 | 21.1367 | 0.097433 | 0.56501
|  | 16:48 | 21.1378 | 0.088452 | 0.56501
|  | 16:48 | 21.1389 | 0.079471 | 0.56501
|  | 16:48 | 21.14 | 0.07049 | 0.56501
|  | 16:48 | 21.1411 | 0.061509 | 0.565
|  | 16:48 | 21.1422 | 0.044761 | 0.565
|  | 16:48 | 21.1433 | 0.020245 | 0.565
|  | 16:48 | 21.1444 | -0.0042709 | 0.565
|  | 16:48 | 21.1456 | -0.0071686 | 0.565
|  | 16:48 | 21.1467 | -0.010066 | 0.56499
|  | 16:48 | 21.1478 | -0.015785 | 0.56499
|  | 16:48 | 21.1489 | -0.024325 | 0.56499
|  | 16:48 | 21.15 | -0.032865 | 0.56499
|  | 16:48 | 21.1511 | -0.041405 | 0.56498
|  | 16:49 | 21.1522 | -0.049945 | 0.56498
|  | 16:49 | 21.1533 | -0.061732 | 0.56498
|  | 16:49 | 21.1544 | -0.076764 | 0.56498
|  | 16:49 | 21.1556 | -0.091797 | 0.56497
|  | 16:49 | 21.1567 | -0.081949 | 0.56497
|  | 16:49 | 21.1578 | -0.072101 | 0.56497
|  | 16:49 | 21.1589 | -0.069993 | 0.56497
|  | 16:49 | 21.16 | -0.075625 | 0.56497
|  | 16:49 | 21.1611 | -0.081256 | 0.56496
|  | 16:49 | 21.1622 | -0.10398 | 0.56496
|  | 16:49 | 21.1633 | -0.12671 | 0.56496
|  | 16:49 | 21.1644 | -0.13424 | 0.56496
|  | 16:49 | 21.1656 | -0.13671 | 0.56495
|  | 16:49 | 21.1667 | -0.13917 | 0.56495
|  | 16:49 | 21.1678 | -0.13967 | 0.56495
|  | 16:50 | 21.1689 | -0.14016 | 0.56495
|  | 16:50 | 21.17 | -0.13967 | 0.56494
|  | 16:50 | 21.1711 | -0.1382 | 0.56494
|  | 16:50 | 21.1722 | -0.13672 | 0.56494
|  | 16:50 | 21.1733 | -0.13986 | 0.56494
|  | 16:50 | 21.1744 | -0.143 | 0.56494
|  | 16:50 | 21.1756 | -0.15783 | 0.56493
|  | 16:50 | 21.1767 | -0.18435 | 0.56493
|  | 16:50 | 21.1778 | -0.21088 | 0.56493
|  | 16:50 | 21.1789 | -0.23015 | 0.56493
|  | 16:50 | 21.18 | -0.24943 | 0.56492
|  | 16:50 | 21.1811 | -0.27026 | 0.56492
|  | 16:50 | 21.1822 | -0.29265 | 0.56492
|  | 16:50 | 21.1833 | -0.31503 | 0.56492
|  | 16:50 | 21.1844 | -0.32195 | 0.56491
|  | 16:51 | 21.1856 | -0.32886 | 0.56491
|  | 16:51 | 21.1867 | -0.34119 | 0.56491
|  | 16:51 | 21.1878 | -0.35894 | 0.56491
|  | 16:51 | 21.1889 | -0.37669 | 0.56491
|  | 16:51 | 21.19 | -0.40678 | 0.5649
|  | 16:51 | 21.1911 | -0.43687 | 0.5649
|  | 16:51 | 21.1922 | -0.47126 | 0.5649
|  | 16:51 | 21.1933 | -0.50996 | 0.5649
|  | 16:51 | 21.1944 | -0.54865 | 0.56489
|  | 16:51 | 21.1956 | -0.56956 | 0.56489
|  | 16:51 | 21.1967 | -0.59046 | 0.56489
|  | 16:51 | 21.1978 | -0.60099 | 0.56489
|  | 16:51 | 21.1989 | -0.60114 | 0.56488
|  | 16:51 | 21.2 | -0.60129 | 0.56488
|  | 16:51 | 21.2011 | -0.60725 | 0.56488
|  | 16:52 | 21.2022 | -0.6132 | 0.56488
|  | 16:52 | 21.2033 | -0.61495 | 0.56487
|  | 16:52 | 21.2044 | -0.6125 | 0.56487
|  | 16:52 | 21.2056 | -0.61004 | 0.56487
|  | 16:52 | 21.2067 | -0.60192 | 0.56487
|  | 16:52 | 21.2078 | -0.59379 | 0.56487
|  | 16:52 | 21.2089 | -0.57338 | 0.56486
|  | 16:52 | 21.21 | -0.54068 | 0.56486
|  | 16:52 | 21.2111 | -0.50798 | 0.56486
|  | 16:52 | 21.2122 | -0.44948 | 0.56486
|  | 16:52 | 21.2133 | -0.39097 | 0.56485
|  | 16:52 | 21.2144 | -0.34491 | 0.56485
|  | 16:52 | 21.2156 | -0.30298 | 0.56485
|  | 16:52 | 21.2167 | -0.26106 | 0.56485
|  | 16:52 | 21.2178 | -0.21372 | 0.56484
|  | 16:53 | 21.2189 | -0.16637 | 0.56484
|  | 16:53 | 21.22 | -0.13138 | 0.56484
|  | 16:53 | 21.2211 | -0.10875 | 0.56484
|  | 16:53 | 21.2222 | -0.086123 | 0.56484
|  | 16:53 | 21.2233 | -0.059309 | 0.56483
|  | 16:53 | 21.2244 | -0.032495 | 0.56483
|  | 16:53 | 21.2256 | -0.0085625 | 0.56483
|  | 16:53 | 21.2267 | 0.01441 | 0.56483
|  | 16:53 | 21.2278 | 0.037382 | 0.56482
|  | 16:53 | 21.2289 | 0.066252 | 0.56482
|  | 16:53 | 21.23 | 0.095122 | 0.56482
|  | 16:53 | 21.2311 | 0.10872 | 0.56482
|  | 16:53 | 21.2322 | 0.10704 | 0.56481
|  | 16:53 | 21.2333 | 0.10536 | 0.56481
|  | 16:53 | 21.2344 | 0.10089 | 0.56481
|  | 16:54 | 21.2356 | 0.088038 | 0.56481
|  | 16:54 | 21.2367 | 0.080428 | 0.56481
|  | 16:54 | 21.2378 | 0.078054 | 0.5648
|  | 16:54 | 21.2389 | 0.07568 | 0.5648
|  | 16:54 | 21.24 | 0.060873 | 0.5648
|  | 16:54 | 21.2411 | 0.046067 | 0.5648
|  | 16:54 | 21.2422 | 0.032489 | 0.56479
|  | 16:54 | 21.2433 | 0.02014 | 0.56479
|  | 16:54 | 21.2444 | 0.0077913 | 0.56479
|  | 16:54 | 21.2456 | 0.0089382 | 0.56479
|  | 16:54 | 21.2467 | 0.010085 | 0.56478
|  | 16:54 | 21.2478 | 0.017944 | 0.56478
|  | 16:54 | 21.2489 | 0.032514 | 0.56478
|  | 16:54 | 21.25 | 0.047085 | 0.56478
|  | 16:54 | 21.2511 | 0.076109 | 0.56478
|  | 16:55 | 21.2522 | 0.10513 | 0.56477
|  | 16:55 | 21.2533 | 0.13867 | 0.56477
|  | 16:55 | 21.2544 | 0.17371 | 0.56477
|  | 16:55 | 21.2556 | 0.20875 | 0.56477
|  | 16:55 | 21.2567 | 0.23334 | 0.56476
|  | 16:55 | 21.2578 | 0.25792 | 0.56476
|  | 16:55 | 21.2589 | 0.27615 | 0.56476
|  | 16:55 | 21.26 | 0.28804 | 0.56476
|  | 16:55 | 21.2611 | 0.29992 | 0.56475
|  | 16:55 | 21.2622 | 0.31798 | 0.56475
|  | 16:55 | 21.2633 | 0.33605 | 0.56475
|  | 16:55 | 21.2644 | 0.36385 | 0.56475
|  | 16:55 | 21.2656 | 0.40137 | 0.56475
|  | 16:55 | 21.2667 | 0.4389 | 0.56474
|  | 16:55 | 21.2678 | 0.47837 | 0.56474
|  | 16:56 | 21.2689 | 0.51784 | 0.56474
|  | 16:56 | 21.27 | 0.54605 | 0.56474
|  | 16:56 | 21.2711 | 0.57051 | 0.56473
|  | 16:56 | 21.2722 | 0.59043 | 0.56473
|  | 16:56 | 21.2733 | 0.59672 | 0.56473
|  | 16:56 | 21.2744 | 0.60301 | 0.56473
|  | 16:56 | 21.2756 | 0.61476 | 0.56472
|  | 16:56 | 21.2767 | 0.62833 | 0.56472
|  | 16:56 | 21.2778 | 0.63908 | 0.56472
|  | 16:56 | 21.2789 | 0.64134 | 0.56472
|  | 16:56 | 21.28 | 0.6436 | 0.56472
|  | 16:56 | 21.2811 | 0.64966 | 0.56471
|  | 16:56 | 21.2822 | 0.65699 | 0.56471
|  | 16:56 | 21.2833 | 0.66861 | 0.56471
|  | 16:56 | 21.2844 | 0.69311 | 0.56471
|  | 16:57 | 21.2856 | 0.71761 | 0.5647
|  | 16:57 | 21.2867 | 0.72431 | 0.5647
|  | 16:57 | 21.2878 | 0.72507 | 0.5647
|  | 16:57 | 21.2889 | 0.72324 | 0.5647
|  | 16:57 | 21.29 | 0.71361 | 0.56469
|  | 16:57 | 21.2911 | 0.70399 | 0.56469
|  | 16:57 | 21.2922 | 0.68391 | 0.56469
|  | 16:57 | 21.2933 | 0.66036 | 0.56469
|  | 16:57 | 21.2944 | 0.63042 | 0.56469
|  | 16:57 | 21.2956 | 0.58134 | 0.56468
|  | 16:57 | 21.2967 | 0.53226 | 0.56468
|  | 16:57 | 21.2978 | 0.48119 | 0.56468
|  | 16:57 | 21.2989 | 0.42944 | 0.56468
|  | 16:57 | 21.3 | 0.38903 | 0.56467
|  | 16:57 | 21.3011 | 0.35995 | 0.56467
|  | 16:58 | 21.3022 | 0.33088 | 0.56467
|  | 16:58 | 21.3033 | 0.2821 | 0.56467
|  | 16:58 | 21.3044 | 0.22676 | 0.56466
|  | 16:58 | 21.3056 | 0.17658 | 0.56466
|  | 16:58 | 21.3067 | 0.1419 | 0.56466
|  | 16:58 | 21.3078 | 0.10722 | 0.56466
|  | 16:58 | 21.3089 | 0.081901 | 0.56466
|  | 16:58 | 21.31 | 0.056586 | 0.56465
|  | 16:58 | 21.3111 | 0.030142 | 0.56465
|  | 16:58 | 21.3122 | 0.00031549 | 0.56465
|  | 16:58 | 21.3133 | -0.029511 | 0.56465
|  | 16:58 | 21.3144 | -0.058698 | 0.56464
|  | 16:58 | 21.3156 | -0.087671 | 0.56464
|  | 16:58 | 21.3167 | -0.11306 | 0.56464
|  | 16:58 | 21.3178 | -0.12771 | 0.56464
|  | 16:59 | 21.3189 | -0.14236 | 0.56463
|  | 16:59 | 21.32 | -0.16624 | 0.56463
|  | 16:59 | 21.3211 | -0.1932 | 0.56463
|  | 16:59 | 21.3222 | -0.22575 | 0.56463
|  | 16:59 | 21.3233 | -0.2751 | 0.56462
|  | 16:59 | 21.3244 | -0.32445 | 0.56462
|  | 16:59 | 21.3256 | -0.35449 | 0.56462
|  | 16:59 | 21.3267 | -0.37809 | 0.56462
|  | 16:59 | 21.3278 | -0.39723 | 0.56462
|  | 16:59 | 21.3289 | -0.40298 | 0.56461
|  | 16:59 | 21.33 | -0.40874 | 0.56461
|  | 16:59 | 21.3311 | -0.41121 | 0.56461
|  | 16:59 | 21.3322 | -0.41258 | 0.56461
|  | 16:59 | 21.3333 | -0.4191 | 0.5646
|  | 16:59 | 21.3344 | -0.44105 | 0.5646
|  | 17:00 | 21.3356 | -0.46301 | 0.5646
|  | 17:00 | 21.3367 | -0.4794 | 0.5646
|  | 17:00 | 21.3378 | -0.49394 | 0.56459
|  | 17:00 | 21.3389 | -0.50803 | 0.56459
|  | 17:00 | 21.34 | -0.52082 | 0.56459
|  | 17:00 | 21.3411 | -0.53361 | 0.56459
|  | 17:00 | 21.3422 | -0.57167 | 0.56459
|  | 17:00 | 21.3433 | -0.61817 | 0.56458
|  | 17:00 | 21.3444 | -0.65686 | 0.56458
|  | 17:00 | 21.3456 | -0.67212 | 0.56458
|  | 17:00 | 21.3467 | -0.68739 | 0.56458
|  | 17:00 | 21.3478 | -0.69862 | 0.56457
|  | 17:00 | 21.3489 | -0.7085 | 0.56457
|  | 17:00 | 21.35 | -0.7136 | 0.56457
|  | 17:00 | 21.3511 | -0.70432 | 0.56457
|  | 17:01 | 21.3522 | -0.69505 | 0.56456
|  | 17:01 | 21.3533 | -0.67207 | 0.56456
|  | 17:01 | 21.3544 | -0.64451 | 0.56456
|  | 17:01 | 21.3556 | -0.61836 | 0.56456
|  | 17:01 | 21.3567 | -0.59644 | 0.56456
|  | 17:01 | 21.3578 | -0.57451 | 0.56455
|  | 17:01 | 21.3589 | -0.55325 | 0.56455
|  | 17:01 | 21.36 | -0.53222 | 0.56455
|  | 17:01 | 21.3611 | -0.51696 | 0.56455
|  | 17:01 | 21.3622 | -0.51903 | 0.56454
|  | 17:01 | 21.3633 | -0.5211 | 0.56454
|  | 17:01 | 21.3644 | -0.52402 | 0.56454
|  | 17:01 | 21.3656 | -0.52724 | 0.56454
|  | 17:01 | 21.3667 | -0.52781 | 0.56453
|  | 17:01 | 21.3678 | -0.52046 | 0.56453
|  | 17:02 | 21.3689 | -0.51311 | 0.56453
|  | 17:02 | 21.37 | -0.49295 | 0.56453
|  | 17:02 | 21.3711 | -0.46852 | 0.56453
|  | 17:02 | 21.3722 | -0.44277 | 0.56452
|  | 17:02 | 21.3733 | -0.41302 | 0.56452
|  | 17:02 | 21.3744 | -0.38327 | 0.56452
|  | 17:02 | 21.3756 | -0.36219 | 0.56452
|  | 17:02 | 21.3767 | -0.34399 | 0.56451
|  | 17:02 | 21.3778 | -0.32331 | 0.56451
|  | 17:02 | 21.3789 | -0.29521 | 0.56451
|  | 17:02 | 21.38 | -0.26711 | 0.56451
|  | 17:02 | 21.3811 | -0.22818 | 0.5645
|  | 17:02 | 21.3822 | -0.18565 | 0.5645
|  | 17:02 | 21.3833 | -0.14681 | 0.5645
|  | 17:02 | 21.3844 | -0.11909 | 0.5645
|  | 17:03 | 21.3856 | -0.091362 | 0.5645
|  | 17:03 | 21.3867 | -0.063635 | 0.56449
|  | 17:03 | 21.3878 | -0.035909 | 0.56449
|  | 17:03 | 21.3889 | -0.010399 | 0.56449
|  | 17:03 | 21.39 | 0.008462 | 0.56449
|  | 17:03 | 21.3911 | 0.027323 | 0.56448
|  | 17:03 | 21.3922 | 0.034398 | 0.56448
|  | 17:03 | 21.3933 | 0.037546 | 0.56448
|  | 17:03 | 21.3944 | 0.043552 | 0.56448
|  | 17:03 | 21.3956 | 0.058133 | 0.56447
|  | 17:03 | 21.3967 | 0.072714 | 0.56447
|  | 17:03 | 21.3978 | 0.058027 | 0.56447
|  | 17:03 | 21.3989 | 0.033585 | 0.56447
|  | 17:03 | 21.4 | 0.0091424 | 0.56447
|  | 17:03 | 21.4011 | -0.0069915 | 0.56446
|  | 17:04 | 21.4022 | -0.014817 | 0.56446
|  | 17:04 | 21.4033 | -0.013008 | 0.56446
|  | 17:04 | 21.4044 | -0.0079873 | 0.56446
|  | 17:04 | 21.4056 | -0.0032145 | 0.56445
|  | 17:04 | 21.4067 | 0.00081442 | 0.56445
|  | 17:04 | 21.4078 | 0.0048433 | 0.56445
|  | 17:04 | 21.4089 | -0.011699 | 0.56445
|  | 17:04 | 21.41 | -0.035099 | 0.56444
|  | 17:04 | 21.4111 | -0.062149 | 0.56444
|  | 17:04 | 21.4122 | -0.10015 | 0.56444
|  | 17:04 | 21.4133 | -0.13814 | 0.56444
|  | 17:04 | 21.4144 | -0.15922 | 0.56444
|  | 17:04 | 21.4156 | -0.17466 | 0.56443
|  | 17:04 | 21.4167 | -0.18651 | 0.56443
|  | 17:04 | 21.4178 | -0.18759 | 0.56443
|  | 17:05 | 21.4189 | -0.18868 | 0.56443
|  | 17:05 | 21.42 | -0.16432 | 0.56442
|  | 17:05 | 21.4211 | -0.13147 | 0.56442
|  | 17:05 | 21.4222 | -0.097254 | 0.56442
|  | 17:05 | 21.4233 | -0.058911 | 0.56442
|  | 17:05 | 21.4244 | -0.020569 | 0.56441
|  | 17:05 | 21.4256 | 0.017096 | 0.56441
|  | 17:05 | 21.4267 | 0.054534 | 0.56441
|  | 17:05 | 21.4278 | 0.085579 | 0.56441
|  | 17:05 | 21.4289 | 0.097447 | 0.56441
|  | 17:05 | 21.43 | 0.10931 | 0.5644
|  | 17:05 | 21.4311 | 0.11074 | 0.5644
|  | 17:05 | 21.4322 | 0.10868 | 0.5644
|  | 17:05 | 21.4333 | 0.10522 | 0.5644
|  | 17:05 | 21.4344 | 0.097578 | 0.56439
|  | 17:06 | 21.4356 | 0.089932 | 0.56439
|  | 17:06 | 21.4367 | 0.073569 | 0.56439
|  | 17:06 | 21.4378 | 0.048491 | 0.56439
|  | 17:06 | 21.4389 | 0.023412 | 0.56438
|  | 17:06 | 21.44 | 0.0095454 | 0.56438
|  | 17:06 | 21.4411 | -0.0043213 | 0.56438
|  | 17:06 | 21.4422 | -0.0022857 | 0.56438
|  | 17:06 | 21.4433 | 0.015652 | 0.56437
|  | 17:06 | 21.4444 | 0.03359 | 0.56437
|  | 17:06 | 21.4456 | 0.10038 | 0.56437
|  | 17:06 | 21.4467 | 0.16717 | 0.56437
|  | 17:06 | 21.4478 | 0.23184 | 0.56437
|  | 17:06 | 21.4489 | 0.29437 | 0.56436
|  | 17:06 | 21.45 | 0.35691 | 0.56436
|  | 17:06 | 21.4511 | 0.38203 | 0.56436
|  | 17:07 | 21.4522 | 0.40715 | 0.56436
|  | 17:07 | 21.4533 | 0.43669 | 0.56435
|  | 17:07 | 21.4544 | 0.47067 | 0.56435
|  | 17:07 | 21.4556 | 0.50464 | 0.56435
|  | 17:07 | 21.4567 | 0.51512 | 0.56435
|  | 17:07 | 21.4578 | 0.52559 | 0.56434
|  | 17:07 | 21.4589 | 0.54013 | 0.56434
|  | 17:07 | 21.46 | 0.55874 | 0.56434
|  | 17:07 | 21.4611 | 0.57735 | 0.56434
|  | 17:07 | 21.4622 | 0.57414 | 0.56434
|  | 17:07 | 21.4633 | 0.57092 | 0.56433
|  | 17:07 | 21.4644 | 0.57038 | 0.56433
|  | 17:07 | 21.4656 | 0.57251 | 0.56433
|  | 17:07 | 21.4667 | 0.57464 | 0.56433
|  | 17:07 | 21.4678 | 0.57446 | 0.56432
|  | 17:08 | 21.4689 | 0.57428 | 0.56432
|  | 17:08 | 21.47 | 0.56794 | 0.56432
|  | 17:08 | 21.4711 | 0.55544 | 0.56432
|  | 17:08 | 21.4722 | 0.54294 | 0.56431
|  | 17:08 | 21.4733 | 0.53362 | 0.56431
|  | 17:08 | 21.4744 | 0.52431 | 0.56431
|  | 17:08 | 21.4756 | 0.51346 | 0.56431
|  | 17:08 | 21.4767 | 0.50109 | 0.56431
|  | 17:08 | 21.4778 | 0.48871 | 0.5643
|  | 17:08 | 21.4789 | 0.46532 | 0.5643
|  | 17:08 | 21.48 | 0.44193 | 0.5643
|  | 17:08 | 21.4811 | 0.41736 | 0.5643
|  | 17:08 | 21.4822 | 0.39241 | 0.56429
|  | 17:08 | 21.4833 | 0.36745 | 0.56429
|  | 17:08 | 21.4844 | 0.32955 | 0.56429
|  | 17:09 | 21.4856 | 0.29165 | 0.56429
|  | 17:09 | 21.4867 | 0.25312 | 0.56428
|  | 17:09 | 21.4878 | 0.21396 | 0.56428
|  | 17:09 | 21.4889 | 0.1748 | 0.56428
|  | 17:09 | 21.49 | 0.11481 | 0.56428
|  | 17:09 | 21.4911 | 0.054818 | 0.56428
|  | 17:09 | 21.4922 | -0.0065868 | 0.56427
|  | 17:09 | 21.4933 | -0.068462 | 0.56427
|  | 17:09 | 21.4944 | -0.13034 | 0.56427
|  | 17:09 | 21.4956 | -0.17611 | 0.56427
|  | 17:09 | 21.4967 | -0.22189 | 0.56426
|  | 17:09 | 21.4978 | -0.26715 | 0.56426
|  | 17:09 | 21.4989 | -0.3119 | 0.56426
|  | 17:09 | 21.5 | -0.35665 | 0.56426
|  | 17:09 | 21.5011 | -0.39577 | 0.56425
|  | 17:10 | 21.5022 | -0.43489 | 0.56425
|  | 17:10 | 21.5033 | -0.45765 | 0.56425
|  | 17:10 | 21.5044 | -0.46406 | 0.56425
|  | 17:10 | 21.5056 | -0.47047 | 0.56425
|  | 17:10 | 21.5067 | -0.45239 | 0.56424
|  | 17:10 | 21.5078 | -0.4343 | 0.56424
|  | 17:10 | 21.5089 | -0.42879 | 0.56424
|  | 17:10 | 21.51 | -0.43588 | 0.56424
|  | 17:10 | 21.5111 | -0.44296 | 0.56423
|  | 17:10 | 21.5122 | -0.44646 | 0.56423
|  | 17:10 | 21.5133 | -0.44997 | 0.56423
|  | 17:10 | 21.5144 | -0.44712 | 0.56423
|  | 17:10 | 21.5156 | -0.43794 | 0.56422
|  | 17:10 | 21.5167 | -0.42875 | 0.56422
|  | 17:10 | 21.5178 | -0.42518 | 0.56422
|  | 17:11 | 21.5189 | -0.42161 | 0.56422
|  | 17:11 | 21.52 | -0.42556 | 0.56422
|  | 17:11 | 21.5211 | -0.43704 | 0.56421
|  | 17:11 | 21.5222 | -0.44852 | 0.56421
|  | 17:11 | 21.5233 | -0.44164 | 0.56421
|  | 17:11 | 21.5244 | -0.43475 | 0.56421
|  | 17:11 | 21.5256 | -0.42925 | 0.5642
|  | 17:11 | 21.5267 | -0.42513 | 0.5642
|  | 17:11 | 21.5278 | -0.421 | 0.5642
|  | 17:11 | 21.5289 | -0.40086 | 0.5642
|  | 17:11 | 21.53 | -0.38072 | 0.56419
|  | 17:11 | 21.5311 | -0.36457 | 0.56419
|  | 17:11 | 21.5322 | -0.35242 | 0.56419
|  | 17:11 | 21.5333 | -0.34187 | 0.56419
|  | 17:11 | 21.5344 | -0.33616 | 0.56419
|  | 17:12 | 21.5356 | -0.33044 | 0.56418
|  | 17:12 | 21.5367 | -0.31632 | 0.56418
|  | 17:12 | 21.5378 | -0.29381 | 0.56418
|  | 17:12 | 21.5389 | -0.2713 | 0.56418
|  | 17:12 | 21.54 | -0.25262 | 0.56417
|  | 17:12 | 21.5411 | -0.23394 | 0.56417
|  | 17:12 | 21.5422 | -0.21066 | 0.56417
|  | 17:12 | 21.5433 | -0.18278 | 0.56417
|  | 17:12 | 21.5444 | -0.1549 | 0.56416
|  | 17:12 | 21.5456 | -0.1598 | 0.56416
|  | 17:12 | 21.5467 | -0.1647 | 0.56416
|  | 17:12 | 21.5478 | -0.16862 | 0.56416
|  | 17:12 | 21.5489 | -0.17156 | 0.56416
|  | 17:12 | 21.55 | -0.17451 | 0.56415
|  | 17:12 | 21.5511 | -0.16854 | 0.56415
|  | 17:13 | 21.5522 | -0.16258 | 0.56415
|  | 17:13 | 21.5533 | -0.16124 | 0.56415
|  | 17:13 | 21.5544 | -0.16454 | 0.56414
|  | 17:13 | 21.5556 | -0.16783 | 0.56414
|  | 17:13 | 21.5567 | -0.15843 | 0.56414
|  | 17:13 | 21.5578 | -0.14903 | 0.56414
|  | 17:13 | 21.5589 | -0.12965 | 0.56413
|  | 17:13 | 21.56 | -0.10029 | 0.56413
|  | 17:13 | 21.5611 | -0.070943 | 0.56413
|  | 17:13 | 21.5622 | -0.066805 | 0.56413
|  | 17:13 | 21.5633 | -0.062667 | 0.56412
|  | 17:13 | 21.5644 | -0.054492 | 0.56412
|  | 17:13 | 21.5656 | -0.042281 | 0.56412
|  | 17:13 | 21.5667 | -0.030069 | 0.56412
|  | 17:13 | 21.5678 | -0.017858 | 0.56412
|  | 17:14 | 21.5689 | 0.0074794 | 0.56411
|  | 17:14 | 21.57 | 0.030449 | 0.56411
|  | 17:14 | 21.5711 | 0.046317 | 0.56411
|  | 17:14 | 21.5722 | 0.062185 | 0.56411
|  | 17:14 | 21.5733 | 0.082672 | 0.5641
|  | 17:14 | 21.5744 | 0.10316 | 0.5641
|  | 17:14 | 21.5756 | 0.12318 | 0.5641
|  | 17:14 | 21.5767 | 0.14273 | 0.5641
|  | 17:14 | 21.5778 | 0.16229 | 0.56409
|  | 17:14 | 21.5789 | 0.17597 | 0.56409
|  | 17:14 | 21.58 | 0.18965 | 0.56409
|  | 17:14 | 21.5811 | 0.21106 | 0.56409
|  | 17:14 | 21.5822 | 0.24018 | 0.56409
|  | 17:14 | 21.5833 | 0.2693 | 0.56408
|  | 17:14 | 21.5844 | 0.28985 | 0.56408
|  | 17:15 | 21.5856 | 0.3104 | 0.56408
|  | 17:15 | 21.5867 | 0.32411 | 0.56408
|  | 17:15 | 21.5878 | 0.33098 | 0.56407
|  | 17:15 | 21.5889 | 0.33785 | 0.56407
|  | 17:15 | 21.59 | 0.3406 | 0.56407
|  | 17:15 | 21.5911 | 0.34335 | 0.56407
|  | 17:15 | 21.5922 | 0.34433 | 0.56406
|  | 17:15 | 21.5933 | 0.34356 | 0.56406
|  | 17:15 | 21.5944 | 0.34278 | 0.56406
|  | 17:15 | 21.5956 | 0.3594 | 0.56406
|  | 17:15 | 21.5967 | 0.37602 | 0.56406
|  | 17:15 | 21.5978 | 0.39263 | 0.56405
|  | 17:15 | 21.5989 | 0.40925 | 0.56405
|  | 17:15 | 21.6 | 0.42587 | 0.56405
|  | 17:15 | 21.6011 | 0.4182 | 0.56405
|  | 17:16 | 21.6022 | 0.41053 | 0.56404
|  | 17:16 | 21.6033 | 0.39842 | 0.56404
|  | 17:16 | 21.6044 | 0.38187 | 0.56404
|  | 17:16 | 21.6056 | 0.36532 | 0.56404
|  | 17:16 | 21.6067 | 0.33087 | 0.56403
|  | 17:16 | 21.6078 | 0.29642 | 0.56403
|  | 17:16 | 21.6089 | 0.28083 | 0.56403
|  | 17:16 | 21.61 | 0.28412 | 0.56403
|  | 17:16 | 21.6111 | 0.2874 | 0.56403
|  | 17:16 | 21.6122 | 0.2724 | 0.56402
|  | 17:16 | 21.6133 | 0.2574 | 0.56402
|  | 17:16 | 21.6144 | 0.2361 | 0.56402
|  | 17:16 | 21.6156 | 0.2085 | 0.56402
|  | 17:16 | 21.6167 | 0.18089 | 0.56401
|  | 17:16 | 21.6178 | 0.14929 | 0.56401
|  | 17:17 | 21.6189 | 0.11769 | 0.56401
|  | 17:17 | 21.62 | 0.10424 | 0.56401
|  | 17:17 | 21.6211 | 0.096831 | 0.564
|  | 17:17 | 21.6222 | 0.089426 | 0.564
|  | 17:17 | 21.6233 | 0.072852 | 0.564
|  | 17:17 | 21.6244 | 0.056277 | 0.564
|  | 17:17 | 21.6256 | 0.041294 | 0.564
|  | 17:17 | 21.6267 | 0.027902 | 0.56399
|  | 17:17 | 21.6278 | 0.01451 | 0.56399
|  | 17:17 | 21.6289 | -0.0091688 | 0.56399
|  | 17:17 | 21.63 | -0.032848 | 0.56399
|  | 17:17 | 21.6311 | -0.066966 | 0.56398
|  | 17:17 | 21.6322 | -0.11152 | 0.56398
|  | 17:17 | 21.6333 | -0.15608 | 0.56398
|  | 17:17 | 21.6344 | -0.17782 | 0.56398
|  | 17:18 | 21.6356 | -0.19956 | 0.56397
|  | 17:18 | 21.6367 | -0.21505 | 0.56397
|  | 17:18 | 21.6378 | -0.2243 | 0.56397
|  | 17:18 | 21.6389 | -0.23485 | 0.56397
|  | 17:18 | 21.64 | -0.24933 | 0.56397
|  | 17:18 | 21.6411 | -0.26381 | 0.56396
|  | 17:18 | 21.6422 | -0.28585 | 0.56396
|  | 17:18 | 21.6433 | -0.31041 | 0.56396
|  | 17:18 | 21.6444 | -0.33498 | 0.56396
|  | 17:18 | 21.6456 | -0.35433 | 0.56395
|  | 17:18 | 21.6467 | -0.37369 | 0.56395
|  | 17:18 | 21.6478 | -0.38334 | 0.56395
|  | 17:18 | 21.6489 | -0.38329 | 0.56395
|  | 17:18 | 21.65 | -0.38325 | 0.56394
|  | 17:18 | 21.6511 | -0.37177 | 0.56394
|  | 17:19 | 21.6522 | -0.36028 | 0.56394
|  | 17:19 | 21.6533 | -0.34955 | 0.56394
|  | 17:19 | 21.6544 | -0.33956 | 0.56394
|  | 17:19 | 21.6556 | -0.32957 | 0.56393
|  | 17:19 | 21.6567 | -0.32282 | 0.56393
|  | 17:19 | 21.6578 | -0.31608 | 0.56393
|  | 17:19 | 21.6589 | -0.30933 | 0.56393
|  | 17:19 | 21.66 | -0.30258 | 0.56392
|  | 17:19 | 21.6611 | -0.2977 | 0.56392
|  | 17:19 | 21.6622 | -0.29843 | 0.56392
|  | 17:19 | 21.6633 | -0.29916 | 0.56392
|  | 17:19 | 21.6644 | -0.3059 | 0.56391
|  | 17:19 | 21.6656 | -0.31865 | 0.56391
|  | 17:19 | 21.6667 | -0.33141 | 0.56391
|  | 17:19 | 21.6678 | -0.34928 | 0.56391
|  | 17:20 | 21.6689 | -0.36715 | 0.56391
|  | 17:20 | 21.67 | -0.36743 | 0.5639
|  | 17:20 | 21.6711 | -0.35014 | 0.5639
|  | 17:20 | 21.6722 | -0.33284 | 0.5639
|  | 17:20 | 21.6733 | -0.32614 | 0.5639
|  | 17:20 | 21.6744 | -0.31945 | 0.56389
|  | 17:20 | 21.6756 | -0.32347 | 0.56389
|  | 17:20 | 21.6767 | -0.33105 | 0.56389
|  | 17:20 | 21.6778 | -0.33863 | 0.56389
|  | 17:20 | 21.6789 | -0.34742 | 0.56388
|  | 17:20 | 21.68 | -0.35621 | 0.56388
|  | 17:20 | 21.6811 | -0.35525 | 0.56388
|  | 17:20 | 21.6822 | -0.34453 | 0.56388
|  | 17:20 | 21.6833 | -0.33382 | 0.56387
|  | 17:20 | 21.6844 | -0.32408 | 0.56387
|  | 17:21 | 21.6856 | -0.31435 | 0.56387
|  | 17:21 | 21.6867 | -0.29629 | 0.56387
|  | 17:21 | 21.6878 | -0.2699 | 0.56387
|  | 17:21 | 21.6889 | -0.24351 | 0.56386
|  | 17:21 | 21.69 | -0.22981 | 0.56386
|  | 17:21 | 21.6911 | -0.21611 | 0.56386
|  | 17:21 | 21.6922 | -0.19988 | 0.56386
|  | 17:21 | 21.6933 | -0.18112 | 0.56385
|  | 17:21 | 21.6944 | -0.16235 | 0.56385
|  | 17:21 | 21.6956 | -0.16142 | 0.56385
|  | 17:21 | 21.6967 | -0.16049 | 0.56385
|  | 17:21 | 21.6978 | -0.15389 | 0.56384
|  | 17:21 | 21.6989 | -0.14164 | 0.56384
|  | 17:21 | 21.7 | -0.12939 | 0.56384
|  | 17:21 | 21.7011 | -0.12526 | 0.56384
|  | 17:22 | 21.7022 | -0.12113 | 0.56384
|  | 17:22 | 21.7033 | -0.12313 | 0.56383
|  | 17:22 | 21.7044 | -0.13125 | 0.56383
|  | 17:22 | 21.7056 | -0.13938 | 0.56383
|  | 17:22 | 21.7067 | -0.13197 | 0.56383
|  | 17:22 | 21.7078 | -0.12456 | 0.56382
|  | 17:22 | 21.7089 | -0.11274 | 0.56382
|  | 17:22 | 21.71 | -0.096521 | 0.56382
|  | 17:22 | 21.7111 | -0.080302 | 0.56382
|  | 17:22 | 21.7122 | -0.054155 | 0.56381
|  | 17:22 | 21.7133 | -0.028008 | 0.56381
|  | 17:22 | 21.7144 | -0.0045076 | 0.56381
|  | 17:22 | 21.7156 | 0.016347 | 0.56381
|  | 17:22 | 21.7167 | 0.037201 | 0.56381
|  | 17:22 | 21.7178 | 0.038561 | 0.5638
|  | 17:23 | 21.7189 | 0.039921 | 0.5638
|  | 17:23 | 21.72 | 0.04462 | 0.5638
|  | 17:23 | 21.7211 | 0.052657 | 0.5638
|  | 17:23 | 21.7222 | 0.060695 | 0.56379
|  | 17:23 | 21.7233 | 0.062016 | 0.56379
|  | 17:23 | 21.7244 | 0.063337 | 0.56379
|  | 17:23 | 21.7256 | 0.059152 | 0.56379
|  | 17:23 | 21.7267 | 0.049461 | 0.56378
|  | 17:23 | 21.7278 | 0.039771 | 0.56378
|  | 17:23 | 21.7289 | 0.03008 | 0.56378
|  | 17:23 | 21.73 | 0.02039 | 0.56378
|  | 17:23 | 21.7311 | 0.012533 | 0.56378
|  | 17:23 | 21.7322 | 0.00651 | 0.56377
|  | 17:23 | 21.7333 | 0.00048686 | 0.56377
|  | 17:23 | 21.7344 | -0.0055363 | 0.56377
|  | 17:24 | 21.7356 | -0.028667 | 0.56377
|  | 17:24 | 21.7367 | -0.055754 | 0.56376
|  | 17:24 | 21.7378 | -0.094714 | 0.56376
|  | 17:24 | 21.7389 | -0.13367 | 0.56376
|  | 17:24 | 21.74 | -0.1564 | 0.56376
|  | 17:24 | 21.7411 | -0.17912 | 0.56375
|  | 17:24 | 21.7422 | -0.20465 | 0.56375
|  | 17:24 | 21.7433 | -0.23296 | 0.56375
|  | 17:24 | 21.7444 | -0.26128 | 0.56375
|  | 17:24 | 21.7456 | -0.28713 | 0.56375
|  | 17:24 | 21.7467 | -0.31299 | 0.56374
|  | 17:24 | 21.7478 | -0.3269 | 0.56374
|  | 17:24 | 21.7489 | -0.32887 | 0.56374
|  | 17:24 | 21.75 | -0.33084 | 0.56374
|  | 17:24 | 21.7511 | -0.34417 | 0.56373
|  | 17:25 | 21.7522 | -0.35749 | 0.56373
|  | 17:25 | 21.7533 | -0.36829 | 0.56373
|  | 17:25 | 21.7544 | -0.37657 | 0.56373
|  | 17:25 | 21.7556 | -0.38484 | 0.56372
|  | 17:25 | 21.7567 | -0.39763 | 0.56372
|  | 17:25 | 21.7578 | -0.41043 | 0.56372
|  | 17:25 | 21.7589 | -0.42784 | 0.56372
|  | 17:25 | 21.76 | -0.44987 | 0.56372
|  | 17:25 | 21.7611 | -0.4719 | 0.56371
|  | 17:25 | 21.7622 | -0.49075 | 0.56371
|  | 17:25 | 21.7633 | -0.50959 | 0.56371
|  | 17:25 | 21.7644 | -0.5272 | 0.56371
|  | 17:25 | 21.7656 | -0.54355 | 0.5637
|  | 17:25 | 21.7667 | -0.5599 | 0.5637
|  | 17:25 | 21.7678 | -0.58263 | 0.5637
|  | 17:26 | 21.7689 | -0.60537 | 0.5637
|  | 17:26 | 21.77 | -0.62365 | 0.56369
|  | 17:26 | 21.7711 | -0.63747 | 0.56369
|  | 17:26 | 21.7722 | -0.65129 | 0.56369
|  | 17:26 | 21.7733 | -0.65879 | 0.56369
|  | 17:26 | 21.7744 | -0.66629 | 0.56369
|  | 17:26 | 21.7756 | -0.67986 | 0.56368
|  | 17:26 | 21.7767 | -0.6995 | 0.56368
|  | 17:26 | 21.7778 | -0.71913 | 0.56368
|  | 17:26 | 21.7789 | -0.73168 | 0.56368
|  | 17:26 | 21.78 | -0.74423 | 0.56367
|  | 17:26 | 21.7811 | -0.7505 | 0.56367
|  | 17:26 | 21.7822 | -0.75049 | 0.56367
|  | 17:26 | 21.7833 | -0.75048 | 0.56367
|  | 17:26 | 21.7844 | -0.73916 | 0.56366
|  | 17:27 | 21.7856 | -0.72783 | 0.56366
|  | 17:27 | 21.7867 | -0.70987 | 0.56366
|  | 17:27 | 21.7878 | -0.68526 | 0.56366
|  | 17:27 | 21.7889 | -0.66066 | 0.56366
|  | 17:27 | 21.79 | -0.6495 | 0.56365
|  | 17:27 | 21.7911 | -0.63834 | 0.56365
|  | 17:27 | 21.7922 | -0.61665 | 0.56365
|  | 17:27 | 21.7933 | -0.58443 | 0.56365
|  | 17:27 | 21.7944 | -0.55221 | 0.56364
|  | 17:27 | 21.7956 | -0.51541 | 0.56364
|  | 17:27 | 21.7967 | -0.47861 | 0.56364
|  | 17:27 | 21.7978 | -0.44523 | 0.56364
|  | 17:27 | 21.7989 | -0.41524 | 0.56363
|  | 17:27 | 21.8 | -0.38526 | 0.56363
|  | 17:27 | 21.8011 | -0.37899 | 0.56363
|  | 17:28 | 21.8022 | -0.37271 | 0.56363
|  | 17:28 | 21.8033 | -0.37159 | 0.56362
|  | 17:28 | 21.8044 | -0.37563 | 0.56362
|  | 17:28 | 21.8056 | -0.37966 | 0.56362
|  | 17:28 | 21.8067 | -0.36377 | 0.56362
|  | 17:28 | 21.8078 | -0.34788 | 0.56362
|  | 17:28 | 21.8089 | -0.32774 | 0.56361
|  | 17:28 | 21.81 | -0.30335 | 0.56361
|  | 17:28 | 21.8111 | -0.27896 | 0.56361
|  | 17:28 | 21.8122 | -0.25074 | 0.56361
|  | 17:28 | 21.8133 | -0.22252 | 0.5636
|  | 17:28 | 21.8144 | -0.19509 | 0.5636
|  | 17:28 | 21.8156 | -0.16792 | 0.5636
|  | 17:28 | 21.8167 | -0.14272 | 0.5636
|  | 17:28 | 21.8178 | -0.12345 | 0.56359
|  | 17:29 | 21.8189 | -0.10417 | 0.56359
|  | 17:29 | 21.82 | -0.087397 | 0.56359
|  | 17:29 | 21.8211 | -0.07313 | 0.56359
|  | 17:29 | 21.8222 | -0.058863 | 0.56359
|  | 17:29 | 21.8233 | -0.061269 | 0.56358
|  | 17:29 | 21.8244 | -0.063676 | 0.56358
|  | 17:29 | 21.8256 | -0.065522 | 0.56358
|  | 17:29 | 21.8267 | -0.066808 | 0.56358
|  | 17:29 | 21.8278 | -0.068094 | 0.56357
|  | 17:29 | 21.8289 | -0.075492 | 0.56357
|  | 17:29 | 21.83 | -0.08289 | 0.56357
|  | 17:29 | 21.8311 | -0.09073 | 0.56357
|  | 17:29 | 21.8322 | -0.099014 | 0.56356
|  | 17:29 | 21.8333 | -0.1073 | 0.56356
|  | 17:29 | 21.8344 | -0.089359 | 0.56356
|  | 17:30 | 21.8356 | -0.071421 | 0.56356
|  | 17:30 | 21.8367 | -0.049309 | 0.56356
|  | 17:30 | 21.8378 | -0.023023 | 0.56355
|  | 17:30 | 21.8389 | 0.0032623 | 0.56355
|  | 17:30 | 21.84 | 0.016532 | 0.56355
|  | 17:30 | 21.8411 | 0.029801 | 0.56355
|  | 17:30 | 21.8422 | 0.036497 | 0.56354
|  | 17:30 | 21.8433 | 0.03662 | 0.56354
|  | 17:30 | 21.8444 | 0.036742 | 0.56354
|  | 17:30 | 21.8456 | 0.031934 | 0.56354
|  | 17:30 | 21.8467 | 0.027126 | 0.56353
|  | 17:30 | 21.8478 | 0.038487 | 0.56353
|  | 17:30 | 21.8489 | 0.06602 | 0.56353
|  | 17:30 | 21.85 | 0.093552 | 0.56353
|  | 17:30 | 21.8511 | 0.12924 | 0.56353
|  | 17:31 | 21.8522 | 0.16492 | 0.56352
|  | 17:31 | 21.8533 | 0.19135 | 0.56352
|  | 17:31 | 21.8544 | 0.20853 | 0.56352
|  | 17:31 | 21.8556 | 0.2257 | 0.56352
|  | 17:31 | 21.8567 | 0.2251 | 0.56351
|  | 17:31 | 21.8578 | 0.22449 | 0.56351
|  | 17:31 | 21.8589 | 0.21902 | 0.56351
|  | 17:31 | 21.86 | 0.2087 | 0.56351
|  | 17:31 | 21.8611 | 0.19838 | 0.5635
|  | 17:31 | 21.8622 | 0.17104 | 0.5635
|  | 17:31 | 21.8633 | 0.14371 | 0.5635
|  | 17:31 | 21.8644 | 0.12041 | 0.5635
|  | 17:31 | 21.8656 | 0.10116 | 0.5635
|  | 17:31 | 21.8667 | 0.081902 | 0.56349
|  | 17:31 | 21.8678 | 0.099815 | 0.56349
|  | 17:32 | 21.8689 | 0.11773 | 0.56349
|  | 17:32 | 21.87 | 0.13342 | 0.56349
|  | 17:32 | 21.8711 | 0.14689 | 0.56348
|  | 17:32 | 21.8722 | 0.16036 | 0.56348
|  | 17:32 | 21.8733 | 0.17384 | 0.56348
|  | 17:32 | 21.8744 | 0.18731 | 0.56348
|  | 17:32 | 21.8756 | 0.20476 | 0.56347
|  | 17:32 | 21.8767 | 0.22619 | 0.56347
|  | 17:32 | 21.8778 | 0.24763 | 0.56347
|  | 17:32 | 21.8789 | 0.26643 | 0.56347
|  | 17:32 | 21.88 | 0.28523 | 0.56347
|  | 17:32 | 21.8811 | 0.29984 | 0.56346
|  | 17:32 | 21.8822 | 0.31025 | 0.56346
|  | 17:32 | 21.8833 | 0.32066 | 0.56346
|  | 17:32 | 21.8844 | 0.33434 | 0.56346
|  | 17:33 | 21.8856 | 0.34802 | 0.56345
|  | 17:33 | 21.8867 | 0.36502 | 0.56345
|  | 17:33 | 21.8878 | 0.38533 | 0.56345
|  | 17:33 | 21.8889 | 0.40565 | 0.56345
|  | 17:33 | 21.89 | 0.42159 | 0.56344
|  | 17:33 | 21.8911 | 0.43753 | 0.56344
|  | 17:33 | 21.8922 | 0.45058 | 0.56344
|  | 17:33 | 21.8933 | 0.46075 | 0.56344
|  | 17:33 | 21.8944 | 0.47091 | 0.56344
|  | 17:33 | 21.8956 | 0.47039 | 0.56343
|  | 17:33 | 21.8967 | 0.46987 | 0.56343
|  | 17:33 | 21.8978 | 0.46317 | 0.56343
|  | 17:33 | 21.8989 | 0.45441 | 0.56343
|  | 17:33 | 21.9 | 0.44565 | 0.56342
|  | 17:33 | 21.9011 | 0.42328 | 0.56342
|  | 17:34 | 21.9022 | 0.4009 | 0.56342
|  | 17:34 | 21.9033 | 0.38572 | 0.56342
|  | 17:34 | 21.9044 | 0.39211 | 0.56341
|  | 17:34 | 21.9056 | 0.3985 | 0.56341
|  | 17:34 | 21.9067 | 0.4237 | 0.56341
|  | 17:34 | 21.9078 | 0.4489 | 0.56341
|  | 17:34 | 21.9089 | 0.46088 | 0.56341
|  | 17:34 | 21.91 | 0.45964 | 0.5634
|  | 17:34 | 21.9111 | 0.45841 | 0.5634
|  | 17:34 | 21.9122 | 0.4475 | 0.5634
|  | 17:34 | 21.9133 | 0.43659 | 0.5634
|  | 17:34 | 21.9144 | 0.42325 | 0.56339
|  | 17:34 | 21.9156 | 0.40749 | 0.56339
|  | 17:34 | 21.9167 | 0.39172 | 0.56339
|  | 17:34 | 21.9178 | 0.40531 | 0.56339
|  | 17:35 | 21.9189 | 0.4189 | 0.56338
|  | 17:35 | 21.92 | 0.43151 | 0.56338
|  | 17:35 | 21.9211 | 0.44314 | 0.56338
|  | 17:35 | 21.9222 | 0.45477 | 0.56338
|  | 17:35 | 21.9233 | 0.4521 | 0.56337
|  | 17:35 | 21.9244 | 0.44943 | 0.56337
|  | 17:35 | 21.9256 | 0.43991 | 0.56337
|  | 17:35 | 21.9267 | 0.42354 | 0.56337
|  | 17:35 | 21.9278 | 0.40717 | 0.56337
|  | 17:35 | 21.9289 | 0.40518 | 0.56336
|  | 17:35 | 21.93 | 0.40319 | 0.56336
|  | 17:35 | 21.9311 | 0.41374 | 0.56336
|  | 17:35 | 21.9322 | 0.43682 | 0.56336
|  | 17:35 | 21.9333 | 0.45991 | 0.56335
|  | 17:35 | 21.9344 | 0.48429 | 0.56335
|  | 17:36 | 21.9356 | 0.50867 | 0.56335
|  | 17:36 | 21.9367 | 0.52763 | 0.56335
|  | 17:36 | 21.9378 | 0.54478 | 0.56334
|  | 17:36 | 21.9389 | 0.56194 | 0.56334
|  | 17:36 | 21.94 | 0.57207 | 0.56334
|  | 17:36 | 21.9411 | 0.58221 | 0.56334
|  | 17:36 | 21.9422 | 0.58718 | 0.56334
|  | 17:36 | 21.9433 | 0.58698 | 0.56333
|  | 17:36 | 21.9444 | 0.58678 | 0.56333
|  | 17:36 | 21.9456 | 0.60128 | 0.56333
|  | 17:36 | 21.9467 | 0.61578 | 0.56333
|  | 17:36 | 21.9478 | 0.62143 | 0.56332
|  | 17:36 | 21.9489 | 0.61825 | 0.56332
|  | 17:36 | 21.95 | 0.61506 | 0.56332
|  | 17:36 | 21.9511 | 0.62239 | 0.56332
|  | 17:37 | 21.9522 | 0.62971 | 0.56331
|  | 17:37 | 21.9533 | 0.63355 | 0.56331
|  | 17:37 | 21.9544 | 0.6339 | 0.56331
|  | 17:37 | 21.9556 | 0.63907 | 0.56331
|  | 17:37 | 21.9567 | 0.65868 | 0.56331
|  | 17:37 | 21.9578 | 0.6783 | 0.5633
|  | 17:37 | 21.9589 | 0.69792 | 0.5633
|  | 17:37 | 21.96 | 0.71754 | 0.5633
|  | 17:37 | 21.9611 | 0.73715 | 0.5633
|  | 17:37 | 21.9622 | 0.75945 | 0.56329
|  | 17:37 | 21.9633 | 0.78175 | 0.56329
|  | 17:37 | 21.9644 | 0.79371 | 0.56329
|  | 17:37 | 21.9656 | 0.79532 | 0.56329
|  | 17:37 | 21.9667 | 0.79693 | 0.56328
|  | 17:37 | 21.9678 | 0.81251 | 0.56328
|  | 17:38 | 21.9689 | 0.82809 | 0.56328
|  | 17:38 | 21.97 | 0.83863 | 0.56328
|  | 17:38 | 21.9711 | 0.84413 | 0.56328
|  | 17:38 | 21.9722 | 0.84963 | 0.56327
|  | 17:38 | 21.9733 | 0.82497 | 0.56327
|  | 17:38 | 21.9744 | 0.8003 | 0.56327
|  | 17:38 | 21.9756 | 0.77953 | 0.56327
|  | 17:38 | 21.9767 | 0.76265 | 0.56326
|  | 17:38 | 21.9778 | 0.74578 | 0.56326
|  | 17:38 | 21.9789 | 0.7289 | 0.56326
|  | 17:38 | 21.98 | 0.71203 | 0.56326
|  | 17:38 | 21.9811 | 0.69599 | 0.56325
|  | 17:38 | 21.9822 | 0.68079 | 0.56325
|  | 17:38 | 21.9833 | 0.66559 | 0.56325
|  | 17:38 | 21.9844 | 0.65039 | 0.56325
|  | 17:39 | 21.9856 | 0.63519 | 0.56325
|  | 17:39 | 21.9867 | 0.6287 | 0.56324
|  | 17:39 | 21.9878 | 0.62511 | 0.56324
|  | 17:39 | 21.9889 | 0.62152 | 0.56324
|  | 17:39 | 21.99 | 0.60905 | 0.56324
|  | 17:39 | 21.9911 | 0.59658 | 0.56323
|  | 17:39 | 21.9922 | 0.59451 | 0.56323
|  | 17:39 | 21.9933 | 0.60285 | 0.56323
|  | 17:39 | 21.9944 | 0.61119 | 0.56323
|  | 17:39 | 21.9956 | 0.62747 | 0.56322
|  | 17:39 | 21.9967 | 0.64374 | 0.56322
|  | 17:39 | 21.9978 | 0.64699 | 0.56322
|  | 17:39 | 21.9989 | 0.6372 | 0.56322
|  | 17:39 | 22 | 0.62494 | 0.56322
|  | 17:39 | 22.0011 | 0.60529 | 0.56321
|  | 17:40 | 22.0022 | 0.58564 | 0.56321
|  | 17:40 | 22.0033 | 0.56408 | 0.56321
|  | 17:40 | 22.0044 | 0.54061 | 0.56321
|  | 17:40 | 22.0056 | 0.51713 | 0.5632
|  | 17:40 | 22.0067 | 0.50205 | 0.5632
|  | 17:40 | 22.0078 | 0.48696 | 0.5632
|  | 17:40 | 22.0089 | 0.46771 | 0.5632
|  | 17:40 | 22.01 | 0.4443 | 0.56319
|  | 17:40 | 22.0111 | 0.4209 | 0.56319
|  | 17:40 | 22.0122 | 0.38558 | 0.56319
|  | 17:40 | 22.0133 | 0.35026 | 0.56319
|  | 17:40 | 22.0144 | 0.31233 | 0.56319
|  | 17:40 | 22.0156 | 0.27179 | 0.56318
|  | 17:40 | 22.0167 | 0.23124 | 0.56318
|  | 17:40 | 22.0178 | 0.20065 | 0.56318
|  | 17:41 | 22.0189 | 0.17005 | 0.56318
|  | 17:41 | 22.02 | 0.14077 | 0.56317
|  | 17:41 | 22.0211 | 0.11281 | 0.56317
|  | 17:41 | 22.0222 | 0.084842 | 0.56317
|  | 17:41 | 22.0233 | 0.038603 | 0.56317
|  | 17:41 | 22.0244 | -0.0076366 | 0.56316
|  | 17:41 | 22.0256 | -0.047739 | 0.56316
|  | 17:41 | 22.0267 | -0.081703 | 0.56316
|  | 17:41 | 22.0278 | -0.11567 | 0.56316
|  | 17:41 | 22.0289 | -0.13646 | 0.56316
|  | 17:41 | 22.03 | -0.15725 | 0.56315
|  | 17:41 | 22.0311 | -0.18325 | 0.56315
|  | 17:41 | 22.0322 | -0.21444 | 0.56315
|  | 17:41 | 22.0333 | -0.24563 | 0.56315
|  | 17:41 | 22.0344 | -0.2745 | 0.56314
|  | 17:42 | 22.0356 | -0.30336 | 0.56314
|  | 17:42 | 22.0367 | -0.34175 | 0.56314
|  | 17:42 | 22.0378 | -0.38967 | 0.56314
|  | 17:42 | 22.0389 | -0.42638 | 0.56313
|  | 17:42 | 22.04 | -0.42948 | 0.56313
|  | 17:42 | 22.0411 | -0.43258 | 0.56313
|  | 17:42 | 22.0422 | -0.44921 | 0.56313
|  | 17:42 | 22.0433 | -0.47935 | 0.56312
|  | 17:42 | 22.0444 | -0.5095 | 0.56312
|  | 17:42 | 22.0456 | -0.53188 | 0.56312
|  | 17:42 | 22.0467 | -0.55427 | 0.56312
|  | 17:42 | 22.0478 | -0.57911 | 0.56312
|  | 17:42 | 22.0489 | -0.60641 | 0.56311
|  | 17:42 | 22.05 | -0.63371 | 0.56311
|  | 17:42 | 22.0511 | -0.64927 | 0.56311
|  | 17:43 | 22.0522 | -0.66484 | 0.56311
|  | 17:43 | 22.0533 | -0.6804 | 0.5631
|  | 17:43 | 22.0544 | -0.69596 | 0.5631
|  | 17:43 | 22.0556 | -0.71153 | 0.5631
|  | 17:43 | 22.0567 | -0.72418 | 0.5631
|  | 17:43 | 22.0578 | -0.73684 | 0.56309
|  | 17:43 | 22.0589 | -0.73522 | 0.56309
|  | 17:43 | 22.06 | -0.71932 | 0.56309
|  | 17:43 | 22.0611 | -0.70341 | 0.56309
|  | 17:43 | 22.0622 | -0.67074 | 0.56309
|  | 17:43 | 22.0633 | -0.63806 | 0.56308
|  | 17:43 | 22.0644 | -0.60994 | 0.56308
|  | 17:43 | 22.0656 | -0.58635 | 0.56308
|  | 17:43 | 22.0667 | -0.56277 | 0.56308
|  | 17:43 | 22.0678 | -0.53527 | 0.56307
|  | 17:44 | 22.0689 | -0.50776 | 0.56307
|  | 17:44 | 22.07 | -0.48763 | 0.56307
|  | 17:44 | 22.0711 | -0.48964 | 0.56307
|  | 17:44 | 22.0722 | -0.49165 | 0.56306
|  | 17:44 | 22.0733 | -0.49001 | 0.56306
|  | 17:44 | 22.0744 | -0.48837 | 0.56306
|  | 17:44 | 22.0756 | -0.48899 | 0.56306
|  | 17:44 | 22.0767 | -0.49188 | 0.56306
|  | 17:44 | 22.0778 | -0.49352 | 0.56305
|  | 17:44 | 22.0789 | -0.49142 | 0.56305
|  | 17:44 | 22.08 | -0.48932 | 0.56305
|  | 17:44 | 22.0811 | -0.49175 | 0.56305
|  | 17:44 | 22.0822 | -0.4987 | 0.56304
|  | 17:44 | 22.0833 | -0.50565 | 0.56304
|  | 17:44 | 22.0844 | -0.50288 | 0.56304
|  | 17:45 | 22.0856 | -0.50011 | 0.56304
|  | 17:45 | 22.0867 | -0.48826 | 0.56303
|  | 17:45 | 22.0878 | -0.46731 | 0.56303
|  | 17:45 | 22.0889 | -0.44636 | 0.56303
|  | 17:45 | 22.09 | -0.413 | 0.56303
|  | 17:45 | 22.0911 | -0.37965 | 0.56303
|  | 17:45 | 22.0922 | -0.35026 | 0.56302
|  | 17:45 | 22.0933 | -0.32485 | 0.56302
|  | 17:45 | 22.0944 | -0.29944 | 0.56302
|  | 17:45 | 22.0956 | -0.27642 | 0.56302
|  | 17:45 | 22.0967 | -0.2534 | 0.56301
|  | 17:45 | 22.0978 | -0.236 | 0.56301
|  | 17:45 | 22.0989 | -0.22421 | 0.56301
|  | 17:45 | 22.1 | -0.21242 | 0.56301
|  | 17:45 | 22.1011 | -0.18995 | 0.563
|  | 17:46 | 22.1022 | -0.16749 | 0.563
|  | 17:46 | 22.1033 | -0.14283 | 0.563
|  | 17:46 | 22.1044 | -0.11597 | 0.563
|  | 17:46 | 22.1056 | -0.089118 | 0.563
|  | 17:46 | 22.1067 | -0.051508 | 0.56299
|  | 17:46 | 22.1078 | -0.013898 | 0.56299
|  | 17:46 | 22.1089 | 0.024607 | 0.56299
|  | 17:46 | 22.11 | 0.064006 | 0.56299
|  | 17:46 | 22.1111 | 0.1034 | 0.56298
|  | 17:46 | 22.1122 | 0.12872 | 0.56298
|  | 17:46 | 22.1133 | 0.15403 | 0.56298
|  | 17:46 | 22.1144 | 0.16833 | 0.56298
|  | 17:46 | 22.1156 | 0.17161 | 0.56297
|  | 17:46 | 22.1167 | 0.1749 | 0.56297
|  | 17:46 | 22.1178 | 0.19225 | 0.56297
|  | 17:47 | 22.1189 | 0.2096 | 0.56297
|  | 17:47 | 22.12 | 0.23125 | 0.56297
|  | 17:47 | 22.1211 | 0.25433 | 0.56296
|  | 17:47 | 22.1222 | 0.28118 | 0.56296
|  | 17:47 | 22.1233 | 0.3193 | 0.56296
|  | 17:47 | 22.1244 | 0.35742 | 0.56296
|  | 17:47 | 22.1256 | 0.37481 | 0.56295
|  | 17:47 | 22.1267 | 0.37146 | 0.56295
|  | 17:47 | 22.1278 | 0.36812 | 0.56295
|  | 17:47 | 22.1289 | 0.36814 | 0.56295
|  | 17:47 | 22.13 | 0.36817 | 0.56294
|  | 17:47 | 22.1311 | 0.36493 | 0.56294
|  | 17:47 | 22.1322 | 0.35842 | 0.56294
|  | 17:47 | 22.1333 | 0.35192 | 0.56294
|  | 17:47 | 22.1344 | 0.35745 | 0.56294
|  | 17:48 | 22.1356 | 0.36298 | 0.56293
|  | 17:48 | 22.1367 | 0.38439 | 0.56293
|  | 17:48 | 22.1378 | 0.42166 | 0.56293
|  | 17:48 | 22.1389 | 0.45893 | 0.56293
|  | 17:48 | 22.14 | 0.50834 | 0.56292
|  | 17:48 | 22.1411 | 0.55774 | 0.56292
|  | 17:48 | 22.1422 | 0.59714 | 0.56292
|  | 17:48 | 22.1433 | 0.62655 | 0.56292
|  | 17:48 | 22.1444 | 0.65595 | 0.56291
|  | 17:48 | 22.1456 | 0.68535 | 0.56291
|  | 17:48 | 22.1467 | 0.71475 | 0.56291
|  | 17:48 | 22.1478 | 0.7405 | 0.56291
|  | 17:48 | 22.1489 | 0.7626 | 0.56291
|  | 17:48 | 22.15 | 0.7847 | 0.5629
|  | 17:48 | 22.1511 | 0.78996 | 0.5629
|  | 17:49 | 22.1522 | 0.79522 | 0.5629
|  | 17:49 | 22.1533 | 0.80048 | 0.5629
|  | 17:49 | 22.1544 | 0.80574 | 0.56289
|  | 17:49 | 22.1556 | 0.811 | 0.56289
|  | 17:49 | 22.1567 | 0.80302 | 0.56289
|  | 17:49 | 22.1578 | 0.79504 | 0.56289
|  | 17:49 | 22.1589 | 0.78335 | 0.56288
|  | 17:49 | 22.16 | 0.76794 | 0.56288
|  | 17:49 | 22.1611 | 0.75254 | 0.56288
|  | 17:49 | 22.1622 | 0.73713 | 0.56288
|  | 17:49 | 22.1633 | 0.72173 | 0.56287
|  | 17:49 | 22.1644 | 0.70357 | 0.56287
|  | 17:49 | 22.1656 | 0.68266 | 0.56287
|  | 17:49 | 22.1667 | 0.66175 | 0.56287
|  | 17:49 | 22.1678 | 0.62242 | 0.56287
|  | 17:50 | 22.1689 | 0.58309 | 0.56286
|  | 17:50 | 22.17 | 0.54171 | 0.56286
|  | 17:50 | 22.1711 | 0.49829 | 0.56286
|  | 17:50 | 22.1722 | 0.45486 | 0.56286
|  | 17:50 | 22.1733 | 0.42925 | 0.56285
|  | 17:50 | 22.1744 | 0.40363 | 0.56285
|  | 17:50 | 22.1756 | 0.37379 | 0.56285
|  | 17:50 | 22.1767 | 0.33971 | 0.56285
|  | 17:50 | 22.1778 | 0.30564 | 0.56284
|  | 17:50 | 22.1789 | 0.27379 | 0.56284
|  | 17:50 | 22.18 | 0.24194 | 0.56284
|  | 17:50 | 22.1811 | 0.22435 | 0.56284
|  | 17:50 | 22.1822 | 0.22102 | 0.56284
|  | 17:50 | 22.1833 | 0.21769 | 0.56283
|  | 17:50 | 22.1844 | 0.20566 | 0.56283
|  | 17:51 | 22.1856 | 0.19362 | 0.56283
|  | 17:51 | 22.1867 | 0.18466 | 0.56283
|  | 17:51 | 22.1878 | 0.17879 | 0.56282
|  | 17:51 | 22.1889 | 0.17291 | 0.56282
|  | 17:51 | 22.19 | 0.16918 | 0.56282
|  | 17:51 | 22.1911 | 0.16545 | 0.56282
|  | 17:51 | 22.1922 | 0.15742 | 0.56281
|  | 17:51 | 22.1933 | 0.14511 | 0.56281
|  | 17:51 | 22.1944 | 0.13279 | 0.56281
|  | 17:51 | 22.1956 | 0.11944 | 0.56281
|  | 17:51 | 22.1967 | 0.10609 | 0.56281
|  | 17:51 | 22.1978 | 0.093734 | 0.5628
|  | 17:51 | 22.1989 | 0.082374 | 0.5628
|  | 17:51 | 22.2 | 0.071013 | 0.5628
|  | 17:51 | 22.2011 | 0.066403 | 0.5628
|  | 17:52 | 22.2022 | 0.061792 | 0.56279
|  | 17:52 | 22.2033 | 0.057755 | 0.56279
|  | 17:52 | 22.2044 | 0.05429 | 0.56279
|  | 17:52 | 22.2056 | 0.050825 | 0.56279
|  | 17:52 | 22.2067 | 0.032276 | 0.56278
|  | 17:52 | 22.2078 | 0.013726 | 0.56278
|  | 17:52 | 22.2089 | -0.0155 | 0.56278
|  | 17:52 | 22.21 | -0.055402 | 0.56278
|  | 17:52 | 22.2111 | -0.095305 | 0.56278
|  | 17:52 | 22.2122 | -0.1476 | 0.56277
|  | 17:52 | 22.2133 | -0.19989 | 0.56277
|  | 17:52 | 22.2144 | -0.25319 | 0.56277
|  | 17:52 | 22.2156 | -0.30752 | 0.56277
|  | 17:52 | 22.2167 | -0.36184 | 0.56276
|  | 17:52 | 22.2178 | -0.40614 | 0.56276
|  | 17:53 | 22.2189 | -0.45044 | 0.56276
|  | 17:53 | 22.22 | -0.48112 | 0.56276
|  | 17:53 | 22.2211 | -0.49819 | 0.56275
|  | 17:53 | 22.2222 | -0.51526 | 0.56275
|  | 17:53 | 22.2233 | -0.54146 | 0.56275
|  | 17:53 | 22.2244 | -0.56767 | 0.56275
|  | 17:53 | 22.2256 | -0.58665 | 0.56275
|  | 17:53 | 22.2267 | -0.59843 | 0.56274
|  | 17:53 | 22.2278 | -0.6102 | 0.56274
|  | 17:53 | 22.2289 | -0.60745 | 0.56274
|  | 17:53 | 22.23 | -0.6047 | 0.56274
|  | 17:53 | 22.2311 | -0.60347 | 0.56273
|  | 17:53 | 22.2322 | -0.60376 | 0.56273
|  | 17:53 | 22.2333 | -0.60405 | 0.56273
|  | 17:53 | 22.2344 | -0.60336 | 0.56273
|  | 17:54 | 22.2356 | -0.60266 | 0.56272
|  | 17:54 | 22.2367 | -0.60291 | 0.56272
|  | 17:54 | 22.2378 | -0.60599 | 0.56272
|  | 17:54 | 22.2389 | -0.60906 | 0.56272
|  | 17:54 | 22.24 | -0.61077 | 0.56272
|  | 17:54 | 22.2411 | -0.61248 | 0.56271
|  | 17:54 | 22.2422 | -0.6045 | 0.56271
|  | 17:54 | 22.2433 | -0.58685 | 0.56271
|  | 17:54 | 22.2444 | -0.56919 | 0.56271
|  | 17:54 | 22.2456 | -0.55636 | 0.5627
|  | 17:54 | 22.2467 | -0.54352 | 0.5627
|  | 17:54 | 22.2478 | -0.53564 | 0.5627
|  | 17:54 | 22.2489 | -0.53272 | 0.5627
|  | 17:54 | 22.25 | -0.5298 | 0.56269
|  | 17:54 | 22.2511 | -0.529 | 0.56269
|  | 17:55 | 22.2522 | -0.52819 | 0.56269
|  | 17:55 | 22.2533 | -0.53152 | 0.56269
|  | 17:55 | 22.2544 | -0.539 | 0.56269
|  | 17:55 | 22.2556 | -0.54647 | 0.56268
|  | 17:55 | 22.2567 | -0.54635 | 0.56268
|  | 17:55 | 22.2578 | -0.54623 | 0.56268
|  | 17:55 | 22.2589 | -0.54252 | 0.56268
|  | 17:55 | 22.26 | -0.53522 | 0.56267
|  | 17:55 | 22.2611 | -0.52791 | 0.56267
|  | 17:55 | 22.2622 | -0.51653 | 0.56267
|  | 17:55 | 22.2633 | -0.50516 | 0.56267
|  | 17:55 | 22.2644 | -0.47674 | 0.56266
|  | 17:55 | 22.2656 | -0.43128 | 0.56266
|  | 17:55 | 22.2667 | -0.38582 | 0.56266
|  | 17:55 | 22.2678 | -0.34134 | 0.56266
|  | 17:56 | 22.2689 | -0.29686 | 0.56266
|  | 17:56 | 22.27 | -0.25636 | 0.56265
|  | 17:56 | 22.2711 | -0.21982 | 0.56265
|  | 17:56 | 22.2722 | -0.18329 | 0.56265
|  | 17:56 | 22.2733 | -0.16697 | 0.56265
|  | 17:56 | 22.2744 | -0.15066 | 0.56264
|  | 17:56 | 22.2756 | -0.13059 | 0.56264
|  | 17:56 | 22.2767 | -0.10676 | 0.56264
|  | 17:56 | 22.2778 | -0.082929 | 0.56264
|  | 17:56 | 22.2789 | -0.064992 | 0.56263
|  | 17:56 | 22.28 | -0.047054 | 0.56263
|  | 17:56 | 22.2811 | -0.033677 | 0.56263
|  | 17:56 | 22.2822 | -0.024861 | 0.56263
|  | 17:56 | 22.2833 | -0.016045 | 0.56262
|  | 17:56 | 22.2844 | -0.015577 | 0.56262
|  | 17:57 | 22.2856 | -0.01511 | 0.56262
|  | 17:57 | 22.2867 | -0.032247 | 0.56262
|  | 17:57 | 22.2878 | -0.066986 | 0.56262
|  | 17:57 | 22.2889 | -0.10173 | 0.56261
|  | 17:57 | 22.29 | -0.11422 | 0.56261
|  | 17:57 | 22.2911 | -0.12672 | 0.56261
|  | 17:57 | 22.2922 | -0.14071 | 0.56261
|  | 17:57 | 22.2933 | -0.15619 | 0.5626
|  | 17:57 | 22.2944 | -0.17167 | 0.5626
|  | 17:57 | 22.2956 | -0.18715 | 0.5626
|  | 17:57 | 22.2967 | -0.20263 | 0.5626
|  | 17:57 | 22.2978 | -0.22463 | 0.56259
|  | 17:57 | 22.2989 | -0.25316 | 0.56259
|  | 17:57 | 22.3 | -0.28168 | 0.56259
|  | 17:57 | 22.3011 | -0.29777 | 0.56259
|  | 17:58 | 22.3022 | -0.31386 | 0.56259
|  | 17:58 | 22.3033 | -0.31394 | 0.56258
|  | 17:58 | 22.3044 | -0.298 | 0.56258
|  | 17:58 | 22.3056 | -0.28207 | 0.56258
|  | 17:58 | 22.3067 | -0.26097 | 0.56258
|  | 17:58 | 22.3078 | -0.23987 | 0.56257
|  | 17:58 | 22.3089 | -0.2201 | 0.56257
|  | 17:58 | 22.31 | -0.20168 | 0.56257
|  | 17:58 | 22.3111 | -0.18325 | 0.56257
|  | 17:58 | 22.3122 | -0.16685 | 0.56256
|  | 17:58 | 22.3133 | -0.15045 | 0.56256
|  | 17:58 | 22.3144 | -0.13497 | 0.56256
|  | 17:58 | 22.3156 | -0.1204 | 0.56256
|  | 17:58 | 22.3167 | -0.10583 | 0.56256
|  | 17:58 | 22.3178 | -0.085856 | 0.56255
|  | 17:59 | 22.3189 | -0.065882 | 0.56255
|  | 17:59 | 22.32 | -0.057483 | 0.56255
|  | 17:59 | 22.3211 | -0.060658 | 0.56255
|  | 17:59 | 22.3222 | -0.063833 | 0.56254
|  | 17:59 | 22.3233 | -0.042603 | 0.56254
|  | 17:59 | 22.3244 | -0.021374 | 0.56254
|  | 17:59 | 22.3256 | -0.0021204 | 0.56254
|  | 17:59 | 22.3267 | 0.015157 | 0.56253
|  | 17:59 | 22.3278 | 0.032435 | 0.56253
|  | 17:59 | 22.3289 | 0.024561 | 0.56253
|  | 17:59 | 22.33 | 0.016687 | 0.56253
|  | 17:59 | 22.3311 | 0.012389 | 0.56253
|  | 17:59 | 22.3322 | 0.011665 | 0.56252
|  | 17:59 | 22.3333 | 0.010942 | 0.56252
|  | 17:59 | 22.3344 | 0.002515 | 0.56252
|  | 18:00 | 22.3356 | -0.0059115 | 0.56252
|  | 18:00 | 22.3367 | -0.026255 | 0.56251
|  | 18:00 | 22.3378 | -0.058516 | 0.56251
|  | 18:00 | 22.3389 | -0.090777 | 0.56251
|  | 18:00 | 22.34 | -0.1219 | 0.56251
|  | 18:00 | 22.3411 | -0.15302 | 0.5625
|  | 18:00 | 22.3422 | -0.18289 | 0.5625
|  | 18:00 | 22.3433 | -0.14425 | 0.5625
|  | 18:00 | 22.3444 | -0.12965 | 0.5625
|  | 18:00 | 22.3456 | -0.13601 | 0.5625
|  | 18:00 | 22.3467 | -0.14238 | 0.56249
|  | 18:00 | 22.3478 | -0.14874 | 0.56249
|  | 18:00 | 22.3489 | -0.15511 | 0.56249
|  | 18:00 | 22.35 | -0.16147 | 0.56249
|  | 18:00 | 22.3511 | -0.15001 | 0.56248
|  | 18:01 | 22.3522 | -0.13855 | 0.56248
|  | 18:01 | 22.3533 | -0.11353 | 0.56248
|  | 18:01 | 22.3544 | -0.083978 | 0.56248
|  | 18:01 | 22.3556 | -0.05443 | 0.56247
|  | 18:01 | 22.3567 | -0.032121 | 0.56247
|  | 18:01 | 22.3578 | -0.0098121 | 0.56247
|  | 18:01 | 22.3589 | 0.0050135 | 0.56247
|  | 18:01 | 22.36 | 0.012356 | 0.56247
|  | 18:01 | 22.3611 | 0.019698 | 0.56246
|  | 18:01 | 22.3622 | 0.0056427 | 0.56246
|  | 18:01 | 22.3633 | -0.0084124 | 0.56246
|  | 18:01 | 22.3644 | -0.016135 | 0.56246
|  | 18:01 | 22.3656 | -0.017526 | 0.56245
|  | 18:01 | 22.3667 | -0.018917 | 0.56245
|  | 18:01 | 22.3678 | -0.0074832 | 0.56245
|  | 18:02 | 22.3689 | 0.0039504 | 0.56245
|  | 18:02 | 22.37 | 0.016937 | 0.56244
|  | 18:02 | 22.3711 | 0.030441 | 0.56244
|  | 18:02 | 22.3722 | 0.043946 | 0.56244
|  | 18:02 | 22.3733 | 0.065859 | 0.56244
|  | 18:02 | 22.3744 | 0.087772 | 0.56244
|  | 18:02 | 22.3756 | 0.10268 | 0.56243
|  | 18:02 | 22.3767 | 0.11526 | 0.56243
|  | 18:02 | 22.3778 | 0.12783 | 0.56243
|  | 18:02 | 22.3789 | 0.13629 | 0.56243
|  | 18:02 | 22.38 | 0.14474 | 0.56242
|  | 18:02 | 22.3811 | 0.1681 | 0.56242
|  | 18:02 | 22.3822 | 0.20635 | 0.56242
|  | 18:02 | 22.3833 | 0.2446 | 0.56242
|  | 18:02 | 22.3844 | 0.28614 | 0.56241
|  | 18:03 | 22.3856 | 0.32769 | 0.56241
|  | 18:03 | 22.3867 | 0.37177 | 0.56241
|  | 18:03 | 22.3878 | 0.41839 | 0.56241
|  | 18:03 | 22.3889 | 0.4646 | 0.56241
|  | 18:03 | 22.39 | 0.50955 | 0.5624
|  | 18:03 | 22.3911 | 0.55451 | 0.5624
|  | 18:03 | 22.3922 | 0.60292 | 0.5624
|  | 18:03 | 22.3933 | 0.65481 | 0.5624
|  | 18:03 | 22.3944 | 0.70669 | 0.56239
|  | 18:03 | 22.3956 | 0.72091 | 0.56239
|  | 18:03 | 22.3967 | 0.73513 | 0.56239
|  | 18:03 | 22.3978 | 0.73769 | 0.56239
|  | 18:03 | 22.3989 | 0.7286 | 0.56238
|  | 18:03 | 22.4 | 0.71951 | 0.56238
|  | 18:03 | 22.4011 | 0.69733 | 0.56238
|  | 18:04 | 22.4022 | 0.66208 | 0.56238
|  | 18:04 | 22.4033 | 0.6161 | 0.56237
|  | 18:04 | 22.4044 | 0.5594 | 0.56237
|  | 18:04 | 22.4056 | 0.50271 | 0.56237
|  | 18:04 | 22.4067 | 0.43484 | 0.56237
|  | 18:04 | 22.4078 | 0.36696 | 0.56237
|  | 18:04 | 22.4089 | 0.2997 | 0.56236
|  | 18:04 | 22.41 | 0.23306 | 0.56236
|  | 18:04 | 22.4111 | 0.16641 | 0.56236
|  | 18:04 | 22.4122 | 0.1269 | 0.56236
|  | 18:04 | 22.4133 | 0.087393 | 0.56235
|  | 18:04 | 22.4144 | 0.062752 | 0.56235
|  | 18:04 | 22.4156 | 0.052981 | 0.56235
|  | 18:04 | 22.4167 | 0.04321 | 0.56235
|  | 18:04 | 22.4178 | 0.031374 | 0.56234
|  | 18:05 | 22.4189 | 0.019538 | 0.56234
|  | 18:05 | 22.42 | 0.0014623 | 0.56234
|  | 18:05 | 22.4211 | -0.022852 | 0.56234
|  | 18:05 | 22.4222 | -0.047167 | 0.56234
|  | 18:05 | 22.4233 | -0.057435 | 0.56233
|  | 18:05 | 22.4244 | -0.067703 | 0.56233
|  | 18:05 | 22.4256 | -0.080728 | 0.56233
|  | 18:05 | 22.4267 | -0.096511 | 0.56233
|  | 18:05 | 22.4278 | -0.11229 | 0.56232
|  | 18:05 | 22.4289 | -0.14181 | 0.56232
|  | 18:05 | 22.43 | -0.17133 | 0.56232
|  | 18:05 | 22.4311 | -0.19213 | 0.56232
|  | 18:05 | 22.4322 | -0.21003 | 0.56231
|  | 18:05 | 22.4333 | -0.22794 | 0.56231
|  | 18:05 | 22.4344 | -0.25217 | 0.56231
|  | 18:06 | 22.4356 | -0.2764 | 0.56231
|  | 18:06 | 22.4367 | -0.29614 | 0.56231
|  | 18:06 | 22.4378 | -0.31141 | 0.5623
|  | 18:06 | 22.4389 | -0.32668 | 0.5623
|  | 18:06 | 22.44 | -0.33634 | 0.5623
|  | 18:06 | 22.4411 | -0.346 | 0.5623
|  | 18:06 | 22.4422 | -0.35417 | 0.56229
|  | 18:06 | 22.4433 | -0.36184 | 0.56229
|  | 18:06 | 22.4444 | -0.3695 | 0.56229
|  | 18:06 | 22.4456 | -0.38223 | 0.56229
|  | 18:06 | 22.4467 | -0.39495 | 0.56228
|  | 18:06 | 22.4478 | -0.41366 | 0.56228
|  | 18:06 | 22.4489 | -0.43836 | 0.56228
|  | 18:06 | 22.45 | -0.46307 | 0.56228
|  | 18:06 | 22.4511 | -0.49142 | 0.56228
|  | 18:07 | 22.4522 | -0.51976 | 0.56227
|  | 18:07 | 22.4533 | -0.53557 | 0.56227
|  | 18:07 | 22.4544 | -0.53885 | 0.56227
|  | 18:07 | 22.4556 | -0.54212 | 0.56227
|  | 18:07 | 22.4567 | -0.52588 | 0.56226
|  | 18:07 | 22.4578 | -0.50964 | 0.56226
|  | 18:07 | 22.4589 | -0.48512 | 0.56226
|  | 18:07 | 22.46 | -0.45232 | 0.56226
|  | 18:07 | 22.4611 | -0.41952 | 0.56225
|  | 18:07 | 22.4622 | -0.39896 | 0.56225
|  | 18:07 | 22.4633 | -0.3784 | 0.56225
|  | 18:07 | 22.4644 | -0.36069 | 0.56225
|  | 18:07 | 22.4656 | -0.34581 | 0.56225
|  | 18:07 | 22.4667 | -0.33094 | 0.56224
|  | 18:07 | 22.4678 | -0.31151 | 0.56224
|  | 18:08 | 22.4689 | -0.29208 | 0.56224
|  | 18:08 | 22.47 | -0.26401 | 0.56224
|  | 18:08 | 22.4711 | -0.2273 | 0.56223
|  | 18:08 | 22.4722 | -0.1906 | 0.56223
|  | 18:08 | 22.4733 | -0.15165 | 0.56223
|  | 18:08 | 22.4744 | -0.1127 | 0.56223
|  | 18:08 | 22.4756 | -0.070709 | 0.56222
|  | 18:08 | 22.4767 | -0.025681 | 0.56222
|  | 18:08 | 22.4778 | 0.019348 | 0.56222
|  | 18:08 | 22.4789 | 0.066808 | 0.56222
|  | 18:08 | 22.48 | 0.11427 | 0.56222
|  | 18:08 | 22.4811 | 0.14906 | 0.56221
|  | 18:08 | 22.4822 | 0.17962 | 0.56221
|  | 18:08 | 22.4833 | 0.21018 | 0.56221
|  | 18:08 | 22.4844 | 0.22659 | 0.56221
|  | 18:09 | 22.4856 | 0.243 | 0.5622
|  | 18:09 | 22.4867 | 0.26015 | 0.5622
|  | 18:09 | 22.4878 | 0.27804 | 0.5622
|  | 18:09 | 22.4889 | 0.29593 | 0.5622
|  | 18:09 | 22.49 | 0.34579 | 0.56219
|  | 18:09 | 22.4911 | 0.39566 | 0.56219
|  | 18:09 | 22.4922 | 0.41648 | 0.56219
|  | 18:09 | 22.4933 | 0.42761 | 0.56219
|  | 18:09 | 22.4944 | 0.43875 | 0.56219
|  | 18:09 | 22.4956 | 0.48488 | 0.56218
|  | 18:09 | 22.4967 | 0.53101 | 0.56218
|  | 18:09 | 22.4978 | 0.56431 | 0.56218
|  | 18:09 | 22.4989 | 0.58479 | 0.56218
|  | 18:09 | 22.5 | 0.60527 | 0.56217
|  | 18:09 | 22.5011 | 0.62576 | 0.56217
|  | 18:10 | 22.5022 | 0.64624 | 0.56217
|  | 18:10 | 22.5033 | 0.65386 | 0.56217
|  | 18:10 | 22.5044 | 0.64862 | 0.56216
|  | 18:10 | 22.5056 | 0.64337 | 0.56216
|  | 18:10 | 22.5067 | 0.61858 | 0.56216
|  | 18:10 | 22.5078 | 0.59379 | 0.56216
|  | 18:10 | 22.5089 | 0.57945 | 0.56216
|  | 18:10 | 22.51 | 0.5686 | 0.56215
|  | 18:10 | 22.5111 | 0.55774 | 0.56215
|  | 18:10 | 22.5122 | 0.53406 | 0.56215
|  | 18:10 | 22.5133 | 0.51037 | 0.56215
|  | 18:10 | 22.5144 | 0.48484 | 0.56214
|  | 18:10 | 22.5156 | 0.45747 | 0.56214
|  | 18:10 | 22.5167 | 0.43009 | 0.56214
|  | 18:10 | 22.5178 | 0.40661 | 0.56214
|  | 18:11 | 22.5189 | 0.38313 | 0.56213
|  | 18:11 | 22.52 | 0.35578 | 0.56213
|  | 18:11 | 22.5211 | 0.32455 | 0.56213
|  | 18:11 | 22.5222 | 0.29332 | 0.56213
|  | 18:11 | 22.5233 | 0.24981 | 0.56212
|  | 18:11 | 22.5244 | 0.20629 | 0.56212
|  | 18:11 | 22.5256 | 0.16355 | 0.56212
|  | 18:11 | 22.5267 | 0.12106 | 0.56212
|  | 18:11 | 22.5278 | 0.078582 | 0.56212
|  | 18:11 | 22.5289 | 0.031632 | 0.56211
|  | 18:11 | 22.53 | -0.015318 | 0.56211
|  | 18:11 | 22.5311 | -0.035845 | 0.56211
|  | 18:11 | 22.5322 | -0.047565 | 0.56211
|  | 18:11 | 22.5333 | -0.059285 | 0.5621
|  | 18:11 | 22.5344 | -0.081598 | 0.5621
|  | 18:12 | 22.5356 | -0.10391 | 0.5621
|  | 18:12 | 22.5367 | -0.13323 | 0.5621
|  | 18:12 | 22.5378 | -0.16956 | 0.56209
|  | 18:12 | 22.5389 | -0.20588 | 0.56209
|  | 18:12 | 22.54 | -0.24997 | 0.56209
|  | 18:12 | 22.5411 | -0.29406 | 0.56209
|  | 18:12 | 22.5422 | -0.33234 | 0.56209
|  | 18:12 | 22.5433 | -0.3648 | 0.56208
|  | 18:12 | 22.5444 | -0.39726 | 0.56208
|  | 18:12 | 22.5456 | -0.42357 | 0.56208
|  | 18:12 | 22.5467 | -0.44987 | 0.56208
|  | 18:12 | 22.5478 | -0.46847 | 0.56207
|  | 18:12 | 22.5489 | -0.47935 | 0.56207
|  | 18:12 | 22.55 | -0.49023 | 0.56207
|  | 18:12 | 22.5511 | -0.5088 | 0.56207
|  | 18:13 | 22.5522 | -0.52738 | 0.56206
|  | 18:13 | 22.5533 | -0.54595 | 0.56206
|  | 18:13 | 22.5544 | -0.56452 | 0.56206
|  | 18:13 | 22.5556 | -0.58056 | 0.56206
|  | 18:13 | 22.5567 | -0.58899 | 0.56206
|  | 18:13 | 22.5578 | -0.59741 | 0.56205
|  | 18:13 | 22.5589 | -0.60464 | 0.56205
|  | 18:13 | 22.56 | -0.61068 | 0.56205
|  | 18:13 | 22.5611 | -0.61671 | 0.56205
|  | 18:13 | 22.5622 | -0.62274 | 0.56204
|  | 18:13 | 22.5633 | -0.62878 | 0.56204
|  | 18:13 | 22.5644 | -0.64556 | 0.56204
|  | 18:13 | 22.5656 | -0.67309 | 0.56204
|  | 18:13 | 22.5667 | -0.70062 | 0.56203
|  | 18:13 | 22.5678 | -0.7259 | 0.56203
|  | 18:14 | 22.5689 | -0.75118 | 0.56203
|  | 18:14 | 22.57 | -0.76373 | 0.56203
|  | 18:14 | 22.5711 | -0.76355 | 0.56203
|  | 18:14 | 22.5722 | -0.76336 | 0.56202
|  | 18:14 | 22.5733 | -0.74165 | 0.56202
|  | 18:14 | 22.5744 | -0.71995 | 0.56202
|  | 18:14 | 22.5756 | -0.69328 | 0.56202
|  | 18:14 | 22.5767 | -0.66166 | 0.56201
|  | 18:14 | 22.5778 | -0.63004 | 0.56201
|  | 18:14 | 22.5789 | -0.60123 | 0.56201
|  | 18:14 | 22.58 | -0.57243 | 0.56201
|  | 18:14 | 22.5811 | -0.55891 | 0.562
|  | 18:14 | 22.5822 | -0.56068 | 0.562
|  | 18:14 | 22.5833 | -0.56245 | 0.562
|  | 18:14 | 22.5844 | -0.54412 | 0.562
|  | 18:15 | 22.5856 | -0.52578 | 0.562
|  | 18:15 | 22.5867 | -0.51626 | 0.56199
|  | 18:15 | 22.5878 | -0.51554 | 0.56199
|  | 18:15 | 22.5889 | -0.51483 | 0.56199
|  | 18:15 | 22.59 | -0.51658 | 0.56199
|  | 18:15 | 22.5911 | -0.51832 | 0.56198
|  | 18:15 | 22.5922 | -0.51742 | 0.56198
|  | 18:15 | 22.5933 | -0.51387 | 0.56198
|  | 18:15 | 22.5944 | -0.51032 | 0.56198
|  | 18:15 | 22.5956 | -0.49265 | 0.56197
|  | 18:15 | 22.5967 | -0.47497 | 0.56197
|  | 18:15 | 22.5978 | -0.4573 | 0.56197
|  | 18:15 | 22.5989 | -0.43963 | 0.56197
|  | 18:15 | 22.6 | -0.42195 | 0.56197
|  | 18:15 | 22.6011 | -0.40033 | 0.56196
|  | 18:16 | 22.6022 | -0.3787 | 0.56196
|  | 18:16 | 22.6033 | -0.35755 | 0.56196
|  | 18:16 | 22.6044 | -0.33687 | 0.56196
|  | 18:16 | 22.6056 | -0.31619 | 0.56195
|  | 18:16 | 22.6067 | -0.27026 | 0.56195
|  | 18:16 | 22.6078 | -0.22432 | 0.56195
|  | 18:16 | 22.6089 | -0.18079 | 0.56195
|  | 18:16 | 22.61 | -0.13806 | 0.56194
|  | 18:16 | 22.6111 | -0.095326 | 0.56194
|  | 18:16 | 22.6122 | -0.056057 | 0.56194
|  | 18:16 | 22.6133 | -0.016788 | 0.56194
|  | 18:16 | 22.6144 | 0.015659 | 0.56194
|  | 18:16 | 22.6156 | 0.041284 | 0.56193
|  | 18:16 | 22.6167 | 0.066908 | 0.56193
|  | 18:16 | 22.6178 | 0.067889 | 0.56193
|  | 18:17 | 22.6189 | 0.06887 | 0.56193
|  | 18:17 | 22.62 | 0.077604 | 0.56192
|  | 18:17 | 22.6211 | 0.094089 | 0.56192
|  | 18:17 | 22.6222 | 0.11057 | 0.56192
|  | 18:17 | 22.6233 | 0.13697 | 0.56192
|  | 18:17 | 22.6244 | 0.16337 | 0.56191
|  | 18:17 | 22.6256 | 0.18555 | 0.56191
|  | 18:17 | 22.6267 | 0.2035 | 0.56191
|  | 18:17 | 22.6278 | 0.22146 | 0.56191
|  | 18:17 | 22.6289 | 0.25483 | 0.56191
|  | 18:17 | 22.63 | 0.2882 | 0.5619
|  | 18:17 | 22.6311 | 0.30837 | 0.5619
|  | 18:17 | 22.6322 | 0.31533 | 0.5619
|  | 18:17 | 22.6333 | 0.32229 | 0.5619
|  | 18:17 | 22.6344 | 0.34371 | 0.56189
|  | 18:18 | 22.6356 | 0.36513 | 0.56189
|  | 18:18 | 22.6367 | 0.39495 | 0.56189
|  | 18:18 | 22.6378 | 0.43316 | 0.56189
|  | 18:18 | 22.6389 | 0.47137 | 0.56188
|  | 18:18 | 22.64 | 0.50421 | 0.56188
|  | 18:18 | 22.6411 | 0.53705 | 0.56188
|  | 18:18 | 22.6422 | 0.56677 | 0.56188
|  | 18:18 | 22.6433 | 0.59337 | 0.56187
|  | 18:18 | 22.6444 | 0.61996 | 0.56187
|  | 18:18 | 22.6456 | 0.63533 | 0.56187
|  | 18:18 | 22.6467 | 0.6507 | 0.56187
|  | 18:18 | 22.6478 | 0.67478 | 0.56187
|  | 18:18 | 22.6489 | 0.70756 | 0.56186
|  | 18:18 | 22.65 | 0.74033 | 0.56186
|  | 18:18 | 22.6511 | 0.7188 | 0.56186
|  | 18:19 | 22.6522 | 0.69726 | 0.56186
|  | 18:19 | 22.6533 | 0.69924 | 0.56185
|  | 18:19 | 22.6544 | 0.72473 | 0.56185
|  | 18:19 | 22.6556 | 0.75023 | 0.56185
|  | 18:19 | 22.6567 | 0.75876 | 0.56185
|  | 18:19 | 22.6578 | 0.76729 | 0.56184
|  | 18:19 | 22.6589 | 0.77299 | 0.56184
|  | 18:19 | 22.66 | 0.77774 | 0.56184
|  | 18:19 | 22.6611 | 0.7825 | 0.56184
|  | 18:19 | 22.6622 | 0.76741 | 0.56184
|  | 18:19 | 22.6633 | 0.75232 | 0.56183
|  | 18:19 | 22.6644 | 0.7296 | 0.56183
|  | 18:19 | 22.6656 | 0.69925 | 0.56183
|  | 18:19 | 22.6667 | 0.6689 | 0.56183
|  | 18:19 | 22.6678 | 0.62576 | 0.56182
|  | 18:20 | 22.6689 | 0.58261 | 0.56182
|  | 18:20 | 22.67 | 0.54949 | 0.56182
|  | 18:20 | 22.6711 | 0.5264 | 0.56182
|  | 18:20 | 22.6722 | 0.50331 | 0.56181
|  | 18:20 | 22.6733 | 0.4765 | 0.56181
|  | 18:20 | 22.6744 | 0.44968 | 0.56181
|  | 18:20 | 22.6756 | 0.4167 | 0.56181
|  | 18:20 | 22.6767 | 0.37755 | 0.56181
|  | 18:20 | 22.6778 | 0.33841 | 0.5618
|  | 18:20 | 22.6789 | 0.29386 | 0.5618
|  | 18:20 | 22.68 | 0.24932 | 0.5618
|  | 18:20 | 22.6811 | 0.21533 | 0.5618
|  | 18:20 | 22.6822 | 0.19189 | 0.56179
|  | 18:20 | 22.6833 | 0.16844 | 0.56179
|  | 18:20 | 22.6844 | 0.16499 | 0.56179
|  | 18:21 | 22.6856 | 0.16153 | 0.56179
|  | 18:21 | 22.6867 | 0.15986 | 0.56178
|  | 18:21 | 22.6878 | 0.15996 | 0.56178
|  | 18:21 | 22.6889 | 0.16005 | 0.56178
|  | 18:21 | 22.69 | 0.14796 | 0.56178
|  | 18:21 | 22.6911 | 0.13587 | 0.56178
|  | 18:21 | 22.6922 | 0.12378 | 0.56177
|  | 18:21 | 22.6933 | 0.1117 | 0.56177
|  | 18:21 | 22.6944 | 0.099605 | 0.56177
|  | 18:21 | 22.6956 | 0.079349 | 0.56177
|  | 18:21 | 22.6967 | 0.059092 | 0.56176
|  | 18:21 | 22.6978 | 0.042185 | 0.56176
|  | 18:21 | 22.6989 | 0.028626 | 0.56176
|  | 18:21 | 22.7 | 0.015067 | 0.56176
|  | 18:21 | 22.7011 | 0.017848 | 0.56175
|  | 18:22 | 22.7022 | 0.020629 | 0.56175
|  | 18:22 | 22.7033 | 0.02341 | 0.56175
|  | 18:22 | 22.7044 | 0.02619 | 0.56175
|  | 18:22 | 22.7056 | 0.028971 | 0.56175
|  | 18:22 | 22.7067 | 0.040168 | 0.56174
|  | 18:22 | 22.7078 | 0.051364 | 0.56174
|  | 18:22 | 22.7089 | 0.060832 | 0.56174
|  | 18:22 | 22.71 | 0.068571 | 0.56174
|  | 18:22 | 22.7111 | 0.076309 | 0.56173
|  | 18:22 | 22.7122 | 0.077437 | 0.56173
|  | 18:22 | 22.7133 | 0.078564 | 0.56173
|  | 18:22 | 22.7144 | 0.080322 | 0.56173
|  | 18:22 | 22.7156 | 0.082711 | 0.56172
|  | 18:22 | 22.7167 | 0.085099 | 0.56172
|  | 18:22 | 22.7178 | 0.082506 | 0.56172
|  | 18:23 | 22.7189 | 0.079913 | 0.56172
|  | 18:23 | 22.72 | 0.07732 | 0.56172
|  | 18:23 | 22.7211 | 0.074727 | 0.56171
|  | 18:23 | 22.7222 | 0.072134 | 0.56171
|  | 18:23 | 22.7233 | 0.05751 | 0.56171
|  | 18:23 | 22.7244 | 0.042887 | 0.56171
|  | 18:23 | 22.7256 | 0.041184 | 0.5617
|  | 18:23 | 22.7267 | 0.052402 | 0.5617
|  | 18:23 | 22.7278 | 0.063621 | 0.5617
|  | 18:23 | 22.7289 | 0.059618 | 0.5617
|  | 18:23 | 22.73 | 0.055615 | 0.56169
|  | 18:23 | 22.7311 | 0.053782 | 0.56169
|  | 18:23 | 22.7322 | 0.054119 | 0.56169
|  | 18:23 | 22.7333 | 0.054456 | 0.56169
|  | 18:23 | 22.7344 | 0.052728 | 0.56169
|  | 18:24 | 22.7356 | 0.051 | 0.56168
|  | 18:24 | 22.7367 | 0.053232 | 0.56168
|  | 18:24 | 22.7378 | 0.059425 | 0.56168
|  | 18:24 | 22.7389 | 0.065617 | 0.56168
|  | 18:24 | 22.74 | 0.089973 | 0.56167
|  | 18:24 | 22.7411 | 0.11433 | 0.56167
|  | 18:24 | 22.7422 | 0.13104 | 0.56167
|  | 18:24 | 22.7433 | 0.14009 | 0.56167
|  | 18:24 | 22.7444 | 0.14915 | 0.56166
|  | 18:24 | 22.7456 | 0.14294 | 0.56166
|  | 18:24 | 22.7467 | 0.13674 | 0.56166
|  | 18:24 | 22.7478 | 0.13903 | 0.56166
|  | 18:24 | 22.7489 | 0.14981 | 0.56166
|  | 18:24 | 22.75 | 0.16059 | 0.56165
|  | 18:24 | 22.7511 | 0.17604 | 0.56165
|  | 18:25 | 22.7522 | 0.1915 | 0.56165
|  | 18:25 | 22.7533 | 0.20614 | 0.56165
|  | 18:25 | 22.7544 | 0.21996 | 0.56164
|  | 18:25 | 22.7556 | 0.23378 | 0.56164
|  | 18:25 | 22.7567 | 0.22649 | 0.56164
|  | 18:25 | 22.7578 | 0.2192 | 0.56164
|  | 18:25 | 22.7589 | 0.2103 | 0.56163
|  | 18:25 | 22.76 | 0.1998 | 0.56163
|  | 18:25 | 22.7611 | 0.18929 | 0.56163
|  | 18:25 | 22.7622 | 0.16969 | 0.56163
|  | 18:25 | 22.7633 | 0.15009 | 0.56162
|  | 18:25 | 22.7644 | 0.12595 | 0.56162
|  | 18:25 | 22.7656 | 0.09729 | 0.56162
|  | 18:25 | 22.7667 | 0.068625 | 0.56162
|  | 18:25 | 22.7678 | 0.07361 | 0.56162
|  | 18:26 | 22.7689 | 0.078594 | 0.56161
|  | 18:26 | 22.77 | 0.072993 | 0.56161
|  | 18:26 | 22.7711 | 0.056805 | 0.56161
|  | 18:26 | 22.7722 | 0.040617 | 0.56161
|  | 18:26 | 22.7733 | 0.014632 | 0.5616
|  | 18:26 | 22.7744 | -0.011353 | 0.5616
|  | 18:26 | 22.7756 | -0.035552 | 0.5616
|  | 18:26 | 22.7767 | -0.057963 | 0.5616
|  | 18:26 | 22.7778 | -0.080375 | 0.56159
|  | 18:26 | 22.7789 | -0.065543 | 0.56159
|  | 18:26 | 22.78 | -0.050712 | 0.56159
|  | 18:26 | 22.7811 | -0.031837 | 0.56159
|  | 18:26 | 22.7822 | -0.0089175 | 0.56159
|  | 18:26 | 22.7833 | 0.014002 | 0.56158
|  | 18:26 | 22.7844 | 0.0028253 | 0.56158
|  | 18:27 | 22.7856 | -0.0083511 | 0.56158
|  | 18:27 | 22.7867 | -0.022928 | 0.56158
|  | 18:27 | 22.7878 | -0.040906 | 0.56157
|  | 18:27 | 22.7889 | -0.058884 | 0.56157
|  | 18:27 | 22.79 | -0.068746 | 0.56157
|  | 18:27 | 22.7911 | -0.078609 | 0.56157
|  | 18:27 | 22.7922 | -0.07932 | 0.56156
|  | 18:27 | 22.7933 | -0.076982 | 0.56156
|  | 18:27 | 22.7944 | -0.074643 | 0.56156
|  | 18:27 | 22.7956 | -0.075455 | 0.56156
|  | 18:27 | 22.7967 | -0.076267 | 0.56156
|  | 18:27 | 22.7978 | -0.073963 | 0.56155
|  | 18:27 | 22.7989 | -0.07062 | 0.56155
|  | 18:27 | 22.8 | -0.067277 | 0.56155
|  | 18:27 | 22.8011 | -0.087801 | 0.56155
|  | 18:28 | 22.8022 | -0.10832 | 0.56154
|  | 18:28 | 22.8033 | -0.11242 | 0.56154
|  | 18:28 | 22.8044 | -0.10009 | 0.56154
|  | 18:28 | 22.8056 | -0.087763 | 0.56154
|  | 18:28 | 22.8067 | -0.068639 | 0.56153
|  | 18:28 | 22.8078 | -0.049516 | 0.56153
|  | 18:28 | 22.8089 | -0.015747 | 0.56153
|  | 18:28 | 22.81 | 0.032669 | 0.56153
|  | 18:28 | 22.8111 | 0.076313 | 0.56153
|  | 18:28 | 22.8122 | 0.10565 | 0.56152
|  | 18:28 | 22.8133 | 0.13498 | 0.56152
|  | 18:28 | 22.8144 | 0.14996 | 0.56152
|  | 18:28 | 22.8156 | 0.1506 | 0.56152
|  | 18:28 | 22.8167 | 0.15123 | 0.56151
|  | 18:28 | 22.8178 | 0.15947 | 0.56151
|  | 18:29 | 22.8189 | 0.1677 | 0.56151
|  | 18:29 | 22.82 | 0.16361 | 0.56151
|  | 18:29 | 22.8211 | 0.14719 | 0.5615
|  | 18:29 | 22.8222 | 0.13078 | 0.5615
|  | 18:29 | 22.8233 | 0.11437 | 0.5615
|  | 18:29 | 22.8244 | 0.097961 | 0.5615
|  | 18:29 | 22.8256 | 0.077558 | 0.5615
|  | 18:29 | 22.8267 | 0.055824 | 0.56149
|  | 18:29 | 22.8278 | 0.034089 | 0.56149
|  | 18:29 | 22.8289 | 0.018564 | 0.56149
|  | 18:29 | 22.83 | 0.0030393 | 0.56149
|  | 18:29 | 22.8311 | -0.016027 | 0.56148
|  | 18:29 | 22.8322 | -0.038635 | 0.56148
|  | 18:29 | 22.8333 | -0.061243 | 0.56148
|  | 18:29 | 22.8344 | -0.068344 | 0.56148
|  | 18:30 | 22.8356 | -0.075445 | 0.56147
|  | 18:30 | 22.8367 | -0.080764 | 0.56147
|  | 18:30 | 22.8378 | -0.0843 | 0.56147
|  | 18:30 | 22.8389 | -0.087836 | 0.56147
|  | 18:30 | 22.84 | -0.08516 | 0.56147
|  | 18:30 | 22.8411 | -0.082483 | 0.56146
|  | 18:30 | 22.8422 | -0.079807 | 0.56146
|  | 18:30 | 22.8433 | -0.07713 | 0.56146
|  | 18:30 | 22.8444 | -0.074454 | 0.56146
|  | 18:30 | 22.8456 | -0.076025 | 0.56145
|  | 18:30 | 22.8467 | -0.077597 | 0.56145
|  | 18:30 | 22.8478 | -0.085439 | 0.56145
|  | 18:30 | 22.8489 | -0.09955 | 0.56145
|  | 18:30 | 22.85 | -0.11366 | 0.56144
|  | 18:30 | 22.8511 | -0.11441 | 0.56144
|  | 18:31 | 22.8522 | -0.11516 | 0.56144
|  | 18:31 | 22.8533 | -0.10971 | 0.56144
|  | 18:31 | 22.8544 | -0.09806 | 0.56144
|  | 18:31 | 22.8556 | -0.084509 | 0.56143
|  | 18:31 | 22.8567 | -0.065244 | 0.56143
|  | 18:31 | 22.8578 | -0.045979 | 0.56143
|  | 18:31 | 22.8589 | -0.029559 | 0.56143
|  | 18:31 | 22.86 | -0.015984 | 0.56142
|  | 18:31 | 22.8611 | -0.0024094 | 0.56142
|  | 18:31 | 22.8622 | 0.022238 | 0.56142
|  | 18:31 | 22.8633 | 0.046885 | 0.56142
|  | 18:31 | 22.8644 | 0.074314 | 0.56141
|  | 18:31 | 22.8656 | 0.10453 | 0.56141
|  | 18:31 | 22.8667 | 0.13474 | 0.56141
|  | 18:31 | 22.8678 | 0.15843 | 0.56141
|  | 18:32 | 22.8689 | 0.18212 | 0.56141
|  | 18:32 | 22.87 | 0.20365 | 0.5614
|  | 18:32 | 22.8711 | 0.22304 | 0.5614
|  | 18:32 | 22.8722 | 0.24243 | 0.5614
|  | 18:32 | 22.8733 | 0.2467 | 0.5614
|  | 18:32 | 22.8744 | 0.25097 | 0.56139
|  | 18:32 | 22.8756 | 0.25524 | 0.56139
|  | 18:32 | 22.8767 | 0.25952 | 0.56139
|  | 18:32 | 22.8778 | 0.26379 | 0.56139
|  | 18:32 | 22.8789 | 0.26806 | 0.56138
|  | 18:32 | 22.88 | 0.27234 | 0.56138
|  | 18:32 | 22.8811 | 0.27055 | 0.56138
|  | 18:32 | 22.8822 | 0.26272 | 0.56138
|  | 18:32 | 22.8833 | 0.25488 | 0.56137
|  | 18:32 | 22.8844 | 0.23498 | 0.56137
|  | 18:33 | 22.8856 | 0.21507 | 0.56137
|  | 18:33 | 22.8867 | 0.20228 | 0.56137
|  | 18:33 | 22.8878 | 0.1966 | 0.56137
|  | 18:33 | 22.8889 | 0.19092 | 0.56136
|  | 18:33 | 22.89 | 0.17374 | 0.56136
|  | 18:33 | 22.8911 | 0.15656 | 0.56136
|  | 18:33 | 22.8922 | 0.14737 | 0.56136
|  | 18:33 | 22.8933 | 0.14617 | 0.56135
|  | 18:33 | 22.8944 | 0.14096 | 0.56135
|  | 18:33 | 22.8956 | 0.1237 | 0.56135
|  | 18:33 | 22.8967 | 0.10644 | 0.56135
|  | 18:33 | 22.8978 | 0.091813 | 0.56134
|  | 18:33 | 22.8989 | 0.079822 | 0.56134
|  | 18:33 | 22.9 | 0.067831 | 0.56134
|  | 18:33 | 22.9011 | 0.075896 | 0.56134
|  | 18:34 | 22.9022 | 0.083961 | 0.56134
|  | 18:34 | 22.9033 | 0.086463 | 0.56133
|  | 18:34 | 22.9044 | 0.083403 | 0.56133
|  | 18:34 | 22.9056 | 0.080342 | 0.56133
|  | 18:34 | 22.9067 | 0.086139 | 0.56133
|  | 18:34 | 22.9078 | 0.091936 | 0.56132
|  | 18:34 | 22.9089 | 0.086932 | 0.56132
|  | 18:34 | 22.91 | 0.071129 | 0.56132
|  | 18:34 | 22.9111 | 0.055325 | 0.56132
|  | 18:34 | 22.9122 | 0.058039 | 0.56131
|  | 18:34 | 22.9133 | 0.060754 | 0.56131
|  | 18:34 | 22.9144 | 0.053289 | 0.56131
|  | 18:34 | 22.9156 | 0.035644 | 0.56131
|  | 18:34 | 22.9167 | 0.018 | 0.56131
|  | 18:34 | 22.9178 | -0.013065 | 0.5613
|  | 18:35 | 22.9189 | -0.04413 | 0.5613
|  | 18:35 | 22.92 | -0.070275 | 0.5613
|  | 18:35 | 22.9211 | -0.091499 | 0.5613
|  | 18:35 | 22.9222 | -0.11272 | 0.56129
|  | 18:35 | 22.9233 | -0.1153 | 0.56129
|  | 18:35 | 22.9244 | -0.11788 | 0.56129
|  | 18:35 | 22.9256 | -0.11783 | 0.56129
|  | 18:35 | 22.9267 | -0.11514 | 0.56128
|  | 18:35 | 22.9278 | -0.11272 | 0.56128
|  | 18:35 | 22.9289 | -0.11108 | 0.56128
|  | 18:35 | 22.93 | -0.10944 | 0.56128
|  | 18:35 | 22.9311 | -0.1078 | 0.56128
|  | 18:35 | 22.9322 | -0.12031 | 0.56127
|  | 18:35 | 22.9333 | -0.13283 | 0.56127
|  | 18:35 | 22.9344 | -0.13556 | 0.56127
|  | 18:36 | 22.9356 | -0.1383 | 0.56127
|  | 18:36 | 22.9367 | -0.13564 | 0.56126
|  | 18:36 | 22.9378 | -0.13119 | 0.56126
|  | 18:36 | 22.9389 | -0.1251 | 0.56126
|  | 18:36 | 22.94 | -0.11411 | 0.56126
|  | 18:36 | 22.9411 | -0.10312 | 0.56125
|  | 18:36 | 22.9422 | -0.087127 | 0.56125
|  | 18:36 | 22.9433 | -0.06947 | 0.56125
|  | 18:36 | 22.9444 | -0.057029 | 0.56125
|  | 18:36 | 22.9456 | -0.060235 | 0.56125
|  | 18:36 | 22.9467 | -0.06344 | 0.56124
|  | 18:36 | 22.9478 | -0.059529 | 0.56124
|  | 18:36 | 22.9489 | -0.053247 | 0.56124
|  | 18:36 | 22.95 | -0.048412 | 0.56124
|  | 18:36 | 22.9511 | -0.047923 | 0.56123
|  | 18:37 | 22.9522 | -0.047434 | 0.56123
|  | 18:37 | 22.9533 | -0.052124 | 0.56123
|  | 18:37 | 22.9544 | -0.05854 | 0.56123
|  | 18:37 | 22.9556 | -0.068618 | 0.56122
|  | 18:37 | 22.9567 | -0.08968 | 0.56122
|  | 18:37 | 22.9578 | -0.11074 | 0.56122
|  | 18:37 | 22.9589 | -0.12803 | 0.56122
|  | 18:37 | 22.96 | -0.14405 | 0.56122
|  | 18:37 | 22.9611 | -0.15587 | 0.56121
|  | 18:37 | 22.9622 | -0.15507 | 0.56121
|  | 18:37 | 22.9633 | -0.15427 | 0.56121
|  | 18:37 | 22.9644 | -0.1689 | 0.56121
|  | 18:37 | 22.9656 | -0.18867 | 0.5612
|  | 18:37 | 22.9667 | -0.19879 | 0.5612
|  | 18:37 | 22.9678 | -0.17995 | 0.5612
|  | 18:38 | 22.9689 | -0.16112 | 0.5612
|  | 18:38 | 22.97 | -0.14042 | 0.56119
|  | 18:38 | 22.9711 | -0.1191 | 0.56119
|  | 18:38 | 22.9722 | -0.087246 | 0.56119
|  | 18:38 | 22.9733 | -0.023777 | 0.56119
|  | 18:38 | 22.9744 | 0.039692 | 0.56119
|  | 18:38 | 22.9756 | 0.084628 | 0.56118
|  | 18:38 | 22.9767 | 0.12956 | 0.56118
|  | 18:38 | 22.9778 | 0.17372 | 0.56118
|  | 18:38 | 22.9789 | 0.21556 | 0.56118
|  | 18:38 | 22.98 | 0.2574 | 0.56117
|  | 18:38 | 22.9811 | 0.26371 | 0.56117
|  | 18:38 | 22.9822 | 0.25818 | 0.56117
|  | 18:38 | 22.9833 | 0.25264 | 0.56117
|  | 18:38 | 22.9844 | 0.24711 | 0.56116
|  | 18:39 | 22.9856 | 0.24157 | 0.56116
|  | 18:39 | 22.9867 | 0.24404 | 0.56116
|  | 18:39 | 22.9878 | 0.24918 | 0.56116
|  | 18:39 | 22.9889 | 0.25653 | 0.56116
|  | 18:39 | 22.99 | 0.27053 | 0.56115
|  | 18:39 | 22.9911 | 0.28454 | 0.56115
|  | 18:39 | 22.9922 | 0.28643 | 0.56115
|  | 18:39 | 22.9933 | 0.28428 | 0.56115
|  | 18:39 | 22.9944 | 0.28637 | 0.56114
|  | 18:39 | 22.9956 | 0.30114 | 0.56114
|  | 18:39 | 22.9967 | 0.31592 | 0.56114
|  | 18:39 | 22.9978 | 0.32289 | 0.56114
|  | 18:39 | 22.9989 | 0.32726 | 0.56113
|  | 18:39 | 23 | 0.32399 | 0.56113
|  | 18:39 | 23.0011 | 0.3131 | 0.56113
|  | 18:40 | 23.0022 | 0.3022 | 0.56113
|  | 18:40 | 23.0033 | 0.28574 | 0.56112
|  | 18:40 | 23.0044 | 0.26742 | 0.56112
|  | 18:40 | 23.0056 | 0.24996 | 0.56112
|  | 18:40 | 23.0067 | 0.23337 | 0.56112
|  | 18:40 | 23.0078 | 0.21678 | 0.56112
|  | 18:40 | 23.0089 | 0.18735 | 0.56111
|  | 18:40 | 23.01 | 0.15364 | 0.56111
|  | 18:40 | 23.0111 | 0.13899 | 0.56111
|  | 18:40 | 23.0122 | 0.1434 | 0.56111
|  | 18:40 | 23.0133 | 0.1478 | 0.5611
|  | 18:40 | 23.0144 | 0.16101 | 0.5611
|  | 18:40 | 23.0156 | 0.17715 | 0.5611
|  | 18:40 | 23.0167 | 0.1784 | 0.5611
|  | 18:40 | 23.0178 | 0.16474 | 0.56109
|  | 18:41 | 23.0189 | 0.15109 | 0.56109
|  | 18:41 | 23.02 | 0.12306 | 0.56109
|  | 18:41 | 23.0211 | 0.090241 | 0.56109
|  | 18:41 | 23.0222 | 0.056587 | 0.56109
|  | 18:41 | 23.0233 | 0.020429 | 0.56108
|  | 18:41 | 23.0244 | -0.015729 | 0.56108
|  | 18:41 | 23.0256 | -0.042232 | 0.56108
|  | 18:41 | 23.0267 | -0.065516 | 0.56108
|  | 18:41 | 23.0278 | -0.087599 | 0.56107
|  | 18:41 | 23.0289 | -0.10608 | 0.56107
|  | 18:41 | 23.03 | -0.12456 | 0.56107
|  | 18:41 | 23.0311 | -0.13921 | 0.56107
|  | 18:41 | 23.0322 | -0.15259 | 0.56106
|  | 18:41 | 23.0333 | -0.16354 | 0.56106
|  | 18:41 | 23.0344 | -0.16719 | 0.56106
|  | 18:42 | 23.0356 | -0.17083 | 0.56106
|  | 18:42 | 23.0367 | -0.19514 | 0.56106
|  | 18:42 | 23.0378 | -0.22632 | 0.56105
|  | 18:42 | 23.0389 | -0.24783 | 0.56105
|  | 18:42 | 23.04 | -0.24028 | 0.56105
|  | 18:42 | 23.0411 | -0.23273 | 0.56105
|  | 18:42 | 23.0422 | -0.22091 | 0.56104
|  | 18:42 | 23.0433 | -0.20767 | 0.56104
|  | 18:42 | 23.0444 | -0.19169 | 0.56104
|  | 18:42 | 23.0456 | -0.1675 | 0.56104
|  | 18:42 | 23.0467 | -0.14331 | 0.56103
|  | 18:42 | 23.0478 | -0.12658 | 0.56103
|  | 18:42 | 23.0489 | -0.11235 | 0.56103
|  | 18:42 | 23.05 | -0.099041 | 0.56103
|  | 18:42 | 23.0511 | -0.088485 | 0.56103
|  | 18:43 | 23.0522 | -0.077929 | 0.56102
|  | 18:43 | 23.0533 | -0.06405 | 0.56102
|  | 18:43 | 23.0544 | -0.049063 | 0.56102
|  | 18:43 | 23.0556 | -0.032325 | 0.56102
|  | 18:43 | 23.0567 | -0.01033 | 0.56101
|  | 18:43 | 23.0578 | 0.011664 | 0.56101
|  | 18:43 | 23.0589 | 0.025807 | 0.56101
|  | 18:43 | 23.06 | 0.037333 | 0.56101
|  | 18:43 | 23.0611 | 0.049144 | 0.561
|  | 18:43 | 23.0622 | 0.06181 | 0.561
|  | 18:43 | 23.0633 | 0.074475 | 0.561
|  | 18:43 | 23.0644 | 0.088406 | 0.561
|  | 18:43 | 23.0656 | 0.10276 | 0.561
|  | 18:43 | 23.0667 | 0.11637 | 0.56099
|  | 18:43 | 23.0678 | 0.12776 | 0.56099
|  | 18:44 | 23.0689 | 0.13916 | 0.56099
|  | 18:44 | 23.07 | 0.15333 | 0.56099
|  | 18:44 | 23.0711 | 0.16843 | 0.56098
|  | 18:44 | 23.0722 | 0.18226 | 0.56098
|  | 18:44 | 23.0733 | 0.19228 | 0.56098
|  | 18:44 | 23.0744 | 0.20229 | 0.56098
|  | 18:44 | 23.0756 | 0.18703 | 0.56097
|  | 18:44 | 23.0767 | 0.17176 | 0.56097
|  | 18:44 | 23.0778 | 0.15361 | 0.56097
|  | 18:44 | 23.0789 | 0.12677 | 0.56097
|  | 18:44 | 23.08 | 0.099932 | 0.56097
|  | 18:44 | 23.0811 | 0.080254 | 0.56096
|  | 18:44 | 23.0822 | 0.062962 | 0.56096
|  | 18:44 | 23.0833 | 0.049071 | 0.56096
|  | 18:44 | 23.0844 | 0.045383 | 0.56096
|  | 18:45 | 23.0856 | 0.041695 | 0.56095
|  | 18:45 | 23.0867 | 0.032198 | 0.56095
|  | 18:45 | 23.0878 | 0.020765 | 0.56095
|  | 18:45 | 23.0889 | 0.010218 | 0.56095
|  | 18:45 | 23.09 | 0.0023298 | 0.56094
|  | 18:45 | 23.0911 | -0.0055582 | 0.56094
|  | 18:45 | 23.0922 | -0.023576 | 0.56094
|  | 18:45 | 23.0933 | -0.04497 | 0.56094
|  | 18:45 | 23.0944 | -0.063236 | 0.56094
|  | 18:45 | 23.0956 | -0.072119 | 0.56093
|  | 18:45 | 23.0967 | -0.081002 | 0.56093
|  | 18:45 | 23.0978 | -0.091497 | 0.56093
|  | 18:45 | 23.0989 | -0.10253 | 0.56093
|  | 18:45 | 23.1 | -0.11184 | 0.56092
|  | 18:45 | 23.1011 | -0.11599 | 0.56092
|  | 18:46 | 23.1022 | -0.12014 | 0.56092
|  | 18:46 | 23.1033 | -0.12608 | 0.56092
|  | 18:46 | 23.1044 | -0.13383 | 0.56091
|  | 18:46 | 23.1056 | -0.14157 | 0.56091
|  | 18:46 | 23.1067 | -0.14002 | 0.56091
|  | 18:46 | 23.1078 | -0.13847 | 0.56091
|  | 18:46 | 23.1089 | -0.14396 | 0.56091
|  | 18:46 | 23.11 | -0.1565 | 0.5609
|  | 18:46 | 23.1111 | -0.16904 | 0.5609
|  | 18:46 | 23.1122 | -0.18405 | 0.5609
|  | 18:46 | 23.1133 | -0.19905 | 0.5609
|  | 18:46 | 23.1144 | -0.20539 | 0.56089
|  | 18:46 | 23.1156 | -0.20306 | 0.56089
|  | 18:46 | 23.1167 | -0.20073 | 0.56089
|  | 18:46 | 23.1178 | -0.17283 | 0.56089
|  | 18:47 | 23.1189 | -0.14493 | 0.56088
|  | 18:47 | 23.12 | -0.1155 | 0.56088
|  | 18:47 | 23.1211 | -0.084542 | 0.56088
|  | 18:47 | 23.1222 | -0.053583 | 0.56088
|  | 18:47 | 23.1233 | -0.01823 | 0.56087
|  | 18:47 | 23.1244 | 0.017124 | 0.56087
|  | 18:47 | 23.1256 | 0.042132 | 0.56087
|  | 18:47 | 23.1267 | 0.056796 | 0.56087
|  | 18:47 | 23.1278 | 0.07146 | 0.56087
|  | 18:47 | 23.1289 | 0.069582 | 0.56086
|  | 18:47 | 23.13 | 0.067705 | 0.56086
|  | 18:47 | 23.1311 | 0.068706 | 0.56086
|  | 18:47 | 23.1322 | 0.072586 | 0.56086
|  | 18:47 | 23.1333 | 0.076467 | 0.56085
|  | 18:47 | 23.1344 | 0.08665 | 0.56085
|  | 18:48 | 23.1356 | 0.096832 | 0.56085
|  | 18:48 | 23.1367 | 0.097433 | 0.56085
|  | 18:48 | 23.1378 | 0.088452 | 0.56084
|  | 18:48 | 23.1389 | 0.079471 | 0.56084
|  | 18:48 | 23.14 | 0.07049 | 0.56084
|  | 18:48 | 23.1411 | 0.061509 | 0.56084
|  | 18:48 | 23.1422 | 0.044761 | 0.56084
|  | 18:48 | 23.1433 | 0.020245 | 0.56083
|  | 18:48 | 23.1444 | -0.0042709 | 0.56083
|  | 18:48 | 23.1456 | -0.0071686 | 0.56083
|  | 18:48 | 23.1467 | -0.010066 | 0.56083
|  | 18:48 | 23.1478 | -0.015785 | 0.56082
|  | 18:48 | 23.1489 | -0.024325 | 0.56082
|  | 18:48 | 23.15 | -0.032865 | 0.56082
|  | 18:48 | 23.1511 | -0.041405 | 0.56082
|  | 18:49 | 23.1522 | -0.049945 | 0.56081
|  | 18:49 | 23.1533 | -0.061732 | 0.56081
|  | 18:49 | 23.1544 | -0.076764 | 0.56081
|  | 18:49 | 23.1556 | -0.091797 | 0.56081
|  | 18:49 | 23.1567 | -0.081949 | 0.56081
|  | 18:49 | 23.1578 | -0.072101 | 0.5608
|  | 18:49 | 23.1589 | -0.069993 | 0.5608
|  | 18:49 | 23.16 | -0.075625 | 0.5608
|  | 18:49 | 23.1611 | -0.081256 | 0.5608
|  | 18:49 | 23.1622 | -0.10398 | 0.56079
|  | 18:49 | 23.1633 | -0.12671 | 0.56079
|  | 18:49 | 23.1644 | -0.13424 | 0.56079
|  | 18:49 | 23.1656 | -0.13671 | 0.56079
|  | 18:49 | 23.1667 | -0.13917 | 0.56078
|  | 18:49 | 23.1678 | -0.13967 | 0.56078
|  | 18:50 | 23.1689 | -0.14016 | 0.56078
|  | 18:50 | 23.17 | -0.13967 | 0.56078
|  | 18:50 | 23.1711 | -0.1382 | 0.56078
|  | 18:50 | 23.1722 | -0.13672 | 0.56077
|  | 18:50 | 23.1733 | -0.13986 | 0.56077
|  | 18:50 | 23.1744 | -0.143 | 0.56077
|  | 18:50 | 23.1756 | -0.15783 | 0.56077
|  | 18:50 | 23.1767 | -0.18435 | 0.56076
|  | 18:50 | 23.1778 | -0.21088 | 0.56076
|  | 18:50 | 23.1789 | -0.23015 | 0.56076
|  | 18:50 | 23.18 | -0.24943 | 0.56076
|  | 18:50 | 23.1811 | -0.27026 | 0.56075
|  | 18:50 | 23.1822 | -0.29265 | 0.56075
|  | 18:50 | 23.1833 | -0.31503 | 0.56075
|  | 18:50 | 23.1844 | -0.32195 | 0.56075
|  | 18:51 | 23.1856 | -0.32886 | 0.56075
|  | 18:51 | 23.1867 | -0.34119 | 0.56074
|  | 18:51 | 23.1878 | -0.35894 | 0.56074
|  | 18:51 | 23.1889 | -0.37669 | 0.56074
|  | 18:51 | 23.19 | -0.40678 | 0.56074
|  | 18:51 | 23.1911 | -0.43687 | 0.56073
|  | 18:51 | 23.1922 | -0.47126 | 0.56073
|  | 18:51 | 23.1933 | -0.50996 | 0.56073
|  | 18:51 | 23.1944 | -0.54865 | 0.56073
|  | 18:51 | 23.1956 | -0.56956 | 0.56072
|  | 18:51 | 23.1967 | -0.59046 | 0.56072
|  | 18:51 | 23.1978 | -0.60099 | 0.56072
|  | 18:51 | 23.1989 | -0.60114 | 0.56072
|  | 18:51 | 23.2 | -0.60129 | 0.56072
|  | 18:51 | 23.2011 | -0.60725 | 0.56071
|  | 18:52 | 23.2022 | -0.6132 | 0.56071
|  | 18:52 | 23.2033 | -0.61495 | 0.56071
|  | 18:52 | 23.2044 | -0.6125 | 0.56071
|  | 18:52 | 23.2056 | -0.61004 | 0.5607
|  | 18:52 | 23.2067 | -0.60192 | 0.5607
|  | 18:52 | 23.2078 | -0.59379 | 0.5607
|  | 18:52 | 23.2089 | -0.57338 | 0.5607
|  | 18:52 | 23.21 | -0.54068 | 0.56069
|  | 18:52 | 23.2111 | -0.50798 | 0.56069
|  | 18:52 | 23.2122 | -0.44948 | 0.56069
|  | 18:52 | 23.2133 | -0.39097 | 0.56069
|  | 18:52 | 23.2144 | -0.34491 | 0.56069
|  | 18:52 | 23.2156 | -0.30298 | 0.56068
|  | 18:52 | 23.2167 | -0.26106 | 0.56068
|  | 18:52 | 23.2178 | -0.21372 | 0.56068
|  | 18:53 | 23.2189 | -0.16637 | 0.56068
|  | 18:53 | 23.22 | -0.13138 | 0.56067
|  | 18:53 | 23.2211 | -0.10875 | 0.56067
|  | 18:53 | 23.2222 | -0.086123 | 0.56067
|  | 18:53 | 23.2233 | -0.059309 | 0.56067
|  | 18:53 | 23.2244 | -0.032495 | 0.56066
|  | 18:53 | 23.2256 | -0.0085625 | 0.56066
|  | 18:53 | 23.2267 | 0.01441 | 0.56066
|  | 18:53 | 23.2278 | 0.037382 | 0.56066
|  | 18:53 | 23.2289 | 0.066252 | 0.56066
|  | 18:53 | 23.23 | 0.095122 | 0.56065
|  | 18:53 | 23.2311 | 0.10872 | 0.56065
|  | 18:53 | 23.2322 | 0.10704 | 0.56065
|  | 18:53 | 23.2333 | 0.10536 | 0.56065
|  | 18:53 | 23.2344 | 0.10089 | 0.56064
|  | 18:54 | 23.2356 | 0.088038 | 0.56064
|  | 18:54 | 23.2367 | 0.080428 | 0.56064
|  | 18:54 | 23.2378 | 0.078054 | 0.56064
|  | 18:54 | 23.2389 | 0.07568 | 0.56063
|  | 18:54 | 23.24 | 0.060873 | 0.56063
|  | 18:54 | 23.2411 | 0.046067 | 0.56063
|  | 18:54 | 23.2422 | 0.032489 | 0.56063
|  | 18:54 | 23.2433 | 0.02014 | 0.56062
|  | 18:54 | 23.2444 | 0.0077913 | 0.56062
|  | 18:54 | 23.2456 | 0.0089382 | 0.56062
|  | 18:54 | 23.2467 | 0.010085 | 0.56062
|  | 18:54 | 23.2478 | 0.017944 | 0.56062
|  | 18:54 | 23.2489 | 0.032514 | 0.56061
|  | 18:54 | 23.25 | 0.047085 | 0.56061
|  | 18:54 | 23.2511 | 0.076109 | 0.56061
|  | 18:55 | 23.2522 | 0.10513 | 0.56061
|  | 18:55 | 23.2533 | 0.13867 | 0.5606
|  | 18:55 | 23.2544 | 0.17371 | 0.5606
|  | 18:55 | 23.2556 | 0.20875 | 0.5606
|  | 18:55 | 23.2567 | 0.23334 | 0.5606
|  | 18:55 | 23.2578 | 0.25792 | 0.56059
|  | 18:55 | 23.2589 | 0.27615 | 0.56059
|  | 18:55 | 23.26 | 0.28804 | 0.56059
|  | 18:55 | 23.2611 | 0.29992 | 0.56059
|  | 18:55 | 23.2622 | 0.31798 | 0.56059
|  | 18:55 | 23.2633 | 0.33605 | 0.56058
|  | 18:55 | 23.2644 | 0.36385 | 0.56058
|  | 18:55 | 23.2656 | 0.40137 | 0.56058
|  | 18:55 | 23.2667 | 0.4389 | 0.56058
|  | 18:55 | 23.2678 | 0.47837 | 0.56057
|  | 18:56 | 23.2689 | 0.51784 | 0.56057
|  | 18:56 | 23.27 | 0.54605 | 0.56057
|  | 18:56 | 23.2711 | 0.57051 | 0.56057
|  | 18:56 | 23.2722 | 0.59043 | 0.56056
|  | 18:56 | 23.2733 | 0.59672 | 0.56056
|  | 18:56 | 23.2744 | 0.60301 | 0.56056
|  | 18:56 | 23.2756 | 0.61476 | 0.56056
|  | 18:56 | 23.2767 | 0.62833 | 0.56056
|  | 18:56 | 23.2778 | 0.63908 | 0.56055
|  | 18:56 | 23.2789 | 0.64134 | 0.56055
|  | 18:56 | 23.28 | 0.6436 | 0.56055
|  | 18:56 | 23.2811 | 0.64966 | 0.56055
|  | 18:56 | 23.2822 | 0.65699 | 0.56054
|  | 18:56 | 23.2833 | 0.66861 | 0.56054
|  | 18:56 | 23.2844 | 0.69311 | 0.56054
|  | 18:57 | 23.2856 | 0.71761 | 0.56054
|  | 18:57 | 23.2867 | 0.72431 | 0.56053
|  | 18:57 | 23.2878 | 0.72507 | 0.56053
|  | 18:57 | 23.2889 | 0.72324 | 0.56053
|  | 18:57 | 23.29 | 0.71361 | 0.56053
|  | 18:57 | 23.2911 | 0.70399 | 0.56053
|  | 18:57 | 23.2922 | 0.68391 | 0.56052
|  | 18:57 | 23.2933 | 0.66036 | 0.56052
|  | 18:57 | 23.2944 | 0.63042 | 0.56052
|  | 18:57 | 23.2956 | 0.58134 | 0.56052
|  | 18:57 | 23.2967 | 0.53226 | 0.56051
|  | 18:57 | 23.2978 | 0.48119 | 0.56051
|  | 18:57 | 23.2989 | 0.42944 | 0.56051
|  | 18:57 | 23.3 | 0.38903 | 0.56051
|  | 18:57 | 23.3011 | 0.35995 | 0.5605
|  | 18:58 | 23.3022 | 0.33088 | 0.5605
|  | 18:58 | 23.3033 | 0.2821 | 0.5605
|  | 18:58 | 23.3044 | 0.22676 | 0.5605
|  | 18:58 | 23.3056 | 0.17658 | 0.5605
|  | 18:58 | 23.3067 | 0.1419 | 0.56049
|  | 18:58 | 23.3078 | 0.10722 | 0.56049
|  | 18:58 | 23.3089 | 0.081901 | 0.56049
|  | 18:58 | 23.31 | 0.056586 | 0.56049
|  | 18:58 | 23.3111 | 0.030142 | 0.56048
|  | 18:58 | 23.3122 | 0.00031549 | 0.56048
|  | 18:58 | 23.3133 | -0.029511 | 0.56048
|  | 18:58 | 23.3144 | -0.058698 | 0.56048
|  | 18:58 | 23.3156 | -0.087671 | 0.56047
|  | 18:58 | 23.3167 | -0.11306 | 0.56047
|  | 18:58 | 23.3178 | -0.12771 | 0.56047
|  | 18:59 | 23.3189 | -0.14236 | 0.56047
|  | 18:59 | 23.32 | -0.16624 | 0.56047
|  | 18:59 | 23.3211 | -0.1932 | 0.56046
|  | 18:59 | 23.3222 | -0.22575 | 0.56046
|  | 18:59 | 23.3233 | -0.2751 | 0.56046
|  | 18:59 | 23.3244 | -0.32445 | 0.56046
|  | 18:59 | 23.3256 | -0.35449 | 0.56045
|  | 18:59 | 23.3267 | -0.37809 | 0.56045
|  | 18:59 | 23.3278 | -0.39723 | 0.56045
|  | 18:59 | 23.3289 | -0.40298 | 0.56045
|  | 18:59 | 23.33 | -0.40874 | 0.56044
|  | 18:59 | 23.3311 | -0.41121 | 0.56044
|  | 18:59 | 23.3322 | -0.41258 | 0.56044
|  | 18:59 | 23.3333 | -0.4191 | 0.56044
|  | 18:59 | 23.3344 | -0.44105 | 0.56044
|  | 19:00 | 23.3356 | -0.46301 | 0.56043
|  | 19:00 | 23.3367 | -0.4794 | 0.56043
|  | 19:00 | 23.3378 | -0.49394 | 0.56043
|  | 19:00 | 23.3389 | -0.50803 | 0.56043
|  | 19:00 | 23.34 | -0.52082 | 0.56042
|  | 19:00 | 23.3411 | -0.53361 | 0.56042
|  | 19:00 | 23.3422 | -0.57167 | 0.56042
|  | 19:00 | 23.3433 | -0.61817 | 0.56042
|  | 19:00 | 23.3444 | -0.65686 | 0.56041
|  | 19:00 | 23.3456 | -0.67212 | 0.56041
|  | 19:00 | 23.3467 | -0.68739 | 0.56041
|  | 19:00 | 23.3478 | -0.69862 | 0.56041
|  | 19:00 | 23.3489 | -0.7085 | 0.56041
|  | 19:00 | 23.35 | -0.7136 | 0.5604
|  | 19:00 | 23.3511 | -0.70432 | 0.5604
|  | 19:01 | 23.3522 | -0.69505 | 0.5604
|  | 19:01 | 23.3533 | -0.67207 | 0.5604
|  | 19:01 | 23.3544 | -0.64451 | 0.56039
|  | 19:01 | 23.3556 | -0.61836 | 0.56039
|  | 19:01 | 23.3567 | -0.59644 | 0.56039
|  | 19:01 | 23.3578 | -0.57451 | 0.56039
|  | 19:01 | 23.3589 | -0.55325 | 0.56038
|  | 19:01 | 23.36 | -0.53222 | 0.56038
|  | 19:01 | 23.3611 | -0.51696 | 0.56038
|  | 19:01 | 23.3622 | -0.51903 | 0.56038
|  | 19:01 | 23.3633 | -0.5211 | 0.56037
|  | 19:01 | 23.3644 | -0.52402 | 0.56037
|  | 19:01 | 23.3656 | -0.52724 | 0.56037
|  | 19:01 | 23.3667 | -0.52781 | 0.56037
|  | 19:01 | 23.3678 | -0.52046 | 0.56037
|  | 19:02 | 23.3689 | -0.51311 | 0.56036
|  | 19:02 | 23.37 | -0.49295 | 0.56036
|  | 19:02 | 23.3711 | -0.46852 | 0.56036
|  | 19:02 | 23.3722 | -0.44277 | 0.56036
|  | 19:02 | 23.3733 | -0.41302 | 0.56035
|  | 19:02 | 23.3744 | -0.38327 | 0.56035
|  | 19:02 | 23.3756 | -0.36219 | 0.56035
|  | 19:02 | 23.3767 | -0.34399 | 0.56035
|  | 19:02 | 23.3778 | -0.32331 | 0.56034
|  | 19:02 | 23.3789 | -0.29521 | 0.56034
|  | 19:02 | 23.38 | -0.26711 | 0.56034
|  | 19:02 | 23.3811 | -0.22818 | 0.56034
|  | 19:02 | 23.3822 | -0.18565 | 0.56034
|  | 19:02 | 23.3833 | -0.14681 | 0.56033
|  | 19:02 | 23.3844 | -0.11909 | 0.56033
|  | 19:03 | 23.3856 | -0.091362 | 0.56033
|  | 19:03 | 23.3867 | -0.063635 | 0.56033
|  | 19:03 | 23.3878 | -0.035909 | 0.56032
|  | 19:03 | 23.3889 | -0.010399 | 0.56032
|  | 19:03 | 23.39 | 0.008462 | 0.56032
|  | 19:03 | 23.3911 | 0.027323 | 0.56032
|  | 19:03 | 23.3922 | 0.034398 | 0.56031
|  | 19:03 | 23.3933 | 0.037546 | 0.56031
|  | 19:03 | 23.3944 | 0.043552 | 0.56031
|  | 19:03 | 23.3956 | 0.058133 | 0.56031
|  | 19:03 | 23.3967 | 0.072714 | 0.56031
|  | 19:03 | 23.3978 | 0.058027 | 0.5603
|  | 19:03 | 23.3989 | 0.033585 | 0.5603
|  | 19:03 | 23.4 | 0.0091424 | 0.5603
|  | 19:03 | 23.4011 | -0.0069915 | 0.5603
|  | 19:04 | 23.4022 | -0.014817 | 0.56029
|  | 19:04 | 23.4033 | -0.013008 | 0.56029
|  | 19:04 | 23.4044 | -0.0079873 | 0.56029
|  | 19:04 | 23.4056 | -0.0032145 | 0.56029
|  | 19:04 | 23.4067 | 0.00081442 | 0.56028
|  | 19:04 | 23.4078 | 0.0048433 | 0.56028
|  | 19:04 | 23.4089 | -0.011699 | 0.56028
|  | 19:04 | 23.41 | -0.035099 | 0.56028
|  | 19:04 | 23.4111 | -0.062149 | 0.56028
|  | 19:04 | 23.4122 | -0.10015 | 0.56027
|  | 19:04 | 23.4133 | -0.13814 | 0.56027
|  | 19:04 | 23.4144 | -0.15922 | 0.56027
|  | 19:04 | 23.4156 | -0.17466 | 0.56027
|  | 19:04 | 23.4167 | -0.18651 | 0.56026
|  | 19:04 | 23.4178 | -0.18759 | 0.56026
|  | 19:05 | 23.4189 | -0.18868 | 0.56026
|  | 19:05 | 23.42 | -0.16432 | 0.56026
|  | 19:05 | 23.4211 | -0.13147 | 0.56025
|  | 19:05 | 23.4222 | -0.097254 | 0.56025
|  | 19:05 | 23.4233 | -0.058911 | 0.56025
|  | 19:05 | 23.4244 | -0.020569 | 0.56025
|  | 19:05 | 23.4256 | 0.017096 | 0.56025
|  | 19:05 | 23.4267 | 0.054534 | 0.56024
|  | 19:05 | 23.4278 | 0.085579 | 0.56024
|  | 19:05 | 23.4289 | 0.097447 | 0.56024
|  | 19:05 | 23.43 | 0.10931 | 0.56024
|  | 19:05 | 23.4311 | 0.11074 | 0.56023
|  | 19:05 | 23.4322 | 0.10868 | 0.56023
|  | 19:05 | 23.4333 | 0.10522 | 0.56023
|  | 19:05 | 23.4344 | 0.097578 | 0.56023
|  | 19:06 | 23.4356 | 0.089932 | 0.56022
|  | 19:06 | 23.4367 | 0.073569 | 0.56022
|  | 19:06 | 23.4378 | 0.048491 | 0.56022
|  | 19:06 | 23.4389 | 0.023412 | 0.56022
|  | 19:06 | 23.44 | 0.0095454 | 0.56022
|  | 19:06 | 23.4411 | -0.0043213 | 0.56021
|  | 19:06 | 23.4422 | -0.0022857 | 0.56021
|  | 19:06 | 23.4433 | 0.015652 | 0.56021
|  | 19:06 | 23.4444 | 0.03359 | 0.56021
|  | 19:06 | 23.4456 | 0.10038 | 0.5602
|  | 19:06 | 23.4467 | 0.16717 | 0.5602
|  | 19:06 | 23.4478 | 0.23184 | 0.5602
|  | 19:06 | 23.4489 | 0.29437 | 0.5602
|  | 19:06 | 23.45 | 0.35691 | 0.56019
|  | 19:06 | 23.4511 | 0.38203 | 0.56019
|  | 19:07 | 23.4522 | 0.40715 | 0.56019
|  | 19:07 | 23.4533 | 0.43669 | 0.56019
|  | 19:07 | 23.4544 | 0.47067 | 0.56019
|  | 19:07 | 23.4556 | 0.50464 | 0.56018
|  | 19:07 | 23.4567 | 0.51512 | 0.56018
|  | 19:07 | 23.4578 | 0.52559 | 0.56018
|  | 19:07 | 23.4589 | 0.54013 | 0.56018
|  | 19:07 | 23.46 | 0.55874 | 0.56017
|  | 19:07 | 23.4611 | 0.57735 | 0.56017
|  | 19:07 | 23.4622 | 0.57414 | 0.56017
|  | 19:07 | 23.4633 | 0.57092 | 0.56017
|  | 19:07 | 23.4644 | 0.57038 | 0.56016
|  | 19:07 | 23.4656 | 0.57251 | 0.56016
|  | 19:07 | 23.4667 | 0.57464 | 0.56016
|  | 19:07 | 23.4678 | 0.57446 | 0.56016
|  | 19:08 | 23.4689 | 0.57428 | 0.56016
|  | 19:08 | 23.47 | 0.56794 | 0.56015
|  | 19:08 | 23.4711 | 0.55544 | 0.56015
|  | 19:08 | 23.4722 | 0.54294 | 0.56015
|  | 19:08 | 23.4733 | 0.53362 | 0.56015
|  | 19:08 | 23.4744 | 0.52431 | 0.56014
|  | 19:08 | 23.4756 | 0.51346 | 0.56014
|  | 19:08 | 23.4767 | 0.50109 | 0.56014
|  | 19:08 | 23.4778 | 0.48871 | 0.56014
|  | 19:08 | 23.4789 | 0.46532 | 0.56013
|  | 19:08 | 23.48 | 0.44193 | 0.56013
|  | 19:08 | 23.4811 | 0.41736 | 0.56013
|  | 19:08 | 23.4822 | 0.39241 | 0.56013
|  | 19:08 | 23.4833 | 0.36745 | 0.56012
|  | 19:08 | 23.4844 | 0.32955 | 0.56012
|  | 19:09 | 23.4856 | 0.29165 | 0.56012
|  | 19:09 | 23.4867 | 0.25312 | 0.56012
|  | 19:09 | 23.4878 | 0.21396 | 0.56012
|  | 19:09 | 23.4889 | 0.1748 | 0.56011
|  | 19:09 | 23.49 | 0.11481 | 0.56011
|  | 19:09 | 23.4911 | 0.054818 | 0.56011
|  | 19:09 | 23.4922 | -0.0065868 | 0.56011
|  | 19:09 | 23.4933 | -0.068462 | 0.5601
|  | 19:09 | 23.4944 | -0.13034 | 0.5601
|  | 19:09 | 23.4956 | -0.17611 | 0.5601
|  | 19:09 | 23.4967 | -0.22189 | 0.5601
|  | 19:09 | 23.4978 | -0.26715 | 0.56009
|  | 19:09 | 23.4989 | -0.3119 | 0.56009
|  | 19:09 | 23.5 | -0.35665 | 0.56009
|  | 19:09 | 23.5011 | -0.39577 | 0.56009
|  | 19:10 | 23.5022 | -0.43489 | 0.56009
|  | 19:10 | 23.5033 | -0.45765 | 0.56008
|  | 19:10 | 23.5044 | -0.46406 | 0.56008
|  | 19:10 | 23.5056 | -0.47047 | 0.56008
|  | 19:10 | 23.5067 | -0.45239 | 0.56008
|  | 19:10 | 23.5078 | -0.4343 | 0.56007
|  | 19:10 | 23.5089 | -0.42879 | 0.56007
|  | 19:10 | 23.51 | -0.43588 | 0.56007
|  | 19:10 | 23.5111 | -0.44296 | 0.56007
|  | 19:10 | 23.5122 | -0.44646 | 0.56006
|  | 19:10 | 23.5133 | -0.44997 | 0.56006
|  | 19:10 | 23.5144 | -0.44712 | 0.56006
|  | 19:10 | 23.5156 | -0.43794 | 0.56006
|  | 19:10 | 23.5167 | -0.42875 | 0.56006
|  | 19:10 | 23.5178 | -0.42518 | 0.56005
|  | 19:11 | 23.5189 | -0.42161 | 0.56005
|  | 19:11 | 23.52 | -0.42556 | 0.56005
|  | 19:11 | 23.5211 | -0.43704 | 0.56005
|  | 19:11 | 23.5222 | -0.44852 | 0.56004
|  | 19:11 | 23.5233 | -0.44164 | 0.56004
|  | 19:11 | 23.5244 | -0.43475 | 0.56004
|  | 19:11 | 23.5256 | -0.42925 | 0.56004
|  | 19:11 | 23.5267 | -0.42513 | 0.56003
|  | 19:11 | 23.5278 | -0.421 | 0.56003
|  | 19:11 | 23.5289 | -0.40086 | 0.56003
|  | 19:11 | 23.53 | -0.38072 | 0.56003
|  | 19:11 | 23.5311 | -0.36457 | 0.56003
|  | 19:11 | 23.5322 | -0.35242 | 0.56002
|  | 19:11 | 23.5333 | -0.34187 | 0.56002
|  | 19:11 | 23.5344 | -0.33616 | 0.56002
|  | 19:12 | 23.5356 | -0.33044 | 0.56002
|  | 19:12 | 23.5367 | -0.31632 | 0.56001
|  | 19:12 | 23.5378 | -0.29381 | 0.56001
|  | 19:12 | 23.5389 | -0.2713 | 0.56001
|  | 19:12 | 23.54 | -0.25262 | 0.56001
|  | 19:12 | 23.5411 | -0.23394 | 0.56
|  | 19:12 | 23.5422 | -0.21066 | 0.56
|  | 19:12 | 23.5433 | -0.18278 | 0.56
|  | 19:12 | 23.5444 | -0.1549 | 0.56
|  | 19:12 | 23.5456 | -0.1598 | 0.56
|  | 19:12 | 23.5467 | -0.1647 | 0.55999
|  | 19:12 | 23.5478 | -0.16862 | 0.55999
|  | 19:12 | 23.5489 | -0.17156 | 0.55999
|  | 19:12 | 23.55 | -0.17451 | 0.55999
|  | 19:12 | 23.5511 | -0.16854 | 0.55998
|  | 19:13 | 23.5522 | -0.16258 | 0.55998
|  | 19:13 | 23.5533 | -0.16124 | 0.55998
|  | 19:13 | 23.5544 | -0.16454 | 0.55998
|  | 19:13 | 23.5556 | -0.16783 | 0.55997
|  | 19:13 | 23.5567 | -0.15843 | 0.55997
|  | 19:13 | 23.5578 | -0.14903 | 0.55997
|  | 19:13 | 23.5589 | -0.12965 | 0.55997
|  | 19:13 | 23.56 | -0.10029 | 0.55997
|  | 19:13 | 23.5611 | -0.070943 | 0.55996
|  | 19:13 | 23.5622 | -0.066805 | 0.55996
|  | 19:13 | 23.5633 | -0.062667 | 0.55996
|  | 19:13 | 23.5644 | -0.054492 | 0.55996
|  | 19:13 | 23.5656 | -0.042281 | 0.55995
|  | 19:13 | 23.5667 | -0.030069 | 0.55995
|  | 19:13 | 23.5678 | -0.017858 | 0.55995
|  | 19:14 | 23.5689 | 0.0074794 | 0.55995
|  | 19:14 | 23.57 | 0.030449 | 0.55994
|  | 19:14 | 23.5711 | 0.046317 | 0.55994
|  | 19:14 | 23.5722 | 0.062185 | 0.55994
|  | 19:14 | 23.5733 | 0.082672 | 0.55994
|  | 19:14 | 23.5744 | 0.10316 | 0.55994
|  | 19:14 | 23.5756 | 0.12318 | 0.55993
|  | 19:14 | 23.5767 | 0.14273 | 0.55993
|  | 19:14 | 23.5778 | 0.16229 | 0.55993
|  | 19:14 | 23.5789 | 0.17597 | 0.55993
|  | 19:14 | 23.58 | 0.18965 | 0.55992
|  | 19:14 | 23.5811 | 0.21106 | 0.55992
|  | 19:14 | 23.5822 | 0.24018 | 0.55992
|  | 19:14 | 23.5833 | 0.2693 | 0.55992
|  | 19:14 | 23.5844 | 0.28985 | 0.55991
|  | 19:15 | 23.5856 | 0.3104 | 0.55991
|  | 19:15 | 23.5867 | 0.32411 | 0.55991
|  | 19:15 | 23.5878 | 0.33098 | 0.55991
|  | 19:15 | 23.5889 | 0.33785 | 0.55991
|  | 19:15 | 23.59 | 0.3406 | 0.5599
|  | 19:15 | 23.5911 | 0.34335 | 0.5599
|  | 19:15 | 23.5922 | 0.34433 | 0.5599
|  | 19:15 | 23.5933 | 0.34356 | 0.5599
|  | 19:15 | 23.5944 | 0.34278 | 0.55989
|  | 19:15 | 23.5956 | 0.3594 | 0.55989
|  | 19:15 | 23.5967 | 0.37602 | 0.55989
|  | 19:15 | 23.5978 | 0.39263 | 0.55989
|  | 19:15 | 23.5989 | 0.40925 | 0.55988
|  | 19:15 | 23.6 | 0.42587 | 0.55988
|  | 19:15 | 23.6011 | 0.4182 | 0.55988
|  | 19:16 | 23.6022 | 0.41053 | 0.55988
|  | 19:16 | 23.6033 | 0.39842 | 0.55987
|  | 19:16 | 23.6044 | 0.38187 | 0.55987
|  | 19:16 | 23.6056 | 0.36532 | 0.55987
|  | 19:16 | 23.6067 | 0.33087 | 0.55987
|  | 19:16 | 23.6078 | 0.29642 | 0.55987
|  | 19:16 | 23.6089 | 0.28083 | 0.55986
|  | 19:16 | 23.61 | 0.28412 | 0.55986
|  | 19:16 | 23.6111 | 0.2874 | 0.55986
|  | 19:16 | 23.6122 | 0.2724 | 0.55986
|  | 19:16 | 23.6133 | 0.2574 | 0.55985
|  | 19:16 | 23.6144 | 0.2361 | 0.55985
|  | 19:16 | 23.6156 | 0.2085 | 0.55985
|  | 19:16 | 23.6167 | 0.18089 | 0.55985
|  | 19:16 | 23.6178 | 0.14929 | 0.55984
|  | 19:17 | 23.6189 | 0.11769 | 0.55984
|  | 19:17 | 23.62 | 0.10424 | 0.55984
|  | 19:17 | 23.6211 | 0.096831 | 0.55984
|  | 19:17 | 23.6222 | 0.089426 | 0.55984
|  | 19:17 | 23.6233 | 0.072852 | 0.55983
|  | 19:17 | 23.6244 | 0.056277 | 0.55983
|  | 19:17 | 23.6256 | 0.041294 | 0.55983
|  | 19:17 | 23.6267 | 0.027902 | 0.55983
|  | 19:17 | 23.6278 | 0.01451 | 0.55982
|  | 19:17 | 23.6289 | -0.0091688 | 0.55982
|  | 19:17 | 23.63 | -0.032848 | 0.55982
|  | 19:17 | 23.6311 | -0.066966 | 0.55982
|  | 19:17 | 23.6322 | -0.11152 | 0.55981
|  | 19:17 | 23.6333 | -0.15608 | 0.55981
|  | 19:17 | 23.6344 | -0.17782 | 0.55981
|  | 19:18 | 23.6356 | -0.19956 | 0.55981
|  | 19:18 | 23.6367 | -0.21505 | 0.55981
|  | 19:18 | 23.6378 | -0.2243 | 0.5598
|  | 19:18 | 23.6389 | -0.23485 | 0.5598
|  | 19:18 | 23.64 | -0.24933 | 0.5598
|  | 19:18 | 23.6411 | -0.26381 | 0.5598
|  | 19:18 | 23.6422 | -0.28585 | 0.55979
|  | 19:18 | 23.6433 | -0.31041 | 0.55979
|  | 19:18 | 23.6444 | -0.33498 | 0.55979
|  | 19:18 | 23.6456 | -0.35433 | 0.55979
|  | 19:18 | 23.6467 | -0.37369 | 0.55978
|  | 19:18 | 23.6478 | -0.38334 | 0.55978
|  | 19:18 | 23.6489 | -0.38329 | 0.55978
|  | 19:18 | 23.65 | -0.38325 | 0.55978
|  | 19:18 | 23.6511 | -0.37177 | 0.55978
|  | 19:19 | 23.6522 | -0.36028 | 0.55977
|  | 19:19 | 23.6533 | -0.34955 | 0.55977
|  | 19:19 | 23.6544 | -0.33956 | 0.55977
|  | 19:19 | 23.6556 | -0.32957 | 0.55977
|  | 19:19 | 23.6567 | -0.32282 | 0.55976
|  | 19:19 | 23.6578 | -0.31608 | 0.55976
|  | 19:19 | 23.6589 | -0.30933 | 0.55976
|  | 19:19 | 23.66 | -0.30258 | 0.55976
|  | 19:19 | 23.6611 | -0.2977 | 0.55975
|  | 19:19 | 23.6622 | -0.29843 | 0.55975
|  | 19:19 | 23.6633 | -0.29916 | 0.55975
|  | 19:19 | 23.6644 | -0.3059 | 0.55975
|  | 19:19 | 23.6656 | -0.31865 | 0.55975
|  | 19:19 | 23.6667 | -0.33141 | 0.55974
|  | 19:19 | 23.6678 | -0.34928 | 0.55974
|  | 19:20 | 23.6689 | -0.36715 | 0.55974
|  | 19:20 | 23.67 | -0.36743 | 0.55974
|  | 19:20 | 23.6711 | -0.35014 | 0.55973
|  | 19:20 | 23.6722 | -0.33284 | 0.55973
|  | 19:20 | 23.6733 | -0.32614 | 0.55973
|  | 19:20 | 23.6744 | -0.31945 | 0.55973
|  | 19:20 | 23.6756 | -0.32347 | 0.55972
|  | 19:20 | 23.6767 | -0.33105 | 0.55972
|  | 19:20 | 23.6778 | -0.33863 | 0.55972
|  | 19:20 | 23.6789 | -0.34742 | 0.55972
|  | 19:20 | 23.68 | -0.35621 | 0.55972
|  | 19:20 | 23.6811 | -0.35525 | 0.55971
|  | 19:20 | 23.6822 | -0.34453 | 0.55971
|  | 19:20 | 23.6833 | -0.33382 | 0.55971
|  | 19:20 | 23.6844 | -0.32408 | 0.55971
|  | 19:21 | 23.6856 | -0.31435 | 0.5597
|  | 19:21 | 23.6867 | -0.29629 | 0.5597
|  | 19:21 | 23.6878 | -0.2699 | 0.5597
|  | 19:21 | 23.6889 | -0.24351 | 0.5597
|  | 19:21 | 23.69 | -0.22981 | 0.55969
|  | 19:21 | 23.6911 | -0.21611 | 0.55969
|  | 19:21 | 23.6922 | -0.19988 | 0.55969
|  | 19:21 | 23.6933 | -0.18112 | 0.55969
|  | 19:21 | 23.6944 | -0.16235 | 0.55969
|  | 19:21 | 23.6956 | -0.16142 | 0.55968
|  | 19:21 | 23.6967 | -0.16049 | 0.55968
|  | 19:21 | 23.6978 | -0.15389 | 0.55968
|  | 19:21 | 23.6989 | -0.14164 | 0.55968
|  | 19:21 | 23.7 | -0.12939 | 0.55967
|  | 19:21 | 23.7011 | -0.12526 | 0.55967
|  | 19:22 | 23.7022 | -0.12113 | 0.55967
|  | 19:22 | 23.7033 | -0.12313 | 0.55967
|  | 19:22 | 23.7044 | -0.13125 | 0.55966
|  | 19:22 | 23.7056 | -0.13938 | 0.55966
|  | 19:22 | 23.7067 | -0.13197 | 0.55966
|  | 19:22 | 23.7078 | -0.12456 | 0.55966
|  | 19:22 | 23.7089 | -0.11274 | 0.55966
|  | 19:22 | 23.71 | -0.096521 | 0.55965
|  | 19:22 | 23.7111 | -0.080302 | 0.55965
|  | 19:22 | 23.7122 | -0.054155 | 0.55965
|  | 19:22 | 23.7133 | -0.028008 | 0.55965
|  | 19:22 | 23.7144 | -0.0045076 | 0.55964
|  | 19:22 | 23.7156 | 0.016347 | 0.55964
|  | 19:22 | 23.7167 | 0.037201 | 0.55964
|  | 19:22 | 23.7178 | 0.038561 | 0.55964
|  | 19:23 | 23.7189 | 0.039921 | 0.55963
|  | 19:23 | 23.72 | 0.04462 | 0.55963
|  | 19:23 | 23.7211 | 0.052657 | 0.55963
|  | 19:23 | 23.7222 | 0.060695 | 0.55963
|  | 19:23 | 23.7233 | 0.062016 | 0.55962
|  | 19:23 | 23.7244 | 0.063337 | 0.55962
|  | 19:23 | 23.7256 | 0.059152 | 0.55962
|  | 19:23 | 23.7267 | 0.049461 | 0.55962
|  | 19:23 | 23.7278 | 0.039771 | 0.55962
|  | 19:23 | 23.7289 | 0.03008 | 0.55961
|  | 19:23 | 23.73 | 0.02039 | 0.55961
|  | 19:23 | 23.7311 | 0.012533 | 0.55961
|  | 19:23 | 23.7322 | 0.00651 | 0.55961
|  | 19:23 | 23.7333 | 0.00048686 | 0.5596
|  | 19:23 | 23.7344 | -0.0055363 | 0.5596
|  | 19:24 | 23.7356 | -0.028667 | 0.5596
|  | 19:24 | 23.7367 | -0.055754 | 0.5596
|  | 19:24 | 23.7378 | -0.094714 | 0.55959
|  | 19:24 | 23.7389 | -0.13367 | 0.55959
|  | 19:24 | 23.74 | -0.1564 | 0.55959
|  | 19:24 | 23.7411 | -0.17912 | 0.55959
|  | 19:24 | 23.7422 | -0.20465 | 0.55959
|  | 19:24 | 23.7433 | -0.23296 | 0.55958
|  | 19:24 | 23.7444 | -0.26128 | 0.55958
|  | 19:24 | 23.7456 | -0.28713 | 0.55958
|  | 19:24 | 23.7467 | -0.31299 | 0.55958
|  | 19:24 | 23.7478 | -0.3269 | 0.55957
|  | 19:24 | 23.7489 | -0.32887 | 0.55957
|  | 19:24 | 23.75 | -0.33084 | 0.55957
|  | 19:24 | 23.7511 | -0.34417 | 0.55957
|  | 19:25 | 23.7522 | -0.35749 | 0.55956
|  | 19:25 | 23.7533 | -0.36829 | 0.55956
|  | 19:25 | 23.7544 | -0.37657 | 0.55956
|  | 19:25 | 23.7556 | -0.38484 | 0.55956
|  | 19:25 | 23.7567 | -0.39763 | 0.55956
|  | 19:25 | 23.7578 | -0.41043 | 0.55955
|  | 19:25 | 23.7589 | -0.42784 | 0.55955
|  | 19:25 | 23.76 | -0.44987 | 0.55955
|  | 19:25 | 23.7611 | -0.4719 | 0.55955
|  | 19:25 | 23.7622 | -0.49075 | 0.55954
|  | 19:25 | 23.7633 | -0.50959 | 0.55954
|  | 19:25 | 23.7644 | -0.5272 | 0.55954
|  | 19:25 | 23.7656 | -0.54355 | 0.55954
|  | 19:25 | 23.7667 | -0.5599 | 0.55953
|  | 19:25 | 23.7678 | -0.58263 | 0.55953
|  | 19:26 | 23.7689 | -0.60537 | 0.55953
|  | 19:26 | 23.77 | -0.62365 | 0.55953
|  | 19:26 | 23.7711 | -0.63747 | 0.55953
|  | 19:26 | 23.7722 | -0.65129 | 0.55952
|  | 19:26 | 23.7733 | -0.65879 | 0.55952
|  | 19:26 | 23.7744 | -0.66629 | 0.55952
|  | 19:26 | 23.7756 | -0.67986 | 0.55952
|  | 19:26 | 23.7767 | -0.6995 | 0.55951
|  | 19:26 | 23.7778 | -0.71913 | 0.55951
|  | 19:26 | 23.7789 | -0.73168 | 0.55951
|  | 19:26 | 23.78 | -0.74423 | 0.55951
|  | 19:26 | 23.7811 | -0.7505 | 0.5595
|  | 19:26 | 23.7822 | -0.75049 | 0.5595
|  | 19:26 | 23.7833 | -0.75048 | 0.5595
|  | 19:26 | 23.7844 | -0.73916 | 0.5595
|  | 19:27 | 23.7856 | -0.72783 | 0.5595
|  | 19:27 | 23.7867 | -0.70987 | 0.55949
|  | 19:27 | 23.7878 | -0.68526 | 0.55949
|  | 19:27 | 23.7889 | -0.66066 | 0.55949
|  | 19:27 | 23.79 | -0.6495 | 0.55949
|  | 19:27 | 23.7911 | -0.63834 | 0.55948
|  | 19:27 | 23.7922 | -0.61665 | 0.55948
|  | 19:27 | 23.7933 | -0.58443 | 0.55948
|  | 19:27 | 23.7944 | -0.55221 | 0.55948
|  | 19:27 | 23.7956 | -0.51541 | 0.55947
|  | 19:27 | 23.7967 | -0.47861 | 0.55947
|  | 19:27 | 23.7978 | -0.44523 | 0.55947
|  | 19:27 | 23.7989 | -0.41524 | 0.55947
|  | 19:27 | 23.8 | -0.38526 | 0.55947
|  | 19:27 | 23.8011 | -0.37899 | 0.55946
|  | 19:28 | 23.8022 | -0.37271 | 0.55946
|  | 19:28 | 23.8033 | -0.37159 | 0.55946
|  | 19:28 | 23.8044 | -0.37563 | 0.55946
|  | 19:28 | 23.8056 | -0.37966 | 0.55945
|  | 19:28 | 23.8067 | -0.36377 | 0.55945
|  | 19:28 | 23.8078 | -0.34788 | 0.55945
|  | 19:28 | 23.8089 | -0.32774 | 0.55945
|  | 19:28 | 23.81 | -0.30335 | 0.55944
|  | 19:28 | 23.8111 | -0.27896 | 0.55944
|  | 19:28 | 23.8122 | -0.25074 | 0.55944
|  | 19:28 | 23.8133 | -0.22252 | 0.55944
|  | 19:28 | 23.8144 | -0.19509 | 0.55944
|  | 19:28 | 23.8156 | -0.16792 | 0.55943
|  | 19:28 | 23.8167 | -0.14272 | 0.55943
|  | 19:28 | 23.8178 | -0.12345 | 0.55943
|  | 19:29 | 23.8189 | -0.10417 | 0.55943
|  | 19:29 | 23.82 | -0.087397 | 0.55942
|  | 19:29 | 23.8211 | -0.07313 | 0.55942
|  | 19:29 | 23.8222 | -0.058863 | 0.55942
|  | 19:29 | 23.8233 | -0.061269 | 0.55942
|  | 19:29 | 23.8244 | -0.063676 | 0.55941
|  | 19:29 | 23.8256 | -0.065522 | 0.55941
|  | 19:29 | 23.8267 | -0.066808 | 0.55941
|  | 19:29 | 23.8278 | -0.068094 | 0.55941
|  | 19:29 | 23.8289 | -0.075492 | 0.55941
|  | 19:29 | 23.83 | -0.08289 | 0.5594
|  | 19:29 | 23.8311 | -0.09073 | 0.5594
|  | 19:29 | 23.8322 | -0.099014 | 0.5594
|  | 19:29 | 23.8333 | -0.1073 | 0.5594
|  | 19:29 | 23.8344 | -0.089359 | 0.55939
|  | 19:30 | 23.8356 | -0.071421 | 0.55939
|  | 19:30 | 23.8367 | -0.049309 | 0.55939
|  | 19:30 | 23.8378 | -0.023023 | 0.55939
|  | 19:30 | 23.8389 | 0.0032623 | 0.55938
|  | 19:30 | 23.84 | 0.016532 | 0.55938
|  | 19:30 | 23.8411 | 0.029801 | 0.55938
|  | 19:30 | 23.8422 | 0.036497 | 0.55938
|  | 19:30 | 23.8433 | 0.03662 | 0.55937
|  | 19:30 | 23.8444 | 0.036742 | 0.55937
|  | 19:30 | 23.8456 | 0.031934 | 0.55937
|  | 19:30 | 23.8467 | 0.027126 | 0.55937
|  | 19:30 | 23.8478 | 0.038487 | 0.55937
|  | 19:30 | 23.8489 | 0.06602 | 0.55936
|  | 19:30 | 23.85 | 0.093552 | 0.55936
|  | 19:30 | 23.8511 | 0.12924 | 0.55936
|  | 19:31 | 23.8522 | 0.16492 | 0.55936
|  | 19:31 | 23.8533 | 0.19135 | 0.55935
|  | 19:31 | 23.8544 | 0.20853 | 0.55935
|  | 19:31 | 23.8556 | 0.2257 | 0.55935
|  | 19:31 | 23.8567 | 0.2251 | 0.55935
|  | 19:31 | 23.8578 | 0.22449 | 0.55934
|  | 19:31 | 23.8589 | 0.21902 | 0.55934
|  | 19:31 | 23.86 | 0.2087 | 0.55934
|  | 19:31 | 23.8611 | 0.19838 | 0.55934
|  | 19:31 | 23.8622 | 0.17104 | 0.55934
|  | 19:31 | 23.8633 | 0.14371 | 0.55933
|  | 19:31 | 23.8644 | 0.12041 | 0.55933
|  | 19:31 | 23.8656 | 0.10116 | 0.55933
|  | 19:31 | 23.8667 | 0.081902 | 0.55933
|  | 19:31 | 23.8678 | 0.099815 | 0.55932
|  | 19:32 | 23.8689 | 0.11773 | 0.55932
|  | 19:32 | 23.87 | 0.13342 | 0.55932
|  | 19:32 | 23.8711 | 0.14689 | 0.55932
|  | 19:32 | 23.8722 | 0.16036 | 0.55931
|  | 19:32 | 23.8733 | 0.17384 | 0.55931
|  | 19:32 | 23.8744 | 0.18731 | 0.55931
|  | 19:32 | 23.8756 | 0.20476 | 0.55931
|  | 19:32 | 23.8767 | 0.22619 | 0.55931
|  | 19:32 | 23.8778 | 0.24763 | 0.5593
|  | 19:32 | 23.8789 | 0.26643 | 0.5593
|  | 19:32 | 23.88 | 0.28523 | 0.5593
|  | 19:32 | 23.8811 | 0.29984 | 0.5593
|  | 19:32 | 23.8822 | 0.31025 | 0.55929
|  | 19:32 | 23.8833 | 0.32066 | 0.55929
|  | 19:32 | 23.8844 | 0.33434 | 0.55929
|  | 19:33 | 23.8856 | 0.34802 | 0.55929
|  | 19:33 | 23.8867 | 0.36502 | 0.55928
|  | 19:33 | 23.8878 | 0.38533 | 0.55928
|  | 19:33 | 23.8889 | 0.40565 | 0.55928
|  | 19:33 | 23.89 | 0.42159 | 0.55928
|  | 19:33 | 23.8911 | 0.43753 | 0.55928
|  | 19:33 | 23.8922 | 0.45058 | 0.55927
|  | 19:33 | 23.8933 | 0.46075 | 0.55927
|  | 19:33 | 23.8944 | 0.47091 | 0.55927
|  | 19:33 | 23.8956 | 0.47039 | 0.55927
|  | 19:33 | 23.8967 | 0.46987 | 0.55926
|  | 19:33 | 23.8978 | 0.46317 | 0.55926
|  | 19:33 | 23.8989 | 0.45441 | 0.55926
|  | 19:33 | 23.9 | 0.44565 | 0.55926
|  | 19:33 | 23.9011 | 0.42328 | 0.55925
|  | 19:34 | 23.9022 | 0.4009 | 0.55925
|  | 19:34 | 23.9033 | 0.38572 | 0.55925
|  | 19:34 | 23.9044 | 0.39211 | 0.55925
|  | 19:34 | 23.9056 | 0.3985 | 0.55925
|  | 19:34 | 23.9067 | 0.4237 | 0.55924
|  | 19:34 | 23.9078 | 0.4489 | 0.55924
|  | 19:34 | 23.9089 | 0.46088 | 0.55924
|  | 19:34 | 23.91 | 0.45964 | 0.55924
|  | 19:34 | 23.9111 | 0.45841 | 0.55923
|  | 19:34 | 23.9122 | 0.4475 | 0.55923
|  | 19:34 | 23.9133 | 0.43659 | 0.55923
|  | 19:34 | 23.9144 | 0.42325 | 0.55923
|  | 19:34 | 23.9156 | 0.40749 | 0.55922
|  | 19:34 | 23.9167 | 0.39172 | 0.55922
|  | 19:34 | 23.9178 | 0.40531 | 0.55922
|  | 19:35 | 23.9189 | 0.4189 | 0.55922
|  | 19:35 | 23.92 | 0.43151 | 0.55922
|  | 19:35 | 23.9211 | 0.44314 | 0.55921
|  | 19:35 | 23.9222 | 0.45477 | 0.55921
|  | 19:35 | 23.9233 | 0.4521 | 0.55921
|  | 19:35 | 23.9244 | 0.44943 | 0.55921
|  | 19:35 | 23.9256 | 0.43991 | 0.5592
|  | 19:35 | 23.9267 | 0.42354 | 0.5592
|  | 19:35 | 23.9278 | 0.40717 | 0.5592
|  | 19:35 | 23.9289 | 0.40518 | 0.5592
|  | 19:35 | 23.93 | 0.40319 | 0.55919
|  | 19:35 | 23.9311 | 0.41374 | 0.55919
|  | 19:35 | 23.9322 | 0.43682 | 0.55919
|  | 19:35 | 23.9333 | 0.45991 | 0.55919
|  | 19:35 | 23.9344 | 0.48429 | 0.55919
|  | 19:36 | 23.9356 | 0.50867 | 0.55918
|  | 19:36 | 23.9367 | 0.52763 | 0.55918
|  | 19:36 | 23.9378 | 0.54478 | 0.55918
|  | 19:36 | 23.9389 | 0.56194 | 0.55918
|  | 19:36 | 23.94 | 0.57207 | 0.55917
|  | 19:36 | 23.9411 | 0.58221 | 0.55917
|  | 19:36 | 23.9422 | 0.58718 | 0.55917
|  | 19:36 | 23.9433 | 0.58698 | 0.55917
|  | 19:36 | 23.9444 | 0.58678 | 0.55916
|  | 19:36 | 23.9456 | 0.60128 | 0.55916
|  | 19:36 | 23.9467 | 0.61578 | 0.55916
|  | 19:36 | 23.9478 | 0.62143 | 0.55916
|  | 19:36 | 23.9489 | 0.61825 | 0.55916
|  | 19:36 | 23.95 | 0.61506 | 0.55915
|  | 19:36 | 23.9511 | 0.62239 | 0.55915
|  | 19:37 | 23.9522 | 0.62971 | 0.55915
|  | 19:37 | 23.9533 | 0.63355 | 0.55915
|  | 19:37 | 23.9544 | 0.6339 | 0.55914
|  | 19:37 | 23.9556 | 0.63907 | 0.55914
|  | 19:37 | 23.9567 | 0.65868 | 0.55914
|  | 19:37 | 23.9578 | 0.6783 | 0.55914
|  | 19:37 | 23.9589 | 0.69792 | 0.55913
|  | 19:37 | 23.96 | 0.71754 | 0.55913
|  | 19:37 | 23.9611 | 0.73715 | 0.55913
|  | 19:37 | 23.9622 | 0.75945 | 0.55913
|  | 19:37 | 23.9633 | 0.78175 | 0.55912
|  | 19:37 | 23.9644 | 0.79371 | 0.55912
|  | 19:37 | 23.9656 | 0.79532 | 0.55912
|  | 19:37 | 23.9667 | 0.79693 | 0.55912
|  | 19:37 | 23.9678 | 0.81251 | 0.55912
|  | 19:38 | 23.9689 | 0.82809 | 0.55911
|  | 19:38 | 23.97 | 0.83863 | 0.55911
|  | 19:38 | 23.9711 | 0.84413 | 0.55911
|  | 19:38 | 23.9722 | 0.84963 | 0.55911
|  | 19:38 | 23.9733 | 0.82497 | 0.5591
|  | 19:38 | 23.9744 | 0.8003 | 0.5591
|  | 19:38 | 23.9756 | 0.77953 | 0.5591
|  | 19:38 | 23.9767 | 0.76265 | 0.5591
|  | 19:38 | 23.9778 | 0.74578 | 0.55909
|  | 19:38 | 23.9789 | 0.7289 | 0.55909
|  | 19:38 | 23.98 | 0.71203 | 0.55909
|  | 19:38 | 23.9811 | 0.69599 | 0.55909
|  | 19:38 | 23.9822 | 0.68079 | 0.55909
|  | 19:38 | 23.9833 | 0.66559 | 0.55908
|  | 19:38 | 23.9844 | 0.65039 | 0.55908
|  | 19:39 | 23.9856 | 0.63519 | 0.55908
|  | 19:39 | 23.9867 | 0.6287 | 0.55908
|  | 19:39 | 23.9878 | 0.62511 | 0.55907
|  | 19:39 | 23.9889 | 0.62152 | 0.55907
|  | 19:39 | 23.99 | 0.60905 | 0.55907
|  | 19:39 | 23.9911 | 0.59658 | 0.55907
|  | 19:39 | 23.9922 | 0.59451 | 0.55906
|  | 19:39 | 23.9933 | 0.60285 | 0.55906
|  | 19:39 | 23.9944 | 0.61119 | 0.55906
|  | 19:39 | 23.9956 | 0.62747 | 0.55906
|  | 19:39 | 23.9967 | 0.64374 | 0.55906
|  | 19:39 | 23.9978 | 0.64699 | 0.55905
|  | 19:39 | 23.9989 | 0.6372 | 0.55905
|  | 19:39 | 24 | 0.62494 | 0.55905
|  | 19:39 | 24.0011 | 0.60529 | 0.55905
|  | 19:40 | 24.0022 | 0.58564 | 0.55904
|  | 19:40 | 24.0033 | 0.56408 | 0.55904
|  | 19:40 | 24.0044 | 0.54061 | 0.55904
|  | 19:40 | 24.0056 | 0.51713 | 0.55904
|  | 19:40 | 24.0067 | 0.50205 | 0.55903
|  | 19:40 | 24.0078 | 0.48696 | 0.55903
|  | 19:40 | 24.0089 | 0.46771 | 0.55903
|  | 19:40 | 24.01 | 0.4443 | 0.55903
|  | 19:40 | 24.0111 | 0.4209 | 0.55903
|  | 19:40 | 24.0122 | 0.38558 | 0.55902
|  | 19:40 | 24.0133 | 0.35026 | 0.55902
|  | 19:40 | 24.0144 | 0.31233 | 0.55902
|  | 19:40 | 24.0156 | 0.27179 | 0.55902
|  | 19:40 | 24.0167 | 0.23124 | 0.55901
|  | 19:40 | 24.0178 | 0.20065 | 0.55901
|  | 19:41 | 24.0189 | 0.17005 | 0.55901
|  | 19:41 | 24.02 | 0.14077 | 0.55901
|  | 19:41 | 24.0211 | 0.11281 | 0.559
|  | 19:41 | 24.0222 | 0.084842 | 0.559
|  | 19:41 | 24.0233 | 0.038603 | 0.559
|  | 19:41 | 24.0244 | -0.0076366 | 0.559
|  | 19:41 | 24.0256 | -0.047739 | 0.559
|  | 19:41 | 24.0267 | -0.081703 | 0.55899
|  | 19:41 | 24.0278 | -0.11567 | 0.55899
|  | 19:41 | 24.0289 | -0.13646 | 0.55899
|  | 19:41 | 24.03 | -0.15725 | 0.55899
|  | 19:41 | 24.0311 | -0.18325 | 0.55898
|  | 19:41 | 24.0322 | -0.21444 | 0.55898
|  | 19:41 | 24.0333 | -0.24563 | 0.55898
|  | 19:41 | 24.0344 | -0.2745 | 0.55898
|  | 19:42 | 24.0356 | -0.30336 | 0.55897
|  | 19:42 | 24.0367 | -0.34175 | 0.55897
|  | 19:42 | 24.0378 | -0.38967 | 0.55897
|  | 19:42 | 24.0389 | -0.42638 | 0.55897
|  | 19:42 | 24.04 | -0.42948 | 0.55897
|  | 19:42 | 24.0411 | -0.43258 | 0.55896
|  | 19:42 | 24.0422 | -0.44921 | 0.55896
|  | 19:42 | 24.0433 | -0.47935 | 0.55896
|  | 19:42 | 24.0444 | -0.5095 | 0.55896
|  | 19:42 | 24.0456 | -0.53188 | 0.55895
|  | 19:42 | 24.0467 | -0.55427 | 0.55895
|  | 19:42 | 24.0478 | -0.57911 | 0.55895
|  | 19:42 | 24.0489 | -0.60641 | 0.55895
|  | 19:42 | 24.05 | -0.63371 | 0.55894
|  | 19:42 | 24.0511 | -0.64927 | 0.55894
|  | 19:43 | 24.0522 | -0.66484 | 0.55894
|  | 19:43 | 24.0533 | -0.6804 | 0.55894
|  | 19:43 | 24.0544 | -0.69596 | 0.55894
|  | 19:43 | 24.0556 | -0.71153 | 0.55893
|  | 19:43 | 24.0567 | -0.72418 | 0.55893
|  | 19:43 | 24.0578 | -0.73684 | 0.55893
|  | 19:43 | 24.0589 | -0.73522 | 0.55893
|  | 19:43 | 24.06 | -0.71932 | 0.55892
|  | 19:43 | 24.0611 | -0.70341 | 0.55892
|  | 19:43 | 24.0622 | -0.67074 | 0.55892
|  | 19:43 | 24.0633 | -0.63806 | 0.55892
|  | 19:43 | 24.0644 | -0.60994 | 0.55891
|  | 19:43 | 24.0656 | -0.58635 | 0.55891
|  | 19:43 | 24.0667 | -0.56277 | 0.55891
|  | 19:43 | 24.0678 | -0.53527 | 0.55891
|  | 19:44 | 24.0689 | -0.50776 | 0.55891
|  | 19:44 | 24.07 | -0.48763 | 0.5589
|  | 19:44 | 24.0711 | -0.48964 | 0.5589
|  | 19:44 | 24.0722 | -0.49165 | 0.5589
|  | 19:44 | 24.0733 | -0.49001 | 0.5589
|  | 19:44 | 24.0744 | -0.48837 | 0.55889
|  | 19:44 | 24.0756 | -0.48899 | 0.55889
|  | 19:44 | 24.0767 | -0.49188 | 0.55889
|  | 19:44 | 24.0778 | -0.49352 | 0.55889
|  | 19:44 | 24.0789 | -0.49142 | 0.55888
|  | 19:44 | 24.08 | -0.48932 | 0.55888
|  | 19:44 | 24.0811 | -0.49175 | 0.55888
|  | 19:44 | 24.0822 | -0.4987 | 0.55888
|  | 19:44 | 24.0833 | -0.50565 | 0.55887
|  | 19:44 | 24.0844 | -0.50288 | 0.55887
|  | 19:45 | 24.0856 | -0.50011 | 0.55887
|  | 19:45 | 24.0867 | -0.48826 | 0.55887
|  | 19:45 | 24.0878 | -0.46731 | 0.55887
|  | 19:45 | 24.0889 | -0.44636 | 0.55886
|  | 19:45 | 24.09 | -0.413 | 0.55886
|  | 19:45 | 24.0911 | -0.37965 | 0.55886
|  | 19:45 | 24.0922 | -0.35026 | 0.55886
|  | 19:45 | 24.0933 | -0.32485 | 0.55885
|  | 19:45 | 24.0944 | -0.29944 | 0.55885
|  | 19:45 | 24.0956 | -0.27642 | 0.55885
|  | 19:45 | 24.0967 | -0.2534 | 0.55885
|  | 19:45 | 24.0978 | -0.236 | 0.55884
|  | 19:45 | 24.0989 | -0.22421 | 0.55884
|  | 19:45 | 24.1 | -0.21242 | 0.55884
|  | 19:45 | 24.1011 | -0.18995 | 0.55884
|  | 19:46 | 24.1022 | -0.16749 | 0.55884
|  | 19:46 | 24.1033 | -0.14283 | 0.55883
|  | 19:46 | 24.1044 | -0.11597 | 0.55883
|  | 19:46 | 24.1056 | -0.089118 | 0.55883
|  | 19:46 | 24.1067 | -0.051508 | 0.55883
|  | 19:46 | 24.1078 | -0.013898 | 0.55882
|  | 19:46 | 24.1089 | 0.024607 | 0.55882
|  | 19:46 | 24.11 | 0.064006 | 0.55882
|  | 19:46 | 24.1111 | 0.1034 | 0.55882
|  | 19:46 | 24.1122 | 0.12872 | 0.55881
|  | 19:46 | 24.1133 | 0.15403 | 0.55881
|  | 19:46 | 24.1144 | 0.16833 | 0.55881
|  | 19:46 | 24.1156 | 0.17161 | 0.55881
|  | 19:46 | 24.1167 | 0.1749 | 0.55881
|  | 19:46 | 24.1178 | 0.19225 | 0.5588
|  | 19:47 | 24.1189 | 0.2096 | 0.5588
|  | 19:47 | 24.12 | 0.23125 | 0.5588
|  | 19:47 | 24.1211 | 0.25433 | 0.5588
|  | 19:47 | 24.1222 | 0.28118 | 0.55879
|  | 19:47 | 24.1233 | 0.3193 | 0.55879
|  | 19:47 | 24.1244 | 0.35742 | 0.55879
|  | 19:47 | 24.1256 | 0.37481 | 0.55879
|  | 19:47 | 24.1267 | 0.37146 | 0.55878
|  | 19:47 | 24.1278 | 0.36812 | 0.55878
|  | 19:47 | 24.1289 | 0.36814 | 0.55878
|  | 19:47 | 24.13 | 0.36817 | 0.55878
|  | 19:47 | 24.1311 | 0.36493 | 0.55878
|  | 19:47 | 24.1322 | 0.35842 | 0.55877
|  | 19:47 | 24.1333 | 0.35192 | 0.55877
|  | 19:47 | 24.1344 | 0.35745 | 0.55877
|  | 19:48 | 24.1356 | 0.36298 | 0.55877
|  | 19:48 | 24.1367 | 0.38439 | 0.55876
|  | 19:48 | 24.1378 | 0.42166 | 0.55876
|  | 19:48 | 24.1389 | 0.45893 | 0.55876
|  | 19:48 | 24.14 | 0.50834 | 0.55876
|  | 19:48 | 24.1411 | 0.55774 | 0.55875
|  | 19:48 | 24.1422 | 0.59714 | 0.55875
|  | 19:48 | 24.1433 | 0.62655 | 0.55875
|  | 19:48 | 24.1444 | 0.65595 | 0.55875
|  | 19:48 | 24.1456 | 0.68535 | 0.55875
|  | 19:48 | 24.1467 | 0.71475 | 0.55874
|  | 19:48 | 24.1478 | 0.7405 | 0.55874
|  | 19:48 | 24.1489 | 0.7626 | 0.55874
|  | 19:48 | 24.15 | 0.7847 | 0.55874
|  | 19:48 | 24.1511 | 0.78996 | 0.55873
|  | 19:49 | 24.1522 | 0.79522 | 0.55873
|  | 19:49 | 24.1533 | 0.80048 | 0.55873
|  | 19:49 | 24.1544 | 0.80574 | 0.55873
|  | 19:49 | 24.1556 | 0.811 | 0.55872
|  | 19:49 | 24.1567 | 0.80302 | 0.55872
|  | 19:49 | 24.1578 | 0.79504 | 0.55872
|  | 19:49 | 24.1589 | 0.78335 | 0.55872
|  | 19:49 | 24.16 | 0.76794 | 0.55872
|  | 19:49 | 24.1611 | 0.75254 | 0.55871
|  | 19:49 | 24.1622 | 0.73713 | 0.55871
|  | 19:49 | 24.1633 | 0.72173 | 0.55871
|  | 19:49 | 24.1644 | 0.70357 | 0.55871
|  | 19:49 | 24.1656 | 0.68266 | 0.5587
|  | 19:49 | 24.1667 | 0.66175 | 0.5587
|  | 19:49 | 24.1678 | 0.62242 | 0.5587
|  | 19:50 | 24.1689 | 0.58309 | 0.5587
|  | 19:50 | 24.17 | 0.54171 | 0.55869
|  | 19:50 | 24.1711 | 0.49829 | 0.55869
|  | 19:50 | 24.1722 | 0.45486 | 0.55869
|  | 19:50 | 24.1733 | 0.42925 | 0.55869
|  | 19:50 | 24.1744 | 0.40363 | 0.55869
|  | 19:50 | 24.1756 | 0.37379 | 0.55868
|  | 19:50 | 24.1767 | 0.33971 | 0.55868
|  | 19:50 | 24.1778 | 0.30564 | 0.55868
|  | 19:50 | 24.1789 | 0.27379 | 0.55868
|  | 19:50 | 24.18 | 0.24194 | 0.55867
|  | 19:50 | 24.1811 | 0.22435 | 0.55867
|  | 19:50 | 24.1822 | 0.22102 | 0.55867
|  | 19:50 | 24.1833 | 0.21769 | 0.55867
|  | 19:50 | 24.1844 | 0.20566 | 0.55866
|  | 19:51 | 24.1856 | 0.19362 | 0.55866
|  | 19:51 | 24.1867 | 0.18466 | 0.55866
|  | 19:51 | 24.1878 | 0.17879 | 0.55866
|  | 19:51 | 24.1889 | 0.17291 | 0.55866
|  | 19:51 | 24.19 | 0.16918 | 0.55865
|  | 19:51 | 24.1911 | 0.16545 | 0.55865
|  | 19:51 | 24.1922 | 0.15742 | 0.55865
|  | 19:51 | 24.1933 | 0.14511 | 0.55865
|  | 19:51 | 24.1944 | 0.13279 | 0.55864
|  | 19:51 | 24.1956 | 0.11944 | 0.55864
|  | 19:51 | 24.1967 | 0.10609 | 0.55864
|  | 19:51 | 24.1978 | 0.093734 | 0.55864
|  | 19:51 | 24.1989 | 0.082374 | 0.55863
|  | 19:51 | 24.2 | 0.071013 | 0.55863
|  | 19:51 | 24.2011 | 0.066403 | 0.55863
|  | 19:52 | 24.2022 | 0.061792 | 0.55863
|  | 19:52 | 24.2033 | 0.057755 | 0.55862
|  | 19:52 | 24.2044 | 0.05429 | 0.55862
|  | 19:52 | 24.2056 | 0.050825 | 0.55862
|  | 19:52 | 24.2067 | 0.032276 | 0.55862
|  | 19:52 | 24.2078 | 0.013726 | 0.55862
|  | 19:52 | 24.2089 | -0.0155 | 0.55861
|  | 19:52 | 24.21 | -0.055402 | 0.55861
|  | 19:52 | 24.2111 | -0.095305 | 0.55861
|  | 19:52 | 24.2122 | -0.1476 | 0.55861
|  | 19:52 | 24.2133 | -0.19989 | 0.5586
|  | 19:52 | 24.2144 | -0.25319 | 0.5586
|  | 19:52 | 24.2156 | -0.30752 | 0.5586
|  | 19:52 | 24.2167 | -0.36184 | 0.5586
|  | 19:52 | 24.2178 | -0.40614 | 0.55859
|  | 19:53 | 24.2189 | -0.45044 | 0.55859
|  | 19:53 | 24.22 | -0.48112 | 0.55859
|  | 19:53 | 24.2211 | -0.49819 | 0.55859
|  | 19:53 | 24.2222 | -0.51526 | 0.55859
|  | 19:53 | 24.2233 | -0.54146 | 0.55858
|  | 19:53 | 24.2244 | -0.56767 | 0.55858
|  | 19:53 | 24.2256 | -0.58665 | 0.55858
|  | 19:53 | 24.2267 | -0.59843 | 0.55858
|  | 19:53 | 24.2278 | -0.6102 | 0.55857
|  | 19:53 | 24.2289 | -0.60745 | 0.55857
|  | 19:53 | 24.23 | -0.6047 | 0.55857
|  | 19:53 | 24.2311 | -0.60347 | 0.55857
|  | 19:53 | 24.2322 | -0.60376 | 0.55856
|  | 19:53 | 24.2333 | -0.60405 | 0.55856
|  | 19:53 | 24.2344 | -0.60336 | 0.55856
|  | 19:54 | 24.2356 | -0.60266 | 0.55856
|  | 19:54 | 24.2367 | -0.60291 | 0.55856
|  | 19:54 | 24.2378 | -0.60599 | 0.55855
|  | 19:54 | 24.2389 | -0.60906 | 0.55855
|  | 19:54 | 24.24 | -0.61077 | 0.55855
|  | 19:54 | 24.2411 | -0.61248 | 0.55855
|  | 19:54 | 24.2422 | -0.6045 | 0.55854
|  | 19:54 | 24.2433 | -0.58685 | 0.55854
|  | 19:54 | 24.2444 | -0.56919 | 0.55854
|  | 19:54 | 24.2456 | -0.55636 | 0.55854
|  | 19:54 | 24.2467 | -0.54352 | 0.55853
|  | 19:54 | 24.2478 | -0.53564 | 0.55853
|  | 19:54 | 24.2489 | -0.53272 | 0.55853
|  | 19:54 | 24.25 | -0.5298 | 0.55853
|  | 19:54 | 24.2511 | -0.529 | 0.55853
|  | 19:55 | 24.2522 | -0.52819 | 0.55852
|  | 19:55 | 24.2533 | -0.53152 | 0.55852
|  | 19:55 | 24.2544 | -0.539 | 0.55852
|  | 19:55 | 24.2556 | -0.54647 | 0.55852
|  | 19:55 | 24.2567 | -0.54635 | 0.55851
|  | 19:55 | 24.2578 | -0.54623 | 0.55851
|  | 19:55 | 24.2589 | -0.54252 | 0.55851
|  | 19:55 | 24.26 | -0.53522 | 0.55851
|  | 19:55 | 24.2611 | -0.52791 | 0.5585
|  | 19:55 | 24.2622 | -0.51653 | 0.5585
|  | 19:55 | 24.2633 | -0.50516 | 0.5585
|  | 19:55 | 24.2644 | -0.47674 | 0.5585
|  | 19:55 | 24.2656 | -0.43128 | 0.5585
|  | 19:55 | 24.2667 | -0.38582 | 0.55849
|  | 19:55 | 24.2678 | -0.34134 | 0.55849
|  | 19:56 | 24.2689 | -0.29686 | 0.55849
|  | 19:56 | 24.27 | -0.25636 | 0.55849
|  | 19:56 | 24.2711 | -0.21982 | 0.55848
|  | 19:56 | 24.2722 | -0.18329 | 0.55848
|  | 19:56 | 24.2733 | -0.16697 | 0.55848
|  | 19:56 | 24.2744 | -0.15066 | 0.55848
|  | 19:56 | 24.2756 | -0.13059 | 0.55847
|  | 19:56 | 24.2767 | -0.10676 | 0.55847
|  | 19:56 | 24.2778 | -0.082929 | 0.55847
|  | 19:56 | 24.2789 | -0.064992 | 0.55847
|  | 19:56 | 24.28 | -0.047054 | 0.55847
|  | 19:56 | 24.2811 | -0.033677 | 0.55846
|  | 19:56 | 24.2822 | -0.024861 | 0.55846
|  | 19:56 | 24.2833 | -0.016045 | 0.55846
|  | 19:56 | 24.2844 | -0.015577 | 0.55846
|  | 19:57 | 24.2856 | -0.01511 | 0.55845
|  | 19:57 | 24.2867 | -0.032247 | 0.55845
|  | 19:57 | 24.2878 | -0.066986 | 0.55845
|  | 19:57 | 24.2889 | -0.10173 | 0.55845
|  | 19:57 | 24.29 | -0.11422 | 0.55844
|  | 19:57 | 24.2911 | -0.12672 | 0.55844
|  | 19:57 | 24.2922 | -0.14071 | 0.55844
|  | 19:57 | 24.2933 | -0.15619 | 0.55844
|  | 19:57 | 24.2944 | -0.17167 | 0.55844
|  | 19:57 | 24.2956 | -0.18715 | 0.55843
|  | 19:57 | 24.2967 | -0.20263 | 0.55843
|  | 19:57 | 24.2978 | -0.22463 | 0.55843
|  | 19:57 | 24.2989 | -0.25316 | 0.55843
|  | 19:57 | 24.3 | -0.28168 | 0.55842
|  | 19:57 | 24.3011 | -0.29777 | 0.55842
|  | 19:58 | 24.3022 | -0.31386 | 0.55842
|  | 19:58 | 24.3033 | -0.31394 | 0.55842
|  | 19:58 | 24.3044 | -0.298 | 0.55841
|  | 19:58 | 24.3056 | -0.28207 | 0.55841
|  | 19:58 | 24.3067 | -0.26097 | 0.55841
|  | 19:58 | 24.3078 | -0.23987 | 0.55841
|  | 19:58 | 24.3089 | -0.2201 | 0.55841
|  | 19:58 | 24.31 | -0.20168 | 0.5584
|  | 19:58 | 24.3111 | -0.18325 | 0.5584
|  | 19:58 | 24.3122 | -0.16685 | 0.5584
|  | 19:58 | 24.3133 | -0.15045 | 0.5584
|  | 19:58 | 24.3144 | -0.13497 | 0.55839
|  | 19:58 | 24.3156 | -0.1204 | 0.55839
|  | 19:58 | 24.3167 | -0.10583 | 0.55839
|  | 19:58 | 24.3178 | -0.085856 | 0.55839
|  | 19:59 | 24.3189 | -0.065882 | 0.55838
|  | 19:59 | 24.32 | -0.057483 | 0.55838
|  | 19:59 | 24.3211 | -0.060658 | 0.55838
|  | 19:59 | 24.3222 | -0.063833 | 0.55838
|  | 19:59 | 24.3233 | -0.042603 | 0.55837
|  | 19:59 | 24.3244 | -0.021374 | 0.55837
|  | 19:59 | 24.3256 | -0.0021204 | 0.55837
|  | 19:59 | 24.3267 | 0.015157 | 0.55837
|  | 19:59 | 24.3278 | 0.032435 | 0.55837
|  | 19:59 | 24.3289 | 0.024561 | 0.55836
|  | 19:59 | 24.33 | 0.016687 | 0.55836
|  | 19:59 | 24.3311 | 0.012389 | 0.55836
|  | 19:59 | 24.3322 | 0.011665 | 0.55836
|  | 19:59 | 24.3333 | 0.010942 | 0.55835
|  | 19:59 | 24.3344 | 0.002515 | 0.55835
|  | 20:00 | 24.3356 | -0.0059115 | 0.55835
|  | 20:00 | 24.3367 | -0.026255 | 0.55835
|  | 20:00 | 24.3378 | -0.058516 | 0.55834
|  | 20:00 | 24.3389 | -0.090777 | 0.55834
|  | 20:00 | 24.34 | -0.1219 | 0.55834
|  | 20:00 | 24.3411 | -0.15302 | 0.55834
|  | 20:00 | 24.3422 | -0.18289 | 0.55834
|  | 20:00 | 24.3433 | -0.14425 | 0.55833
|  | 20:00 | 24.3444 | -0.12965 | 0.55833
|  | 20:00 | 24.3456 | -0.13601 | 0.55833
|  | 20:00 | 24.3467 | -0.14238 | 0.55833
|  | 20:00 | 24.3478 | -0.14874 | 0.55832
|  | 20:00 | 24.3489 | -0.15511 | 0.55832
|  | 20:00 | 24.35 | -0.16147 | 0.55832
|  | 20:00 | 24.3511 | -0.15001 | 0.55832
|  | 20:01 | 24.3522 | -0.13855 | 0.55831
|  | 20:01 | 24.3533 | -0.11353 | 0.55831
|  | 20:01 | 24.3544 | -0.083978 | 0.55831
|  | 20:01 | 24.3556 | -0.05443 | 0.55831
|  | 20:01 | 24.3567 | -0.032121 | 0.55831
|  | 20:01 | 24.3578 | -0.0098121 | 0.5583
|  | 20:01 | 24.3589 | 0.0050135 | 0.5583
|  | 20:01 | 24.36 | 0.012356 | 0.5583
|  | 20:01 | 24.3611 | 0.019698 | 0.5583
|  | 20:01 | 24.3622 | 0.0056427 | 0.55829
|  | 20:01 | 24.3633 | -0.0084124 | 0.55829
|  | 20:01 | 24.3644 | -0.016135 | 0.55829
|  | 20:01 | 24.3656 | -0.017526 | 0.55829
|  | 20:01 | 24.3667 | -0.018917 | 0.55828
|  | 20:01 | 24.3678 | -0.0074832 | 0.55828
|  | 20:02 | 24.3689 | 0.0039504 | 0.55828
|  | 20:02 | 24.37 | 0.016937 | 0.55828
|  | 20:02 | 24.3711 | 0.030441 | 0.55828
|  | 20:02 | 24.3722 | 0.043946 | 0.55827
|  | 20:02 | 24.3733 | 0.065859 | 0.55827
|  | 20:02 | 24.3744 | 0.087772 | 0.55827
|  | 20:02 | 24.3756 | 0.10268 | 0.55827
|  | 20:02 | 24.3767 | 0.11526 | 0.55826
|  | 20:02 | 24.3778 | 0.12783 | 0.55826
|  | 20:02 | 24.3789 | 0.13629 | 0.55826
|  | 20:02 | 24.38 | 0.14474 | 0.55826
|  | 20:02 | 24.3811 | 0.1681 | 0.55825
|  | 20:02 | 24.3822 | 0.20635 | 0.55825
|  | 20:02 | 24.3833 | 0.2446 | 0.55825
|  | 20:02 | 24.3844 | 0.28614 | 0.55825
|  | 20:03 | 24.3856 | 0.32769 | 0.55825
|  | 20:03 | 24.3867 | 0.37177 | 0.55824
|  | 20:03 | 24.3878 | 0.41839 | 0.55824
|  | 20:03 | 24.3889 | 0.4646 | 0.55824
|  | 20:03 | 24.39 | 0.50955 | 0.55824
|  | 20:03 | 24.3911 | 0.55451 | 0.55823
|  | 20:03 | 24.3922 | 0.60292 | 0.55823
|  | 20:03 | 24.3933 | 0.65481 | 0.55823
|  | 20:03 | 24.3944 | 0.70669 | 0.55823
|  | 20:03 | 24.3956 | 0.72091 | 0.55822
|  | 20:03 | 24.3967 | 0.73513 | 0.55822
|  | 20:03 | 24.3978 | 0.73769 | 0.55822
|  | 20:03 | 24.3989 | 0.7286 | 0.55822
|  | 20:03 | 24.4 | 0.71951 | 0.55822
|  | 20:03 | 24.4011 | 0.69733 | 0.55821
|  | 20:04 | 24.4022 | 0.66208 | 0.55821
|  | 20:04 | 24.4033 | 0.6161 | 0.55821
|  | 20:04 | 24.4044 | 0.5594 | 0.55821
|  | 20:04 | 24.4056 | 0.50271 | 0.5582
|  | 20:04 | 24.4067 | 0.43484 | 0.5582
|  | 20:04 | 24.4078 | 0.36696 | 0.5582
|  | 20:04 | 24.4089 | 0.2997 | 0.5582
|  | 20:04 | 24.41 | 0.23306 | 0.55819
|  | 20:04 | 24.4111 | 0.16641 | 0.55819
|  | 20:04 | 24.4122 | 0.1269 | 0.55819
|  | 20:04 | 24.4133 | 0.087393 | 0.55819
|  | 20:04 | 24.4144 | 0.062752 | 0.55819
|  | 20:04 | 24.4156 | 0.052981 | 0.55818
|  | 20:04 | 24.4167 | 0.04321 | 0.55818
|  | 20:04 | 24.4178 | 0.031374 | 0.55818
|  | 20:05 | 24.4189 | 0.019538 | 0.55818
|  | 20:05 | 24.42 | 0.0014623 | 0.55817
|  | 20:05 | 24.4211 | -0.022852 | 0.55817
|  | 20:05 | 24.4222 | -0.047167 | 0.55817
|  | 20:05 | 24.4233 | -0.057435 | 0.55817
|  | 20:05 | 24.4244 | -0.067703 | 0.55816
|  | 20:05 | 24.4256 | -0.080728 | 0.55816
|  | 20:05 | 24.4267 | -0.096511 | 0.55816
|  | 20:05 | 24.4278 | -0.11229 | 0.55816
|  | 20:05 | 24.4289 | -0.14181 | 0.55816
|  | 20:05 | 24.43 | -0.17133 | 0.55815
|  | 20:05 | 24.4311 | -0.19213 | 0.55815
|  | 20:05 | 24.4322 | -0.21003 | 0.55815
|  | 20:05 | 24.4333 | -0.22794 | 0.55815
|  | 20:05 | 24.4344 | -0.25217 | 0.55814
|  | 20:06 | 24.4356 | -0.2764 | 0.55814
|  | 20:06 | 24.4367 | -0.29614 | 0.55814
|  | 20:06 | 24.4378 | -0.31141 | 0.55814
|  | 20:06 | 24.4389 | -0.32668 | 0.55813
|  | 20:06 | 24.44 | -0.33634 | 0.55813
|  | 20:06 | 24.4411 | -0.346 | 0.55813
|  | 20:06 | 24.4422 | -0.35417 | 0.55813
|  | 20:06 | 24.4433 | -0.36184 | 0.55812
|  | 20:06 | 24.4444 | -0.3695 | 0.55812
|  | 20:06 | 24.4456 | -0.38223 | 0.55812
|  | 20:06 | 24.4467 | -0.39495 | 0.55812
|  | 20:06 | 24.4478 | -0.41366 | 0.55812
|  | 20:06 | 24.4489 | -0.43836 | 0.55811
|  | 20:06 | 24.45 | -0.46307 | 0.55811
|  | 20:06 | 24.4511 | -0.49142 | 0.55811
|  | 20:07 | 24.4522 | -0.51976 | 0.55811
|  | 20:07 | 24.4533 | -0.53557 | 0.5581
|  | 20:07 | 24.4544 | -0.53885 | 0.5581
|  | 20:07 | 24.4556 | -0.54212 | 0.5581
|  | 20:07 | 24.4567 | -0.52588 | 0.5581
|  | 20:07 | 24.4578 | -0.50964 | 0.55809
|  | 20:07 | 24.4589 | -0.48512 | 0.55809
|  | 20:07 | 24.46 | -0.45232 | 0.55809
|  | 20:07 | 24.4611 | -0.41952 | 0.55809
|  | 20:07 | 24.4622 | -0.39896 | 0.55809
|  | 20:07 | 24.4633 | -0.3784 | 0.55808
|  | 20:07 | 24.4644 | -0.36069 | 0.55808
|  | 20:07 | 24.4656 | -0.34581 | 0.55808
|  | 20:07 | 24.4667 | -0.33094 | 0.55808
|  | 20:07 | 24.4678 | -0.31151 | 0.55807
|  | 20:08 | 24.4689 | -0.29208 | 0.55807
|  | 20:08 | 24.47 | -0.26401 | 0.55807
|  | 20:08 | 24.4711 | -0.2273 | 0.55807
|  | 20:08 | 24.4722 | -0.1906 | 0.55806
|  | 20:08 | 24.4733 | -0.15165 | 0.55806
|  | 20:08 | 24.4744 | -0.1127 | 0.55806
|  | 20:08 | 24.4756 | -0.070709 | 0.55806
|  | 20:08 | 24.4767 | -0.025681 | 0.55806
|  | 20:08 | 24.4778 | 0.019348 | 0.55805
|  | 20:08 | 24.4789 | 0.066808 | 0.55805
|  | 20:08 | 24.48 | 0.11427 | 0.55805
|  | 20:08 | 24.4811 | 0.14906 | 0.55805
|  | 20:08 | 24.4822 | 0.17962 | 0.55804
|  | 20:08 | 24.4833 | 0.21018 | 0.55804
|  | 20:08 | 24.4844 | 0.22659 | 0.55804
|  | 20:09 | 24.4856 | 0.243 | 0.55804
|  | 20:09 | 24.4867 | 0.26015 | 0.55803
|  | 20:09 | 24.4878 | 0.27804 | 0.55803
|  | 20:09 | 24.4889 | 0.29593 | 0.55803
|  | 20:09 | 24.49 | 0.34579 | 0.55803
|  | 20:09 | 24.4911 | 0.39566 | 0.55803
|  | 20:09 | 24.4922 | 0.41648 | 0.55802
|  | 20:09 | 24.4933 | 0.42761 | 0.55802
|  | 20:09 | 24.4944 | 0.43875 | 0.55802
|  | 20:09 | 24.4956 | 0.48488 | 0.55802
|  | 20:09 | 24.4967 | 0.53101 | 0.55801
|  | 20:09 | 24.4978 | 0.56431 | 0.55801
|  | 20:09 | 24.4989 | 0.58479 | 0.55801
|  | 20:09 | 24.5 | 0.60527 | 0.55801
|  | 20:09 | 24.5011 | 0.62576 | 0.558
|  | 20:10 | 24.5022 | 0.64624 | 0.558
|  | 20:10 | 24.5033 | 0.65386 | 0.558
|  | 20:10 | 24.5044 | 0.64862 | 0.558
|  | 20:10 | 24.5056 | 0.64337 | 0.558
|  | 20:10 | 24.5067 | 0.61858 | 0.55799
|  | 20:10 | 24.5078 | 0.59379 | 0.55799
|  | 20:10 | 24.5089 | 0.57945 | 0.55799
|  | 20:10 | 24.51 | 0.5686 | 0.55799
|  | 20:10 | 24.5111 | 0.55774 | 0.55798
|  | 20:10 | 24.5122 | 0.53406 | 0.55798
|  | 20:10 | 24.5133 | 0.51037 | 0.55798
|  | 20:10 | 24.5144 | 0.48484 | 0.55798
|  | 20:10 | 24.5156 | 0.45747 | 0.55797
|  | 20:10 | 24.5167 | 0.43009 | 0.55797
|  | 20:10 | 24.5178 | 0.40661 | 0.55797
|  | 20:11 | 24.5189 | 0.38313 | 0.55797
|  | 20:11 | 24.52 | 0.35578 | 0.55797
|  | 20:11 | 24.5211 | 0.32455 | 0.55796
|  | 20:11 | 24.5222 | 0.29332 | 0.55796
|  | 20:11 | 24.5233 | 0.24981 | 0.55796
|  | 20:11 | 24.5244 | 0.20629 | 0.55796
|  | 20:11 | 24.5256 | 0.16355 | 0.55795
|  | 20:11 | 24.5267 | 0.12106 | 0.55795
|  | 20:11 | 24.5278 | 0.078582 | 0.55795
|  | 20:11 | 24.5289 | 0.031632 | 0.55795
|  | 20:11 | 24.53 | -0.015318 | 0.55794
|  | 20:11 | 24.5311 | -0.035845 | 0.55794
|  | 20:11 | 24.5322 | -0.047565 | 0.55794
|  | 20:11 | 24.5333 | -0.059285 | 0.55794
|  | 20:11 | 24.5344 | -0.081598 | 0.55794
|  | 20:12 | 24.5356 | -0.10391 | 0.55793
|  | 20:12 | 24.5367 | -0.13323 | 0.55793
|  | 20:12 | 24.5378 | -0.16956 | 0.55793
|  | 20:12 | 24.5389 | -0.20588 | 0.55793
|  | 20:12 | 24.54 | -0.24997 | 0.55792
|  | 20:12 | 24.5411 | -0.29406 | 0.55792
|  | 20:12 | 24.5422 | -0.33234 | 0.55792
|  | 20:12 | 24.5433 | -0.3648 | 0.55792
|  | 20:12 | 24.5444 | -0.39726 | 0.55791
|  | 20:12 | 24.5456 | -0.42357 | 0.55791
|  | 20:12 | 24.5467 | -0.44987 | 0.55791
|  | 20:12 | 24.5478 | -0.46847 | 0.55791
|  | 20:12 | 24.5489 | -0.47935 | 0.55791
|  | 20:12 | 24.55 | -0.49023 | 0.5579
|  | 20:12 | 24.5511 | -0.5088 | 0.5579
|  | 20:13 | 24.5522 | -0.52738 | 0.5579
|  | 20:13 | 24.5533 | -0.54595 | 0.5579
|  | 20:13 | 24.5544 | -0.56452 | 0.55789
|  | 20:13 | 24.5556 | -0.58056 | 0.55789
|  | 20:13 | 24.5567 | -0.58899 | 0.55789
|  | 20:13 | 24.5578 | -0.59741 | 0.55789
|  | 20:13 | 24.5589 | -0.60464 | 0.55788
|  | 20:13 | 24.56 | -0.61068 | 0.55788
|  | 20:13 | 24.5611 | -0.61671 | 0.55788
|  | 20:13 | 24.5622 | -0.62274 | 0.55788
|  | 20:13 | 24.5633 | -0.62878 | 0.55787
|  | 20:13 | 24.5644 | -0.64556 | 0.55787
|  | 20:13 | 24.5656 | -0.67309 | 0.55787
|  | 20:13 | 24.5667 | -0.70062 | 0.55787
|  | 20:13 | 24.5678 | -0.7259 | 0.55787
|  | 20:14 | 24.5689 | -0.75118 | 0.55786
|  | 20:14 | 24.57 | -0.76373 | 0.55786
|  | 20:14 | 24.5711 | -0.76355 | 0.55786
|  | 20:14 | 24.5722 | -0.76336 | 0.55786
|  | 20:14 | 24.5733 | -0.74165 | 0.55785
|  | 20:14 | 24.5744 | -0.71995 | 0.55785
|  | 20:14 | 24.5756 | -0.69328 | 0.55785
|  | 20:14 | 24.5767 | -0.66166 | 0.55785
|  | 20:14 | 24.5778 | -0.63004 | 0.55784
|  | 20:14 | 24.5789 | -0.60123 | 0.55784
|  | 20:14 | 24.58 | -0.57243 | 0.55784
|  | 20:14 | 24.5811 | -0.55891 | 0.55784
|  | 20:14 | 24.5822 | -0.56068 | 0.55784
|  | 20:14 | 24.5833 | -0.56245 | 0.55783
|  | 20:14 | 24.5844 | -0.54412 | 0.55783
|  | 20:15 | 24.5856 | -0.52578 | 0.55783
|  | 20:15 | 24.5867 | -0.51626 | 0.55783
|  | 20:15 | 24.5878 | -0.51554 | 0.55782
|  | 20:15 | 24.5889 | -0.51483 | 0.55782
|  | 20:15 | 24.59 | -0.51658 | 0.55782
|  | 20:15 | 24.5911 | -0.51832 | 0.55782
|  | 20:15 | 24.5922 | -0.51742 | 0.55781
|  | 20:15 | 24.5933 | -0.51387 | 0.55781
|  | 20:15 | 24.5944 | -0.51032 | 0.55781
|  | 20:15 | 24.5956 | -0.49265 | 0.55781
|  | 20:15 | 24.5967 | -0.47497 | 0.55781
|  | 20:15 | 24.5978 | -0.4573 | 0.5578
|  | 20:15 | 24.5989 | -0.43963 | 0.5578
|  | 20:15 | 24.6 | -0.42195 | 0.5578
|  | 20:15 | 24.6011 | -0.40033 | 0.5578
|  | 20:16 | 24.6022 | -0.3787 | 0.55779
|  | 20:16 | 24.6033 | -0.35755 | 0.55779
|  | 20:16 | 24.6044 | -0.33687 | 0.55779
|  | 20:16 | 24.6056 | -0.31619 | 0.55779
|  | 20:16 | 24.6067 | -0.27026 | 0.55778
|  | 20:16 | 24.6078 | -0.22432 | 0.55778
|  | 20:16 | 24.6089 | -0.18079 | 0.55778
|  | 20:16 | 24.61 | -0.13806 | 0.55778
|  | 20:16 | 24.6111 | -0.095326 | 0.55778
|  | 20:16 | 24.6122 | -0.056057 | 0.55777
|  | 20:16 | 24.6133 | -0.016788 | 0.55777
|  | 20:16 | 24.6144 | 0.015659 | 0.55777
|  | 20:16 | 24.6156 | 0.041284 | 0.55777
|  | 20:16 | 24.6167 | 0.066908 | 0.55776
|  | 20:16 | 24.6178 | 0.067889 | 0.55776
|  | 20:17 | 24.6189 | 0.06887 | 0.55776
|  | 20:17 | 24.62 | 0.077604 | 0.55776
|  | 20:17 | 24.6211 | 0.094089 | 0.55775
|  | 20:17 | 24.6222 | 0.11057 | 0.55775
|  | 20:17 | 24.6233 | 0.13697 | 0.55775
|  | 20:17 | 24.6244 | 0.16337 | 0.55775
|  | 20:17 | 24.6256 | 0.18555 | 0.55775
|  | 20:17 | 24.6267 | 0.2035 | 0.55774
|  | 20:17 | 24.6278 | 0.22146 | 0.55774
|  | 20:17 | 24.6289 | 0.25483 | 0.55774
|  | 20:17 | 24.63 | 0.2882 | 0.55774
|  | 20:17 | 24.6311 | 0.30837 | 0.55773
|  | 20:17 | 24.6322 | 0.31533 | 0.55773
|  | 20:17 | 24.6333 | 0.32229 | 0.55773
|  | 20:17 | 24.6344 | 0.34371 | 0.55773
|  | 20:18 | 24.6356 | 0.36513 | 0.55772
|  | 20:18 | 24.6367 | 0.39495 | 0.55772
|  | 20:18 | 24.6378 | 0.43316 | 0.55772
|  | 20:18 | 24.6389 | 0.47137 | 0.55772
|  | 20:18 | 24.64 | 0.50421 | 0.55772
|  | 20:18 | 24.6411 | 0.53705 | 0.55771
|  | 20:18 | 24.6422 | 0.56677 | 0.55771
|  | 20:18 | 24.6433 | 0.59337 | 0.55771
|  | 20:18 | 24.6444 | 0.61996 | 0.55771
|  | 20:18 | 24.6456 | 0.63533 | 0.5577
|  | 20:18 | 24.6467 | 0.6507 | 0.5577
|  | 20:18 | 24.6478 | 0.67478 | 0.5577
|  | 20:18 | 24.6489 | 0.70756 | 0.5577
|  | 20:18 | 24.65 | 0.74033 | 0.55769
|  | 20:18 | 24.6511 | 0.7188 | 0.55769
|  | 20:19 | 24.6522 | 0.69726 | 0.55769
|  | 20:19 | 24.6533 | 0.69924 | 0.55769
|  | 20:19 | 24.6544 | 0.72473 | 0.55769
|  | 20:19 | 24.6556 | 0.75023 | 0.55768
|  | 20:19 | 24.6567 | 0.75876 | 0.55768
|  | 20:19 | 24.6578 | 0.76729 | 0.55768
|  | 20:19 | 24.6589 | 0.77299 | 0.55768
|  | 20:19 | 24.66 | 0.77774 | 0.55767
|  | 20:19 | 24.6611 | 0.7825 | 0.55767
|  | 20:19 | 24.6622 | 0.76741 | 0.55767
|  | 20:19 | 24.6633 | 0.75232 | 0.55767
|  | 20:19 | 24.6644 | 0.7296 | 0.55766
|  | 20:19 | 24.6656 | 0.69925 | 0.55766
|  | 20:19 | 24.6667 | 0.6689 | 0.55766
|  | 20:19 | 24.6678 | 0.62576 | 0.55766
|  | 20:20 | 24.6689 | 0.58261 | 0.55766
|  | 20:20 | 24.67 | 0.54949 | 0.55765
|  | 20:20 | 24.6711 | 0.5264 | 0.55765
|  | 20:20 | 24.6722 | 0.50331 | 0.55765
|  | 20:20 | 24.6733 | 0.4765 | 0.55765
|  | 20:20 | 24.6744 | 0.44968 | 0.55764
|  | 20:20 | 24.6756 | 0.4167 | 0.55764
|  | 20:20 | 24.6767 | 0.37755 | 0.55764
|  | 20:20 | 24.6778 | 0.33841 | 0.55764
|  | 20:20 | 24.6789 | 0.29386 | 0.55763
|  | 20:20 | 24.68 | 0.24932 | 0.55763
|  | 20:20 | 24.6811 | 0.21533 | 0.55763
|  | 20:20 | 24.6822 | 0.19189 | 0.55763
|  | 20:20 | 24.6833 | 0.16844 | 0.55762
|  | 20:20 | 24.6844 | 0.16499 | 0.55762
|  | 20:21 | 24.6856 | 0.16153 | 0.55762
|  | 20:21 | 24.6867 | 0.15986 | 0.55762
|  | 20:21 | 24.6878 | 0.15996 | 0.55762
|  | 20:21 | 24.6889 | 0.16005 | 0.55761
|  | 20:21 | 24.69 | 0.14796 | 0.55761
|  | 20:21 | 24.6911 | 0.13587 | 0.55761
|  | 20:21 | 24.6922 | 0.12378 | 0.55761
|  | 20:21 | 24.6933 | 0.1117 | 0.5576
|  | 20:21 | 24.6944 | 0.099605 | 0.5576
|  | 20:21 | 24.6956 | 0.079349 | 0.5576
|  | 20:21 | 24.6967 | 0.059092 | 0.5576
|  | 20:21 | 24.6978 | 0.042185 | 0.55759
|  | 20:21 | 24.6989 | 0.028626 | 0.55759
|  | 20:21 | 24.7 | 0.015067 | 0.55759
|  | 20:21 | 24.7011 | 0.017848 | 0.55759
|  | 20:22 | 24.7022 | 0.020629 | 0.55759
|  | 20:22 | 24.7033 | 0.02341 | 0.55758
|  | 20:22 | 24.7044 | 0.02619 | 0.55758
|  | 20:22 | 24.7056 | 0.028971 | 0.55758
|  | 20:22 | 24.7067 | 0.040168 | 0.55758
|  | 20:22 | 24.7078 | 0.051364 | 0.55757
|  | 20:22 | 24.7089 | 0.060832 | 0.55757
|  | 20:22 | 24.71 | 0.068571 | 0.55757
|  | 20:22 | 24.7111 | 0.076309 | 0.55757
|  | 20:22 | 24.7122 | 0.077437 | 0.55756
|  | 20:22 | 24.7133 | 0.078564 | 0.55756
|  | 20:22 | 24.7144 | 0.080322 | 0.55756
|  | 20:22 | 24.7156 | 0.082711 | 0.55756
|  | 20:22 | 24.7167 | 0.085099 | 0.55756
|  | 20:22 | 24.7178 | 0.082506 | 0.55755
|  | 20:23 | 24.7189 | 0.079913 | 0.55755
|  | 20:23 | 24.72 | 0.07732 | 0.55755
|  | 20:23 | 24.7211 | 0.074727 | 0.55755
|  | 20:23 | 24.7222 | 0.072134 | 0.55754
|  | 20:23 | 24.7233 | 0.05751 | 0.55754
|  | 20:23 | 24.7244 | 0.042887 | 0.55754
|  | 20:23 | 24.7256 | 0.041184 | 0.55754
|  | 20:23 | 24.7267 | 0.052402 | 0.55753
|  | 20:23 | 24.7278 | 0.063621 | 0.55753
|  | 20:23 | 24.7289 | 0.059618 | 0.55753
|  | 20:23 | 24.73 | 0.055615 | 0.55753
|  | 20:23 | 24.7311 | 0.053782 | 0.55753
|  | 20:23 | 24.7322 | 0.054119 | 0.55752
|  | 20:23 | 24.7333 | 0.054456 | 0.55752
|  | 20:23 | 24.7344 | 0.052728 | 0.55752
|  | 20:24 | 24.7356 | 0.051 | 0.55752
|  | 20:24 | 24.7367 | 0.053232 | 0.55751
|  | 20:24 | 24.7378 | 0.059425 | 0.55751
|  | 20:24 | 24.7389 | 0.065617 | 0.55751
|  | 20:24 | 24.74 | 0.089973 | 0.55751
|  | 20:24 | 24.7411 | 0.11433 | 0.5575
|  | 20:24 | 24.7422 | 0.13104 | 0.5575
|  | 20:24 | 24.7433 | 0.14009 | 0.5575
|  | 20:24 | 24.7444 | 0.14915 | 0.5575
|  | 20:24 | 24.7456 | 0.14294 | 0.5575
|  | 20:24 | 24.7467 | 0.13674 | 0.55749
|  | 20:24 | 24.7478 | 0.13903 | 0.55749
|  | 20:24 | 24.7489 | 0.14981 | 0.55749
|  | 20:24 | 24.75 | 0.16059 | 0.55749
|  | 20:24 | 24.7511 | 0.17604 | 0.55748
|  | 20:25 | 24.7522 | 0.1915 | 0.55748
|  | 20:25 | 24.7533 | 0.20614 | 0.55748
|  | 20:25 | 24.7544 | 0.21996 | 0.55748
|  | 20:25 | 24.7556 | 0.23378 | 0.55747
|  | 20:25 | 24.7567 | 0.22649 | 0.55747
|  | 20:25 | 24.7578 | 0.2192 | 0.55747
|  | 20:25 | 24.7589 | 0.2103 | 0.55747
|  | 20:25 | 24.76 | 0.1998 | 0.55747
|  | 20:25 | 24.7611 | 0.18929 | 0.55746
|  | 20:25 | 24.7622 | 0.16969 | 0.55746
|  | 20:25 | 24.7633 | 0.15009 | 0.55746
|  | 20:25 | 24.7644 | 0.12595 | 0.55746
|  | 20:25 | 24.7656 | 0.09729 | 0.55745
|  | 20:25 | 24.7667 | 0.068625 | 0.55745
|  | 20:25 | 24.7678 | 0.07361 | 0.55745
|  | 20:26 | 24.7689 | 0.078594 | 0.55745
|  | 20:26 | 24.77 | 0.072993 | 0.55744
|  | 20:26 | 24.7711 | 0.056805 | 0.55744
|  | 20:26 | 24.7722 | 0.040617 | 0.55744
|  | 20:26 | 24.7733 | 0.014632 | 0.55744
|  | 20:26 | 24.7744 | -0.011353 | 0.55744
|  | 20:26 | 24.7756 | -0.035552 | 0.55743
|  | 20:26 | 24.7767 | -0.057963 | 0.55743
|  | 20:26 | 24.7778 | -0.080375 | 0.55743
|  | 20:26 | 24.7789 | -0.065543 | 0.55743
|  | 20:26 | 24.78 | -0.050712 | 0.55742
|  | 20:26 | 24.7811 | -0.031837 | 0.55742
|  | 20:26 | 24.7822 | -0.0089175 | 0.55742
|  | 20:26 | 24.7833 | 0.014002 | 0.55742
|  | 20:26 | 24.7844 | 0.0028253 | 0.55741
|  | 20:27 | 24.7856 | -0.0083511 | 0.55741
|  | 20:27 | 24.7867 | -0.022928 | 0.55741
|  | 20:27 | 24.7878 | -0.040906 | 0.55741
|  | 20:27 | 24.7889 | -0.058884 | 0.55741
|  | 20:27 | 24.79 | -0.068746 | 0.5574
|  | 20:27 | 24.7911 | -0.078609 | 0.5574
|  | 20:27 | 24.7922 | -0.07932 | 0.5574
|  | 20:27 | 24.7933 | -0.076982 | 0.5574
|  | 20:27 | 24.7944 | -0.074643 | 0.55739
|  | 20:27 | 24.7956 | -0.075455 | 0.55739
|  | 20:27 | 24.7967 | -0.076267 | 0.55739
|  | 20:27 | 24.7978 | -0.073963 | 0.55739
|  | 20:27 | 24.7989 | -0.07062 | 0.55738
|  | 20:27 | 24.8 | -0.067277 | 0.55738
|  | 20:27 | 24.8011 | -0.087801 | 0.55738
|  | 20:28 | 24.8022 | -0.10832 | 0.55738
|  | 20:28 | 24.8033 | -0.11242 | 0.55737
|  | 20:28 | 24.8044 | -0.10009 | 0.55737
|  | 20:28 | 24.8056 | -0.087763 | 0.55737
|  | 20:28 | 24.8067 | -0.068639 | 0.55737
|  | 20:28 | 24.8078 | -0.049516 | 0.55737
|  | 20:28 | 24.8089 | -0.015747 | 0.55736
|  | 20:28 | 24.81 | 0.032669 | 0.55736
|  | 20:28 | 24.8111 | 0.076313 | 0.55736
|  | 20:28 | 24.8122 | 0.10565 | 0.55736
|  | 20:28 | 24.8133 | 0.13498 | 0.55735
|  | 20:28 | 24.8144 | 0.14996 | 0.55735
|  | 20:28 | 24.8156 | 0.1506 | 0.55735
|  | 20:28 | 24.8167 | 0.15123 | 0.55735
|  | 20:28 | 24.8178 | 0.15947 | 0.55734
|  | 20:29 | 24.8189 | 0.1677 | 0.55734
|  | 20:29 | 24.82 | 0.16361 | 0.55734
|  | 20:29 | 24.8211 | 0.14719 | 0.55734
|  | 20:29 | 24.8222 | 0.13078 | 0.55734
|  | 20:29 | 24.8233 | 0.11437 | 0.55733
|  | 20:29 | 24.8244 | 0.097961 | 0.55733
|  | 20:29 | 24.8256 | 0.077558 | 0.55733
|  | 20:29 | 24.8267 | 0.055824 | 0.55733
|  | 20:29 | 24.8278 | 0.034089 | 0.55732
|  | 20:29 | 24.8289 | 0.018564 | 0.55732
|  | 20:29 | 24.83 | 0.0030393 | 0.55732
|  | 20:29 | 24.8311 | -0.016027 | 0.55732
|  | 20:29 | 24.8322 | -0.038635 | 0.55731
|  | 20:29 | 24.8333 | -0.061243 | 0.55731
|  | 20:29 | 24.8344 | -0.068344 | 0.55731
|  | 20:30 | 24.8356 | -0.075445 | 0.55731
|  | 20:30 | 24.8367 | -0.080764 | 0.55731
|  | 20:30 | 24.8378 | -0.0843 | 0.5573
|  | 20:30 | 24.8389 | -0.087836 | 0.5573
|  | 20:30 | 24.84 | -0.08516 | 0.5573
|  | 20:30 | 24.8411 | -0.082483 | 0.5573
|  | 20:30 | 24.8422 | -0.079807 | 0.55729
|  | 20:30 | 24.8433 | -0.07713 | 0.55729
|  | 20:30 | 24.8444 | -0.074454 | 0.55729
|  | 20:30 | 24.8456 | -0.076025 | 0.55729
|  | 20:30 | 24.8467 | -0.077597 | 0.55728
|  | 20:30 | 24.8478 | -0.085439 | 0.55728
|  | 20:30 | 24.8489 | -0.09955 | 0.55728
|  | 20:30 | 24.85 | -0.11366 | 0.55728
|  | 20:30 | 24.8511 | -0.11441 | 0.55728
|  | 20:31 | 24.8522 | -0.11516 | 0.55727
|  | 20:31 | 24.8533 | -0.10971 | 0.55727
|  | 20:31 | 24.8544 | -0.09806 | 0.55727
|  | 20:31 | 24.8556 | -0.084509 | 0.55727
|  | 20:31 | 24.8567 | -0.065244 | 0.55726
|  | 20:31 | 24.8578 | -0.045979 | 0.55726
|  | 20:31 | 24.8589 | -0.029559 | 0.55726
|  | 20:31 | 24.86 | -0.015984 | 0.55726
|  | 20:31 | 24.8611 | -0.0024094 | 0.55725
|  | 20:31 | 24.8622 | 0.022238 | 0.55725
|  | 20:31 | 24.8633 | 0.046885 | 0.55725
|  | 20:31 | 24.8644 | 0.074314 | 0.55725
|  | 20:31 | 24.8656 | 0.10453 | 0.55725
|  | 20:31 | 24.8667 | 0.13474 | 0.55724
|  | 20:31 | 24.8678 | 0.15843 | 0.55724
|  | 20:32 | 24.8689 | 0.18212 | 0.55724
|  | 20:32 | 24.87 | 0.20365 | 0.55724
|  | 20:32 | 24.8711 | 0.22304 | 0.55723
|  | 20:32 | 24.8722 | 0.24243 | 0.55723
|  | 20:32 | 24.8733 | 0.2467 | 0.55723
|  | 20:32 | 24.8744 | 0.25097 | 0.55723
|  | 20:32 | 24.8756 | 0.25524 | 0.55722
|  | 20:32 | 24.8767 | 0.25952 | 0.55722
|  | 20:32 | 24.8778 | 0.26379 | 0.55722
|  | 20:32 | 24.8789 | 0.26806 | 0.55722
|  | 20:32 | 24.88 | 0.27234 | 0.55722
|  | 20:32 | 24.8811 | 0.27055 | 0.55721
|  | 20:32 | 24.8822 | 0.26272 | 0.55721
|  | 20:32 | 24.8833 | 0.25488 | 0.55721
|  | 20:32 | 24.8844 | 0.23498 | 0.55721
|  | 20:33 | 24.8856 | 0.21507 | 0.5572
|  | 20:33 | 24.8867 | 0.20228 | 0.5572
|  | 20:33 | 24.8878 | 0.1966 | 0.5572
|  | 20:33 | 24.8889 | 0.19092 | 0.5572
|  | 20:33 | 24.89 | 0.17374 | 0.55719
|  | 20:33 | 24.8911 | 0.15656 | 0.55719
|  | 20:33 | 24.8922 | 0.14737 | 0.55719
|  | 20:33 | 24.8933 | 0.14617 | 0.55719
|  | 20:33 | 24.8944 | 0.14096 | 0.55719
|  | 20:33 | 24.8956 | 0.1237 | 0.55718
|  | 20:33 | 24.8967 | 0.10644 | 0.55718
|  | 20:33 | 24.8978 | 0.091813 | 0.55718
|  | 20:33 | 24.8989 | 0.079822 | 0.55718
|  | 20:33 | 24.9 | 0.067831 | 0.55717
|  | 20:33 | 24.9011 | 0.075896 | 0.55717
|  | 20:34 | 24.9022 | 0.083961 | 0.55717
|  | 20:34 | 24.9033 | 0.086463 | 0.55717
|  | 20:34 | 24.9044 | 0.083403 | 0.55716
|  | 20:34 | 24.9056 | 0.080342 | 0.55716
|  | 20:34 | 24.9067 | 0.086139 | 0.55716
|  | 20:34 | 24.9078 | 0.091936 | 0.55716
|  | 20:34 | 24.9089 | 0.086932 | 0.55716
|  | 20:34 | 24.91 | 0.071129 | 0.55715
|  | 20:34 | 24.9111 | 0.055325 | 0.55715
|  | 20:34 | 24.9122 | 0.058039 | 0.55715
|  | 20:34 | 24.9133 | 0.060754 | 0.55715
|  | 20:34 | 24.9144 | 0.053289 | 0.55714
|  | 20:34 | 24.9156 | 0.035644 | 0.55714
|  | 20:34 | 24.9167 | 0.018 | 0.55714
|  | 20:34 | 24.9178 | -0.013065 | 0.55714
|  | 20:35 | 24.9189 | -0.04413 | 0.55713
|  | 20:35 | 24.92 | -0.070275 | 0.55713
|  | 20:35 | 24.9211 | -0.091499 | 0.55713
|  | 20:35 | 24.9222 | -0.11272 | 0.55713
|  | 20:35 | 24.9233 | -0.1153 | 0.55712
|  | 20:35 | 24.9244 | -0.11788 | 0.55712
|  | 20:35 | 24.9256 | -0.11783 | 0.55712
|  | 20:35 | 24.9267 | -0.11514 | 0.55712
|  | 20:35 | 24.9278 | -0.11272 | 0.55712
|  | 20:35 | 24.9289 | -0.11108 | 0.55711
|  | 20:35 | 24.93 | -0.10944 | 0.55711
|  | 20:35 | 24.9311 | -0.1078 | 0.55711
|  | 20:35 | 24.9322 | -0.12031 | 0.55711
|  | 20:35 | 24.9333 | -0.13283 | 0.5571
|  | 20:35 | 24.9344 | -0.13556 | 0.5571
|  | 20:36 | 24.9356 | -0.1383 | 0.5571
|  | 20:36 | 24.9367 | -0.13564 | 0.5571
|  | 20:36 | 24.9378 | -0.13119 | 0.55709
|  | 20:36 | 24.9389 | -0.1251 | 0.55709
|  | 20:36 | 24.94 | -0.11411 | 0.55709
|  | 20:36 | 24.9411 | -0.10312 | 0.55709
|  | 20:36 | 24.9422 | -0.087127 | 0.55709
|  | 20:36 | 24.9433 | -0.06947 | 0.55708
|  | 20:36 | 24.9444 | -0.057029 | 0.55708
|  | 20:36 | 24.9456 | -0.060235 | 0.55708
|  | 20:36 | 24.9467 | -0.06344 | 0.55708
|  | 20:36 | 24.9478 | -0.059529 | 0.55707
|  | 20:36 | 24.9489 | -0.053247 | 0.55707
|  | 20:36 | 24.95 | -0.048412 | 0.55707
|  | 20:36 | 24.9511 | -0.047923 | 0.55707
|  | 20:37 | 24.9522 | -0.047434 | 0.55706
|  | 20:37 | 24.9533 | -0.052124 | 0.55706
|  | 20:37 | 24.9544 | -0.05854 | 0.55706
|  | 20:37 | 24.9556 | -0.068618 | 0.55706
|  | 20:37 | 24.9567 | -0.08968 | 0.55706
|  | 20:37 | 24.9578 | -0.11074 | 0.55705
|  | 20:37 | 24.9589 | -0.12803 | 0.55705
|  | 20:37 | 24.96 | -0.14405 | 0.55705
|  | 20:37 | 24.9611 | -0.15587 | 0.55705
|  | 20:37 | 24.9622 | -0.15507 | 0.55704
|  | 20:37 | 24.9633 | -0.15427 | 0.55704
|  | 20:37 | 24.9644 | -0.1689 | 0.55704
|  | 20:37 | 24.9656 | -0.18867 | 0.55704
|  | 20:37 | 24.9667 | -0.19879 | 0.55703
|  | 20:37 | 24.9678 | -0.17995 | 0.55703
|  | 20:38 | 24.9689 | -0.16112 | 0.55703
|  | 20:38 | 24.97 | -0.14042 | 0.55703
|  | 20:38 | 24.9711 | -0.1191 | 0.55703
|  | 20:38 | 24.9722 | -0.087246 | 0.55702
|  | 20:38 | 24.9733 | -0.023777 | 0.55702
|  | 20:38 | 24.9744 | 0.039692 | 0.55702
|  | 20:38 | 24.9756 | 0.084628 | 0.55702
|  | 20:38 | 24.9767 | 0.12956 | 0.55701
|  | 20:38 | 24.9778 | 0.17372 | 0.55701
|  | 20:38 | 24.9789 | 0.21556 | 0.55701
|  | 20:38 | 24.98 | 0.2574 | 0.55701
|  | 20:38 | 24.9811 | 0.26371 | 0.557
|  | 20:38 | 24.9822 | 0.25818 | 0.557
|  | 20:38 | 24.9833 | 0.25264 | 0.557
|  | 20:38 | 24.9844 | 0.24711 | 0.557
|  | 20:39 | 24.9856 | 0.24157 | 0.557
|  | 20:39 | 24.9867 | 0.24404 | 0.55699
|  | 20:39 | 24.9878 | 0.24918 | 0.55699
|  | 20:39 | 24.9889 | 0.25653 | 0.55699
|  | 20:39 | 24.99 | 0.27053 | 0.55699
|  | 20:39 | 24.9911 | 0.28454 | 0.55698
|  | 20:39 | 24.9922 | 0.28643 | 0.55698
|  | 20:39 | 24.9933 | 0.28428 | 0.55698
|  | 20:39 | 24.9944 | 0.28637 | 0.55698
|  | 20:39 | 24.9956 | 0.30114 | 0.55697
|  | 20:39 | 24.9967 | 0.31592 | 0.55697
|  | 20:39 | 24.9978 | 0.32289 | 0.55697
|  | 20:39 | 24.9989 | 0.32726 | 0.55697
|  | 20:39 | 25 | 0.32399 | 0.55697
|  | 20:39 | 25.0011 | 0.3131 | 0.55696
|  | 20:40 | 25.0022 | 0.3022 | 0.55696
|  | 20:40 | 25.0033 | 0.28574 | 0.55696
|  | 20:40 | 25.0044 | 0.26742 | 0.55696
|  | 20:40 | 25.0056 | 0.24996 | 0.55695
|  | 20:40 | 25.0067 | 0.23337 | 0.55695
|  | 20:40 | 25.0078 | 0.21678 | 0.55695
|  | 20:40 | 25.0089 | 0.18735 | 0.55695
|  | 20:40 | 25.01 | 0.15364 | 0.55694
|  | 20:40 | 25.0111 | 0.13899 | 0.55694
|  | 20:40 | 25.0122 | 0.1434 | 0.55694
|  | 20:40 | 25.0133 | 0.1478 | 0.55694
|  | 20:40 | 25.0144 | 0.16101 | 0.55694
|  | 20:40 | 25.0156 | 0.17715 | 0.55693
|  | 20:40 | 25.0167 | 0.1784 | 0.55693
|  | 20:40 | 25.0178 | 0.16474 | 0.55693
|  | 20:41 | 25.0189 | 0.15109 | 0.55693
|  | 20:41 | 25.02 | 0.12306 | 0.55692
|  | 20:41 | 25.0211 | 0.090241 | 0.55692
|  | 20:41 | 25.0222 | 0.056587 | 0.55692
|  | 20:41 | 25.0233 | 0.020429 | 0.55692
|  | 20:41 | 25.0244 | -0.015729 | 0.55691
|  | 20:41 | 25.0256 | -0.042232 | 0.55691
|  | 20:41 | 25.0267 | -0.065516 | 0.55691
|  | 20:41 | 25.0278 | -0.087599 | 0.55691
|  | 20:41 | 25.0289 | -0.10608 | 0.55691
|  | 20:41 | 25.03 | -0.12456 | 0.5569
|  | 20:41 | 25.0311 | -0.13921 | 0.5569
|  | 20:41 | 25.0322 | -0.15259 | 0.5569
|  | 20:41 | 25.0333 | -0.16354 | 0.5569
|  | 20:41 | 25.0344 | -0.16719 | 0.55689
|  | 20:42 | 25.0356 | -0.17083 | 0.55689
|  | 20:42 | 25.0367 | -0.19514 | 0.55689
|  | 20:42 | 25.0378 | -0.22632 | 0.55689
|  | 20:42 | 25.0389 | -0.24783 | 0.55688
|  | 20:42 | 25.04 | -0.24028 | 0.55688
|  | 20:42 | 25.0411 | -0.23273 | 0.55688
|  | 20:42 | 25.0422 | -0.22091 | 0.55688
|  | 20:42 | 25.0433 | -0.20767 | 0.55687
|  | 20:42 | 25.0444 | -0.19169 | 0.55687
|  | 20:42 | 25.0456 | -0.1675 | 0.55687
|  | 20:42 | 25.0467 | -0.14331 | 0.55687
|  | 20:42 | 25.0478 | -0.12658 | 0.55687
|  | 20:42 | 25.0489 | -0.11235 | 0.55686
|  | 20:42 | 25.05 | -0.099041 | 0.55686
|  | 20:42 | 25.0511 | -0.088485 | 0.55686
|  | 20:43 | 25.0522 | -0.077929 | 0.55686
|  | 20:43 | 25.0533 | -0.06405 | 0.55685
|  | 20:43 | 25.0544 | -0.049063 | 0.55685
|  | 20:43 | 25.0556 | -0.032325 | 0.55685
|  | 20:43 | 25.0567 | -0.01033 | 0.55685
|  | 20:43 | 25.0578 | 0.011664 | 0.55684
|  | 20:43 | 25.0589 | 0.025807 | 0.55684
|  | 20:43 | 25.06 | 0.037333 | 0.55684
|  | 20:43 | 25.0611 | 0.049144 | 0.55684
|  | 20:43 | 25.0622 | 0.06181 | 0.55684
|  | 20:43 | 25.0633 | 0.074475 | 0.55683
|  | 20:43 | 25.0644 | 0.088406 | 0.55683
|  | 20:43 | 25.0656 | 0.10276 | 0.55683
|  | 20:43 | 25.0667 | 0.11637 | 0.55683
|  | 20:43 | 25.0678 | 0.12776 | 0.55682
|  | 20:44 | 25.0689 | 0.13916 | 0.55682
|  | 20:44 | 25.07 | 0.15333 | 0.55682
|  | 20:44 | 25.0711 | 0.16843 | 0.55682
|  | 20:44 | 25.0722 | 0.18226 | 0.55681
|  | 20:44 | 25.0733 | 0.19228 | 0.55681
|  | 20:44 | 25.0744 | 0.20229 | 0.55681
|  | 20:44 | 25.0756 | 0.18703 | 0.55681
|  | 20:44 | 25.0767 | 0.17176 | 0.55681
|  | 20:44 | 25.0778 | 0.15361 | 0.5568
|  | 20:44 | 25.0789 | 0.12677 | 0.5568
|  | 20:44 | 25.08 | 0.099932 | 0.5568
|  | 20:44 | 25.0811 | 0.080254 | 0.5568
|  | 20:44 | 25.0822 | 0.062962 | 0.55679
|  | 20:44 | 25.0833 | 0.049071 | 0.55679
|  | 20:44 | 25.0844 | 0.045383 | 0.55679
|  | 20:45 | 25.0856 | 0.041695 | 0.55679
|  | 20:45 | 25.0867 | 0.032198 | 0.55678
|  | 20:45 | 25.0878 | 0.020765 | 0.55678
|  | 20:45 | 25.0889 | 0.010218 | 0.55678
|  | 20:45 | 25.09 | 0.0023298 | 0.55678
|  | 20:45 | 25.0911 | -0.0055582 | 0.55678
|  | 20:45 | 25.0922 | -0.023576 | 0.55677
|  | 20:45 | 25.0933 | -0.04497 | 0.55677
|  | 20:45 | 25.0944 | -0.063236 | 0.55677
|  | 20:45 | 25.0956 | -0.072119 | 0.55677
|  | 20:45 | 25.0967 | -0.081002 | 0.55676
|  | 20:45 | 25.0978 | -0.091497 | 0.55676
|  | 20:45 | 25.0989 | -0.10253 | 0.55676
|  | 20:45 | 25.1 | -0.11184 | 0.55676
|  | 20:45 | 25.1011 | -0.11599 | 0.55675
|  | 20:46 | 25.1022 | -0.12014 | 0.55675
|  | 20:46 | 25.1033 | -0.12608 | 0.55675
|  | 20:46 | 25.1044 | -0.13383 | 0.55675
|  | 20:46 | 25.1056 | -0.14157 | 0.55675
|  | 20:46 | 25.1067 | -0.14002 | 0.55674
|  | 20:46 | 25.1078 | -0.13847 | 0.55674
|  | 20:46 | 25.1089 | -0.14396 | 0.55674
|  | 20:46 | 25.11 | -0.1565 | 0.55674
|  | 20:46 | 25.1111 | -0.16904 | 0.55673
|  | 20:46 | 25.1122 | -0.18405 | 0.55673
|  | 20:46 | 25.1133 | -0.19905 | 0.55673
|  | 20:46 | 25.1144 | -0.20539 | 0.55673
|  | 20:46 | 25.1156 | -0.20306 | 0.55672
|  | 20:46 | 25.1167 | -0.20073 | 0.55672
|  | 20:46 | 25.1178 | -0.17283 | 0.55672
|  | 20:47 | 25.1189 | -0.14493 | 0.55672
|  | 20:47 | 25.12 | -0.1155 | 0.55672
|  | 20:47 | 25.1211 | -0.084542 | 0.55671
|  | 20:47 | 25.1222 | -0.053583 | 0.55671
|  | 20:47 | 25.1233 | -0.01823 | 0.55671
|  | 20:47 | 25.1244 | 0.017124 | 0.55671
|  | 20:47 | 25.1256 | 0.042132 | 0.5567
|  | 20:47 | 25.1267 | 0.056796 | 0.5567
|  | 20:47 | 25.1278 | 0.07146 | 0.5567
|  | 20:47 | 25.1289 | 0.069582 | 0.5567
|  | 20:47 | 25.13 | 0.067705 | 0.55669
|  | 20:47 | 25.1311 | 0.068706 | 0.55669
|  | 20:47 | 25.1322 | 0.072586 | 0.55669
|  | 20:47 | 25.1333 | 0.076467 | 0.55669
|  | 20:47 | 25.1344 | 0.08665 | 0.55669
|  | 20:48 | 25.1356 | 0.096832 | 0.55668
|  | 20:48 | 25.1367 | 0.097433 | 0.55668
|  | 20:48 | 25.1378 | 0.088452 | 0.55668
|  | 20:48 | 25.1389 | 0.079471 | 0.55668
|  | 20:48 | 25.14 | 0.07049 | 0.55667
|  | 20:48 | 25.1411 | 0.061509 | 0.55667
|  | 20:48 | 25.1422 | 0.044761 | 0.55667
|  | 20:48 | 25.1433 | 0.020245 | 0.55667
|  | 20:48 | 25.1444 | -0.0042709 | 0.55666
|  | 20:48 | 25.1456 | -0.0071686 | 0.55666
|  | 20:48 | 25.1467 | -0.010066 | 0.55666
|  | 20:48 | 25.1478 | -0.015785 | 0.55666
|  | 20:48 | 25.1489 | -0.024325 | 0.55666
|  | 20:48 | 25.15 | -0.032865 | 0.55665
|  | 20:48 | 25.1511 | -0.041405 | 0.55665
|  | 20:49 | 25.1522 | -0.049945 | 0.55665
|  | 20:49 | 25.1533 | -0.061732 | 0.55665
|  | 20:49 | 25.1544 | -0.076764 | 0.55664
|  | 20:49 | 25.1556 | -0.091797 | 0.55664
|  | 20:49 | 25.1567 | -0.081949 | 0.55664
|  | 20:49 | 25.1578 | -0.072101 | 0.55664
|  | 20:49 | 25.1589 | -0.069993 | 0.55663
|  | 20:49 | 25.16 | -0.075625 | 0.55663
|  | 20:49 | 25.1611 | -0.081256 | 0.55663
|  | 20:49 | 25.1622 | -0.10398 | 0.55663
|  | 20:49 | 25.1633 | -0.12671 | 0.55662
|  | 20:49 | 25.1644 | -0.13424 | 0.55662
|  | 20:49 | 25.1656 | -0.13671 | 0.55662
|  | 20:49 | 25.1667 | -0.13917 | 0.55662
|  | 20:49 | 25.1678 | -0.13967 | 0.55662
|  | 20:50 | 25.1689 | -0.14016 | 0.55661
|  | 20:50 | 25.17 | -0.13967 | 0.55661
|  | 20:50 | 25.1711 | -0.1382 | 0.55661
|  | 20:50 | 25.1722 | -0.13672 | 0.55661
|  | 20:50 | 25.1733 | -0.13986 | 0.5566
|  | 20:50 | 25.1744 | -0.143 | 0.5566
|  | 20:50 | 25.1756 | -0.15783 | 0.5566
|  | 20:50 | 25.1767 | -0.18435 | 0.5566
|  | 20:50 | 25.1778 | -0.21088 | 0.55659
|  | 20:50 | 25.1789 | -0.23015 | 0.55659
|  | 20:50 | 25.18 | -0.24943 | 0.55659
|  | 20:50 | 25.1811 | -0.27026 | 0.55659
|  | 20:50 | 25.1822 | -0.29265 | 0.55659
|  | 20:50 | 25.1833 | -0.31503 | 0.55658
|  | 20:50 | 25.1844 | -0.32195 | 0.55658
|  | 20:51 | 25.1856 | -0.32886 | 0.55658
|  | 20:51 | 25.1867 | -0.34119 | 0.55658
|  | 20:51 | 25.1878 | -0.35894 | 0.55657
|  | 20:51 | 25.1889 | -0.37669 | 0.55657
|  | 20:51 | 25.19 | -0.40678 | 0.55657
|  | 20:51 | 25.1911 | -0.43687 | 0.55657
|  | 20:51 | 25.1922 | -0.47126 | 0.55656
|  | 20:51 | 25.1933 | -0.50996 | 0.55656
|  | 20:51 | 25.1944 | -0.54865 | 0.55656
|  | 20:51 | 25.1956 | -0.56956 | 0.55656
|  | 20:51 | 25.1967 | -0.59046 | 0.55656
|  | 20:51 | 25.1978 | -0.60099 | 0.55655
|  | 20:51 | 25.1989 | -0.60114 | 0.55655
|  | 20:51 | 25.2 | -0.60129 | 0.55655
|  | 20:51 | 25.2011 | -0.60725 | 0.55655
|  | 20:52 | 25.2022 | -0.6132 | 0.55654
|  | 20:52 | 25.2033 | -0.61495 | 0.55654
|  | 20:52 | 25.2044 | -0.6125 | 0.55654
|  | 20:52 | 25.2056 | -0.61004 | 0.55654
|  | 20:52 | 25.2067 | -0.60192 | 0.55653
|  | 20:52 | 25.2078 | -0.59379 | 0.55653
|  | 20:52 | 25.2089 | -0.57338 | 0.55653
|  | 20:52 | 25.21 | -0.54068 | 0.55653
|  | 20:52 | 25.2111 | -0.50798 | 0.55653
|  | 20:52 | 25.2122 | -0.44948 | 0.55652
|  | 20:52 | 25.2133 | -0.39097 | 0.55652
|  | 20:52 | 25.2144 | -0.34491 | 0.55652
|  | 20:52 | 25.2156 | -0.30298 | 0.55652
|  | 20:52 | 25.2167 | -0.26106 | 0.55651
|  | 20:52 | 25.2178 | -0.21372 | 0.55651
|  | 20:53 | 25.2189 | -0.16637 | 0.55651
|  | 20:53 | 25.22 | -0.13138 | 0.55651
|  | 20:53 | 25.2211 | -0.10875 | 0.5565
|  | 20:53 | 25.2222 | -0.086123 | 0.5565
|  | 20:53 | 25.2233 | -0.059309 | 0.5565
|  | 20:53 | 25.2244 | -0.032495 | 0.5565
|  | 20:53 | 25.2256 | -0.0085625 | 0.5565
|  | 20:53 | 25.2267 | 0.01441 | 0.55649
|  | 20:53 | 25.2278 | 0.037382 | 0.55649
|  | 20:53 | 25.2289 | 0.066252 | 0.55649
|  | 20:53 | 25.23 | 0.095122 | 0.55649
|  | 20:53 | 25.2311 | 0.10872 | 0.55648
|  | 20:53 | 25.2322 | 0.10704 | 0.55648
|  | 20:53 | 25.2333 | 0.10536 | 0.55648
|  | 20:53 | 25.2344 | 0.10089 | 0.55648
|  | 20:54 | 25.2356 | 0.088038 | 0.55647
|  | 20:54 | 25.2367 | 0.080428 | 0.55647
|  | 20:54 | 25.2378 | 0.078054 | 0.55647
|  | 20:54 | 25.2389 | 0.07568 | 0.55647
|  | 20:54 | 25.24 | 0.060873 | 0.55647
|  | 20:54 | 25.2411 | 0.046067 | 0.55646
|  | 20:54 | 25.2422 | 0.032489 | 0.55646
|  | 20:54 | 25.2433 | 0.02014 | 0.55646
|  | 20:54 | 25.2444 | 0.0077913 | 0.55646
|  | 20:54 | 25.2456 | 0.0089382 | 0.55645
|  | 20:54 | 25.2467 | 0.010085 | 0.55645
|  | 20:54 | 25.2478 | 0.017944 | 0.55645
|  | 20:54 | 25.2489 | 0.032514 | 0.55645
|  | 20:54 | 25.25 | 0.047085 | 0.55644
|  | 20:54 | 25.2511 | 0.076109 | 0.55644
|  | 20:55 | 25.2522 | 0.10513 | 0.55644
|  | 20:55 | 25.2533 | 0.13867 | 0.55644
|  | 20:55 | 25.2544 | 0.17371 | 0.55644
|  | 20:55 | 25.2556 | 0.20875 | 0.55643
|  | 20:55 | 25.2567 | 0.23334 | 0.55643
|  | 20:55 | 25.2578 | 0.25792 | 0.55643
|  | 20:55 | 25.2589 | 0.27615 | 0.55643
|  | 20:55 | 25.26 | 0.28804 | 0.55642
|  | 20:55 | 25.2611 | 0.29992 | 0.55642
|  | 20:55 | 25.2622 | 0.31798 | 0.55642
|  | 20:55 | 25.2633 | 0.33605 | 0.55642
|  | 20:55 | 25.2644 | 0.36385 | 0.55641
|  | 20:55 | 25.2656 | 0.40137 | 0.55641
|  | 20:55 | 25.2667 | 0.4389 | 0.55641
|  | 20:55 | 25.2678 | 0.47837 | 0.55641
|  | 20:56 | 25.2689 | 0.51784 | 0.55641
|  | 20:56 | 25.27 | 0.54605 | 0.5564
|  | 20:56 | 25.2711 | 0.57051 | 0.5564
|  | 20:56 | 25.2722 | 0.59043 | 0.5564
|  | 20:56 | 25.2733 | 0.59672 | 0.5564
|  | 20:56 | 25.2744 | 0.60301 | 0.55639
|  | 20:56 | 25.2756 | 0.61476 | 0.55639
|  | 20:56 | 25.2767 | 0.62833 | 0.55639
|  | 20:56 | 25.2778 | 0.63908 | 0.55639
|  | 20:56 | 25.2789 | 0.64134 | 0.55638
|  | 20:56 | 25.28 | 0.6436 | 0.55638
|  | 20:56 | 25.2811 | 0.64966 | 0.55638
|  | 20:56 | 25.2822 | 0.65699 | 0.55638
|  | 20:56 | 25.2833 | 0.66861 | 0.55637
|  | 20:56 | 25.2844 | 0.69311 | 0.55637
|  | 20:57 | 25.2856 | 0.71761 | 0.55637
|  | 20:57 | 25.2867 | 0.72431 | 0.55637
|  | 20:57 | 25.2878 | 0.72507 | 0.55637
|  | 20:57 | 25.2889 | 0.72324 | 0.55636
|  | 20:57 | 25.29 | 0.71361 | 0.55636
|  | 20:57 | 25.2911 | 0.70399 | 0.55636
|  | 20:57 | 25.2922 | 0.68391 | 0.55636
|  | 20:57 | 25.2933 | 0.66036 | 0.55635
|  | 20:57 | 25.2944 | 0.63042 | 0.55635
|  | 20:57 | 25.2956 | 0.58134 | 0.55635
|  | 20:57 | 25.2967 | 0.53226 | 0.55635
|  | 20:57 | 25.2978 | 0.48119 | 0.55634
|  | 20:57 | 25.2989 | 0.42944 | 0.55634
|  | 20:57 | 25.3 | 0.38903 | 0.55634
|  | 20:57 | 25.3011 | 0.35995 | 0.55634
|  | 20:58 | 25.3022 | 0.33088 | 0.55634
|  | 20:58 | 25.3033 | 0.2821 | 0.55633
|  | 20:58 | 25.3044 | 0.22676 | 0.55633
|  | 20:58 | 25.3056 | 0.17658 | 0.55633
|  | 20:58 | 25.3067 | 0.1419 | 0.55633
|  | 20:58 | 25.3078 | 0.10722 | 0.55632
|  | 20:58 | 25.3089 | 0.081901 | 0.55632
|  | 20:58 | 25.31 | 0.056586 | 0.55632
|  | 20:58 | 25.3111 | 0.030142 | 0.55632
|  | 20:58 | 25.3122 | 0.00031549 | 0.55631
|  | 20:58 | 25.3133 | -0.029511 | 0.55631
|  | 20:58 | 25.3144 | -0.058698 | 0.55631
|  | 20:58 | 25.3156 | -0.087671 | 0.55631
|  | 20:58 | 25.3167 | -0.11306 | 0.55631
|  | 20:58 | 25.3178 | -0.12771 | 0.5563
|  | 20:59 | 25.3189 | -0.14236 | 0.5563
|  | 20:59 | 25.32 | -0.16624 | 0.5563
|  | 20:59 | 25.3211 | -0.1932 | 0.5563
|  | 20:59 | 25.3222 | -0.22575 | 0.55629
|  | 20:59 | 25.3233 | -0.2751 | 0.55629
|  | 20:59 | 25.3244 | -0.32445 | 0.55629
|  | 20:59 | 25.3256 | -0.35449 | 0.55629
|  | 20:59 | 25.3267 | -0.37809 | 0.55628
|  | 20:59 | 25.3278 | -0.39723 | 0.55628
|  | 20:59 | 25.3289 | -0.40298 | 0.55628
|  | 20:59 | 25.33 | -0.40874 | 0.55628
|  | 20:59 | 25.3311 | -0.41121 | 0.55628
|  | 20:59 | 25.3322 | -0.41258 | 0.55627
|  | 20:59 | 25.3333 | -0.4191 | 0.55627
|  | 20:59 | 25.3344 | -0.44105 | 0.55627
|  | 21:00 | 25.3356 | -0.46301 | 0.55627
|  | 21:00 | 25.3367 | -0.4794 | 0.55626
|  | 21:00 | 25.3378 | -0.49394 | 0.55626
|  | 21:00 | 25.3389 | -0.50803 | 0.55626
|  | 21:00 | 25.34 | -0.52082 | 0.55626
|  | 21:00 | 25.3411 | -0.53361 | 0.55625
|  | 21:00 | 25.3422 | -0.57167 | 0.55625
|  | 21:00 | 25.3433 | -0.61817 | 0.55625
|  | 21:00 | 25.3444 | -0.65686 | 0.55625
|  | 21:00 | 25.3456 | -0.67212 | 0.55625
|  | 21:00 | 25.3467 | -0.68739 | 0.55624
|  | 21:00 | 25.3478 | -0.69862 | 0.55624
|  | 21:00 | 25.3489 | -0.7085 | 0.55624
|  | 21:00 | 25.35 | -0.7136 | 0.55624
|  | 21:00 | 25.3511 | -0.70432 | 0.55623
|  | 21:01 | 25.3522 | -0.69505 | 0.55623
|  | 21:01 | 25.3533 | -0.67207 | 0.55623
|  | 21:01 | 25.3544 | -0.64451 | 0.55623
|  | 21:01 | 25.3556 | -0.61836 | 0.55622
|  | 21:01 | 25.3567 | -0.59644 | 0.55622
|  | 21:01 | 25.3578 | -0.57451 | 0.55622
|  | 21:01 | 25.3589 | -0.55325 | 0.55622
|  | 21:01 | 25.36 | -0.53222 | 0.55622
|  | 21:01 | 25.3611 | -0.51696 | 0.55621
|  | 21:01 | 25.3622 | -0.51903 | 0.55621
|  | 21:01 | 25.3633 | -0.5211 | 0.55621
|  | 21:01 | 25.3644 | -0.52402 | 0.55621
|  | 21:01 | 25.3656 | -0.52724 | 0.5562
|  | 21:01 | 25.3667 | -0.52781 | 0.5562
|  | 21:01 | 25.3678 | -0.52046 | 0.5562
|  | 21:02 | 25.3689 | -0.51311 | 0.5562
|  | 21:02 | 25.37 | -0.49295 | 0.55619
|  | 21:02 | 25.3711 | -0.46852 | 0.55619
|  | 21:02 | 25.3722 | -0.44277 | 0.55619
|  | 21:02 | 25.3733 | -0.41302 | 0.55619
|  | 21:02 | 25.3744 | -0.38327 | 0.55619
|  | 21:02 | 25.3756 | -0.36219 | 0.55618
|  | 21:02 | 25.3767 | -0.34399 | 0.55618
|  | 21:02 | 25.3778 | -0.32331 | 0.55618
|  | 21:02 | 25.3789 | -0.29521 | 0.55618
|  | 21:02 | 25.38 | -0.26711 | 0.55617
|  | 21:02 | 25.3811 | -0.22818 | 0.55617
|  | 21:02 | 25.3822 | -0.18565 | 0.55617
|  | 21:02 | 25.3833 | -0.14681 | 0.55617
|  | 21:02 | 25.3844 | -0.11909 | 0.55616
|  | 21:03 | 25.3856 | -0.091362 | 0.55616
|  | 21:03 | 25.3867 | -0.063635 | 0.55616
|  | 21:03 | 25.3878 | -0.035909 | 0.55616
|  | 21:03 | 25.3889 | -0.010399 | 0.55616
|  | 21:03 | 25.39 | 0.008462 | 0.55615
|  | 21:03 | 25.3911 | 0.027323 | 0.55615
|  | 21:03 | 25.3922 | 0.034398 | 0.55615
|  | 21:03 | 25.3933 | 0.037546 | 0.55615
|  | 21:03 | 25.3944 | 0.043552 | 0.55614
|  | 21:03 | 25.3956 | 0.058133 | 0.55614
|  | 21:03 | 25.3967 | 0.072714 | 0.55614
|  | 21:03 | 25.3978 | 0.058027 | 0.55614
|  | 21:03 | 25.3989 | 0.033585 | 0.55613
|  | 21:03 | 25.4 | 0.0091424 | 0.55613
|  | 21:03 | 25.4011 | -0.0069915 | 0.55613
|  | 21:04 | 25.4022 | -0.014817 | 0.55613
|  | 21:04 | 25.4033 | -0.013008 | 0.55612
|  | 21:04 | 25.4044 | -0.0079873 | 0.55612
|  | 21:04 | 25.4056 | -0.0032145 | 0.55612
|  | 21:04 | 25.4067 | 0.00081442 | 0.55612
|  | 21:04 | 25.4078 | 0.0048433 | 0.55612
|  | 21:04 | 25.4089 | -0.011699 | 0.55611
|  | 21:04 | 25.41 | -0.035099 | 0.55611
|  | 21:04 | 25.4111 | -0.062149 | 0.55611
|  | 21:04 | 25.4122 | -0.10015 | 0.55611
|  | 21:04 | 25.4133 | -0.13814 | 0.5561
|  | 21:04 | 25.4144 | -0.15922 | 0.5561
|  | 21:04 | 25.4156 | -0.17466 | 0.5561
|  | 21:04 | 25.4167 | -0.18651 | 0.5561
|  | 21:04 | 25.4178 | -0.18759 | 0.55609
|  | 21:05 | 25.4189 | -0.18868 | 0.55609
|  | 21:05 | 25.42 | -0.16432 | 0.55609
|  | 21:05 | 25.4211 | -0.13147 | 0.55609
|  | 21:05 | 25.4222 | -0.097254 | 0.55609
|  | 21:05 | 25.4233 | -0.058911 | 0.55608
|  | 21:05 | 25.4244 | -0.020569 | 0.55608
|  | 21:05 | 25.4256 | 0.017096 | 0.55608
|  | 21:05 | 25.4267 | 0.054534 | 0.55608
|  | 21:05 | 25.4278 | 0.085579 | 0.55607
|  | 21:05 | 25.4289 | 0.097447 | 0.55607
|  | 21:05 | 25.43 | 0.10931 | 0.55607
|  | 21:05 | 25.4311 | 0.11074 | 0.55607
|  | 21:05 | 25.4322 | 0.10868 | 0.55606
|  | 21:05 | 25.4333 | 0.10522 | 0.55606
|  | 21:05 | 25.4344 | 0.097578 | 0.55606
|  | 21:06 | 25.4356 | 0.089932 | 0.55606
|  | 21:06 | 25.4367 | 0.073569 | 0.55606
|  | 21:06 | 25.4378 | 0.048491 | 0.55605
|  | 21:06 | 25.4389 | 0.023412 | 0.55605
|  | 21:06 | 25.44 | 0.0095454 | 0.55605
|  | 21:06 | 25.4411 | -0.0043213 | 0.55605
|  | 21:06 | 25.4422 | -0.0022857 | 0.55604
|  | 21:06 | 25.4433 | 0.015652 | 0.55604
|  | 21:06 | 25.4444 | 0.03359 | 0.55604
|  | 21:06 | 25.4456 | 0.10038 | 0.55604
|  | 21:06 | 25.4467 | 0.16717 | 0.55603
|  | 21:06 | 25.4478 | 0.23184 | 0.55603
|  | 21:06 | 25.4489 | 0.29437 | 0.55603
|  | 21:06 | 25.45 | 0.35691 | 0.55603
|  | 21:06 | 25.4511 | 0.38203 | 0.55603
|  | 21:07 | 25.4522 | 0.40715 | 0.55602
|  | 21:07 | 25.4533 | 0.43669 | 0.55602
|  | 21:07 | 25.4544 | 0.47067 | 0.55602
|  | 21:07 | 25.4556 | 0.50464 | 0.55602
|  | 21:07 | 25.4567 | 0.51512 | 0.55601
|  | 21:07 | 25.4578 | 0.52559 | 0.55601
|  | 21:07 | 25.4589 | 0.54013 | 0.55601
|  | 21:07 | 25.46 | 0.55874 | 0.55601
|  | 21:07 | 25.4611 | 0.57735 | 0.556
|  | 21:07 | 25.4622 | 0.57414 | 0.556
|  | 21:07 | 25.4633 | 0.57092 | 0.556
|  | 21:07 | 25.4644 | 0.57038 | 0.556
|  | 21:07 | 25.4656 | 0.57251 | 0.556
|  | 21:07 | 25.4667 | 0.57464 | 0.55599
|  | 21:07 | 25.4678 | 0.57446 | 0.55599
|  | 21:08 | 25.4689 | 0.57428 | 0.55599
|  | 21:08 | 25.47 | 0.56794 | 0.55599
|  | 21:08 | 25.4711 | 0.55544 | 0.55598
|  | 21:08 | 25.4722 | 0.54294 | 0.55598
|  | 21:08 | 25.4733 | 0.53362 | 0.55598
|  | 21:08 | 25.4744 | 0.52431 | 0.55598
|  | 21:08 | 25.4756 | 0.51346 | 0.55597
|  | 21:08 | 25.4767 | 0.50109 | 0.55597
|  | 21:08 | 25.4778 | 0.48871 | 0.55597
|  | 21:08 | 25.4789 | 0.46532 | 0.55597
|  | 21:08 | 25.48 | 0.44193 | 0.55597
|  | 21:08 | 25.4811 | 0.41736 | 0.55596
|  | 21:08 | 25.4822 | 0.39241 | 0.55596
|  | 21:08 | 25.4833 | 0.36745 | 0.55596
|  | 21:08 | 25.4844 | 0.32955 | 0.55596
|  | 21:09 | 25.4856 | 0.29165 | 0.55595
|  | 21:09 | 25.4867 | 0.25312 | 0.55595
|  | 21:09 | 25.4878 | 0.21396 | 0.55595
|  | 21:09 | 25.4889 | 0.1748 | 0.55595
|  | 21:09 | 25.49 | 0.11481 | 0.55594
|  | 21:09 | 25.4911 | 0.054818 | 0.55594
|  | 21:09 | 25.4922 | -0.0065868 | 0.55594
|  | 21:09 | 25.4933 | -0.068462 | 0.55594
|  | 21:09 | 25.4944 | -0.13034 | 0.55594
|  | 21:09 | 25.4956 | -0.17611 | 0.55593
|  | 21:09 | 25.4967 | -0.22189 | 0.55593
|  | 21:09 | 25.4978 | -0.26715 | 0.55593
|  | 21:09 | 25.4989 | -0.3119 | 0.55593
|  | 21:09 | 25.5 | -0.35665 | 0.55592
|  | 21:09 | 25.5011 | -0.39577 | 0.55592
|  | 21:10 | 25.5022 | -0.43489 | 0.55592
|  | 21:10 | 25.5033 | -0.45765 | 0.55592
|  | 21:10 | 25.5044 | -0.46406 | 0.55591
|  | 21:10 | 25.5056 | -0.47047 | 0.55591
|  | 21:10 | 25.5067 | -0.45239 | 0.55591
|  | 21:10 | 25.5078 | -0.4343 | 0.55591
|  | 21:10 | 25.5089 | -0.42879 | 0.55591
|  | 21:10 | 25.51 | -0.43588 | 0.5559
|  | 21:10 | 25.5111 | -0.44296 | 0.5559
|  | 21:10 | 25.5122 | -0.44646 | 0.5559
|  | 21:10 | 25.5133 | -0.44997 | 0.5559
|  | 21:10 | 25.5144 | -0.44712 | 0.55589
|  | 21:10 | 25.5156 | -0.43794 | 0.55589
|  | 21:10 | 25.5167 | -0.42875 | 0.55589
|  | 21:10 | 25.5178 | -0.42518 | 0.55589
|  | 21:11 | 25.5189 | -0.42161 | 0.55588
|  | 21:11 | 25.52 | -0.42556 | 0.55588
|  | 21:11 | 25.5211 | -0.43704 | 0.55588
|  | 21:11 | 25.5222 | -0.44852 | 0.55588
|  | 21:11 | 25.5233 | -0.44164 | 0.55587
|  | 21:11 | 25.5244 | -0.43475 | 0.55587
|  | 21:11 | 25.5256 | -0.42925 | 0.55587
|  | 21:11 | 25.5267 | -0.42513 | 0.55587
|  | 21:11 | 25.5278 | -0.421 | 0.55587
|  | 21:11 | 25.5289 | -0.40086 | 0.55586
|  | 21:11 | 25.53 | -0.38072 | 0.55586
|  | 21:11 | 25.5311 | -0.36457 | 0.55586
|  | 21:11 | 25.5322 | -0.35242 | 0.55586
|  | 21:11 | 25.5333 | -0.34187 | 0.55585
|  | 21:11 | 25.5344 | -0.33616 | 0.55585
|  | 21:12 | 25.5356 | -0.33044 | 0.55585
|  | 21:12 | 25.5367 | -0.31632 | 0.55585
|  | 21:12 | 25.5378 | -0.29381 | 0.55584
|  | 21:12 | 25.5389 | -0.2713 | 0.55584
|  | 21:12 | 25.54 | -0.25262 | 0.55584
|  | 21:12 | 25.5411 | -0.23394 | 0.55584
|  | 21:12 | 25.5422 | -0.21066 | 0.55584
|  | 21:12 | 25.5433 | -0.18278 | 0.55583
|  | 21:12 | 25.5444 | -0.1549 | 0.55583
|  | 21:12 | 25.5456 | -0.1598 | 0.55583
|  | 21:12 | 25.5467 | -0.1647 | 0.55583
|  | 21:12 | 25.5478 | -0.16862 | 0.55582
|  | 21:12 | 25.5489 | -0.17156 | 0.55582
|  | 21:12 | 25.55 | -0.17451 | 0.55582
|  | 21:12 | 25.5511 | -0.16854 | 0.55582
|  | 21:13 | 25.5522 | -0.16258 | 0.55581
|  | 21:13 | 25.5533 | -0.16124 | 0.55581
|  | 21:13 | 25.5544 | -0.16454 | 0.55581
|  | 21:13 | 25.5556 | -0.16783 | 0.55581
|  | 21:13 | 25.5567 | -0.15843 | 0.55581
|  | 21:13 | 25.5578 | -0.14903 | 0.5558
|  | 21:13 | 25.5589 | -0.12965 | 0.5558
|  | 21:13 | 25.56 | -0.10029 | 0.5558
|  | 21:13 | 25.5611 | -0.070943 | 0.5558
|  | 21:13 | 25.5622 | -0.066805 | 0.55579
|  | 21:13 | 25.5633 | -0.062667 | 0.55579
|  | 21:13 | 25.5644 | -0.054492 | 0.55579
|  | 21:13 | 25.5656 | -0.042281 | 0.55579
|  | 21:13 | 25.5667 | -0.030069 | 0.55578
|  | 21:13 | 25.5678 | -0.017858 | 0.55578
|  | 21:14 | 25.5689 | 0.0074794 | 0.55578
|  | 21:14 | 25.57 | 0.030449 | 0.55578
|  | 21:14 | 25.5711 | 0.046317 | 0.55578
|  | 21:14 | 25.5722 | 0.062185 | 0.55577
|  | 21:14 | 25.5733 | 0.082672 | 0.55577
|  | 21:14 | 25.5744 | 0.10316 | 0.55577
|  | 21:14 | 25.5756 | 0.12318 | 0.55577
|  | 21:14 | 25.5767 | 0.14273 | 0.55576
|  | 21:14 | 25.5778 | 0.16229 | 0.55576
|  | 21:14 | 25.5789 | 0.17597 | 0.55576
|  | 21:14 | 25.58 | 0.18965 | 0.55576
|  | 21:14 | 25.5811 | 0.21106 | 0.55575
|  | 21:14 | 25.5822 | 0.24018 | 0.55575
|  | 21:14 | 25.5833 | 0.2693 | 0.55575
|  | 21:14 | 25.5844 | 0.28985 | 0.55575
|  | 21:15 | 25.5856 | 0.3104 | 0.55575
|  | 21:15 | 25.5867 | 0.32411 | 0.55574
|  | 21:15 | 25.5878 | 0.33098 | 0.55574
|  | 21:15 | 25.5889 | 0.33785 | 0.55574
|  | 21:15 | 25.59 | 0.3406 | 0.55574
|  | 21:15 | 25.5911 | 0.34335 | 0.55573
|  | 21:15 | 25.5922 | 0.34433 | 0.55573
|  | 21:15 | 25.5933 | 0.34356 | 0.55573
|  | 21:15 | 25.5944 | 0.34278 | 0.55573
|  | 21:15 | 25.5956 | 0.3594 | 0.55572
|  | 21:15 | 25.5967 | 0.37602 | 0.55572
|  | 21:15 | 25.5978 | 0.39263 | 0.55572
|  | 21:15 | 25.5989 | 0.40925 | 0.55572
|  | 21:15 | 25.6 | 0.42587 | 0.55572
|  | 21:15 | 25.6011 | 0.4182 | 0.55571
|  | 21:16 | 25.6022 | 0.41053 | 0.55571
|  | 21:16 | 25.6033 | 0.39842 | 0.55571
|  | 21:16 | 25.6044 | 0.38187 | 0.55571
|  | 21:16 | 25.6056 | 0.36532 | 0.5557
|  | 21:16 | 25.6067 | 0.33087 | 0.5557
|  | 21:16 | 25.6078 | 0.29642 | 0.5557
|  | 21:16 | 25.6089 | 0.28083 | 0.5557
|  | 21:16 | 25.61 | 0.28412 | 0.55569
|  | 21:16 | 25.6111 | 0.2874 | 0.55569
|  | 21:16 | 25.6122 | 0.2724 | 0.55569
|  | 21:16 | 25.6133 | 0.2574 | 0.55569
|  | 21:16 | 25.6144 | 0.2361 | 0.55569
|  | 21:16 | 25.6156 | 0.2085 | 0.55568
|  | 21:16 | 25.6167 | 0.18089 | 0.55568
|  | 21:16 | 25.6178 | 0.14929 | 0.55568
|  | 21:17 | 25.6189 | 0.11769 | 0.55568
|  | 21:17 | 25.62 | 0.10424 | 0.55567
|  | 21:17 | 25.6211 | 0.096831 | 0.55567
|  | 21:17 | 25.6222 | 0.089426 | 0.55567
|  | 21:17 | 25.6233 | 0.072852 | 0.55567
|  | 21:17 | 25.6244 | 0.056277 | 0.55566
|  | 21:17 | 25.6256 | 0.041294 | 0.55566
|  | 21:17 | 25.6267 | 0.027902 | 0.55566
|  | 21:17 | 25.6278 | 0.01451 | 0.55566
|  | 21:17 | 25.6289 | -0.0091688 | 0.55566
|  | 21:17 | 25.63 | -0.032848 | 0.55565
|  | 21:17 | 25.6311 | -0.066966 | 0.55565
|  | 21:17 | 25.6322 | -0.11152 | 0.55565
|  | 21:17 | 25.6333 | -0.15608 | 0.55565
|  | 21:17 | 25.6344 | -0.17782 | 0.55564
|  | 21:18 | 25.6356 | -0.19956 | 0.55564
|  | 21:18 | 25.6367 | -0.21505 | 0.55564
|  | 21:18 | 25.6378 | -0.2243 | 0.55564
|  | 21:18 | 25.6389 | -0.23485 | 0.55563
|  | 21:18 | 25.64 | -0.24933 | 0.55563
|  | 21:18 | 25.6411 | -0.26381 | 0.55563
|  | 21:18 | 25.6422 | -0.28585 | 0.55563
|  | 21:18 | 25.6433 | -0.31041 | 0.55562
|  | 21:18 | 25.6444 | -0.33498 | 0.55562
|  | 21:18 | 25.6456 | -0.35433 | 0.55562
|  | 21:18 | 25.6467 | -0.37369 | 0.55562
|  | 21:18 | 25.6478 | -0.38334 | 0.55562
|  | 21:18 | 25.6489 | -0.38329 | 0.55561
|  | 21:18 | 25.65 | -0.38325 | 0.55561
|  | 21:18 | 25.6511 | -0.37177 | 0.55561
|  | 21:19 | 25.6522 | -0.36028 | 0.55561
|  | 21:19 | 25.6533 | -0.34955 | 0.5556
|  | 21:19 | 25.6544 | -0.33956 | 0.5556
|  | 21:19 | 25.6556 | -0.32957 | 0.5556
|  | 21:19 | 25.6567 | -0.32282 | 0.5556
|  | 21:19 | 25.6578 | -0.31608 | 0.55559
|  | 21:19 | 25.6589 | -0.30933 | 0.55559
|  | 21:19 | 25.66 | -0.30258 | 0.55559
|  | 21:19 | 25.6611 | -0.2977 | 0.55559
|  | 21:19 | 25.6622 | -0.29843 | 0.55559
|  | 21:19 | 25.6633 | -0.29916 | 0.55558
|  | 21:19 | 25.6644 | -0.3059 | 0.55558
|  | 21:19 | 25.6656 | -0.31865 | 0.55558
|  | 21:19 | 25.6667 | -0.33141 | 0.55558
|  | 21:19 | 25.6678 | -0.34928 | 0.55557
|  | 21:20 | 25.6689 | -0.36715 | 0.55557
|  | 21:20 | 25.67 | -0.36743 | 0.55557
|  | 21:20 | 25.6711 | -0.35014 | 0.55557
|  | 21:20 | 25.6722 | -0.33284 | 0.55556
|  | 21:20 | 25.6733 | -0.32614 | 0.55556
|  | 21:20 | 25.6744 | -0.31945 | 0.55556
|  | 21:20 | 25.6756 | -0.32347 | 0.55556
|  | 21:20 | 25.6767 | -0.33105 | 0.55556
|  | 21:20 | 25.6778 | -0.33863 | 0.55555
|  | 21:20 | 25.6789 | -0.34742 | 0.55555
|  | 21:20 | 25.68 | -0.35621 | 0.55555
|  | 21:20 | 25.6811 | -0.35525 | 0.55555
|  | 21:20 | 25.6822 | -0.34453 | 0.55554
|  | 21:20 | 25.6833 | -0.33382 | 0.55554
|  | 21:20 | 25.6844 | -0.32408 | 0.55554
|  | 21:21 | 25.6856 | -0.31435 | 0.55554
|  | 21:21 | 25.6867 | -0.29629 | 0.55553
|  | 21:21 | 25.6878 | -0.2699 | 0.55553
|  | 21:21 | 25.6889 | -0.24351 | 0.55553
|  | 21:21 | 25.69 | -0.22981 | 0.55553
|  | 21:21 | 25.6911 | -0.21611 | 0.55553
|  | 21:21 | 25.6922 | -0.19988 | 0.55552
|  | 21:21 | 25.6933 | -0.18112 | 0.55552
|  | 21:21 | 25.6944 | -0.16235 | 0.55552
|  | 21:21 | 25.6956 | -0.16142 | 0.55552
|  | 21:21 | 25.6967 | -0.16049 | 0.55551
|  | 21:21 | 25.6978 | -0.15389 | 0.55551
|  | 21:21 | 25.6989 | -0.14164 | 0.55551
|  | 21:21 | 25.7 | -0.12939 | 0.55551
|  | 21:21 | 25.7011 | -0.12526 | 0.5555
|  | 21:22 | 25.7022 | -0.12113 | 0.5555
|  | 21:22 | 25.7033 | -0.12313 | 0.5555
|  | 21:22 | 25.7044 | -0.13125 | 0.5555
|  | 21:22 | 25.7056 | -0.13938 | 0.5555
|  | 21:22 | 25.7067 | -0.13197 | 0.55549
|  | 21:22 | 25.7078 | -0.12456 | 0.55549
|  | 21:22 | 25.7089 | -0.11274 | 0.55549
|  | 21:22 | 25.71 | -0.096521 | 0.55549
|  | 21:22 | 25.7111 | -0.080302 | 0.55548
|  | 21:22 | 25.7122 | -0.054155 | 0.55548
|  | 21:22 | 25.7133 | -0.028008 | 0.55548
|  | 21:22 | 25.7144 | -0.0045076 | 0.55548
|  | 21:22 | 25.7156 | 0.016347 | 0.55547
|  | 21:22 | 25.7167 | 0.037201 | 0.55547
|  | 21:22 | 25.7178 | 0.038561 | 0.55547
|  | 21:23 | 25.7189 | 0.039921 | 0.55547
|  | 21:23 | 25.72 | 0.04462 | 0.55547
|  | 21:23 | 25.7211 | 0.052657 | 0.55546
|  | 21:23 | 25.7222 | 0.060695 | 0.55546
|  | 21:23 | 25.7233 | 0.062016 | 0.55546
|  | 21:23 | 25.7244 | 0.063337 | 0.55546
|  | 21:23 | 25.7256 | 0.059152 | 0.55545
|  | 21:23 | 25.7267 | 0.049461 | 0.55545
|  | 21:23 | 25.7278 | 0.039771 | 0.55545
|  | 21:23 | 25.7289 | 0.03008 | 0.55545
|  | 21:23 | 25.73 | 0.02039 | 0.55544
|  | 21:23 | 25.7311 | 0.012533 | 0.55544
|  | 21:23 | 25.7322 | 0.00651 | 0.55544
|  | 21:23 | 25.7333 | 0.00048686 | 0.55544
|  | 21:23 | 25.7344 | -0.0055363 | 0.55544
|  | 21:24 | 25.7356 | -0.028667 | 0.55543
|  | 21:24 | 25.7367 | -0.055754 | 0.55543
|  | 21:24 | 25.7378 | -0.094714 | 0.55543
|  | 21:24 | 25.7389 | -0.13367 | 0.55543
|  | 21:24 | 25.74 | -0.1564 | 0.55542
|  | 21:24 | 25.7411 | -0.17912 | 0.55542
|  | 21:24 | 25.7422 | -0.20465 | 0.55542
|  | 21:24 | 25.7433 | -0.23296 | 0.55542
|  | 21:24 | 25.7444 | -0.26128 | 0.55541
|  | 21:24 | 25.7456 | -0.28713 | 0.55541
|  | 21:24 | 25.7467 | -0.31299 | 0.55541
|  | 21:24 | 25.7478 | -0.3269 | 0.55541
|  | 21:24 | 25.7489 | -0.32887 | 0.55541
|  | 21:24 | 25.75 | -0.33084 | 0.5554
|  | 21:24 | 25.7511 | -0.34417 | 0.5554
|  | 21:25 | 25.7522 | -0.35749 | 0.5554
|  | 21:25 | 25.7533 | -0.36829 | 0.5554
|  | 21:25 | 25.7544 | -0.37657 | 0.55539
|  | 21:25 | 25.7556 | -0.38484 | 0.55539
|  | 21:25 | 25.7567 | -0.39763 | 0.55539
|  | 21:25 | 25.7578 | -0.41043 | 0.55539
|  | 21:25 | 25.7589 | -0.42784 | 0.55538
|  | 21:25 | 25.76 | -0.44987 | 0.55538
|  | 21:25 | 25.7611 | -0.4719 | 0.55538
|  | 21:25 | 25.7622 | -0.49075 | 0.55538
|  | 21:25 | 25.7633 | -0.50959 | 0.55537
|  | 21:25 | 25.7644 | -0.5272 | 0.55537
|  | 21:25 | 25.7656 | -0.54355 | 0.55537
|  | 21:25 | 25.7667 | -0.5599 | 0.55537
|  | 21:25 | 25.7678 | -0.58263 | 0.55537
|  | 21:26 | 25.7689 | -0.60537 | 0.55536
|  | 21:26 | 25.77 | -0.62365 | 0.55536
|  | 21:26 | 25.7711 | -0.63747 | 0.55536
|  | 21:26 | 25.7722 | -0.65129 | 0.55536
|  | 21:26 | 25.7733 | -0.65879 | 0.55535
|  | 21:26 | 25.7744 | -0.66629 | 0.55535
|  | 21:26 | 25.7756 | -0.67986 | 0.55535
|  | 21:26 | 25.7767 | -0.6995 | 0.55535
|  | 21:26 | 25.7778 | -0.71913 | 0.55534
|  | 21:26 | 25.7789 | -0.73168 | 0.55534
|  | 21:26 | 25.78 | -0.74423 | 0.55534
|  | 21:26 | 25.7811 | -0.7505 | 0.55534
|  | 21:26 | 25.7822 | -0.75049 | 0.55534
|  | 21:26 | 25.7833 | -0.75048 | 0.55533
|  | 21:26 | 25.7844 | -0.73916 | 0.55533
|  | 21:27 | 25.7856 | -0.72783 | 0.55533
|  | 21:27 | 25.7867 | -0.70987 | 0.55533
|  | 21:27 | 25.7878 | -0.68526 | 0.55532
|  | 21:27 | 25.7889 | -0.66066 | 0.55532
|  | 21:27 | 25.79 | -0.6495 | 0.55532
|  | 21:27 | 25.7911 | -0.63834 | 0.55532
|  | 21:27 | 25.7922 | -0.61665 | 0.55531
|  | 21:27 | 25.7933 | -0.58443 | 0.55531
|  | 21:27 | 25.7944 | -0.55221 | 0.55531
|  | 21:27 | 25.7956 | -0.51541 | 0.55531
|  | 21:27 | 25.7967 | -0.47861 | 0.55531
|  | 21:27 | 25.7978 | -0.44523 | 0.5553
|  | 21:27 | 25.7989 | -0.41524 | 0.5553
|  | 21:27 | 25.8 | -0.38526 | 0.5553
|  | 21:27 | 25.8011 | -0.37899 | 0.5553
|  | 21:28 | 25.8022 | -0.37271 | 0.55529
|  | 21:28 | 25.8033 | -0.37159 | 0.55529
|  | 21:28 | 25.8044 | -0.37563 | 0.55529
|  | 21:28 | 25.8056 | -0.37966 | 0.55529
|  | 21:28 | 25.8067 | -0.36377 | 0.55528
|  | 21:28 | 25.8078 | -0.34788 | 0.55528
|  | 21:28 | 25.8089 | -0.32774 | 0.55528
|  | 21:28 | 25.81 | -0.30335 | 0.55528
|  | 21:28 | 25.8111 | -0.27896 | 0.55528
|  | 21:28 | 25.8122 | -0.25074 | 0.55527
|  | 21:28 | 25.8133 | -0.22252 | 0.55527
|  | 21:28 | 25.8144 | -0.19509 | 0.55527
|  | 21:28 | 25.8156 | -0.16792 | 0.55527
|  | 21:28 | 25.8167 | -0.14272 | 0.55526
|  | 21:28 | 25.8178 | -0.12345 | 0.55526
|  | 21:29 | 25.8189 | -0.10417 | 0.55526
|  | 21:29 | 25.82 | -0.087397 | 0.55526
|  | 21:29 | 25.8211 | -0.07313 | 0.55525
|  | 21:29 | 25.8222 | -0.058863 | 0.55525
|  | 21:29 | 25.8233 | -0.061269 | 0.55525
|  | 21:29 | 25.8244 | -0.063676 | 0.55525
|  | 21:29 | 25.8256 | -0.065522 | 0.55525
|  | 21:29 | 25.8267 | -0.066808 | 0.55524
|  | 21:29 | 25.8278 | -0.068094 | 0.55524
|  | 21:29 | 25.8289 | -0.075492 | 0.55524
|  | 21:29 | 25.83 | -0.08289 | 0.55524
|  | 21:29 | 25.8311 | -0.09073 | 0.55523
|  | 21:29 | 25.8322 | -0.099014 | 0.55523
|  | 21:29 | 25.8333 | -0.1073 | 0.55523
|  | 21:29 | 25.8344 | -0.089359 | 0.55523
|  | 21:30 | 25.8356 | -0.071421 | 0.55522
|  | 21:30 | 25.8367 | -0.049309 | 0.55522
|  | 21:30 | 25.8378 | -0.023023 | 0.55522
|  | 21:30 | 25.8389 | 0.0032623 | 0.55522
|  | 21:30 | 25.84 | 0.016532 | 0.55522
|  | 21:30 | 25.8411 | 0.029801 | 0.55521
|  | 21:30 | 25.8422 | 0.036497 | 0.55521
|  | 21:30 | 25.8433 | 0.03662 | 0.55521
|  | 21:30 | 25.8444 | 0.036742 | 0.55521
|  | 21:30 | 25.8456 | 0.031934 | 0.5552
|  | 21:30 | 25.8467 | 0.027126 | 0.5552
|  | 21:30 | 25.8478 | 0.038487 | 0.5552
|  | 21:30 | 25.8489 | 0.06602 | 0.5552
|  | 21:30 | 25.85 | 0.093552 | 0.55519
|  | 21:30 | 25.8511 | 0.12924 | 0.55519
|  | 21:31 | 25.8522 | 0.16492 | 0.55519
|  | 21:31 | 25.8533 | 0.19135 | 0.55519
|  | 21:31 | 25.8544 | 0.20853 | 0.55519
|  | 21:31 | 25.8556 | 0.2257 | 0.55518
|  | 21:31 | 25.8567 | 0.2251 | 0.55518
|  | 21:31 | 25.8578 | 0.22449 | 0.55518
|  | 21:31 | 25.8589 | 0.21902 | 0.55518
|  | 21:31 | 25.86 | 0.2087 | 0.55517
|  | 21:31 | 25.8611 | 0.19838 | 0.55517
|  | 21:31 | 25.8622 | 0.17104 | 0.55517
|  | 21:31 | 25.8633 | 0.14371 | 0.55517
|  | 21:31 | 25.8644 | 0.12041 | 0.55516
|  | 21:31 | 25.8656 | 0.10116 | 0.55516
|  | 21:31 | 25.8667 | 0.081902 | 0.55516
|  | 21:31 | 25.8678 | 0.099815 | 0.55516
|  | 21:32 | 25.8689 | 0.11773 | 0.55516
|  | 21:32 | 25.87 | 0.13342 | 0.55515
|  | 21:32 | 25.8711 | 0.14689 | 0.55515
|  | 21:32 | 25.8722 | 0.16036 | 0.55515
|  | 21:32 | 25.8733 | 0.17384 | 0.55515
|  | 21:32 | 25.8744 | 0.18731 | 0.55514
|  | 21:32 | 25.8756 | 0.20476 | 0.55514
|  | 21:32 | 25.8767 | 0.22619 | 0.55514
|  | 21:32 | 25.8778 | 0.24763 | 0.55514
|  | 21:32 | 25.8789 | 0.26643 | 0.55513
|  | 21:32 | 25.88 | 0.28523 | 0.55513
|  | 21:32 | 25.8811 | 0.29984 | 0.55513
|  | 21:32 | 25.8822 | 0.31025 | 0.55513
|  | 21:32 | 25.8833 | 0.32066 | 0.55512
|  | 21:32 | 25.8844 | 0.33434 | 0.55512
|  | 21:33 | 25.8856 | 0.34802 | 0.55512
|  | 21:33 | 25.8867 | 0.36502 | 0.55512
|  | 21:33 | 25.8878 | 0.38533 | 0.55512
|  | 21:33 | 25.8889 | 0.40565 | 0.55511
|  | 21:33 | 25.89 | 0.42159 | 0.55511
|  | 21:33 | 25.8911 | 0.43753 | 0.55511
|  | 21:33 | 25.8922 | 0.45058 | 0.55511
|  | 21:33 | 25.8933 | 0.46075 | 0.5551
|  | 21:33 | 25.8944 | 0.47091 | 0.5551
|  | 21:33 | 25.8956 | 0.47039 | 0.5551
|  | 21:33 | 25.8967 | 0.46987 | 0.5551
|  | 21:33 | 25.8978 | 0.46317 | 0.55509
|  | 21:33 | 25.8989 | 0.45441 | 0.55509
|  | 21:33 | 25.9 | 0.44565 | 0.55509
|  | 21:33 | 25.9011 | 0.42328 | 0.55509
|  | 21:34 | 25.9022 | 0.4009 | 0.55509
|  | 21:34 | 25.9033 | 0.38572 | 0.55508
|  | 21:34 | 25.9044 | 0.39211 | 0.55508
|  | 21:34 | 25.9056 | 0.3985 | 0.55508
|  | 21:34 | 25.9067 | 0.4237 | 0.55508
|  | 21:34 | 25.9078 | 0.4489 | 0.55507
|  | 21:34 | 25.9089 | 0.46088 | 0.55507
|  | 21:34 | 25.91 | 0.45964 | 0.55507
|  | 21:34 | 25.9111 | 0.45841 | 0.55507
|  | 21:34 | 25.9122 | 0.4475 | 0.55506
|  | 21:34 | 25.9133 | 0.43659 | 0.55506
|  | 21:34 | 25.9144 | 0.42325 | 0.55506
|  | 21:34 | 25.9156 | 0.40749 | 0.55506
|  | 21:34 | 25.9167 | 0.39172 | 0.55506
|  | 21:34 | 25.9178 | 0.40531 | 0.55505
|  | 21:35 | 25.9189 | 0.4189 | 0.55505
|  | 21:35 | 25.92 | 0.43151 | 0.55505
|  | 21:35 | 25.9211 | 0.44314 | 0.55505
|  | 21:35 | 25.9222 | 0.45477 | 0.55504
|  | 21:35 | 25.9233 | 0.4521 | 0.55504
|  | 21:35 | 25.9244 | 0.44943 | 0.55504
|  | 21:35 | 25.9256 | 0.43991 | 0.55504
|  | 21:35 | 25.9267 | 0.42354 | 0.55503
|  | 21:35 | 25.9278 | 0.40717 | 0.55503
|  | 21:35 | 25.9289 | 0.40518 | 0.55503
|  | 21:35 | 25.93 | 0.40319 | 0.55503
|  | 21:35 | 25.9311 | 0.41374 | 0.55503
|  | 21:35 | 25.9322 | 0.43682 | 0.55502
|  | 21:35 | 25.9333 | 0.45991 | 0.55502
|  | 21:35 | 25.9344 | 0.48429 | 0.55502
|  | 21:36 | 25.9356 | 0.50867 | 0.55502
|  | 21:36 | 25.9367 | 0.52763 | 0.55501
|  | 21:36 | 25.9378 | 0.54478 | 0.55501
|  | 21:36 | 25.9389 | 0.56194 | 0.55501
|  | 21:36 | 25.94 | 0.57207 | 0.55501
|  | 21:36 | 25.9411 | 0.58221 | 0.555
|  | 21:36 | 25.9422 | 0.58718 | 0.555
|  | 21:36 | 25.9433 | 0.58698 | 0.555
|  | 21:36 | 25.9444 | 0.58678 | 0.555
|  | 21:36 | 25.9456 | 0.60128 | 0.555
|  | 21:36 | 25.9467 | 0.61578 | 0.55499
|  | 21:36 | 25.9478 | 0.62143 | 0.55499
|  | 21:36 | 25.9489 | 0.61825 | 0.55499
|  | 21:36 | 25.95 | 0.61506 | 0.55499
|  | 21:36 | 25.9511 | 0.62239 | 0.55498
|  | 21:37 | 25.9522 | 0.62971 | 0.55498
|  | 21:37 | 25.9533 | 0.63355 | 0.55498
|  | 21:37 | 25.9544 | 0.6339 | 0.55498
|  | 21:37 | 25.9556 | 0.63907 | 0.55497
|  | 21:37 | 25.9567 | 0.65868 | 0.55497
|  | 21:37 | 25.9578 | 0.6783 | 0.55497
|  | 21:37 | 25.9589 | 0.69792 | 0.55497
|  | 21:37 | 25.96 | 0.71754 | 0.55497
|  | 21:37 | 25.9611 | 0.73715 | 0.55496
|  | 21:37 | 25.9622 | 0.75945 | 0.55496
|  | 21:37 | 25.9633 | 0.78175 | 0.55496
|  | 21:37 | 25.9644 | 0.79371 | 0.55496
|  | 21:37 | 25.9656 | 0.79532 | 0.55495
|  | 21:37 | 25.9667 | 0.79693 | 0.55495
|  | 21:37 | 25.9678 | 0.81251 | 0.55495
|  | 21:38 | 25.9689 | 0.82809 | 0.55495
|  | 21:38 | 25.97 | 0.83863 | 0.55494
|  | 21:38 | 25.9711 | 0.84413 | 0.55494
|  | 21:38 | 25.9722 | 0.84963 | 0.55494
|  | 21:38 | 25.9733 | 0.82497 | 0.55494
|  | 21:38 | 25.9744 | 0.8003 | 0.55494
|  | 21:38 | 25.9756 | 0.77953 | 0.55493
|  | 21:38 | 25.9767 | 0.76265 | 0.55493
|  | 21:38 | 25.9778 | 0.74578 | 0.55493
|  | 21:38 | 25.9789 | 0.7289 | 0.55493
|  | 21:38 | 25.98 | 0.71203 | 0.55492
|  | 21:38 | 25.9811 | 0.69599 | 0.55492
|  | 21:38 | 25.9822 | 0.68079 | 0.55492
|  | 21:38 | 25.9833 | 0.66559 | 0.55492
|  | 21:38 | 25.9844 | 0.65039 | 0.55491
|  | 21:39 | 25.9856 | 0.63519 | 0.55491
|  | 21:39 | 25.9867 | 0.6287 | 0.55491
|  | 21:39 | 25.9878 | 0.62511 | 0.55491
|  | 21:39 | 25.9889 | 0.62152 | 0.55491
|  | 21:39 | 25.99 | 0.60905 | 0.5549
|  | 21:39 | 25.9911 | 0.59658 | 0.5549
|  | 21:39 | 25.9922 | 0.59451 | 0.5549
|  | 21:39 | 25.9933 | 0.60285 | 0.5549
|  | 21:39 | 25.9944 | 0.61119 | 0.55489
|  | 21:39 | 25.9956 | 0.62747 | 0.55489
|  | 21:39 | 25.9967 | 0.64374 | 0.55489
|  | 21:39 | 25.9978 | 0.64699 | 0.55489
|  | 21:39 | 25.9989 | 0.6372 | 0.55488
|  | 21:39 | 26 | 0.62494 | 0.55488
|  | 21:39 | 26.0011 | 0.60529 | 0.55488
|  | 21:40 | 26.0022 | 0.58564 | 0.55488
|  | 21:40 | 26.0033 | 0.56408 | 0.55487
|  | 21:40 | 26.0044 | 0.54061 | 0.55487
|  | 21:40 | 26.0056 | 0.51713 | 0.55487
|  | 21:40 | 26.0067 | 0.50205 | 0.55487
|  | 21:40 | 26.0078 | 0.48696 | 0.55487
|  | 21:40 | 26.0089 | 0.46771 | 0.55486
|  | 21:40 | 26.01 | 0.4443 | 0.55486
|  | 21:40 | 26.0111 | 0.4209 | 0.55486
|  | 21:40 | 26.0122 | 0.38558 | 0.55486
|  | 21:40 | 26.0133 | 0.35026 | 0.55485
|  | 21:40 | 26.0144 | 0.31233 | 0.55485
|  | 21:40 | 26.0156 | 0.27179 | 0.55485
|  | 21:40 | 26.0167 | 0.23124 | 0.55485
|  | 21:40 | 26.0178 | 0.20065 | 0.55484
|  | 21:41 | 26.0189 | 0.17005 | 0.55484
|  | 21:41 | 26.02 | 0.14077 | 0.55484
|  | 21:41 | 26.0211 | 0.11281 | 0.55484
|  | 21:41 | 26.0222 | 0.084842 | 0.55484
|  | 21:41 | 26.0233 | 0.038603 | 0.55483
|  | 21:41 | 26.0244 | -0.0076366 | 0.55483
|  | 21:41 | 26.0256 | -0.047739 | 0.55483
|  | 21:41 | 26.0267 | -0.081703 | 0.55483
|  | 21:41 | 26.0278 | -0.11567 | 0.55482
|  | 21:41 | 26.0289 | -0.13646 | 0.55482
|  | 21:41 | 26.03 | -0.15725 | 0.55482
|  | 21:41 | 26.0311 | -0.18325 | 0.55482
|  | 21:41 | 26.0322 | -0.21444 | 0.55481
|  | 21:41 | 26.0333 | -0.24563 | 0.55481
|  | 21:41 | 26.0344 | -0.2745 | 0.55481
|  | 21:42 | 26.0356 | -0.30336 | 0.55481
|  | 21:42 | 26.0367 | -0.34175 | 0.55481
|  | 21:42 | 26.0378 | -0.38967 | 0.5548
|  | 21:42 | 26.0389 | -0.42638 | 0.5548
|  | 21:42 | 26.04 | -0.42948 | 0.5548
|  | 21:42 | 26.0411 | -0.43258 | 0.5548
|  | 21:42 | 26.0422 | -0.44921 | 0.55479
|  | 21:42 | 26.0433 | -0.47935 | 0.55479
|  | 21:42 | 26.0444 | -0.5095 | 0.55479
|  | 21:42 | 26.0456 | -0.53188 | 0.55479
|  | 21:42 | 26.0467 | -0.55427 | 0.55478
|  | 21:42 | 26.0478 | -0.57911 | 0.55478
|  | 21:42 | 26.0489 | -0.60641 | 0.55478
|  | 21:42 | 26.05 | -0.63371 | 0.55478
|  | 21:42 | 26.0511 | -0.64927 | 0.55478
|  | 21:43 | 26.0522 | -0.66484 | 0.55477
|  | 21:43 | 26.0533 | -0.6804 | 0.55477
|  | 21:43 | 26.0544 | -0.69596 | 0.55477
|  | 21:43 | 26.0556 | -0.71153 | 0.55477
|  | 21:43 | 26.0567 | -0.72418 | 0.55476
|  | 21:43 | 26.0578 | -0.73684 | 0.55476
|  | 21:43 | 26.0589 | -0.73522 | 0.55476
|  | 21:43 | 26.06 | -0.71932 | 0.55476
|  | 21:43 | 26.0611 | -0.70341 | 0.55475
|  | 21:43 | 26.0622 | -0.67074 | 0.55475
|  | 21:43 | 26.0633 | -0.63806 | 0.55475
|  | 21:43 | 26.0644 | -0.60994 | 0.55475
|  | 21:43 | 26.0656 | -0.58635 | 0.55475
|  | 21:43 | 26.0667 | -0.56277 | 0.55474
|  | 21:43 | 26.0678 | -0.53527 | 0.55474
|  | 21:44 | 26.0689 | -0.50776 | 0.55474
|  | 21:44 | 26.07 | -0.48763 | 0.55474
|  | 21:44 | 26.0711 | -0.48964 | 0.55473
|  | 21:44 | 26.0722 | -0.49165 | 0.55473
|  | 21:44 | 26.0733 | -0.49001 | 0.55473
|  | 21:44 | 26.0744 | -0.48837 | 0.55473
|  | 21:44 | 26.0756 | -0.48899 | 0.55472
|  | 21:44 | 26.0767 | -0.49188 | 0.55472
|  | 21:44 | 26.0778 | -0.49352 | 0.55472
|  | 21:44 | 26.0789 | -0.49142 | 0.55472
|  | 21:44 | 26.08 | -0.48932 | 0.55472
|  | 21:44 | 26.0811 | -0.49175 | 0.55471
|  | 21:44 | 26.0822 | -0.4987 | 0.55471
|  | 21:44 | 26.0833 | -0.50565 | 0.55471
|  | 21:44 | 26.0844 | -0.50288 | 0.55471
|  | 21:45 | 26.0856 | -0.50011 | 0.5547
|  | 21:45 | 26.0867 | -0.48826 | 0.5547
|  | 21:45 | 26.0878 | -0.46731 | 0.5547
|  | 21:45 | 26.0889 | -0.44636 | 0.5547
|  | 21:45 | 26.09 | -0.413 | 0.55469
|  | 21:45 | 26.0911 | -0.37965 | 0.55469
|  | 21:45 | 26.0922 | -0.35026 | 0.55469
|  | 21:45 | 26.0933 | -0.32485 | 0.55469
|  | 21:45 | 26.0944 | -0.29944 | 0.55469
|  | 21:45 | 26.0956 | -0.27642 | 0.55468
|  | 21:45 | 26.0967 | -0.2534 | 0.55468
|  | 21:45 | 26.0978 | -0.236 | 0.55468
|  | 21:45 | 26.0989 | -0.22421 | 0.55468
|  | 21:45 | 26.1 | -0.21242 | 0.55467
|  | 21:45 | 26.1011 | -0.18995 | 0.55467
|  | 21:46 | 26.1022 | -0.16749 | 0.55467
|  | 21:46 | 26.1033 | -0.14283 | 0.55467
|  | 21:46 | 26.1044 | -0.11597 | 0.55466
|  | 21:46 | 26.1056 | -0.089118 | 0.55466
|  | 21:46 | 26.1067 | -0.051508 | 0.55466
|  | 21:46 | 26.1078 | -0.013898 | 0.55466
|  | 21:46 | 26.1089 | 0.024607 | 0.55466
|  | 21:46 | 26.11 | 0.064006 | 0.55465
|  | 21:46 | 26.1111 | 0.1034 | 0.55465
|  | 21:46 | 26.1122 | 0.12872 | 0.55465
|  | 21:46 | 26.1133 | 0.15403 | 0.55465
|  | 21:46 | 26.1144 | 0.16833 | 0.55464
|  | 21:46 | 26.1156 | 0.17161 | 0.55464
|  | 21:46 | 26.1167 | 0.1749 | 0.55464
|  | 21:46 | 26.1178 | 0.19225 | 0.55464
|  | 21:47 | 26.1189 | 0.2096 | 0.55463
|  | 21:47 | 26.12 | 0.23125 | 0.55463
|  | 21:47 | 26.1211 | 0.25433 | 0.55463
|  | 21:47 | 26.1222 | 0.28118 | 0.55463
|  | 21:47 | 26.1233 | 0.3193 | 0.55462
|  | 21:47 | 26.1244 | 0.35742 | 0.55462
|  | 21:47 | 26.1256 | 0.37481 | 0.55462
|  | 21:47 | 26.1267 | 0.37146 | 0.55462
|  | 21:47 | 26.1278 | 0.36812 | 0.55462
|  | 21:47 | 26.1289 | 0.36814 | 0.55461
|  | 21:47 | 26.13 | 0.36817 | 0.55461
|  | 21:47 | 26.1311 | 0.36493 | 0.55461
|  | 21:47 | 26.1322 | 0.35842 | 0.55461
|  | 21:47 | 26.1333 | 0.35192 | 0.5546
|  | 21:47 | 26.1344 | 0.35745 | 0.5546
|  | 21:48 | 26.1356 | 0.36298 | 0.5546
|  | 21:48 | 26.1367 | 0.38439 | 0.5546
|  | 21:48 | 26.1378 | 0.42166 | 0.55459
|  | 21:48 | 26.1389 | 0.45893 | 0.55459
|  | 21:48 | 26.14 | 0.50834 | 0.55459
|  | 21:48 | 26.1411 | 0.55774 | 0.55459
|  | 21:48 | 26.1422 | 0.59714 | 0.55459
|  | 21:48 | 26.1433 | 0.62655 | 0.55458
|  | 21:48 | 26.1444 | 0.65595 | 0.55458
|  | 21:48 | 26.1456 | 0.68535 | 0.55458
|  | 21:48 | 26.1467 | 0.71475 | 0.55458
|  | 21:48 | 26.1478 | 0.7405 | 0.55457
|  | 21:48 | 26.1489 | 0.7626 | 0.55457
|  | 21:48 | 26.15 | 0.7847 | 0.55457
|  | 21:48 | 26.1511 | 0.78996 | 0.55457
|  | 21:49 | 26.1522 | 0.79522 | 0.55456
|  | 21:49 | 26.1533 | 0.80048 | 0.55456
|  | 21:49 | 26.1544 | 0.80574 | 0.55456
|  | 21:49 | 26.1556 | 0.811 | 0.55456
|  | 21:49 | 26.1567 | 0.80302 | 0.55456
|  | 21:49 | 26.1578 | 0.79504 | 0.55455
|  | 21:49 | 26.1589 | 0.78335 | 0.55455
|  | 21:49 | 26.16 | 0.76794 | 0.55455
|  | 21:49 | 26.1611 | 0.75254 | 0.55455
|  | 21:49 | 26.1622 | 0.73713 | 0.55454
|  | 21:49 | 26.1633 | 0.72173 | 0.55454
|  | 21:49 | 26.1644 | 0.70357 | 0.55454
|  | 21:49 | 26.1656 | 0.68266 | 0.55454
|  | 21:49 | 26.1667 | 0.66175 | 0.55453
|  | 21:49 | 26.1678 | 0.62242 | 0.55453
|  | 21:50 | 26.1689 | 0.58309 | 0.55453
|  | 21:50 | 26.17 | 0.54171 | 0.55453
|  | 21:50 | 26.1711 | 0.49829 | 0.55453
|  | 21:50 | 26.1722 | 0.45486 | 0.55452
|  | 21:50 | 26.1733 | 0.42925 | 0.55452
|  | 21:50 | 26.1744 | 0.40363 | 0.55452
|  | 21:50 | 26.1756 | 0.37379 | 0.55452
|  | 21:50 | 26.1767 | 0.33971 | 0.55451
|  | 21:50 | 26.1778 | 0.30564 | 0.55451
|  | 21:50 | 26.1789 | 0.27379 | 0.55451
|  | 21:50 | 26.18 | 0.24194 | 0.55451
|  | 21:50 | 26.1811 | 0.22435 | 0.5545
|  | 21:50 | 26.1822 | 0.22102 | 0.5545
|  | 21:50 | 26.1833 | 0.21769 | 0.5545
|  | 21:50 | 26.1844 | 0.20566 | 0.5545
|  | 21:51 | 26.1856 | 0.19362 | 0.5545
|  | 21:51 | 26.1867 | 0.18466 | 0.55449
|  | 21:51 | 26.1878 | 0.17879 | 0.55449
|  | 21:51 | 26.1889 | 0.17291 | 0.55449
|  | 21:51 | 26.19 | 0.16918 | 0.55449
|  | 21:51 | 26.1911 | 0.16545 | 0.55448
|  | 21:51 | 26.1922 | 0.15742 | 0.55448
|  | 21:51 | 26.1933 | 0.14511 | 0.55448
|  | 21:51 | 26.1944 | 0.13279 | 0.55448
|  | 21:51 | 26.1956 | 0.11944 | 0.55447
|  | 21:51 | 26.1967 | 0.10609 | 0.55447
|  | 21:51 | 26.1978 | 0.093734 | 0.55447
|  | 21:51 | 26.1989 | 0.082374 | 0.55447
|  | 21:51 | 26.2 | 0.071013 | 0.55447
|  | 21:51 | 26.2011 | 0.066403 | 0.55446
|  | 21:52 | 26.2022 | 0.061792 | 0.55446
|  | 21:52 | 26.2033 | 0.057755 | 0.55446
|  | 21:52 | 26.2044 | 0.05429 | 0.55446
|  | 21:52 | 26.2056 | 0.050825 | 0.55445
|  | 21:52 | 26.2067 | 0.032276 | 0.55445
|  | 21:52 | 26.2078 | 0.013726 | 0.55445
|  | 21:52 | 26.2089 | -0.0155 | 0.55445
|  | 21:52 | 26.21 | -0.055402 | 0.55444
|  | 21:52 | 26.2111 | -0.095305 | 0.55444
|  | 21:52 | 26.2122 | -0.1476 | 0.55444
|  | 21:52 | 26.2133 | -0.19989 | 0.55444
|  | 21:52 | 26.2144 | -0.25319 | 0.55444
|  | 21:52 | 26.2156 | -0.30752 | 0.55443
|  | 21:52 | 26.2167 | -0.36184 | 0.55443
|  | 21:52 | 26.2178 | -0.40614 | 0.55443
|  | 21:53 | 26.2189 | -0.45044 | 0.55443
|  | 21:53 | 26.22 | -0.48112 | 0.55442
|  | 21:53 | 26.2211 | -0.49819 | 0.55442
|  | 21:53 | 26.2222 | -0.51526 | 0.55442
|  | 21:53 | 26.2233 | -0.54146 | 0.55442
|  | 21:53 | 26.2244 | -0.56767 | 0.55441
|  | 21:53 | 26.2256 | -0.58665 | 0.55441
|  | 21:53 | 26.2267 | -0.59843 | 0.55441
|  | 21:53 | 26.2278 | -0.6102 | 0.55441
|  | 21:53 | 26.2289 | -0.60745 | 0.55441
|  | 21:53 | 26.23 | -0.6047 | 0.5544
|  | 21:53 | 26.2311 | -0.60347 | 0.5544
|  | 21:53 | 26.2322 | -0.60376 | 0.5544
|  | 21:53 | 26.2333 | -0.60405 | 0.5544
|  | 21:53 | 26.2344 | -0.60336 | 0.55439
|  | 21:54 | 26.2356 | -0.60266 | 0.55439
|  | 21:54 | 26.2367 | -0.60291 | 0.55439
|  | 21:54 | 26.2378 | -0.60599 | 0.55439
|  | 21:54 | 26.2389 | -0.60906 | 0.55438
|  | 21:54 | 26.24 | -0.61077 | 0.55438
|  | 21:54 | 26.2411 | -0.61248 | 0.55438
|  | 21:54 | 26.2422 | -0.6045 | 0.55438
|  | 21:54 | 26.2433 | -0.58685 | 0.55437
|  | 21:54 | 26.2444 | -0.56919 | 0.55437
|  | 21:54 | 26.2456 | -0.55636 | 0.55437
|  | 21:54 | 26.2467 | -0.54352 | 0.55437
|  | 21:54 | 26.2478 | -0.53564 | 0.55437
|  | 21:54 | 26.2489 | -0.53272 | 0.55436
|  | 21:54 | 26.25 | -0.5298 | 0.55436
|  | 21:54 | 26.2511 | -0.529 | 0.55436
|  | 21:55 | 26.2522 | -0.52819 | 0.55436
|  | 21:55 | 26.2533 | -0.53152 | 0.55435
|  | 21:55 | 26.2544 | -0.539 | 0.55435
|  | 21:55 | 26.2556 | -0.54647 | 0.55435
|  | 21:55 | 26.2567 | -0.54635 | 0.55435
|  | 21:55 | 26.2578 | -0.54623 | 0.55434
|  | 21:55 | 26.2589 | -0.54252 | 0.55434
|  | 21:55 | 26.26 | -0.53522 | 0.55434
|  | 21:55 | 26.2611 | -0.52791 | 0.55434
|  | 21:55 | 26.2622 | -0.51653 | 0.55434
|  | 21:55 | 26.2633 | -0.50516 | 0.55433
|  | 21:55 | 26.2644 | -0.47674 | 0.55433
|  | 21:55 | 26.2656 | -0.43128 | 0.55433
|  | 21:55 | 26.2667 | -0.38582 | 0.55433
|  | 21:55 | 26.2678 | -0.34134 | 0.55432
|  | 21:56 | 26.2689 | -0.29686 | 0.55432
|  | 21:56 | 26.27 | -0.25636 | 0.55432
|  | 21:56 | 26.2711 | -0.21982 | 0.55432
|  | 21:56 | 26.2722 | -0.18329 | 0.55431
|  | 21:56 | 26.2733 | -0.16697 | 0.55431
|  | 21:56 | 26.2744 | -0.15066 | 0.55431
|  | 21:56 | 26.2756 | -0.13059 | 0.55431
|  | 21:56 | 26.2767 | -0.10676 | 0.55431
|  | 21:56 | 26.2778 | -0.082929 | 0.5543
|  | 21:56 | 26.2789 | -0.064992 | 0.5543
|  | 21:56 | 26.28 | -0.047054 | 0.5543
|  | 21:56 | 26.2811 | -0.033677 | 0.5543
|  | 21:56 | 26.2822 | -0.024861 | 0.55429
|  | 21:56 | 26.2833 | -0.016045 | 0.55429
|  | 21:56 | 26.2844 | -0.015577 | 0.55429
|  | 21:57 | 26.2856 | -0.01511 | 0.55429
|  | 21:57 | 26.2867 | -0.032247 | 0.55428
|  | 21:57 | 26.2878 | -0.066986 | 0.55428
|  | 21:57 | 26.2889 | -0.10173 | 0.55428
|  | 21:57 | 26.29 | -0.11422 | 0.55428
|  | 21:57 | 26.2911 | -0.12672 | 0.55428
|  | 21:57 | 26.2922 | -0.14071 | 0.55427
|  | 21:57 | 26.2933 | -0.15619 | 0.55427
|  | 21:57 | 26.2944 | -0.17167 | 0.55427
|  | 21:57 | 26.2956 | -0.18715 | 0.55427
|  | 21:57 | 26.2967 | -0.20263 | 0.55426
|  | 21:57 | 26.2978 | -0.22463 | 0.55426
|  | 21:57 | 26.2989 | -0.25316 | 0.55426
|  | 21:57 | 26.3 | -0.28168 | 0.55426
|  | 21:57 | 26.3011 | -0.29777 | 0.55425
|  | 21:58 | 26.3022 | -0.31386 | 0.55425
|  | 21:58 | 26.3033 | -0.31394 | 0.55425
|  | 21:58 | 26.3044 | -0.298 | 0.55425
|  | 21:58 | 26.3056 | -0.28207 | 0.55425
|  | 21:58 | 26.3067 | -0.26097 | 0.55424
|  | 21:58 | 26.3078 | -0.23987 | 0.55424
|  | 21:58 | 26.3089 | -0.2201 | 0.55424
|  | 21:58 | 26.31 | -0.20168 | 0.55424
|  | 21:58 | 26.3111 | -0.18325 | 0.55423
|  | 21:58 | 26.3122 | -0.16685 | 0.55423
|  | 21:58 | 26.3133 | -0.15045 | 0.55423
|  | 21:58 | 26.3144 | -0.13497 | 0.55423
|  | 21:58 | 26.3156 | -0.1204 | 0.55422
|  | 21:58 | 26.3167 | -0.10583 | 0.55422
|  | 21:58 | 26.3178 | -0.085856 | 0.55422
|  | 21:59 | 26.3189 | -0.065882 | 0.55422
|  | 21:59 | 26.32 | -0.057483 | 0.55422
|  | 21:59 | 26.3211 | -0.060658 | 0.55421
|  | 21:59 | 26.3222 | -0.063833 | 0.55421
|  | 21:59 | 26.3233 | -0.042603 | 0.55421
|  | 21:59 | 26.3244 | -0.021374 | 0.55421
|  | 21:59 | 26.3256 | -0.0021204 | 0.5542
|  | 21:59 | 26.3267 | 0.015157 | 0.5542
|  | 21:59 | 26.3278 | 0.032435 | 0.5542
|  | 21:59 | 26.3289 | 0.024561 | 0.5542
|  | 21:59 | 26.33 | 0.016687 | 0.55419
|  | 21:59 | 26.3311 | 0.012389 | 0.55419
|  | 21:59 | 26.3322 | 0.011665 | 0.55419
|  | 21:59 | 26.3333 | 0.010942 | 0.55419
|  | 21:59 | 26.3344 | 0.002515 | 0.55419
|  | 22:00 | 26.3356 | -0.0059115 | 0.55418
|  | 22:00 | 26.3367 | -0.026255 | 0.55418
|  | 22:00 | 26.3378 | -0.058516 | 0.55418
|  | 22:00 | 26.3389 | -0.090777 | 0.55418
|  | 22:00 | 26.34 | -0.1219 | 0.55417
|  | 22:00 | 26.3411 | -0.15302 | 0.55417
|  | 22:00 | 26.3422 | -0.18289 | 0.55417
|  | 22:00 | 26.3433 | -0.14425 | 0.55417
|  | 22:00 | 26.3444 | -0.12965 | 0.55416
|  | 22:00 | 26.3456 | -0.13601 | 0.55416
|  | 22:00 | 26.3467 | -0.14238 | 0.55416
|  | 22:00 | 26.3478 | -0.14874 | 0.55416
|  | 22:00 | 26.3489 | -0.15511 | 0.55416
|  | 22:00 | 26.35 | -0.16147 | 0.55415
|  | 22:00 | 26.3511 | -0.15001 | 0.55415
|  | 22:01 | 26.3522 | -0.13855 | 0.55415
|  | 22:01 | 26.3533 | -0.11353 | 0.55415
|  | 22:01 | 26.3544 | -0.083978 | 0.55414
|  | 22:01 | 26.3556 | -0.05443 | 0.55414
|  | 22:01 | 26.3567 | -0.032121 | 0.55414
|  | 22:01 | 26.3578 | -0.0098121 | 0.55414
|  | 22:01 | 26.3589 | 0.0050135 | 0.55413
|  | 22:01 | 26.36 | 0.012356 | 0.55413
|  | 22:01 | 26.3611 | 0.019698 | 0.55413
|  | 22:01 | 26.3622 | 0.0056427 | 0.55413
|  | 22:01 | 26.3633 | -0.0084124 | 0.55412
|  | 22:01 | 26.3644 | -0.016135 | 0.55412
|  | 22:01 | 26.3656 | -0.017526 | 0.55412
|  | 22:01 | 26.3667 | -0.018917 | 0.55412
|  | 22:01 | 26.3678 | -0.0074832 | 0.55412
|  | 22:02 | 26.3689 | 0.0039504 | 0.55411
|  | 22:02 | 26.37 | 0.016937 | 0.55411
|  | 22:02 | 26.3711 | 0.030441 | 0.55411
|  | 22:02 | 26.3722 | 0.043946 | 0.55411
|  | 22:02 | 26.3733 | 0.065859 | 0.5541
|  | 22:02 | 26.3744 | 0.087772 | 0.5541
|  | 22:02 | 26.3756 | 0.10268 | 0.5541
|  | 22:02 | 26.3767 | 0.11526 | 0.5541
|  | 22:02 | 26.3778 | 0.12783 | 0.55409
|  | 22:02 | 26.3789 | 0.13629 | 0.55409
|  | 22:02 | 26.38 | 0.14474 | 0.55409
|  | 22:02 | 26.3811 | 0.1681 | 0.55409
|  | 22:02 | 26.3822 | 0.20635 | 0.55409
|  | 22:02 | 26.3833 | 0.2446 | 0.55408
|  | 22:02 | 26.3844 | 0.28614 | 0.55408
|  | 22:03 | 26.3856 | 0.32769 | 0.55408
|  | 22:03 | 26.3867 | 0.37177 | 0.55408
|  | 22:03 | 26.3878 | 0.41839 | 0.55407
|  | 22:03 | 26.3889 | 0.4646 | 0.55407
|  | 22:03 | 26.39 | 0.50955 | 0.55407
|  | 22:03 | 26.3911 | 0.55451 | 0.55407
|  | 22:03 | 26.3922 | 0.60292 | 0.55406
|  | 22:03 | 26.3933 | 0.65481 | 0.55406
|  | 22:03 | 26.3944 | 0.70669 | 0.55406
|  | 22:03 | 26.3956 | 0.72091 | 0.55406
|  | 22:03 | 26.3967 | 0.73513 | 0.55406
|  | 22:03 | 26.3978 | 0.73769 | 0.55405
|  | 22:03 | 26.3989 | 0.7286 | 0.55405
|  | 22:03 | 26.4 | 0.71951 | 0.55405
|  | 22:03 | 26.4011 | 0.69733 | 0.55405
|  | 22:04 | 26.4022 | 0.66208 | 0.55404
|  | 22:04 | 26.4033 | 0.6161 | 0.55404
|  | 22:04 | 26.4044 | 0.5594 | 0.55404
|  | 22:04 | 26.4056 | 0.50271 | 0.55404
|  | 22:04 | 26.4067 | 0.43484 | 0.55403
|  | 22:04 | 26.4078 | 0.36696 | 0.55403
|  | 22:04 | 26.4089 | 0.2997 | 0.55403
|  | 22:04 | 26.41 | 0.23306 | 0.55403
|  | 22:04 | 26.4111 | 0.16641 | 0.55403
|  | 22:04 | 26.4122 | 0.1269 | 0.55402
|  | 22:04 | 26.4133 | 0.087393 | 0.55402
|  | 22:04 | 26.4144 | 0.062752 | 0.55402
|  | 22:04 | 26.4156 | 0.052981 | 0.55402
|  | 22:04 | 26.4167 | 0.04321 | 0.55401
|  | 22:04 | 26.4178 | 0.031374 | 0.55401
|  | 22:05 | 26.4189 | 0.019538 | 0.55401
|  | 22:05 | 26.42 | 0.0014623 | 0.55401
|  | 22:05 | 26.4211 | -0.022852 | 0.554
|  | 22:05 | 26.4222 | -0.047167 | 0.554
|  | 22:05 | 26.4233 | -0.057435 | 0.554
|  | 22:05 | 26.4244 | -0.067703 | 0.554
|  | 22:05 | 26.4256 | -0.080728 | 0.554
|  | 22:05 | 26.4267 | -0.096511 | 0.55399
|  | 22:05 | 26.4278 | -0.11229 | 0.55399
|  | 22:05 | 26.4289 | -0.14181 | 0.55399
|  | 22:05 | 26.43 | -0.17133 | 0.55399
|  | 22:05 | 26.4311 | -0.19213 | 0.55398
|  | 22:05 | 26.4322 | -0.21003 | 0.55398
|  | 22:05 | 26.4333 | -0.22794 | 0.55398
|  | 22:05 | 26.4344 | -0.25217 | 0.55398
|  | 22:06 | 26.4356 | -0.2764 | 0.55397
|  | 22:06 | 26.4367 | -0.29614 | 0.55397
|  | 22:06 | 26.4378 | -0.31141 | 0.55397
|  | 22:06 | 26.4389 | -0.32668 | 0.55397
|  | 22:06 | 26.44 | -0.33634 | 0.55397
|  | 22:06 | 26.4411 | -0.346 | 0.55396
|  | 22:06 | 26.4422 | -0.35417 | 0.55396
|  | 22:06 | 26.4433 | -0.36184 | 0.55396
|  | 22:06 | 26.4444 | -0.3695 | 0.55396
|  | 22:06 | 26.4456 | -0.38223 | 0.55395
|  | 22:06 | 26.4467 | -0.39495 | 0.55395
|  | 22:06 | 26.4478 | -0.41366 | 0.55395
|  | 22:06 | 26.4489 | -0.43836 | 0.55395
|  | 22:06 | 26.45 | -0.46307 | 0.55394
|  | 22:06 | 26.4511 | -0.49142 | 0.55394
|  | 22:07 | 26.4522 | -0.51976 | 0.55394
|  | 22:07 | 26.4533 | -0.53557 | 0.55394
|  | 22:07 | 26.4544 | -0.53885 | 0.55394
|  | 22:07 | 26.4556 | -0.54212 | 0.55393
|  | 22:07 | 26.4567 | -0.52588 | 0.55393
|  | 22:07 | 26.4578 | -0.50964 | 0.55393
|  | 22:07 | 26.4589 | -0.48512 | 0.55393
|  | 22:07 | 26.46 | -0.45232 | 0.55392
|  | 22:07 | 26.4611 | -0.41952 | 0.55392
|  | 22:07 | 26.4622 | -0.39896 | 0.55392
|  | 22:07 | 26.4633 | -0.3784 | 0.55392
|  | 22:07 | 26.4644 | -0.36069 | 0.55391
|  | 22:07 | 26.4656 | -0.34581 | 0.55391
|  | 22:07 | 26.4667 | -0.33094 | 0.55391
|  | 22:07 | 26.4678 | -0.31151 | 0.55391
|  | 22:08 | 26.4689 | -0.29208 | 0.55391
|  | 22:08 | 26.47 | -0.26401 | 0.5539
|  | 22:08 | 26.4711 | -0.2273 | 0.5539
|  | 22:08 | 26.4722 | -0.1906 | 0.5539
|  | 22:08 | 26.4733 | -0.15165 | 0.5539
|  | 22:08 | 26.4744 | -0.1127 | 0.55389
|  | 22:08 | 26.4756 | -0.070709 | 0.55389
|  | 22:08 | 26.4767 | -0.025681 | 0.55389
|  | 22:08 | 26.4778 | 0.019348 | 0.55389
|  | 22:08 | 26.4789 | 0.066808 | 0.55388
|  | 22:08 | 26.48 | 0.11427 | 0.55388
|  | 22:08 | 26.4811 | 0.14906 | 0.55388
|  | 22:08 | 26.4822 | 0.17962 | 0.55388
|  | 22:08 | 26.4833 | 0.21018 | 0.55387
|  | 22:08 | 26.4844 | 0.22659 | 0.55387
|  | 22:09 | 26.4856 | 0.243 | 0.55387
|  | 22:09 | 26.4867 | 0.26015 | 0.55387
|  | 22:09 | 26.4878 | 0.27804 | 0.55387
|  | 22:09 | 26.4889 | 0.29593 | 0.55386
|  | 22:09 | 26.49 | 0.34579 | 0.55386
|  | 22:09 | 26.4911 | 0.39566 | 0.55386
|  | 22:09 | 26.4922 | 0.41648 | 0.55386
|  | 22:09 | 26.4933 | 0.42761 | 0.55385
|  | 22:09 | 26.4944 | 0.43875 | 0.55385
|  | 22:09 | 26.4956 | 0.48488 | 0.55385
|  | 22:09 | 26.4967 | 0.53101 | 0.55385
|  | 22:09 | 26.4978 | 0.56431 | 0.55384
|  | 22:09 | 26.4989 | 0.58479 | 0.55384
|  | 22:09 | 26.5 | 0.60527 | 0.55384
|  | 22:09 | 26.5011 | 0.62576 | 0.55384
|  | 22:10 | 26.5022 | 0.64624 | 0.55384
|  | 22:10 | 26.5033 | 0.65386 | 0.55383
|  | 22:10 | 26.5044 | 0.64862 | 0.55383
|  | 22:10 | 26.5056 | 0.64337 | 0.55383
|  | 22:10 | 26.5067 | 0.61858 | 0.55383
|  | 22:10 | 26.5078 | 0.59379 | 0.55382
|  | 22:10 | 26.5089 | 0.57945 | 0.55382
|  | 22:10 | 26.51 | 0.5686 | 0.55382
|  | 22:10 | 26.5111 | 0.55774 | 0.55382
|  | 22:10 | 26.5122 | 0.53406 | 0.55381
|  | 22:10 | 26.5133 | 0.51037 | 0.55381
|  | 22:10 | 26.5144 | 0.48484 | 0.55381
|  | 22:10 | 26.5156 | 0.45747 | 0.55381
|  | 22:10 | 26.5167 | 0.43009 | 0.55381
|  | 22:10 | 26.5178 | 0.40661 | 0.5538
|  | 22:11 | 26.5189 | 0.38313 | 0.5538
|  | 22:11 | 26.52 | 0.35578 | 0.5538
|  | 22:11 | 26.5211 | 0.32455 | 0.5538
|  | 22:11 | 26.5222 | 0.29332 | 0.55379
|  | 22:11 | 26.5233 | 0.24981 | 0.55379
|  | 22:11 | 26.5244 | 0.20629 | 0.55379
|  | 22:11 | 26.5256 | 0.16355 | 0.55379
|  | 22:11 | 26.5267 | 0.12106 | 0.55378
|  | 22:11 | 26.5278 | 0.078582 | 0.55378
|  | 22:11 | 26.5289 | 0.031632 | 0.55378
|  | 22:11 | 26.53 | -0.015318 | 0.55378
|  | 22:11 | 26.5311 | -0.035845 | 0.55378
|  | 22:11 | 26.5322 | -0.047565 | 0.55377
|  | 22:11 | 26.5333 | -0.059285 | 0.55377
|  | 22:11 | 26.5344 | -0.081598 | 0.55377
|  | 22:12 | 26.5356 | -0.10391 | 0.55377
|  | 22:12 | 26.5367 | -0.13323 | 0.55376
|  | 22:12 | 26.5378 | -0.16956 | 0.55376
|  | 22:12 | 26.5389 | -0.20588 | 0.55376
|  | 22:12 | 26.54 | -0.24997 | 0.55376
|  | 22:12 | 26.5411 | -0.29406 | 0.55375
|  | 22:12 | 26.5422 | -0.33234 | 0.55375
|  | 22:12 | 26.5433 | -0.3648 | 0.55375
|  | 22:12 | 26.5444 | -0.39726 | 0.55375
|  | 22:12 | 26.5456 | -0.42357 | 0.55375
|  | 22:12 | 26.5467 | -0.44987 | 0.55374
|  | 22:12 | 26.5478 | -0.46847 | 0.55374
|  | 22:12 | 26.5489 | -0.47935 | 0.55374
|  | 22:12 | 26.55 | -0.49023 | 0.55374
|  | 22:12 | 26.5511 | -0.5088 | 0.55373
|  | 22:13 | 26.5522 | -0.52738 | 0.55373
|  | 22:13 | 26.5533 | -0.54595 | 0.55373
|  | 22:13 | 26.5544 | -0.56452 | 0.55373
|  | 22:13 | 26.5556 | -0.58056 | 0.55372
|  | 22:13 | 26.5567 | -0.58899 | 0.55372
|  | 22:13 | 26.5578 | -0.59741 | 0.55372
|  | 22:13 | 26.5589 | -0.60464 | 0.55372
|  | 22:13 | 26.56 | -0.61068 | 0.55372
|  | 22:13 | 26.5611 | -0.61671 | 0.55371
|  | 22:13 | 26.5622 | -0.62274 | 0.55371
|  | 22:13 | 26.5633 | -0.62878 | 0.55371
|  | 22:13 | 26.5644 | -0.64556 | 0.55371
|  | 22:13 | 26.5656 | -0.67309 | 0.5537
|  | 22:13 | 26.5667 | -0.70062 | 0.5537
|  | 22:13 | 26.5678 | -0.7259 | 0.5537
|  | 22:14 | 26.5689 | -0.75118 | 0.5537
|  | 22:14 | 26.57 | -0.76373 | 0.55369
|  | 22:14 | 26.5711 | -0.76355 | 0.55369
|  | 22:14 | 26.5722 | -0.76336 | 0.55369
|  | 22:14 | 26.5733 | -0.74165 | 0.55369
|  | 22:14 | 26.5744 | -0.71995 | 0.55369
|  | 22:14 | 26.5756 | -0.69328 | 0.55368
|  | 22:14 | 26.5767 | -0.66166 | 0.55368
|  | 22:14 | 26.5778 | -0.63004 | 0.55368
|  | 22:14 | 26.5789 | -0.60123 | 0.55368
|  | 22:14 | 26.58 | -0.57243 | 0.55367
|  | 22:14 | 26.5811 | -0.55891 | 0.55367
|  | 22:14 | 26.5822 | -0.56068 | 0.55367
|  | 22:14 | 26.5833 | -0.56245 | 0.55367
|  | 22:14 | 26.5844 | -0.54412 | 0.55366
|  | 22:15 | 26.5856 | -0.52578 | 0.55366
|  | 22:15 | 26.5867 | -0.51626 | 0.55366
|  | 22:15 | 26.5878 | -0.51554 | 0.55366
|  | 22:15 | 26.5889 | -0.51483 | 0.55366
|  | 22:15 | 26.59 | -0.51658 | 0.55365
|  | 22:15 | 26.5911 | -0.51832 | 0.55365
|  | 22:15 | 26.5922 | -0.51742 | 0.55365
|  | 22:15 | 26.5933 | -0.51387 | 0.55365
|  | 22:15 | 26.5944 | -0.51032 | 0.55364
|  | 22:15 | 26.5956 | -0.49265 | 0.55364
|  | 22:15 | 26.5967 | -0.47497 | 0.55364
|  | 22:15 | 26.5978 | -0.4573 | 0.55364
|  | 22:15 | 26.5989 | -0.43963 | 0.55363
|  | 22:15 | 26.6 | -0.42195 | 0.55363
|  | 22:15 | 26.6011 | -0.40033 | 0.55363
|  | 22:16 | 26.6022 | -0.3787 | 0.55363
|  | 22:16 | 26.6033 | -0.35755 | 0.55362
|  | 22:16 | 26.6044 | -0.33687 | 0.55362
|  | 22:16 | 26.6056 | -0.31619 | 0.55362
|  | 22:16 | 26.6067 | -0.27026 | 0.55362
|  | 22:16 | 26.6078 | -0.22432 | 0.55362
|  | 22:16 | 26.6089 | -0.18079 | 0.55361
|  | 22:16 | 26.61 | -0.13806 | 0.55361
|  | 22:16 | 26.6111 | -0.095326 | 0.55361
|  | 22:16 | 26.6122 | -0.056057 | 0.55361
|  | 22:16 | 26.6133 | -0.016788 | 0.5536
|  | 22:16 | 26.6144 | 0.015659 | 0.5536
|  | 22:16 | 26.6156 | 0.041284 | 0.5536
|  | 22:16 | 26.6167 | 0.066908 | 0.5536
|  | 22:16 | 26.6178 | 0.067889 | 0.55359
|  | 22:17 | 26.6189 | 0.06887 | 0.55359
|  | 22:17 | 26.62 | 0.077604 | 0.55359
|  | 22:17 | 26.6211 | 0.094089 | 0.55359
|  | 22:17 | 26.6222 | 0.11057 | 0.55359
|  | 22:17 | 26.6233 | 0.13697 | 0.55358
|  | 22:17 | 26.6244 | 0.16337 | 0.55358
|  | 22:17 | 26.6256 | 0.18555 | 0.55358
|  | 22:17 | 26.6267 | 0.2035 | 0.55358
|  | 22:17 | 26.6278 | 0.22146 | 0.55357
|  | 22:17 | 26.6289 | 0.25483 | 0.55357
|  | 22:17 | 26.63 | 0.2882 | 0.55357
|  | 22:17 | 26.6311 | 0.30837 | 0.55357
|  | 22:17 | 26.6322 | 0.31533 | 0.55356
|  | 22:17 | 26.6333 | 0.32229 | 0.55356
|  | 22:17 | 26.6344 | 0.34371 | 0.55356
|  | 22:18 | 26.6356 | 0.36513 | 0.55356
|  | 22:18 | 26.6367 | 0.39495 | 0.55356
|  | 22:18 | 26.6378 | 0.43316 | 0.55355
|  | 22:18 | 26.6389 | 0.47137 | 0.55355
|  | 22:18 | 26.64 | 0.50421 | 0.55355
|  | 22:18 | 26.6411 | 0.53705 | 0.55355
|  | 22:18 | 26.6422 | 0.56677 | 0.55354
|  | 22:18 | 26.6433 | 0.59337 | 0.55354
|  | 22:18 | 26.6444 | 0.61996 | 0.55354
|  | 22:18 | 26.6456 | 0.63533 | 0.55354
|  | 22:18 | 26.6467 | 0.6507 | 0.55353
|  | 22:18 | 26.6478 | 0.67478 | 0.55353
|  | 22:18 | 26.6489 | 0.70756 | 0.55353
|  | 22:18 | 26.65 | 0.74033 | 0.55353
|  | 22:18 | 26.6511 | 0.7188 | 0.55353
|  | 22:19 | 26.6522 | 0.69726 | 0.55352
|  | 22:19 | 26.6533 | 0.69924 | 0.55352
|  | 22:19 | 26.6544 | 0.72473 | 0.55352
|  | 22:19 | 26.6556 | 0.75023 | 0.55352
|  | 22:19 | 26.6567 | 0.75876 | 0.55351
|  | 22:19 | 26.6578 | 0.76729 | 0.55351
|  | 22:19 | 26.6589 | 0.77299 | 0.55351
|  | 22:19 | 26.66 | 0.77774 | 0.55351
|  | 22:19 | 26.6611 | 0.7825 | 0.5535
|  | 22:19 | 26.6622 | 0.76741 | 0.5535
|  | 22:19 | 26.6633 | 0.75232 | 0.5535
|  | 22:19 | 26.6644 | 0.7296 | 0.5535
|  | 22:19 | 26.6656 | 0.69925 | 0.5535
|  | 22:19 | 26.6667 | 0.6689 | 0.55349
|  | 22:19 | 26.6678 | 0.62576 | 0.55349
|  | 22:20 | 26.6689 | 0.58261 | 0.55349
|  | 22:20 | 26.67 | 0.54949 | 0.55349
|  | 22:20 | 26.6711 | 0.5264 | 0.55348
|  | 22:20 | 26.6722 | 0.50331 | 0.55348
|  | 22:20 | 26.6733 | 0.4765 | 0.55348
|  | 22:20 | 26.6744 | 0.44968 | 0.55348
|  | 22:20 | 26.6756 | 0.4167 | 0.55347
|  | 22:20 | 26.6767 | 0.37755 | 0.55347
|  | 22:20 | 26.6778 | 0.33841 | 0.55347
|  | 22:20 | 26.6789 | 0.29386 | 0.55347
|  | 22:20 | 26.68 | 0.24932 | 0.55347
|  | 22:20 | 26.6811 | 0.21533 | 0.55346
|  | 22:20 | 26.6822 | 0.19189 | 0.55346
|  | 22:20 | 26.6833 | 0.16844 | 0.55346
|  | 22:20 | 26.6844 | 0.16499 | 0.55346
|  | 22:21 | 26.6856 | 0.16153 | 0.55345
|  | 22:21 | 26.6867 | 0.15986 | 0.55345
|  | 22:21 | 26.6878 | 0.15996 | 0.55345
|  | 22:21 | 26.6889 | 0.16005 | 0.55345
|  | 22:21 | 26.69 | 0.14796 | 0.55344
|  | 22:21 | 26.6911 | 0.13587 | 0.55344
|  | 22:21 | 26.6922 | 0.12378 | 0.55344
|  | 22:21 | 26.6933 | 0.1117 | 0.55344
|  | 22:21 | 26.6944 | 0.099605 | 0.55344
|  | 22:21 | 26.6956 | 0.079349 | 0.55343
|  | 22:21 | 26.6967 | 0.059092 | 0.55343
|  | 22:21 | 26.6978 | 0.042185 | 0.55343
|  | 22:21 | 26.6989 | 0.028626 | 0.55343
|  | 22:21 | 26.7 | 0.015067 | 0.55342
|  | 22:21 | 26.7011 | 0.017848 | 0.55342
|  | 22:22 | 26.7022 | 0.020629 | 0.55342
|  | 22:22 | 26.7033 | 0.02341 | 0.55342
|  | 22:22 | 26.7044 | 0.02619 | 0.55341
|  | 22:22 | 26.7056 | 0.028971 | 0.55341
|  | 22:22 | 26.7067 | 0.040168 | 0.55341
|  | 22:22 | 26.7078 | 0.051364 | 0.55341
|  | 22:22 | 26.7089 | 0.060832 | 0.55341
|  | 22:22 | 26.71 | 0.068571 | 0.5534
|  | 22:22 | 26.7111 | 0.076309 | 0.5534
|  | 22:22 | 26.7122 | 0.077437 | 0.5534
|  | 22:22 | 26.7133 | 0.078564 | 0.5534
|  | 22:22 | 26.7144 | 0.080322 | 0.55339
|  | 22:22 | 26.7156 | 0.082711 | 0.55339
|  | 22:22 | 26.7167 | 0.085099 | 0.55339
|  | 22:22 | 26.7178 | 0.082506 | 0.55339
|  | 22:23 | 26.7189 | 0.079913 | 0.55338
|  | 22:23 | 26.72 | 0.07732 | 0.55338
|  | 22:23 | 26.7211 | 0.074727 | 0.55338
|  | 22:23 | 26.7222 | 0.072134 | 0.55338
|  | 22:23 | 26.7233 | 0.05751 | 0.55337
|  | 22:23 | 26.7244 | 0.042887 | 0.55337
|  | 22:23 | 26.7256 | 0.041184 | 0.55337
|  | 22:23 | 26.7267 | 0.052402 | 0.55337
|  | 22:23 | 26.7278 | 0.063621 | 0.55337
|  | 22:23 | 26.7289 | 0.059618 | 0.55336
|  | 22:23 | 26.73 | 0.055615 | 0.55336
|  | 22:23 | 26.7311 | 0.053782 | 0.55336
|  | 22:23 | 26.7322 | 0.054119 | 0.55336
|  | 22:23 | 26.7333 | 0.054456 | 0.55335
|  | 22:23 | 26.7344 | 0.052728 | 0.55335
|  | 22:24 | 26.7356 | 0.051 | 0.55335
|  | 22:24 | 26.7367 | 0.053232 | 0.55335
|  | 22:24 | 26.7378 | 0.059425 | 0.55334
|  | 22:24 | 26.7389 | 0.065617 | 0.55334
|  | 22:24 | 26.74 | 0.089973 | 0.55334
|  | 22:24 | 26.7411 | 0.11433 | 0.55334
|  | 22:24 | 26.7422 | 0.13104 | 0.55334
|  | 22:24 | 26.7433 | 0.14009 | 0.55333
|  | 22:24 | 26.7444 | 0.14915 | 0.55333
|  | 22:24 | 26.7456 | 0.14294 | 0.55333
|  | 22:24 | 26.7467 | 0.13674 | 0.55333
|  | 22:24 | 26.7478 | 0.13903 | 0.55332
|  | 22:24 | 26.7489 | 0.14981 | 0.55332
|  | 22:24 | 26.75 | 0.16059 | 0.55332
|  | 22:24 | 26.7511 | 0.17604 | 0.55332
|  | 22:25 | 26.7522 | 0.1915 | 0.55331
|  | 22:25 | 26.7533 | 0.20614 | 0.55331
|  | 22:25 | 26.7544 | 0.21996 | 0.55331
|  | 22:25 | 26.7556 | 0.23378 | 0.55331
|  | 22:25 | 26.7567 | 0.22649 | 0.55331
|  | 22:25 | 26.7578 | 0.2192 | 0.5533
|  | 22:25 | 26.7589 | 0.2103 | 0.5533
|  | 22:25 | 26.76 | 0.1998 | 0.5533
|  | 22:25 | 26.7611 | 0.18929 | 0.5533
|  | 22:25 | 26.7622 | 0.16969 | 0.55329
|  | 22:25 | 26.7633 | 0.15009 | 0.55329
|  | 22:25 | 26.7644 | 0.12595 | 0.55329
|  | 22:25 | 26.7656 | 0.09729 | 0.55329
|  | 22:25 | 26.7667 | 0.068625 | 0.55328
|  | 22:25 | 26.7678 | 0.07361 | 0.55328
|  | 22:26 | 26.7689 | 0.078594 | 0.55328
|  | 22:26 | 26.77 | 0.072993 | 0.55328
|  | 22:26 | 26.7711 | 0.056805 | 0.55328
|  | 22:26 | 26.7722 | 0.040617 | 0.55327
|  | 22:26 | 26.7733 | 0.014632 | 0.55327
|  | 22:26 | 26.7744 | -0.011353 | 0.55327
|  | 22:26 | 26.7756 | -0.035552 | 0.55327
|  | 22:26 | 26.7767 | -0.057963 | 0.55326
|  | 22:26 | 26.7778 | -0.080375 | 0.55326
|  | 22:26 | 26.7789 | -0.065543 | 0.55326
|  | 22:26 | 26.78 | -0.050712 | 0.55326
|  | 22:26 | 26.7811 | -0.031837 | 0.55325
|  | 22:26 | 26.7822 | -0.0089175 | 0.55325
|  | 22:26 | 26.7833 | 0.014002 | 0.55325
|  | 22:26 | 26.7844 | 0.0028253 | 0.55325
|  | 22:27 | 26.7856 | -0.0083511 | 0.55325
|  | 22:27 | 26.7867 | -0.022928 | 0.55324
|  | 22:27 | 26.7878 | -0.040906 | 0.55324
|  | 22:27 | 26.7889 | -0.058884 | 0.55324
|  | 22:27 | 26.79 | -0.068746 | 0.55324
|  | 22:27 | 26.7911 | -0.078609 | 0.55323
|  | 22:27 | 26.7922 | -0.07932 | 0.55323
|  | 22:27 | 26.7933 | -0.076982 | 0.55323
|  | 22:27 | 26.7944 | -0.074643 | 0.55323
|  | 22:27 | 26.7956 | -0.075455 | 0.55322
|  | 22:27 | 26.7967 | -0.076267 | 0.55322
|  | 22:27 | 26.7978 | -0.073963 | 0.55322
|  | 22:27 | 26.7989 | -0.07062 | 0.55322
|  | 22:27 | 26.8 | -0.067277 | 0.55322
|  | 22:27 | 26.8011 | -0.087801 | 0.55321
|  | 22:28 | 26.8022 | -0.10832 | 0.55321
|  | 22:28 | 26.8033 | -0.11242 | 0.55321
|  | 22:28 | 26.8044 | -0.10009 | 0.55321
|  | 22:28 | 26.8056 | -0.087763 | 0.5532
|  | 22:28 | 26.8067 | -0.068639 | 0.5532
|  | 22:28 | 26.8078 | -0.049516 | 0.5532
|  | 22:28 | 26.8089 | -0.015747 | 0.5532
|  | 22:28 | 26.81 | 0.032669 | 0.55319
|  | 22:28 | 26.8111 | 0.076313 | 0.55319
|  | 22:28 | 26.8122 | 0.10565 | 0.55319
|  | 22:28 | 26.8133 | 0.13498 | 0.55319
|  | 22:28 | 26.8144 | 0.14996 | 0.55319
|  | 22:28 | 26.8156 | 0.1506 | 0.55318
|  | 22:28 | 26.8167 | 0.15123 | 0.55318
|  | 22:28 | 26.8178 | 0.15947 | 0.55318
|  | 22:29 | 26.8189 | 0.1677 | 0.55318
|  | 22:29 | 26.82 | 0.16361 | 0.55317
|  | 22:29 | 26.8211 | 0.14719 | 0.55317
|  | 22:29 | 26.8222 | 0.13078 | 0.55317
|  | 22:29 | 26.8233 | 0.11437 | 0.55317
|  | 22:29 | 26.8244 | 0.097961 | 0.55316
|  | 22:29 | 26.8256 | 0.077558 | 0.55316
|  | 22:29 | 26.8267 | 0.055824 | 0.55316
|  | 22:29 | 26.8278 | 0.034089 | 0.55316
|  | 22:29 | 26.8289 | 0.018564 | 0.55316
|  | 22:29 | 26.83 | 0.0030393 | 0.55315
|  | 22:29 | 26.8311 | -0.016027 | 0.55315
|  | 22:29 | 26.8322 | -0.038635 | 0.55315
|  | 22:29 | 26.8333 | -0.061243 | 0.55315
|  | 22:29 | 26.8344 | -0.068344 | 0.55314
|  | 22:30 | 26.8356 | -0.075445 | 0.55314
|  | 22:30 | 26.8367 | -0.080764 | 0.55314
|  | 22:30 | 26.8378 | -0.0843 | 0.55314
|  | 22:30 | 26.8389 | -0.087836 | 0.55313
|  | 22:30 | 26.84 | -0.08516 | 0.55313
|  | 22:30 | 26.8411 | -0.082483 | 0.55313
|  | 22:30 | 26.8422 | -0.079807 | 0.55313
|  | 22:30 | 26.8433 | -0.07713 | 0.55312
|  | 22:30 | 26.8444 | -0.074454 | 0.55312
|  | 22:30 | 26.8456 | -0.076025 | 0.55312
|  | 22:30 | 26.8467 | -0.077597 | 0.55312
|  | 22:30 | 26.8478 | -0.085439 | 0.55312
|  | 22:30 | 26.8489 | -0.09955 | 0.55311
|  | 22:30 | 26.85 | -0.11366 | 0.55311
|  | 22:30 | 26.8511 | -0.11441 | 0.55311
|  | 22:31 | 26.8522 | -0.11516 | 0.55311
|  | 22:31 | 26.8533 | -0.10971 | 0.5531
|  | 22:31 | 26.8544 | -0.09806 | 0.5531
|  | 22:31 | 26.8556 | -0.084509 | 0.5531
|  | 22:31 | 26.8567 | -0.065244 | 0.5531
|  | 22:31 | 26.8578 | -0.045979 | 0.55309
|  | 22:31 | 26.8589 | -0.029559 | 0.55309
|  | 22:31 | 26.86 | -0.015984 | 0.55309
|  | 22:31 | 26.8611 | -0.0024094 | 0.55309
|  | 22:31 | 26.8622 | 0.022238 | 0.55309
|  | 22:31 | 26.8633 | 0.046885 | 0.55308
|  | 22:31 | 26.8644 | 0.074314 | 0.55308
|  | 22:31 | 26.8656 | 0.10453 | 0.55308
|  | 22:31 | 26.8667 | 0.13474 | 0.55308
|  | 22:31 | 26.8678 | 0.15843 | 0.55307
|  | 22:32 | 26.8689 | 0.18212 | 0.55307
|  | 22:32 | 26.87 | 0.20365 | 0.55307
|  | 22:32 | 26.8711 | 0.22304 | 0.55307
|  | 22:32 | 26.8722 | 0.24243 | 0.55306
|  | 22:32 | 26.8733 | 0.2467 | 0.55306
|  | 22:32 | 26.8744 | 0.25097 | 0.55306
|  | 22:32 | 26.8756 | 0.25524 | 0.55306
|  | 22:32 | 26.8767 | 0.25952 | 0.55306
|  | 22:32 | 26.8778 | 0.26379 | 0.55305
|  | 22:32 | 26.8789 | 0.26806 | 0.55305
|  | 22:32 | 26.88 | 0.27234 | 0.55305
|  | 22:32 | 26.8811 | 0.27055 | 0.55305
|  | 22:32 | 26.8822 | 0.26272 | 0.55304
|  | 22:32 | 26.8833 | 0.25488 | 0.55304
|  | 22:32 | 26.8844 | 0.23498 | 0.55304
|  | 22:33 | 26.8856 | 0.21507 | 0.55304
|  | 22:33 | 26.8867 | 0.20228 | 0.55303
|  | 22:33 | 26.8878 | 0.1966 | 0.55303
|  | 22:33 | 26.8889 | 0.19092 | 0.55303
|  | 22:33 | 26.89 | 0.17374 | 0.55303
|  | 22:33 | 26.8911 | 0.15656 | 0.55303
|  | 22:33 | 26.8922 | 0.14737 | 0.55302
|  | 22:33 | 26.8933 | 0.14617 | 0.55302
|  | 22:33 | 26.8944 | 0.14096 | 0.55302
|  | 22:33 | 26.8956 | 0.1237 | 0.55302
|  | 22:33 | 26.8967 | 0.10644 | 0.55301
|  | 22:33 | 26.8978 | 0.091813 | 0.55301
|  | 22:33 | 26.8989 | 0.079822 | 0.55301
|  | 22:33 | 26.9 | 0.067831 | 0.55301
|  | 22:33 | 26.9011 | 0.075896 | 0.553
|  | 22:34 | 26.9022 | 0.083961 | 0.553
|  | 22:34 | 26.9033 | 0.086463 | 0.553
|  | 22:34 | 26.9044 | 0.083403 | 0.553
|  | 22:34 | 26.9056 | 0.080342 | 0.553
|  | 22:34 | 26.9067 | 0.086139 | 0.55299
|  | 22:34 | 26.9078 | 0.091936 | 0.55299
|  | 22:34 | 26.9089 | 0.086932 | 0.55299
|  | 22:34 | 26.91 | 0.071129 | 0.55299
|  | 22:34 | 26.9111 | 0.055325 | 0.55298
|  | 22:34 | 26.9122 | 0.058039 | 0.55298
|  | 22:34 | 26.9133 | 0.060754 | 0.55298
|  | 22:34 | 26.9144 | 0.053289 | 0.55298
|  | 22:34 | 26.9156 | 0.035644 | 0.55297
|  | 22:34 | 26.9167 | 0.018 | 0.55297
|  | 22:34 | 26.9178 | -0.013065 | 0.55297
|  | 22:35 | 26.9189 | -0.04413 | 0.55297
|  | 22:35 | 26.92 | -0.070275 | 0.55297
|  | 22:35 | 26.9211 | -0.091499 | 0.55296
|  | 22:35 | 26.9222 | -0.11272 | 0.55296
|  | 22:35 | 26.9233 | -0.1153 | 0.55296
|  | 22:35 | 26.9244 | -0.11788 | 0.55296
|  | 22:35 | 26.9256 | -0.11783 | 0.55295
|  | 22:35 | 26.9267 | -0.11514 | 0.55295
|  | 22:35 | 26.9278 | -0.11272 | 0.55295
|  | 22:35 | 26.9289 | -0.11108 | 0.55295
|  | 22:35 | 26.93 | -0.10944 | 0.55294
|  | 22:35 | 26.9311 | -0.1078 | 0.55294
|  | 22:35 | 26.9322 | -0.12031 | 0.55294
|  | 22:35 | 26.9333 | -0.13283 | 0.55294
|  | 22:35 | 26.9344 | -0.13556 | 0.55294
|  | 22:36 | 26.9356 | -0.1383 | 0.55293
|  | 22:36 | 26.9367 | -0.13564 | 0.55293
|  | 22:36 | 26.9378 | -0.13119 | 0.55293
|  | 22:36 | 26.9389 | -0.1251 | 0.55293
|  | 22:36 | 26.94 | -0.11411 | 0.55292
|  | 22:36 | 26.9411 | -0.10312 | 0.55292
|  | 22:36 | 26.9422 | -0.087127 | 0.55292
|  | 22:36 | 26.9433 | -0.06947 | 0.55292
|  | 22:36 | 26.9444 | -0.057029 | 0.55291
|  | 22:36 | 26.9456 | -0.060235 | 0.55291
|  | 22:36 | 26.9467 | -0.06344 | 0.55291
|  | 22:36 | 26.9478 | -0.059529 | 0.55291
|  | 22:36 | 26.9489 | -0.053247 | 0.55291
|  | 22:36 | 26.95 | -0.048412 | 0.5529
|  | 22:36 | 26.9511 | -0.047923 | 0.5529
|  | 22:37 | 26.9522 | -0.047434 | 0.5529
|  | 22:37 | 26.9533 | -0.052124 | 0.5529
|  | 22:37 | 26.9544 | -0.05854 | 0.55289
|  | 22:37 | 26.9556 | -0.068618 | 0.55289
|  | 22:37 | 26.9567 | -0.08968 | 0.55289
|  | 22:37 | 26.9578 | -0.11074 | 0.55289
|  | 22:37 | 26.9589 | -0.12803 | 0.55288
|  | 22:37 | 26.96 | -0.14405 | 0.55288
|  | 22:37 | 26.9611 | -0.15587 | 0.55288
|  | 22:37 | 26.9622 | -0.15507 | 0.55288
|  | 22:37 | 26.9633 | -0.15427 | 0.55287
|  | 22:37 | 26.9644 | -0.1689 | 0.55287
|  | 22:37 | 26.9656 | -0.18867 | 0.55287
|  | 22:37 | 26.9667 | -0.19879 | 0.55287
|  | 22:37 | 26.9678 | -0.17995 | 0.55287
|  | 22:38 | 26.9689 | -0.16112 | 0.55286
|  | 22:38 | 26.97 | -0.14042 | 0.55286
|  | 22:38 | 26.9711 | -0.1191 | 0.55286
|  | 22:38 | 26.9722 | -0.087246 | 0.55286
|  | 22:38 | 26.9733 | -0.023777 | 0.55285
|  | 22:38 | 26.9744 | 0.039692 | 0.55285
|  | 22:38 | 26.9756 | 0.084628 | 0.55285
|  | 22:38 | 26.9767 | 0.12956 | 0.55285
|  | 22:38 | 26.9778 | 0.17372 | 0.55284
|  | 22:38 | 26.9789 | 0.21556 | 0.55284
|  | 22:38 | 26.98 | 0.2574 | 0.55284
|  | 22:38 | 26.9811 | 0.26371 | 0.55284
|  | 22:38 | 26.9822 | 0.25818 | 0.55284
|  | 22:38 | 26.9833 | 0.25264 | 0.55283
|  | 22:38 | 26.9844 | 0.24711 | 0.55283
|  | 22:39 | 26.9856 | 0.24157 | 0.55283
|  | 22:39 | 26.9867 | 0.24404 | 0.55283
|  | 22:39 | 26.9878 | 0.24918 | 0.55282
|  | 22:39 | 26.9889 | 0.25653 | 0.55282
|  | 22:39 | 26.99 | 0.27053 | 0.55282
|  | 22:39 | 26.9911 | 0.28454 | 0.55282
|  | 22:39 | 26.9922 | 0.28643 | 0.55281
|  | 22:39 | 26.9933 | 0.28428 | 0.55281
|  | 22:39 | 26.9944 | 0.28637 | 0.55281
|  | 22:39 | 26.9956 | 0.30114 | 0.55281
|  | 22:39 | 26.9967 | 0.31592 | 0.55281
|  | 22:39 | 26.9978 | 0.32289 | 0.5528
|  | 22:39 | 26.9989 | 0.32726 | 0.5528
|  | 22:39 | 27 | 0.32399 | 0.5528
|  | 22:39 | 27.0011 | 0.3131 | 0.5528
|  | 22:40 | 27.0022 | 0.3022 | 0.55279
|  | 22:40 | 27.0033 | 0.28574 | 0.55279
|  | 22:40 | 27.0044 | 0.26742 | 0.55279
|  | 22:40 | 27.0056 | 0.24996 | 0.55279
|  | 22:40 | 27.0067 | 0.23337 | 0.55278
|  | 22:40 | 27.0078 | 0.21678 | 0.55278
|  | 22:40 | 27.0089 | 0.18735 | 0.55278
|  | 22:40 | 27.01 | 0.15364 | 0.55278
|  | 22:40 | 27.0111 | 0.13899 | 0.55278
|  | 22:40 | 27.0122 | 0.1434 | 0.55277
|  | 22:40 | 27.0133 | 0.1478 | 0.55277
|  | 22:40 | 27.0144 | 0.16101 | 0.55277
|  | 22:40 | 27.0156 | 0.17715 | 0.55277
|  | 22:40 | 27.0167 | 0.1784 | 0.55276
|  | 22:40 | 27.0178 | 0.16474 | 0.55276
|  | 22:41 | 27.0189 | 0.15109 | 0.55276
|  | 22:41 | 27.02 | 0.12306 | 0.55276
|  | 22:41 | 27.0211 | 0.090241 | 0.55275
|  | 22:41 | 27.0222 | 0.056587 | 0.55275
|  | 22:41 | 27.0233 | 0.020429 | 0.55275
|  | 22:41 | 27.0244 | -0.015729 | 0.55275
|  | 22:41 | 27.0256 | -0.042232 | 0.55275
|  | 22:41 | 27.0267 | -0.065516 | 0.55274
|  | 22:41 | 27.0278 | -0.087599 | 0.55274
|  | 22:41 | 27.0289 | -0.10608 | 0.55274
|  | 22:41 | 27.03 | -0.12456 | 0.55274
|  | 22:41 | 27.0311 | -0.13921 | 0.55273
|  | 22:41 | 27.0322 | -0.15259 | 0.55273
|  | 22:41 | 27.0333 | -0.16354 | 0.55273
|  | 22:41 | 27.0344 | -0.16719 | 0.55273
|  | 22:42 | 27.0356 | -0.17083 | 0.55272
|  | 22:42 | 27.0367 | -0.19514 | 0.55272
|  | 22:42 | 27.0378 | -0.22632 | 0.55272
|  | 22:42 | 27.0389 | -0.24783 | 0.55272
|  | 22:42 | 27.04 | -0.24028 | 0.55272
|  | 22:42 | 27.0411 | -0.23273 | 0.55271
|  | 22:42 | 27.0422 | -0.22091 | 0.55271
|  | 22:42 | 27.0433 | -0.20767 | 0.55271
|  | 22:42 | 27.0444 | -0.19169 | 0.55271
|  | 22:42 | 27.0456 | -0.1675 | 0.5527
|  | 22:42 | 27.0467 | -0.14331 | 0.5527
|  | 22:42 | 27.0478 | -0.12658 | 0.5527
|  | 22:42 | 27.0489 | -0.11235 | 0.5527
|  | 22:42 | 27.05 | -0.099041 | 0.55269
|  | 22:42 | 27.0511 | -0.088485 | 0.55269
|  | 22:43 | 27.0522 | -0.077929 | 0.55269
|  | 22:43 | 27.0533 | -0.06405 | 0.55269
|  | 22:43 | 27.0544 | -0.049063 | 0.55269
|  | 22:43 | 27.0556 | -0.032325 | 0.55268
|  | 22:43 | 27.0567 | -0.01033 | 0.55268
|  | 22:43 | 27.0578 | 0.011664 | 0.55268
|  | 22:43 | 27.0589 | 0.025807 | 0.55268
|  | 22:43 | 27.06 | 0.037333 | 0.55267
|  | 22:43 | 27.0611 | 0.049144 | 0.55267
|  | 22:43 | 27.0622 | 0.06181 | 0.55267
|  | 22:43 | 27.0633 | 0.074475 | 0.55267
|  | 22:43 | 27.0644 | 0.088406 | 0.55266
|  | 22:43 | 27.0656 | 0.10276 | 0.55266
|  | 22:43 | 27.0667 | 0.11637 | 0.55266
|  | 22:43 | 27.0678 | 0.12776 | 0.55266
|  | 22:44 | 27.0689 | 0.13916 | 0.55266
|  | 22:44 | 27.07 | 0.15333 | 0.55265
|  | 22:44 | 27.0711 | 0.16843 | 0.55265
|  | 22:44 | 27.0722 | 0.18226 | 0.55265
|  | 22:44 | 27.0733 | 0.19228 | 0.55265
|  | 22:44 | 27.0744 | 0.20229 | 0.55264
|  | 22:44 | 27.0756 | 0.18703 | 0.55264
|  | 22:44 | 27.0767 | 0.17176 | 0.55264
|  | 22:44 | 27.0778 | 0.15361 | 0.55264
|  | 22:44 | 27.0789 | 0.12677 | 0.55263
|  | 22:44 | 27.08 | 0.099932 | 0.55263
|  | 22:44 | 27.0811 | 0.080254 | 0.55263
|  | 22:44 | 27.0822 | 0.062962 | 0.55263
|  | 22:44 | 27.0833 | 0.049071 | 0.55262
|  | 22:44 | 27.0844 | 0.045383 | 0.55262
|  | 22:45 | 27.0856 | 0.041695 | 0.55262
|  | 22:45 | 27.0867 | 0.032198 | 0.55262
|  | 22:45 | 27.0878 | 0.020765 | 0.55262
|  | 22:45 | 27.0889 | 0.010218 | 0.55261
|  | 22:45 | 27.09 | 0.0023298 | 0.55261
|  | 22:45 | 27.0911 | -0.0055582 | 0.55261
|  | 22:45 | 27.0922 | -0.023576 | 0.55261
|  | 22:45 | 27.0933 | -0.04497 | 0.5526
|  | 22:45 | 27.0944 | -0.063236 | 0.5526
|  | 22:45 | 27.0956 | -0.072119 | 0.5526
|  | 22:45 | 27.0967 | -0.081002 | 0.5526
|  | 22:45 | 27.0978 | -0.091497 | 0.55259
|  | 22:45 | 27.0989 | -0.10253 | 0.55259
|  | 22:45 | 27.1 | -0.11184 | 0.55259
|  | 22:45 | 27.1011 | -0.11599 | 0.55259
|  | 22:46 | 27.1022 | -0.12014 | 0.55259
|  | 22:46 | 27.1033 | -0.12608 | 0.55258
|  | 22:46 | 27.1044 | -0.13383 | 0.55258
|  | 22:46 | 27.1056 | -0.14157 | 0.55258
|  | 22:46 | 27.1067 | -0.14002 | 0.55258
|  | 22:46 | 27.1078 | -0.13847 | 0.55257
|  | 22:46 | 27.1089 | -0.14396 | 0.55257
|  | 22:46 | 27.11 | -0.1565 | 0.55257
|  | 22:46 | 27.1111 | -0.16904 | 0.55257
|  | 22:46 | 27.1122 | -0.18405 | 0.55256
|  | 22:46 | 27.1133 | -0.19905 | 0.55256
|  | 22:46 | 27.1144 | -0.20539 | 0.55256
|  | 22:46 | 27.1156 | -0.20306 | 0.55256
|  | 22:46 | 27.1167 | -0.20073 | 0.55256
|  | 22:46 | 27.1178 | -0.17283 | 0.55255
|  | 22:47 | 27.1189 | -0.14493 | 0.55255
|  | 22:47 | 27.12 | -0.1155 | 0.55255
|  | 22:47 | 27.1211 | -0.084542 | 0.55255
|  | 22:47 | 27.1222 | -0.053583 | 0.55254
|  | 22:47 | 27.1233 | -0.01823 | 0.55254
|  | 22:47 | 27.1244 | 0.017124 | 0.55254
|  | 22:47 | 27.1256 | 0.042132 | 0.55254
|  | 22:47 | 27.1267 | 0.056796 | 0.55253
|  | 22:47 | 27.1278 | 0.07146 | 0.55253
|  | 22:47 | 27.1289 | 0.069582 | 0.55253
|  | 22:47 | 27.13 | 0.067705 | 0.55253
|  | 22:47 | 27.1311 | 0.068706 | 0.55253
|  | 22:47 | 27.1322 | 0.072586 | 0.55252
|  | 22:47 | 27.1333 | 0.076467 | 0.55252
|  | 22:47 | 27.1344 | 0.08665 | 0.55252
|  | 22:48 | 27.1356 | 0.096832 | 0.55252
|  | 22:48 | 27.1367 | 0.097433 | 0.55251
|  | 22:48 | 27.1378 | 0.088452 | 0.55251
|  | 22:48 | 27.1389 | 0.079471 | 0.55251
|  | 22:48 | 27.14 | 0.07049 | 0.55251
|  | 22:48 | 27.1411 | 0.061509 | 0.5525
|  | 22:48 | 27.1422 | 0.044761 | 0.5525
|  | 22:48 | 27.1433 | 0.020245 | 0.5525
|  | 22:48 | 27.1444 | -0.0042709 | 0.5525
|  | 22:48 | 27.1456 | -0.0071686 | 0.5525
|  | 22:48 | 27.1467 | -0.010066 | 0.55249
|  | 22:48 | 27.1478 | -0.015785 | 0.55249
|  | 22:48 | 27.1489 | -0.024325 | 0.55249
|  | 22:48 | 27.15 | -0.032865 | 0.55249
|  | 22:48 | 27.1511 | -0.041405 | 0.55248
|  | 22:49 | 27.1522 | -0.049945 | 0.55248
|  | 22:49 | 27.1533 | -0.061732 | 0.55248
|  | 22:49 | 27.1544 | -0.076764 | 0.55248
|  | 22:49 | 27.1556 | -0.091797 | 0.55247
|  | 22:49 | 27.1567 | -0.081949 | 0.55247
|  | 22:49 | 27.1578 | -0.072101 | 0.55247
|  | 22:49 | 27.1589 | -0.069993 | 0.55247
|  | 22:49 | 27.16 | -0.075625 | 0.55247
|  | 22:49 | 27.1611 | -0.081256 | 0.55246
|  | 22:49 | 27.1622 | -0.10398 | 0.55246
|  | 22:49 | 27.1633 | -0.12671 | 0.55246
|  | 22:49 | 27.1644 | -0.13424 | 0.55246
|  | 22:49 | 27.1656 | -0.13671 | 0.55245
|  | 22:49 | 27.1667 | -0.13917 | 0.55245
|  | 22:49 | 27.1678 | -0.13967 | 0.55245
|  | 22:50 | 27.1689 | -0.14016 | 0.55245
|  | 22:50 | 27.17 | -0.13967 | 0.55244
|  | 22:50 | 27.1711 | -0.1382 | 0.55244
|  | 22:50 | 27.1722 | -0.13672 | 0.55244
|  | 22:50 | 27.1733 | -0.13986 | 0.55244
|  | 22:50 | 27.1744 | -0.143 | 0.55244
|  | 22:50 | 27.1756 | -0.15783 | 0.55243
|  | 22:50 | 27.1767 | -0.18435 | 0.55243
|  | 22:50 | 27.1778 | -0.21088 | 0.55243
|  | 22:50 | 27.1789 | -0.23015 | 0.55243
|  | 22:50 | 27.18 | -0.24943 | 0.55242
|  | 22:50 | 27.1811 | -0.27026 | 0.55242
|  | 22:50 | 27.1822 | -0.29265 | 0.55242
|  | 22:50 | 27.1833 | -0.31503 | 0.55242
|  | 22:50 | 27.1844 | -0.32195 | 0.55241
|  | 22:51 | 27.1856 | -0.32886 | 0.55241
|  | 22:51 | 27.1867 | -0.34119 | 0.55241
|  | 22:51 | 27.1878 | -0.35894 | 0.55241
|  | 22:51 | 27.1889 | -0.37669 | 0.55241
|  | 22:51 | 27.19 | -0.40678 | 0.5524
|  | 22:51 | 27.1911 | -0.43687 | 0.5524
|  | 22:51 | 27.1922 | -0.47126 | 0.5524
|  | 22:51 | 27.1933 | -0.50996 | 0.5524
|  | 22:51 | 27.1944 | -0.54865 | 0.55239
|  | 22:51 | 27.1956 | -0.56956 | 0.55239
|  | 22:51 | 27.1967 | -0.59046 | 0.55239
|  | 22:51 | 27.1978 | -0.60099 | 0.55239
|  | 22:51 | 27.1989 | -0.60114 | 0.55238
|  | 22:51 | 27.2 | -0.60129 | 0.55238
|  | 22:51 | 27.2011 | -0.60725 | 0.55238
|  | 22:52 | 27.2022 | -0.6132 | 0.55238
|  | 22:52 | 27.2033 | -0.61495 | 0.55237
|  | 22:52 | 27.2044 | -0.6125 | 0.55237
|  | 22:52 | 27.2056 | -0.61004 | 0.55237
|  | 22:52 | 27.2067 | -0.60192 | 0.55237
|  | 22:52 | 27.2078 | -0.59379 | 0.55237
|  | 22:52 | 27.2089 | -0.57338 | 0.55236
|  | 22:52 | 27.21 | -0.54068 | 0.55236
|  | 22:52 | 27.2111 | -0.50798 | 0.55236
|  | 22:52 | 27.2122 | -0.44948 | 0.55236
|  | 22:52 | 27.2133 | -0.39097 | 0.55235
|  | 22:52 | 27.2144 | -0.34491 | 0.55235
|  | 22:52 | 27.2156 | -0.30298 | 0.55235
|  | 22:52 | 27.2167 | -0.26106 | 0.55235
|  | 22:52 | 27.2178 | -0.21372 | 0.55234
|  | 22:53 | 27.2189 | -0.16637 | 0.55234
|  | 22:53 | 27.22 | -0.13138 | 0.55234
|  | 22:53 | 27.2211 | -0.10875 | 0.55234
|  | 22:53 | 27.2222 | -0.086123 | 0.55234
|  | 22:53 | 27.2233 | -0.059309 | 0.55233
|  | 22:53 | 27.2244 | -0.032495 | 0.55233
|  | 22:53 | 27.2256 | -0.0085625 | 0.55233
|  | 22:53 | 27.2267 | 0.01441 | 0.55233
|  | 22:53 | 27.2278 | 0.037382 | 0.55232
|  | 22:53 | 27.2289 | 0.066252 | 0.55232
|  | 22:53 | 27.23 | 0.095122 | 0.55232
|  | 22:53 | 27.2311 | 0.10872 | 0.55232
|  | 22:53 | 27.2322 | 0.10704 | 0.55231
|  | 22:53 | 27.2333 | 0.10536 | 0.55231
|  | 22:53 | 27.2344 | 0.10089 | 0.55231
|  | 22:54 | 27.2356 | 0.088038 | 0.55231
|  | 22:54 | 27.2367 | 0.080428 | 0.55231
|  | 22:54 | 27.2378 | 0.078054 | 0.5523
|  | 22:54 | 27.2389 | 0.07568 | 0.5523
|  | 22:54 | 27.24 | 0.060873 | 0.5523
|  | 22:54 | 27.2411 | 0.046067 | 0.5523
|  | 22:54 | 27.2422 | 0.032489 | 0.55229
|  | 22:54 | 27.2433 | 0.02014 | 0.55229
|  | 22:54 | 27.2444 | 0.0077913 | 0.55229
|  | 22:54 | 27.2456 | 0.0089382 | 0.55229
|  | 22:54 | 27.2467 | 0.010085 | 0.55228
|  | 22:54 | 27.2478 | 0.017944 | 0.55228
|  | 22:54 | 27.2489 | 0.032514 | 0.55228
|  | 22:54 | 27.25 | 0.047085 | 0.55228
|  | 22:54 | 27.2511 | 0.076109 | 0.55228
|  | 22:55 | 27.2522 | 0.10513 | 0.55227
|  | 22:55 | 27.2533 | 0.13867 | 0.55227
|  | 22:55 | 27.2544 | 0.17371 | 0.55227
|  | 22:55 | 27.2556 | 0.20875 | 0.55227
|  | 22:55 | 27.2567 | 0.23334 | 0.55226
|  | 22:55 | 27.2578 | 0.25792 | 0.55226
|  | 22:55 | 27.2589 | 0.27615 | 0.55226
|  | 22:55 | 27.26 | 0.28804 | 0.55226
|  | 22:55 | 27.2611 | 0.29992 | 0.55225
|  | 22:55 | 27.2622 | 0.31798 | 0.55225
|  | 22:55 | 27.2633 | 0.33605 | 0.55225
|  | 22:55 | 27.2644 | 0.36385 | 0.55225
|  | 22:55 | 27.2656 | 0.40137 | 0.55225
|  | 22:55 | 27.2667 | 0.4389 | 0.55224
|  | 22:55 | 27.2678 | 0.47837 | 0.55224
|  | 22:56 | 27.2689 | 0.51784 | 0.55224
|  | 22:56 | 27.27 | 0.54605 | 0.55224
|  | 22:56 | 27.2711 | 0.57051 | 0.55223
|  | 22:56 | 27.2722 | 0.59043 | 0.55223
|  | 22:56 | 27.2733 | 0.59672 | 0.55223
|  | 22:56 | 27.2744 | 0.60301 | 0.55223
|  | 22:56 | 27.2756 | 0.61476 | 0.55222
|  | 22:56 | 27.2767 | 0.62833 | 0.55222
|  | 22:56 | 27.2778 | 0.63908 | 0.55222
|  | 22:56 | 27.2789 | 0.64134 | 0.55222
|  | 22:56 | 27.28 | 0.6436 | 0.55222
|  | 22:56 | 27.2811 | 0.64966 | 0.55221
|  | 22:56 | 27.2822 | 0.65699 | 0.55221
|  | 22:56 | 27.2833 | 0.66861 | 0.55221
|  | 22:56 | 27.2844 | 0.69311 | 0.55221
|  | 22:57 | 27.2856 | 0.71761 | 0.5522
|  | 22:57 | 27.2867 | 0.72431 | 0.5522
|  | 22:57 | 27.2878 | 0.72507 | 0.5522
|  | 22:57 | 27.2889 | 0.72324 | 0.5522
|  | 22:57 | 27.29 | 0.71361 | 0.55219
|  | 22:57 | 27.2911 | 0.70399 | 0.55219
|  | 22:57 | 27.2922 | 0.68391 | 0.55219
|  | 22:57 | 27.2933 | 0.66036 | 0.55219
|  | 22:57 | 27.2944 | 0.63042 | 0.55219
|  | 22:57 | 27.2956 | 0.58134 | 0.55218
|  | 22:57 | 27.2967 | 0.53226 | 0.55218
|  | 22:57 | 27.2978 | 0.48119 | 0.55218
|  | 22:57 | 27.2989 | 0.42944 | 0.55218
|  | 22:57 | 27.3 | 0.38903 | 0.55217
|  | 22:57 | 27.3011 | 0.35995 | 0.55217
|  | 22:58 | 27.3022 | 0.33088 | 0.55217
|  | 22:58 | 27.3033 | 0.2821 | 0.55217
|  | 22:58 | 27.3044 | 0.22676 | 0.55216
|  | 22:58 | 27.3056 | 0.17658 | 0.55216
|  | 22:58 | 27.3067 | 0.1419 | 0.55216
|  | 22:58 | 27.3078 | 0.10722 | 0.55216
|  | 22:58 | 27.3089 | 0.081901 | 0.55216
|  | 22:58 | 27.31 | 0.056586 | 0.55215
|  | 22:58 | 27.3111 | 0.030142 | 0.55215
|  | 22:58 | 27.3122 | 0.00031549 | 0.55215
|  | 22:58 | 27.3133 | -0.029511 | 0.55215
|  | 22:58 | 27.3144 | -0.058698 | 0.55214
|  | 22:58 | 27.3156 | -0.087671 | 0.55214
|  | 22:58 | 27.3167 | -0.11306 | 0.55214
|  | 22:58 | 27.3178 | -0.12771 | 0.55214
|  | 22:59 | 27.3189 | -0.14236 | 0.55213
|  | 22:59 | 27.32 | -0.16624 | 0.55213
|  | 22:59 | 27.3211 | -0.1932 | 0.55213
|  | 22:59 | 27.3222 | -0.22575 | 0.55213
|  | 22:59 | 27.3233 | -0.2751 | 0.55212
|  | 22:59 | 27.3244 | -0.32445 | 0.55212
|  | 22:59 | 27.3256 | -0.35449 | 0.55212
|  | 22:59 | 27.3267 | -0.37809 | 0.55212
|  | 22:59 | 27.3278 | -0.39723 | 0.55212
|  | 22:59 | 27.3289 | -0.40298 | 0.55211
|  | 22:59 | 27.33 | -0.40874 | 0.55211
|  | 22:59 | 27.3311 | -0.41121 | 0.55211
|  | 22:59 | 27.3322 | -0.41258 | 0.55211
|  | 22:59 | 27.3333 | -0.4191 | 0.5521
|  | 22:59 | 27.3344 | -0.44105 | 0.5521
|  | 23:00 | 27.3356 | -0.46301 | 0.5521
|  | 23:00 | 27.3367 | -0.4794 | 0.5521
|  | 23:00 | 27.3378 | -0.49394 | 0.55209
|  | 23:00 | 27.3389 | -0.50803 | 0.55209
|  | 23:00 | 27.34 | -0.52082 | 0.55209
|  | 23:00 | 27.3411 | -0.53361 | 0.55209
|  | 23:00 | 27.3422 | -0.57167 | 0.55209
|  | 23:00 | 27.3433 | -0.61817 | 0.55208
|  | 23:00 | 27.3444 | -0.65686 | 0.55208
|  | 23:00 | 27.3456 | -0.67212 | 0.55208
|  | 23:00 | 27.3467 | -0.68739 | 0.55208
|  | 23:00 | 27.3478 | -0.69862 | 0.55207
|  | 23:00 | 27.3489 | -0.7085 | 0.55207
|  | 23:00 | 27.35 | -0.7136 | 0.55207
|  | 23:00 | 27.3511 | -0.70432 | 0.55207
|  | 23:01 | 27.3522 | -0.69505 | 0.55206
|  | 23:01 | 27.3533 | -0.67207 | 0.55206
|  | 23:01 | 27.3544 | -0.64451 | 0.55206
|  | 23:01 | 27.3556 | -0.61836 | 0.55206
|  | 23:01 | 27.3567 | -0.59644 | 0.55206
|  | 23:01 | 27.3578 | -0.57451 | 0.55205
|  | 23:01 | 27.3589 | -0.55325 | 0.55205
|  | 23:01 | 27.36 | -0.53222 | 0.55205
|  | 23:01 | 27.3611 | -0.51696 | 0.55205
|  | 23:01 | 27.3622 | -0.51903 | 0.55204
|  | 23:01 | 27.3633 | -0.5211 | 0.55204
|  | 23:01 | 27.3644 | -0.52402 | 0.55204
|  | 23:01 | 27.3656 | -0.52724 | 0.55204
|  | 23:01 | 27.3667 | -0.52781 | 0.55203
|  | 23:01 | 27.3678 | -0.52046 | 0.55203
|  | 23:02 | 27.3689 | -0.51311 | 0.55203
|  | 23:02 | 27.37 | -0.49295 | 0.55203
|  | 23:02 | 27.3711 | -0.46852 | 0.55203
|  | 23:02 | 27.3722 | -0.44277 | 0.55202
|  | 23:02 | 27.3733 | -0.41302 | 0.55202
|  | 23:02 | 27.3744 | -0.38327 | 0.55202
|  | 23:02 | 27.3756 | -0.36219 | 0.55202
|  | 23:02 | 27.3767 | -0.34399 | 0.55201
|  | 23:02 | 27.3778 | -0.32331 | 0.55201
|  | 23:02 | 27.3789 | -0.29521 | 0.55201
|  | 23:02 | 27.38 | -0.26711 | 0.55201
|  | 23:02 | 27.3811 | -0.22818 | 0.552
|  | 23:02 | 27.3822 | -0.18565 | 0.552
|  | 23:02 | 27.3833 | -0.14681 | 0.552
|  | 23:02 | 27.3844 | -0.11909 | 0.552
|  | 23:03 | 27.3856 | -0.091362 | 0.552
|  | 23:03 | 27.3867 | -0.063635 | 0.55199
|  | 23:03 | 27.3878 | -0.035909 | 0.55199
|  | 23:03 | 27.3889 | -0.010399 | 0.55199
|  | 23:03 | 27.39 | 0.008462 | 0.55199
|  | 23:03 | 27.3911 | 0.027323 | 0.55198
|  | 23:03 | 27.3922 | 0.034398 | 0.55198
|  | 23:03 | 27.3933 | 0.037546 | 0.55198
|  | 23:03 | 27.3944 | 0.043552 | 0.55198
|  | 23:03 | 27.3956 | 0.058133 | 0.55197
|  | 23:03 | 27.3967 | 0.072714 | 0.55197
|  | 23:03 | 27.3978 | 0.058027 | 0.55197
|  | 23:03 | 27.3989 | 0.033585 | 0.55197
|  | 23:03 | 27.4 | 0.0091424 | 0.55197
|  | 23:03 | 27.4011 | -0.0069915 | 0.55196
|  | 23:04 | 27.4022 | -0.014817 | 0.55196
|  | 23:04 | 27.4033 | -0.013008 | 0.55196
|  | 23:04 | 27.4044 | -0.0079873 | 0.55196
|  | 23:04 | 27.4056 | -0.0032145 | 0.55195
|  | 23:04 | 27.4067 | 0.00081442 | 0.55195
|  | 23:04 | 27.4078 | 0.0048433 | 0.55195
|  | 23:04 | 27.4089 | -0.011699 | 0.55195
|  | 23:04 | 27.41 | -0.035099 | 0.55194
|  | 23:04 | 27.4111 | -0.062149 | 0.55194
|  | 23:04 | 27.4122 | -0.10015 | 0.55194
|  | 23:04 | 27.4133 | -0.13814 | 0.55194
|  | 23:04 | 27.4144 | -0.15922 | 0.55194
|  | 23:04 | 27.4156 | -0.17466 | 0.55193
|  | 23:04 | 27.4167 | -0.18651 | 0.55193
|  | 23:04 | 27.4178 | -0.18759 | 0.55193
|  | 23:05 | 27.4189 | -0.18868 | 0.55193
|  | 23:05 | 27.42 | -0.16432 | 0.55192
|  | 23:05 | 27.4211 | -0.13147 | 0.55192
|  | 23:05 | 27.4222 | -0.097254 | 0.55192
|  | 23:05 | 27.4233 | -0.058911 | 0.55192
|  | 23:05 | 27.4244 | -0.020569 | 0.55191
|  | 23:05 | 27.4256 | 0.017096 | 0.55191
|  | 23:05 | 27.4267 | 0.054534 | 0.55191
|  | 23:05 | 27.4278 | 0.085579 | 0.55191
|  | 23:05 | 27.4289 | 0.097447 | 0.55191
|  | 23:05 | 27.43 | 0.10931 | 0.5519
|  | 23:05 | 27.4311 | 0.11074 | 0.5519
|  | 23:05 | 27.4322 | 0.10868 | 0.5519
|  | 23:05 | 27.4333 | 0.10522 | 0.5519
|  | 23:05 | 27.4344 | 0.097578 | 0.55189
|  | 23:06 | 27.4356 | 0.089932 | 0.55189
|  | 23:06 | 27.4367 | 0.073569 | 0.55189
|  | 23:06 | 27.4378 | 0.048491 | 0.55189
|  | 23:06 | 27.4389 | 0.023412 | 0.55188
|  | 23:06 | 27.44 | 0.0095454 | 0.55188
|  | 23:06 | 27.4411 | -0.0043213 | 0.55188
|  | 23:06 | 27.4422 | -0.0022857 | 0.55188
|  | 23:06 | 27.4433 | 0.015652 | 0.55187
|  | 23:06 | 27.4444 | 0.03359 | 0.55187
|  | 23:06 | 27.4456 | 0.10038 | 0.55187
|  | 23:06 | 27.4467 | 0.16717 | 0.55187
|  | 23:06 | 27.4478 | 0.23184 | 0.55187
|  | 23:06 | 27.4489 | 0.29437 | 0.55186
|  | 23:06 | 27.45 | 0.35691 | 0.55186
|  | 23:06 | 27.4511 | 0.38203 | 0.55186
|  | 23:07 | 27.4522 | 0.40715 | 0.55186
|  | 23:07 | 27.4533 | 0.43669 | 0.55185
|  | 23:07 | 27.4544 | 0.47067 | 0.55185
|  | 23:07 | 27.4556 | 0.50464 | 0.55185
|  | 23:07 | 27.4567 | 0.51512 | 0.55185
|  | 23:07 | 27.4578 | 0.52559 | 0.55184
|  | 23:07 | 27.4589 | 0.54013 | 0.55184
|  | 23:07 | 27.46 | 0.55874 | 0.55184
|  | 23:07 | 27.4611 | 0.57735 | 0.55184
|  | 23:07 | 27.4622 | 0.57414 | 0.55184
|  | 23:07 | 27.4633 | 0.57092 | 0.55183
|  | 23:07 | 27.4644 | 0.57038 | 0.55183
|  | 23:07 | 27.4656 | 0.57251 | 0.55183
|  | 23:07 | 27.4667 | 0.57464 | 0.55183
|  | 23:07 | 27.4678 | 0.57446 | 0.55182
|  | 23:08 | 27.4689 | 0.57428 | 0.55182
|  | 23:08 | 27.47 | 0.56794 | 0.55182
|  | 23:08 | 27.4711 | 0.55544 | 0.55182
|  | 23:08 | 27.4722 | 0.54294 | 0.55181
|  | 23:08 | 27.4733 | 0.53362 | 0.55181
|  | 23:08 | 27.4744 | 0.52431 | 0.55181
|  | 23:08 | 27.4756 | 0.51346 | 0.55181
|  | 23:08 | 27.4767 | 0.50109 | 0.55181
|  | 23:08 | 27.4778 | 0.48871 | 0.5518
|  | 23:08 | 27.4789 | 0.46532 | 0.5518
|  | 23:08 | 27.48 | 0.44193 | 0.5518
|  | 23:08 | 27.4811 | 0.41736 | 0.5518
|  | 23:08 | 27.4822 | 0.39241 | 0.55179
|  | 23:08 | 27.4833 | 0.36745 | 0.55179
|  | 23:08 | 27.4844 | 0.32955 | 0.55179
|  | 23:09 | 27.4856 | 0.29165 | 0.55179
|  | 23:09 | 27.4867 | 0.25312 | 0.55178
|  | 23:09 | 27.4878 | 0.21396 | 0.55178
|  | 23:09 | 27.4889 | 0.1748 | 0.55178
|  | 23:09 | 27.49 | 0.11481 | 0.55178
|  | 23:09 | 27.4911 | 0.054818 | 0.55178
|  | 23:09 | 27.4922 | -0.0065868 | 0.55177
|  | 23:09 | 27.4933 | -0.068462 | 0.55177
|  | 23:09 | 27.4944 | -0.13034 | 0.55177
|  | 23:09 | 27.4956 | -0.17611 | 0.55177
|  | 23:09 | 27.4967 | -0.22189 | 0.55176
|  | 23:09 | 27.4978 | -0.26715 | 0.55176
|  | 23:09 | 27.4989 | -0.3119 | 0.55176
|  | 23:09 | 27.5 | -0.35665 | 0.55176
|  | 23:09 | 27.5011 | -0.39577 | 0.55175
|  | 23:10 | 27.5022 | -0.43489 | 0.55175
|  | 23:10 | 27.5033 | -0.45765 | 0.55175
|  | 23:10 | 27.5044 | -0.46406 | 0.55175
|  | 23:10 | 27.5056 | -0.47047 | 0.55175
|  | 23:10 | 27.5067 | -0.45239 | 0.55174
|  | 23:10 | 27.5078 | -0.4343 | 0.55174
|  | 23:10 | 27.5089 | -0.42879 | 0.55174
|  | 23:10 | 27.51 | -0.43588 | 0.55174
|  | 23:10 | 27.5111 | -0.44296 | 0.55173
|  | 23:10 | 27.5122 | -0.44646 | 0.55173
|  | 23:10 | 27.5133 | -0.44997 | 0.55173
|  | 23:10 | 27.5144 | -0.44712 | 0.55173
|  | 23:10 | 27.5156 | -0.43794 | 0.55172
|  | 23:10 | 27.5167 | -0.42875 | 0.55172
|  | 23:10 | 27.5178 | -0.42518 | 0.55172
|  | 23:11 | 27.5189 | -0.42161 | 0.55172
|  | 23:11 | 27.52 | -0.42556 | 0.55172
|  | 23:11 | 27.5211 | -0.43704 | 0.55171
|  | 23:11 | 27.5222 | -0.44852 | 0.55171
|  | 23:11 | 27.5233 | -0.44164 | 0.55171
|  | 23:11 | 27.5244 | -0.43475 | 0.55171
|  | 23:11 | 27.5256 | -0.42925 | 0.5517
|  | 23:11 | 27.5267 | -0.42513 | 0.5517
|  | 23:11 | 27.5278 | -0.421 | 0.5517
|  | 23:11 | 27.5289 | -0.40086 | 0.5517
|  | 23:11 | 27.53 | -0.38072 | 0.55169
|  | 23:11 | 27.5311 | -0.36457 | 0.55169
|  | 23:11 | 27.5322 | -0.35242 | 0.55169
|  | 23:11 | 27.5333 | -0.34187 | 0.55169
|  | 23:11 | 27.5344 | -0.33616 | 0.55169
|  | 23:12 | 27.5356 | -0.33044 | 0.55168
|  | 23:12 | 27.5367 | -0.31632 | 0.55168
|  | 23:12 | 27.5378 | -0.29381 | 0.55168
|  | 23:12 | 27.5389 | -0.2713 | 0.55168
|  | 23:12 | 27.54 | -0.25262 | 0.55167
|  | 23:12 | 27.5411 | -0.23394 | 0.55167
|  | 23:12 | 27.5422 | -0.21066 | 0.55167
|  | 23:12 | 27.5433 | -0.18278 | 0.55167
|  | 23:12 | 27.5444 | -0.1549 | 0.55166
|  | 23:12 | 27.5456 | -0.1598 | 0.55166
|  | 23:12 | 27.5467 | -0.1647 | 0.55166
|  | 23:12 | 27.5478 | -0.16862 | 0.55166
|  | 23:12 | 27.5489 | -0.17156 | 0.55166
|  | 23:12 | 27.55 | -0.17451 | 0.55165
|  | 23:12 | 27.5511 | -0.16854 | 0.55165
|  | 23:13 | 27.5522 | -0.16258 | 0.55165
|  | 23:13 | 27.5533 | -0.16124 | 0.55165
|  | 23:13 | 27.5544 | -0.16454 | 0.55164
|  | 23:13 | 27.5556 | -0.16783 | 0.55164
|  | 23:13 | 27.5567 | -0.15843 | 0.55164
|  | 23:13 | 27.5578 | -0.14903 | 0.55164
|  | 23:13 | 27.5589 | -0.12965 | 0.55163
|  | 23:13 | 27.56 | -0.10029 | 0.55163
|  | 23:13 | 27.5611 | -0.070943 | 0.55163
|  | 23:13 | 27.5622 | -0.066805 | 0.55163
|  | 23:13 | 27.5633 | -0.062667 | 0.55162
|  | 23:13 | 27.5644 | -0.054492 | 0.55162
|  | 23:13 | 27.5656 | -0.042281 | 0.55162
|  | 23:13 | 27.5667 | -0.030069 | 0.55162
|  | 23:13 | 27.5678 | -0.017858 | 0.55162
|  | 23:14 | 27.5689 | 0.0074794 | 0.55161
|  | 23:14 | 27.57 | 0.030449 | 0.55161
|  | 23:14 | 27.5711 | 0.046317 | 0.55161
|  | 23:14 | 27.5722 | 0.062185 | 0.55161
|  | 23:14 | 27.5733 | 0.082672 | 0.5516
|  | 23:14 | 27.5744 | 0.10316 | 0.5516
|  | 23:14 | 27.5756 | 0.12318 | 0.5516
|  | 23:14 | 27.5767 | 0.14273 | 0.5516
|  | 23:14 | 27.5778 | 0.16229 | 0.55159
|  | 23:14 | 27.5789 | 0.17597 | 0.55159
|  | 23:14 | 27.58 | 0.18965 | 0.55159
|  | 23:14 | 27.5811 | 0.21106 | 0.55159
|  | 23:14 | 27.5822 | 0.24018 | 0.55159
|  | 23:14 | 27.5833 | 0.2693 | 0.55158
|  | 23:14 | 27.5844 | 0.28985 | 0.55158
|  | 23:15 | 27.5856 | 0.3104 | 0.55158
|  | 23:15 | 27.5867 | 0.32411 | 0.55158
|  | 23:15 | 27.5878 | 0.33098 | 0.55157
|  | 23:15 | 27.5889 | 0.33785 | 0.55157
|  | 23:15 | 27.59 | 0.3406 | 0.55157
|  | 23:15 | 27.5911 | 0.34335 | 0.55157
|  | 23:15 | 27.5922 | 0.34433 | 0.55156
|  | 23:15 | 27.5933 | 0.34356 | 0.55156
|  | 23:15 | 27.5944 | 0.34278 | 0.55156
|  | 23:15 | 27.5956 | 0.3594 | 0.55156
|  | 23:15 | 27.5967 | 0.37602 | 0.55156
|  | 23:15 | 27.5978 | 0.39263 | 0.55155
|  | 23:15 | 27.5989 | 0.40925 | 0.55155
|  | 23:15 | 27.6 | 0.42587 | 0.55155
|  | 23:15 | 27.6011 | 0.4182 | 0.55155
|  | 23:16 | 27.6022 | 0.41053 | 0.55154
|  | 23:16 | 27.6033 | 0.39842 | 0.55154
|  | 23:16 | 27.6044 | 0.38187 | 0.55154
|  | 23:16 | 27.6056 | 0.36532 | 0.55154
|  | 23:16 | 27.6067 | 0.33087 | 0.55153
|  | 23:16 | 27.6078 | 0.29642 | 0.55153
|  | 23:16 | 27.6089 | 0.28083 | 0.55153
|  | 23:16 | 27.61 | 0.28412 | 0.55153
|  | 23:16 | 27.6111 | 0.2874 | 0.55153
|  | 23:16 | 27.6122 | 0.2724 | 0.55152
|  | 23:16 | 27.6133 | 0.2574 | 0.55152
|  | 23:16 | 27.6144 | 0.2361 | 0.55152
|  | 23:16 | 27.6156 | 0.2085 | 0.55152
|  | 23:16 | 27.6167 | 0.18089 | 0.55151
|  | 23:16 | 27.6178 | 0.14929 | 0.55151
|  | 23:17 | 27.6189 | 0.11769 | 0.55151
|  | 23:17 | 27.62 | 0.10424 | 0.55151
|  | 23:17 | 27.6211 | 0.096831 | 0.5515
|  | 23:17 | 27.6222 | 0.089426 | 0.5515
|  | 23:17 | 27.6233 | 0.072852 | 0.5515
|  | 23:17 | 27.6244 | 0.056277 | 0.5515
|  | 23:17 | 27.6256 | 0.041294 | 0.5515
|  | 23:17 | 27.6267 | 0.027902 | 0.55149
|  | 23:17 | 27.6278 | 0.01451 | 0.55149
|  | 23:17 | 27.6289 | -0.0091688 | 0.55149
|  | 23:17 | 27.63 | -0.032848 | 0.55149
|  | 23:17 | 27.6311 | -0.066966 | 0.55148
|  | 23:17 | 27.6322 | -0.11152 | 0.55148
|  | 23:17 | 27.6333 | -0.15608 | 0.55148
|  | 23:17 | 27.6344 | -0.17782 | 0.55148
|  | 23:18 | 27.6356 | -0.19956 | 0.55147
|  | 23:18 | 27.6367 | -0.21505 | 0.55147
|  | 23:18 | 27.6378 | -0.2243 | 0.55147
|  | 23:18 | 27.6389 | -0.23485 | 0.55147
|  | 23:18 | 27.64 | -0.24933 | 0.55147
|  | 23:18 | 27.6411 | -0.26381 | 0.55146
|  | 23:18 | 27.6422 | -0.28585 | 0.55146
|  | 23:18 | 27.6433 | -0.31041 | 0.55146
|  | 23:18 | 27.6444 | -0.33498 | 0.55146
|  | 23:18 | 27.6456 | -0.35433 | 0.55145
|  | 23:18 | 27.6467 | -0.37369 | 0.55145
|  | 23:18 | 27.6478 | -0.38334 | 0.55145
|  | 23:18 | 27.6489 | -0.38329 | 0.55145
|  | 23:18 | 27.65 | -0.38325 | 0.55144
|  | 23:18 | 27.6511 | -0.37177 | 0.55144
|  | 23:19 | 27.6522 | -0.36028 | 0.55144
|  | 23:19 | 27.6533 | -0.34955 | 0.55144
|  | 23:19 | 27.6544 | -0.33956 | 0.55144
|  | 23:19 | 27.6556 | -0.32957 | 0.55143
|  | 23:19 | 27.6567 | -0.32282 | 0.55143
|  | 23:19 | 27.6578 | -0.31608 | 0.55143
|  | 23:19 | 27.6589 | -0.30933 | 0.55143
|  | 23:19 | 27.66 | -0.30258 | 0.55142
|  | 23:19 | 27.6611 | -0.2977 | 0.55142
|  | 23:19 | 27.6622 | -0.29843 | 0.55142
|  | 23:19 | 27.6633 | -0.29916 | 0.55142
|  | 23:19 | 27.6644 | -0.3059 | 0.55141
|  | 23:19 | 27.6656 | -0.31865 | 0.55141
|  | 23:19 | 27.6667 | -0.33141 | 0.55141
|  | 23:19 | 27.6678 | -0.34928 | 0.55141
|  | 23:20 | 27.6689 | -0.36715 | 0.55141
|  | 23:20 | 27.67 | -0.36743 | 0.5514
|  | 23:20 | 27.6711 | -0.35014 | 0.5514
|  | 23:20 | 27.6722 | -0.33284 | 0.5514
|  | 23:20 | 27.6733 | -0.32614 | 0.5514
|  | 23:20 | 27.6744 | -0.31945 | 0.55139
|  | 23:20 | 27.6756 | -0.32347 | 0.55139
|  | 23:20 | 27.6767 | -0.33105 | 0.55139
|  | 23:20 | 27.6778 | -0.33863 | 0.55139
|  | 23:20 | 27.6789 | -0.34742 | 0.55138
|  | 23:20 | 27.68 | -0.35621 | 0.55138
|  | 23:20 | 27.6811 | -0.35525 | 0.55138
|  | 23:20 | 27.6822 | -0.34453 | 0.55138
|  | 23:20 | 27.6833 | -0.33382 | 0.55137
|  | 23:20 | 27.6844 | -0.32408 | 0.55137
|  | 23:21 | 27.6856 | -0.31435 | 0.55137
|  | 23:21 | 27.6867 | -0.29629 | 0.55137
|  | 23:21 | 27.6878 | -0.2699 | 0.55137
|  | 23:21 | 27.6889 | -0.24351 | 0.55136
|  | 23:21 | 27.69 | -0.22981 | 0.55136
|  | 23:21 | 27.6911 | -0.21611 | 0.55136
|  | 23:21 | 27.6922 | -0.19988 | 0.55136
|  | 23:21 | 27.6933 | -0.18112 | 0.55135
|  | 23:21 | 27.6944 | -0.16235 | 0.55135
|  | 23:21 | 27.6956 | -0.16142 | 0.55135
|  | 23:21 | 27.6967 | -0.16049 | 0.55135
|  | 23:21 | 27.6978 | -0.15389 | 0.55134
|  | 23:21 | 27.6989 | -0.14164 | 0.55134
|  | 23:21 | 27.7 | -0.12939 | 0.55134
|  | 23:21 | 27.7011 | -0.12526 | 0.55134
|  | 23:22 | 27.7022 | -0.12113 | 0.55134
|  | 23:22 | 27.7033 | -0.12313 | 0.55133
|  | 23:22 | 27.7044 | -0.13125 | 0.55133
|  | 23:22 | 27.7056 | -0.13938 | 0.55133
|  | 23:22 | 27.7067 | -0.13197 | 0.55133
|  | 23:22 | 27.7078 | -0.12456 | 0.55132
|  | 23:22 | 27.7089 | -0.11274 | 0.55132
|  | 23:22 | 27.71 | -0.096521 | 0.55132
|  | 23:22 | 27.7111 | -0.080302 | 0.55132
|  | 23:22 | 27.7122 | -0.054155 | 0.55131
|  | 23:22 | 27.7133 | -0.028008 | 0.55131
|  | 23:22 | 27.7144 | -0.0045076 | 0.55131
|  | 23:22 | 27.7156 | 0.016347 | 0.55131
|  | 23:22 | 27.7167 | 0.037201 | 0.55131
|  | 23:22 | 27.7178 | 0.038561 | 0.5513
|  | 23:23 | 27.7189 | 0.039921 | 0.5513
|  | 23:23 | 27.72 | 0.04462 | 0.5513
|  | 23:23 | 27.7211 | 0.052657 | 0.5513
|  | 23:23 | 27.7222 | 0.060695 | 0.55129
|  | 23:23 | 27.7233 | 0.062016 | 0.55129
|  | 23:23 | 27.7244 | 0.063337 | 0.55129
|  | 23:23 | 27.7256 | 0.059152 | 0.55129
|  | 23:23 | 27.7267 | 0.049461 | 0.55128
|  | 23:23 | 27.7278 | 0.039771 | 0.55128
|  | 23:23 | 27.7289 | 0.03008 | 0.55128
|  | 23:23 | 27.73 | 0.02039 | 0.55128
|  | 23:23 | 27.7311 | 0.012533 | 0.55128
|  | 23:23 | 27.7322 | 0.00651 | 0.55127
|  | 23:23 | 27.7333 | 0.00048686 | 0.55127
|  | 23:23 | 27.7344 | -0.0055363 | 0.55127
|  | 23:24 | 27.7356 | -0.028667 | 0.55127
|  | 23:24 | 27.7367 | -0.055754 | 0.55126
|  | 23:24 | 27.7378 | -0.094714 | 0.55126
|  | 23:24 | 27.7389 | -0.13367 | 0.55126
|  | 23:24 | 27.74 | -0.1564 | 0.55126
|  | 23:24 | 27.7411 | -0.17912 | 0.55125
|  | 23:24 | 27.7422 | -0.20465 | 0.55125
|  | 23:24 | 27.7433 | -0.23296 | 0.55125
|  | 23:24 | 27.7444 | -0.26128 | 0.55125
|  | 23:24 | 27.7456 | -0.28713 | 0.55125
|  | 23:24 | 27.7467 | -0.31299 | 0.55124
|  | 23:24 | 27.7478 | -0.3269 | 0.55124
|  | 23:24 | 27.7489 | -0.32887 | 0.55124
|  | 23:24 | 27.75 | -0.33084 | 0.55124
|  | 23:24 | 27.7511 | -0.34417 | 0.55123
|  | 23:25 | 27.7522 | -0.35749 | 0.55123
|  | 23:25 | 27.7533 | -0.36829 | 0.55123
|  | 23:25 | 27.7544 | -0.37657 | 0.55123
|  | 23:25 | 27.7556 | -0.38484 | 0.55122
|  | 23:25 | 27.7567 | -0.39763 | 0.55122
|  | 23:25 | 27.7578 | -0.41043 | 0.55122
|  | 23:25 | 27.7589 | -0.42784 | 0.55122
|  | 23:25 | 27.76 | -0.44987 | 0.55122
|  | 23:25 | 27.7611 | -0.4719 | 0.55121
|  | 23:25 | 27.7622 | -0.49075 | 0.55121
|  | 23:25 | 27.7633 | -0.50959 | 0.55121
|  | 23:25 | 27.7644 | -0.5272 | 0.55121
|  | 23:25 | 27.7656 | -0.54355 | 0.5512
|  | 23:25 | 27.7667 | -0.5599 | 0.5512
|  | 23:25 | 27.7678 | -0.58263 | 0.5512
|  | 23:26 | 27.7689 | -0.60537 | 0.5512
|  | 23:26 | 27.77 | -0.62365 | 0.55119
|  | 23:26 | 27.7711 | -0.63747 | 0.55119
|  | 23:26 | 27.7722 | -0.65129 | 0.55119
|  | 23:26 | 27.7733 | -0.65879 | 0.55119
|  | 23:26 | 27.7744 | -0.66629 | 0.55119
|  | 23:26 | 27.7756 | -0.67986 | 0.55118
|  | 23:26 | 27.7767 | -0.6995 | 0.55118
|  | 23:26 | 27.7778 | -0.71913 | 0.55118
|  | 23:26 | 27.7789 | -0.73168 | 0.55118
|  | 23:26 | 27.78 | -0.74423 | 0.55117
|  | 23:26 | 27.7811 | -0.7505 | 0.55117
|  | 23:26 | 27.7822 | -0.75049 | 0.55117
|  | 23:26 | 27.7833 | -0.75048 | 0.55117
|  | 23:26 | 27.7844 | -0.73916 | 0.55116
|  | 23:27 | 27.7856 | -0.72783 | 0.55116
|  | 23:27 | 27.7867 | -0.70987 | 0.55116
|  | 23:27 | 27.7878 | -0.68526 | 0.55116
|  | 23:27 | 27.7889 | -0.66066 | 0.55116
|  | 23:27 | 27.79 | -0.6495 | 0.55115
|  | 23:27 | 27.7911 | -0.63834 | 0.55115
|  | 23:27 | 27.7922 | -0.61665 | 0.55115
|  | 23:27 | 27.7933 | -0.58443 | 0.55115
|  | 23:27 | 27.7944 | -0.55221 | 0.55114
|  | 23:27 | 27.7956 | -0.51541 | 0.55114
|  | 23:27 | 27.7967 | -0.47861 | 0.55114
|  | 23:27 | 27.7978 | -0.44523 | 0.55114
|  | 23:27 | 27.7989 | -0.41524 | 0.55113
|  | 23:27 | 27.8 | -0.38526 | 0.55113
|  | 23:27 | 27.8011 | -0.37899 | 0.55113
|  | 23:28 | 27.8022 | -0.37271 | 0.55113
|  | 23:28 | 27.8033 | -0.37159 | 0.55112
|  | 23:28 | 27.8044 | -0.37563 | 0.55112
|  | 23:28 | 27.8056 | -0.37966 | 0.55112
|  | 23:28 | 27.8067 | -0.36377 | 0.55112
|  | 23:28 | 27.8078 | -0.34788 | 0.55112
|  | 23:28 | 27.8089 | -0.32774 | 0.55111
|  | 23:28 | 27.81 | -0.30335 | 0.55111
|  | 23:28 | 27.8111 | -0.27896 | 0.55111
|  | 23:28 | 27.8122 | -0.25074 | 0.55111
|  | 23:28 | 27.8133 | -0.22252 | 0.5511
|  | 23:28 | 27.8144 | -0.19509 | 0.5511
|  | 23:28 | 27.8156 | -0.16792 | 0.5511
|  | 23:28 | 27.8167 | -0.14272 | 0.5511
|  | 23:28 | 27.8178 | -0.12345 | 0.55109
|  | 23:29 | 27.8189 | -0.10417 | 0.55109
|  | 23:29 | 27.82 | -0.087397 | 0.55109
|  | 23:29 | 27.8211 | -0.07313 | 0.55109
|  | 23:29 | 27.8222 | -0.058863 | 0.55109
|  | 23:29 | 27.8233 | -0.061269 | 0.55108
|  | 23:29 | 27.8244 | -0.063676 | 0.55108
|  | 23:29 | 27.8256 | -0.065522 | 0.55108
|  | 23:29 | 27.8267 | -0.066808 | 0.55108
|  | 23:29 | 27.8278 | -0.068094 | 0.55107
|  | 23:29 | 27.8289 | -0.075492 | 0.55107
|  | 23:29 | 27.83 | -0.08289 | 0.55107
|  | 23:29 | 27.8311 | -0.09073 | 0.55107
|  | 23:29 | 27.8322 | -0.099014 | 0.55106
|  | 23:29 | 27.8333 | -0.1073 | 0.55106
|  | 23:29 | 27.8344 | -0.089359 | 0.55106
|  | 23:30 | 27.8356 | -0.071421 | 0.55106
|  | 23:30 | 27.8367 | -0.049309 | 0.55106
|  | 23:30 | 27.8378 | -0.023023 | 0.55105
|  | 23:30 | 27.8389 | 0.0032623 | 0.55105
|  | 23:30 | 27.84 | 0.016532 | 0.55105
|  | 23:30 | 27.8411 | 0.029801 | 0.55105
|  | 23:30 | 27.8422 | 0.036497 | 0.55104
|  | 23:30 | 27.8433 | 0.03662 | 0.55104
|  | 23:30 | 27.8444 | 0.036742 | 0.55104
|  | 23:30 | 27.8456 | 0.031934 | 0.55104
|  | 23:30 | 27.8467 | 0.027126 | 0.55103
|  | 23:30 | 27.8478 | 0.038487 | 0.55103
|  | 23:30 | 27.8489 | 0.06602 | 0.55103
|  | 23:30 | 27.85 | 0.093552 | 0.55103
|  | 23:30 | 27.8511 | 0.12924 | 0.55103
|  | 23:31 | 27.8522 | 0.16492 | 0.55102
|  | 23:31 | 27.8533 | 0.19135 | 0.55102
|  | 23:31 | 27.8544 | 0.20853 | 0.55102
|  | 23:31 | 27.8556 | 0.2257 | 0.55102
|  | 23:31 | 27.8567 | 0.2251 | 0.55101
|  | 23:31 | 27.8578 | 0.22449 | 0.55101
|  | 23:31 | 27.8589 | 0.21902 | 0.55101
|  | 23:31 | 27.86 | 0.2087 | 0.55101
|  | 23:31 | 27.8611 | 0.19838 | 0.551
|  | 23:31 | 27.8622 | 0.17104 | 0.551
|  | 23:31 | 27.8633 | 0.14371 | 0.551
|  | 23:31 | 27.8644 | 0.12041 | 0.551
|  | 23:31 | 27.8656 | 0.10116 | 0.551
|  | 23:31 | 27.8667 | 0.081902 | 0.55099
|  | 23:31 | 27.8678 | 0.099815 | 0.55099
|  | 23:32 | 27.8689 | 0.11773 | 0.55099
|  | 23:32 | 27.87 | 0.13342 | 0.55099
|  | 23:32 | 27.8711 | 0.14689 | 0.55098
|  | 23:32 | 27.8722 | 0.16036 | 0.55098
|  | 23:32 | 27.8733 | 0.17384 | 0.55098
|  | 23:32 | 27.8744 | 0.18731 | 0.55098
|  | 23:32 | 27.8756 | 0.20476 | 0.55097
|  | 23:32 | 27.8767 | 0.22619 | 0.55097
|  | 23:32 | 27.8778 | 0.24763 | 0.55097
|  | 23:32 | 27.8789 | 0.26643 | 0.55097
|  | 23:32 | 27.88 | 0.28523 | 0.55097
|  | 23:32 | 27.8811 | 0.29984 | 0.55096
|  | 23:32 | 27.8822 | 0.31025 | 0.55096
|  | 23:32 | 27.8833 | 0.32066 | 0.55096
|  | 23:32 | 27.8844 | 0.33434 | 0.55096
|  | 23:33 | 27.8856 | 0.34802 | 0.55095
|  | 23:33 | 27.8867 | 0.36502 | 0.55095
|  | 23:33 | 27.8878 | 0.38533 | 0.55095
|  | 23:33 | 27.8889 | 0.40565 | 0.55095
|  | 23:33 | 27.89 | 0.42159 | 0.55094
|  | 23:33 | 27.8911 | 0.43753 | 0.55094
|  | 23:33 | 27.8922 | 0.45058 | 0.55094
|  | 23:33 | 27.8933 | 0.46075 | 0.55094
|  | 23:33 | 27.8944 | 0.47091 | 0.55094
|  | 23:33 | 27.8956 | 0.47039 | 0.55093
|  | 23:33 | 27.8967 | 0.46987 | 0.55093
|  | 23:33 | 27.8978 | 0.46317 | 0.55093
|  | 23:33 | 27.8989 | 0.45441 | 0.55093
|  | 23:33 | 27.9 | 0.44565 | 0.55092
|  | 23:33 | 27.9011 | 0.42328 | 0.55092
|  | 23:34 | 27.9022 | 0.4009 | 0.55092
|  | 23:34 | 27.9033 | 0.38572 | 0.55092
|  | 23:34 | 27.9044 | 0.39211 | 0.55091
|  | 23:34 | 27.9056 | 0.3985 | 0.55091
|  | 23:34 | 27.9067 | 0.4237 | 0.55091
|  | 23:34 | 27.9078 | 0.4489 | 0.55091
|  | 23:34 | 27.9089 | 0.46088 | 0.55091
|  | 23:34 | 27.91 | 0.45964 | 0.5509
|  | 23:34 | 27.9111 | 0.45841 | 0.5509
|  | 23:34 | 27.9122 | 0.4475 | 0.5509
|  | 23:34 | 27.9133 | 0.43659 | 0.5509
|  | 23:34 | 27.9144 | 0.42325 | 0.55089
|  | 23:34 | 27.9156 | 0.40749 | 0.55089
|  | 23:34 | 27.9167 | 0.39172 | 0.55089
|  | 23:34 | 27.9178 | 0.40531 | 0.55089
|  | 23:35 | 27.9189 | 0.4189 | 0.55088
|  | 23:35 | 27.92 | 0.43151 | 0.55088
|  | 23:35 | 27.9211 | 0.44314 | 0.55088
|  | 23:35 | 27.9222 | 0.45477 | 0.55088
|  | 23:35 | 27.9233 | 0.4521 | 0.55087
|  | 23:35 | 27.9244 | 0.44943 | 0.55087
|  | 23:35 | 27.9256 | 0.43991 | 0.55087
|  | 23:35 | 27.9267 | 0.42354 | 0.55087
|  | 23:35 | 27.9278 | 0.40717 | 0.55087
|  | 23:35 | 27.9289 | 0.40518 | 0.55086
|  | 23:35 | 27.93 | 0.40319 | 0.55086
|  | 23:35 | 27.9311 | 0.41374 | 0.55086
|  | 23:35 | 27.9322 | 0.43682 | 0.55086
|  | 23:35 | 27.9333 | 0.45991 | 0.55085
|  | 23:35 | 27.9344 | 0.48429 | 0.55085
|  | 23:36 | 27.9356 | 0.50867 | 0.55085
|  | 23:36 | 27.9367 | 0.52763 | 0.55085
|  | 23:36 | 27.9378 | 0.54478 | 0.55084
|  | 23:36 | 27.9389 | 0.56194 | 0.55084
|  | 23:36 | 27.94 | 0.57207 | 0.55084
|  | 23:36 | 27.9411 | 0.58221 | 0.55084
|  | 23:36 | 27.9422 | 0.58718 | 0.55084
|  | 23:36 | 27.9433 | 0.58698 | 0.55083
|  | 23:36 | 27.9444 | 0.58678 | 0.55083
|  | 23:36 | 27.9456 | 0.60128 | 0.55083
|  | 23:36 | 27.9467 | 0.61578 | 0.55083
|  | 23:36 | 27.9478 | 0.62143 | 0.55082
|  | 23:36 | 27.9489 | 0.61825 | 0.55082
|  | 23:36 | 27.95 | 0.61506 | 0.55082
|  | 23:36 | 27.9511 | 0.62239 | 0.55082
|  | 23:37 | 27.9522 | 0.62971 | 0.55081
|  | 23:37 | 27.9533 | 0.63355 | 0.55081
|  | 23:37 | 27.9544 | 0.6339 | 0.55081
|  | 23:37 | 27.9556 | 0.63907 | 0.55081
|  | 23:37 | 27.9567 | 0.65868 | 0.55081
|  | 23:37 | 27.9578 | 0.6783 | 0.5508
|  | 23:37 | 27.9589 | 0.69792 | 0.5508
|  | 23:37 | 27.96 | 0.71754 | 0.5508
|  | 23:37 | 27.9611 | 0.73715 | 0.5508
|  | 23:37 | 27.9622 | 0.75945 | 0.55079
|  | 23:37 | 27.9633 | 0.78175 | 0.55079
|  | 23:37 | 27.9644 | 0.79371 | 0.55079
|  | 23:37 | 27.9656 | 0.79532 | 0.55079
|  | 23:37 | 27.9667 | 0.79693 | 0.55078
|  | 23:37 | 27.9678 | 0.81251 | 0.55078
|  | 23:38 | 27.9689 | 0.82809 | 0.55078
|  | 23:38 | 27.97 | 0.83863 | 0.55078
|  | 23:38 | 27.9711 | 0.84413 | 0.55078
|  | 23:38 | 27.9722 | 0.84963 | 0.55077
|  | 23:38 | 27.9733 | 0.82497 | 0.55077
|  | 23:38 | 27.9744 | 0.8003 | 0.55077
|  | 23:38 | 27.9756 | 0.77953 | 0.55077
|  | 23:38 | 27.9767 | 0.76265 | 0.55076
|  | 23:38 | 27.9778 | 0.74578 | 0.55076
|  | 23:38 | 27.9789 | 0.7289 | 0.55076
|  | 23:38 | 27.98 | 0.71203 | 0.55076
|  | 23:38 | 27.9811 | 0.69599 | 0.55075
|  | 23:38 | 27.9822 | 0.68079 | 0.55075
|  | 23:38 | 27.9833 | 0.66559 | 0.55075
|  | 23:38 | 27.9844 | 0.65039 | 0.55075
|  | 23:39 | 27.9856 | 0.63519 | 0.55075
|  | 23:39 | 27.9867 | 0.6287 | 0.55074
|  | 23:39 | 27.9878 | 0.62511 | 0.55074
|  | 23:39 | 27.9889 | 0.62152 | 0.55074
|  | 23:39 | 27.99 | 0.60905 | 0.55074
|  | 23:39 | 27.9911 | 0.59658 | 0.55073
|  | 23:39 | 27.9922 | 0.59451 | 0.55073
|  | 23:39 | 27.9933 | 0.60285 | 0.55073
|  | 23:39 | 27.9944 | 0.61119 | 0.55073
|  | 23:39 | 27.9956 | 0.62747 | 0.55072
|  | 23:39 | 27.9967 | 0.64374 | 0.55072
|  | 23:39 | 27.9978 | 0.64699 | 0.55072
|  | 23:39 | 27.9989 | 0.6372 | 0.55072
|  | 23:39 | 28 | 0.62494 | 0.55072
|  | 23:39 | 28.0011 | 0.60529 | 0.55071
|  | 23:40 | 28.0022 | 0.58564 | 0.55071
|  | 23:40 | 28.0033 | 0.56408 | 0.55071
|  | 23:40 | 28.0044 | 0.54061 | 0.55071
|  | 23:40 | 28.0056 | 0.51713 | 0.5507
|  | 23:40 | 28.0067 | 0.50205 | 0.5507
|  | 23:40 | 28.0078 | 0.48696 | 0.5507
|  | 23:40 | 28.0089 | 0.46771 | 0.5507
|  | 23:40 | 28.01 | 0.4443 | 0.55069
|  | 23:40 | 28.0111 | 0.4209 | 0.55069
|  | 23:40 | 28.0122 | 0.38558 | 0.55069
|  | 23:40 | 28.0133 | 0.35026 | 0.55069
|  | 23:40 | 28.0144 | 0.31233 | 0.55069
|  | 23:40 | 28.0156 | 0.27179 | 0.55068
|  | 23:40 | 28.0167 | 0.23124 | 0.55068
|  | 23:40 | 28.0178 | 0.20065 | 0.55068
|  | 23:41 | 28.0189 | 0.17005 | 0.55068
|  | 23:41 | 28.02 | 0.14077 | 0.55067
|  | 23:41 | 28.0211 | 0.11281 | 0.55067
|  | 23:41 | 28.0222 | 0.084842 | 0.55067
|  | 23:41 | 28.0233 | 0.038603 | 0.55067
|  | 23:41 | 28.0244 | -0.0076366 | 0.55066
|  | 23:41 | 28.0256 | -0.047739 | 0.55066
|  | 23:41 | 28.0267 | -0.081703 | 0.55066
|  | 23:41 | 28.0278 | -0.11567 | 0.55066
|  | 23:41 | 28.0289 | -0.13646 | 0.55066
|  | 23:41 | 28.03 | -0.15725 | 0.55065
|  | 23:41 | 28.0311 | -0.18325 | 0.55065
|  | 23:41 | 28.0322 | -0.21444 | 0.55065
|  | 23:41 | 28.0333 | -0.24563 | 0.55065
|  | 23:41 | 28.0344 | -0.2745 | 0.55064
|  | 23:42 | 28.0356 | -0.30336 | 0.55064
|  | 23:42 | 28.0367 | -0.34175 | 0.55064
|  | 23:42 | 28.0378 | -0.38967 | 0.55064
|  | 23:42 | 28.0389 | -0.42638 | 0.55063
|  | 23:42 | 28.04 | -0.42948 | 0.55063
|  | 23:42 | 28.0411 | -0.43258 | 0.55063
|  | 23:42 | 28.0422 | -0.44921 | 0.55063
|  | 23:42 | 28.0433 | -0.47935 | 0.55062
|  | 23:42 | 28.0444 | -0.5095 | 0.55062
|  | 23:42 | 28.0456 | -0.53188 | 0.55062
|  | 23:42 | 28.0467 | -0.55427 | 0.55062
|  | 23:42 | 28.0478 | -0.57911 | 0.55062
|  | 23:42 | 28.0489 | -0.60641 | 0.55061
|  | 23:42 | 28.05 | -0.63371 | 0.55061
|  | 23:42 | 28.0511 | -0.64927 | 0.55061
|  | 23:43 | 28.0522 | -0.66484 | 0.55061
|  | 23:43 | 28.0533 | -0.6804 | 0.5506
|  | 23:43 | 28.0544 | -0.69596 | 0.5506
|  | 23:43 | 28.0556 | -0.71153 | 0.5506
|  | 23:43 | 28.0567 | -0.72418 | 0.5506
|  | 23:43 | 28.0578 | -0.73684 | 0.55059
|  | 23:43 | 28.0589 | -0.73522 | 0.55059
|  | 23:43 | 28.06 | -0.71932 | 0.55059
|  | 23:43 | 28.0611 | -0.70341 | 0.55059
|  | 23:43 | 28.0622 | -0.67074 | 0.55059
|  | 23:43 | 28.0633 | -0.63806 | 0.55058
|  | 23:43 | 28.0644 | -0.60994 | 0.55058
|  | 23:43 | 28.0656 | -0.58635 | 0.55058
|  | 23:43 | 28.0667 | -0.56277 | 0.55058
|  | 23:43 | 28.0678 | -0.53527 | 0.55057
|  | 23:44 | 28.0689 | -0.50776 | 0.55057
|  | 23:44 | 28.07 | -0.48763 | 0.55057
|  | 23:44 | 28.0711 | -0.48964 | 0.55057
|  | 23:44 | 28.0722 | -0.49165 | 0.55056
|  | 23:44 | 28.0733 | -0.49001 | 0.55056
|  | 23:44 | 28.0744 | -0.48837 | 0.55056
|  | 23:44 | 28.0756 | -0.48899 | 0.55056
|  | 23:44 | 28.0767 | -0.49188 | 0.55056
|  | 23:44 | 28.0778 | -0.49352 | 0.55055
|  | 23:44 | 28.0789 | -0.49142 | 0.55055
|  | 23:44 | 28.08 | -0.48932 | 0.55055
|  | 23:44 | 28.0811 | -0.49175 | 0.55055
|  | 23:44 | 28.0822 | -0.4987 | 0.55054
|  | 23:44 | 28.0833 | -0.50565 | 0.55054
|  | 23:44 | 28.0844 | -0.50288 | 0.55054
|  | 23:45 | 28.0856 | -0.50011 | 0.55054
|  | 23:45 | 28.0867 | -0.48826 | 0.55053
|  | 23:45 | 28.0878 | -0.46731 | 0.55053
|  | 23:45 | 28.0889 | -0.44636 | 0.55053
|  | 23:45 | 28.09 | -0.413 | 0.55053
|  | 23:45 | 28.0911 | -0.37965 | 0.55053
|  | 23:45 | 28.0922 | -0.35026 | 0.55052
|  | 23:45 | 28.0933 | -0.32485 | 0.55052
|  | 23:45 | 28.0944 | -0.29944 | 0.55052
|  | 23:45 | 28.0956 | -0.27642 | 0.55052
|  | 23:45 | 28.0967 | -0.2534 | 0.55051
|  | 23:45 | 28.0978 | -0.236 | 0.55051
|  | 23:45 | 28.0989 | -0.22421 | 0.55051
|  | 23:45 | 28.1 | -0.21242 | 0.55051
|  | 23:45 | 28.1011 | -0.18995 | 0.5505
|  | 23:46 | 28.1022 | -0.16749 | 0.5505
|  | 23:46 | 28.1033 | -0.14283 | 0.5505
|  | 23:46 | 28.1044 | -0.11597 | 0.5505
|  | 23:46 | 28.1056 | -0.089118 | 0.5505
|  | 23:46 | 28.1067 | -0.051508 | 0.55049
|  | 23:46 | 28.1078 | -0.013898 | 0.55049
|  | 23:46 | 28.1089 | 0.024607 | 0.55049
|  | 23:46 | 28.11 | 0.064006 | 0.55049
|  | 23:46 | 28.1111 | 0.1034 | 0.55048
|  | 23:46 | 28.1122 | 0.12872 | 0.55048
|  | 23:46 | 28.1133 | 0.15403 | 0.55048
|  | 23:46 | 28.1144 | 0.16833 | 0.55048
|  | 23:46 | 28.1156 | 0.17161 | 0.55047
|  | 23:46 | 28.1167 | 0.1749 | 0.55047
|  | 23:46 | 28.1178 | 0.19225 | 0.55047
|  | 23:47 | 28.1189 | 0.2096 | 0.55047
|  | 23:47 | 28.12 | 0.23125 | 0.55047
|  | 23:47 | 28.1211 | 0.25433 | 0.55046
|  | 23:47 | 28.1222 | 0.28118 | 0.55046
|  | 23:47 | 28.1233 | 0.3193 | 0.55046
|  | 23:47 | 28.1244 | 0.35742 | 0.55046
|  | 23:47 | 28.1256 | 0.37481 | 0.55045
|  | 23:47 | 28.1267 | 0.37146 | 0.55045
|  | 23:47 | 28.1278 | 0.36812 | 0.55045
|  | 23:47 | 28.1289 | 0.36814 | 0.55045
|  | 23:47 | 28.13 | 0.36817 | 0.55044
|  | 23:47 | 28.1311 | 0.36493 | 0.55044
|  | 23:47 | 28.1322 | 0.35842 | 0.55044
|  | 23:47 | 28.1333 | 0.35192 | 0.55044
|  | 23:47 | 28.1344 | 0.35745 | 0.55044
|  | 23:48 | 28.1356 | 0.36298 | 0.55043
|  | 23:48 | 28.1367 | 0.38439 | 0.55043
|  | 23:48 | 28.1378 | 0.42166 | 0.55043
|  | 23:48 | 28.1389 | 0.45893 | 0.55043
|  | 23:48 | 28.14 | 0.50834 | 0.55042
|  | 23:48 | 28.1411 | 0.55774 | 0.55042
|  | 23:48 | 28.1422 | 0.59714 | 0.55042
|  | 23:48 | 28.1433 | 0.62655 | 0.55042
|  | 23:48 | 28.1444 | 0.65595 | 0.55041
|  | 23:48 | 28.1456 | 0.68535 | 0.55041
|  | 23:48 | 28.1467 | 0.71475 | 0.55041
|  | 23:48 | 28.1478 | 0.7405 | 0.55041
|  | 23:48 | 28.1489 | 0.7626 | 0.55041
|  | 23:48 | 28.15 | 0.7847 | 0.5504
|  | 23:48 | 28.1511 | 0.78996 | 0.5504
|  | 23:49 | 28.1522 | 0.79522 | 0.5504
|  | 23:49 | 28.1533 | 0.80048 | 0.5504
|  | 23:49 | 28.1544 | 0.80574 | 0.55039
|  | 23:49 | 28.1556 | 0.811 | 0.55039
|  | 23:49 | 28.1567 | 0.80302 | 0.55039
|  | 23:49 | 28.1578 | 0.79504 | 0.55039
|  | 23:49 | 28.1589 | 0.78335 | 0.55038
|  | 23:49 | 28.16 | 0.76794 | 0.55038
|  | 23:49 | 28.1611 | 0.75254 | 0.55038
|  | 23:49 | 28.1622 | 0.73713 | 0.55038
|  | 23:49 | 28.1633 | 0.72173 | 0.55037
|  | 23:49 | 28.1644 | 0.70357 | 0.55037
|  | 23:49 | 28.1656 | 0.68266 | 0.55037
|  | 23:49 | 28.1667 | 0.66175 | 0.55037
|  | 23:49 | 28.1678 | 0.62242 | 0.55037
|  | 23:50 | 28.1689 | 0.58309 | 0.55036
|  | 23:50 | 28.17 | 0.54171 | 0.55036
|  | 23:50 | 28.1711 | 0.49829 | 0.55036
|  | 23:50 | 28.1722 | 0.45486 | 0.55036
|  | 23:50 | 28.1733 | 0.42925 | 0.55035
|  | 23:50 | 28.1744 | 0.40363 | 0.55035
|  | 23:50 | 28.1756 | 0.37379 | 0.55035
|  | 23:50 | 28.1767 | 0.33971 | 0.55035
|  | 23:50 | 28.1778 | 0.30564 | 0.55034
|  | 23:50 | 28.1789 | 0.27379 | 0.55034
|  | 23:50 | 28.18 | 0.24194 | 0.55034
|  | 23:50 | 28.1811 | 0.22435 | 0.55034
|  | 23:50 | 28.1822 | 0.22102 | 0.55034
|  | 23:50 | 28.1833 | 0.21769 | 0.55033
|  | 23:50 | 28.1844 | 0.20566 | 0.55033
|  | 23:51 | 28.1856 | 0.19362 | 0.55033
|  | 23:51 | 28.1867 | 0.18466 | 0.55033
|  | 23:51 | 28.1878 | 0.17879 | 0.55032
|  | 23:51 | 28.1889 | 0.17291 | 0.55032
|  | 23:51 | 28.19 | 0.16918 | 0.55032
|  | 23:51 | 28.1911 | 0.16545 | 0.55032
|  | 23:51 | 28.1922 | 0.15742 | 0.55031
|  | 23:51 | 28.1933 | 0.14511 | 0.55031
|  | 23:51 | 28.1944 | 0.13279 | 0.55031
|  | 23:51 | 28.1956 | 0.11944 | 0.55031
|  | 23:51 | 28.1967 | 0.10609 | 0.55031
|  | 23:51 | 28.1978 | 0.093734 | 0.5503
|  | 23:51 | 28.1989 | 0.082374 | 0.5503
|  | 23:51 | 28.2 | 0.071013 | 0.5503
|  | 23:51 | 28.2011 | 0.066403 | 0.5503
|  | 23:52 | 28.2022 | 0.061792 | 0.55029
|  | 23:52 | 28.2033 | 0.057755 | 0.55029
|  | 23:52 | 28.2044 | 0.05429 | 0.55029
|  | 23:52 | 28.2056 | 0.050825 | 0.55029
|  | 23:52 | 28.2067 | 0.032276 | 0.55028
|  | 23:52 | 28.2078 | 0.013726 | 0.55028
|  | 23:52 | 28.2089 | -0.0155 | 0.55028
|  | 23:52 | 28.21 | -0.055402 | 0.55028
|  | 23:52 | 28.2111 | -0.095305 | 0.55028
|  | 23:52 | 28.2122 | -0.1476 | 0.55027
|  | 23:52 | 28.2133 | -0.19989 | 0.55027
|  | 23:52 | 28.2144 | -0.25319 | 0.55027
|  | 23:52 | 28.2156 | -0.30752 | 0.55027
|  | 23:52 | 28.2167 | -0.36184 | 0.55026
|  | 23:52 | 28.2178 | -0.40614 | 0.55026
|  | 23:53 | 28.2189 | -0.45044 | 0.55026
|  | 23:53 | 28.22 | -0.48112 | 0.55026
|  | 23:53 | 28.2211 | -0.49819 | 0.55025
|  | 23:53 | 28.2222 | -0.51526 | 0.55025
|  | 23:53 | 28.2233 | -0.54146 | 0.55025
|  | 23:53 | 28.2244 | -0.56767 | 0.55025
|  | 23:53 | 28.2256 | -0.58665 | 0.55025
|  | 23:53 | 28.2267 | -0.59843 | 0.55024
|  | 23:53 | 28.2278 | -0.6102 | 0.55024
|  | 23:53 | 28.2289 | -0.60745 | 0.55024
|  | 23:53 | 28.23 | -0.6047 | 0.55024
|  | 23:53 | 28.2311 | -0.60347 | 0.55023
|  | 23:53 | 28.2322 | -0.60376 | 0.55023
|  | 23:53 | 28.2333 | -0.60405 | 0.55023
|  | 23:53 | 28.2344 | -0.60336 | 0.55023
|  | 23:54 | 28.2356 | -0.60266 | 0.55022
|  | 23:54 | 28.2367 | -0.60291 | 0.55022
|  | 23:54 | 28.2378 | -0.60599 | 0.55022
|  | 23:54 | 28.2389 | -0.60906 | 0.55022
|  | 23:54 | 28.24 | -0.61077 | 0.55022
|  | 23:54 | 28.2411 | -0.61248 | 0.55021
|  | 23:54 | 28.2422 | -0.6045 | 0.55021
|  | 23:54 | 28.2433 | -0.58685 | 0.55021
|  | 23:54 | 28.2444 | -0.56919 | 0.55021
|  | 23:54 | 28.2456 | -0.55636 | 0.5502
|  | 23:54 | 28.2467 | -0.54352 | 0.5502
|  | 23:54 | 28.2478 | -0.53564 | 0.5502
|  | 23:54 | 28.2489 | -0.53272 | 0.5502
|  | 23:54 | 28.25 | -0.5298 | 0.55019
|  | 23:54 | 28.2511 | -0.529 | 0.55019
|  | 23:55 | 28.2522 | -0.52819 | 0.55019
|  | 23:55 | 28.2533 | -0.53152 | 0.55019
|  | 23:55 | 28.2544 | -0.539 | 0.55019
|  | 23:55 | 28.2556 | -0.54647 | 0.55018
|  | 23:55 | 28.2567 | -0.54635 | 0.55018
|  | 23:55 | 28.2578 | -0.54623 | 0.55018
|  | 23:55 | 28.2589 | -0.54252 | 0.55018
|  | 23:55 | 28.26 | -0.53522 | 0.55017
|  | 23:55 | 28.2611 | -0.52791 | 0.55017
|  | 23:55 | 28.2622 | -0.51653 | 0.55017
|  | 23:55 | 28.2633 | -0.50516 | 0.55017
|  | 23:55 | 28.2644 | -0.47674 | 0.55016
|  | 23:55 | 28.2656 | -0.43128 | 0.55016
|  | 23:55 | 28.2667 | -0.38582 | 0.55016
|  | 23:55 | 28.2678 | -0.34134 | 0.55016
|  | 23:56 | 28.2689 | -0.29686 | 0.55016
|  | 23:56 | 28.27 | -0.25636 | 0.55015
|  | 23:56 | 28.2711 | -0.21982 | 0.55015
|  | 23:56 | 28.2722 | -0.18329 | 0.55015
|  | 23:56 | 28.2733 | -0.16697 | 0.55015
|  | 23:56 | 28.2744 | -0.15066 | 0.55014
|  | 23:56 | 28.2756 | -0.13059 | 0.55014
|  | 23:56 | 28.2767 | -0.10676 | 0.55014
|  | 23:56 | 28.2778 | -0.082929 | 0.55014
|  | 23:56 | 28.2789 | -0.064992 | 0.55013
|  | 23:56 | 28.28 | -0.047054 | 0.55013
|  | 23:56 | 28.2811 | -0.033677 | 0.55013
|  | 23:56 | 28.2822 | -0.024861 | 0.55013
|  | 23:56 | 28.2833 | -0.016045 | 0.55012
|  | 23:56 | 28.2844 | -0.015577 | 0.55012
|  | 23:57 | 28.2856 | -0.01511 | 0.55012
|  | 23:57 | 28.2867 | -0.032247 | 0.55012
|  | 23:57 | 28.2878 | -0.066986 | 0.55012
|  | 23:57 | 28.2889 | -0.10173 | 0.55011
|  | 23:57 | 28.29 | -0.11422 | 0.55011
|  | 23:57 | 28.2911 | -0.12672 | 0.55011
|  | 23:57 | 28.2922 | -0.14071 | 0.55011
|  | 23:57 | 28.2933 | -0.15619 | 0.5501
|  | 23:57 | 28.2944 | -0.17167 | 0.5501
|  | 23:57 | 28.2956 | -0.18715 | 0.5501
|  | 23:57 | 28.2967 | -0.20263 | 0.5501
|  | 23:57 | 28.2978 | -0.22463 | 0.55009
|  | 23:57 | 28.2989 | -0.25316 | 0.55009
|  | 23:57 | 28.3 | -0.28168 | 0.55009
|  | 23:57 | 28.3011 | -0.29777 | 0.55009
|  | 23:58 | 28.3022 | -0.31386 | 0.55009
|  | 23:58 | 28.3033 | -0.31394 | 0.55008
|  | 23:58 | 28.3044 | -0.298 | 0.55008
|  | 23:58 | 28.3056 | -0.28207 | 0.55008
|  | 23:58 | 28.3067 | -0.26097 | 0.55008
|  | 23:58 | 28.3078 | -0.23987 | 0.55007
|  | 23:58 | 28.3089 | -0.2201 | 0.55007
|  | 23:58 | 28.31 | -0.20168 | 0.55007
|  | 23:58 | 28.3111 | -0.18325 | 0.55007
|  | 23:58 | 28.3122 | -0.16685 | 0.55006
|  | 23:58 | 28.3133 | -0.15045 | 0.55006
|  | 23:58 | 28.3144 | -0.13497 | 0.55006
|  | 23:58 | 28.3156 | -0.1204 | 0.55006
|  | 23:58 | 28.3167 | -0.10583 | 0.55006
|  | 23:58 | 28.3178 | -0.085856 | 0.55005
|  | 23:59 | 28.3189 | -0.065882 | 0.55005
|  | 23:59 | 28.32 | -0.057483 | 0.55005
|  | 23:59 | 28.3211 | -0.060658 | 0.55005
|  | 23:59 | 28.3222 | -0.063833 | 0.55004
|  | 23:59 | 28.3233 | -0.042603 | 0.55004
|  | 23:59 | 28.3244 | -0.021374 | 0.55004
|  | 23:59 | 28.3256 | -0.0021204 | 0.55004
|  | 23:59 | 28.3267 | 0.015157 | 0.55003
|  | 23:59 | 28.3278 | 0.032435 | 0.55003
|  | 23:59 | 28.3289 | 0.024561 | 0.55003
|  | 23:59 | 28.33 | 0.016687 | 0.55003
|  | 23:59 | 28.3311 | 0.012389 | 0.55003
|  | 23:59 | 28.3322 | 0.011665 | 0.55002
|  | 23:59 | 28.3333 | 0.010942 | 0.55002
|  | 23:59 | 28.3344 | 0.002515 | 0.55002
|  | 24:00 | 28.3356 | -0.0059115 | 0.55002
|  | 24:00 | 28.3367 | -0.026255 | 0.55001
|  | 24:00 | 28.3378 | -0.058516 | 0.55001
|  | 24:00 | 28.3389 | -0.090777 | 0.55001
|  | 24:00 | 28.34 | -0.1219 | 0.55001
|  | 24:00 | 28.3411 | -0.15302 | 0.55
|  | 24:00 | 28.3422 | -0.18289 | 0.55
|  |  | 28.3522 | 0
|  |  | 28.6756 | 0
|  |  | 28.6856 | -1
|  |  | 29.9256 | -1

## Standby Energy Loss
Standby Energy Loss Rate and self-discharge Rate test performed once a year
BESS duration (h) | 10
RTE assumed (AC-AC) | 0.8
Extra duration for taper during charge | 1
10h duration, 0.1 MW
| Estimated duration (h) |  | Time (h) | Fraction of rated power | SOC
1) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS | 1 | Assume BESS is at max SOC before this test | 0 | 0 | 1
2) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0.33333 |  | 0.01 | -1 | 1
3) Discharge at rated power to lower SOC limit as dictated by BMS (which may be > 0% SOC) | 10 |  | 1 | -1 | 1
4) Rest for 20 min (if duration is 10 hours), 10 min if duration is 24 hours | 0.33333 |  | 1.01 | 0
5) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS | 13.5 |  | 1.3333 | 0
6) Rest BESS for3 days | 72 |  | 1.3433 | 1 | 1
7) Discharge at rated power to lower SOC limit as dictated by BMS (which may be > 0% SOC) | 10 |  | 11.3333 | 1 | 0
8) Rest for 20 min | 0.33333 |  | 11.3433 | 0 | 0
9) Charge the BESS to max SOC as dictated by BMS (which may be < 100% SOC) using recommended charge power, x% of rated power, allowing power to taper as dictated by BMS | 13.5 |  | 11.6667 | 0 | 0
|  |  | 11.6767 | -1 | 0
Total duration for test (h) | 121 |  | 25.1667 | -1 | 1
Total duration for test (d) | 5.0417 |  | 25.1767 | 0 | 1
|  |  | 97.1767 | 0 | 1
|  |  | 97.1867 | 1 | 1
|  |  | 107.1867 | 1 | 0
|  |  | 107.1967 | 0 | 0
|  |  | 107.53 | 0 | 0
|  |  | 107.54 | -1 | 0
|  |  | 121.04 | -1 | 1