## Metadata (System Properties)
Metadata | Unit | Value | Description
General System Specifications
Rated power | kVA
Rated energy | kWh |  | Provide power at which Rated Energy is measured.
Min operating temperature | C
Max operating temperature | C
Preferred operating temperature window (lower to upper bound) | C
Max SOC (operating limit) | percent
Min SOC (operating limit) | percent
Metadata | Unit | Value | Description
Power Conversation System (PCS) Specifications
Power conversion system rated power | kVA |  | For each PCS
AC/DC bidirectional inverter rated power | kVA |  | For each inverter
AC/DC bidirectional inverter rated voltage (in/out) | V |  | For each inverter
AC/DC bidirectional inverter rated current | A |  | For each inverter
DC/DC bidirectional converter rated power | kW |  | For each converter
DC/DC bidirectional converter rated voltage | V |  | For each converter
DC/DC bidirectional converter rated current | A |  | For each converter
# of DC/DC converters | -- |  | For each PCS
# of AC/DC inverter | -- |  | For each PCS
Rack Specifications
Total # (y) modules in series in rack with xPyS configuration | --
Total # (x) modules in parallel in rack with xPyS configuration | --
# racks in series in container | --
# racks in parallel in container | --
External dimensions (l x w x h) | m
Module Specifications
Total # (y) cells in series in module with xPyS configuration | --
Total # (x) cells in parallel in module with xPyS configuration | --
External dimensions (l x w x h) | mm
Applied pressure | psi |  | If applicable
Metadata | Unit | Value | Description
Cell Specifications
Cathode chemistry
Anode chemistry
Electrolyte chemistry |  |  | optional
Nominal capacity | Ah
Nominal voltage | V
Cell external packaging dimensions (l x w x h) | mm
Weight | g
Max charge current | A
Standard charge current | A
Max discharge current | A
Standard discharge current | A
Operational voltage limits (lower to upper bound) | V
Allowed temperature window during charge (lower to upper bound) | C
Allowed temperature window during discharge (lower to upper bound) | C
Specific energy | Wh/kg
Energy density | Wh/L
Electrode stack - length | mm
Electrode stack - width | mm
Electrode stack - thickness | mm
Thermal Management System
Method of thermal management | -- |  | e.g., liquid cooling, overhead fans, etc.
Heat convection rate | W/m2-K
Component Manufacturers + Product IDs
Cell | Name/ID
Module | Name/ID
Rack | Name/ID
Battery management system | Name/ID
Thermal management system | Name/ID
Power conversion system or inverter | Name/ID
Transformer | Name/ID
HVAC | Name/ID
Container | Name/ID
Contactors | Name/ID
Cabling | Name/ID

## Streaming Data
Data Point | Units | Sample Rate Minimum (sample/s) | Values | Notes
System Level
Time |  | 1 | value | ISO 8601 format
Power at Point of Connection with Grid | kW | 1 | value | see meter layout diagram
Reactive Power at Point of Connection with Grid | kVAR | 1 | value | see meter layout diagram
Power Factor at Point of Connection with Grid |  | 1 | value | see meter layout diagram
AC RMS Voltage (A/B/C) | VRMS | 1 | value | distinct output for A/B/C
AC RMS Current (A/B/C) | IRMS | 1 | value | distinct output for A/B/C
Power at Transformer | kW | 1 | value | see meter layout diagram
Reactive Power at Transformer | kVAR | 1 | value | see meter layout diagram
Power Factor at Transformer |  | 1 | value | see meter layout diagram
AC RMS Voltage (A/B/C) at Transformer | VRMS | 1 | value | distinct output for A/B/C
AC RMS Current (A/B/C) at Transformer | IRMS | 1 | value | distinct output for A/B/C
Power Requested (command) | kW | 1 | value | At what meter does BESS attempt to provide the requested power
Reactive Power Requested (command) | kVAR | 1 | value
SOC |  | 1 | value | 0.01% precision
SOH |  | 1 per day | value | 1% precision
Temperature of Air Inside Container | C | 1 per min | value | report output for each sensor in container; 0.1C precision
Humidity Inside Container | % | 1 per min | value | report output for each sensor in container
Total AC Discharge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation? If at meter, get at each meter.
Total AC Charge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation? If at meter, get at each meter.
Contactor Status | Binary | 1 | 1 = closed, 0 = open | For every contactor
Breaker Status | Binary | 1 | 1 = closed, 0 = open | For every breaker
Data Point | Units | Sample Rate Minimum (sample/s) | Values | Notes
Power Conversion System
Power at PCS | kW | 1 | value | see meter layout diagram
Reactive Power at PCS | kVAR | 1 | value | see meter layout diagram
Power Factor at PCS |  | 1 | value | see meter layout diagram
AC RMS Voltage (A/B/C) at PCS | VRMS | 1 | value | distinct output for A/B/C
AC RMS Current (A/B/C) at PCS | IRMS | 1 | value | distinct output for A/B/C
System Frequency | Hz | 1 | value
THD | dBm | 1 | value | Usually measured at converter level
Contactor Status | Binary | 1 | 1 = closed, 0 = open | For every contactor
Breaker Status | Binary | 1 | 1 = closed, 0 = open | For every breaker
Total DC Discharge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation?
Total DC Charge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation?
DC Power | kW | 1 | value | For each PCS
DC Voltage | V | 1 | value | For each PCS
DC Current | I | 1 | value | For each PCS
Temperature | C | 1 | value | For each PCS; 0.1C precision
String Level (Connected Racks), if part of architecture
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | A | 1 | value
SOC |  | 1 |  | if available at this level, 0.01% precision
Rack Level (if part of architecture)
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | A | 1 | value
Temperature | C | 1 | value | 0.1C precision
SOC |  | 1 | value | 0.01% precision
SOH |  | 1 per day | value | 1% precision
Data Point | Units | Sample Rate Minimum (sample/s) | Values | Notes
Module Level (if part of architecture)
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | A | 1 | value
Temperature | C | 1 | value | 0.1C precision
SOC |  | 1 | value | 0.01% precision
SOH |  | 1 per day | value | 1% precision
Cell Level
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | A | 1 | value
Temperature | C | 1 | value
SOC |  | 1 | value | 1% precision
Auxiliary Systems
Auxiliary System Power | kW | 1 | value | For every auxiliary meter
Auxiliary System Reactive Power | kVAR | 1 | value | For every auxiliary meter
HVAC/Thermal Control Power | kW | 1 | value
External Conditions
Outside Temperature | C | 1 per min | value | 0.1C precision
Outside Dew Point Or Humidity % | C | 1 per min | value
Precipitation | mm | 1 per min | value
Solar Irradiance | W/m2 | 1 per min | value
Battery Management System
Balancing | binary | 1 | 1 = on; 0 = off | At all hierarchies

## O&M Written Log
| Event Information |  |  | Component Information |  | Event Description |  | Resolution
Event # | Planned vs Unplanned | % System Rated Power Unavailable | Event Category (see options) | Component (see options) | Additional Component Details? (e.g., associated streaming label in system diagram) | Event Start Time (ISO 8601 format) | Short Event Description | Root Cause | Solution | Event Resolution Time (ISO 8601 format) | Event Duration (x days, y hours, z minutes) | Related to Previous Event # | Enter outage duration if less than event duration | Additional Details (provide version ID# if standard firmware update)
1 | Unplanned |  | Hardware | Battery | Container 2, Rack 12 | 2020-02-02 |  |  |  | 2020-03-13 11:01 | 40 days, 11 hours, 1 minutes | none | 3 days
2 | Unplanned |  | Firmware / Software | Database issue |  | 2020-07-17 | Database software crash | firmware issue / update firmware with vendors help. |  | 2020-07-20 00:01 | 3 days, 0 hours, 1 minutes | 1
3 | Planned |  | Firmware / Software | Update | [9 empty] | BMS upgraded to Version 11.2
4 | Planned |  | Hardware | Battery |  |  | Replace bad module

## O&M Event Category Options
Event Category Options: Hardware, Firmware/Software, Network, External
Hardware | Notes
Battery | Catch all for the part of the system that is storing the electrical energy in another form
Inverter | Bi or mono-directional AC-DC converter
Converter | Bi or mono-directional DC-DC converter
Thermal management | Anything related to HVAC
Electrical conductor | Only conductors used for moving energy in/out of storage system (excludes comms or auxiliary conductors)
Energy management system | High level system controller typically used to orchestrate the operation of many storage devices and inverters
Transformer | Generic transformer. Details about the transformer can be provided in the blue table
Meter | Any device in the system that is measuring and externally reporting data
Battery management system | Controller that manages the operation of a single battery / storage system
Data acquisition (DAQ) | A device which collects and communicates data from many different metering devices, but does not necessarily measure data directly
Database | A repository for historical system data
Network equipment
Uninterruptible power supply
Fire detection or suppression systems
Firmware/Software | Notes
Update
Error | Bug in firmware requiring update
Database issue
Network | Notes
Data transfer error
Device failure
Internet service provider error
Local area network error
VPN error
Firewall error
Physical disconnection
Cloud service outages
External | Notes
Loss of grid power
Loss of auxiliary power
Weather/natural causes | Earthquake, thunderstorm, pandemic, rodents, corrosion, erosion
Operator error
External tampering | Vandalism
Site access issues