## Instructions
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5
Latest Template Revision: | 2017-07-06
Tab Name: | Instructions
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Reference Test Procedure
10 CFR 431.96 (which references AHRI 310/380 - 2004, Standard for Packaged Terminal Air-Conditioners and Heat Pumps)
AHRI 310/380 - 2004, Standard for Packaged Terminal Air-Conditioners and Heat Pumps
Table of Contents
Tab | Contents
Instructions | Instructions and summary of template contents
General Info & Test Results | Lab information, product information and test results
Setup & Instrumentation | Instrumentation requirements and space for sensor placement descriptions
Photos | Product and sensor placement photos
Photo Adding | Space to input photos into the workbook (for Excel 2003 users only)
General Test Comments | Comments, clarifications, and documentation of discrepancies or other anomalies
Settings | Unit control settings
A16-Recorded Data | Recorded data on test conditions from ASHRAE 16
A16-Capacity Calculations | Measurement inputs and calculations for ASHRAE 16 capacity test
A58-Recorded Data | Recorded data on test conditions from ASHRAE 58 (for PTHPs)
Report Sign-Off Block | Report review history
Drop-Downs | Used for drop-down lists; summary of drop-down options
Version Control | Report template revision history
LEGEND
Tabs | Tabs with input cells
Cells | Input cell
Auto-populated cell
Provided data
NOT USED
Instructions for Completing this Template
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THIS TAB:
Step 1 | General Info & Test Results
Step 2 | Setup & Instrumentation
Step 3 | Photos
Step 3a | Photo Adding, if applicable (for Excel 2003 users only)
Step 4 | General Test Comments
Step 5 | Settings
Step 6 | A16-Recorded Data
Step 7 | A16-Capacity Calculation
Step 8 (For PTHPs) | A58-Recorded Data
Step 9 | Report Sign-off Block

## General Info & Test Results
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 | Back to Instructions tab
Latest Template Revision: | 2017-07-06
Tab Name: | General Info & Test Results
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
Lab Information |  | Figures of Merit for Tested Unit
Lab Name: |  | Variable | Measurement | Units
Lab Location: |  | Cooling Capacity |  | Btu/hr
|  | Electrical Power Input (Cooling) |  | Watts
Test Information |  | Calculated EER |  | -
Date Test Started: | [MM/DD/YYYY] | Heating Capacity |  | Btu/hr
Date Test Finished: | [MM/DD/YYYY] | Electrical Power Input (Heating) |  | Watts
Date of Last Calibration for Partition Wall: | [MM/DD/YYYY] | Calculated COP |  | -
Was the test performed according to DOE Test Procedure, including relevant section of AHRI 310/380 - 2004, ASHRAE 16-1999, ASHRAE 37-1988, ASHRAE 58-1999?
ASHRAE 58-1999 Heating Test Performed?
NOTE: Copy only; sign off is done in the Report Sign-Off Block tab
Product Information |  | Test Report Sign-Off Block
Manufacturer: (if applicable) |  | We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Brand: (if applicable)
Manufacturer Model Number:
Serial Number: |  | Role |  | Date | Entity
Date Manufactured: | [MM/YYYY] | Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Date Product Received: | [MM/DD/YYYY] | Template Population |  | [MM/DD/YYYY] | [Test Lab Name]
Condition as Received: |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
|  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Product Characteristics
Product Description:
PTAC or PTHP?
Refrigerant Used (eg. R-22, R-410A)?
Rated Performance
Nameplate Cooling Capacity (Btu/hr):
Nameplate Heating Capacity (Btu/hr):
Nameplate EER:
Nameplate COP:
Nameplate Input Voltage(s):

## Setup & Instrumentation
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 |  | Back to Instructions tab
Latest Template Revision: | 2017-07-06
Tab Name: | Setup & Instrumentation
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
Set-Up (This table should include instrumentation, sensors, and all equipment used during testing)
Instrument Type | Brand | Model # | Sensor Location | Accuracy | Date of Last Calibration | Deadline for Next Calibration
1. Sensor Placement
Describe placement of sensors used to measure ambient temperature:
If additional sensors were used, describe placement:
2. Installation Instructions
Please quote the relevant manufacturer instructions for installing this unit, as it pertains to this test. (May use a focused picture with instructions)
- Include instructions on the use of the installation kit and selection and use of the wall sleeve and grille
- Please include references, including page numbers.
Describe the TTW sleeve that was selected for this test, including manufacturer, model number, and dimensions. Please note if this sleeve was listed in the manufacturer's instructions.
- Also include information on the metal grille, and whether it was included with the cabinet or the unit.

## Photos
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 | Back to Instructions tab
Latest Template Revision: | 2017-07-06
Tab Name: | Photos
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
1. Picture of the nameplate showing model number and a picture showing serial number (may require 2 separate photos)
2. FTC EnergyGuide label (if present).
3. Picture of both inside and outside portions of test unit , once it is out of the package (include as many pictures as neccesary)
4. Exact placement of all sensors on, in, or around the device (please label where unclear, take multiple pictures if neccesary)
5. Picture of room air conditioner as installed in final set-up (evaporator side)
6. Picture of room air conditioner as installed in final set-up (condenser side)
7. Picture showing the space around the room air conditioner on the indoor room side, to show clearance limits
8. Room air conditioner control panel or controls as set during test
9. [IF NEEDED] Picture of the sleeve and grille used to test unit, separate from test set-up
10. [IF NEEDED] Picture of test kit components (such as foam insulation) used with test set-up
11. [IF NEEDED] Picture showing how test kit components were applied in test set-up (take multiple if needed, for example: front and back)
12. Photos of test unit from all sides
13. Additional Photos (if necessary)

## Photo Adding
Title Block |  | This tab is for users of Excel 2003 only so that they may be able to easily upload photos to this template. | Back to Instructions tab
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 | Instructions: Input the required test photos on this tab first, then transfer to the "Photos" tab
Latest Template Revision: | 2017-07-06
Tab Name: | Photo Adding | Note
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx | • Any photos uploaded to this tab MUST be transferred over to the "Photos" tab.
Test Completion Date: | [MM/DD/YYYY] | • DOE will not consider any photos that remain on this tab in its evaluation of the test report template.

## General Test Comments
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump | Back to Instructions tab
Version Number: | v1.5
Latest Template Revision: | 2017-07-06
Tab Name: | General Test Comments
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
1. Overall Test Comments
Please describe any unusual events or issues that occurred during this test:
Please note whether this test was run more than once, and why:
2. Test Unit Discrepancies
Please note any features about the test unit that required special modification of the test set-up:
3. Additional Comments
Please provide any further comments about this test that should be noted:
If any pictures would help describe and enhance these comments, please include them in the 'Photos' Tab under Additional Photos.

## Settings
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 |  | Back to Instructions tab
Latest Template Revision: | 2017-07-06
Tab Name: | Settings
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
PTAC/PTHP Settings - Controls
Please include a description of how the settings were entered, specific to this particular test unit:
Electromechanical or Electronic Controls?
| Cooling Mode | Heating Mode
Cooling Setting?
Fan Setting?
Temperature Setting?
Other settings (if neccesary) | Extra Setting #1 |  | Extra Setting #2 | Extra Setting #3
--- Description
--- Setting
Additional Description
Describe settings used on the PTAC/PTHP for test, or reference picture of controls in 'Photos' Tab

## A16-Recorded Data
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 |  | Back to Instructions tab
Latest Template Revision: | 2017-07-06
Tab Name: | A16-Recorded Data
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Data Inputs
Product Information (if applicable)
Test Number
| Date | [MM/DD/YYYY]
Report Number
Unit Model Number
Unit Serial Number
Rated Cooling Capacity [Btu/hr]
| Date of Run-In | [MM/DD/YYYY]
Length of Run-In Time (hr)
Test Conditions Summary - Test Chamber Devices
In Accordance with Section 6.1.5 of ANSI/ASHRAE Standard 16-1999
Compliance with Equilibrium Requirements
Has chamber been at equilibrium for the minimum 1 hour?
Recorded Data
From ANSI/ASHRAE Standard 16-1999, Table 2
| Electrical Inputs | Measurement | Unit
| Applied Voltage to Test Unit |  | V
| Frequency |  | Hz
| Line Current |  | A
| Power Input |  | W
| Power Factor |  | %
| Fan speed |  | rpm
| Pressure Measurements | Measurement | Unit
| Barometric Pressure |  | in. Hg
| Water Measurements | Measurement | Unit
| Water quantity evaporated in humidifier |  | lb/h
| Temperature of humidifier water entering room-side compartment or in humidifier tank |  | °F
| Cooling water flow rate through outdoor-side compartment, reconditioning coil |  | lb/h
| Temperature of cooling water entering outdoor-side compartment, reconditioning coil |  | °F
| Temperature of cooling water leaving outdoor-side compartment, reconditioning coil |  | °F
| Temperature of condensed water leaving outdoor-side compartment |  | °F
| Airflow Measurements | Measurement | Unit
| Volume of airflow through measuring nozzle of separating partition flowmeter, including direction, in or out of room |  | cfm
| Static air pressure difference across separating partition of calorimeter compartments |  | in. H2O
| Air Temperatures | Measurement | Unit
| Wet-bulb temperature of air leaving room side of air conditioner |  | °F
| Dry-bulb temperature of air surrounding inner compartments of balanced ambient calorimeter |  | °F
| Wet-bulb temperature of air surrounding inner compartments of balanced ambient calorimeter |  | °F
Test Conditions (from raw data)
| Measurement | Min | Max | Average | Absolute Variation |  | Unit
[5 empty] | Average Variation | Range Variation
| Room Air Dry Bulb |  |  |  | 0 | 0 | °F
| Room Air Wet Bulb |  |  |  | 0 | 0 | °F
| Outside Air Dry Bulb |  |  |  | 0 | 0 | °F
| Outside Air Wet Bulb |  |  |  | 0 | 0 | °F
| Voltage |  |  |  | 0 | 0 | V
Not Compliant with Standard
Compliant with Standard
Notes/Comments: (Please clarify any pertinent details, unusual events, etc.)

## A16-Capacity Calculation
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 |  | Back to Instructions tab
Latest Template Revision: | 2017-07-06
Tab Name: | A16-Capacity Calculation
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Data Inputs
Capacity Calculation
| In Accordance with Section 6.2 of ANSI/ASHRAE Standard 16-1999 |  | Measurement | Unit
|  | Barometric Pressure |  | in. Hg
Capacity Calculation - Room Side
From ANSI/ASHRAE Standard 16-1999, Section 6.2.1
|  |  | Measurement | Unit
| ∑Er | Sum of all power input to room-side compartment [W] |  | Watts
| hw1 (@XX ⁰F) | Enthalpy of water or steam supplied to maintain humidity [Btu/lb]. If no water is introduced during the test, hw1 is taken at the temperature of the water in the humidifier tank of the reconditioning equipment. |  | Btu/lbs.
| hw2 (@XX ⁰F) | Enthalpy of condensed moisture leaving the roomside compartment [Btu/lb]. Since transfer of condensed moisture from room-side to outdoor-side compartment usually takes place within the air conditioner, with consequent difficulty in measuring its temperature, the temperature of the condensate may be assumed to be at the measured wet-bulb temperature of the air leaving the air conditioner. |  | Btu/lbs.
| wr | Water vapor condensed by air conditioner. This is measured by reconditioning equipment as the amount of water evaporated into room-side compartment to maintain required humidity [lb/h] |  | lb/h
| qlp | Heat leakage into room-side compartment through separating partition between room-side and outdoorside compartments, as determined from calibrating test [Btu/hr] |  | Btu/hr
| qlr | Heat leakage into room-side compartment through walls, floor, and ceiling (but not including the separating partition) as determined from calibrating test [Btu/hr] |  | Btu/hr
| qtr | Net total cooling effect as determined on room-side compartment [Btu/hr] |  | Btu/hr
| qd | Net latent cooling effect [Btu/hr] |  | Btu/hr
| qs | Net sensible cooling effect [Btu/hr] |  | Btu/hr
Notable temperatures, as noted in ANSI/ASHRAE Standard 16-1999
Was water introduced during the test to maintain humidity?
|  | IF NO: What was the temperature of the water in the humidifer tank? |  | °F
Was the temperature of the condensate assumed to be at the measured wet-bulb temperature of the air leaving the air conditioner?
|  | IF YES: What was this temperature? |  | °F
Capacity Calculation - Outdoor Side
From ANSI/ASHRAE Standard 16-1999, Section 6.2.2
|  |  | Measurement | Unit
| qc | Heat removed by cooling coil in outdoor-side compartment [Btu/hr] |  | Btu/hr
| ∑Eo | Sum of all power input to any equipment, such as reheaters, circulating fans, etc., in outdoor-side compartment [W] |  | Watts
| E | Total power input to air conditioner [W] |  | Watts
| hw2 (@XX ⁰F) | Enthalpy of condensed moisture leaving the roomside compartment, as defined in 6.2.1 [Btu/lb] |  | Btu/lbs.
| hw2 (@XX ⁰F) | Enthalpy of condensate removed by air-treating coil in outdoor-side compartment reconditioning equipment, taken at the temperature at which the condensate leaves the compartment [Btu/lb] |  | Btu/lbs.
| wr | Water vapor condensed by air conditioner, as defined in 6.2.1 [lb/h] |  | lb/h
| qlp | Heat leakage out of outdoor-side compartment through separating partition between room-side and outdoor-side compartments, as determined from calibrating test - [Btu/hr] (this quantity will be numerically equal to qlp used in Equation 1 if and only if the area of separating partition exposed to the outdoor side is equal to the area exposed to the roomside compartment) |  | Btu/hr
| q1o | Heat leakage out of outdoor side (but not including the separating partition), as determined from calibrating test [Btu/hr] |  | Btu/hr
| qlo | Net total cooling effect as determined on outdoor-side [Btu/hr] |  | Btu/hr
|  | Adjusted net total cooling effect as determined on outdoor-side [Btu/hr] |  | Btu/hr
| Notable temperatures, as noted in ANSI/ASHRAE Standard 16-1999 |  | Measurement
|  | What is the temperature at which the condensate leaves the compartment? |  | °F
EER Calculation (Automatically Calculated)
In Accordance with ANSI/ASHRAE Standard 16-1983 (RA09)
Capacity Agreement Calculation - Room Side
|  |  | Measurement | Calculated Result (rounded per significant figures conventions and instrumentation resolution) | Units
|  | Net total cooling effect as determined on room-side compartment [Btu/hr] |  |  | Btu/hr
|  | Net total cooling effect as determined on outdoor-side [Btu/hr] |  |  | Btu/hr
|  | Agreement Check: Does the room-side and outdoor-side capacity agree to within 4%? |  |  | -
|  | Difference between room-side and outdoor-side capacities (%) |  |  | %
|  | Electrical Power Input [W] |  |  | W
|  | Non-Adjusted EER |  |  | (Btu/hr)/W
Barometric Pressure Adjustment
|  |  | Measurement | Calculated Result (rounded per significant figures conventions and instrumentation resolution) | Units
|  | Measured Barometric Pressure |  |  | in. Hg
|  | Measured Deviation from Standard Pressure |  |  | in. Hg
|  | Upward adjustment of capacity measurements |  |  | %
|  | Adjusted net total cooling effect as determined on room-side compartment [Btu/hr] |  |  | Btu/hr
|  | Energy Efficiency Ratio (EER) |  |  | (Btu/hr)/W

## A58-Recorded Data
Title Block |  |  | Back to Instructions tab
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5
Latest Template Revision: | 2017-07-06
Tab Name: | A58-Recorded Data
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
'A Test' Data to be recorded
Product Information (if applicable)
Test Number
| Date | [MM/DD/YYYY]
Report Number
Unit Model Number
Unit Serial Number
Rated Heating Capacity
| Date of Run-In | [MM/DD/YYYY]
Length of Run-In Time (hr)
Heating Test Conditions Summary - Test Chamber Devices
Compliance with Equilibrium Requirements
Did the defrost controls become operative during testing?
Has chamber been at equilibrium for the minimum 60 minutes?
Electrical Input
Measurement
|  | Avg | Min | Max
Applied Voltage to Unit [V]
Frequency [Hz]
Line Current [A]
Total System Power [W]
Pressure Measurements
Measurement
Barometric Pressure [in. Hg]
Static Discharge Pressure [in. H₂O]
Airflow Measurements
Measurement
Indoor Unit Airflow [cfm]
Indoor Unit Standard Airflow [scfm]
Indoor Fan Speed [rpm]
Volume and direction (in or out of room) of airflow through pressure equalizing device [cfm]
Static air pressure difference between rooms [in. H20]
Air Temperatures
Measurement
|  | Avg | Min | Max
Indoor air entering dry bulb temperature [°F]
Indoor air entering wet bulb temperature [°F]
Indoor air leaving dry bulb temperature [°F]
Indoor air leaving wet bulb temperature [°F]
Indoor air nozzle dry bulb temperature [°F]
Outdoor air entering dry bulb temperature [°F]
Outdoor air entering wet bulb temperature [°F]
Heating Capacity Calculations
Measurement
Was moisture deliberately added to the indoor airstream?
Qm - Indoor Airflow Rate [cfm]
ta2 - temperature of air leaving indoor side [°F]
ta1 - temperature of air entering indoor side [°F]
ha2 - enthalpy of air leaving indoor side [Btu/lb]
ha1 - enthalpy of air entering indoor side [Btu/lb]
vn' - specific volume of air [ft^3/lb]
W - specific humidity of air
Cp' - specific heat capacity of air
q1 - heat loss through measuring apparatus [Btu/hr]
Total Heating Capacity [Btu/hr]
COP Calculations
|  | Measurement |  |  | Calculated Result (rounded per significant figures conventions and instrumentation resolution)
Total Heating Capacity [Btu/hr]
System Total Power Draw [W]
COP

## Report Sign-Off Block
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5 |  | Back to Instructions tab
Latest Template Revision: | 2017-07-06
Tab Name: | Report Sign-Off Block
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Template Population |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]

## Drop-Downs
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump |  | Back to Instructions tab
Version Number: | v1.5
Latest Template Revision: | 2017-07-06
Tab Name: | Drop-Downs
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
Yes_no | PTAC_PTHP | Electronic
Electronic
Yes | PTAC | Electromechanical
No | PTHP
ANSI/ASHRAE Standard 16-1999 - Table 1
Reading | Variation of Arithmetric Average from Rating Conditions | Maximum Variation of individual 10 min. readings from rating conditions | Unit
Dry-Bulb Temperature | 0.5 | 1 | °F
Wet-Bulb Temperature | 0.3 | 0.6 | °F
Voltage | 1% | 2% | V
Cooling Capacity Measurements Standard Test Conditions
Reading | Value | Unit
Room Air Dry Bulb (deg F) | 80 | °F
Room Air Wet Bulb (deg F) | 67 | °F
Outside Air Dry Bulb (deg F) | 95 | °F
Outside Air Wet Bulb (deg F) | 75 | °F
Unit Voltage at 60 Hz (V) | 115 | V
Nameplate voltages, from Table 1 of ANSI/AHRI Standard 110-2012, referenced by ANSI/AHRI/CSA Standard 310/380-2004 section 4.2.2
Voltage Class | Nameplate Voltage Marking | Unit
Low Voltage | 115 | V
| 208 | V
| 230 | V
| 265 | V
| 460 | V
| 575 | V

## Version Control
Title Block
Test Report Template Name: | Packaged Terminal Air Conditioner and Heat Pump
Version Number: | v1.5
Latest Template Revision: | 2017-07-06
Tab Name: | Version Control
File Name: | Packaged Terminal Air Conditioner - v1.5.xlsx
Test Completion Date: | [MM/DD/YYYY]
Revisions List
Version | Date
v1.0_draft 2 | 2013-08-05
v1.0_draft 3 | 2013-11-07
v1.0_draft 4 | 2013-11-13
v1.0_draft 5 | 2013-12-11
v1.1_draft1 | 2014-02-20
v1.2 | 2015-06-22
v1.3 | 2015-08-10
v1.4 | 2015-08-21
v1.5 | 2017-07-06