## BuildingSummary
Building Summary Full Service Restaurant new construction
|  | Value | Data Source
Program
| Building Name | Full Service Restaurant
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Service
Form |  |  | Time Saver Standards; Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991 for all Form parameters
| Total Floor Area (m2) | 511.15
| Building Shape | Rectangle
| Aspect Ratio | 1
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.28
| East | 0.224
| North | 0
| West | 0.224
| Total | 0.182
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 2 zones plus attic
| Floor to Ceiling Height (m) | 3.048
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 275.72
| Net Dimensions - Total Area (m2) | 225.54
| Wall to Skin Ratio | 0.326
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 569.52
| Net Dimensions - Total Area (m2) | 569.52
| Roof to Skin Ratio | 0.674
| Window Dimensions (m2) |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991
| South | 19.3
| East | 15.44
| North | 0
| West | 15.44
| Total Area (m2) | 50.18
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab-on-grade
| Dimensions - Total Area (m2) | 511.15
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 68.93
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.55 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 1377.36

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Dining | Yes | 1 | 371.75 | 1133.39 | 3.0488 | 169.1902 | 47.17 | 1.3935 | 266.7653 | 22.6042 | 60.2778 |  |  | 10 |  | 2667.6532 |  | 0.51945
Kitchen | Yes | 1 | 139.41 | 425.02 | 3.0487 | 106.5301 | 0 | 18.5806 | 7.503 | 12.9167 | 376.7365 | 1198.345 | 503.4582 | 8 |  | 60.0238 | 1887.788 | 0.62979
Attic | No | 1 | 511.15 | 856.26 | 1.6752 | 0 | 0 | [10 empty] | 1
Total Conditioned Zones |  |  | 511.16 | 1558.41 |  | 275.7203 | 47.17 |  | 274.2683
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Building Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 21.72 | 253.9818 | 59.0764 | 267.6909 |  | 114.1855 | 13.8582 | 305.8982 | 13.9891 | 24.5709 | 344.1964 | 74.7018 | 74.6182 | 9.6255 | 8.8145 | 0.33091
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall | Steel frame wall
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value attic floor (m2·K / W) | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 6.5229 | 6.5229 | 6.5229 | 6.5229
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_COOLC DXCOIL | 74.0884 | 74.702 | 74.3682 | 73.5956 | 59.0133 | 72.4578 | 53.9183 | 72.2505 | 67.4798 | 57.0875 | 71.5232 | 66.4685 | 71.4646 | 54.6166 | 68.7668 | 44.2716
| PSZ-AC_2:2_COOLC DXCOIL | 19.0869 | 19.0818 | 18.8162 | 19.6625 | 17.1776 | 19.0223 | 9.5005 | 18.3905 | 16.3237 | 12.0004 | 18.1464 | 14.8844 | 17.6743 | 13.1734 | 11.1489 | 9.586
Heating (kW)
| PSZ-AC_1:1_HEATC | 110.6493 | 144.3383 | 122.4017 | 153.8625 | 108.0201 | 129.8418 | 121.5692 | 169.5206 | 141.4995 | 143.2111 | 196.3816 | 165.4385 | 211.7691 | 195.955 | 214.1865 | 262.6721
| PSZ-AC_2:2_HEATC | 29.7582 | 39.2745 | 32.6745 | 43.6562 | 27.8538 | 35.7087 | 25.5438 | 45.4533 | 43.5398 | 34.509 | 52.3943 | 50.6039 | 55.1497 | 56.1901 | 53.4171 | 56.8758
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.3 | 3.3
| PSZ-AC_2:2_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
Heating Efficiency (%)
| PSZ-AC_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_1:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| DINING EXHAUST FAN | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83
| KITCHEN EXHAUST FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| PSZ-AC_1:1_FAN | 2.98 | 3.01 | 2.99 | 2.96 | 2.69 | 2.92 | 2.78 | 2.91 | 3.26 | 2.73 | 2.88 | 3.19 | 2.88 | 3.03 | 2.77 | 2.67
| PSZ-AC_2:2_FAN | 0.77 | 0.77 | 0.76 | 0.79 | 0.69 | 0.77 | 0.57 | 0.74 | 0.89 | 0.65 | 0.73 | 0.87 | 0.71 | 0.8 | 0.67 | 0.58
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.076926 | 0.10668 | 0.095687 | 0.10387 | 0.1238 | 0.094057 | 0.14458 | 0.066345 | 0.037525 | 0.072253 | 0.052271 | 0.037541 | 0.051987 | 0.068189 | 0.050793 | 0.087397
| Total Cost ($/m2) | 57.68 | 74.88 | 67.84 | 67.05 | 74.13 | 63.53 | 84.15 | 41.66 | 23.67 | 42.2 | 31.99 | 23.06 | 31.61 | 40.82 | 29.74 | 50.33
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011468 | 0.0081861 | 0.0085715 | 0.01059 | 0.008418 | 0.0081051 | 0.0084323 | 0.0099821 | 0.0071459 | 0.0083176 | 0.0087421 | 0.0071351 | 0.0079327 | 0.0085764 | 0.0079269 | 0.0041722
| Total Cost ($/m2) | 21.93 | 19.17 | 18.9 | 29.18 | 18.83 | 19.83 | 23.28 | 33.58 | 20.91 | 27.68 | 33.73 | 24.04 | 34.48 | 34.19 | 39.22 | 27.25
Total Utility Costs
| Cost Intensity ($/m2) | 79.61 | 94.06 | 86.75 | 96.23 | 92.96 | 83.36 | 107.44 | 75.25 | 44.57 | 69.89 | 65.72 | 47.1 | 66.08 | 75.01 | 68.97 | 77.57
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 83427.7778 | 59480.5556 | 63355.5556 | 31441.6667 | 10477.7778 | 47263.8889 | 2811.1111 | 23858.3333 | 21263.8889 | 3950 | 16330.5556 | 13936.1111 | 14488.8889 | 8166.6667 | 4705.5556 | 1733.3333
| Interior Lighting | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222
| Exterior Lighting | 18516.6667 | 18483.3333 | 18480.5556 | 18511.1111 | 18508.3333 | 18488.8889 | 18469.4444 | 18488.8889 | 18483.3333 | 18458.3333 | 18461.1111 | 18466.6667 | 18477.7778 | 18455.5556 | 18450 | 18338.8889
| Interior Equipment | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 30211.1111 | 30405.5556 | 30211.1111 | 30244.4444 | 27325 | 29663.8889 | 27091.6667 | 29386.1111 | 33452.7778 | 27300 | 29072.2222 | 32705.5556 | 29002.7778 | 30819.4444 | 27811.1111 | 26275
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 18819.4444 | 18127.7778 | 18063.8889 | 17438.8889 | 17480.5556 | 17561.1111 | 16850 | 16966.6667 | 16911.1111 | 16552.7778 | 16663.8889 | 16575 | 16516.6667 | 16263.8889 | 16055.5556 | 15691.6667
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 383277.7778 | 358797.2222 | 362411.1111 | 329936.1111 | 306088.8889 | 345280.5556 | 297522.2222 | 321002.7778 | 322411.1111 | 298558.3333 | 312827.7778 | 313980.5556 | 310786.1111 | 306005.5556 | 299322.2222 | 294338.8889
Gas (MJ)
| Heating | 13960 | 202860 | 150700 | 384170 | 124540 | 252320 | 367250 | 671850 | 451970 | 641130 | 903800 | 654850 | 1135110 | 947810 | 1413400 | 2186760
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 162410 | 193490 | 175610 | 223430 | 217620 | 197130 | 243250 | 246970 | 242500 | 259220 | 267630 | 266550 | 285480 | 288730 | 314930 | 350570
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 977280 | 1197260 | 1127230 | 1408520 | 1143080 | 1250380 | 1411420 | 1719740 | 1495400 | 1701270 | 1972350 | 1722320 | 2221510 | 2037460 | 2529250 | 3338250
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2357080 | 2488940 | 2431910 | 2596290 | 2245000 | 2493390 | 2482500 | 2875350 | 2656080 | 2776080 | 3098530 | 2852660 | 3340340 | 3139080 | 3606810 | 4397870
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 587.577 | 418.9181 | 446.2095 | 221.4418 | 73.7944 | 332.8768 | 19.7985 | 168.0329 | 149.7603 | 27.8196 | 115.0152 | 98.1512 | 102.0444 | 57.5174 | 33.141 | 12.2078
| Interior Lighting (elec) | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103
| Exterior Lighting (elec) | 130.4118 | 130.1771 | 130.1575 | 130.3727 | 130.3531 | 130.2162 | 130.0792 | 130.2162 | 130.1771 | 130.001 | 130.0205 | 130.0597 | 130.1379 | 129.9814 | 129.9423 | 129.1597
| Interior Equipment (elec) | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 212.7751 | 214.1446 | 212.7751 | 213.0099 | 192.4484 | 208.9211 | 190.805 | 206.9647 | 235.606 | 192.2723 | 204.754 | 230.3433 | 204.2649 | 217.0596 | 195.8721 | 185.0533
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 132.5443 | 127.6729 | 127.2229 | 122.8211 | 123.1145 | 123.6819 | 118.6736 | 119.4953 | 119.104 | 116.5803 | 117.3628 | 116.7368 | 116.3259 | 114.5456 | 113.0784 | 110.5155
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2699.4033 | 2526.9882 | 2552.4406 | 2323.721 | 2155.7664 | 2431.7911 | 2095.4319 | 2260.8041 | 2270.7229 | 2102.7291 | 2203.228 | 2211.347 | 2188.8487 | 2155.1795 | 2108.1092 | 2073.0118
Gas (MJ/m2)
| Heating (gas) | 27.311 | 396.8698 | 294.8254 | 751.5798 | 243.6467 | 493.632 | 718.4779 | 1314.3891 | 884.2219 | 1254.2893 | 1768.1698 | 1281.1308 | 2220.6984 | 1854.2698 | 2765.1374 | 4278.118
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 317.7345 | 378.5386 | 343.5586 | 437.1124 | 425.7459 | 385.6598 | 475.8877 | 483.1654 | 474.4204 | 507.131 | 523.5841 | 521.4712 | 558.5053 | 564.8635 | 616.1205 | 685.8456
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1911.9241 | 2342.287 | 2205.2822 | 2755.5903 | 2236.2907 | 2446.2095 | 2761.2638 | 3364.4527 | 2925.56 | 3328.3185 | 3858.6521 | 3369.5001 | 4346.1019 | 3986.0315 | 4948.1561 | 6530.8618
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 4611.3274 | 4869.2947 | 4757.7228 | 5079.3114 | 4392.0571 | 4878.0006 | 4856.6957 | 5625.2568 | 5196.2829 | 5431.0476 | 6061.8801 | 5580.8667 | 6534.9506 | 6141.211 | 7056.2653 | 8603.8736
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 62.0291 | 58.092 | 52.9515 | 47.5983 | 54.0462 | 46.2873 | 45.9315 | 46.2883 | 46.8818 | 45.9519 | 46.1331 | 47.0956 | 46.0546 | 46.3433 | 45.8672 | 47.2062
| Feb | 63.262 | 55.2636 | 55.8029 | 48.1215 | 53.7801 | 47.8018 | 47.8775 | 46.193 | 47.9525 | 45.93 | 46.1028 | 46.634 | 46.0216 | 46.4177 | 45.8961 | 45.6219
| Mar | 63.5883 | 59.3205 | 61.8912 | 50.85 | 51.8162 | 51.1254 | 45.9119 | 52.654 | 48.0198 | 45.9311 | 47.092 | 51.2707 | 46.0801 | 47.0429 | 45.8528 | 45.6591
| Apr | 65.4931 | 63.6519 | 64.1817 | 56.0243 | 55.9443 | 62.1809 | 47.7867 | 50.8411 | 55.415 | 45.5035 | 45.5899 | 51.0528 | 49.0923 | 46.0288 | 43.2818 | 45.6015
| May | 68.53 | 70.3351 | 75.3865 | 65.4136 | 52.313 | 68.3746 | 50.0111 | 59.1952 | 60.8589 | 49.1518 | 58.2736 | 57.1852 | 65.4285 | 52.4092 | 49.3091 | 45.2207
| Jun | 71.0159 | 70.6582 | 80.9681 | 66.6313 | 50.7785 | 78.4786 | 51.1439 | 70.4556 | 66.2845 | 52.8243 | 67.7418 | 64.9179 | 67.822 | 62.7727 | 56.7575 | 53.6751
| Jul | 70.4258 | 72.5363 | 78.789 | 72.0131 | 54.2353 | 76.8911 | 57.7795 | 71.5311 | 69.1756 | 55.334 | 69.8764 | 64.8358 | 68.3761 | 63.1649 | 62.1071 | 54.7028
| Aug | 70.5209 | 71.9957 | 79.8582 | 69.3568 | 59.2439 | 75.015 | 54.0416 | 70.7248 | 63.8049 | 54.1195 | 68.4676 | 65.5108 | 67.8112 | 61.6977 | 59.4369 | 51.6931
| Sep | 69.6228 | 70.9145 | 74.7148 | 63.905 | 64.2359 | 71.8419 | 59.4326 | 61.4558 | 59.4806 | 63.538 | 59.9879 | 60.2169 | 55.1647 | 58.1193 | 50.8123 | 45.7728
| Oct | 71.3282 | 67.9341 | 65.5846 | 58.843 | 57.9942 | 63.5296 | 51.847 | 59.0021 | 56.9894 | 50.1614 | 53.7826 | 54.7558 | 52.2778 | 51.1501 | 50.1507 | 45.7338
| Nov | 67.9211 | 64.2594 | 60.0994 | 48.7868 | 53.5233 | 49.0294 | 46.3569 | 52.9285 | 48.2034 | 46.3315 | 53.5744 | 47.5723 | 46.4564 | 46.4194 | 45.9793 | 45.6556
| Dec | 62.8626 | 62.1134 | 51.244 | 47.5563 | 54.7604 | 47.9079 | 45.9504 | 46.2759 | 46.7355 | 45.9356 | 46.1516 | 46.6241 | 46.0527 | 46.3422 | 45.867 | 47.2595
Time of Peak Electrical Demand
| Jan | 06-JAN-12:15 | 03-JAN-12:15 | 28-JAN-18:15 | 23-JAN-18:15 | 26-JAN-12:00 | 18-JAN-16:00 | 15-JAN-17:15 | 09-JAN-07:30 | 25-JAN-17:30 | 14-JAN-07:45 | 18-JAN-07:15 | 27-JAN-17:15 | 16-JAN-07:45 | 10-JAN-07:00 | 16-JAN-07:45 | 01-JAN-11:15
| Feb | 23-FEB-12:15 | 22-FEB-18:15 | 28-FEB-18:30 | 20-FEB-18:30 | 12-FEB-12:00 | 08-FEB-17:15 | 15-FEB-18:15 | 15-FEB-17:45 | 14-FEB-17:45 | 21-FEB-18:15 | 27-FEB-18:45 | 11-FEB-17:30 | 18-FEB-07:15 | 02-FEB-17:30 | 28-FEB-17:00 | 27-FEB-08:15
| Mar | 13-MAR-11:00 | 25-MAR-17:30 | 17-MAR-17:15 | 28-MAR-17:30 | 04-MAR-11:00 | 30-MAR-17:00 | 22-MAR-06:15 | 09-MAR-18:00 | 01-MAR-18:15 | 13-MAR-06:30 | 14-MAR-17:00 | 26-MAR-16:30 | 23-MAR-06:15 | 30-MAR-17:15 | 13-MAR-06:30 | 09-MAR-07:30
| Apr | 04-APR-17:15 | 29-APR-17:15 | 01-APR-17:15 | 14-APR-17:15 | 11-APR-17:15 | 21-APR-17:15 | 29-APR-11:00 | 05-APR-17:15 | 21-APR-17:15 | 29-APR-17:15 | 07-APR-11:00 | 24-APR-11:00 | 16-APR-17:15 | 06-APR-17:15 | 14-APR-10:15 | 01-APR-06:15
| May | 23-MAY-11:15 | 26-MAY-17:30 | 28-MAY-16:00 | 31-MAY-17:45 | 29-MAY-11:00 | 31-MAY-17:15 | 09-MAY-11:00 | 15-MAY-17:15 | 31-MAY-17:15 | 15-MAY-17:15 | 30-MAY-17:15 | 23-MAY-17:15 | 27-MAY-17:15 | 16-MAY-17:15 | 31-MAY-17:15 | 30-MAY-17:15
| Jun | 26-JUN-10:00 | 13-JUN-17:15 | 08-JUN-15:00 | 08-JUN-17:15 | 28-JUN-11:15 | 27-JUN-16:15 | 16-JUN-11:15 | 30-JUN-16:00 | 19-JUN-17:15 | 27-JUN-17:45 | 08-JUN-11:00 | 28-JUN-11:00 | 29-JUN-17:30 | 30-JUN-16:15 | 14-JUN-17:15 | 20-JUN-17:00
| Jul | 13-JUL-10:00 | 30-JUL-10:00 | 19-JUL-16:00 | 03-JUL-17:30 | 29-JUL-10:15 | 24-JUL-16:15 | 02-JUL-15:30 | 25-JUL-10:00 | 31-JUL-17:30 | 24-JUL-17:00 | 14-JUL-11:15 | 17-JUL-11:00 | 15-JUL-15:30 | 21-JUL-16:00 | 06-JUL-17:30 | 29-JUL-17:00
| Aug | 21-AUG-15:30 | 31-AUG-10:00 | 01-AUG-16:00 | 17-AUG-11:00 | 08-AUG-11:00 | 04-AUG-16:30 | 15-AUG-11:00 | 17-AUG-15:15 | 01-AUG-17:15 | 07-AUG-17:15 | 04-AUG-16:15 | 30-AUG-11:00 | 27-AUG-15:15 | 09-AUG-17:15 | 11-AUG-17:30 | 15-AUG-17:15
| Sep | 06-SEP-11:00 | 16-SEP-10:00 | 12-SEP-17:30 | 11-SEP-11:00 | 24-SEP-10:00 | 01-SEP-11:00 | 28-SEP-15:15 | 05-SEP-11:00 | 20-SEP-17:15 | 02-SEP-15:00 | 06-SEP-11:15 | 02-SEP-15:15 | 14-SEP-11:00 | 01-SEP-17:15 | 08-SEP-17:00 | 19-SEP-06:30
| Oct | 07-OCT-17:00 | 29-OCT-17:45 | 24-OCT-17:45 | 21-OCT-17:00 | 19-OCT-10:00 | 03-OCT-17:30 | 16-OCT-17:30 | 20-OCT-17:30 | 12-OCT-17:45 | 17-OCT-17:30 | 31-OCT-17:15 | 05-OCT-11:00 | 08-OCT-17:45 | 05-OCT-17:00 | 07-OCT-17:45 | 04-OCT-06:00
| Nov | 01-NOV-17:00 | 27-NOV-18:30 | 12-NOV-17:30 | 19-NOV-17:30 | 20-NOV-12:00 | 10-NOV-17:15 | 02-NOV-17:00 | 04-NOV-17:15 | 01-NOV-17:30 | 04-NOV-17:45 | 02-NOV-17:30 | 04-NOV-17:15 | 02-NOV-17:15 | 21-NOV-07:30 | 08-NOV-18:45 | 14-NOV-08:30
| Dec | 15-DEC-18:15 | 02-DEC-18:00 | 11-DEC-17:30 | 04-DEC-18:00 | 19-DEC-12:00 | 05-DEC-18:15 | 03-DEC-17:45 | 23-DEC-07:15 | 08-DEC-16:00 | 31-DEC-07:45 | 12-DEC-18:45 | 21-DEC-16:45 | 02-DEC-07:15 | 29-DEC-07:00 | 26-DEC-07:30 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 5643.98 | 5998.77 | 5357.63 | 5533.75 | 4658.69 | 5811.65 | 4856.26 | 6010.41 | 5484.12 | 3730.11 | 6147.26 | 5631.23 | 6271.32 | 6054.15 | 6465.5 | 7430.33
| Total Source Energy (MJ/m2) | 11041.66 | 11735.76 | 10481.45 | 10826.01 | 9114.08 | 11369.69 | 9500.6 | 11758.52 | 10728.92 | 7297.44 | 12026.25 | 11016.71 | 12268.95 | 11844.09 | 12648.86 | 14536.4
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
| Total Building | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
Emissions
| Carbon Equivalent (kg) | 122736.6634 | 141271.0685 | 129729.74 | 127031.5723 | 56384.2377 | 139002.1068 | 60221.9037 | 117635.6994 | 158670.7803 | 52423.7859 | 202351.4217 | 159319.1003 | 146439.978 | 148567.1428 | 148064.8667 | 143020.9054
| CO2 (kg) | 294312.6379 | 362691.7444 | 316010.9198 | 304048.1961 | 155058.0692 | 340968.3413 | 166365.4608 | 283856.003 | 384794.9668 | 140291.6157 | 487576.7505 | 388593.4579 | 360988.7326 | 366244.8761 | 367974.4502 | 381396.3564
| NOX (kg) | 475.4803 | 451.3663 | 488.1665 | 512.0354 | 135.7973 | 511.4738 | 146.2021 | 469.7431 | 609.1734 | 163.4671 | 794.0043 | 605.8281 | 552.6103 | 558.0621 | 550.6564 | 417.8239
| SO2 (kg) | 1640.8403 | 1711.7898 | 1457.6247 | 1158.4496 | 890.9912 | 1899.6529 | 866.133 | 1172.2458 | 1408.3098 | 231.2184 | 2108.7464 | 1371.5576 | 734.1016 | 817.6198 | 707.1243 | 1499.1959
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0076 | 0.0049 | 0.0041 | 0.0044 | 0.0005 | 0.0037 | 0.0005 | 0.0049 | 0.0056 | 0.0011 | 0.0066 | 0.0055 | 0.0056 | 0.0059 | 0.0054 | 0.0054
| Water for Electricity (m3) | 203.044 | 583.8072 | 10765.2 | 2059.98 | 5374.25 | 9472.42 | 5223.83 | 72.8795 | 1464.01 | 3050.32 | 485.3356 | 1425.73 | 482.1669 | 19383.7 | 464.3793 | 300.7199

## Picture
DOE Commercial Reference Building - Full Service Restaurant

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
BLDG_LIGHT_SCH | Fraction | Through 12/31 | SummerDesign | [24 empty] | 24 | 35.4 | 1845.86 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 17.7
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | 8.4 | 56.8 | 2961.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | 8.25
|  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | 6.55
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5 | 101.5 | 5292.5
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456
|  |  | Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
CLGSETP_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 600
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482.4
HVACOperationSchd | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
MinOA_Sched | Fraction | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 7.75 | 52.65 | 2745.32
|  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 7.45
|  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 6.45
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600