## BuildingSummary
Building Summary Large Hotel pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Large Hotel pre-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.59998 | See Reference Buildings Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZCAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | 2 air cooled chillers | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 44332.9

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 7.5347 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 38.099 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 1.0572
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 38.099 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.35236
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 8.6039 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.39384
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 3.9573 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.39382
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 12.2365 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 1.1318
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 15.7419 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.82991
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 20.2858 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.34234
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60879
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60863
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 13.1176 |  |  |  |  | 0.25 | 97.35 |  | 0.16612
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 3.4487
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 16.8341 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 1.132
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 13.081 |  |  |  |  | 0.25 | 103.03 |  | 0.44675
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 |  |  |  | 15229.9891
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls - commercial space
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Exterior walls - residential space
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Underground walls
| Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
| R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Windows - fixed, commercial
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Windows - operable, residential
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER 1 | 747.0562 | 756.0121 | 630.387 | 677.0964 | 454.8781 | 493.5297 | 318.8042 | 689.8485 | 359.2899 | 353.1287 | 636.1552 | 303.3452 | 629.6027 | 285.8003 | 485.7894 | 254.7872
| COOLSYS1 CHILLER 2 | 747.0562 | 756.0121 | 630.387 | 677.0964 | 454.8781 | 493.5297 | 318.8042 | 689.8485 | 359.2899 | 353.1287 | 636.1552 | 303.3452 | 629.6027 | 285.8003 | 485.7894 | 254.7872
Heating (kW)
| HEATSYS1 BOILER | 2853.3571 | 3547.8467 | 3087.6181 | 3800.5772 | 2890.3308 | 3287.227 | 3102.263 | 4155.4364 | 3407.0826 | 3635.3411 | 4724.0541 | 3931.2693 | 5068.4706 | 4659.6448 | 5144.6648 | 6251.9205
| CORRIDOR_FLR_6 UNIT HEATER COIL | 5.774 | 13.2924 | 9.5946 | 16.5627 | 6.9952 | 12.5342 | 9.3845 | 17.6413 | 15.8021 | 13.2739 | 20.0543 | 18.389 | 21.2294 | 21.0153 | 22.6241 | 29.1742
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER 1 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
| COOLSYS1 CHILLER 2 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
| CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Control - Economizer
| FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| CAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CORRIDOR_FLR_6 UNIT HEATERFAN | 0.16 | 0.37 | 0.28 | 0.48 | 0.2 | 0.38 | 0.26 | 0.49 | 0.54 | 0.37 | 0.54 | 0.61 | 0.56 | 0.64 | 0.61 | 0.76
| DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
| KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 1.76 | 1.81 | 2.01 | 1.87 | 1.69 | 2.02 | 1.73 | 1.81 | 1.98 | 1.81 | 1.44 | 1.54 | 1.43 | 1.5 | 1.38 | 1.33
| ROOM_1_FLR_6 FAN COILFAN | 0.51 | 0.53 | 0.58 | 0.54 | 0.48 | 0.58 | 0.48 | 0.51 | 0.56 | 0.5 | 0.4 | 0.43 | 0.39 | 0.4 | 0.37 | 0.35
| ROOM_2_FLR_3 FAN COILFAN | 1.8 | 1.84 | 2.01 | 1.87 | 1.61 | 2.01 | 1.49 | 1.78 | 1.98 | 1.63 | 1.41 | 1.51 | 1.4 | 1.45 | 1.34 | 1.24
| ROOM_2_FLR_6 FAN COILFAN | 0.52 | 0.53 | 0.58 | 0.54 | 0.46 | 0.58 | 0.41 | 0.51 | 0.56 | 0.46 | 0.39 | 0.42 | 0.38 | 0.39 | 0.36 | 0.33
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.63 | 1.82 | 2.2 | 2.01 | 2.05 | 2.23 | 2.63 | 2.07 | 2.03 | 2.65 | 1.48 | 1.52 | 1.5 | 1.59 | 1.48 | 2.06
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_5_FLR_3 FAN COILFAN | 1.5 | 1.52 | 1.71 | 1.59 | 1.43 | 1.66 | 1.43 | 1.55 | 1.61 | 1.56 | 1.21 | 1.24 | 1.23 | 1.24 | 1.16 | 1.2
| ROOM_6_FLR_3 FAN COILFAN | 1.57 | 1.57 | 1.74 | 1.63 | 1.38 | 1.67 | 1.23 | 1.55 | 1.63 | 1.4 | 1.24 | 1.26 | 1.25 | 1.25 | 1.18 | 1.15
| FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
| CAV WITH REHEAT_FAN | 37.78 | 37.97 | 39.18 | 39.07 | 36.7 | 39.78 | 35.56 | 38.02 | 41.99 | 37.07 | 37.14 | 40.71 | 37.41 | 39.32 | 36.29 | 35.26
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.072957 | 0.098768 | 0.066677 | 0.099375 | 0.041323 | 0.086017 | 0.12275 | 0.058392 | 0.036977 | 0.066648 | 0.095804 | 0.036982 | 0.053985 | 0.069603 | 0.054701 | 0.090831
| Total Cost ($/m2) | 45.6 | 54.04 | 35.26 | 45.05 | 16.92 | 37.66 | 40.28 | 23.77 | 12.87 | 19.9 | 35.52 | 11.59 | 19.4 | 20.24 | 16.28 | 22.23
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.008183 | 0.0085607 | 0.010763 | 0.0084001 | 0.0081045 | 0.0084042 | 0.010076 | 0.0071925 | 0.0082864 | 0.0089279 | 0.0071994 | 0.0079839 | 0.00878 | 0.0079866 | 0.0042094
| Total Cost ($/m2) | 5.08 | 4.52 | 4.22 | 7.09 | 5.1 | 4.59 | 5.9 | 7.67 | 5.26 | 6.54 | 7.6 | 5.97 | 7.46 | 8.17 | 8.42 | 5.25
Total Utility Costs
| Cost Intensity ($/m2) | 50.68 | 58.56 | 39.48 | 52.14 | 22.03 | 42.25 | 46.18 | 31.44 | 18.13 | 26.44 | 43.12 | 17.56 | 26.85 | 28.41 | 24.71 | 27.48
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 33.3333 | 0 | 141.6667 | 0 | 0 | 0 | 325 | 0 | 0 | 394.4444 | 291.6667 | 1025 | 805.5556 | 2125 | 11733.3333
| Cooling | 5082066.6667 | 4219777.7778 | 3990483.3333 | 3168288.8889 | 2680194.4444 | 2969744.4444 | 1774252.7778 | 2661205.5556 | 1962191.6667 | 1444936.1111 | 2268905.5556 | 1601777.7778 | 2140177.7778 | 1357763.8889 | 1452661.1111 | 851166.6667
| Interior Lighting | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111
| Exterior Lighting | 121627.7778 | 121580.5556 | 121558.3333 | 121538.8889 | 121447.2222 | 121419.4444 | 121483.3333 | 121408.3333 | 121455.5556 | 121213.8889 | 121427.7778 | 121358.3333 | 121350 | 121322.2222 | 121252.7778 | 120511.1111
| Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
| Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
| Fans | 400194.4444 | 384802.7778 | 407511.1111 | 376900 | 371347.2222 | 400216.6667 | 356988.8889 | 362719.4444 | 391030.5556 | 353202.7778 | 345066.6667 | 362661.1111 | 343627.7778 | 351027.7778 | 333402.7778 | 326297.2222
| Pumps | 30922.2222 | 25647.2222 | 24247.2222 | 21116.6667 | 19044.4444 | 20675 | 16094.4444 | 18719.4444 | 18788.8889 | 14997.2222 | 16755.5556 | 15705.5556 | 16433.3333 | 14936.1111 | 14213.8889 | 13425
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 22238.8889 | 21477.7778 | 21633.3333 | 20783.3333 | 20841.6667 | 21105.5556 | 20200 | 20319.4444 | 20311.1111 | 19888.8889 | 20061.1111 | 19969.4444 | 19925 | 19675 | 19430.5556 | 19083.3333
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 7090913.8889 | 6207183.3333 | 5999294.4444 | 5142633.3333 | 4646738.8889 | 4967025 | 3722883.3333 | 4618561.1111 | 3947644.4444 | 3388105.5556 | 4206475 | 3555625 | 4076402.7778 | 3299391.6667 | 3376950 | 2776080.5556
Gas (MJ)
| Heating | 13930 | 242480 | 147880 | 492990 | 91660 | 280910 | 336750 | 893770 | 700830 | 819410 | 1254650 | 1033620 | 1614970 | 1476120 | 2038150 | 3088700
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3783380 | 4783230 | 4208950 | 5746480 | 5559200 | 4901180 | 6383440 | 6503500 | 6359970 | 6897320 | 7168010 | 7133310 | 7742170 | 7846400 | 8689170 | 9835570
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5035950 | 6264360 | 5595480 | 7478110 | 6889510 | 6420740 | 7958830 | 8635930 | 8299450 | 8955380 | 9661310 | 9405580 | 10595790 | 10561170 | 11965970 | 14162920
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 30563240 | 28610230 | 27192940 | 25991600 | 23617770 | 24302030 | 21361210 | 25262740 | 22510970 | 21152560 | 24804620 | 22205830 | 25270840 | 22438980 | 24122990 | 24156810
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0.010577 | 0 | 0.044953 | 0 | 0 | 0 | 0.10313 | 0 | 0 | 0.12516 | 0.092549 | 0.32525 | 0.25561 | 0.67429 | 3.7231
| Cooling (elec) | 1612.6022 | 1338.9874 | 1266.2294 | 1005.337 | 850.4586 | 942.3364 | 562.9922 | 844.4332 | 622.6275 | 458.496 | 719.9516 | 508.2638 | 679.1047 | 430.8352 | 460.9472 | 270.0856
| Interior Lighting (elec) | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946
| Exterior Lighting (elec) | 38.594 | 38.579 | 38.572 | 38.5658 | 38.5367 | 38.5279 | 38.5482 | 38.5244 | 38.5393 | 38.4627 | 38.5305 | 38.5085 | 38.5058 | 38.497 | 38.475 | 38.2397
| Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
| Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
| Fans (elec) | 126.9866 | 122.1027 | 129.3083 | 119.595 | 117.833 | 126.9937 | 113.277 | 115.0953 | 124.0788 | 112.0756 | 109.4939 | 115.0768 | 109.0373 | 111.3854 | 105.7928 | 103.5381
| Pumps (elec) | 9.812 | 8.1382 | 7.6939 | 6.7006 | 6.043 | 6.5604 | 5.107 | 5.9399 | 5.9619 | 4.7588 | 5.3167 | 4.9836 | 5.2145 | 4.7394 | 4.5102 | 4.2599
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 7.0567 | 6.8152 | 6.8645 | 6.5948 | 6.6133 | 6.6971 | 6.4097 | 6.4476 | 6.445 | 6.311 | 6.3656 | 6.3366 | 6.3224 | 6.2431 | 6.1656 | 6.0554
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2250.0342 | 1969.6156 | 1903.6499 | 1631.8208 | 1474.4674 | 1576.0981 | 1181.3167 | 1465.5262 | 1252.6361 | 1075.0875 | 1334.7662 | 1128.2435 | 1293.4927 | 1046.9375 | 1071.5478 | 880.8845
Gas (MJ/m2)
| Heating (gas) | 1.2278 | 21.3727 | 13.0345 | 43.4533 | 8.0791 | 24.7601 | 29.6819 | 78.7789 | 61.7728 | 72.2247 | 110.5877 | 91.1056 | 142.3472 | 130.1086 | 179.6472 | 272.2451
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 333.4758 | 421.6049 | 370.9866 | 506.508 | 490.0007 | 432.0013 | 562.6511 | 573.2335 | 560.5824 | 607.9457 | 631.8049 | 628.7464 | 682.4127 | 691.5998 | 765.8835 | 866.9298
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 443.8802 | 552.1551 | 493.1985 | 659.1378 | 607.2573 | 565.9388 | 701.5096 | 761.1908 | 731.5326 | 789.3478 | 851.5701 | 829.0295 | 933.9373 | 930.8859 | 1054.7082 | 1248.3524
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2693.9144 | 2521.7716 | 2396.8484 | 2290.9595 | 2081.7247 | 2142.0369 | 1882.8263 | 2226.7161 | 1984.1688 | 1864.4354 | 2186.3364 | 1957.273 | 2227.4301 | 1977.8234 | 2126.2559 | 2129.2369
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1081.0159 | 1078.701 | 968.2755 | 903.7733 | 796.7976 | 721.8043 | 654.5865 | 611.3113 | 654.9418 | 551.6269 | 589.5279 | 650.0136 | 542.8826 | 558.5837 | 516.6652 | 505.1188
| Feb | 1079.1158 | 1095.1526 | 973.5511 | 894.7235 | 789.5063 | 823.2144 | 664.5473 | 586.9195 | 700.6747 | 676.0002 | 579.0037 | 648.9655 | 569.4513 | 634.1698 | 564.3966 | 505.9616
| Mar | 1093.0055 | 1096.3244 | 1002.7869 | 1028.7392 | 790.1299 | 836.1976 | 664.7324 | 1047.6866 | 703.3144 | 694.6332 | 875.7449 | 653.6521 | 740.6117 | 634.4132 | 581.6771 | 587.1854
| Apr | 1103.0646 | 1096.279 | 1003.4541 | 1026.3405 | 802.6543 | 854.3526 | 663.9924 | 1035.1076 | 705.1925 | 695.8785 | 860.279 | 651.0676 | 957.658 | 634.6861 | 693.4105 | 585.6287
| May | 1103.1738 | 1106.8453 | 1014.6826 | 1031.9902 | 789.8052 | 853.4162 | 664.4834 | 1046.1479 | 706.8869 | 696.3803 | 995.8669 | 651.4526 | 983.6592 | 636.5038 | 818.2905 | 581.0134
| Jun | 1089.8219 | 1079.4249 | 1022.7388 | 1039.6884 | 792.7933 | 857.6858 | 664.22 | 1035.983 | 707.492 | 695.084 | 999.7557 | 650.7333 | 976.7651 | 606.5976 | 823.6058 | 578.5247
| Jul | 1066.4917 | 1099.1563 | 1022.8122 | 1021.1503 | 787.1671 | 857.6204 | 664.1467 | 1034.65 | 708.669 | 696.4492 | 985.2503 | 648.8136 | 973.4767 | 625.972 | 817.6203 | 576.4966
| Aug | 1066.0056 | 1088.9004 | 1023.4842 | 1012.8366 | 783.3364 | 859.273 | 666.4033 | 1054.8097 | 709.9097 | 696.5121 | 975.231 | 652.407 | 972.0155 | 633.6936 | 827.6101 | 579.6175
| Sep | 1066.7557 | 1114.8715 | 1017.3462 | 1006.3018 | 791.0619 | 851.7508 | 662.9468 | 1037.4292 | 705.6783 | 697.3455 | 990.6998 | 651.1118 | 968.5783 | 634.5388 | 819.4933 | 606.0414
| Oct | 1085.4107 | 1074.0337 | 1001.954 | 1015.2625 | 796.4047 | 847.6525 | 664.0913 | 1029.7643 | 705.037 | 697.2354 | 980.1178 | 650.9001 | 949.0381 | 637.6887 | 799.6917 | 606.3176
| Nov | 1091.2621 | 1078.99 | 975.6724 | 975.0652 | 793.0295 | 830.039 | 667.3264 | 1014.3479 | 703.5585 | 669.716 | 986.6597 | 649.7353 | 771.7616 | 636.2853 | 622.4247 | 513.4287
| Dec | 1085.7498 | 1081.6201 | 966.5768 | 853.7146 | 803.2201 | 800.4275 | 649.8846 | 559.346 | 623.3998 | 535.4109 | 592.1439 | 612.3011 | 542.85 | 569.715 | 521.5521 | 451.7571
Time of Peak Electrical Demand
| Jan | 04-JAN-20:30 | 02-JAN-20:00 | 27-JAN-20:10 | 24-JAN-21:00 | 26-JAN-20:10 | 29-JAN-08:00 | 27-JAN-20:19 | 08-JAN-20:00 | 26-JAN-20:19 | 27-JAN-21:00 | 17-JAN-21:00 | 24-JAN-20:10 | 30-JAN-21:00 | 30-JAN-21:00 | 16-JAN-20:00 | 21-JAN-20:00
| Feb | 17-FEB-20:10 | 22-FEB-20:00 | 27-FEB-20:10 | 18-FEB-18:10 | 23-FEB-20:10 | 27-FEB-20:10 | 13-FEB-20:10 | 15-FEB-20:19 | 13-FEB-20:10 | 21-FEB-20:10 | 20-FEB-20:00 | 10-FEB-20:40 | 19-FEB-20:00 | 03-FEB-20:10 | 22-FEB-21:00 | 28-FEB-20:10
| Mar | 14-MAR-19:10 | 21-MAR-19:10 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:10 | 22-MAR-19:10 | 29-MAR-19:10 | 09-MAR-20:19 | 31-MAR-19:10 | 28-MAR-19:10 | 31-MAR-18:10 | 31-MAR-19:00 | 19-MAR-19:00 | 09-MAR-20:49 | 22-MAR-19:40 | 29-MAR-19:30
| Apr | 19-APR-19:10 | 04-APR-19:10 | 26-APR-19:10 | 13-APR-19:10 | 11-APR-19:10 | 28-APR-19:10 | 27-APR-19:10 | 05-APR-19:10 | 19-APR-19:10 | 14-APR-19:10 | 28-APR-17:19 | 10-APR-19:19 | 16-APR-19:10 | 13-APR-19:10 | 04-APR-19:10 | 28-APR-20:00
| May | 05-MAY-19:10 | 11-MAY-19:10 | 19-MAY-19:19 | 26-MAY-19:40 | 09-MAY-19:10 | 31-MAY-19:10 | 02-MAY-19:10 | 05-MAY-19:10 | 15-MAY-19:10 | 01-MAY-19:19 | 04-MAY-19:10 | 30-MAY-19:19 | 15-MAY-19:30 | 10-MAY-19:00 | 31-MAY-19:49 | 12-MAY-19:00
| Jun | 02-JUN-19:10 | 23-JUN-19:30 | 27-JUN-19:00 | 12-JUN-19:49 | 29-JUN-19:00 | 21-JUN-19:10 | 08-JUN-19:00 | 21-JUN-19:40 | 13-JUN-19:19 | 08-JUN-19:00 | 15-JUN-19:30 | 01-JUN-19:19 | 22-JUN-19:00 | 15-JUN-19:10 | 15-JUN-19:00 | 07-JUN-19:10
| Jul | 24-JUL-19:00 | 28-JUL-19:19 | 10-JUL-19:00 | 11-JUL-19:49 | 28-JUL-19:10 | 06-JUL-19:10 | 06-JUL-19:49 | 20-JUL-19:30 | 12-JUL-19:19 | 12-JUL-19:00 | 21-JUL-19:19 | 10-JUL-19:30 | 03-JUL-19:00 | 31-JUL-19:00 | 26-JUL-19:49 | 05-JUL-19:10
| Aug | 24-AUG-19:10 | 11-AUG-19:10 | 01-AUG-19:00 | 29-AUG-19:10 | 23-AUG-19:10 | 09-AUG-19:10 | 02-AUG-19:19 | 18-AUG-19:10 | 24-AUG-19:40 | 31-AUG-19:10 | 01-AUG-19:10 | 23-AUG-19:10 | 29-AUG-19:10 | 02-AUG-19:00 | 23-AUG-19:10 | 31-AUG-19:10
| Sep | 08-SEP-19:00 | 26-SEP-19:10 | 11-SEP-19:10 | 12-SEP-19:10 | 20-SEP-19:10 | 11-SEP-19:10 | 18-SEP-19:10 | 08-SEP-19:10 | 08-SEP-19:10 | 06-SEP-19:10 | 26-SEP-19:10 | 15-SEP-19:19 | 13-SEP-19:10 | 21-SEP-19:10 | 06-SEP-19:10 | 20-SEP-19:10
| Oct | 24-OCT-19:10 | 19-OCT-19:10 | 02-OCT-19:10 | 06-OCT-19:10 | 20-OCT-19:00 | 06-OCT-19:10 | 06-OCT-19:10 | 20-OCT-19:10 | 25-OCT-19:10 | 05-OCT-19:10 | 11-OCT-19:19 | 02-OCT-19:10 | 08-OCT-19:10 | 20-OCT-19:00 | 07-OCT-19:10 | 03-OCT-19:00
| Nov | 16-NOV-20:10 | 24-NOV-20:10 | 06-NOV-20:10 | 22-NOV-20:00 | 07-NOV-20:10 | 21-NOV-20:10 | 02-NOV-19:10 | 03-NOV-19:10 | 09-NOV-20:10 | 04-NOV-19:10 | 02-NOV-19:10 | 10-NOV-20:10 | 02-NOV-15:09 | 21-NOV-20:10 | 02-NOV-20:00 | 14-NOV-21:00
| Dec | 28-DEC-20:10 | 20-DEC-20:30 | 13-DEC-20:00 | 04-DEC-20:00 | 29-DEC-20:10 | 05-DEC-19:19 | 17-DEC-20:10 | 03-DEC-20:00 | 05-DEC-20:19 | 25-DEC-20:00 | 11-DEC-21:00 | 22-DEC-20:00 | 01-DEC-21:00 | 31-DEC-20:00 | 01-DEC-20:00 | 19-DEC-21:00
Source Energy
| Total Source Energy (GJ) | 90173.28 | 88000.86 | 74423.03 | 70445.46 | 59297.3 | 70972.81 | 50171.41 | 68887.93 | 56216.81 | 31026.77 | 64248.32 | 52742.13 | 62008.76 | 52820.05 | 54850.52 | 51164.08
| Total Source Energy (MJ/m2) | 7948.08 | 7756.6 | 6559.82 | 6209.23 | 5226.6 | 6255.71 | 4422.22 | 6071.94 | 4955.08 | 2734.77 | 5663 | 4648.81 | 5465.6 | 4655.68 | 4834.65 | 4509.72
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
| Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
Emissions
| Carbon Equivalent (kg) | 2035490 | 2183440 | 1911940 | 1718970 | 667281.3899 | 1791040 | 578597.0804 | 1402070 | 1762270 | 408259.4792 | 2416900 | 1622070 | 1586400 | 1396170 | 1371690 | 1036550
| CO2 (kg) | 4765390 | 5521790 | 4550540 | 3984930 | 1808780 | 4302380 | 1576240 | 3244900 | 4189930 | 1052770 | 5677820 | 3874420 | 3768810 | 3354590 | 3288250 | 2694690
| NOX (kg) | 8179.7402 | 7125.2002 | 7463.0998 | 7296.2708 | 1566.6087 | 6810.7008 | 1370.5072 | 5996.7523 | 6985.2862 | 1365.4558 | 9879.1474 | 6382.9208 | 6371.2017 | 5477.5319 | 5428.7983 | 3121.4069
| SO2 (kg) | 30353.296 | 29609.948 | 24125.863 | 18052.6498 | 13523.2956 | 27324.3246 | 10835.2757 | 16861.9064 | 17240.793 | 2621.1347 | 28350.8657 | 15529.2268 | 9623.8039 | 8812.5992 | 7973.3488 | 14135.1546
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1388 | 0.0839 | 0.066 | 0.0667 | 0.0068 | 0.0519 | 0.0057 | 0.0688 | 0.068 | 0.0112 | 0.0865 | 0.0615 | 0.0713 | 0.0622 | 0.0594 | 0.0493
| Water for Electricity (m3) | 3756.47 | 10099.8 | 178205 | 32108.5 | 81586.3 | 136265 | 65365.5 | 1048.59 | 17925.5 | 34615.6 | 6526.09 | 16145.4 | 6324.3 | 208997 | 5239.14 | 2836.27

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 618 | 4326 | 225570
HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 469 | 3283 | 171185
Corr_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
Corr_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Guest_CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Guest_HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652 | 4564 | 237980
Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 435 | 3045 | 158775
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HVACOperationSchd | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
MinOA_Sched | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
Kitchen_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Guest Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Guest Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Laundry Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600