## BuildingSummary
Building Summary Outpatient Health Care post-1980 construction
|  | Value | Data Source
Program
| Building Name | Outpatient Health Care Reference Building post-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, outpatient
Form
| Total Floor Area (m2) | 3804.01 | Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health Care Facilities – 30% Energy Savings. Golden, CO: National Renewable Energy Laboratory, NREL/TP-550-46314. Available at www.nrel.gov/docs/fy10osti/46314.pdf
| Building Shape | Irregular
| Aspect Ratio | 1.43
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.2408
| East | 0.1914
| North | 0.2052
| West | 0.1288
| Total | 0.1985
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Zoned By Use
| Floor to Ceiling Height (m) | 3.05
| Floor to Floor Height (m) | 3.05
| Roof type | Built-up flat roof, insulation entirely above deck | Doebber, et al. 2009
Fabric
Exterior walls
| Construction Type | Steel frame | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1553.34
| Net Dimensions - Total Area (m2) | 1245.05
| Wall to Skin Ratio | 0.53076
Roof
| Construction Type | IEAD | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1373.29
| Net Dimensions - Total Area (m2) | 1373.29
| Roof to Skin Ratio | 0.46924
Window Dimensions (m2)
| South | 114.08
| East | 57.97
| North | 97.22
| West | 39.02
| Total Area (m2) | 308.29
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor | Doebber, et al. 2009
| Construction | 8in slab w/carpet | Doebber, et al. 2009
| Dimensions - Total Area (m2) | 1373.29
Interior Partitions
| Construction | Gypsum Board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 2746.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ft3/min per ft2 of exterior wall) | 0.93401
HVAC
| System Type | Packaged VAV With Reheat | Doebber, et al. 2009
| Heating Type | Hot Water Boiler, Furnace | Doebber, et al. 2009
| Cooling Type | DX Cooling Coil | Doebber, et al. 2009
| Fan Control | VAV | Doebber, et al. 2009
Service Water Heating
| SWH Type | Gas Water Heater
| Fuel | Gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 240.48

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Floor 1 Anesthesia | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 |  | 0 | 22.6042 | 21.53 |  | 3.7854 |  | 6 | 60.2012 | 67.9604 | 1.1157
Floor 1 Bio Haz | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0
Floor 1 Café | Yes | 1 | 39.0193 | 118.9309 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 13.9931 | 10.76 |  |  | 10 |  | 390.1928 |  | 0.63761
Floor 1 Clean | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 13.9931 | 21.53 |  |  |  | 1.5 | 17.5587 |  | 0
Floor 1 Clean Work | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 13.9931 | 21.53 |  |  |  | 1.5 | 22.9935 |  | 0
Floor 1 Dictation | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 20 | 0.58529 | 19.375 | 11.84 |  |  | 10 |  | 5.8529 |  | 0
Floor 1 Dressing Room | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 19.375 | 11.84 |  |  | 10 |  | 2.0903 |  | 2.6777
Floor 1 Electrical Room | No | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 |  | 0 | 7.5347 | 53.82 | [6 empty] | 0.95598
Floor 1 Elevator Pump Room | No | 1 | 8.4542 | 25.7684 | 3.048 | 18.58 | 0 |  | 0 | 7.5347 | 529.29 | [6 empty] | 2.9428
Floor 1 Humid | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 19.375 | 11.84 |  |  | 10 |  | 2.5084 |  | 0
Floor 1 IT Hall | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 0
Floor 1 IT Room | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 19.375 | 11.84 |  |  | 10 |  | 5.2026 |  | 0
Floor 1 Lobby | Yes | 1 | 57.7857 | 176.1309 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 10.7639 | 11.84 |  |  | 8 |  | 138.6857 |  | 0.47364
Floor 1 Lobby Hall | Yes | 1 | 22.2967 | 67.9605 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.5742 |  | 0
Floor 1 Lobby Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
Floor 1 Locker Room | Yes | 1 | 61.316 | 186.8913 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 9.6875 | 32.29 |  |  | 8 |  | 73.5792 |  | 0.44637
Floor 1 Locker Room Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Lounge | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 9.6875 | 32.29 |  |  | 8 | 0 | 40.1341 |  | 0
Floor 1 Med Gas | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 4.9269
Floor 1 MRI Control Room | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 22.6042 | 11.84 |  | 3.7854 |  | 1.5 | 23.4116 | 79.2871 | 0.39894
Floor 1 MRI Hall | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.4142 |  | 0
Floor 1 MRI Room | Yes | 1 | 40.8773 | 124.5942 | 3.048 | 0 | 0 | 5 | 8.1755 | 22.6042 | 571.116 |  | 3.7854 |  | 1.5 | 61.316 | 207.6567 | 0
Floor 1 MRI Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
Floor 1 Nourishment | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 22.6042 | 21.53 |  |  | 10 |  | 33.8167 |  | 0
Floor 1 Nurse Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Nurse Janitor | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 1 Nurse Station | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 22.6042 | 21.53 |  |  | 10 |  | 48.4954 |  | 0
Floor 1 Nurse Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 0
Floor 1 Office | Yes | 1 | 44.8722 | 136.7705 | 3.048 | 0 | 0 | 20 | 2.2436 | 19.375 | 11.84 |  |  | 10 |  | 22.4361 |  | 0
Floor 1 Operating Room 1 | Yes | 1 | 42.7354 | 130.2576 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 108.5479 |  | 1.2518
Floor 1 Operating Room 2 | Yes | 1 | 44.5935 | 135.921 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 113.2674 |  | 0.66961
Floor 1 Operating Room 3 | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 112.3235 |  | 0
Floor 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 24.757 | 32.29 |  | 3.7854 |  |  | 16.9901 |  | 0
Floor 1 Pre-Op Hall | Yes | 1 | 49.0528 | 149.5131 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 12.2632 |  | 0
Floor 1 Pre-Op Room 1 | Yes | 1 | 17.5587 | 53.5189 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 15.0695 | 21.53 |  | 3.7854 |  |  | 29.7327 |  | 0.28369
Floor 1 Pre-Op Room 2 | Yes | 1 | 31.4012 | 95.711 | 3.048 | 0 | 0 | 10 | 3.1401 | 15.0695 | 21.53 |  | 3.7854 |  |  | 53.1727 |  | 0
Floor 1 Pre-Op Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
Floor 1 Procedure Room | Yes | 1 | 26.4774 | 80.7031 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 17.2222 | 32.29 |  | 3.7854 |  |  | 67.2525 |  | 0.89261
Floor 1 Reception | Yes | 1 | 47.2876 | 144.1329 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 10.7639 | 11.84 |  |  | 8 |  | 113.4904 |  | 0.34207
Floor 1 Reception Hall | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 2.9729 |  | 0
Floor 1 Recovery Room | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 24.757 | 32.29 |  | 3.7854 |  |  | 84.9505 |  | 1.116
Floor 1 Scheduling | Yes | 1 | 11.0555 | 33.6971 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 19.375 | 11.84 |  |  | 10 |  | 5.5277 |  | 0.78728
Floor 1 Scrub | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.951 |  | 0
Floor 1 Soil | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 9.6875 | 21.53 |  |  |  | 7.5 | 87.7934 | 99.1089 | 0
Floor 1 Soil Hold | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 9.6875 | 21.53 |  |  |  | 7.5 | 39.0193 | 44.0468 | 0
Floor 1 Soil Work | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 9.6875 | 21.53 |  |  |  | 7.5 | 125.4191 | 141.5841 | 0
Floor 1 Step Down | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 24.757 | 32.29 |  | 3.7854 |  |  | 47.1947 |  | 1.6513
Floor 1 Sterile Hall | Yes | 1 | 57.2283 | 174.4319 | 3.048 | 7.43 | 2.23 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 14.3071 |  | 0.17385
Floor 1 Sterile Storage | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 27.5922 |  | 0
Floor 1 Storage | No | 1 | 85.4708 | 260.5152 | 3.048 | 58.5301 | 8.36 |  | 0 | 10.7639 | 0 | [6 empty] | 2.256
Floor 1 Sub-Sterile | Yes | 1 | 18.209 | 55.5011 | 3.048 | 13.01 | 2.97 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5522 |  | 0.95671
Floor 1 Utility Hall | Yes | 1 | 23.7832 | 72.4912 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.9458 |  | 0.83664
Floor 1 Utility Janitor | No | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 1 Utility Room | No | 1 | 33.4451 | 101.9407 | 3.048 | 16.72 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 2.0084
Floor 1 Vestibule | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.6723 |  | 1.4874
Floor 2 Conference | Yes | 1 | 31.2154 | 95.1447 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 19.375 | 10.76 |  |  | 10 |  | 156.0771 |  | 1.594
Floor 2 Conference Toilet | No | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 50.3426 | 0
Floor 2 Dictation | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 19.375 | 11.84 |  |  | 10 |  | 3.2516 |  | 0
Floor 2 Exam 1 | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 17.2222 | 11.84 |  |  |  | 1.5 | 50.1676 |  | 1.5622
Floor 2 Exam 2 | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 17.2222 | 11.84 |  |  |  | 1.5 | 75.2515 |  | 0.44628
Floor 2 Exam 3 | Yes | 1 | 66.8902 | 203.8815 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 17.2222 | 11.84 |  |  |  | 1.5 | 100.3353 |  | 0.44641
Floor 2 Exam 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 17.2222 | 11.84 |  |  |  | 1.5 | 11.7058 |  | 1.1153
Floor 2 Exam 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 17.2222 | 11.84 |  |  |  | 1.5 | 48.7741 |  | 0.95663
Floor 2 Exam 6 | Yes | 1 | 20.9032 | 63.713 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 17.2222 | 11.84 |  |  |  | 1.5 | 31.3548 |  | 0.89298
Floor 2 Exam 7 | Yes | 1 | 73.5792 | 224.2696 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 17.2222 | 11.84 |  |  |  | 1.5 | 110.3688 |  | 0.40583
Floor 2 Exam 8 | Yes | 1 | 25.0838 | 76.4556 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 17.2222 | 11.84 |  |  |  | 1.5 | 37.6257 |  | 0.89255
Floor 2 Exam 9 | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 17.2222 | 11.84 |  |  |  | 1.5 | 55.1844 |  | 0.40583
Floor 2 Exam Hall 1 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 3 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Exam Hall 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Exam Hall 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 3.3997
Floor 2 Lounge | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 9.6875 | 32.29 |  |  | 8 |  | 8.9187 |  | 0
Floor 2 Nurse Station 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 22.6042 | 21.53 |  |  | 10 |  | 27.8709 |  | 0
Floor 2 Nurse Station 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 22.6042 | 21.53 |  |  | 10 |  | 33.4451 |  | 0
Floor 2 Office | Yes | 1 | 52.0257 | 158.5745 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 19.375 | 11.84 |  |  | 10 |  | 26.0129 |  | 0.95642
Floor 2 Office Hall | Yes | 1 | 41.2489 | 125.7269 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 10.3122 |  | 0
Floor 2 Reception | Yes | 1 | 91.4166 | 278.638 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 10.7639 | 11.84 |  |  | 8 |  | 219.3998 |  | 0.66676
Floor 2 Reception Hall | Yes | 1 | 52.3973 | 159.7072 | 3.048 | 87.3301 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 13.0993 |  | 2.2318
Floor 2 Reception Toilet | No | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 99.1089 | 0
Floor 2 Scheduling 1 | Yes | 1 | 30.1006 | 91.7467 | 3.048 | 0 | 0 | 20 | 1.505 | 19.375 | 11.84 |  |  | 10 |  | 15.0503 |  | 0
Floor 2 Scheduling 2 | Yes | 1 | 31.7728 | 96.8437 | 3.048 | 0 | 0 | 20 | 1.5886 | 19.375 | 11.84 |  |  | 10 |  | 15.8864 |  | 0
Floor 2 Storage 1 | No | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 2 Storage 2 | No | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 2 Storage 3 | No | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 2 Utility | No | 1 | 11.7058 | 35.6793 | 3.048 | 8.36 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 0.95631
Floor 2 Work | Yes | 1 | 157.0061 | 478.5551 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 19.375 | 11.84 |  |  | 10 |  | 78.5031 |  | 0.20596
Floor 2 Work Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.096261
Floor 2 Work Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
Floor 2 X-Ray | Yes | 1 | 83.6127 | 254.8518 | 3.048 | 0 | 0 | 5 | 16.7225 | 22.6042 | 14.0206 |  | 3.7854 |  | 1.5 | 125.4191 |  | 0
Floor 3 Dressing Room | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 19.375 | 11.84 |  |  | 10 |  | 1.951 |  | 1.339
Floor 3 Elevator Hall | Yes | 1 | 34.3741 | 104.7724 | 3.048 | 3.72 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 8.5935 |  | 1.4839
Floor 3 Humid | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 19.375 | 11.84 |  |  | 10 | 0 | 5.0168 |  | 1.339
Floor 3 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 4.7387
Floor 3 Locker | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 9.6875 | 32.29 |  |  | 8 |  | 13.378 |  | 1.339
Floor 3 Lounge | Yes | 1 | 70.5134 | 214.925 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 9.6875 | 32.29 |  |  | 8 |  | 84.6161 |  | 1.7448
Floor 3 Lounge Toilet | No | 1 | 17.8374 | 54.3684 | 3.048 | 11.15 | 4.18 |  | 0 | 8.6111 | 4.31 | [5 empty] | 151.023 | 2.1761
Floor 3 Mechanical | No | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 |  | 0 | 7.5347 | 53.82 | [6 empty] | 2.2957
Floor 3 Mechanical Hall | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 6.9677 |  | 1.339
Floor 3 Office | Yes | 1 | 282.0536 | 859.7002 | 3.048 | 68.7501 | 19.51 | 20 | 14.1027 | 19.375 | 11.84 |  |  | 10 |  | 141.0268 |  | 1.6654
Floor 3 Office Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 1.4353
Floor 3 Office Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 2.8257
Floor 3 Physical Therapy 1 | Yes | 1 | 120.774 | 368.1193 | 3.048 | 78.9701 | 28.99 | 5 | 24.1548 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 193.2383 |  | 2.2146
Floor 3 Physical Therapy 2 | Yes | 1 | 54.9986 | 167.6359 | 3.048 | 0 | 0 | 5 | 10.9997 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 87.9978 |  | 1.339
Floor 3 Physical Therapy Toilet | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 66.0726 | 1.339
Floor 3 Storage 1 | No | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
Floor 3 Storage 2 | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
Floor 3 Treatment | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 17.2222 | 11.84 |  |  |  | 1.5 | 66.3328 |  | 1.339
Floor 3 Undeveloped 1 | No | 1 | 210.7041 | 642.2266 | 3.048 | 66.8901 | 25.64 |  | 0 | 0 | 0 | [6 empty] | 1.7641
Floor 3 Undeveloped 2 | No | 1 | 107.0243 | 326.2103 | 3.048 | 52.03 | 13.38 |  | 0 | 0 | 0 | [6 empty] | 1.99
Floor 3 Utility | No | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 | [6 empty] | 1.339
Floor 3 Work | Yes | 1 | 53.3263 | 162.5388 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 19.375 | 11.84 |  |  | 10 |  | 26.6632 |  | 2.2955
NE Stair | No | 1 | 15.6077 | 142.717 | 9.144 | 97.5501 | 12.02 |  | 0 | 8.6111 | 0 | [6 empty] | 1
NW Elevator | No | 1 | 13.0064 | 118.9309 | 9.144 | 75.2501 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 1
NW Stair | No | 1 | 17.8374 | 163.1052 | 9.144 | 111.4801 | 11.15 |  | 0 | 8.6111 | 0 | [6 empty] | 1
SW Stair | No | 1 | 8.9187 | 81.5526 | 9.144 | 55.7401 | 1.11 |  | 0 | 8.6111 | 0 | [6 empty] | 1
Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164
Data Source | [7 empty] | 1 |  | 2 | 5 | 5 | 5 | 3, 4 | 3, 4 | 3, 4 | 5 | 6
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health
[6] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Weighting Factor
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| AHU-1_COOLC DXCOIL | 286.8035 | 269.2847 | 266.6469 | 255.4428 | 219.1736 | 235.9666 | 186.385 | 251.0221 | 218.8229 | 195.2891 | 251.2542 | 214.6713 | 244.1834 | 205.5078 | 215.4211 | 189.5021
| AHU-2_COOLC DXCOIL | 329.2242 | 305.2283 | 314.8425 | 289.849 | 250.3202 | 276.6911 | 210.8402 | 278.7642 | 228.2325 | 219.6227 | 277.6274 | 215.8177 | 264.1392 | 207.5315 | 232.6732 | 202.4202
Heating (kW)
| HEATSYS1 BOILER | 135.6875 | 131.4663 | 127.2951 | 132.1069 | 126.3248 | 121.191 | 121.3352 | 135.6571 | 120.4736 | 126.737 | 145.764 | 128.8369 | 151.4411 | 142.1619 | 151.5431 | 174.2775
HVAC Efficiency
Air Conditioning (COP)
| AHU-1_COOLC DXCOIL | 2.73 | 2.73 | 2.73 | 2.73 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.8 | 2.8
| AHU-2_COOLC DXCOIL | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.8 | 2.73 | 2.73 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8 | 2.73 | 2.8
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
HVAC Control - Economizer
| AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| AHU-1_FAN | 13.29 | 12.15 | 12.84 | 12.22 | 12.38 | 12.6 | 11.26 | 11.65 | 13.22 | 11.61 | 11.77 | 12.97 | 11.73 | 12.41 | 11.56 | 11.45
| AHU-2_FAN | 14.75 | 13.09 | 14.58 | 13.27 | 13.54 | 14.08 | 12.41 | 12.26 | 13.79 | 12.44 | 12.28 | 13.04 | 11.86 | 12.54 | 11.64 | 12.23
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.080165 | 0.10702 | 0.078327 | 0.098916 | 0.12324 | 0.09154 | 0.14444 | 0.069075 | 0.037042 | 0.071677 | 0.096473 | 0.037047 | 0.054354 | 0.071664 | 0.054275 | 0.091169
| Total Cost ($/m2) | 41 | 49.76 | 38.29 | 43.67 | 51.08 | 43.92 | 53.18 | 29.54 | 16.37 | 27.1 | 40.2 | 15.78 | 22.62 | 29.45 | 21.85 | 38.38
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011406 | 0.0081604 | 0.0085862 | 0.010809 | 0.0083903 | 0.0081365 | 0.0083875 | 0.01011 | 0.0072235 | 0.0082712 | 0.0089819 | 0.0072313 | 0.0079826 | 0.0088559 | 0.0079909 | 0.0041922
| Total Cost ($/m2) | 8.98 | 7 | 7.94 | 10.32 | 8.59 | 7.25 | 8.25 | 9.87 | 6.41 | 8.53 | 9.29 | 6.65 | 8.63 | 8.84 | 8.88 | 5.78
Total Utility Costs
| Cost Intensity ($/m2) | 49.98 | 56.77 | 46.23 | 53.98 | 59.67 | 51.17 | 61.43 | 39.41 | 22.78 | 35.64 | 49.49 | 22.42 | 31.25 | 38.29 | 30.73 | 44.16
Energy - End Uses
Electricity (kWh)
| Heating | 13044.4444 | 33286.1111 | 33233.3333 | 51858.3333 | 35038.8889 | 38630.5556 | 45369.4444 | 64322.2222 | 44352.7778 | 75094.4444 | 81652.7778 | 52363.8889 | 89177.7778 | 74480.5556 | 101427.7778 | 162750
| Cooling | 834647.2222 | 648575 | 655994.4444 | 502066.6667 | 449238.8889 | 529458.3333 | 299855.5556 | 417052.7778 | 365055.5556 | 273858.3333 | 336661.1111 | 296691.6667 | 298544.4444 | 238769.4444 | 203872.2222 | 146863.8889
| Interior Lighting | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667
| Exterior Lighting | 74091.6667 | 74063.8889 | 74050 | 74038.8889 | 73983.3333 | 73966.6667 | 74005.5556 | 73961.1111 | 73988.8889 | 73841.6667 | 73972.2222 | 73927.7778 | 73922.2222 | 73905.5556 | 73863.8889 | 73411.1111
| Interior Equipment | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 295391.6667 | 265569.4444 | 285658.3333 | 265500 | 269791.6667 | 278952.7778 | 243766.6667 | 251680.5556 | 288844.4444 | 250872.2222 | 253883.3333 | 281280.5556 | 253455.5556 | 267661.1111 | 250058.3333 | 246744.4444
| Pumps | 5941.6667 | 5750 | 5569.4444 | 5777.7778 | 5530.5556 | 5294.4444 | 5311.1111 | 5905.5556 | 5263.8889 | 5544.4444 | 6341.6667 | 5625 | 6594.4444 | 6183.3333 | 6602.7778 | 7516.6667
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 1600 | 20852.7778 | 84441.6667 | 59205.5556 | 22300 | 177911.1111 | 11355.5556 | 92838.8889 | 182325 | 38494.4444 | 111880.5556 | 189183.3333 | 140775 | 181691.6667 | 175102.7778 | 243411.1111
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1945511.1111 | 1768894.4444 | 1859738.8889 | 1679247.2222 | 1576677.7778 | 1825008.3333 | 1400461.1111 | 1626555.5556 | 1680625 | 1438500 | 1585183.3333 | 1619866.6667 | 1583266.6667 | 1563486.1111 | 1531719.4444 | 1601494.4444
Gas (MJ)
| Heating | 2778310 | 3041030 | 3296200 | 3403580 | 3665620 | 3167940 | 3508990 | 3481260 | 3146490 | 3689280 | 3699140 | 3261640 | 3872850 | 3557370 | 3982480 | 4995550
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 28810 | 34370 | 31140 | 39730 | 38690 | 34980 | 43280 | 43930 | 43120 | 46130 | 47650 | 47460 | 50860 | 51440 | 56140 | 62520
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2995490 | 3263770 | 3515710 | 3631690 | 3892690 | 3391300 | 3740650 | 3713570 | 3377990 | 3923790 | 3935170 | 3497470 | 4112090 | 3797180 | 4226990 | 5246450
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 9999330 | 9631790 | 10210770 | 9676970 | 9568730 | 9961330 | 8782310 | 9569160 | 9428240 | 9102380 | 9641820 | 9329000 | 9811840 | 9425730 | 9741180 | 11011830
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 12.3449 | 31.501 | 31.451 | 49.0772 | 33.1597 | 36.5588 | 42.9363 | 60.8726 | 41.9741 | 71.0671 | 77.2737 | 49.5556 | 84.3952 | 70.4861 | 95.9882 | 154.0217
| Cooling (elec) | 789.8849 | 613.7918 | 620.8133 | 475.1407 | 425.1461 | 501.0634 | 283.7742 | 394.6861 | 345.4775 | 259.1712 | 318.6059 | 280.78 | 282.5334 | 225.9642 | 192.9385 | 138.9875
| Interior Lighting (elec) | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635
| Exterior Lighting (elec) | 70.1181 | 70.0918 | 70.0787 | 70.0682 | 70.0156 | 69.9998 | 70.0366 | 69.9946 | 70.0208 | 69.8815 | 70.0051 | 69.963 | 69.9578 | 69.942 | 69.9026 | 69.4741
| Interior Equipment (elec) | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 279.5497 | 251.3269 | 270.3384 | 251.2612 | 255.3227 | 263.9925 | 230.6934 | 238.1829 | 273.3536 | 237.4179 | 240.2675 | 266.1954 | 239.8627 | 253.3064 | 236.6476 | 233.5115
| Pumps (elec) | 5.623 | 5.4416 | 5.2708 | 5.4679 | 5.234 | 5.0105 | 5.0263 | 5.5888 | 4.9816 | 5.2471 | 6.0016 | 5.3233 | 6.2408 | 5.8517 | 6.2487 | 7.1135
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 1.5142 | 19.7344 | 79.913 | 56.0303 | 21.104 | 168.3697 | 10.7466 | 87.8599 | 172.5469 | 36.43 | 105.8804 | 179.0374 | 133.2252 | 171.9475 | 165.712 | 230.3569
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1841.1729 | 1674.0282 | 1760.0006 | 1589.1888 | 1492.1202 | 1727.1327 | 1325.354 | 1539.323 | 1590.4927 | 1361.3529 | 1500.1696 | 1532.9928 | 1498.3557 | 1479.636 | 1449.573 | 1515.6059
Gas (MJ/m2)
| Heating (gas) | 730.3635 | 799.4274 | 866.5067 | 894.7348 | 963.62 | 832.7896 | 922.445 | 915.1553 | 827.1508 | 969.8397 | 972.4317 | 857.4215 | 1018.0967 | 935.1632 | 1046.9163 | 1313.2326
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 7.5736 | 9.0352 | 8.1861 | 10.4442 | 10.1708 | 9.1956 | 11.3775 | 11.5483 | 11.3354 | 12.1267 | 12.5263 | 12.4763 | 13.3701 | 13.5226 | 14.7581 | 16.4353
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 787.4559 | 857.9814 | 924.2116 | 954.7004 | 1023.3122 | 891.5066 | 983.3439 | 976.2251 | 888.0077 | 1031.4878 | 1034.4794 | 919.4166 | 1080.9882 | 998.2045 | 1111.1932 | 1379.1893
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2628.6287 | 2532.0096 | 2684.2122 | 2543.8866 | 2515.4324 | 2618.6393 | 2308.6979 | 2515.5454 | 2478.5003 | 2392.8381 | 2534.6463 | 2452.4121 | 2579.3413 | 2477.8405 | 2560.7661 | 2894.7952
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 351.7617 | 335.42 | 342.1046 | 306.2954 | 341.6143 | 324.055 | 278.9807 | 319.6956 | 315.6498 | 299.5163 | 348.3721 | 330.6245 | 343.4463 | 351.9208 | 347.2728 | 385.9663
| Feb | 357.4768 | 330.2036 | 361.6186 | 312.582 | 317.9031 | 327.0362 | 287.2511 | 305.9119 | 332.18 | 279.9633 | 292.2291 | 305.5707 | 313.7784 | 333.7046 | 323.8527 | 352.4819
| Mar | 361.0189 | 325.5666 | 395.671 | 332.706 | 334.8761 | 331.8934 | 266.645 | 306.9737 | 343.5946 | 278.3322 | 287.109 | 348.7159 | 304.2495 | 310.5792 | 296.13 | 332.4717
| Apr | 367.7395 | 340.6957 | 388.9422 | 328.4834 | 369.4794 | 350.4356 | 291.4577 | 304.2753 | 379.1471 | 275.5866 | 288.6751 | 328.2817 | 283.1911 | 311.2965 | 285.3638 | 310.1424
| May | 389.8239 | 372.7968 | 416.9051 | 343.8535 | 305.8807 | 413.8993 | 289.3258 | 326.5397 | 373.8388 | 290.5297 | 327.68 | 352.1484 | 323.887 | 321.4923 | 300.2032 | 313.0997
| Jun | 400.9024 | 376.9163 | 497.5041 | 358.578 | 308.9648 | 467.2832 | 292.4751 | 368.3755 | 408.4364 | 298.3723 | 359.8627 | 374.2173 | 350.6225 | 353.1295 | 316.4893 | 317.9088
| Jul | 387.4647 | 379.1577 | 443.8997 | 380.1265 | 314.2392 | 441.8366 | 305.2487 | 372.9904 | 410.1113 | 311.2731 | 363.1668 | 369.1095 | 348.0783 | 354.0181 | 328.7173 | 306.1844
| Aug | 397.4916 | 385.0278 | 442.2988 | 363.4671 | 327.5939 | 407.8575 | 299.7347 | 371.9186 | 355.1227 | 302.7964 | 354.9109 | 368.1173 | 347.8164 | 336.8123 | 322.589 | 296.6809
| Sep | 389.7029 | 373.4634 | 405.6355 | 345.339 | 335.2429 | 407.6558 | 329.5637 | 345.9737 | 364.9469 | 307.8686 | 335.9421 | 375.1284 | 327.9538 | 320.7134 | 305.439 | 276.5238
| Oct | 382.8024 | 355.2212 | 385.2831 | 341.3645 | 348.9459 | 370.3047 | 295.9194 | 324.6748 | 353.0935 | 278.5899 | 316.2812 | 358.2367 | 287.501 | 309.5484 | 283.8634 | 321.0342
| Nov | 365.2649 | 341.2682 | 369.4778 | 300.7525 | 318.454 | 324.6616 | 278.6927 | 308.8059 | 320.4295 | 294.5807 | 315.7257 | 330.665 | 305.359 | 294.12 | 307.9501 | 333.5688
| Dec | 352.5185 | 330.2368 | 351.1293 | 320.8906 | 341.0617 | 334.1632 | 283.3969 | 299.0145 | 310.5269 | 298.8879 | 310.1917 | 325.2075 | 311.6556 | 342.7808 | 314.7393 | 349.55
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-13:00 | 26-JAN-15:00 | 30-JAN-07:10 | 26-JAN-13:00 | 30-JAN-16:00 | 17-JAN-07:10 | 17-JAN-07:10 | 09-JAN-07:10 | 03-JAN-17:00 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-07:10 | 09-JAN-08:09 | 09-JAN-07:10 | 17-JAN-09:09
| Feb | 23-FEB-11:00 | 23-FEB-14:39 | 28-FEB-17:19 | 14-FEB-07:10 | 10-FEB-10:00 | 07-FEB-17:10 | 15-FEB-17:49 | 06-FEB-07:10 | 14-FEB-14:00 | 21-FEB-17:40 | 23-FEB-17:30 | 08-FEB-17:30 | 06-FEB-07:10 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
| Mar | 13-MAR-15:50 | 24-MAR-13:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-12:09 | 17-MAR-15:00 | 13-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 20-MAR-06:10 | 08-MAR-17:00 | 30-MAR-13:00 | 13-MAR-06:10 | 30-MAR-16:19 | 06-MAR-17:00 | 14-MAR-07:10
| Apr | 03-APR-14:09 | 21-APR-14:00 | 26-APR-16:19 | 14-APR-15:00 | 11-APR-16:00 | 21-APR-16:19 | 13-APR-16:10 | 04-APR-15:00 | 21-APR-16:00 | 14-APR-16:00 | 28-APR-16:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-16:00 | 03-APR-08:09 | 03-APR-06:10
| May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-16:19 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-13:00 | 05-MAY-15:00 | 04-MAY-16:00 | 18-MAY-12:00 | 31-MAY-12:09 | 04-MAY-16:00 | 31-MAY-16:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 27-JUN-16:00 | 08-JUN-12:00 | 28-JUN-12:09 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 15-JUN-16:19
| Jul | 13-JUL-14:00 | 12-JUL-14:30 | 19-JUL-16:00 | 03-JUL-15:00 | 10-JUL-14:00 | 24-JUL-16:19 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-16:19 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 13-JUL-15:39 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
| Aug | 21-AUG-14:00 | 31-AUG-13:00 | 01-AUG-16:00 | 17-AUG-13:00 | 08-AUG-12:00 | 18-AUG-14:00 | 15-AUG-12:09 | 17-AUG-15:09 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-14:00 | 15-AUG-16:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-12:00 | 21-SEP-14:39 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:00 | 01-SEP-15:39 | 27-SEP-15:00 | 06-SEP-12:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 25-SEP-06:10
| Oct | 06-OCT-14:20 | 06-OCT-15:00 | 24-OCT-13:00 | 12-OCT-15:00 | 30-OCT-12:00 | 03-OCT-15:00 | 30-OCT-13:20 | 20-OCT-15:39 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-16:49 | 05-OCT-14:00 | 06-OCT-14:00 | 19-OCT-16:00 | 30-OCT-06:10 | 30-OCT-08:09
| Nov | 07-NOV-14:00 | 27-NOV-17:19 | 13-NOV-13:00 | 16-NOV-17:40 | 08-NOV-11:00 | 10-NOV-16:40 | 16-NOV-16:00 | 03-NOV-13:00 | 08-NOV-17:19 | 20-NOV-07:10 | 02-NOV-16:49 | 10-NOV-13:00 | 27-NOV-07:10 | 27-NOV-07:10 | 24-NOV-07:10 | 06-NOV-08:09
| Dec | 15-DEC-17:30 | 19-DEC-17:30 | 06-DEC-17:19 | 18-DEC-07:10 | 18-DEC-11:50 | 05-DEC-16:30 | 29-DEC-16:00 | 11-DEC-07:10 | 18-DEC-07:10 | 11-DEC-07:10 | 26-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 11-DEC-07:10 | 21-DEC-07:10 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 26502.81 | 26692.68 | 25015.63 | 24302.14 | 21818.15 | 27204.28 | 19688.72 | 24994.83 | 23763.51 | 13305.89 | 24533.01 | 23168.23 | 24080.47 | 23711.35 | 23568.16 | 26323.05
| Total Source Energy (MJ/m2) | 6967.08 | 7016.99 | 6576.13 | 6388.56 | 5735.57 | 7151.48 | 5175.78 | 6570.66 | 6246.97 | 3497.86 | 6449.25 | 6090.48 | 6330.29 | 6233.26 | 6195.61 | 6919.82
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 2.14 | 27.93 | 113.08 | 79.29 | 29.86 | 238.26 | 15.21 | 124.33 | 244.17 | 51.55 | 149.83 | 253.35 | 188.52 | 243.32 | 234.5 | 325.98
| Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
| Total Building | 242.62 | 268.4 | 353.56 | 319.77 | 270.34 | 478.74 | 255.69 | 364.81 | 484.65 | 292.03 | 390.31 | 493.83 | 429 | 483.8 | 474.98 | 566.46
Emissions
| Carbon Equivalent (kg) | 587572.6583 | 648888.4922 | 624807.3466 | 582758.5013 | 254455.3546 | 676683.7261 | 231120.0328 | 505900.3267 | 747446.748 | 175528.3064 | 916100.9166 | 724781.5482 | 616092.9568 | 639829.6339 | 600521.255 | 545247.7917
| CO2 (kg) | 1391540 | 1650610 | 1503430 | 1363210 | 694751.1708 | 1634580 | 631848.3841 | 1177800 | 1775680 | 453312.6277 | 2154990 | 1724070 | 1463630 | 1526730 | 1428940 | 1402200
| NOX (kg) | 2320.581 | 2100.4425 | 2397.7566 | 2438.7608 | 605.1158 | 2551.2411 | 550.8725 | 2143.7178 | 2966.4919 | 585.4863 | 3736.8167 | 2870.6739 | 2474.405 | 2538.5309 | 2405.6142 | 1662.4044
| SO2 (kg) | 8328.3673 | 8438.4981 | 7479.3242 | 5895.1263 | 4588.9829 | 10039.9089 | 4076.1733 | 5938.5704 | 7339.8645 | 1112.8961 | 10683.9207 | 7074.5744 | 3737.8636 | 4175.7111 | 3616.2386 | 8153.652
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0383 | 0.0241 | 0.0207 | 0.0219 | 0.0025 | 0.0192 | 0.0022 | 0.0243 | 0.0289 | 0.0048 | 0.0326 | 0.0279 | 0.0277 | 0.0293 | 0.0268 | 0.0281
| Water for Electricity (m3) | 1030.65 | 2878.2 | 55242.4 | 10484.5 | 27682.9 | 50067.2 | 24588.9 | 369.2891 | 7631.39 | 14696.9 | 2459.32 | 7355.49 | 2456.34 | 99037.7 | 2376.37 | 1636.21

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | 12.29 | 71.86 | 3666.11
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 6.41
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_OCC_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
INFIL_SCH | Fraction | Through 12/31 | SummerDesign, WinterDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
RADIOLOGY_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 11.64 | 70.08 | 3654.17
|  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | Sat, WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
HTGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | Sat, WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
AHU-1_MinOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
AHU-1_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 17 | 102 | 5151
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU-2_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HeatSys1 Loop Setpoint Sched | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600