## BuildingSummary
Building Summary Secondary School new construction
|  | Value | Data Source
Program
| Building Name | Secondary School Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 19592 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.28
| Total | 0.34
| Skylight/TDD Percentage | 1.12%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6384
| Net Dimensions - Total Area (m2) | 4088.16
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11902
| Net Dimensions - Total Area (m2) | 11768.6976
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Pless, et al. 2007
| South | 753.18
| East | 291.61
| North | 753.18
| West | 291.2
| Total Area (m2) | 2089.17
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 133.8
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 11902
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 6792
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 39184
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.16087 | See Reference Building Technical Report
HVAC
| System Type | MZ VAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | Air cooled chiller, PACU (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Fan Control | Variable, constant (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 2677.93

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 5.3819 | 4 |  |  |  | 0.5 | 570 |  | 0.047735
LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 13.9931 | 4 |  |  |  | 0.5 | 105 |  | 0.07774
BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6875 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.1503
OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 11.8403 | 10.7639 |  |  | 10 |  | 266 |  | 0.10638
GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.2801 | 1 | 1976 | 15.0695 | 5 |  | 717.2337 | 10 |  | 19760 |  | 0
AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608.0006 | 266.3502 | 3 | 416 | 15.0695 | 5 |  |  | 10 |  | 4160 |  | 0.066279
AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512.0005 | 106.4001 | 1 | 988 | 9.6875 | 5 |  |  | 8 |  | 7904 |  | 0.070501
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6 | 36 | 12.9167 | 222.2745 | 1119.4456 | 503.4582 | 8 |  | 288 | 1887.788 | 0.045349
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200.0002 | 70.0001 | 1.39 | 448.9209 | 15.0695 | 19.2674 |  |  | 10 |  | 4489.2086 |  | 0.087209
MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.1458 | 4 |  |  |  | 0.25 | 85.5 |  | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 20 |  |  | 8 |  | 954 |  | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 20 |  |  | 8 |  | 954 |  | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 5.3819 | 4 |  |  |  | 0.5 | 570 |  | 0.31983
LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 13.9931 | 4 |  |  |  | 0.5 | 105 |  | 0.34983
BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6875 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.42239
OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 11.8403 | 10.7639 |  |  | 10 |  | 266 |  | 0.37847
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236.0002 | 83.0101 | 4.35 | 193.1034 | 13.9931 | 10 |  |  | 8 |  | 1544.8276 |  | 0.34854
MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.1458 | 4 |  |  |  | 0.25 | 85.5 |  | 0.27209
Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 6080.0643
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 10.0524 | 95.5362 | 14.4042 | 118.7841 |  | 51.3966 | 6.8698 | 126.3091 | 3.9685 | 15.2202 | 143.1615 | 27.465 | 26.0558 | 5.3932 | 4.7269 | 0.77492
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | 5.765 | 5.765 | 5.765 | 2.627 | 2.627 | 2.627 | 5.679 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.561
| SHGC | 0.174 | 0.174 | 0.174 | 0.229 | 0.229 | 0.229 | 0.394 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.777 | 0.767
| Visible transmittance | 0.029 | 0.029 | 0.029 | 0.008 | 0.008 | 0.008 | 0.09 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.855 | 0.855
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 1433.9134 | 1438.5933 | 1255.5248 | 1253.2162 | 829.3954 | 950.878 | 999.2912 | 1313.718 | 707.6784 | 725.0307 | 1282.3329 | 677.4345 | 1203.1122 | 584.8858 | 978.5211 | 458.3334
| PSZ-AC_1:5_COOLC DXCOIL | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 360.1228 | 490.6879 | 450.0072 | 431.3644 | 490.6879 | 453.2368 | 490.6879 | 382.7021 | 490.6879 | 327.0982
| PSZ-AC_2:6_COOLC DXCOIL | 119.535 | 125.12 | 131.1385 | 121.2674 | 99.4057 | 115.1091 | 96.1142 | 128.9025 | 108.9913 | 93.3151 | 123.3013 | 103.4424 | 121.2863 | 88.9406 | 135.9543 | 62.0385
| PSZ-AC_3:7_COOLC DXCOIL | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 145.2494 | 196.2751 | 155.4081 | 153.7999 | 196.2751 | 150.1517 | 196.2751 | 130.8393 | 196.2751 | 130.8393
| PSZ-AC_4:8_COOLC DXCOIL | 14.546 | 14.3439 | 13.0542 | 13.7858 | 12.0859 | 11.4227 | 20.0203 | 13.8838 | 12.5022 | 9.8717 | 13.6353 | 12.2806 | 13.7837 | 10.2448 | 13.2188 | 5.4413
| PSZ-AC_5:9_COOLC DXCOIL | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 86.162 | 111.4777 | 102.2356 | 96.8256 | 111.4777 | 102.9694 | 111.4777 | 88.4408 | 111.4777 | 74.3123
Heating (kW)
| HEATSYS1 BOILER | 607.8453 | 779.1028 | 727.7958 | 769.0858 | 528.1856 | 676.9445 | 967.6964 | 874.7364 | 708.0175 | 738.8774 | 957.3471 | 764.9544 | 1007.6678 | 898.62 | 1023.5416 | 1014.542
| PSZ-AC_1:5_HEATC | 765.0269 | 1009.9404 | 852.0818 | 1089.4655 | 795.6607 | 921.1228 | 879.4681 | 1212.7703 | 963.6127 | 1048.8159 | 1416.7661 | 1150.2765 | 1531.1076 | 1395.2101 | 1567.2052 | 1940.738
| PSZ-AC_2:6_HEATC | 169.6012 | 221.1158 | 195.4696 | 231.787 | 156.7562 | 193.5592 | 203.5508 | 263.0206 | 210.6753 | 212.2395 | 296.0842 | 238.077 | 315.7493 | 282.3318 | 334.9677 | 368.0869
| PSZ-AC_3:7_HEATC | 306.0108 | 403.9762 | 340.8327 | 435.7862 | 318.2643 | 368.4491 | 351.7872 | 485.1081 | 385.4451 | 419.5263 | 566.7064 | 460.1106 | 612.443 | 558.084 | 626.8821 | 776.2952
| PSZ-AC_4:8_HEATC | 22.6785 | 29.5229 | 22.6687 | 30.6083 | 19.5976 | 21.4428 | 45.718 | 34.3147 | 26.4474 | 23.6444 | 39.3692 | 30.7322 | 43.0098 | 36.4618 | 42.2194 | 32.2845
| PSZ-AC_5:9_HEATC | 173.8039 | 229.445 | 193.5816 | 247.512 | 180.7635 | 209.2668 | 199.8034 | 275.5253 | 218.92 | 238.277 | 321.8704 | 261.3275 | 347.8472 | 316.9731 | 356.0481 | 440.9098
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| PSZ-AC_1:5_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
| PSZ-AC_2:6_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3
| PSZ-AC_3:7_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| PSZ-AC_4:8_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-AC_5:9_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.75 | 0.78 | 0.75 | 0.78 | 0.75 | 0.75 | 0.78 | 0.78 | 0.75 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_4:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:6_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_3:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_4:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_5:9_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
| PSZ-AC_1:5_FAN | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76
| PSZ-AC_2:6_FAN | 4.81 | 5.04 | 5.28 | 4.88 | 4 | 4.64 | 5.35 | 5.19 | 5.22 | 4.34 | 4.97 | 4.8 | 4.88 | 4.64 | 5.47 | 3.75
| PSZ-AC_3:7_FAN | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
| PSZ-AC_4:8_FAN | 0.59 | 0.58 | 0.53 | 0.56 | 0.49 | 0.46 | 1.03 | 0.56 | 0.54 | 0.45 | 0.55 | 0.53 | 0.56 | 0.52 | 0.53 | 0.33
| PSZ-AC_5:9_FAN | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
| VAV_OTHER_FAN | 13.43 | 13.88 | 14.57 | 13.04 | 11.2 | 12.76 | 16.15 | 13.29 | 13.24 | 11.74 | 12.66 | 12.12 | 12.39 | 11.78 | 12.02 | 10.49
| VAV_POD_1_FAN | 8.56 | 8.87 | 9.67 | 8.24 | 7.26 | 8.53 | 13.74 | 8.62 | 8.73 | 8.55 | 8.31 | 8.11 | 8.17 | 7.97 | 8.25 | 6.25
| VAV_POD_2_FAN | 8.4 | 8.68 | 9.48 | 8.07 | 7.1 | 8.36 | 13.34 | 8.43 | 8.52 | 8.31 | 8.14 | 7.9 | 8 | 7.77 | 8 | 6.21
| VAV_POD_3_FAN | 9.01 | 9.3 | 10.13 | 8.71 | 7.7 | 9.02 | 13.42 | 9.05 | 9.28 | 8.94 | 8.77 | 8.66 | 8.64 | 8.49 | 8.67 | 6.65
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.081268 | 0.11226 | 0.078691 | 0.10076 | 0.060437 | 0.098504 | 0.16639 | 0.080537 | 0.036995 | 0.074524 | 0.083162 | 0.037002 | 0.065486 | 0.079761 | 0.064712 | 0.096882
| Total Cost ($/m2) | 22.34 | 26.11 | 19.26 | 18.35 | 9.14 | 18.94 | 21.87 | 13.53 | 5.42 | 8.87 | 12.66 | 4.88 | 9.46 | 9.64 | 7.9 | 10.71
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011429 | 0.0080806 | 0.0082902 | 0.0097412 | 0.0085464 | 0.0077548 | 0.0085645 | 0.0097024 | 0.006926 | 0.0084062 | 0.0083637 | 0.0069455 | 0.0078692 | 0.0081481 | 0.0078681 | 0.004134
| Total Cost ($/m2) | 0.44 | 1.02 | 0.82 | 2.06 | 0.71 | 1.03 | 1.69 | 3.41 | 1.68 | 2.81 | 3.84 | 2.37 | 4.85 | 4.09 | 5.82 | 4.75
Total Utility Costs
| Cost Intensity ($/m2) | 22.79 | 27.13 | 20.08 | 20.41 | 9.85 | 19.97 | 23.56 | 16.94 | 7.1 | 11.68 | 16.49 | 7.25 | 14.31 | 13.73 | 13.72 | 15.46
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 3335219.4444 | 2531572.2222 | 2746291.6667 | 1566727.7778 | 979636.1111 | 1745805.5556 | 590897.2222 | 1290913.8889 | 854138.8889 | 364144.4444 | 982752.7778 | 588622.2222 | 828616.6667 | 369127.7778 | 374913.8889 | 135544.4444
| Interior Lighting | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333
| Exterior Lighting | 78358.3333 | 78327.7778 | 78313.8889 | 78302.7778 | 78241.6667 | 78225 | 78266.6667 | 78219.4444 | 78247.2222 | 78091.6667 | 78230.5556 | 78186.1111 | 78180.5556 | 78161.1111 | 78116.6667 | 77638.8889
| Interior Equipment | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 339963.8889 | 320611.1111 | 344511.1111 | 303747.2222 | 287508.3333 | 321663.8889 | 291872.2222 | 304355.5556 | 318238.8889 | 277119.4444 | 304933.3333 | 303377.7778 | 307519.4444 | 306183.3333 | 325377.7778 | 339816.6667
| Pumps | 16827.7778 | 12161.1111 | 12336.1111 | 8005.5556 | 5944.4444 | 9088.8889 | 3477.7778 | 6616.6667 | 6158.3333 | 2847.2222 | 5466.6667 | 4705.5556 | 5586.1111 | 4291.6667 | 4844.4444 | 5850
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 43672.2222 | 41769.4444 | 41911.1111 | 40013.8889 | 40047.2222 | 40658.3333 | 38377.7778 | 38847.2222 | 38866.6667 | 37638.8889 | 38041.6667 | 37852.7778 | 37622.2222 | 36991.6667 | 36425 | 35547.2222
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5386258.3333 | 4556655.5556 | 4795577.7778 | 3569008.3333 | 2963591.6667 | 3767652.7778 | 2575102.7778 | 3291161.1111 | 2867863.8889 | 2332055.5556 | 2981636.1111 | 2584958.3333 | 2829736.1111 | 2366966.6667 | 2391886.1111 | 2166605.5556
Gas (MJ)
| Heating | 154840 | 1791180 | 1283790 | 3401220 | 914390 | 1912860 | 3101940 | 6115510 | 3992340 | 5743450 | 8172930 | 5861040 | 11219000 | 8984290 | 13581750 | 21521580
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 253290 | 319760 | 289380 | 378840 | 358800 | 332800 | 408800 | 425840 | 416770 | 442430 | 465820 | 462090 | 501500 | 504770 | 554740 | 617760
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 761520 | 2464340 | 1926570 | 4133440 | 1626580 | 2599050 | 3864140 | 6894750 | 4762500 | 6539270 | 8992150 | 6676530 | 12073890 | 9842450 | 14489880 | 22492740
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 20152040 | 18868300 | 19190650 | 16981880 | 12295510 | 16162600 | 13134510 | 18742930 | 15086820 | 14934670 | 19726040 | 15982370 | 22260940 | 18363530 | 23100670 | 30292520
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 612.8415 | 465.1725 | 504.6269 | 287.8838 | 180.0066 | 320.7891 | 108.5765 | 237.2035 | 156.9467 | 66.911 | 180.5793 | 108.1584 | 152.257 | 67.8267 | 68.8899 | 24.9061
| Interior Lighting (elec) | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286
| Exterior Lighting (elec) | 14.3982 | 14.3926 | 14.3901 | 14.388 | 14.3768 | 14.3737 | 14.3814 | 14.3727 | 14.3778 | 14.3492 | 14.3747 | 14.3666 | 14.3656 | 14.362 | 14.3538 | 14.266
| Interior Equipment (elec) | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 62.4678 | 58.9118 | 63.3034 | 55.8131 | 52.8292 | 59.1052 | 53.6311 | 55.9249 | 58.4759 | 50.9203 | 56.031 | 55.7452 | 56.5062 | 56.2607 | 59.7877 | 62.4408
| Pumps (elec) | 3.0921 | 2.2346 | 2.2667 | 1.471 | 1.0923 | 1.6701 | 0.63904 | 1.2158 | 1.1316 | 0.52317 | 1.0045 | 0.86464 | 1.0264 | 0.78859 | 0.89016 | 1.0749
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 8.0247 | 7.6751 | 7.7011 | 7.3525 | 7.3586 | 7.4709 | 7.0519 | 7.1381 | 7.1417 | 6.9161 | 6.9901 | 6.9554 | 6.913 | 6.7972 | 6.693 | 6.5317
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 989.7167 | 837.2785 | 881.1801 | 655.7998 | 544.5554 | 692.3004 | 473.1712 | 604.7458 | 526.9656 | 428.5116 | 547.8711 | 474.9821 | 519.9597 | 434.9265 | 439.5054 | 398.1105
Gas (MJ/m2)
| Heating (gas) | 7.9032 | 91.4241 | 65.5262 | 173.6025 | 46.6716 | 97.6347 | 158.3269 | 312.1432 | 203.774 | 293.1528 | 417.1565 | 299.1548 | 572.6317 | 458.5693 | 693.2294 | 1098.4882
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 12.9282 | 16.3209 | 14.7703 | 19.3365 | 18.3136 | 16.9865 | 20.8657 | 21.7354 | 21.2725 | 22.5822 | 23.776 | 23.5856 | 25.5972 | 25.7641 | 28.3146 | 31.5312
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 38.8689 | 125.783 | 98.3345 | 210.9759 | 83.0227 | 132.6587 | 197.2305 | 351.9166 | 243.0839 | 333.7725 | 458.9705 | 340.7784 | 616.2663 | 502.3709 | 739.5815 | 1148.0574
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1028.5851 | 963.0615 | 979.5146 | 866.7762 | 627.5781 | 824.9592 | 670.4017 | 956.6624 | 770.05 | 762.2841 | 1006.8416 | 815.76 | 1136.226 | 937.2974 | 1179.0869 | 1546.1678
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1196.6515 | 1190.8535 | 1098.6752 | 880.1278 | 913.5609 | 867.9179 | 652.7774 | 595.1012 | 690.4612 | 450.2359 | 452.9999 | 745.4716 | 454.9307 | 464.9267 | 456.4077 | 471.2785
| Feb | 1217.9073 | 1260.8113 | 1146.7287 | 828.0171 | 894.4 | 908.8317 | 918.5783 | 606.0902 | 792.534 | 675.0251 | 452.8105 | 625.1294 | 452.8091 | 694.3327 | 455.9076 | 463.0906
| Mar | 1262.6745 | 1210.7664 | 1240.5408 | 1101.741 | 885.9792 | 967.5682 | 857.365 | 1144.5196 | 794.5117 | 784.2963 | 1062.4393 | 808.1113 | 698.1228 | 734.2483 | 453.3099 | 462.7844
| Apr | 1259.5127 | 1264.9213 | 1264.7352 | 1163.7761 | 959.5068 | 1093.4868 | 927.9895 | 1139.8418 | 890.9621 | 754.6744 | 1060.3708 | 830.2067 | 1040.99 | 722.2949 | 747.8667 | 449.599
| May | 1296.5882 | 1308.972 | 1327.2771 | 1187.9909 | 882.4387 | 1158.2597 | 957.0466 | 1170.8406 | 951.2474 | 841.1231 | 1205.758 | 902.1131 | 1143.5878 | 790.2447 | 964.8803 | 656.5695
| Jun | 1320.5413 | 1327.0683 | 1424.9517 | 1241.0952 | 890.4714 | 1237.6354 | 977.2861 | 1283.9562 | 998.278 | 857.7249 | 1243.5191 | 970.9076 | 1215.823 | 921.3838 | 1050.3369 | 731.1299
| Jul | 1143.0705 | 1186.0901 | 1258.8639 | 1091.2982 | 739.3374 | 1064.8193 | 865.3489 | 1106.8018 | 838.1785 | 726.295 | 1091.3565 | 812.8598 | 1007.9144 | 726.4821 | 888.9637 | 545.8645
| Aug | 1139.1765 | 1183.6636 | 1282.707 | 1048.888 | 787.2828 | 1057.9464 | 852.194 | 1114.3515 | 813.7445 | 698.3858 | 1044.9299 | 809.5195 | 982.3837 | 685.4296 | 850.1812 | 541.397
| Sep | 1292.5365 | 1304.774 | 1357.0134 | 1194.4498 | 990.6357 | 1157.6406 | 1060.1692 | 1272.6614 | 927.2149 | 879.0487 | 1237.3536 | 931.8963 | 1132.8918 | 814.1025 | 966.4662 | 607.2361
| Oct | 1265.2693 | 1303.9644 | 1264.1846 | 1224.4137 | 965.1734 | 1093.9881 | 955.7376 | 1206.7839 | 871.607 | 792.9984 | 1127.4275 | 883.7914 | 1050.2676 | 756.2462 | 870.8227 | 459.8995
| Nov | 1234.9421 | 1220.2158 | 1199.9593 | 1043.1432 | 913.9091 | 920.6435 | 853.3197 | 1086.2077 | 774.4953 | 634.9045 | 1088.8522 | 765.2465 | 909.772 | 529.2884 | 465.294 | 465.8995
| Dec | 1218.8637 | 1201.9119 | 1090.0416 | 881.4813 | 920.5901 | 900.648 | 671.5494 | 453.8095 | 621.5799 | 450.244 | 451.6682 | 568.9522 | 452.0821 | 463.8941 | 453.7355 | 470.8295
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 02-JAN-16:19 | 26-JAN-16:10 | 23-JAN-15:00 | 26-JAN-12:00 | 18-JAN-14:00 | 17-JAN-14:00 | 09-JAN-11:00 | 26-JAN-15:00 | 27-JAN-11:39 | 27-JAN-11:09 | 27-JAN-12:00 | 05-JAN-11:09 | 05-JAN-08:09 | 09-JAN-11:09 | 02-JAN-11:09
| Feb | 22-FEB-16:10 | 23-FEB-16:10 | 28-FEB-16:00 | 17-FEB-14:00 | 13-FEB-11:00 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-15:00 | 14-FEB-16:10 | 21-FEB-13:00 | 17-FEB-11:39 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-08:20
| Mar | 13-MAR-15:00 | 27-MAR-15:09 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-10:50 | 31-MAR-15:00 | 20-MAR-14:00 | 09-MAR-16:10 | 02-MAR-16:10 | 29-MAR-15:00 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-14:00 | 30-MAR-15:00 | 01-MAR-11:39 | 14-MAR-07:19
| Apr | 03-APR-15:20 | 28-APR-15:30 | 26-APR-15:39 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 13-APR-15:09 | 04-APR-15:00 | 21-APR-15:00 | 18-APR-13:00 | 07-APR-14:39 | 25-APR-15:09 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 26-APR-10:39
| May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:00 | 12-MAY-15:00 | 30-MAY-09:09 | 31-MAY-15:00 | 09-MAY-11:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 04-MAY-15:00 | 23-MAY-15:00 | 15-MAY-15:20 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:20
| Jun | 09-JUN-15:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-15:30 | 30-JUN-15:20 | 27-JUN-15:00 | 16-JUN-10:39 | 23-JUN-15:00 | 29-JUN-13:00 | 28-JUN-15:20 | 06-JUN-15:00 | 28-JUN-11:00 | 30-JUN-15:20 | 30-JUN-15:20 | 14-JUN-15:39 | 20-JUN-15:00
| Jul | 05-JUL-11:00 | 31-JUL-13:00 | 19-JUL-17:19 | 03-JUL-14:00 | 10-JUL-14:00 | 25-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 18-JUL-13:00 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-14:00 | 21-JUL-15:00
| Aug | 21-AUG-12:00 | 31-AUG-13:00 | 01-AUG-17:10 | 17-AUG-14:00 | 08-AUG-09:00 | 04-AUG-14:00 | 15-AUG-11:00 | 04-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 03-AUG-13:00 | 30-AUG-13:00 | 25-AUG-13:00 | 09-AUG-15:00 | 11-AUG-13:00 | 15-AUG-13:00
| Sep | 26-SEP-11:00 | 19-SEP-15:09 | 25-SEP-13:00 | 14-SEP-15:00 | 25-SEP-11:00 | 20-SEP-15:00 | 28-SEP-15:09 | 08-SEP-15:20 | 20-SEP-15:20 | 13-SEP-15:00 | 27-SEP-15:00 | 06-SEP-15:00 | 14-SEP-15:09 | 07-SEP-15:00 | 07-SEP-15:09 | 07-SEP-14:00
| Oct | 10-OCT-15:39 | 06-OCT-15:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:00 | 16-OCT-15:00 | 20-OCT-15:00 | 11-OCT-15:00 | 17-OCT-15:00 | 04-OCT-15:20 | 05-OCT-15:20 | 06-OCT-15:09 | 06-OCT-15:00 | 06-OCT-14:00 | 31-OCT-07:10
| Nov | 01-NOV-15:00 | 03-NOV-15:20 | 13-NOV-16:00 | 22-NOV-16:10 | 20-NOV-12:00 | 10-NOV-16:40 | 16-NOV-15:00 | 03-NOV-11:00 | 08-NOV-16:10 | 03-NOV-13:00 | 02-NOV-15:20 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-12:00 | 09-NOV-12:00 | 27-NOV-10:09
| Dec | 13-DEC-16:10 | 19-DEC-16:10 | 11-DEC-16:19 | 26-DEC-14:00 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 06-DEC-11:39 | 08-DEC-14:00 | 28-DEC-11:39 | 12-DEC-11:39 | 21-DEC-14:30 | 20-DEC-11:09 | 18-DEC-08:09 | 20-DEC-11:09 | 29-DEC-11:09
Source Energy
| Total Source Energy (GJ) | 65149.95 | 62270.23 | 56710.1 | 47735.85 | 34796.55 | 51354.99 | 32911.43 | 49898.17 | 39456.72 | 21765.66 | 47881.81 | 38167.57 | 48197.57 | 40367.24 | 45418.24 | 52422.9
| Total Source Energy (MJ/m2) | 3325.33 | 3178.35 | 2894.55 | 2436.5 | 1776.06 | 2621.22 | 1679.84 | 2546.86 | 2013.92 | 1110.95 | 2443.95 | 1948.12 | 2460.06 | 2060.39 | 2318.2 | 2675.73
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
| Total Building | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
Emissions
| Carbon Equivalent (kg) | 1490910 | 1564360 | 1482410 | 1173920 | 375674.0988 | 1317600 | 370622.3622 | 1012470 | 1257400 | 287773.8826 | 1751810 | 1176350 | 1186320 | 1042460 | 1080020 | 1015260
| CO2 (kg) | 3460160 | 3942310 | 3504850 | 2710520 | 1009420 | 3145160 | 1004780 | 2350900 | 2977870 | 744178.674 | 4136260 | 2808310 | 2862050 | 2524620 | 2642410 | 2699070
| NOX (kg) | 6068.4122 | 5129.6127 | 5845.2449 | 5013.6742 | 868.2516 | 5058.7117 | 870.3571 | 4308.2959 | 5014.7154 | 957.6 | 7103.9563 | 4632.7827 | 4645.9134 | 4036.7336 | 4129.6884 | 2977.1935
| SO2 (kg) | 23055.5389 | 21735.9046 | 19284.495 | 12528.33 | 8624.1282 | 20725.8039 | 7494.276 | 12015.9056 | 12524.6685 | 1804.2446 | 20096.2561 | 11289.7834 | 6681.863 | 6322.7249 | 5649.119 | 11034.9228
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1051 | 0.0613 | 0.0525 | 0.0461 | 0.004 | 0.0391 | 0.0038 | 0.0491 | 0.0493 | 0.0077 | 0.0615 | 0.0447 | 0.05 | 0.0449 | 0.0428 | 0.0398
| Water for Electricity (m3) | 2853.41 | 7414.21 | 142450 | 22283.5 | 52034 | 103362 | 45213 | 747.2175 | 13022.4 | 23826.1 | 4625.83 | 11737.8 | 4390.16 | 149934 | 3710.87 | 2213.58

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 586.61
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69 | 3348.11
|  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 41.25
|  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69
|  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87 | 3466.2
|  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 40.64
|  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87
|  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_OCC_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1457.54
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.95 | 19.75 | 944.32
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.95 | 19.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13 | 628.36
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 7.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5 | 2255.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2176.29
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 22.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25 | 784.83
|  |  | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82 | 14.1
|  |  | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25
|  |  | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 7.2 | 389.41
|  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.19 | 6.91
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLGSETP_SCH | Temperature | Through 6/30 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296 | 67577.14
|  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
|  | Through 9/1 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
|  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | 615
|  | Through 12/31 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
|  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
CLGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | SummerDesign | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603 | 0 | 0
|  |  | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
HTGSETP_SCH | Temperature | Through 6/30 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768 | 40045.71
|  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
|  | Through 9/1 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
|  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 439
|  | Through 12/31 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
|  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
HTGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | WinterDesign | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459 | 0 | 0
|  |  | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
Showers_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8 | 1848.37
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SHW_default Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
SHW_Kitchen Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600