## BuildingSummary
Building Summary Strip Mall post-1980 construction
|  | Value | Data Source
Program
| Building Name | Strip Mall Reference Building post-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Strip Mall
Form
| Total Floor Area (m2) | 2090 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 4
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 10 stores
| Floor to Ceiling Height (m) | 5.1816
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1184.13
| Net Dimensions - Total Area (m2) | 1059.67
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2090
| Net Dimensions - Total Area (m2) | 2090
| Roof to Skin Ratio | 0.64
Window
| Dimensions - Total Area (m2) | South: 124 East: 0.00 North: 0.00 West: 0.00 Total: 124
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2090
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.23 | See Reference Building Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
LGStore1 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 276.3003 | 20.75 | 6.1939 | 56.2472 | 60.2778 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.4124
SMStore1 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 60.2778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore2 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore3 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore4 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
LGStore2 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 157.8901 | 20.75 | 6.1939 | 56.2472 | 29.0625 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.1446
SMStore5 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore6 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore7 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore8 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 197.3602 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.6801
Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 337.4831
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Weighting Factor
Fabric
Exterior walls
| Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 38.5949 | 26.1373 | 28.4239 | 25.9957 | 20.5005 | 21.7242 | 13.0774 | 27.6097 | 19.9367 | 16.2551 | 37.2093 | 27.5345 | 41.9609 | 31.0378 | 44.8493 | 39.3675
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 83.331 | 67.4229 | 64.3683 | 62.6198 | 51.2514 | 53.0879 | 35.3736 | 58.1394 | 41.5959 | 37.6208 | 60.9154 | 40.367 | 57.7318 | 50.0428 | 67.2752 | 66.2267
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 33.4639 | 31.6905 | 24.5271 | 30.1801 | 24.5021 | 24.4298 | 17.6378 | 24.6248 | 20.0359 | 18.9239 | 24.129 | 18.7732 | 24.4355 | 20.3744 | 20.5222 | 27.0733
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 27.2467 | 24.9474 | 24.5818 | 25.21 | 20.4342 | 20.1425 | 13.8131 | 22.1868 | 15.713 | 15.0183 | 25.0788 | 17.7372 | 25.6148 | 20.4762 | 30.1405 | 27.0236
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 26.6372 | 24.3143 | 23.9202 | 24.556 | 20.0427 | 19.7057 | 13.4259 | 21.5473 | 15.2497 | 14.619 | 25.0752 | 17.9067 | 26.1693 | 20.5099 | 30.5258 | 27.0216
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 26.5415 | 24.2036 | 23.7908 | 24.4409 | 19.9747 | 19.6143 | 13.344 | 21.4291 | 15.161 | 14.5365 | 25.089 | 17.9582 | 26.3747 | 20.5537 | 30.5455 | 27.0326
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 47.4863 | 43.0097 | 42.3259 | 43.3126 | 35.7678 | 35.9847 | 23.2167 | 37.6622 | 27.0658 | 25.6109 | 49.8874 | 36.9904 | 56.6841 | 42.0728 | 60.7862 | 53.8402
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 24.755 | 22.371 | 21.9492 | 22.5502 | 18.8262 | 18.3955 | 12.2484 | 19.6155 | 13.9798 | 13.4159 | 25.0894 | 18.4927 | 28.4896 | 20.9848 | 30.5458 | 27.0328
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 24.6631 | 22.2699 | 21.8638 | 22.4457 | 18.7597 | 18.3377 | 12.1917 | 19.5162 | 13.9192 | 13.3571 | 25.0817 | 18.5144 | 28.4812 | 21.0004 | 30.5367 | 27.0252
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 24.9836 | 22.3834 | 22.1076 | 22.5504 | 18.8141 | 18.4302 | 12.2151 | 19.5865 | 13.9472 | 13.3946 | 25.1884 | 18.5985 | 28.5797 | 21.0763 | 30.633 | 27.0864
Heating (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 15.9982 | 26.3699 | 20.726 | 31.4867 | 16.8678 | 24.6744 | 19.8979 | 35.6436 | 28.795 | 27.7433 | 46.7607 | 38.0306 | 52.3582 | 49.4862 | 54.722 | 73.9084
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 26.0055 | 45.8321 | 35.4647 | 54.9918 | 28.9946 | 42.8275 | 34.716 | 62.6765 | 50.4473 | 48.7378 | 82.3214 | 66.8201 | 92.3812 | 87.1698 | 96.625 | 130.6716
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6647 | 14.9645 | 23.7484 | 12.3331 | 18.4002 | 15.0157 | 27.2555 | 21.9023 | 21.1977 | 35.8239 | 29.0568 | 40.2824 | 37.9746 | 42.1633 | 57.0552
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6 | 14.8913 | 23.6794 | 12.2765 | 18.3325 | 14.9683 | 27.1962 | 21.8407 | 21.1475 | 35.7537 | 28.9893 | 40.2157 | 37.9015 | 42.098 | 56.9873
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.5966 | 14.8874 | 23.676 | 12.2735 | 18.3291 | 14.9659 | 27.1933 | 21.8378 | 21.145 | 35.7504 | 28.9862 | 40.2127 | 37.8982 | 42.0951 | 56.9845
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6047 | 14.8963 | 23.6865 | 12.2812 | 18.3396 | 14.9738 | 27.2035 | 21.8492 | 21.1537 | 35.7629 | 28.9988 | 40.2254 | 37.9126 | 42.108 | 56.9996
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 39.023 | 29.583 | 47.1394 | 24.3739 | 36.4396 | 29.7617 | 54.1857 | 43.4504 | 42.1103 | 71.2637 | 57.7323 | 80.1876 | 75.5307 | 83.9496 | 113.6946
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6051 | 14.8967 | 23.6869 | 12.2815 | 18.34 | 14.9741 | 27.2038 | 21.8495 | 21.154 | 35.7632 | 28.9991 | 40.2257 | 37.9129 | 42.1083 | 56.9999
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6029 | 14.8947 | 23.6822 | 12.279 | 18.3353 | 14.9703 | 27.1985 | 21.8431 | 21.1495 | 35.7563 | 28.9918 | 40.2181 | 37.904 | 42.1003 | 56.9894
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.701 | 15.0085 | 23.7834 | 12.3658 | 18.4349 | 15.0391 | 27.2816 | 21.9288 | 21.2197 | 35.8529 | 29.0844 | 40.3067 | 38.0019 | 42.1851 | 57.0731
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.3
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
Heating Efficiency (%)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 1.64 | 1.05 | 1.23 | 1.05 | 1.01 | 1.01 | 0.74 | 1.11 | 1.1 | 0.87 | 1.5 | 1.46 | 1.69 | 1.81 | 1.81 | 2.38
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 3.77 | 2.78 | 2.97 | 2.76 | 2.75 | 2.7 | 2.14 | 2.41 | 2.51 | 2.16 | 2.5 | 2.43 | 2.83 | 3.02 | 3.03 | 4
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 1.37 | 1.28 | 1.21 | 1.29 | 1.29 | 1.21 | 1.05 | 1.19 | 1.21 | 1.07 | 1.19 | 1.12 | 1.22 | 1.23 | 1.23 | 1.64
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 1.1 | 1 | 0.99 | 1.02 | 1.02 | 0.92 | 0.79 | 0.89 | 0.9 | 0.81 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 1.07 | 0.98 | 0.96 | 0.99 | 0.99 | 0.9 | 0.76 | 0.87 | 0.87 | 0.78 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 1.07 | 0.97 | 0.96 | 0.98 | 0.99 | 0.89 | 0.76 | 0.86 | 0.86 | 0.78 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.91 | 1.73 | 1.7 | 1.74 | 1.74 | 1.57 | 1.31 | 1.52 | 1.48 | 1.35 | 2.01 | 1.95 | 2.28 | 2.44 | 2.45 | 3.25
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 1 | 0.9 | 0.88 | 0.91 | 0.91 | 0.81 | 0.69 | 0.79 | 0.77 | 0.71 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 0.99 | 0.9 | 0.88 | 0.9 | 0.91 | 0.81 | 0.68 | 0.79 | 0.77 | 0.7 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 1.01 | 0.9 | 0.89 | 0.91 | 0.91 | 0.81 | 0.68 | 0.79 | 0.77 | 0.7 | 1.01 | 0.99 | 1.15 | 1.23 | 1.23 | 1.64
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.085981 | 0.11851 | 0.098066 | 0.10031 | 0.1292 | 0.098601 | 0.14743 | 0.075138 | 0.037315 | 0.074674 | 0.092801 | 0.037317 | 0.05981 | 0.074528 | 0.058619 | 0.094569
| Total Cost ($/m2) | 28.03 | 32.89 | 27.75 | 25.53 | 30.6 | 25.64 | 32.3 | 18.17 | 8.89 | 16.47 | 22.49 | 8.83 | 14.64 | 17.94 | 14.04 | 24.64
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011402 | 0.0080428 | 0.0081367 | 0.0095074 | 0.0086118 | 0.0076272 | 0.0085626 | 0.0096568 | 0.0068692 | 0.0084142 | 0.0083001 | 0.0069032 | 0.0078719 | 0.0080778 | 0.0078601 | 0.0041214
| Total Cost ($/m2) | 0.11 | 1.17 | 0.93 | 2.91 | 0.83 | 1.49 | 2.24 | 5.19 | 2.61 | 4.08 | 6.24 | 3.77 | 7.7 | 6.49 | 9.52 | 8.13
Total Utility Costs
| Cost Intensity ($/m2) | 28.15 | 34.06 | 28.69 | 28.44 | 31.43 | 27.13 | 34.53 | 23.36 | 11.5 | 20.55 | 28.73 | 12.59 | 22.34 | 24.43 | 23.56 | 32.77
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 184266.6667 | 112600 | 123238.8889 | 63738.8889 | 28077.7778 | 81047.2222 | 7322.2222 | 44291.6667 | 36855.5556 | 8022.2222 | 32791.6667 | 23272.2222 | 26791.6667 | 13386.1111 | 8827.7778 | 3738.8889
| Interior Lighting | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500
| Exterior Lighting | 59002.7778 | 58980.5556 | 58969.4444 | 58961.1111 | 58916.6667 | 58902.7778 | 58933.3333 | 58897.2222 | 58922.2222 | 58802.7778 | 58908.3333 | 58875 | 58869.4444 | 58855.5556 | 58822.2222 | 58461.1111
| Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 104269.4444 | 74538.8889 | 75419.4444 | 75336.1111 | 74141.6667 | 69622.2222 | 57683.3333 | 68222.2222 | 68258.3333 | 60238.8889 | 80966.6667 | 78391.6667 | 91861.1111 | 96991.6667 | 98916.6667 | 148550
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 681519.4444 | 580097.2222 | 591605.5556 | 532016.6667 | 495111.1111 | 543550 | 457919.4444 | 505391.6667 | 498011.1111 | 461044.4444 | 506641.6667 | 494516.6667 | 511497.2222 | 503211.1111 | 500541.6667 | 544727.7778
Gas (MJ)
| Heating | 20930 | 304360 | 239280 | 640080 | 202040 | 408880 | 546110 | 1123780 | 794360 | 1013040 | 1571380 | 1140500 | 2045500 | 1679390 | 2531880 | 4123460
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 20930 | 304360 | 239280 | 640080 | 202040 | 408880 | 546110 | 1123780 | 794360 | 1013040 | 1571380 | 1140500 | 2045500 | 1679390 | 2531880 | 4123460
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2474400 | 2392710 | 2369070 | 2555330 | 1984440 | 2365670 | 2194610 | 2943190 | 2587200 | 2672800 | 3395290 | 2920760 | 3886900 | 3490950 | 4333830 | 6084480
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 317.3485 | 193.9225 | 212.245 | 109.7727 | 48.3562 | 139.5815 | 12.6105 | 76.2802 | 63.4735 | 13.8161 | 56.4746 | 40.08 | 46.1413 | 23.0539 | 15.2034 | 6.4392
| Interior Lighting (elec) | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506
| Exterior Lighting (elec) | 101.616 | 101.5777 | 101.5586 | 101.5443 | 101.4677 | 101.4438 | 101.4964 | 101.4342 | 101.4773 | 101.2716 | 101.4534 | 101.396 | 101.3864 | 101.3625 | 101.3051 | 100.6831
| Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 179.5754 | 128.3727 | 129.8892 | 129.7457 | 127.6886 | 119.9051 | 99.3436 | 117.494 | 117.5562 | 103.7449 | 139.4428 | 135.008 | 158.2054 | 167.0414 | 170.3567 | 255.8364
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1173.7294 | 999.0576 | 1018.8775 | 916.2521 | 852.6924 | 936.115 | 788.64 | 870.3978 | 857.6869 | 794.022 | 872.5506 | 851.6686 | 880.913 | 866.6424 | 862.045 | 938.1434
Gas (MJ/m2)
| Heating (gas) | 10.0128 | 145.6045 | 114.4705 | 306.2115 | 96.6551 | 195.6064 | 261.2566 | 537.6115 | 380.0184 | 484.6339 | 751.7414 | 545.6102 | 978.5583 | 803.4129 | 1211.2404 | 1972.6453
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10.0128 | 145.6045 | 114.4705 | 306.2115 | 96.6551 | 195.6064 | 261.2566 | 537.6115 | 380.0184 | 484.6339 | 751.7414 | 545.6102 | 978.5583 | 803.4129 | 1211.2404 | 1972.6453
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1183.7422 | 1144.6621 | 1133.3528 | 1222.4588 | 949.3475 | 1131.7262 | 1049.8919 | 1408.0093 | 1237.7052 | 1278.6559 | 1624.292 | 1397.2789 | 1859.4761 | 1670.0553 | 2073.2854 | 2910.7888
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 151.875 | 129.6433 | 121.1975 | 111.1091 | 123.7558 | 107.8488 | 104.8852 | 106.5513 | 106.5815 | 105.2225 | 108.7885 | 108.6378 | 110.6292 | 111.7051 | 111.7336 | 120.1262
| Feb | 161.2532 | 129.7635 | 121.0756 | 108.5374 | 119.2404 | 110.8051 | 110.3555 | 106.5513 | 109.3355 | 105.2953 | 108.7885 | 108.3765 | 110.6292 | 111.7051 | 111.7336 | 120.1262
| Mar | 161.6141 | 132.9997 | 139.9083 | 116.1252 | 118.8241 | 110.743 | 104.8361 | 111.2814 | 109.1137 | 105.2225 | 108.7885 | 108.3591 | 110.6292 | 100.5033 | 111.7336 | 120.1262
| Apr | 169.3764 | 152.0499 | 143.9271 | 133.3819 | 127.737 | 134.6792 | 108.3888 | 111.8665 | 119.6036 | 101.6254 | 105.2512 | 111.8467 | 108.6757 | 98.4163 | 98.8319 | 106.6272
| May | 182.0987 | 164.593 | 167.7781 | 144.35 | 121.0839 | 148.9759 | 110.3379 | 128.3161 | 127.5458 | 108.2104 | 131.5707 | 120.7716 | 156.6421 | 115.9307 | 112.1106 | 112.0684
| Jun | 189.5886 | 167.0954 | 195.8494 | 158.254 | 123.8345 | 177.9383 | 111.8133 | 159.4259 | 140.9244 | 113.4891 | 157.7059 | 133.3694 | 154.2701 | 142.5481 | 131.223 | 129.1781
| Jul | 182.0984 | 173.0166 | 192.2219 | 173.7236 | 130.7825 | 174.1913 | 121.5404 | 166.2414 | 146.3072 | 124.7929 | 161.1805 | 141.5792 | 161.3828 | 143.5059 | 145.9516 | 136.4676
| Aug | 191.781 | 172.8423 | 192.0455 | 162.5702 | 141.4515 | 167.739 | 116.6136 | 166.1445 | 142.926 | 120.0471 | 157.5578 | 142.9763 | 152.4149 | 137.9098 | 144.915 | 128.8724
| Sep | 182.1956 | 169.2129 | 177.8835 | 150.465 | 142.113 | 164.3095 | 135.2407 | 141.9637 | 128.9196 | 139.5998 | 136.2839 | 132.4375 | 132.7477 | 128.3562 | 121.5762 | 107.3007
| Oct | 178.5807 | 150.7902 | 146.1754 | 140.1981 | 132.4643 | 136.9624 | 109.6829 | 125.1131 | 116.1917 | 105.2225 | 124.0134 | 119.8442 | 119.1833 | 111.2794 | 117.3894 | 120.1262
| Nov | 164.0877 | 139.1921 | 135.8803 | 114.6112 | 125.7293 | 115.5319 | 105.3253 | 119.5133 | 109.1439 | 105.6915 | 121.8748 | 109.9764 | 110.869 | 111.7051 | 111.7336 | 120.1262
| Dec | 153.6085 | 136.1412 | 119.2566 | 109.7288 | 126.4283 | 112.442 | 104.8361 | 106.5513 | 106.5815 | 105.2225 | 108.7885 | 108.3591 | 110.6292 | 111.7051 | 111.7336 | 120.1262
Time of Peak Electrical Demand
| Jan | 24-JAN-13:00 | 20-JAN-17:49 | 28-JAN-17:00 | 23-JAN-17:00 | 26-JAN-13:00 | 18-JAN-16:49 | 06-JAN-17:10 | 02-JAN-16:49 | 02-JAN-17:10 | 02-JAN-16:30 | 02-JAN-16:30 | 27-JAN-17:10 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 25-FEB-13:39 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-15:00 | 13-FEB-11:00 | 08-FEB-17:10 | 15-FEB-17:49 | 01-FEB-17:30 | 14-FEB-17:49 | 21-FEB-17:40 | 01-FEB-16:00 | 11-FEB-17:30 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 01-FEB-09:09
| Mar | 13-MAR-15:39 | 25-MAR-12:30 | 17-MAR-14:00 | 28-MAR-15:00 | 31-MAR-14:09 | 31-MAR-15:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-17:00 | 01-MAR-17:49 | 01-MAR-17:40 | 01-MAR-17:49 | 01-MAR-17:00 | 30-MAR-16:00 | 01-MAR-17:49 | 01-MAR-17:00
| Apr | 01-APR-15:09 | 29-APR-14:20 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 06-APR-16:00 | 04-APR-14:00 | 01-APR-09:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:00 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 30-MAY-16:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-15:00 | 29-JUN-14:09 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-14:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-15:00
| Aug | 21-AUG-14:30 | 31-AUG-14:09 | 01-AUG-16:00 | 17-AUG-14:39 | 08-AUG-12:00 | 05-AUG-12:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-14:39
| Sep | 11-SEP-14:00 | 16-SEP-14:50 | 09-SEP-14:00 | 11-SEP-13:00 | 23-SEP-13:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 02-SEP-14:00 | 02-SEP-15:00 | 27-SEP-15:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 02-SEP-15:00
| Oct | 06-OCT-14:20 | 06-OCT-15:00 | 24-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-15:00 | 13-OCT-14:00 | 26-OCT-16:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 23-OCT-08:09
| Nov | 07-NOV-14:39 | 27-NOV-17:19 | 13-NOV-17:30 | 22-NOV-17:30 | 20-NOV-12:00 | 10-NOV-16:40 | 13-NOV-16:00 | 04-NOV-16:00 | 08-NOV-17:10 | 04-NOV-16:49 | 02-NOV-16:49 | 04-NOV-16:00 | 02-NOV-16:00 | 06-NOV-17:10 | 01-NOV-16:49 | 01-NOV-08:09
| Dec | 16-DEC-12:00 | 02-DEC-17:19 | 09-DEC-17:19 | 01-DEC-17:30 | 19-DEC-12:00 | 05-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 8161.02 | 7917.26 | 6997.8 | 7141.89 | 5737.17 | 7445.92 | 5698.48 | 7733.38 | 6816.09 | 3997.54 | 8183.54 | 7152.32 | 8562.56 | 8130.87 | 8958.13 | 11507.59
| Total Source Energy (MJ/m2) | 3904.2 | 3787.58 | 3347.72 | 3416.65 | 2744.64 | 3562.1 | 2726.13 | 3699.62 | 3260.79 | 1912.41 | 3914.97 | 3421.64 | 4096.3 | 3889.78 | 4285.53 | 5505.19
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 187284.03 | 198986.428 | 182906.4895 | 175422.6782 | 61505.0376 | 190699.4509 | 63362.8629 | 156647.4652 | 217761.2384 | 51847.6277 | 298452.121 | 222575.0163 | 211968.26 | 214175.989 | 216988.961 | 227636.9247
| CO2 (kg) | 433882.727 | 501399.0654 | 432460.1189 | 405290.8404 | 165007.2914 | 455513.1098 | 171328.3874 | 364391.726 | 515413.5469 | 132547.506 | 705099.5097 | 530119.9969 | 510204.2958 | 515205.1648 | 526899.2978 | 598800.6535
| NOX (kg) | 764.2649 | 652.5967 | 721.1753 | 748.4969 | 141.7574 | 731.4137 | 148.1007 | 664.6582 | 869.2727 | 176.0834 | 1209.1641 | 879.8067 | 833.3099 | 838.6592 | 840.5396 | 676.0787
| SO2 (kg) | 2917.1833 | 2767.1486 | 2379.0337 | 1867.5471 | 1440.7714 | 2990.0747 | 1332.6361 | 1845.1816 | 2174.931 | 356.6213 | 3414.7838 | 2159.7562 | 1207.766 | 1344.0827 | 1182.0398 | 2773.9918
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0133 | 0.0078 | 0.0065 | 0.0069 | 0.0007 | 0.0056 | 0.0007 | 0.0076 | 0.0086 | 0.0015 | 0.0105 | 0.0085 | 0.009 | 0.0095 | 0.0089 | 0.0098
| Water for Electricity (m3) | 361.0406 | 943.8873 | 17573.3 | 3321.69 | 8693.06 | 14911.8 | 8040.03 | 114.7428 | 2261.37 | 4710.39 | 786.0249 | 2245.5 | 793.559 | 31875.5 | 776.5623 | 556.5384

## Picture
DOE Commercial Building Benchmark - Strip Mall

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 43.5 | 2268.21
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 2737.8 | 142756.71
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 91 | 4745
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 91 | 4745
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11