## Run Summary
Yorktown Power Station July 2017 Circulating Water Usage for DOE Emergency Run per PJM dispatch
Unit | On-Line | Off-Line | Days On-Line | Start-up Notification | Turbine Metal Temp < 300 deg | Total Cooling Water Days | Total Water Amount (Mgal)
1 | 2017-07-13 16:52 | 2017-07-14 23:03 | 1.2576 | 2017-07-12 14:47 | 2017-07-16 21:11 | 4.2667 | 528
1 | 2017-07-19 06:24 | 2017-07-25 15:08 | 6.3639 | 2017-07-18 08:06 | 2017-07-27 13:23 | 9.2201 | 1211
|  |  | Million gallons of Intake Circulating Water through Unit 1 |  |  |  | 1739
Unit | On-Line | Off-Line | Days On-Line | Start-up Notification* | Turbine Metal Temp < 300 deg* | Total Cooling Water Days | Total Water Amount (Mgal)
2 | 2017-07-11 05:10 | 2017-07-15 01:15 | 3.8368 | 2017-07-10 08:40 | 2017-07-18 17:20 | 8.3611 | 974
2 | 2017-07-18 23:40 | 2017-07-25 13:24 | 6.5722 | 2017-07-18 08:07 | 2017-07-28 15:33 | 10.3097 | 1297
|  |  | Million gallons of Intake Circulating Water through Unit 2 |  |  |  | 2271
|  |  | Total million gallons through Unit 1 & 2 |  |  |  | 4010
* Within this timeframe, there were a different number of pumps in service for Unit 2, and this variation was accounted for in the total water amount calculation. During the cool down only one pump is necessary but as the start-up proceeds, the second pump must be energized. This transition from one pump to two pumps is demonstrated by the time overlap and was accommodated in the total water amount calculation.