## BuildingSummary
Building Summary Large Hotel pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Large Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.59998 | See Benchmark Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZCAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Air cooled chiller | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 44332.9

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 7.5347 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 38.099 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 1.0572
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 38.099 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.35236
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 8.6039 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.39384
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 3.9573 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.39382
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 12.2365 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 1.1318
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 15.7419 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.82991
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 20.2858 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.34234
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60879
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60863
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 13.1176 |  |  |  |  | 0.25 | 97.35 |  | 0.16612
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 3.4487
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 16.8341 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 1.132
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 13.081 |  |  |  |  | 0.25 | 103.03 |  | 0.44675
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 |  |  |  | 15229.9891
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 3769.6561 | 3793.3384 | 3165.4365 | 3405.3878 | 2311.9923 | 2479.5226 | 1601.3242 | 3483.4595 | 1809.6023 | 1800.5027 | 3214.4413 | 1544.287 | 3179.2013 | 1457.5341 | 2456.2439 | 1305.6101
Heating (kW)
| HEATSYS1 BOILER | 2901.395 | 3586.5801 | 3125.9021 | 3838.0146 | 2939.7473 | 3322.5057 | 3135.9999 | 4198.4403 | 3438.9098 | 3681.5005 | 4766.5349 | 3963.8026 | 5109.2911 | 4693.5566 | 5181.4328 | 6289.8943
| CORRIDOR_FLR_6 UNIT HEATER COIL | 5.7674 | 13.2902 | 9.5911 | 16.5613 | 6.9908 | 12.531 | 9.3817 | 17.6397 | 15.8009 | 13.2713 | 20.0526 | 18.3876 | 21.2264 | 21.0138 | 22.6214 | 29.1761
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
| CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Control - Economizer
| FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| CAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CORRIDOR_FLR_6 UNIT HEATERFAN | 0.16 | 0.37 | 0.28 | 0.48 | 0.2 | 0.38 | 0.26 | 0.49 | 0.54 | 0.37 | 0.54 | 0.61 | 0.56 | 0.64 | 0.61 | 0.76
| DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
| KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 1.75 | 1.81 | 2.01 | 1.87 | 1.69 | 2.02 | 1.73 | 1.81 | 1.99 | 1.81 | 1.43 | 1.54 | 1.43 | 1.49 | 1.38 | 1.33
| ROOM_1_FLR_6 FAN COILFAN | 0.51 | 0.53 | 0.58 | 0.54 | 0.48 | 0.58 | 0.48 | 0.51 | 0.56 | 0.5 | 0.4 | 0.43 | 0.39 | 0.4 | 0.37 | 0.35
| ROOM_2_FLR_3 FAN COILFAN | 1.8 | 1.84 | 2.01 | 1.87 | 1.61 | 2.01 | 1.49 | 1.78 | 1.98 | 1.64 | 1.41 | 1.51 | 1.4 | 1.45 | 1.34 | 1.24
| ROOM_2_FLR_6 FAN COILFAN | 0.52 | 0.53 | 0.58 | 0.54 | 0.46 | 0.58 | 0.41 | 0.51 | 0.56 | 0.46 | 0.39 | 0.42 | 0.38 | 0.39 | 0.36 | 0.33
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.56 | 1.74 | 2.11 | 1.92 | 1.97 | 2.13 | 2.52 | 1.98 | 1.94 | 2.54 | 1.42 | 1.45 | 1.44 | 1.53 | 1.42 | 1.97
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_5_FLR_3 FAN COILFAN | 1.44 | 1.46 | 1.64 | 1.52 | 1.37 | 1.59 | 1.37 | 1.48 | 1.54 | 1.49 | 1.16 | 1.19 | 1.17 | 1.19 | 1.11 | 1.15
| ROOM_6_FLR_3 FAN COILFAN | 1.46 | 1.46 | 1.62 | 1.51 | 1.29 | 1.56 | 1.15 | 1.44 | 1.52 | 1.31 | 1.15 | 1.18 | 1.16 | 1.17 | 1.09 | 1.07
| FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
| CAV WITH REHEAT_FAN | 39.24 | 39.25 | 40.49 | 40.4 | 38.31 | 41.12 | 36.64 | 39.54 | 43.36 | 38.65 | 38.67 | 42.13 | 38.89 | 40.74 | 37.66 | 36.71
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.077828 | 0.10497 | 0.075197 | 0.097038 | 0.12298 | 0.092159 | 0.14462 | 0.0709 | 0.037011 | 0.067869 | 0.094873 | 0.037017 | 0.056545 | 0.072022 | 0.056197 | 0.092108
| Total Cost ($/m2) | 20.97 | 25.63 | 18.58 | 20.97 | 24.94 | 21.09 | 26.93 | 14.5 | 7.52 | 12.38 | 18.29 | 7.04 | 10.77 | 13.21 | 10.03 | 16.01
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.0081834 | 0.008562 | 0.010768 | 0.0083991 | 0.0081062 | 0.0084041 | 0.010077 | 0.0071932 | 0.0082865 | 0.0089293 | 0.0071998 | 0.0079851 | 0.0087797 | 0.007987 | 0.0042088
| Total Cost ($/m2) | 5.03 | 4.46 | 4.16 | 7 | 5.03 | 4.52 | 5.79 | 7.57 | 5.2 | 6.44 | 7.51 | 5.89 | 7.37 | 8.07 | 8.32 | 5.2
Total Utility Costs
| Cost Intensity ($/m2) | 26 | 30.09 | 22.74 | 27.98 | 29.97 | 25.6 | 32.71 | 22.07 | 12.72 | 18.81 | 25.79 | 12.93 | 18.14 | 21.28 | 18.36 | 21.22
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 33.3333 | 0 | 141.6667 | 0 | 0 | 0 | 325 | 0 | 0 | 394.4444 | 291.6667 | 1033.3333 | 808.3333 | 2136.1111 | 11755.5556
| Cooling | 1115969.4444 | 853597.2222 | 867350 | 551341.6667 | 409333.3333 | 672227.7778 | 240311.1111 | 437269.4444 | 395733.3333 | 202441.6667 | 324469.4444 | 280552.7778 | 299644.4444 | 215525 | 177777.7778 | 124147.2222
| Interior Lighting | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667
| Exterior Lighting | 51961.1111 | 51941.6667 | 51933.3333 | 51925 | 51886.1111 | 51872.2222 | 51900 | 51869.4444 | 51888.8889 | 51786.1111 | 51877.7778 | 51847.2222 | 51844.4444 | 51830.5556 | 51802.7778 | 51486.1111
| Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
| Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
| Fans | 400158.3333 | 384691.6667 | 407450 | 376450 | 371625 | 400286.1111 | 357005.5556 | 362441.6667 | 391133.3333 | 352763.8889 | 344619.4444 | 362208.3333 | 343177.7778 | 350352.7778 | 332880.5556 | 325541.6667
| Pumps | 39386.1111 | 31580.5556 | 28586.1111 | 24416.6667 | 19772.2222 | 23225 | 16080.5556 | 21319.4444 | 20011.1111 | 15033.3333 | 18172.2222 | 16091.6667 | 17625 | 15136.1111 | 14447.2222 | 13369.4444
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 22216.6667 | 21461.1111 | 21613.8889 | 20772.2222 | 20827.7778 | 21094.4444 | 20186.1111 | 20311.1111 | 20308.3333 | 19880.5556 | 20055.5556 | 19963.8889 | 19919.4444 | 19672.2222 | 19427.7778 | 19083.3333
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3056741.6667 | 2770350 | 2803977.7778 | 2452091.6667 | 2300486.1111 | 2595750 | 2112530.5556 | 2320583.3333 | 2306122.2222 | 2068952.7778 | 2186633.3333 | 2158002.7778 | 2160286.1111 | 2080372.2222 | 2025516.6667 | 1972425
Gas (MJ)
| Heating | 8120 | 210880 | 114310 | 443630 | 44550 | 233460 | 238770 | 831940 | 648720 | 726150 | 1179420 | 964080 | 1540980 | 1392770 | 1945990 | 3005310
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3733830 | 4733830 | 4159440 | 5696980 | 5509720 | 4851700 | 6333940 | 6454020 | 6310520 | 6847830 | 7118510 | 7083820 | 7692650 | 7796900 | 8639670 | 9786050
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4980600 | 6183350 | 5512400 | 7379270 | 6792920 | 6323800 | 7811360 | 8524610 | 8197890 | 8812630 | 9536590 | 9286550 | 10472280 | 10428320 | 11824310 | 14030000
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 15984870 | 16156620 | 15606720 | 16206800 | 15074670 | 15668510 | 15416470 | 16878710 | 16499920 | 16260860 | 17408470 | 17055360 | 18249310 | 17917660 | 19116170 | 21130740
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0.010577 | 0 | 0.044953 | 0 | 0 | 0 | 0.10313 | 0 | 0 | 0.12516 | 0.092549 | 0.32789 | 0.25649 | 0.67781 | 3.7302
| Cooling (elec) | 354.1108 | 270.8569 | 275.2208 | 174.9475 | 129.8865 | 213.3061 | 76.2537 | 138.751 | 125.5711 | 64.2372 | 102.9581 | 89.0228 | 95.0809 | 68.3887 | 56.4111 | 39.3934
| Interior Lighting (elec) | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307
| Exterior Lighting (elec) | 16.4879 | 16.4817 | 16.4791 | 16.4764 | 16.4641 | 16.4597 | 16.4685 | 16.4588 | 16.465 | 16.4324 | 16.4615 | 16.4518 | 16.4509 | 16.4465 | 16.4377 | 16.3372
| Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
| Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
| Fans (elec) | 126.9752 | 122.0674 | 129.2889 | 119.4522 | 117.9212 | 127.0157 | 113.2823 | 115.0072 | 124.1114 | 111.9363 | 109.352 | 114.9332 | 108.8945 | 111.1712 | 105.6271 | 103.2984
| Pumps (elec) | 12.4977 | 10.0209 | 9.0707 | 7.7477 | 6.274 | 7.3696 | 5.1026 | 6.7649 | 6.3498 | 4.7703 | 5.7663 | 5.1061 | 5.5926 | 4.8029 | 4.5843 | 4.2423
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 7.0496 | 6.8099 | 6.8584 | 6.5913 | 6.6089 | 6.6935 | 6.4053 | 6.445 | 6.4441 | 6.3083 | 6.3639 | 6.3348 | 6.3207 | 6.2422 | 6.1647 | 6.0554
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 969.9417 | 879.0661 | 889.7366 | 778.0788 | 729.9725 | 823.6634 | 670.3319 | 736.3496 | 731.7609 | 656.5042 | 693.8456 | 684.7608 | 685.4853 | 660.1277 | 642.7213 | 625.8747
Gas (MJ/m2)
| Heating (gas) | 0.71572 | 18.5874 | 10.0755 | 39.1026 | 3.9267 | 20.5777 | 21.0457 | 73.3291 | 57.1797 | 64.0045 | 103.9568 | 84.9762 | 135.8255 | 122.762 | 171.524 | 264.8949
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 329.1084 | 417.2507 | 366.6226 | 502.1449 | 485.6394 | 427.64 | 558.2881 | 568.8722 | 556.2238 | 603.5835 | 627.4419 | 624.3842 | 678.0479 | 687.2367 | 761.5204 | 862.565
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 439.0016 | 545.0147 | 485.8756 | 650.4259 | 598.7436 | 557.3943 | 688.5113 | 751.3788 | 722.5809 | 776.7655 | 840.577 | 818.5379 | 923.0509 | 919.1762 | 1042.2219 | 1236.6365
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1408.9433 | 1424.0817 | 1375.6123 | 1428.5047 | 1328.7161 | 1381.0586 | 1358.8432 | 1487.7284 | 1454.341 | 1433.2697 | 1534.4227 | 1503.2987 | 1608.5362 | 1579.3038 | 1684.9433 | 1862.5121
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 542.6819 | 498.0981 | 442.393 | 423.6896 | 442.8606 | 403.8841 | 400.7398 | 390.0154 | 402.978 | 388.5171 | 391.721 | 401.407 | 385.9464 | 389.1026 | 381.2442 | 379.8067
| Feb | 548.488 | 463.1123 | 452.7511 | 408.4269 | 431.1621 | 422.7252 | 425.682 | 393.1068 | 409.2756 | 402.6229 | 390.7818 | 400.9763 | 387.7136 | 399.7323 | 389.0812 | 380.8703
| Mar | 573.5121 | 515.6631 | 544.569 | 462.1807 | 430.8967 | 445.5852 | 406.2518 | 443.2612 | 423.8598 | 429.1803 | 420.3684 | 427.8745 | 402.9044 | 420.427 | 391.8221 | 391.6908
| Apr | 593.2961 | 575.3647 | 542.2245 | 502.935 | 471.6901 | 526.8379 | 428.5575 | 454.0868 | 466.4228 | 420.737 | 416.285 | 448.4326 | 434.2725 | 423.6737 | 403.8708 | 394.4862
| May | 622.5735 | 657.2872 | 620.8506 | 572.7995 | 473.0668 | 564.5247 | 433.6854 | 522.1437 | 502.4218 | 457.7074 | 476.3725 | 478.6603 | 542.6521 | 444.7301 | 432.9413 | 429.1979
| Jun | 678.3829 | 637.6929 | 759.5698 | 618.3558 | 470.5009 | 694.5006 | 442.6872 | 640.6267 | 539.4977 | 472.8631 | 543.1748 | 493.1407 | 584.7003 | 511.6777 | 515.2914 | 472.8471
| Jul | 646.0361 | 676.9752 | 739.4951 | 659.758 | 481.1668 | 682.5611 | 494.3193 | 671.4287 | 561.609 | 499.4902 | 596.7134 | 526.4581 | 610.7305 | 518.1146 | 553.2647 | 473.9145
| Aug | 656.209 | 701.7106 | 733.1488 | 614.3648 | 501.608 | 650.0313 | 437.0558 | 673.7572 | 561.1693 | 486.0332 | 635.0084 | 508.1137 | 609.3347 | 498.3301 | 536.5172 | 459.3916
| Sep | 628.8961 | 637.7463 | 653.2044 | 568.5123 | 491.4985 | 591.4166 | 494.7815 | 518.9199 | 496.2064 | 535.0653 | 522.2549 | 484.7054 | 491.7367 | 479.4227 | 479.0499 | 404.1727
| Oct | 627.2885 | 578.8536 | 557.3568 | 498.5534 | 471.5668 | 511.3633 | 447.2083 | 507.599 | 469.4248 | 429.7697 | 454.8227 | 439.4185 | 442.2793 | 432.3181 | 409.3707 | 394.8724
| Nov | 577.7228 | 542.6668 | 465.0584 | 436.8871 | 448.1354 | 432.3758 | 414.8803 | 456.9124 | 421.893 | 399.4092 | 451.7764 | 406.6832 | 405.9887 | 399.7089 | 396.2155 | 381.1743
| Dec | 543.0811 | 496.485 | 437.0254 | 423.2274 | 446.4534 | 416.3639 | 399.2383 | 386.8167 | 398.7214 | 386.607 | 392.1531 | 396.2816 | 385.8171 | 390.2181 | 383.253 | 374.5456
Time of Peak Electrical Demand
| Jan | 06-JAN-20:00 | 03-JAN-07:10 | 27-JAN-20:10 | 24-JAN-20:00 | 26-JAN-20:10 | 18-JAN-20:19 | 27-JAN-20:30 | 05-JAN-20:00 | 26-JAN-20:10 | 27-JAN-20:00 | 17-JAN-20:00 | 24-JAN-20:40 | 30-JAN-20:00 | 30-JAN-20:00 | 17-JAN-20:00 | 20-JAN-20:00
| Feb | 23-FEB-20:19 | 23-FEB-20:19 | 28-FEB-20:10 | 20-FEB-20:30 | 13-FEB-20:00 | 27-FEB-20:10 | 15-FEB-20:10 | 15-FEB-20:30 | 14-FEB-20:10 | 21-FEB-20:10 | 27-FEB-20:00 | 10-FEB-20:00 | 27-FEB-20:00 | 03-FEB-20:49 | 22-FEB-20:00 | 28-FEB-20:19
| Mar | 13-MAR-19:10 | 26-MAR-19:00 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:40 | 30-MAR-19:10 | 30-MAR-19:49 | 09-MAR-20:00 | 20-MAR-19:10 | 29-MAR-19:10 | 31-MAR-19:10 | 30-MAR-19:10 | 23-MAR-19:00 | 30-MAR-19:10 | 22-MAR-19:30 | 31-MAR-19:30
| Apr | 03-APR-19:10 | 30-APR-19:10 | 26-APR-19:10 | 14-APR-19:10 | 11-APR-19:10 | 21-APR-19:10 | 13-APR-19:19 | 05-APR-19:10 | 21-APR-19:10 | 14-APR-19:10 | 28-APR-19:00 | 26-APR-19:10 | 02-APR-19:00 | 06-APR-19:10 | 04-APR-19:10 | 25-APR-19:30
| May | 19-MAY-19:10 | 26-MAY-19:10 | 28-MAY-18:10 | 31-MAY-19:10 | 30-MAY-19:10 | 31-MAY-19:10 | 25-MAY-19:19 | 15-MAY-19:10 | 30-MAY-19:10 | 04-MAY-19:19 | 30-MAY-19:19 | 23-MAY-19:19 | 27-MAY-17:19 | 25-MAY-19:00 | 31-MAY-19:49 | 24-MAY-19:10
| Jun | 27-JUN-19:19 | 29-JUN-19:30 | 27-JUN-19:10 | 08-JUN-19:10 | 28-JUN-19:10 | 27-JUN-19:10 | 16-JUN-19:30 | 30-JUN-18:10 | 28-JUN-19:19 | 27-JUN-19:10 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:10 | 25-JUN-19:10 | 14-JUN-19:00 | 15-JUN-19:00
| Jul | 12-JUL-19:19 | 05-JUL-19:30 | 19-JUL-18:10 | 03-JUL-18:10 | 10-JUL-19:10 | 25-JUL-19:10 | 02-JUL-19:30 | 24-JUL-19:30 | 18-JUL-19:10 | 24-JUL-19:10 | 14-JUL-19:30 | 17-JUL-19:30 | 13-JUL-19:10 | 21-JUL-19:10 | 06-JUL-19:10 | 11-JUL-19:19
| Aug | 21-AUG-19:10 | 06-AUG-19:10 | 01-AUG-19:10 | 14-AUG-19:10 | 16-AUG-19:10 | 04-AUG-19:10 | 14-AUG-19:10 | 17-AUG-19:10 | 01-AUG-19:10 | 08-AUG-19:30 | 04-AUG-19:10 | 29-AUG-19:10 | 25-AUG-19:10 | 11-AUG-19:49 | 13-AUG-19:19 | 15-AUG-19:10
| Sep | 01-SEP-19:00 | 15-SEP-19:10 | 08-SEP-19:10 | 05-SEP-19:10 | 25-SEP-19:10 | 01-SEP-18:10 | 28-SEP-19:00 | 09-SEP-17:10 | 13-SEP-19:10 | 02-SEP-17:10 | 06-SEP-19:10 | 01-SEP-19:10 | 13-SEP-19:10 | 01-SEP-19:10 | 08-SEP-19:10 | 12-SEP-19:30
| Oct | 06-OCT-19:10 | 30-OCT-06:10 | 02-OCT-19:10 | 20-OCT-19:10 | 05-OCT-19:00 | 03-OCT-19:10 | 16-OCT-19:10 | 20-OCT-19:40 | 02-OCT-19:10 | 17-OCT-19:10 | 30-OCT-19:19 | 01-OCT-19:10 | 08-OCT-19:10 | 05-OCT-19:10 | 07-OCT-19:10 | 03-OCT-19:19
| Nov | 01-NOV-19:00 | 27-NOV-20:10 | 02-NOV-19:10 | 22-NOV-20:00 | 09-NOV-20:49 | 09-NOV-20:19 | 15-NOV-20:00 | 03-NOV-19:10 | 09-NOV-20:00 | 03-NOV-19:00 | 02-NOV-19:00 | 03-NOV-19:19 | 02-NOV-19:19 | 21-NOV-20:19 | 02-NOV-19:00 | 14-NOV-20:00
| Dec | 15-DEC-20:10 | 02-DEC-20:10 | 13-DEC-20:00 | 04-DEC-20:00 | 18-DEC-20:10 | 05-DEC-20:10 | 01-DEC-20:10 | 06-DEC-20:00 | 05-DEC-20:10 | 28-DEC-20:00 | 11-DEC-20:00 | 22-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 28-DEC-20:10
Source Energy
| Total Source Energy (GJ) | 41939.97 | 42975.11 | 37947.87 | 37753.97 | 33049.89 | 40331.6 | 32067.83 | 39183.14 | 36498.25 | 22598.2 | 38327.65 | 35917.82 | 38165.4 | 37420.68 | 37974.26 | 40684.59
| Total Source Energy (MJ/m2) | 3696.69 | 3787.93 | 3344.81 | 3327.72 | 2913.09 | 3554.92 | 2826.53 | 3453.69 | 3217.04 | 1991.86 | 3378.29 | 3165.88 | 3363.99 | 3298.35 | 3347.14 | 3586.03
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
| Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
Emissions
| Carbon Equivalent (kg) | 928124.0417 | 1035580 | 945855.5201 | 888402.3253 | 391343.0363 | 989517.2482 | 387742.7021 | 779943.947 | 1089880 | 309605.8668 | 1337770 | 1049000 | 928294.7876 | 948297.1017 | 906544.2278 | 808014.7602
| CO2 (kg) | 2200640 | 2640940 | 2277800 | 2098770 | 1071690 | 2403060 | 1066110 | 1848460 | 2622170 | 817099.726 | 3186680 | 2537900 | 2250330 | 2311550 | 2214420 | 2121290
| NOX (kg) | 3659.0096 | 3340.3018 | 3625.1729 | 3659.3629 | 935.5627 | 3699.6533 | 933.5485 | 3211.0273 | 4239.0747 | 991.9894 | 5348.9667 | 4043.2045 | 3606.1525 | 3632.0428 | 3476.0326 | 2405.4293
| SO2 (kg) | 13085.4074 | 13216.231 | 11276.8306 | 8608.819 | 6695.9591 | 14280.4004 | 6149.304 | 8473.3435 | 10072.5671 | 1601.4958 | 14738.7225 | 9426.0543 | 5101.4302 | 5557.6398 | 4783.7101 | 10044.1983
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0602 | 0.0378 | 0.0312 | 0.0322 | 0.0037 | 0.0274 | 0.0036 | 0.0351 | 0.0401 | 0.0072 | 0.0454 | 0.0377 | 0.0383 | 0.0396 | 0.0362 | 0.0355
| Water for Electricity (m3) | 1619.33 | 4507.69 | 83290.5 | 15309.9 | 40391.4 | 71211.8 | 37091.3 | 526.8598 | 10471.6 | 21138.1 | 3392.43 | 9799.06 | 3351.56 | 131779 | 3142.47 | 2015.19

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15984.87 | 1408.94 | 1408.94
Net Site Energy | 15984.87 | 1408.94 | 1408.94
Total Source Energy | 41939.97 | 3696.69 | 3696.69
Net Source Energy | 41939.97 | 3696.69 | 3696.69
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8.12 | 0 | 0 | 0 | 0
Cooling | 4017.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 187.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1440.57 | 0 | 0 | 0 | 0 | 0
Pumps | 141.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 3733.83 | 0 | 0 | 0 | 44332.9
Refrigeration | 79.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11004.27 | 4980.6 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3769656.11 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 2901394.95 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 45257.78 | 31452.99 | 13804.79 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 12928.61 | 9015.48 | 3913.13 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 46435.7 | 32291.88 | 14143.82 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 13266.64 | 9256.65 | 4009.99 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 706193.2 | 446107.78 | 260085.42 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 52384.01 | 33288.9 | 19095.11 | 0.64 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 706193.2 | 446107.78 | 260085.42 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 37568.77 | 25965.12 | 11603.65 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 38013.59 | 26280.87 | 11732.72 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 81953.12 | 51797.69 | 30155.42 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5422.63 | 3419.68 | 2002.95 | 0.63 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 879373.49 | 588506.65 | 290866.84 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 137004.81 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 145794.03 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 68935.56 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42239.3 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 18093.78 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 5767.37 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 140428.23 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 54676.36 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 155876.88 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 311143.94 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1568.08 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21783.87 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23930.92 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10061.36 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2921.42 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10069.24 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 2928.96 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 710011.01 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 42386.78 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 710011.01 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 9953.32 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 9955.31 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2061.92 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 25443.75 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 1665.96 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 57717.89 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.16 | 15.05 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.75 | 1116.89 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.51 | 321.58 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.8 | 1147.67 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.52 | 330.45 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.56 | 992.57 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.44 | 915.57 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.46 | 927.1 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 39.24 | 65286.22 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34543.68 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15976.31 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 167780.281 | 274.3734 | 961.4848 | 0 | 0.0044 | 118980.8728 | 70301.1594
February | 152875.32 | 250.5428 | 880.3494 | 0 | 0.0041 | 108941.0811 | 64110.3501
March | 170486.6094 | 280.3672 | 989.3365 | 0 | 0.0046 | 122428.8072 | 71592.2638
April | 174574.1106 | 289.4974 | 1032.0105 | 0 | 0.0047 | 127711.7299 | 73550.026
May | 193292.6158 | 323.1513 | 1163.2321 | 0 | 0.0053 | 143952.6761 | 81698.1569
June | 195202.0101 | 328.0263 | 1187.9674 | 0 | 0.0055 | 147015.1191 | 82673.8057
July | 209420.6926 | 352.9993 | 1282.9946 | 0 | 0.0059 | 158775.9581 | 88803.9805
August | 207993.6235 | 350.1943 | 1271.1074 | 0 | 0.0058 | 157304.5495 | 88158.8079
September | 196901.6432 | 330.3542 | 1194.1537 | 0 | 0.0055 | 147780.269 | 83340.7244
October | 193643.5713 | 322.8178 | 1158.1011 | 0 | 0.0053 | 143316.9261 | 81754.2829
November | 172640.9536 | 285.1504 | 1011.5999 | 0 | 0.0047 | 125184.9348 | 72621.2093
December | 165830.404 | 271.5353 | 953.0701 | 0 | 0.0044 | 117939.8848 | 69519.2748
Annual Sum or Average | 2200640 | 3659.0096 | 13085.4074 | 0 | 0.0602 | 1619330 | 928124.0417
Minimum of Months | 152875.32 | 250.5428 | 880.3494 | 0 | 0.0041 | 108941.0811 | 64110.3501
Maximum of Months | 209420.6926 | 352.9993 | 1282.9946 | 0 | 0.0059 | 158775.9581 | 88803.9805
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 808541000000 | 542681.906 | 06-JAN-20:00 | 177438.022 | 92719.3 | 48360.935 | 0 | 155851.025 | 11888 | 5077.549 | 0 | 48888.791 | 0 | 0 | 0 | 2458.285 | 0 | 0
February | 740315000000 | 548488.043 | 23-FEB-20:19 | 177438.022 | 92719.3 | 49881.744 | 0 | 159468.117 | 11888 | 5211.806 | 0 | 48888.791 | 0 | 0 | 0 | 2992.264 | 0 | 0
March | 831972000000 | 573512.117 | 13-MAR-19:10 | 177438.022 | 92719.3 | 50512.502 | 0 | 183446.86 | 11888 | 5579.788 | 0 | 48888.791 | 0 | 0 | 0 | 3038.854 | 0 | 0
April | 867872000000 | 593296.084 | 03-APR-19:10 | 177438.022 | 92719.3 | 51865.549 | 0 | 201514.938 | 11888 | 5913.159 | 0 | 48888.791 | 0 | 0 | 0 | 3068.325 | 0 | 0
May | 978238000000 | 622573.535 | 19-MAY-19:10 | 177438.022 | 92719.3 | 52130.853 | 0 | 230522.182 | 11888 | 6463.724 | 0 | 48888.791 | 0 | 0 | 0 | 2522.663 | 0 | 0
June | 999049000000 | 678382.865 | 27-JUN-19:19 | 177438.022 | 92719.3 | 53213.296 | 0 | 284488.948 | 11888 | 7172.281 | 0 | 48888.791 | 0 | 0 | 0 | 2574.227 | 0 | 0
July | 1078970000000 | 646036.131 | 12-JUL-19:19 | 177438.022 | 92719.3 | 52715.654 | 0 | 252513.531 | 11888 | 6754.872 | 0 | 48888.791 | 0 | 0 | 0 | 3117.961 | 0 | 0
August | 1068970000000 | 656208.963 | 21-AUG-19:10 | 177438.022 | 92719.3 | 52655.759 | 0 | 262617.135 | 11888 | 6869.413 | 0 | 48888.791 | 0 | 0 | 0 | 3132.544 | 0 | 0
September | 1004250000000 | 628896.077 | 01-SEP-19:00 | 177438.022 | 92719.3 | 51726.227 | 0 | 237230.981 | 11888 | 6471.32 | 0 | 48888.791 | 0 | 0 | 0 | 2533.436 | 0 | 0
October | 973918000000 | 627288.506 | 06-OCT-19:10 | 177438.022 | 92719.3 | 52170.151 | 0 | 235158.305 | 11888 | 6494.38 | 0 | 48888.791 | 0 | 0 | 0 | 2531.558 | 0 | 0
November | 850701000000 | 577722.819 | 01-NOV-19:00 | 177438.022 | 92719.3 | 50410.618 | 0 | 187786.971 | 11888 | 5534.122 | 0 | 48888.791 | 0 | 0 | 0 | 3056.995 | 0 | 0
December | 801467000000 | 543081.08 | 15-DEC-20:10 | 177438.022 | 92719.3 | 49271.46 | 0 | 155743.332 | 11888 | 4686.367 | 0 | 48888.791 | 0 | 0 | 0 | 2445.808 | 0 | 0
Annual Sum or Average | 11004300000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 740315000000 | 542681.906 |  | 177438.022 | 92719.3 | 48360.935 | 0 | 155743.332 | 11888 | 4686.367 | 0 | 48888.791 | 0 | 0 | 0 | 2445.808 | 0 | 0
Maximum of Months | 1078970000000 | 678382.865 |  | 177438.022 | 92719.3 | 53213.296 | 0 | 284488.948 | 11888 | 7172.281 | 0 | 48888.791 | 0 | 0 | 0 | 3132.544 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 237899.92 | 57032.01 | 0 | 294931.93
Cost per Total Building Area ($/m2) | 20.97 | 5.03 | 0 | 26
Cost per Net Conditioned Building Area ($/m2) | 20.97 | 5.03 | 0 | 26

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16156.62 | 1424.08 | 1424.08
Net Site Energy | 16156.62 | 1424.08 | 1424.08
Total Source Energy | 42975.11 | 3787.93 | 3787.93
Net Source Energy | 42975.11 | 3787.93 | 3787.93
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.12 | 210.88 | 0 | 0 | 0 | 0
Cooling | 3072.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1384.89 | 0 | 0 | 0 | 0 | 0
Pumps | 113.69 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4733.83 | 0 | 0 | 0 | 44332.9
Refrigeration | 77.26 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9973.26 | 6183.35 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3793338.38 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3586580.11 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 45999.51 | 31953 | 14046.51 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 13263.06 | 9245 | 4018.06 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 46579.66 | 32365.48 | 14214.17 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 13436.34 | 9368.42 | 4067.92 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 713334.62 | 447825.84 | 265508.78 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 57451.48 | 36511.45 | 20940.03 | 0.64 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 703162.93 | 442776.43 | 260386.49 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 37478.16 | 25885.88 | 11592.27 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 37568.97 | 25950.05 | 11618.93 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 82119.65 | 51667.61 | 30452.04 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5402.82 | 3395.87 | 2006.95 | 0.63 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 888815.07 | 594974.73 | 293840.34 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 134325.41 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 141786.68 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 74354.57 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42816.27 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 19506.88 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 13290.19 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 137804.39 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 54650.06 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 155696.82 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 307724.14 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1381.09 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23744.72 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23850.88 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16649.85 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4855.46 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16632.22 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4858.75 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 823599.64 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 51081 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 823599.64 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16318.43 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16288.38 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2054.37 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 45387.07 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2971.77 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 152805.39 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.37 | 34.86 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.81 | 1153.5 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.53 | 335.26 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.84 | 1168.88 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.53 | 339.87 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.74 | 1109.4 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.46 | 928.03 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.46 | 930.4 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 39.25 | 65302.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34760.7 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19749.23 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 191150.2116 | 236.9122 | 888.5501 | 0 | 0.0026 | 303035.6194 | 74329.0615
February | 167783.4094 | 207.7287 | 776.8132 | 0 | 0.0022 | 264927.147 | 65214.1503
March | 195183.6697 | 243.9395 | 935.7052 | 0 | 0.0027 | 319128.3856 | 76158.9093
April | 206964.8349 | 261.1564 | 1027.0982 | 0 | 0.0029 | 350311.3364 | 81077.1453
May | 236295.1948 | 300.5459 | 1205.9781 | 0 | 0.0034 | 411333.5304 | 92873.8114
June | 253239.8752 | 324.0899 | 1320.3554 | 0 | 0.0038 | 450354.8071 | 99790.5203
July | 275550.5583 | 353.654 | 1450.8464 | 0 | 0.0041 | 494868.2354 | 108712.5428
August | 268606.8041 | 344.4339 | 1409.9702 | 0 | 0.004 | 480924.3668 | 105933.3168
September | 240976.2974 | 307.7703 | 1247.6623 | 0 | 0.0036 | 425557.2589 | 94877.4383
October | 223437.3616 | 283.3236 | 1128.1939 | 0 | 0.0032 | 384798.801 | 87708.2197
November | 195821.0276 | 245.9963 | 956.4116 | 0 | 0.0027 | 326196.9111 | 76570.0496
December | 185927.1319 | 230.7511 | 868.6464 | 0 | 0.0025 | 296249.2166 | 72338.3281
Annual Sum or Average | 2640940 | 3340.3018 | 13216.231 | 0 | 0.0378 | 4507690 | 1035580
Minimum of Months | 167783.4094 | 207.7287 | 776.8132 | 0 | 0.0022 | 264927.147 | 65214.1503
Maximum of Months | 275550.5583 | 353.654 | 1450.8464 | 0 | 0.0041 | 494868.2354 | 108712.5428
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 670467000000 | 498098.07 | 03-JAN-07:10 | 98971.313 | 109708.624 | 52816.743 | 0 | 154487.839 | 11888 | 5454.856 | 0 | 61110.989 | 0 | 0 | 0 | 3659.706 | 0 | 0
February | 586152000000 | 463112.315 | 23-FEB-20:19 | 177438.022 | 92719.3 | 46829.73 | 0 | 79498.838 | 11888 | 3003.126 | 0 | 48888.791 | 0 | 0 | 0 | 2846.509 | 0 | 0
March | 706072000000 | 515663.136 | 26-MAR-19:00 | 167588.533 | 91473.541 | 48160.766 | 0 | 139867.968 | 11888 | 4836.257 | 0 | 48888.791 | 0 | 0 | 0 | 2959.28 | 0 | 0
April | 775065000000 | 575364.692 | 30-APR-19:10 | 167588.533 | 91473.541 | 49972.79 | 0 | 196769.281 | 11888 | 5787.263 | 0 | 48888.791 | 0 | 0 | 0 | 2996.493 | 0 | 0
May | 910076000000 | 657287.242 | 26-MAY-19:10 | 177438.022 | 92719.3 | 53153.783 | 0 | 263798.907 | 11888 | 6836.399 | 0 | 48888.791 | 0 | 0 | 0 | 2564.04 | 0 | 0
June | 996411000000 | 637692.853 | 29-JUN-19:30 | 177438.022 | 92719.3 | 52700.236 | 0 | 244363.045 | 11888 | 6591.679 | 0 | 48888.791 | 0 | 0 | 0 | 3103.78 | 0 | 0
July | 1094900000000 | 676975.202 | 05-JUL-19:30 | 177438.022 | 92719.3 | 53817.263 | 0 | 281899.457 | 11888 | 7175.249 | 0 | 48888.791 | 0 | 0 | 0 | 3149.119 | 0 | 0
August | 1064050000000 | 701710.611 | 06-AUG-19:10 | 167588.533 | 91473.541 | 52905.767 | 0 | 318203.41 | 11888 | 7625.994 | 0 | 48888.791 | 0 | 0 | 0 | 3136.575 | 0 | 0
September | 941546000000 | 637746.345 | 15-SEP-19:10 | 177438.022 | 92719.3 | 51803.654 | 0 | 245960.564 | 11888 | 6508.407 | 0 | 48888.791 | 0 | 0 | 0 | 2539.607 | 0 | 0
October | 851368000000 | 578853.605 | 30-OCT-06:10 | 98971.313 | 109708.624 | 60854.868 | 0 | 225827.202 | 11888 | 8044.47 | 0 | 61110.989 | 0 | 0 | 0 | 2448.14 | 0 | 0
November | 721711000000 | 542666.757 | 27-NOV-20:10 | 177438.022 | 92719.3 | 47497.098 | 0 | 156260.272 | 11888 | 4982.824 | 0 | 48888.791 | 0 | 0 | 0 | 2992.45 | 0 | 0
December | 655452000000 | 496484.963 | 02-DEC-20:10 | 157739.045 | 88982.023 | 44605.095 | 0 | 136944.351 | 11888 | 4507.022 | 0 | 48888.791 | 0 | 0 | 0 | 2930.635 | 0 | 0
Annual Sum or Average | 9973260000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 586152000000 | 463112.315 |  | 98971.313 | 88982.023 | 44605.095 | 0 | 79498.838 | 11888 | 3003.126 | 0 | 48888.791 | 0 | 0 | 0 | 2448.14 | 0 | 0
Maximum of Months | 1094900000000 | 701710.611 |  | 177438.022 | 109708.624 | 60854.868 | 0 | 318203.41 | 11888 | 8044.47 | 0 | 61110.989 | 0 | 0 | 0 | 3659.706 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 290814.76 | 50600.86 | 0 | 341415.62
Cost per Total Building Area ($/m2) | 25.63 | 4.46 | 0 | 30.09
Cost per Net Conditioned Building Area ($/m2) | 25.63 | 4.46 | 0 | 30.09

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15606.72 | 1375.61 | 1375.61
Net Site Energy | 15606.72 | 1375.61 | 1375.61
Total Source Energy | 37947.87 | 3344.81 | 3344.81
Net Source Energy | 37947.87 | 3344.81 | 3344.81
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 114.31 | 0 | 0 | 0 | 0
Cooling | 3122.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1466.82 | 0 | 0 | 0 | 0 | 0
Pumps | 102.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4159.44 | 0 | 0 | 0 | 44332.9
Refrigeration | 77.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10094.32 | 5512.4 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3165436.47 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3125902.06 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 46116.82 | 31768.68 | 14348.14 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 13297.74 | 9183.84 | 4113.9 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 46195.05 | 31824.77 | 14370.28 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 13332.8 | 9208.5 | 4124.3 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 630988.87 | 392167.3 | 238821.57 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 61114.96 | 38707.77 | 22407.19 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 568031.31 | 357315.03 | 210716.29 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 37871.83 | 25973.28 | 11898.55 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 37560.37 | 25762.59 | 11797.78 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 60803.17 | 38361.67 | 22441.5 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4215.8 | 2648.49 | 1567.31 | 0.63 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 924166.31 | 608492.12 | 315674.19 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 137480.23 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 104478.08 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 82628.54 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 46430.96 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 22536.61 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 9591.12 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 140915.3 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 56552.1 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 156487.78 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 311931.52 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1625.13 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26833.44 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24009.52 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13360.5 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3873.31 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13383.53 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3882.46 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 740650.98 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 46846.18 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 740650.98 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13125.89 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13139.13 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1981.01 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 34545.72 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2261.92 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 76501.96 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.28 | 26.36 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.01 | 1279.63 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.58 | 371.02 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.01 | 1282.08 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.58 | 372.09 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.11 | 1345.15 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.64 | 1041.45 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.62 | 1033.37 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 40.49 | 67083.94 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29006.84 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17212.55 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 162486.4273 | 248.7974 | 733.5088 | 0 | 0.0021 | 5417140 | 66481.1383
February | 147986.5251 | 227.2357 | 672.6845 | 0 | 0.0019 | 4967970 | 60613.2719
March | 174992.1051 | 273.1835 | 827.8516 | 0 | 0.0023 | 6114200 | 72127.4539
April | 178121.0133 | 282.1919 | 872.4852 | 0 | 0.0024 | 6444090 | 73834.1146
May | 195648.3129 | 314.2829 | 989.6116 | 0 | 0.0027 | 7309410 | 81536.6241
June | 218605.4883 | 355.9714 | 1140.5342 | 0 | 0.0031 | 8424410 | 91590.5415
July | 239184.2325 | 391.4725 | 1262.3043 | 0 | 0.0035 | 9323960 | 100413.9009
August | 232190.722 | 379.1827 | 1219.294 | 0 | 0.0033 | 9006220 | 97392.6037
September | 211974.5004 | 343.5986 | 1094.5441 | 0 | 0.003 | 8084630 | 88653.0397
October | 189177.1088 | 301.6878 | 940.9651 | 0 | 0.0026 | 6949980 | 78617.281
November | 166477.839 | 260.6831 | 793.2972 | 0 | 0.0022 | 5859040 | 68698.1084
December | 160951.5064 | 246.8854 | 729.7499 | 0 | 0.002 | 5389400 | 65897.442
Annual Sum or Average | 2277800 | 3625.1729 | 11276.8306 | 0 | 0.0312 | 83290500 | 945855.5201
Minimum of Months | 147986.5251 | 227.2357 | 672.6845 | 0 | 0.0019 | 4967970 | 60613.2719
Maximum of Months | 239184.2325 | 391.4725 | 1262.3043 | 0 | 0.0035 | 9323960 | 100413.9009
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 656525000000 | 442392.989 | 27-JAN-20:10 | 177438.022 | 92719.3 | 46835.485 | 0 | 60149.183 | 11888 | 2138.58 | 0 | 48888.791 | 0 | 0 | 0 | 2335.628 | 0 | 0
February | 602090000000 | 452751.055 | 28-FEB-20:10 | 177438.022 | 92719.3 | 48033.376 | 0 | 69170.174 | 11888 | 2264.664 | 0 | 48888.791 | 0 | 0 | 0 | 2348.728 | 0 | 0
March | 741005000000 | 544569.033 | 17-MAR-19:10 | 177438.022 | 92719.3 | 52928.528 | 0 | 154365.835 | 11888 | 3827.932 | 0 | 48888.791 | 0 | 0 | 0 | 2512.625 | 0 | 0
April | 780986000000 | 542224.535 | 26-APR-19:10 | 177438.022 | 92719.3 | 53167.312 | 0 | 151237.358 | 11888 | 3809.68 | 0 | 48888.791 | 0 | 0 | 0 | 3076.072 | 0 | 0
May | 885858000000 | 620850.626 | 28-MAY-18:10 | 157739.045 | 77674.8 | 56543.44 | 0 | 271926.878 | 0 | 4907.724 | 0 | 48888.791 | 0 | 0 | 0 | 3169.947 | 0 | 0
June | 1020990000000 | 759569.85 | 27-JUN-19:10 | 177438.022 | 92719.3 | 59991.42 | 0 | 369998.892 | 0 | 7923.083 | 0 | 48888.791 | 0 | 0 | 0 | 2610.342 | 0 | 0
July | 1130010000000 | 739495.12 | 19-JUL-18:10 | 157821.345 | 80166.318 | 59471.704 | 0 | 383226.468 | 0 | 6671.781 | 0 | 48888.791 | 0 | 0 | 0 | 3248.713 | 0 | 0
August | 1091500000000 | 733148.803 | 01-AUG-19:10 | 177438.022 | 92719.3 | 59352.108 | 0 | 345082.872 | 0 | 7049.247 | 0 | 48888.791 | 0 | 0 | 0 | 2618.462 | 0 | 0
September | 979810000000 | 653204.358 | 08-SEP-19:10 | 177438.022 | 92719.3 | 57064.631 | 0 | 256816.93 | 11888 | 5756.966 | 0 | 48888.791 | 0 | 0 | 0 | 2631.718 | 0 | 0
October | 842298000000 | 557356.785 | 02-OCT-19:10 | 177438.022 | 92719.3 | 54098.393 | 0 | 163876.684 | 11888 | 5320.463 | 0 | 48888.791 | 0 | 0 | 0 | 3127.132 | 0 | 0
November | 710082000000 | 465058.425 | 02-NOV-19:10 | 177438.022 | 92719.3 | 49814.584 | 0 | 79010.631 | 11888 | 2410.24 | 0 | 48888.791 | 0 | 0 | 0 | 2888.857 | 0 | 0
December | 653164000000 | 437025.378 | 13-DEC-20:00 | 177438.022 | 92719.3 | 46079.237 | 0 | 54350.996 | 11888 | 2825.891 | 0 | 48888.791 | 0 | 0 | 0 | 2835.142 | 0 | 0
Annual Sum or Average | 10094300000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 602090000000 | 437025.378 |  | 157739.045 | 77674.8 | 46079.237 | 0 | 54350.996 | 0 | 2138.58 | 0 | 48888.791 | 0 | 0 | 0 | 2335.628 | 0 | 0
Maximum of Months | 1130010000000 | 759569.85 |  | 177438.022 | 92719.3 | 59991.42 | 0 | 383226.468 | 11888 | 7923.083 | 0 | 48888.791 | 0 | 0 | 0 | 3248.713 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 210850.63 | 47196.98 | 0 | 258047.61
Cost per Total Building Area ($/m2) | 18.58 | 4.16 | 0 | 22.74
Cost per Net Conditioned Building Area ($/m2) | 18.58 | 4.16 | 0 | 22.74

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16206.8 | 1428.5 | 1428.5
Net Site Energy | 16206.8 | 1428.5 | 1428.5
Total Source Energy | 37753.97 | 3327.72 | 3327.72
Net Source Energy | 37753.97 | 3327.72 | 3327.72
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.51 | 443.63 | 0 | 0 | 0 | 0
Cooling | 1984.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1355.22 | 0 | 0 | 0 | 0 | 0
Pumps | 87.9 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5696.98 | 0 | 0 | 0 | 44332.9
Refrigeration | 74.78 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8827.53 | 7379.27 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.278 | 1.58 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3405387.77 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3838014.59 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 43403.45 | 29872.67 | 13530.77 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 12450.63 | 8594.1 | 3856.53 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 43462.71 | 29915.28 | 13547.43 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 12474.61 | 8611.18 | 3863.43 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 691914.89 | 426574.35 | 265340.53 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 50172.32 | 31983.84 | 18188.48 | 0.64 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 678452.13 | 420059.8 | 258392.33 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35746.16 | 24475.78 | 11270.38 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35493.93 | 24301.48 | 11192.46 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 79397.41 | 49094.38 | 30303.03 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5233.19 | 3231.23 | 2001.96 | 0.62 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 847064.04 | 557596.36 | 289467.67 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 133707.77 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 135694.44 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 77933.71 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42810.12 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 19574.18 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 16561.29 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 137130.94 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 53911.72 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 155620.06 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 305983.37 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1372.12 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25009.52 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23768.07 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19797.44 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5773.35 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19808.19 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5789.56 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 840547.16 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 53609.51 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 840547.16 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19322.87 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19313.4 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1986.69 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 51475.21 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3370.4 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 205235.33 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.48 | 45.09 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.87 | 1188.94 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.54 | 343.1 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.87 | 1190.78 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.54 | 343.84 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.92 | 1224.44 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.52 | 969.4 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.51 | 962.54 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 40.4 | 66929.08 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31205.67 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21133.74 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 159080.6191 | 263.15 | 582.8193 | 0 | 0.0022 | 1036330 | 66025.2051
February | 145216.5708 | 241.6807 | 539.2052 | 0 | 0.002 | 958793.3904 | 60406.2899
March | 161592.535 | 273.9101 | 624.3998 | 0 | 0.0024 | 1110340 | 67677.7387
April | 164308.53 | 284.1494 | 662.5202 | 0 | 0.0025 | 1178200 | 69335.6982
May | 182948.6835 | 322.9947 | 770.0819 | 0 | 0.0029 | 1369550 | 77811.988
June | 192990.0105 | 346.0759 | 838.5907 | 0 | 0.0031 | 1491450 | 82577.1674
July | 212148.7322 | 383.9567 | 939.1191 | 0 | 0.0035 | 1670280 | 91100.3884
August | 208588.2961 | 377.2303 | 921.9727 | 0 | 0.0034 | 1639780 | 89545.3743
September | 191192.496 | 343.1403 | 832.1905 | 0 | 0.0031 | 1480070 | 81834.6147
October | 169632.4444 | 297.4385 | 703.9983 | 0 | 0.0026 | 1252000 | 71959.3109
November | 153345.52 | 261.86 | 601.9899 | 0 | 0.0023 | 1070520 | 64401.9092
December | 157721.6497 | 263.7764 | 591.9313 | 0 | 0.0022 | 1052560 | 65726.6405
Annual Sum or Average | 2098770 | 3659.3629 | 8608.819 | 0 | 0.0322 | 15309900 | 888402.3253
Minimum of Months | 145216.5708 | 241.6807 | 539.2052 | 0 | 0.002 | 958793.3904 | 60406.2899
Maximum of Months | 212148.7322 | 383.9567 | 939.1191 | 0 | 0.0035 | 1670280 | 91100.3884
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 597536000000 | 423689.583 | 24-JAN-20:00 | 177438.022 | 92719.3 | 42404.511 | 0 | 45791.903 | 11888 | 2231.343 | 0 | 48888.791 | 0 | 0 | 0 | 2327.713 | 0 | 0
February | 552831000000 | 408426.892 | 20-FEB-20:30 | 167588.533 | 91473.541 | 43310.99 | 0 | 40371.993 | 11888 | 2176.191 | 0 | 48888.791 | 0 | 0 | 0 | 2728.852 | 0 | 0
March | 640214000000 | 462180.71 | 28-MAR-19:10 | 177438.022 | 92719.3 | 47549.737 | 0 | 78015.978 | 11888 | 3263.165 | 0 | 48888.791 | 0 | 0 | 0 | 2417.717 | 0 | 0
April | 679337000000 | 502935.014 | 14-APR-19:10 | 177438.022 | 92719.3 | 49649.228 | 0 | 115446.246 | 11888 | 4436.736 | 0 | 48888.791 | 0 | 0 | 0 | 2468.691 | 0 | 0
May | 789671000000 | 572799.509 | 31-MAY-19:10 | 177438.022 | 92719.3 | 52513.352 | 0 | 192459.761 | 0 | 5702.665 | 0 | 48888.791 | 0 | 0 | 0 | 3077.618 | 0 | 0
June | 859956000000 | 618355.755 | 08-JUN-19:10 | 177438.022 | 92719.3 | 53424.806 | 0 | 236368.758 | 0 | 6384.536 | 0 | 48888.791 | 0 | 0 | 0 | 3131.542 | 0 | 0
July | 963067000000 | 659757.971 | 03-JUL-18:10 | 157821.345 | 80166.318 | 56953.029 | 0 | 305395.136 | 0 | 7282.804 | 0 | 48888.791 | 0 | 0 | 0 | 3250.547 | 0 | 0
August | 945481000000 | 614364.77 | 14-AUG-19:10 | 177438.022 | 92719.3 | 54048.806 | 0 | 231796.367 | 0 | 6340.093 | 0 | 48888.791 | 0 | 0 | 0 | 3133.392 | 0 | 0
September | 853394000000 | 568512.277 | 05-SEP-19:10 | 177438.022 | 92719.3 | 52247.408 | 0 | 177308.695 | 11888 | 5529.781 | 0 | 48888.791 | 0 | 0 | 0 | 2492.28 | 0 | 0
October | 721894000000 | 498553.381 | 20-OCT-19:10 | 177438.022 | 92719.3 | 48073.672 | 0 | 113581.237 | 11888 | 3538.589 | 0 | 48888.791 | 0 | 0 | 0 | 2425.77 | 0 | 0
November | 617249000000 | 436887.128 | 22-NOV-20:00 | 177438.022 | 92719.3 | 45645.089 | 0 | 54994.328 | 11888 | 2493.923 | 0 | 48888.791 | 0 | 0 | 0 | 2819.676 | 0 | 0
December | 606899000000 | 423227.372 | 04-DEC-20:00 | 177438.022 | 92719.3 | 42944.615 | 0 | 44332.703 | 11888 | 2227.797 | 0 | 48888.791 | 0 | 0 | 0 | 2788.144 | 0 | 0
Annual Sum or Average | 8827530000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 552831000000 | 408426.892 |  | 157821.345 | 80166.318 | 42404.511 | 0 | 40371.993 | 0 | 2176.191 | 0 | 48888.791 | 0 | 0 | 0 | 2327.713 | 0 | 0
Maximum of Months | 963067000000 | 659757.971 |  | 177438.022 | 92719.3 | 56953.029 | 0 | 305395.136 | 11888 | 7282.804 | 0 | 48888.791 | 0 | 0 | 0 | 3250.547 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 237945.04 | 79460.31 | 0 | 317405.35
Cost per Total Building Area ($/m2) | 20.97 | 7 | 0 | 27.98
Cost per Net Conditioned Building Area ($/m2) | 20.97 | 7 | 0 | 27.98

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15074.67 | 1328.72 | 1328.72
Net Site Energy | 15074.67 | 1328.72 | 1328.72
Total Source Energy | 33049.89 | 2913.09 | 2913.09
Net Source Energy | 33049.89 | 2913.09 | 2913.09
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 44.55 | 0 | 0 | 0 | 0
Cooling | 1473.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1337.85 | 0 | 0 | 0 | 0 | 0
Pumps | 71.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5509.72 | 0 | 0 | 0 | 44332.9
Refrigeration | 74.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8281.75 | 6792.92 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2311992.29 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 2939747.31 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 41860.79 | 29387.45 | 12473.34 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 11811.61 | 8307.58 | 3504.03 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 39896.56 | 27986.98 | 11909.58 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 11304.63 | 7945.8 | 3358.83 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 554565.74 | 363364.28 | 191201.46 | 0.66 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 55838.88 | 36938.3 | 18900.58 | 0.66 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 599146.61 | 391974.9 | 207171.71 | 0.65 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 34368.07 | 24030.21 | 10337.86 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 32301.81 | 22562.9 | 9738.92 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 70288.18 | 45880.43 | 24407.75 | 0.65 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4690.53 | 3046.52 | 1644.01 | 0.65 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 879117.98 | 602559.46 | 276558.52 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 127893.87 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 135121.08 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 82913.1 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 39719.13 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16711.24 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 6990.75 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 131466.41 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 53688.9 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 153954.16 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 298743.1 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1171.45 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26502.63 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23092.31 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10837.34 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3179.19 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10802.45 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3172.74 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 724970.81 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 44982.39 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 724970.81 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10666.31 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 10614.05 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2054.61 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 28369.63 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 1857.54 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 53185.88 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.2 | 18.45 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.69 | 1075.12 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.48 | 304.64 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.61 | 1022.91 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.46 | 291.15 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.97 | 1254.08 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 875.07 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.29 | 820.7 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 38.31 | 63739.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21186.21 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16187.5 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 88787.5581 | 77.6711 | 525.8595 | 0 | 0.0003 | 3171950 | 32333.8999
February | 80414.195 | 70.3413 | 477.1171 | 0 | 0.0003 | 2877940 | 29287.1536
March | 88650.5414 | 77.5154 | 531.4549 | 0 | 0.0003 | 3205730 | 32303.5496
April | 85742.6894 | 74.9188 | 523.6872 | 0 | 0.0003 | 3158930 | 31273.438
May | 89436.5077 | 78.0723 | 559.4812 | 0 | 0.0003 | 3374910 | 32661.0808
June | 87027.0877 | 75.9142 | 554.2248 | 0 | 0.0003 | 3343250 | 31811.1396
July | 93878.4505 | 81.794 | 615.1503 | 0 | 0.0003 | 3710850 | 34368.2889
August | 95988.1587 | 83.6001 | 634.7137 | 0 | 0.0003 | 3828890 | 35158.1495
September | 92196.9941 | 80.3315 | 603.6962 | 0 | 0.0003 | 3641750 | 33751.388
October | 92808.8523 | 80.9501 | 592.4074 | 0 | 0.0003 | 3573580 | 33928.7117
November | 87248.3346 | 76.2003 | 538.9706 | 0 | 0.0003 | 3251150 | 31841.1735
December | 89511.258 | 78.2536 | 539.1962 | 0 | 0.0003 | 3252440 | 32625.0633
Annual Sum or Average | 1071690 | 935.5627 | 6695.9591 | 0 | 0.0037 | 40391400 | 391343.0363
Minimum of Months | 80414.195 | 70.3413 | 477.1171 | 0 | 0.0003 | 2877940 | 29287.1536
Maximum of Months | 95988.1587 | 83.6001 | 634.7137 | 0 | 0.0003 | 3828890 | 35158.1495
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 650368000000 | 442860.648 | 26-JAN-20:10 | 177438.022 | 92719.3 | 45642 | 0 | 61335.411 | 11888 | 2102.385 | 0 | 48888.791 | 0 | 0 | 0 | 2846.738 | 0 | 0
February | 590086000000 | 431162.074 | 13-FEB-20:00 | 177438.022 | 92719.3 | 45656.448 | 0 | 49191.011 | 11888 | 2601.226 | 0 | 48888.791 | 0 | 0 | 0 | 2779.278 | 0 | 0
March | 657295000000 | 430896.713 | 29-MAR-19:40 | 177438.022 | 92719.3 | 45580.984 | 0 | 49180.147 | 11888 | 2434.841 | 0 | 48888.791 | 0 | 0 | 0 | 2766.628 | 0 | 0
April | 647699000000 | 471690.147 | 11-APR-19:10 | 177438.022 | 92719.3 | 47504.521 | 0 | 87502.285 | 11888 | 3346.343 | 0 | 48888.791 | 0 | 0 | 0 | 2402.885 | 0 | 0
May | 691983000000 | 473066.847 | 30-MAY-19:10 | 177438.022 | 92719.3 | 47747.71 | 0 | 88857.608 | 11888 | 3127.551 | 0 | 48888.791 | 0 | 0 | 0 | 2399.866 | 0 | 0
June | 685492000000 | 470500.857 | 28-JUN-19:10 | 177438.022 | 92719.3 | 47766.469 | 0 | 85822.375 | 11888 | 3071.413 | 0 | 48888.791 | 0 | 0 | 0 | 2906.487 | 0 | 0
July | 760864000000 | 481166.81 | 10-JUL-19:10 | 177438.022 | 92719.3 | 49369.623 | 0 | 94653.861 | 11888 | 3276.758 | 0 | 48888.791 | 0 | 0 | 0 | 2932.455 | 0 | 0
August | 785067000000 | 501607.972 | 16-AUG-19:10 | 177438.022 | 92719.3 | 49407.753 | 0 | 114689.207 | 11888 | 3651.75 | 0 | 48888.791 | 0 | 0 | 0 | 2925.15 | 0 | 0
September | 746697000000 | 491498.539 | 25-SEP-19:10 | 177438.022 | 92719.3 | 50219.758 | 0 | 103805.348 | 11888 | 3600.5 | 0 | 48888.791 | 0 | 0 | 0 | 2938.819 | 0 | 0
October | 732719000000 | 471566.836 | 05-OCT-19:00 | 177438.022 | 92719.3 | 48217.826 | 0 | 86383.216 | 11888 | 3180.288 | 0 | 48888.791 | 0 | 0 | 0 | 2851.393 | 0 | 0
November | 666608000000 | 448135.432 | 09-NOV-20:49 | 177438.022 | 92719.3 | 46081.399 | 0 | 65501.703 | 11888 | 2800.095 | 0 | 48888.791 | 0 | 0 | 0 | 2818.122 | 0 | 0
December | 666873000000 | 446453.391 | 18-DEC-20:10 | 177438.022 | 92719.3 | 45938.49 | 0 | 64581.953 | 11888 | 2151.756 | 0 | 48888.791 | 0 | 0 | 0 | 2847.079 | 0 | 0
Annual Sum or Average | 8281750000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 590086000000 | 430896.713 |  | 177438.022 | 92719.3 | 45580.984 | 0 | 49180.147 | 11888 | 2102.385 | 0 | 48888.791 | 0 | 0 | 0 | 2399.866 | 0 | 0
Maximum of Months | 785067000000 | 501607.972 |  | 177438.022 | 92719.3 | 50219.758 | 0 | 114689.207 | 11888 | 3651.75 | 0 | 48888.791 | 0 | 0 | 0 | 2938.819 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 282916.81 | 57054.16 | 0 | 339970.97
Cost per Total Building Area ($/m2) | 24.94 | 5.03 | 0 | 29.97
Cost per Net Conditioned Building Area ($/m2) | 24.94 | 5.03 | 0 | 29.97

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15668.51 | 1381.06 | 1381.06
Net Site Energy | 15668.51 | 1381.06 | 1381.06
Total Source Energy | 40331.6 | 3554.92 | 3554.92
Net Source Energy | 40331.6 | 3554.92 | 3554.92
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 233.46 | 0 | 0 | 0 | 0
Cooling | 2420.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1441.03 | 0 | 0 | 0 | 0 | 0
Pumps | 83.61 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4851.7 | 0 | 0 | 0 | 44332.9
Refrigeration | 75.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9344.7 | 6323.8 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.306 | 1.623 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2479522.59 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3322505.67 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 42272.04 | 28997.04 | 13275 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 12029.43 | 8266.3 | 3763.13 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 42007.98 | 28816.43 | 13191.55 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 11979.51 | 8232.37 | 3747.14 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 572228.57 | 354901.46 | 217327.11 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 55362.25 | 35133.09 | 20229.16 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 538812.13 | 337501.12 | 201311.02 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33362.05 | 22805.7 | 10556.35 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 32753.07 | 22390.72 | 10362.35 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 59013.07 | 37056.4 | 21956.67 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4044.82 | 2524.44 | 1520.38 | 0.62 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 840813.96 | 555966 | 284847.97 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 134589.6 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 96895.55 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 82265.37 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 45074.72 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 20345.63 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 12531.03 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 138143.3 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 58296.69 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 155635.48 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 303588.71 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1249.73 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26594.52 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23449.04 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16011.86 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4665.62 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16021.75 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4669.66 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 757424.29 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 48546.51 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 757424.29 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15726.41 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15715.42 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1905.45 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 40987.52 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2683.71 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 124128.75 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.38 | 35.85 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.02 | 1287.1 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.58 | 367.63 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.01 | 1279.32 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.58 | 366.19 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.13 | 1358.69 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.59 | 1011.07 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.56 | 993.18 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 41.12 | 68125.43 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22721.39 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18295.13 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 177392.1999 | 262.2218 | 951.8671 | 0 | 0.0019 | 4746220 | 71914.2148
February | 163487.0476 | 244.0958 | 900.0812 | 0 | 0.0018 | 4488110 | 66529.5402
March | 179733.3147 | 269.734 | 1002.511 | 0 | 0.0019 | 4998920 | 73284.4045
April | 188197.1138 | 288.1887 | 1103.7909 | 0 | 0.0021 | 5504190 | 77333.3478
May | 203186.9611 | 315.2085 | 1229.9224 | 0 | 0.0024 | 6133330 | 83915.5086
June | 229308.9087 | 361.2247 | 1439.6697 | 0 | 0.0027 | 7179510 | 95274.6758
July | 250312.1469 | 396.6181 | 1593.2227 | 0 | 0.003 | 7945350 | 104241.0622
August | 247451.9875 | 391.7428 | 1571.7905 | 0 | 0.003 | 7838460 | 103014.276
September | 219460.4418 | 344.6619 | 1367.9799 | 0 | 0.0026 | 6821960 | 91073.7626
October | 195265.3701 | 301.6184 | 1169.7415 | 0 | 0.0022 | 5833170 | 80508.6762
November | 172836.9145 | 261.6515 | 985.3551 | 0 | 0.0019 | 4913470 | 70708.1223
December | 176427.3318 | 262.687 | 964.4684 | 0 | 0.0019 | 4809130 | 71719.6574
Annual Sum or Average | 2403060 | 3699.6533 | 14280.4004 | 0 | 0.0274 | 71211800 | 989517.2482
Minimum of Months | 163487.0476 | 244.0958 | 900.0812 | 0 | 0.0018 | 4488110 | 66529.5402
Maximum of Months | 250312.1469 | 396.6181 | 1593.2227 | 0 | 0.003 | 7945350 | 104241.0622
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 622818000000 | 403884.103 | 18-JAN-20:19 | 177438.022 | 92719.3 | 43446.725 | 0 | 25408.414 | 11888 | 1511.549 | 0 | 48888.791 | 0 | 0 | 0 | 2583.303 | 0 | 0
February | 588948000000 | 422725.222 | 27-FEB-20:10 | 177438.022 | 92719.3 | 46086.424 | 0 | 41167.042 | 11888 | 1839.901 | 0 | 48888.791 | 0 | 0 | 0 | 2697.743 | 0 | 0
March | 655979000000 | 445585.193 | 30-MAR-19:10 | 177438.022 | 92719.3 | 47841.187 | 0 | 61833.998 | 11888 | 2159.662 | 0 | 48888.791 | 0 | 0 | 0 | 2816.233 | 0 | 0
April | 722282000000 | 526837.92 | 21-APR-19:10 | 177438.022 | 92719.3 | 52911.914 | 0 | 136997.931 | 11888 | 3495.984 | 0 | 48888.791 | 0 | 0 | 0 | 2497.978 | 0 | 0
May | 804840000000 | 564524.72 | 31-MAY-19:10 | 177438.022 | 92719.3 | 55098.797 | 0 | 171542.346 | 11888 | 3805.953 | 0 | 48888.791 | 0 | 0 | 0 | 3143.512 | 0 | 0
June | 942124000000 | 694500.564 | 27-JUN-19:10 | 177438.022 | 92719.3 | 59525.431 | 0 | 296722.418 | 11888 | 4730.797 | 0 | 48888.791 | 0 | 0 | 0 | 2587.805 | 0 | 0
July | 1042620000000 | 682561.057 | 25-JUL-19:10 | 177438.022 | 92719.3 | 58801.857 | 0 | 284620.757 | 11888 | 5609.845 | 0 | 48888.791 | 0 | 0 | 0 | 2594.484 | 0 | 0
August | 1028590000000 | 650031.34 | 04-AUG-19:10 | 177438.022 | 92719.3 | 58132.141 | 0 | 251944.223 | 11888 | 6408.798 | 0 | 48888.791 | 0 | 0 | 0 | 2612.065 | 0 | 0
September | 895205000000 | 591416.573 | 01-SEP-18:10 | 157821.345 | 80166.318 | 57475.992 | 0 | 227455.141 | 11888 | 5156.741 | 0 | 48888.791 | 0 | 0 | 0 | 2564.244 | 0 | 0
October | 765452000000 | 511363.277 | 03-OCT-19:10 | 177438.022 | 92719.3 | 52950.512 | 0 | 121593.212 | 11888 | 3421.464 | 0 | 48888.791 | 0 | 0 | 0 | 2463.977 | 0 | 0
November | 644766000000 | 432375.769 | 09-NOV-20:19 | 177438.022 | 92719.3 | 46788.606 | 0 | 49913.317 | 11888 | 1973.904 | 0 | 48888.791 | 0 | 0 | 0 | 2765.829 | 0 | 0
December | 631074000000 | 416363.888 | 05-DEC-20:10 | 177438.022 | 92719.3 | 44486.861 | 0 | 36929.109 | 11888 | 1759.747 | 0 | 48888.791 | 0 | 0 | 0 | 2254.058 | 0 | 0
Annual Sum or Average | 9344700000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 588948000000 | 403884.103 |  | 157821.345 | 80166.318 | 43446.725 | 0 | 25408.414 | 11888 | 1511.549 | 0 | 48888.791 | 0 | 0 | 0 | 2254.058 | 0 | 0
Maximum of Months | 1042620000000 | 694500.564 |  | 177438.022 | 92719.3 | 59525.431 | 0 | 296722.418 | 11888 | 6408.798 | 0 | 48888.791 | 0 | 0 | 0 | 3143.512 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 239222.36 | 51261.87 | 0 | 290484.23
Cost per Total Building Area ($/m2) | 21.09 | 4.52 | 0 | 25.6
Cost per Net Conditioned Building Area ($/m2) | 21.09 | 4.52 | 0 | 25.6

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15416.47 | 1358.84 | 1358.84
Net Site Energy | 15416.47 | 1358.84 | 1358.84
Total Source Energy | 32067.83 | 2826.53 | 2826.53
Net Source Energy | 32067.83 | 2826.53 | 2826.53
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 238.77 | 0 | 0 | 0 | 0
Cooling | 865.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1285.22 | 0 | 0 | 0 | 0 | 0
Pumps | 57.89 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6333.94 | 0 | 0 | 0 | 44332.9
Refrigeration | 72.67 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7605.11 | 7811.36 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.272 | 1.571 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1601324.22 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3135999.88 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 42451.06 | 29858.19 | 12592.88 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 11691.83 | 8230.13 | 3461.69 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36679.65 | 25768.47 | 10911.18 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 10124.57 | 7120.29 | 3004.28 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 578349.13 | 385016.19 | 193332.94 | 0.67 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 66840.37 | 45577.29 | 21263.08 | 0.68 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 493229.57 | 344991.2 | 148238.36 | 0.7 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33919.65 | 23797.84 | 10121.8 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28448.21 | 19931.83 | 8516.38 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 54151.5 | 37488.63 | 16662.87 | 0.69 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3834.98 | 2606.64 | 1228.34 | 0.68 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 819568.69 | 573832.41 | 245736.28 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 122314.02 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 90715.7 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 98988.17 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 44231.95 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 17371.39 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 9381.74 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 125822.26 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 48972.85 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 152614.86 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 290280.92 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1175.2 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31964.39 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22139.03 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13192.63 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3793.16 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13068.33 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3758.04 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 767298.31 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 49548.67 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 767298.31 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12919.98 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12725.43 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2061.19 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 35365.36 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2315.59 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 90994.54 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.26 | 24.59 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.73 | 1099.65 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.48 | 303.43 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.49 | 947.6 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 262.21 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.52 | 1603.29 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 873.99 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 730.89 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 36.64 | 60956.41 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14673.92 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17268.15 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 91396.0498 | 80.2268 | 492.3195 | 0 | 0.0003 | 2969380 | 33134.3741
February | 82723.1407 | 72.5359 | 459.5368 | 0 | 0.0003 | 2771730 | 30032.6468
March | 90592.8603 | 79.4516 | 500.5456 | 0 | 0.0003 | 3019070 | 32881.4863
April | 87316.5161 | 76.5074 | 495.1053 | 0 | 0.0003 | 2986320 | 31730.94
May | 89692.3571 | 78.519 | 521.1331 | 0 | 0.0003 | 3143380 | 32632.6321
June | 86483.7253 | 75.6552 | 512.297 | 0 | 0.0003 | 3090140 | 31495.1607
July | 90227.0952 | 78.8667 | 545.7846 | 0 | 0.0003 | 3292190 | 32892.9168
August | 90115.9504 | 78.7648 | 545.9468 | 0 | 0.0003 | 3293180 | 32854.9443
September | 89324.1801 | 78.0515 | 544.9694 | 0 | 0.0003 | 3287300 | 32577.9292
October | 91227.968 | 79.7871 | 543.6813 | 0 | 0.0003 | 3279460 | 33232.9035
November | 86737.3813 | 75.9733 | 496.5841 | 0 | 0.0003 | 2995270 | 31535.0122
December | 90269.7503 | 79.2093 | 491.4005 | 0 | 0.0003 | 2963870 | 32741.7561
Annual Sum or Average | 1066110 | 933.5485 | 6149.304 | 0 | 0.0036 | 37091300 | 387742.7021
Minimum of Months | 82723.1407 | 72.5359 | 459.5368 | 0 | 0.0003 | 2771730 | 30032.6468
Maximum of Months | 91396.0498 | 80.2268 | 545.9468 | 0 | 0.0003 | 3293180 | 33232.9035
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 608834000000 | 400739.804 | 27-JAN-20:30 | 177438.022 | 92719.3 | 41938.053 | 0 | 23800.954 | 11888 | 1870.895 | 0 | 48888.791 | 0 | 0 | 0 | 2195.79 | 0 | 0
February | 568310000000 | 425682.045 | 15-FEB-20:10 | 177438.022 | 92719.3 | 44473.746 | 0 | 45102.726 | 11888 | 2389.043 | 0 | 48888.791 | 0 | 0 | 0 | 2782.417 | 0 | 0
March | 619022000000 | 406251.781 | 30-MAR-19:49 | 177438.022 | 92719.3 | 42860.723 | 0 | 27895.885 | 11888 | 1879.129 | 0 | 48888.791 | 0 | 0 | 0 | 2681.931 | 0 | 0
April | 612309000000 | 428557.55 | 13-APR-19:19 | 177438.022 | 92719.3 | 45509.589 | 0 | 47417.21 | 11888 | 1941.184 | 0 | 48888.791 | 0 | 0 | 0 | 2755.455 | 0 | 0
May | 644512000000 | 433685.376 | 25-MAY-19:19 | 177438.022 | 92719.3 | 45119.394 | 0 | 52377.019 | 11888 | 2431.469 | 0 | 48888.791 | 0 | 0 | 0 | 2823.381 | 0 | 0
June | 633595000000 | 442687.221 | 16-JUN-19:30 | 177438.022 | 92719.3 | 46822.638 | 0 | 59644.85 | 11888 | 2935.344 | 0 | 48888.791 | 0 | 0 | 0 | 2350.277 | 0 | 0
July | 675023000000 | 494319.335 | 02-JUL-19:30 | 167588.533 | 91473.541 | 48731.796 | 0 | 118920.367 | 11888 | 3775.662 | 0 | 48888.791 | 0 | 0 | 0 | 3052.645 | 0 | 0
August | 675225000000 | 437055.799 | 14-AUG-19:10 | 177438.022 | 92719.3 | 46284.004 | 0 | 54424.666 | 11888 | 2592.288 | 0 | 48888.791 | 0 | 0 | 0 | 2820.728 | 0 | 0
September | 674020000000 | 494781.495 | 28-SEP-19:00 | 177438.022 | 92719.3 | 49540.183 | 0 | 107837.539 | 11888 | 3442.71 | 0 | 48888.791 | 0 | 0 | 0 | 3026.951 | 0 | 0
October | 672414000000 | 447208.273 | 16-OCT-19:10 | 177438.022 | 92719.3 | 45802.573 | 0 | 64788.108 | 11888 | 2794.597 | 0 | 48888.791 | 0 | 0 | 0 | 2888.881 | 0 | 0
November | 614143000000 | 414880.348 | 15-NOV-20:00 | 177438.022 | 92719.3 | 43118.087 | 0 | 35980.114 | 11888 | 2093.197 | 0 | 48888.791 | 0 | 0 | 0 | 2754.838 | 0 | 0
December | 607704000000 | 399238.328 | 01-DEC-20:10 | 177438.022 | 92719.3 | 41451.285 | 0 | 22793.741 | 11888 | 1821.165 | 0 | 48888.791 | 0 | 0 | 0 | 2238.023 | 0 | 0
Annual Sum or Average | 7605110000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 568310000000 | 399238.328 |  | 167588.533 | 91473.541 | 41451.285 | 0 | 22793.741 | 11888 | 1821.165 | 0 | 48888.791 | 0 | 0 | 0 | 2195.79 | 0 | 0
Maximum of Months | 675225000000 | 494781.495 |  | 177438.022 | 92719.3 | 49540.183 | 0 | 118920.367 | 11888 | 3775.662 | 0 | 48888.791 | 0 | 0 | 0 | 3052.645 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 305506.84 | 65647.71 | 0 | 371154.55
Cost per Total Building Area ($/m2) | 26.93 | 5.79 | 0 | 32.71
Cost per Net Conditioned Building Area ($/m2) | 26.93 | 5.79 | 0 | 32.71

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16878.71 | 1487.73 | 1487.73
Net Site Energy | 16878.71 | 1487.73 | 1487.73
Total Source Energy | 39183.14 | 3453.69 | 3453.69
Net Source Energy | 39183.14 | 3453.69 | 3453.69
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.17 | 831.94 | 0 | 0 | 0 | 0
Cooling | 1574.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1304.79 | 0 | 0 | 0 | 0 | 0
Pumps | 76.75 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6454.02 | 0 | 0 | 0 | 44332.9
Refrigeration | 73.12 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8354.1 | 8524.61 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.489 | 0.539 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.011 | 1.191 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3483459.48 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 4198440.34 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 45784.55 | 31757.87 | 14026.69 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 12840.89 | 8929.83 | 3911.07 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 45163.96 | 31314.4 | 13849.55 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 12709.07 | 8835.36 | 3873.71 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 704194.17 | 442292.48 | 261901.69 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 59409.47 | 38235.53 | 21173.94 | 0.64 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 691581.86 | 436056.97 | 255524.9 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 37873.61 | 26141.84 | 11731.77 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36828.06 | 25408.77 | 11419.29 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 80860.72 | 50928.71 | 29932.02 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5333.37 | 3353.86 | 1979.51 | 0.63 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 911949.27 | 609746.36 | 302202.9 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 134936.66 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 132208.85 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 82800.4 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 43357.06 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 18553.6 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 17639.71 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 138487.53 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 57318.9 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 156041.81 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 308651.7 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1242.44 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26720.17 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23662.98 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20841.77 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6017.72 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20803.73 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6014.23 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 898860.19 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 58071.26 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 898860.19 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20389.5 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20307.33 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2050.97 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 58511.62 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3831.12 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 260344.02 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.49 | 45.33 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.81 | 1152.45 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.51 | 325.15 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.78 | 1135.83 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.51 | 321.6 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.98 | 1260.53 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.48 | 943.09 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.44 | 916.26 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 39.54 | 65780.74 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31921.08 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23118.4 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 148868.5562 | 241.927 | 590.3236 | 0 | 0.0025 | 36699.0005 | 61289.0685
February | 134489.1603 | 219.0979 | 536.279 | 0 | 0.0023 | 33339.4192 | 55418.3567
March | 147093.0634 | 245.1833 | 617.1948 | 0 | 0.0026 | 38372.2586 | 61119.6782
April | 139299.5431 | 237.5757 | 614.2165 | 0 | 0.0026 | 38189.3617 | 58373.5491
May | 152965.2172 | 268.8768 | 718.6137 | 0 | 0.003 | 44683.5361 | 64831.1285
June | 168719.579 | 305.2879 | 840.7664 | 0 | 0.0034 | 52282.2943 | 72305.4926
July | 185194.721 | 339.5533 | 947.4621 | 0 | 0.0039 | 58918.6532 | 79773.3031
August | 184250.9833 | 338.209 | 944.7654 | 0 | 0.0039 | 58751.0887 | 79402.0817
September | 154261.3511 | 277.9181 | 762.0454 | 0 | 0.0031 | 47386.6717 | 65998.861
October | 148644.7578 | 261.1613 | 697.6478 | 0 | 0.0029 | 43379.8299 | 62988.9161
November | 139451.0232 | 237.677 | 614.0171 | 0 | 0.0026 | 38176.8999 | 58422.6638
December | 145218.4492 | 238.5601 | 590.0116 | 0 | 0.0025 | 36680.7499 | 60020.8478
Annual Sum or Average | 1848460 | 3211.0273 | 8473.3435 | 0 | 0.0351 | 526859.7636 | 779943.947
Minimum of Months | 134489.1603 | 219.0979 | 536.279 | 0 | 0.0023 | 33339.4192 | 55418.3567
Maximum of Months | 185194.721 | 339.5533 | 947.4621 | 0 | 0.0039 | 58918.6532 | 79773.3031
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 581914000000 | 390015.428 | 05-JAN-20:00 | 177438.022 | 92719.3 | 39571.329 | 0 | 15602.737 | 11888 | 1398.723 | 0 | 48888.791 | 0 | 0 | 0 | 2508.525 | 0 | 0
February | 528643000000 | 393106.817 | 15-FEB-20:30 | 177438.022 | 92719.3 | 40733.007 | 0 | 17473.755 | 11888 | 1395.043 | 0 | 48888.791 | 0 | 0 | 0 | 2570.9 | 0 | 0
March | 608446000000 | 443261.199 | 09-MAR-20:00 | 177438.022 | 92719.3 | 43729.48 | 0 | 63020.205 | 11888 | 2643.095 | 0 | 48888.791 | 0 | 0 | 0 | 2934.306 | 0 | 0
April | 605546000000 | 454086.844 | 05-APR-19:10 | 177438.022 | 92719.3 | 46667.143 | 0 | 70429.575 | 11888 | 3154.822 | 0 | 48888.791 | 0 | 0 | 0 | 2901.191 | 0 | 0
May | 708520000000 | 522143.661 | 15-MAY-19:10 | 177438.022 | 92719.3 | 48393.411 | 0 | 135202.747 | 11888 | 4633.428 | 0 | 48888.791 | 0 | 0 | 0 | 2979.962 | 0 | 0
June | 829009000000 | 640626.736 | 30-JUN-18:10 | 157821.345 | 80166.318 | 53393.537 | 0 | 291101.196 | 0 | 6689.287 | 0 | 48888.791 | 0 | 0 | 0 | 2566.262 | 0 | 0
July | 934238000000 | 671428.717 | 24-JUL-19:30 | 177438.022 | 92719.3 | 52537.715 | 0 | 277971.594 | 11888 | 6854.275 | 0 | 48888.791 | 0 | 0 | 0 | 3131.02 | 0 | 0
August | 931581000000 | 673757.215 | 17-AUG-19:10 | 177438.022 | 92719.3 | 52792.525 | 0 | 279945.689 | 11888 | 6955.497 | 0 | 48888.791 | 0 | 0 | 0 | 3129.39 | 0 | 0
September | 751382000000 | 518919.868 | 09-SEP-17:10 | 134570.663 | 86260.044 | 51544.052 | 0 | 177908.552 | 0 | 5081.812 | 0 | 61110.989 | 0 | 0 | 0 | 2443.756 | 0 | 0
October | 687848000000 | 507599.033 | 20-OCT-19:40 | 177438.022 | 92719.3 | 47800.431 | 0 | 121870.885 | 11888 | 4525.915 | 0 | 48888.791 | 0 | 0 | 0 | 2467.688 | 0 | 0
November | 605348000000 | 456912.434 | 03-NOV-19:10 | 177438.022 | 92719.3 | 45398.223 | 0 | 75365.754 | 11888 | 2827.83 | 0 | 48888.791 | 0 | 0 | 0 | 2386.515 | 0 | 0
December | 581625000000 | 386816.667 | 06-DEC-20:00 | 177438.022 | 92719.3 | 38893.691 | 0 | 13133.17 | 11888 | 1364.398 | 0 | 48888.791 | 0 | 0 | 0 | 2491.295 | 0 | 0
Annual Sum or Average | 8354100000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 528643000000 | 386816.667 |  | 134570.663 | 80166.318 | 38893.691 | 0 | 13133.17 | 0 | 1364.398 | 0 | 48888.791 | 0 | 0 | 0 | 2386.515 | 0 | 0
Maximum of Months | 934238000000 | 673757.215 |  | 177438.022 | 92719.3 | 53393.537 | 0 | 291101.196 | 11888 | 6955.497 | 0 | 61110.989 | 0 | 0 | 0 | 3131.02 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 164529.94 | 85901.3 | 0 | 250431.24
Cost per Total Building Area ($/m2) | 14.5 | 7.57 | 0 | 22.07
Cost per Net Conditioned Building Area ($/m2) | 14.5 | 7.57 | 0 | 22.07

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16499.92 | 1454.34 | 1454.34
Net Site Energy | 16499.92 | 1454.34 | 1454.34
Total Source Energy | 36498.25 | 3217.04 | 3217.04
Net Source Energy | 36498.25 | 3217.04 | 3217.04
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 648.72 | 0 | 0 | 0 | 0
Cooling | 1424.64 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1408.08 | 0 | 0 | 0 | 0 | 0
Pumps | 72.04 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6310.52 | 0 | 0 | 0 | 44332.9
Refrigeration | 73.11 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8302.04 | 8197.89 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.506 | 0.56 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.045 | 1.238 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1809602.34 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3438909.84 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33823.96 | 21958.47 | 11865.49 | 0.65 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9586.16 | 6232.04 | 3354.12 | 0.65 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33758.03 | 21913.32 | 11844.71 | 0.65 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9590.79 | 6234.31 | 3356.48 | 0.65 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 495030.3 | 293719.39 | 201310.91 | 0.59 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 37283.51 | 22786.99 | 14496.52 | 0.61 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 419523.26 | 256072.97 | 163450.29 | 0.61 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 26328.13 | 17017.5 | 9310.63 | 0.65 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25907.79 | 16747.69 | 9160.1 | 0.65 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 53025.76 | 32024.08 | 21001.68 | 0.6 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3664.14 | 2189.93 | 1474.21 | 0.6 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 648684.99 | 407528.06 | 241156.93 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 125214.29 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 105530.4 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 71426.7 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 38557.42 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 14954.47 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 15800.9 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 128839.13 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 54563.44 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 154063.63 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 281272.6 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 967.45 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22436 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22110.04 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18610.43 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5422 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18574.83 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5423.76 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 730040.18 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 46791.96 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 730040.18 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18064.53 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17998.51 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1696.82 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 46044.69 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3014.83 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 183931.9 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.54 | 50.8 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.99 | 1263.98 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.56 | 358.95 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.98 | 1261.6 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.56 | 359.2 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.94 | 1236.73 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.54 | 981.44 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.52 | 966.85 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 43.36 | 71832.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16582.5 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18936.1 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 207980.5187 | 324.9726 | 738.0013 | 0 | 0.003 | 767155.3214 | 85340.8872
February | 189390.4658 | 297.3441 | 679.7151 | 0 | 0.0027 | 706578.0856 | 77851.9729
March | 208933.2398 | 330.3576 | 762.4707 | 0 | 0.0031 | 792623.1838 | 86114.0042
April | 207390.7794 | 333.2369 | 785.6267 | 0 | 0.0031 | 816737.128 | 85999.9254
May | 228315.3814 | 372.6362 | 896.163 | 0 | 0.0036 | 931694.8208 | 95243.5635
June | 233726.8918 | 385.7463 | 940.558 | 0 | 0.0037 | 977881.6049 | 97920.6355
July | 253864.4218 | 422.0287 | 1038.0871 | 0 | 0.0041 | 1079300 | 106656.2016
August | 247081.6965 | 410.4875 | 1008.9149 | 0 | 0.004 | 1048970 | 103780.5347
September | 225494.5622 | 372.3677 | 908.556 | 0 | 0.0036 | 944611.1062 | 94492.0853
October | 214109.863 | 348.2231 | 833.7576 | 0 | 0.0033 | 866806.0302 | 89197.154
November | 199485.8628 | 317.9449 | 741.6612 | 0 | 0.003 | 771010.8145 | 82467.8585
December | 206394.6435 | 323.7291 | 739.0552 | 0 | 0.003 | 768260.8944 | 84811.2349
Annual Sum or Average | 2622170 | 4239.0747 | 10072.5671 | 0 | 0.0401 | 10471600 | 1089880
Minimum of Months | 189390.4658 | 297.3441 | 679.7151 | 0 | 0.0027 | 706578.0856 | 77851.9729
Maximum of Months | 253864.4218 | 422.0287 | 1038.0871 | 0 | 0.0041 | 1079300 | 106656.2016
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 608210000000 | 402977.962 | 26-JAN-20:10 | 177438.022 | 92719.3 | 44355.227 | 0 | 23629.408 | 11888 | 1498.818 | 0 | 48888.791 | 0 | 0 | 0 | 2560.397 | 0 | 0
February | 560184000000 | 409275.598 | 14-FEB-20:10 | 177438.022 | 92719.3 | 46049.889 | 0 | 28555.271 | 11888 | 1552.809 | 0 | 48888.791 | 0 | 0 | 0 | 2183.517 | 0 | 0
March | 628401000000 | 423859.762 | 20-MAR-19:10 | 177438.022 | 92719.3 | 47096.633 | 0 | 41267.478 | 11888 | 1850.219 | 0 | 48888.791 | 0 | 0 | 0 | 2711.319 | 0 | 0
April | 647519000000 | 466422.754 | 21-APR-19:10 | 177438.022 | 92719.3 | 51251.62 | 0 | 79391.18 | 11888 | 2474.009 | 0 | 48888.791 | 0 | 0 | 0 | 2371.831 | 0 | 0
May | 738659000000 | 502421.787 | 30-MAY-19:10 | 177438.022 | 92719.3 | 53850.639 | 0 | 111842.428 | 11888 | 3327.663 | 0 | 48888.791 | 0 | 0 | 0 | 2466.945 | 0 | 0
June | 775276000000 | 539497.666 | 28-JUN-19:19 | 177438.022 | 92719.3 | 56837.519 | 0 | 144721.352 | 11888 | 3913.337 | 0 | 48888.791 | 0 | 0 | 0 | 3091.345 | 0 | 0
July | 855684000000 | 561608.999 | 18-JUL-19:10 | 177438.022 | 92719.3 | 57948.645 | 0 | 176411.584 | 0 | 5608.151 | 0 | 48888.791 | 0 | 0 | 0 | 2594.507 | 0 | 0
August | 831636000000 | 561169.265 | 01-AUG-19:10 | 177438.022 | 92719.3 | 57211.135 | 0 | 164694.537 | 11888 | 5800.037 | 0 | 48888.791 | 0 | 0 | 0 | 2529.443 | 0 | 0
September | 748899000000 | 496206.353 | 13-SEP-19:10 | 177438.022 | 92719.3 | 54946.352 | 0 | 103370.557 | 11888 | 3966.526 | 0 | 48888.791 | 0 | 0 | 0 | 2988.805 | 0 | 0
October | 687214000000 | 469424.795 | 02-OCT-19:10 | 177438.022 | 92719.3 | 51643.788 | 0 | 81367.684 | 11888 | 2560.481 | 0 | 48888.791 | 0 | 0 | 0 | 2918.729 | 0 | 0
November | 611267000000 | 421892.985 | 09-NOV-20:00 | 177438.022 | 92719.3 | 46456.819 | 0 | 39944.279 | 11888 | 1823.267 | 0 | 48888.791 | 0 | 0 | 0 | 2734.508 | 0 | 0
December | 609086000000 | 398721.381 | 05-DEC-20:10 | 177438.022 | 92719.3 | 43334.314 | 0 | 20847.884 | 11888 | 1467.261 | 0 | 48888.791 | 0 | 0 | 0 | 2137.809 | 0 | 0
Annual Sum or Average | 8302040000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 560184000000 | 398721.381 |  | 177438.022 | 92719.3 | 43334.314 | 0 | 20847.884 | 0 | 1467.261 | 0 | 48888.791 | 0 | 0 | 0 | 2137.809 | 0 | 0
Maximum of Months | 855684000000 | 561608.999 |  | 177438.022 | 92719.3 | 57948.645 | 0 | 176411.584 | 11888 | 5800.037 | 0 | 48888.791 | 0 | 0 | 0 | 3091.345 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 85352.47 | 58969.32 | 0 | 144321.8
Cost per Total Building Area ($/m2) | 7.52 | 5.2 | 0 | 12.72
Cost per Net Conditioned Building Area ($/m2) | 7.52 | 5.2 | 0 | 12.72

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16260.86 | 1433.27 | 1433.27
Net Site Energy | 16260.86 | 1433.27 | 1433.27
Total Source Energy | 22598.2 | 1991.86 | 1991.86
Net Source Energy | 22598.2 | 1991.86 | 1991.86
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 726.15 | 0 | 0 | 0 | 0
Cooling | 728.79 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.43 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1269.95 | 0 | 0 | 0 | 0 | 0
Pumps | 54.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6847.83 | 0 | 0 | 0 | 44332.9
Refrigeration | 71.57 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7448.23 | 8812.63 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.483 | 0.532 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.994 | 1.167 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.54 | 0.384 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.54 | 0.384 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.54 | 0.384 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.54 | 0.384 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.54 | 0.384 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.54 | 0.384 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 432.93 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1800502.71 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3681500.54 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 42966.82 | 30088.22 | 12878.6 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 11922.18 | 8356.76 | 3565.42 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 38929.75 | 27239.87 | 11689.89 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 10844.88 | 7597.06 | 3247.83 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 589846.37 | 384488.05 | 205358.32 | 0.65 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 67234.51 | 45152.12 | 22082.39 | 0.67 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 508911.94 | 345522.77 | 163389.17 | 0.68 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35666.94 | 24916.57 | 10750.37 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31311.85 | 21852.39 | 9459.47 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 56808.51 | 38238.66 | 18569.85 | 0.67 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3992.29 | 2645.62 | 1346.67 | 0.66 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 859173.17 | 593287.97 | 265885.2 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 128083.6 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 103289.39 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 98093.13 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 46311.54 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 18799.09 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 13271.33 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 131639.84 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 53863.92 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 154729.08 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 298083.47 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1159.01 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31911.29 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22842 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17251.51 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4891.93 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17082.03 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4855.07 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 834899.41 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 55257.86 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 834899.41 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16924.26 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16664.41 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2032.81 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 48342.5 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3165.28 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 180902.31 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.37 | 34.41 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.81 | 1150.88 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.5 | 320.04 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.64 | 1040.99 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.46 | 290.76 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.54 | 1617.27 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.49 | 950.79 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.31 | 833.07 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 38.65 | 64293.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16499.12 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20271.91 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 74419.6454 | 87.1142 | 125.2122 | 0 | 0.0006 | 1651950 | 27851.8572
February | 66019.7587 | 77.8723 | 114.8513 | 0 | 0.0005 | 1515410 | 24771.4389
March | 72602.8394 | 86.0152 | 128.7172 | 0 | 0.0006 | 1698460 | 27281.9789
April | 67380.631 | 80.9973 | 126.9228 | 0 | 0.0006 | 1675070 | 25444.8334
May | 67769.3469 | 83.2192 | 138.8582 | 0 | 0.0006 | 1832990 | 25779.5491
June | 64505.4639 | 80.3272 | 139.2956 | 0 | 0.0006 | 1839000 | 24657.4818
July | 66938.3186 | 84.5364 | 152.0808 | 0 | 0.0007 | 2008030 | 25713.7864
August | 66884.0976 | 84.6824 | 153.3274 | 0 | 0.0007 | 2024530 | 25715.9359
September | 64101.3587 | 80.3192 | 141.5853 | 0 | 0.0006 | 1869330 | 24556.0566
October | 65870.5074 | 80.6728 | 133.5968 | 0 | 0.0006 | 1763490 | 25034.2351
November | 67398.8748 | 80.3354 | 122.5912 | 0 | 0.0006 | 1617740 | 25378.486
December | 73208.8835 | 85.8977 | 124.457 | 0 | 0.0006 | 1642040 | 27420.2274
Annual Sum or Average | 817099.726 | 991.9894 | 1601.4958 | 0 | 0.0072 | 21138100 | 309605.8668
Minimum of Months | 64101.3587 | 77.8723 | 114.8513 | 0 | 0.0005 | 1515410 | 24556.0566
Maximum of Months | 74419.6454 | 87.1142 | 153.3274 | 0 | 0.0007 | 2024530 | 27851.8572
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 582083000000 | 388517.096 | 27-JAN-20:00 | 177438.022 | 92719.3 | 39655.22 | 0 | 14180.912 | 11888 | 1563.738 | 0 | 48888.791 | 0 | 0 | 0 | 2183.113 | 0 | 0
February | 533972000000 | 402622.875 | 21-FEB-20:10 | 177438.022 | 92719.3 | 42290.299 | 0 | 25606.228 | 11888 | 1557.195 | 0 | 48888.791 | 0 | 0 | 0 | 2235.039 | 0 | 0
March | 598471000000 | 429180.26 | 29-MAR-19:10 | 177438.022 | 92719.3 | 45492.001 | 0 | 47216.195 | 11888 | 2757.064 | 0 | 48888.791 | 0 | 0 | 0 | 2780.887 | 0 | 0
April | 590229000000 | 420737.001 | 14-APR-19:10 | 177438.022 | 92719.3 | 44447.143 | 0 | 41226.675 | 11888 | 1830.451 | 0 | 48888.791 | 0 | 0 | 0 | 2298.619 | 0 | 0
May | 645875000000 | 457707.429 | 04-MAY-19:19 | 177438.022 | 92719.3 | 47753.859 | 0 | 73036.813 | 11888 | 3080.06 | 0 | 48888.791 | 0 | 0 | 0 | 2902.584 | 0 | 0
June | 647993000000 | 472863.065 | 27-JUN-19:10 | 177438.022 | 92719.3 | 50041.238 | 0 | 97848.698 | 0 | 3487.039 | 0 | 48888.791 | 0 | 0 | 0 | 2439.977 | 0 | 0
July | 707552000000 | 499490.249 | 24-JUL-19:10 | 177438.022 | 92719.3 | 51645.589 | 0 | 121732.87 | 0 | 4003.909 | 0 | 48888.791 | 0 | 0 | 0 | 3061.768 | 0 | 0
August | 713366000000 | 486033.199 | 08-AUG-19:30 | 177438.022 | 92719.3 | 50190.57 | 0 | 98761.992 | 11888 | 3683.387 | 0 | 48888.791 | 0 | 0 | 0 | 2463.137 | 0 | 0
September | 658679000000 | 535065.293 | 02-SEP-17:10 | 134570.663 | 86260.044 | 51617.362 | 0 | 194102.493 | 0 | 4901.836 | 0 | 61110.989 | 0 | 0 | 0 | 2501.907 | 0 | 0
October | 621386000000 | 429769.677 | 17-OCT-19:10 | 177438.022 | 92719.3 | 45240.905 | 0 | 48890.448 | 11888 | 2386.461 | 0 | 48888.791 | 0 | 0 | 0 | 2317.75 | 0 | 0
November | 570030000000 | 399409.155 | 03-NOV-19:00 | 177438.022 | 92719.3 | 41543.635 | 0 | 22943.183 | 11888 | 1707.705 | 0 | 48888.791 | 0 | 0 | 0 | 2280.519 | 0 | 0
December | 578591000000 | 386606.998 | 28-DEC-20:00 | 177438.022 | 92719.3 | 39163.024 | 0 | 12456.93 | 11888 | 1486.044 | 0 | 48888.791 | 0 | 0 | 0 | 2566.887 | 0 | 0
Annual Sum or Average | 7448230000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 533972000000 | 386606.998 |  | 134570.663 | 86260.044 | 39163.024 | 0 | 12456.93 | 0 | 1486.044 | 0 | 48888.791 | 0 | 0 | 0 | 2183.113 | 0 | 0
Maximum of Months | 713366000000 | 535065.293 |  | 177438.022 | 92719.3 | 51645.589 | 0 | 194102.493 | 11888 | 4901.836 | 0 | 61110.989 | 0 | 0 | 0 | 3061.768 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 140418.51 | 73025.72 | 0 | 213444.23
Cost per Total Building Area ($/m2) | 12.38 | 6.44 | 0 | 18.81
Cost per Net Conditioned Building Area ($/m2) | 12.38 | 6.44 | 0 | 18.81

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17408.47 | 1534.42 | 1534.42
Net Site Energy | 17408.47 | 1534.42 | 1534.42
Total Source Energy | 38327.65 | 3378.29 | 3378.29
Net Source Energy | 38327.65 | 3378.29 | 3378.29
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.42 | 1179.42 | 0 | 0 | 0 | 0
Cooling | 1168.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1240.63 | 0 | 0 | 0 | 0 | 0
Pumps | 65.42 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7118.51 | 0 | 0 | 0 | 44332.9
Refrigeration | 72.2 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7871.88 | 9536.59 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.4 | 0.433 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.886 | 1.021 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.525 | 0.407 | 0.316 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.525 | 0.407 | 0.316 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.525 | 0.407 | 0.316 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 432.93 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 781.15 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3214441.33 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 4766534.93 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 34858.97 | 24101.61 | 10757.37 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9612.07 | 6662.23 | 2949.84 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 34317.15 | 23717.43 | 10599.72 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9493.99 | 6578.42 | 2915.56 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 677490.23 | 425361.55 | 252128.69 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 46860.92 | 29435.68 | 17425.24 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 677490.23 | 425361.55 | 252128.69 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28508.87 | 19616.3 | 8892.57 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28263.91 | 19443.03 | 8820.87 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 78559.42 | 49359.77 | 29199.65 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5265.04 | 3290.92 | 1974.12 | 0.63 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 811601.47 | 541569.05 | 270032.41 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 135737.02 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 125985.42 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63006.68 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 38335.33 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15085.51 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 20052.57 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 139299.62 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 56399.74 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 156122.5 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 306500 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1707.58 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20170.99 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23472.36 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 21512.8 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6187.7 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 21489.81 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6188.3 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 952901.87 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 57423.08 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 952901.87 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 21127.21 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 21111.01 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2016.46 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 69468.24 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4548.52 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 368831.47 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.54 | 50.26 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.43 | 913.24 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.4 | 253.17 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.41 | 898.27 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 249.9 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.42 | 902.45 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.16 | 740.81 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 734.09 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 38.67 | 64332.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29455.91 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26246.57 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 253529.6057 | 410.1456 | 1080.1987 | 0 | 0.0034 | 248607.1747 | 104958.4148
February | 229031.7268 | 371.1605 | 979.6958 | 0 | 0.0031 | 225477.5676 | 94878.3512
March | 253152.3318 | 413.3052 | 1101.1912 | 0 | 0.0034 | 253444.8704 | 105162.6761
April | 243631.8033 | 404.7197 | 1101.4894 | 0 | 0.0034 | 253524.8717 | 101872.993
May | 268099.1251 | 453.6904 | 1262.0196 | 0 | 0.0039 | 290486.4637 | 112899.8648
June | 290450.3104 | 498.9986 | 1412.1001 | 0 | 0.0043 | 325042.6693 | 123027.8154
July | 322134.1981 | 557.9568 | 1593.264 | 0 | 0.0049 | 366750.2983 | 136880.9642
August | 310475.9313 | 537.4402 | 1533.6622 | 0 | 0.0047 | 353030.2128 | 131896.1961
September | 270611.7018 | 464.7894 | 1314.8936 | 0 | 0.004 | 302667.125 | 114612.5989
October | 254789.394 | 430.8974 | 1197.7505 | 0 | 0.0037 | 275692.8686 | 107269.1929
November | 240686.5473 | 398.8782 | 1082.4852 | 0 | 0.0034 | 249149.2572 | 100550.7294
December | 250086.1466 | 406.9846 | 1079.9723 | 0 | 0.0034 | 248559.078 | 103763.2447
Annual Sum or Average | 3186680 | 5348.9667 | 14738.7225 | 0 | 0.0454 | 3392430 | 1337770
Minimum of Months | 229031.7268 | 371.1605 | 979.6958 | 0 | 0.0031 | 225477.5676 | 94878.3512
Maximum of Months | 322134.1981 | 557.9568 | 1593.264 | 0 | 0.0049 | 366750.2983 | 136880.9642
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 576874000000 | 391720.986 | 17-JAN-20:00 | 177438.022 | 92719.3 | 39301.109 | 0 | 17910.432 | 11888 | 1426.575 | 0 | 48888.791 | 0 | 0 | 0 | 2148.758 | 0 | 0
February | 523204000000 | 390781.849 | 27-FEB-20:00 | 177438.022 | 92719.3 | 38992.941 | 0 | 16895.56 | 11888 | 1395.359 | 0 | 48888.791 | 0 | 0 | 0 | 2563.877 | 0 | 0
March | 588100000000 | 420368.412 | 31-MAR-19:10 | 177438.022 | 92719.3 | 42558.19 | 0 | 42678.02 | 11888 | 1876.108 | 0 | 48888.791 | 0 | 0 | 0 | 2321.981 | 0 | 0
April | 588285000000 | 416285.042 | 28-APR-19:00 | 177438.022 | 92719.3 | 43655.697 | 0 | 37639.845 | 11888 | 1785.893 | 0 | 48888.791 | 0 | 0 | 0 | 2269.495 | 0 | 0
May | 674052000000 | 476372.484 | 30-MAY-19:19 | 177438.022 | 92719.3 | 46316.66 | 0 | 92716.571 | 11888 | 3952.739 | 0 | 48888.791 | 0 | 0 | 0 | 2452.402 | 0 | 0
June | 754237000000 | 543174.762 | 16-JUN-19:30 | 177438.022 | 92719.3 | 50073.657 | 0 | 154830.996 | 11888 | 4797.132 | 0 | 48888.791 | 0 | 0 | 0 | 2538.864 | 0 | 0
July | 851016000000 | 596713.41 | 14-JUL-19:30 | 177438.022 | 92719.3 | 50266.858 | 0 | 207014.557 | 11888 | 5974.994 | 0 | 48888.791 | 0 | 0 | 0 | 2522.888 | 0 | 0
August | 819180000000 | 635008.414 | 04-AUG-19:10 | 177438.022 | 92719.3 | 50276.511 | 0 | 244610.307 | 11888 | 6646.874 | 0 | 48888.791 | 0 | 0 | 0 | 2540.608 | 0 | 0
September | 702316000000 | 522254.879 | 06-SEP-19:10 | 177438.022 | 92719.3 | 48371.259 | 0 | 135812.345 | 11888 | 4175.343 | 0 | 48888.791 | 0 | 0 | 0 | 2961.819 | 0 | 0
October | 639725000000 | 454822.706 | 30-OCT-19:19 | 177438.022 | 92719.3 | 44207.161 | 0 | 73993.665 | 11888 | 2814.203 | 0 | 48888.791 | 0 | 0 | 0 | 2873.565 | 0 | 0
November | 578132000000 | 451776.443 | 02-NOV-19:00 | 177438.022 | 92719.3 | 44155.133 | 0 | 70973.22 | 11888 | 2777.311 | 0 | 48888.791 | 0 | 0 | 0 | 2936.666 | 0 | 0
December | 576763000000 | 392153.08 | 11-DEC-20:00 | 177438.022 | 92719.3 | 39164.831 | 0 | 18073.518 | 11888 | 1411.285 | 0 | 48888.791 | 0 | 0 | 0 | 2569.334 | 0 | 0
Annual Sum or Average | 7871880000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 523204000000 | 390781.849 |  | 177438.022 | 92719.3 | 38992.941 | 0 | 16895.56 | 11888 | 1395.359 | 0 | 48888.791 | 0 | 0 | 0 | 2148.758 | 0 | 0
Maximum of Months | 851016000000 | 635008.414 |  | 177438.022 | 92719.3 | 50276.511 | 0 | 244610.307 | 11888 | 6646.874 | 0 | 48888.791 | 0 | 0 | 0 | 2961.819 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 207453.4 | 85155.26 | 0 | 292608.66
Cost per Total Building Area ($/m2) | 18.29 | 7.51 | 0 | 25.79
Cost per Net Conditioned Building Area ($/m2) | 18.29 | 7.51 | 0 | 25.79

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17055.36 | 1503.3 | 1503.3
Net Site Energy | 17055.36 | 1503.3 | 1503.3
Total Source Energy | 35917.82 | 3165.88 | 3165.88
Net Source Energy | 35917.82 | 3165.88 | 3165.88
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.05 | 964.08 | 0 | 0 | 0 | 0
Cooling | 1009.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.65 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1303.95 | 0 | 0 | 0 | 0 | 0
Pumps | 57.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7083.82 | 0 | 0 | 0 | 44332.9
Refrigeration | 71.87 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7768.81 | 9286.55 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.422 | 0.459 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.914 | 1.059 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.525 | 0.407 | 0.316 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.525 | 0.407 | 0.316 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.525 | 0.407 | 0.316 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 432.93 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 781.15 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1544286.97 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 3963802.62 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 26396.18 | 16838.85 | 9557.33 | 0.64 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7317.51 | 4674.8 | 2642.71 | 0.64 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 26005.92 | 16586.44 | 9419.48 | 0.64 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7227.41 | 4616.3 | 2611.11 | 0.64 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 474406.98 | 288058.67 | 186348.31 | 0.61 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 33634.75 | 19975.52 | 13659.23 | 0.59 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 474406.98 | 288058.67 | 186348.31 | 0.61 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 20400.02 | 12955.85 | 7444.17 | 0.64 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 20197.11 | 12824.74 | 7372.37 | 0.63 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 54606.36 | 33268.1 | 21338.26 | 0.61 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3538.56 | 2097.14 | 1441.42 | 0.59 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 833274.4 | 522914.98 | 310359.42 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 125657.04 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 103930.71 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56751.22 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 34012.99 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 14380.65 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 18387.63 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 129273.74 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 53522.05 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 154060.89 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 279924 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1424.09 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17203.13 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21954.11 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19246.85 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5618.52 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19253.54 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5623.5 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 789447.48 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 47843.26 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 789447.48 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18780.89 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18787.31 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1693.7 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 56417.29 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3693.99 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 283786.57 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.61 | 57.04 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.54 | 977.26 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.43 | 271.41 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.51 | 962.56 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.42 | 268.07 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.45 | 925.08 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.19 | 756.46 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.18 | 748.85 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 42.13 | 69786.09 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14151.25 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21826.38 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 209566.3306 | 324.0439 | 725.1901 | 0 | 0.0029 | 753810.193 | 85657.4423
February | 189645.8106 | 293.5253 | 657.7923 | 0 | 0.0027 | 683754.8843 | 77543.0288
March | 210187.4823 | 327.4612 | 740.6372 | 0 | 0.003 | 769887.4743 | 86152.319
April | 203120.7506 | 321.1475 | 741.1528 | 0 | 0.003 | 770462.0438 | 83716.4029
May | 212718.8186 | 340.8135 | 800.4814 | 0 | 0.0032 | 832172.5287 | 88112.7634
June | 214416.6824 | 348.0925 | 831.5445 | 0 | 0.0033 | 864500.4524 | 89263.2123
July | 239133.5658 | 392.6252 | 951.25 | 0 | 0.0038 | 988983.1297 | 99985.243
August | 230846.2345 | 378.6471 | 916.2737 | 0 | 0.0036 | 952616.7488 | 96483.7603
September | 212053.9254 | 345.2811 | 827.926 | 0 | 0.0033 | 860746.2683 | 88380.0654
October | 210173.6917 | 337.5031 | 795.057 | 0 | 0.0032 | 826539.294 | 87133.7832
November | 198747.8472 | 312.6929 | 716.8574 | 0 | 0.0029 | 745193.6645 | 81762.9741
December | 207291.3871 | 321.3713 | 721.8917 | 0 | 0.0029 | 750388.6971 | 84810.4808
Annual Sum or Average | 2537900 | 4043.2045 | 9426.0543 | 0 | 0.0377 | 9799060 | 1049000
Minimum of Months | 189645.8106 | 293.5253 | 657.7923 | 0 | 0.0027 | 683754.8843 | 77543.0288
Maximum of Months | 239133.5658 | 392.6252 | 951.25 | 0 | 0.0038 | 988983.1297 | 99985.243
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 597630000000 | 401406.953 | 24-JAN-20:40 | 177438.022 | 92719.3 | 43280.228 | 0 | 23539.943 | 11888 | 1487.142 | 0 | 48888.791 | 0 | 0 | 0 | 2165.527 | 0 | 0
February | 542089000000 | 400976.332 | 10-FEB-20:00 | 177438.022 | 92719.3 | 42947.705 | 0 | 23441.421 | 11888 | 1493.088 | 0 | 48888.791 | 0 | 0 | 0 | 2160.006 | 0 | 0
March | 610376000000 | 427874.471 | 30-MAR-19:10 | 177438.022 | 92719.3 | 46404.756 | 0 | 45873.638 | 11888 | 1914.524 | 0 | 48888.791 | 0 | 0 | 0 | 2747.44 | 0 | 0
April | 610832000000 | 448432.646 | 26-APR-19:10 | 177438.022 | 92719.3 | 47884.675 | 0 | 64611.04 | 11888 | 2157.942 | 0 | 48888.791 | 0 | 0 | 0 | 2844.877 | 0 | 0
May | 659756000000 | 478660.322 | 23-MAY-19:19 | 177438.022 | 92719.3 | 50511.239 | 0 | 91984.973 | 11888 | 2787.075 | 0 | 48888.791 | 0 | 0 | 0 | 2442.922 | 0 | 0
June | 685386000000 | 493140.687 | 27-JUN-19:30 | 177438.022 | 92719.3 | 52463.19 | 0 | 103758.549 | 11888 | 3519.792 | 0 | 48888.791 | 0 | 0 | 0 | 2465.042 | 0 | 0
July | 784078000000 | 526458.074 | 17-JUL-19:30 | 177438.022 | 92719.3 | 54375.391 | 0 | 134133.543 | 11888 | 3906.263 | 0 | 48888.791 | 0 | 0 | 0 | 3108.764 | 0 | 0
August | 755246000000 | 508113.66 | 29-AUG-19:10 | 177438.022 | 92719.3 | 53905.218 | 0 | 116765.941 | 11888 | 4004.661 | 0 | 48888.791 | 0 | 0 | 0 | 2503.728 | 0 | 0
September | 682410000000 | 484705.364 | 01-SEP-19:10 | 177438.022 | 92719.3 | 51649.731 | 0 | 96208.752 | 11888 | 3463.871 | 0 | 48888.791 | 0 | 0 | 0 | 2448.897 | 0 | 0
October | 655290000000 | 439418.468 | 01-OCT-19:10 | 167588.533 | 91473.541 | 47676.155 | 0 | 65633.439 | 11888 | 3440.241 | 0 | 48888.791 | 0 | 0 | 0 | 2829.768 | 0 | 0
November | 590799000000 | 406683.229 | 03-NOV-19:19 | 177438.022 | 92719.3 | 43704.813 | 0 | 28236.872 | 11888 | 1595.332 | 0 | 48888.791 | 0 | 0 | 0 | 2212.099 | 0 | 0
December | 594917000000 | 396281.589 | 22-DEC-20:00 | 177438.022 | 92719.3 | 41761.842 | 0 | 20008.432 | 11888 | 1480.63 | 0 | 48888.791 | 0 | 0 | 0 | 2096.573 | 0 | 0
Annual Sum or Average | 7768810000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 542089000000 | 396281.589 |  | 167588.533 | 91473.541 | 41761.842 | 0 | 20008.432 | 11888 | 1480.63 | 0 | 48888.791 | 0 | 0 | 0 | 2096.573 | 0 | 0
Maximum of Months | 784078000000 | 526458.074 |  | 177438.022 | 92719.3 | 54375.391 | 0 | 134133.543 | 11888 | 4004.661 | 0 | 48888.791 | 0 | 0 | 0 | 3108.764 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 79882.78 | 66861.45 | 0 | 146744.24
Cost per Total Building Area ($/m2) | 7.04 | 5.89 | 0 | 12.93
Cost per Net Conditioned Building Area ($/m2) | 7.04 | 5.89 | 0 | 12.93

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18249.31 | 1608.54 | 1608.54
Net Site Energy | 18249.31 | 1608.54 | 1608.54
Total Source Energy | 38165.4 | 3363.99 | 3363.99
Net Source Energy | 38165.4 | 3363.99 | 3363.99
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 3.72 | 1540.98 | 0 | 0 | 0 | 0
Cooling | 1078.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1235.44 | 0 | 0 | 0 | 0 | 0
Pumps | 63.45 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7692.65 | 0 | 0 | 0 | 44332.9
Refrigeration | 71.71 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7777.03 | 10472.28 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.525 | 0.407 | 0.316 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.525 | 0.407 | 0.316 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.525 | 0.407 | 0.316 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 432.93 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 781.15 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3179201.28 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 5109291.11 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 34315.66 | 23406.44 | 10909.23 | 0.68 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9198.98 | 6285.1 | 2913.89 | 0.68 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33595.47 | 22903.71 | 10691.75 | 0.68 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9038 | 6173 | 2865 | 0.68 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 690165.47 | 426199.41 | 263966.05 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 47080.98 | 29271.94 | 17809.04 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 670916.42 | 416855.26 | 254061.16 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28395.47 | 19277.2 | 9118.27 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28069.06 | 19053.1 | 9015.97 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 78859.94 | 48886.37 | 29973.57 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5219.28 | 3228.01 | 1991.27 | 0.62 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 814349.32 | 536261.77 | 278087.55 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 136638.56 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 123864.29 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63881.73 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 38173.22 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15616.21 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 21226.4 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 140157.84 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 56066.77 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 156174.14 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 305907.11 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1986.01 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20149.64 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23398.75 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 23321.78 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6586.42 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 23268.17 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6584.63 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 978860.92 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 59506.28 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 978860.92 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 22909.36 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 22870.64 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2000.94 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 74682.8 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4889.94 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 423362.52 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.56 | 52.43 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.43 | 911.39 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 245.21 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.4 | 891.31 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.38 | 240.76 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.44 | 916.4 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.17 | 747.8 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.16 | 739.14 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 38.89 | 64708.51 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29132.98 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28133.93 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 189430.0491 | 286.771 | 374.76 | 0 | 0.0029 | 246129.5072 | 76537.7425
February | 170751.7411 | 259.4147 | 340.8036 | 0 | 0.0026 | 223833.2599 | 69078.8655
March | 185230.1759 | 286.2811 | 385.5585 | 0 | 0.0029 | 253254.3027 | 75401.7242
April | 176573.6271 | 279.9634 | 390.533 | 0 | 0.0029 | 256559.2141 | 72552.8785
May | 192392.9287 | 313.5239 | 453.1283 | 0 | 0.0034 | 297723.2434 | 79863.3491
June | 199844.4728 | 332.2424 | 492.0889 | 0 | 0.0037 | 323352.7573 | 83585.0485
July | 214024.0382 | 359.6517 | 539.4938 | 0 | 0.004 | 354519.7421 | 89882.2991
August | 209872.2559 | 353.1211 | 530.481 | 0 | 0.0039 | 348599.1161 | 88181.3474
September | 178578.7089 | 296.0053 | 436.8507 | 0 | 0.0033 | 287051.6454 | 74606.2565
October | 176194.0909 | 285.1164 | 408.4319 | 0 | 0.0031 | 268346.5717 | 72947.0071
November | 172856.1889 | 271.5435 | 374.0867 | 0 | 0.0028 | 245742.311 | 70783.9797
December | 184583.4071 | 282.5179 | 375.2138 | 0 | 0.0029 | 246444.7549 | 74874.2895
Annual Sum or Average | 2250330 | 3606.1525 | 5101.4302 | 0 | 0.0383 | 3351560 | 928294.7876
Minimum of Months | 170751.7411 | 259.4147 | 340.8036 | 0 | 0.0026 | 223833.2599 | 69078.8655
Maximum of Months | 214024.0382 | 359.6517 | 539.4938 | 0 | 0.004 | 354519.7421 | 89882.2991
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 571125000000 | 385946.425 | 30-JAN-20:00 | 177438.022 | 92719.3 | 37715.255 | 0 | 13432.381 | 11888 | 1369.093 | 0 | 48888.791 | 0 | 0 | 0 | 2495.583 | 0 | 0
February | 519388000000 | 387713.614 | 27-FEB-20:00 | 177438.022 | 92719.3 | 38306.996 | 0 | 14575.002 | 11888 | 1376.13 | 0 | 48888.791 | 0 | 0 | 0 | 2521.372 | 0 | 0
March | 587658000000 | 402904.378 | 23-MAR-19:00 | 177438.022 | 92719.3 | 41872.503 | 0 | 25901.668 | 11888 | 1551.211 | 0 | 48888.791 | 0 | 0 | 0 | 2644.883 | 0 | 0
April | 595326000000 | 434272.46 | 02-APR-19:00 | 167588.533 | 91473.541 | 42458.553 | 0 | 66471.949 | 11888 | 2662.867 | 0 | 48888.791 | 0 | 0 | 0 | 2840.226 | 0 | 0
May | 690844000000 | 542652.143 | 27-MAY-17:19 | 134570.663 | 86260.044 | 47706.55 | 0 | 205438.476 | 0 | 5066.86 | 0 | 61110.989 | 0 | 0 | 0 | 2498.562 | 0 | 0
June | 750316000000 | 584700.348 | 29-JUN-19:10 | 177438.022 | 92719.3 | 50614.035 | 0 | 206116.04 | 0 | 5816.005 | 0 | 48888.791 | 0 | 0 | 0 | 3108.155 | 0 | 0
July | 822636000000 | 610730.47 | 13-JUL-19:10 | 177438.022 | 92719.3 | 49699.738 | 0 | 232723.909 | 0 | 6123.2 | 0 | 48888.791 | 0 | 0 | 0 | 3137.511 | 0 | 0
August | 808898000000 | 609334.712 | 25-AUG-19:10 | 177438.022 | 92719.3 | 49965.538 | 0 | 219723.041 | 11888 | 6184.011 | 0 | 48888.791 | 0 | 0 | 0 | 2528.009 | 0 | 0
September | 666082000000 | 491736.688 | 13-SEP-19:10 | 177438.022 | 92719.3 | 47377.928 | 0 | 106193.93 | 11888 | 4246.28 | 0 | 48888.791 | 0 | 0 | 0 | 2984.437 | 0 | 0
October | 622678000000 | 442279.31 | 08-OCT-19:10 | 167588.533 | 91473.541 | 44750.349 | 0 | 71970.804 | 11888 | 2872.667 | 0 | 48888.791 | 0 | 0 | 0 | 2846.624 | 0 | 0
November | 570227000000 | 405988.727 | 02-NOV-19:19 | 177438.022 | 92719.3 | 42388.863 | 0 | 27983.879 | 11888 | 2020.819 | 0 | 48888.791 | 0 | 0 | 0 | 2661.054 | 0 | 0
December | 571856000000 | 385817.12 | 01-DEC-20:00 | 177438.022 | 92719.3 | 37764.327 | 0 | 13665.947 | 11888 | 1380.241 | 0 | 48888.791 | 0 | 0 | 0 | 2072.492 | 0 | 0
Annual Sum or Average | 7777030000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 519388000000 | 385817.12 |  | 134570.663 | 86260.044 | 37715.255 | 0 | 13432.381 | 0 | 1369.093 | 0 | 48888.791 | 0 | 0 | 0 | 2072.492 | 0 | 0
Maximum of Months | 822636000000 | 610730.47 |  | 177438.022 | 92719.3 | 50614.035 | 0 | 232723.909 | 11888 | 6184.011 | 0 | 61110.989 | 0 | 0 | 0 | 3137.511 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 122153.32 | 83622.32 | 0 | 205775.64
Cost per Total Building Area ($/m2) | 10.77 | 7.37 | 0 | 18.14
Cost per Net Conditioned Building Area ($/m2) | 10.77 | 7.37 | 0 | 18.14

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17917.66 | 1579.3 | 1579.3
Net Site Energy | 17917.66 | 1579.3 | 1579.3
Total Source Energy | 37420.68 | 3298.35 | 3298.35
Net Source Energy | 37420.68 | 3298.35 | 3298.35
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.91 | 1392.77 | 0 | 0 | 0 | 0
Cooling | 775.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.59 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1261.27 | 0 | 0 | 0 | 0 | 0
Pumps | 54.49 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7796.9 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7489.34 | 10428.32 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.823 | 0.939 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.525 | 0.407 | 0.316 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.525 | 0.407 | 0.316 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.525 | 0.407 | 0.316 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 432.93 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 781.15 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1457534.08 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 4693556.56 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27853.52 | 18386.02 | 9467.5 | 0.66 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7481.02 | 4942.93 | 2538.09 | 0.66 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27054.76 | 17855.63 | 9199.13 | 0.66 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7291.93 | 4816.93 | 2475 | 0.66 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 459165.32 | 283960.82 | 175204.5 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 33071.66 | 20694.16 | 12377.5 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 317500.98 | 207223.1 | 110277.88 | 0.65 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 22172.27 | 14589.48 | 7582.79 | 0.66 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 21748.67 | 14311.46 | 7437.2 | 0.66 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 41865.84 | 26698.31 | 15167.53 | 0.64 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3074.99 | 1930.19 | 1144.8 | 0.63 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 669435.96 | 435343.77 | 234092.19 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 129432.34 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 102798.63 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 61619.29 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35404.72 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15807.61 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 21013.75 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 132962.76 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 53782.94 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 154567.01 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 285752.8 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2016.54 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19052.81 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22268.63 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 22526.3 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6408.19 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 22433.4 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6390.11 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 881855.12 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 55945.86 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 881855.12 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 22071.41 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 21989.36 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1788.55 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 67921.02 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4447.21 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 387517.4 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.64 | 59.38 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.49 | 951.59 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.4 | 256.12 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.45 | 924.27 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 249.56 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.53 | 973.27 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.19 | 756.04 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.17 | 742.11 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 40.74 | 67492.83 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13356.28 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25844.72 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 196467.8849 | 296.7693 | 429.2116 | 0 | 0.0031 | 10175000 | 79446.1351
February | 177627.7404 | 269.3022 | 391.6383 | 0 | 0.0028 | 9284490 | 71923.5435
March | 195512.0937 | 300.8075 | 446.9493 | 0 | 0.0032 | 10596600 | 79589.5531
April | 186080.4117 | 289.211 | 435.9288 | 0 | 0.0031 | 10335900 | 76031.8199
May | 192438.4998 | 304.4672 | 470.2603 | 0 | 0.0033 | 11150900 | 79149.2201
June | 194773.868 | 313.5918 | 495.6035 | 0 | 0.0035 | 11752800 | 80634.5962
July | 210412.0664 | 342.7946 | 549.9507 | 0 | 0.0039 | 13042300 | 87497.7204
August | 204154.5694 | 332.4116 | 532.9138 | 0 | 0.0038 | 12638300 | 84877.3806
September | 188650.3259 | 304.6208 | 483.2341 | 0 | 0.0034 | 11459700 | 78185.3577
October | 188462.1355 | 298.8484 | 462.975 | 0 | 0.0033 | 10978300 | 77578.7525
November | 183357.5078 | 284.5899 | 428.1429 | 0 | 0.0031 | 10151200 | 74881.6435
December | 193612.0638 | 294.6286 | 430.8316 | 0 | 0.0031 | 10213900 | 78501.3791
Annual Sum or Average | 2311550 | 3632.0428 | 5557.6398 | 0 | 0.0396 | 131779000 | 948297.1017
Minimum of Months | 177627.7404 | 269.3022 | 391.6383 | 0 | 0.0028 | 9284490 | 71923.5435
Maximum of Months | 210412.0664 | 342.7946 | 549.9507 | 0 | 0.0039 | 13042300 | 87497.7204
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 578271000000 | 389102.632 | 30-JAN-20:00 | 177438.022 | 92719.3 | 39098.956 | 0 | 15189.825 | 11888 | 1410.7 | 0 | 48888.791 | 0 | 0 | 0 | 2469.037 | 0 | 0
February | 527660000000 | 399732.344 | 03-FEB-20:49 | 177438.022 | 92719.3 | 42520.797 | 0 | 22638.803 | 11888 | 1474.386 | 0 | 48888.791 | 0 | 0 | 0 | 2164.245 | 0 | 0
March | 602231000000 | 420426.979 | 30-MAR-19:10 | 177438.022 | 92719.3 | 44780.492 | 0 | 40160.838 | 11888 | 1829.384 | 0 | 48888.791 | 0 | 0 | 0 | 2722.152 | 0 | 0
April | 587414000000 | 423673.728 | 06-APR-19:10 | 177438.022 | 92719.3 | 44387.107 | 0 | 43714.518 | 11888 | 1878.534 | 0 | 48888.791 | 0 | 0 | 0 | 2759.457 | 0 | 0
May | 633733000000 | 444730.075 | 25-MAY-19:00 | 177438.022 | 92719.3 | 46862.418 | 0 | 61302.036 | 11888 | 2776.16 | 0 | 48888.791 | 0 | 0 | 0 | 2855.348 | 0 | 0
June | 667942000000 | 511677.741 | 25-JUN-19:10 | 167588.533 | 91473.541 | 50634.476 | 0 | 144643.167 | 0 | 5337.997 | 0 | 48888.791 | 0 | 0 | 0 | 3111.236 | 0 | 0
July | 741228000000 | 518114.595 | 21-JUL-19:10 | 177438.022 | 92719.3 | 53135.503 | 0 | 139253.629 | 0 | 4145.678 | 0 | 48888.791 | 0 | 0 | 0 | 2533.673 | 0 | 0
August | 718263000000 | 498330.096 | 11-AUG-19:49 | 177438.022 | 92719.3 | 51515.163 | 0 | 109711.156 | 11888 | 3677.698 | 0 | 48888.791 | 0 | 0 | 0 | 2491.966 | 0 | 0
September | 651280000000 | 479422.748 | 01-SEP-19:10 | 177438.022 | 92719.3 | 49451.832 | 0 | 93612.38 | 11888 | 2971.255 | 0 | 48888.791 | 0 | 0 | 0 | 2453.168 | 0 | 0
October | 623922000000 | 432318.111 | 05-OCT-19:10 | 177438.022 | 92719.3 | 45346.768 | 0 | 51155.129 | 11888 | 2071.946 | 0 | 48888.791 | 0 | 0 | 0 | 2810.154 | 0 | 0
November | 576918000000 | 399708.908 | 21-NOV-20:19 | 177438.022 | 92719.3 | 42276.637 | 0 | 22787.37 | 11888 | 1497.004 | 0 | 48888.791 | 0 | 0 | 0 | 2213.784 | 0 | 0
December | 580478000000 | 390218.059 | 01-DEC-20:00 | 177438.022 | 92719.3 | 39831.508 | 0 | 15949.857 | 11888 | 1411.414 | 0 | 48888.791 | 0 | 0 | 0 | 2091.167 | 0 | 0
Annual Sum or Average | 7489340000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 527660000000 | 389102.632 |  | 167588.533 | 91473.541 | 39098.956 | 0 | 15189.825 | 0 | 1410.7 | 0 | 48888.791 | 0 | 0 | 0 | 2091.167 | 0 | 0
Maximum of Months | 741228000000 | 518114.595 |  | 177438.022 | 92719.3 | 53135.503 | 0 | 144643.167 | 11888 | 5337.997 | 0 | 48888.791 | 0 | 0 | 0 | 3111.236 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 149832 | 91558.04 | 0 | 241390.04
Cost per Total Building Area ($/m2) | 13.21 | 8.07 | 0 | 21.28
Cost per Net Conditioned Building Area ($/m2) | 13.21 | 8.07 | 0 | 21.28

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19116.17 | 1684.94 | 1684.94
Net Site Energy | 19116.17 | 1684.94 | 1684.94
Total Source Energy | 37974.26 | 3347.14 | 3347.14
Net Source Energy | 37974.26 | 3347.14 | 3347.14
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 7.69 | 1945.99 | 0 | 0 | 0 | 0
Cooling | 640 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1198.37 | 0 | 0 | 0 | 0 | 0
Pumps | 52.01 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 8639.67 | 0 | 0 | 0 | 44332.9
Refrigeration | 69.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7291.86 | 11824.31 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.341 | 0.365 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.772 | 0.873 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.525 | 0.407 | 0.316 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.525 | 0.407 | 0.316 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.525 | 0.407 | 0.316 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 432.93 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 781.15 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2456243.88 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 5181432.79 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30930.64 | 21218.86 | 9711.78 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8295.46 | 5699.22 | 2596.24 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30109.07 | 20643.84 | 9465.23 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8105.25 | 5566.45 | 2538.8 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 643048.34 | 399508.21 | 243540.14 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 43175.97 | 27029.87 | 16146.1 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 611116.3 | 384501.26 | 226615.05 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25116.4 | 17154.69 | 7961.7 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24718.19 | 16876.45 | 7841.73 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 72488.54 | 45383.32 | 27105.22 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4842.32 | 3016.71 | 1825.61 | 0.62 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 720927.56 | 481431.79 | 239495.77 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 132550.87 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 98008.58 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62410.34 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35795.08 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16726.96 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 22621.42 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 136113.95 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 54907.9 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 155086.28 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 293910.48 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2112.03 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18324.81 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22623.67 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 24119.55 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6845.27 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 24051.73 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6840.24 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 975135.2 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 59733.02 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 975135.2 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 23563.88 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 23511.8 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 1959.15 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 76011.74 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4976.96 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 446363.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.61 | 57.36 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.38 | 877.02 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 235.89 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.34 | 852.85 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 230.35 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.42 | 901.88 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.11 | 708.15 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.09 | 696.49 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 37.66 | 62652.75 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22508.08 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28531.17 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 192224.0385 | 288.8308 | 373.2218 | 0 | 0.0029 | 245107.2091 | 77459.2157
February | 173799.7748 | 261.5441 | 338.7423 | 0 | 0.0026 | 222465.5961 | 70072.871
March | 190075.114 | 288.6746 | 379.0547 | 0 | 0.0029 | 248955.3245 | 76886.9885
April | 179321.263 | 277.7571 | 375.2404 | 0 | 0.0028 | 246480.1013 | 73054.5457
May | 182782.0777 | 289.4426 | 403.0772 | 0 | 0.003 | 264798.303 | 75069.0384
June | 183135.4636 | 296.4141 | 424.735 | 0 | 0.0032 | 279058.2761 | 75827.0758
July | 202085.5314 | 332.2899 | 485.6301 | 0 | 0.0036 | 319092.1519 | 84170.7756
August | 193104.682 | 316.6596 | 461.2379 | 0 | 0.0034 | 303060.8806 | 80347.6567
September | 174498.5396 | 282.2324 | 404.0449 | 0 | 0.003 | 265463.5461 | 72231.6191
October | 178785.4916 | 283.8516 | 396.6662 | 0 | 0.003 | 260590.3114 | 73498.1538
November | 176268.7521 | 272.9902 | 368.7266 | 0 | 0.0028 | 242201.2316 | 71807.2622
December | 188340.8545 | 285.3456 | 373.3329 | 0 | 0.0029 | 245193.5073 | 76119.0254
Annual Sum or Average | 2214420 | 3476.0326 | 4783.7101 | 0 | 0.0362 | 3142470 | 906544.2278
Minimum of Months | 173799.7748 | 261.5441 | 338.7423 | 0 | 0.0026 | 222465.5961 | 70072.871
Maximum of Months | 202085.5314 | 332.2899 | 485.6301 | 0 | 0.0036 | 319092.1519 | 84170.7756
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 568753000000 | 381244.162 | 17-JAN-20:00 | 177438.022 | 92719.3 | 36188.788 | 0 | 10706.632 | 11888 | 1345.311 | 0 | 48888.791 | 0 | 0 | 0 | 2069.318 | 0 | 0
February | 516215000000 | 389081.193 | 22-FEB-20:00 | 177438.022 | 92719.3 | 38552.164 | 0 | 15701.818 | 11888 | 1418.729 | 0 | 48888.791 | 0 | 0 | 0 | 2474.37 | 0 | 0
March | 577682000000 | 391822.125 | 22-MAR-19:30 | 177438.022 | 92719.3 | 39760.597 | 0 | 17202.967 | 11888 | 1443.452 | 0 | 48888.791 | 0 | 0 | 0 | 2480.996 | 0 | 0
April | 571939000000 | 403870.835 | 04-APR-19:10 | 177438.022 | 92719.3 | 41789.442 | 0 | 27322.94 | 11888 | 1589.975 | 0 | 48888.791 | 0 | 0 | 0 | 2234.365 | 0 | 0
May | 614445000000 | 432941.279 | 31-MAY-19:49 | 177438.022 | 92719.3 | 45116.337 | 0 | 52003.495 | 11888 | 2100.063 | 0 | 48888.791 | 0 | 0 | 0 | 2787.271 | 0 | 0
June | 647534000000 | 515291.402 | 14-JUN-19:00 | 177438.022 | 92719.3 | 47620.032 | 0 | 129372.554 | 11888 | 4331.11 | 0 | 48888.791 | 0 | 0 | 0 | 3033.592 | 0 | 0
July | 740429000000 | 553264.693 | 06-JUL-19:10 | 177438.022 | 92719.3 | 50098.185 | 0 | 175829.546 | 0 | 5182.094 | 0 | 48888.791 | 0 | 0 | 0 | 3108.755 | 0 | 0
August | 703230000000 | 536517.201 | 13-AUG-19:19 | 167588.533 | 91473.541 | 47867.743 | 0 | 160949.189 | 11888 | 4819.746 | 0 | 48888.791 | 0 | 0 | 0 | 3041.657 | 0 | 0
September | 615988000000 | 479049.897 | 08-SEP-19:10 | 177438.022 | 92719.3 | 45587.231 | 0 | 96854.808 | 11888 | 3261.814 | 0 | 48888.791 | 0 | 0 | 0 | 2411.932 | 0 | 0
October | 604680000000 | 409370.658 | 07-OCT-19:10 | 157739.045 | 88982.023 | 42884.652 | 0 | 53614.119 | 11888 | 2601.283 | 0 | 48888.791 | 0 | 0 | 0 | 2772.746 | 0 | 0
November | 562010000000 | 396215.535 | 02-NOV-19:00 | 177438.022 | 92719.3 | 40691.496 | 0 | 20574.465 | 11888 | 1444.317 | 0 | 48888.791 | 0 | 0 | 0 | 2571.145 | 0 | 0
December | 568953000000 | 383253.016 | 01-DEC-20:00 | 177438.022 | 92719.3 | 36993.264 | 0 | 11900.522 | 11888 | 1354.662 | 0 | 48888.791 | 0 | 0 | 0 | 2070.455 | 0 | 0
Annual Sum or Average | 7291860000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 516215000000 | 381244.162 |  | 157739.045 | 88982.023 | 36188.788 | 0 | 10706.632 | 0 | 1345.311 | 0 | 48888.791 | 0 | 0 | 0 | 2069.318 | 0 | 0
Maximum of Months | 740429000000 | 553264.693 |  | 177438.022 | 92719.3 | 50098.185 | 0 | 175829.546 | 11888 | 5182.094 | 0 | 48888.791 | 0 | 0 | 0 | 3108.755 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 113827.14 | 94441.13 | 0 | 208268.27
Cost per Total Building Area ($/m2) | 10.03 | 8.32 | 0 | 18.36
Cost per Net Conditioned Building Area ($/m2) | 10.03 | 8.32 | 0 | 18.36

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21130.74 | 1862.51 | 1862.51
Net Site Energy | 21130.74 | 1862.51 | 1862.51
Total Source Energy | 40684.59 | 3586.03 | 3586.03
Net Source Energy | 40684.59 | 3586.03 | 3586.03
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 42.32 | 3005.31 | 0 | 0 | 0 | 0
Cooling | 446.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 185.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1171.95 | 0 | 0 | 0 | 0 | 0
Pumps | 48.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9786.05 | 0 | 0 | 0 | 44332.9
Refrigeration | 68.7 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7100.73 | 14030 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.357 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.71 | 0.794 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.525 | 0.407 | 0.316 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.525 | 0.407 | 0.316 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.525 | 0.407 | 0.316 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.525 | 0.407 | 0.316 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.525 | 0.407 | 0.316 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.525 | 0.407 | 0.316 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 432.93 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 781.15 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1305610.13 | 2.64
HEATSYS1 BOILER | Boiler:HotWater | 6289894.26 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31393.78 | 21989.03 | 9404.75 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8325.63 | 5833.59 | 2492.04 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29251.56 | 20480.52 | 8771.05 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7824.25 | 5482.86 | 2341.4 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 519386.41 | 352595.02 | 166791.4 | 0.68 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 48832.61 | 33509.01 | 15323.6 | 0.69 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 397936.18 | 296862.5 | 101073.69 | 0.75 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27265.88 | 19049.12 | 8216.76 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25383.03 | 17733.27 | 7649.76 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 47562.79 | 33975.3 | 13587.49 | 0.71 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3399.39 | 2369.36 | 1030.03 | 0.7 | -
CAV WITH REHEAT_COOLC | Coil:Cooling:Water | 763577.22 | 537516.35 | 226060.87 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 132379.98 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 77562.46 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 79655.5 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41057.73 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 21274.4 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 29176.13 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 135961.3 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 54495.24 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 155042.34 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 293092.7 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3237.19 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25418.91 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22555.21 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 28765.08 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 8201.19 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 28484.75 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 8132.02 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 1077309.31 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 78852.27 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 1077309.31 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 28196.31 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 27873.03 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2028.95 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 90416.75 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 5920.14 | -
CAV WITH REHEAT_HEATC | Coil:Heating:Water | 591557.55 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.76 | 70.44 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.33 | 849.46 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 225.46 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.24 | 791.01 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.33 | 212.01 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.97 | 1257.03 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 733.65 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 683.37 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
CAV WITH REHEAT_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 36.71 | 61067.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11964.11 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34634.83 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 193037.4749 | 214.211 | 816.0414 | 0 | 0.0029 | 163702.6979 | 72808.764
February | 170647.1824 | 189.7421 | 729.2821 | 0 | 0.0026 | 146300.2071 | 64421.7786
March | 180644.6184 | 202.4399 | 805.0972 | 0 | 0.0029 | 161517.3536 | 68439.349
April | 171795.2115 | 194.2732 | 802.2773 | 0 | 0.0028 | 160960.129 | 65356.0087
May | 174396.4176 | 199.9975 | 872.6438 | 0 | 0.0031 | 175090.5734 | 66773.8181
June | 174169.4477 | 201.3641 | 905.5453 | 0 | 0.0032 | 181699.0784 | 66937.2773
July | 180893.2437 | 210.1681 | 962.059 | 0 | 0.0034 | 193042.9216 | 69679.9354
August | 173241.1848 | 200.7573 | 910.4762 | 0 | 0.0032 | 182690.4076 | 66652.2939
September | 163697.7717 | 188.1119 | 827.1342 | 0 | 0.0029 | 165961.0037 | 62736.4867
October | 173194.6175 | 196.436 | 820.9539 | 0 | 0.0029 | 164709.8708 | 65977.6909
November | 176156.1138 | 197.1374 | 779.3933 | 0 | 0.0028 | 156359.3697 | 66696.9033
December | 189413.7234 | 210.7908 | 813.2947 | 0 | 0.0029 | 163154.7703 | 71534.4544
Annual Sum or Average | 2121290 | 2405.4293 | 10044.1983 | 0 | 0.0355 | 2015190 | 808014.7602
Minimum of Months | 163697.7717 | 188.1119 | 729.2821 | 0 | 0.0026 | 146300.2071 | 62736.4867
Maximum of Months | 193037.4749 | 214.211 | 962.059 | 0 | 0.0034 | 193042.9216 | 72808.764
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 576824000000 | 379806.733 | 20-JAN-20:00 | 177438.022 | 92719.3 | 35797.571 | 0 | 9655.737 | 11888 | 1291.026 | 0 | 48888.791 | 0 | 0 | 0 | 2128.286 | 0 | 0
February | 515505000000 | 380870.348 | 28-FEB-20:19 | 177438.022 | 92719.3 | 36052.343 | 0 | 10458.089 | 11888 | 1358.297 | 0 | 48888.791 | 0 | 0 | 0 | 2067.507 | 0 | 0
March | 569124000000 | 391690.771 | 31-MAR-19:30 | 177438.022 | 92719.3 | 39613.088 | 0 | 17599.415 | 11888 | 1439.689 | 0 | 48888.791 | 0 | 0 | 0 | 2104.466 | 0 | 0
April | 567160000000 | 394486.159 | 25-APR-19:30 | 177438.022 | 92719.3 | 42727.769 | 0 | 28964.15 | 0 | 1570.671 | 0 | 48888.791 | 0 | 0 | 0 | 2177.455 | 0 | 0
May | 616951000000 | 429197.911 | 24-MAY-19:10 | 177438.022 | 92719.3 | 45581.712 | 0 | 59624.182 | 0 | 2140.345 | 0 | 48888.791 | 0 | 0 | 0 | 2805.559 | 0 | 0
June | 640236000000 | 472847.085 | 15-JUN-19:00 | 177438.022 | 92719.3 | 48248.197 | 0 | 99764.242 | 0 | 2809.35 | 0 | 48888.791 | 0 | 0 | 0 | 2979.183 | 0 | 0
July | 680208000000 | 473914.532 | 11-JUL-19:19 | 177438.022 | 92719.3 | 48218.616 | 0 | 100240.133 | 0 | 3938.343 | 0 | 48888.791 | 0 | 0 | 0 | 2471.327 | 0 | 0
August | 643729000000 | 459391.57 | 15-AUG-19:10 | 177438.022 | 92719.3 | 47173.839 | 0 | 87339.777 | 0 | 3373.494 | 0 | 48888.791 | 0 | 0 | 0 | 2458.347 | 0 | 0
September | 584782000000 | 404172.701 | 12-SEP-19:30 | 177438.022 | 92719.3 | 42083.919 | 0 | 26979.824 | 11888 | 1950.542 | 0 | 48888.791 | 0 | 0 | 0 | 2224.304 | 0 | 0
October | 580373000000 | 394872.388 | 03-OCT-19:19 | 177438.022 | 92719.3 | 40373.573 | 0 | 19962.291 | 11888 | 1452.795 | 0 | 48888.791 | 0 | 0 | 0 | 2149.615 | 0 | 0
November | 550949000000 | 381174.324 | 14-NOV-20:00 | 177438.022 | 92719.3 | 36040.672 | 0 | 10792.242 | 11888 | 1329.498 | 0 | 48888.791 | 0 | 0 | 0 | 2077.798 | 0 | 0
December | 574893000000 | 374545.639 | 28-DEC-20:10 | 177438.022 | 92719.3 | 32158.072 | 7619.803 | 0 | 11888 | 1380.978 | 0 | 48888.791 | 0 | 0 | 0 | 2452.673 | 0 | 0
Annual Sum or Average | 7100730000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 515505000000 | 374545.639 |  | 177438.022 | 92719.3 | 32158.072 | 0 | 0 | 0 | 1291.026 | 0 | 48888.791 | 0 | 0 | 0 | 2067.507 | 0 | 0
Maximum of Months | 680208000000 | 473914.532 |  | 177438.022 | 92719.3 | 48248.197 | 7619.803 | 100240.133 | 11888 | 3938.343 | 0 | 48888.791 | 0 | 0 | 0 | 2979.183 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 181675.66 | 59049.66 | 0 | 240725.32
Cost per Total Building Area ($/m2) | 16.01 | 5.2 | 0 | 21.22
Cost per Net Conditioned Building Area ($/m2) | 16.01 | 5.2 | 0 | 21.22

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
UnitHeater_HtgSP_Sch | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
UnitHeater_ClgSP_Sch | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laundry_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Laundry_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Laundry_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_5_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
FLR_3_DOAS_OAminOAFracSchedule | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FLR_6_DOAS_OAminOAFracSchedule | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720