## BuildingSummary
Building Summary Large Hotel post-1980 construction
|  | Value | Data Source
Program
| Building Name | Large Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.59998 | See Benchmark Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZVAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Air cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 44332.9

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 7.5347 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 38.099 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 1.0572
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 38.099 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.35236
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 8.6039 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.39384
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 3.9573 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.39382
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 12.2365 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 1.1318
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 15.7419 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.82991
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 20.2858 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.34234
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60879
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60863
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 13.1176 |  |  |  |  | 0.25 | 97.35 |  | 0.16612
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 3.4487
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 16.8341 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 1.132
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 13.081 |  |  |  |  | 0.25 | 103.03 |  | 0.44675
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 |  |  |  | 15229.9891
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 3722.3837 | 3546.2532 | 3069.7807 | 3177.8995 | 2293.6415 | 2329.6373 | 1549.7147 | 3225.9733 | 1550.2391 | 1743.8716 | 3200.4686 | 1531.253 | 3032.445 | 1450.373 | 2484.5221 | 1345.8524
Heating (kW)
| HEATSYS1 BOILER | 2175.3328 | 2900.2141 | 2454.7389 | 3151.6312 | 2253.9123 | 2665.6264 | 2464.816 | 3478.471 | 2816.9222 | 2989.1157 | 4092.3248 | 3366.8854 | 4430.7562 | 4070.176 | 4534.1945 | 5637.1797
| CORRIDOR_FLR_6 UNIT HEATER COIL | 5.5508 | 11.8867 | 7.7636 | 14.1864 | 7.627 | 9.7958 | 9.2529 | 13.1907 | 12.6185 | 10.4767 | 16.9595 | 15.3225 | 17.4613 | 17.9061 | 17.7811 | 21.4845
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Control - Economizer
| FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| VAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CORRIDOR_FLR_6 UNIT HEATERFAN | 0.15 | 0.33 | 0.22 | 0.4 | 0.22 | 0.28 | 0.26 | 0.33 | 0.41 | 0.27 | 0.43 | 0.48 | 0.43 | 0.51 | 0.44 | 0.49
| DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
| KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 1.34 | 1.36 | 1.58 | 1.3 | 1.55 | 1.51 | 1.37 | 1.3 | 1.53 | 1.39 | 1.36 | 1.48 | 1.35 | 1.42 | 1.5 | 1.68
| ROOM_1_FLR_6 FAN COILFAN | 0.37 | 0.37 | 0.41 | 0.36 | 0.43 | 0.39 | 0.37 | 0.35 | 0.41 | 0.38 | 0.36 | 0.39 | 0.35 | 0.37 | 0.39 | 0.44
| ROOM_2_FLR_3 FAN COILFAN | 1.36 | 1.37 | 1.57 | 1.29 | 1.46 | 1.49 | 1.19 | 1.29 | 1.52 | 1.31 | 1.35 | 1.46 | 1.33 | 1.4 | 1.46 | 1.56
| ROOM_2_FLR_6 FAN COILFAN | 0.37 | 0.37 | 0.41 | 0.36 | 0.41 | 0.39 | 0.32 | 0.35 | 0.41 | 0.36 | 0.36 | 0.39 | 0.35 | 0.37 | 0.38 | 0.41
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.31 | 1.34 | 1.5 | 1.37 | 1.75 | 1.46 | 1.94 | 1.25 | 1.33 | 1.85 | 1.26 | 1.27 | 1.28 | 1.38 | 1.53 | 2.54
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_5_FLR_3 FAN COILFAN | 1.08 | 1.08 | 1.26 | 1.07 | 1.2 | 1.17 | 1.03 | 1.07 | 1.19 | 1.16 | 1.12 | 1.15 | 1.13 | 1.16 | 1.23 | 1.49
| ROOM_6_FLR_3 FAN COILFAN | 1.09 | 1.09 | 1.25 | 1.07 | 1.13 | 1.16 | 0.89 | 1.07 | 1.19 | 1.07 | 1.11 | 1.14 | 1.12 | 1.14 | 1.21 | 1.37
| FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
| VAV WITH REHEAT_FAN | 38.15 | 37.98 | 39.3 | 38.99 | 37.14 | 39.47 | 34.63 | 38.11 | 42.32 | 37.54 | 38.69 | 42.36 | 39.02 | 41.1 | 38.84 | 39.24
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.077573 | 0.10511 | 0.075465 | 0.097058 | 0.12318 | 0.091957 | 0.14487 | 0.07068 | 0.037014 | 0.067846 | 0.09498 | 0.037018 | 0.056342 | 0.071862 | 0.055986 | 0.091877
| Total Cost ($/m2) | 21.15 | 25.74 | 18.23 | 20.75 | 24.56 | 20.28 | 26.17 | 14.48 | 7.27 | 12.27 | 18.51 | 6.99 | 10.87 | 13.18 | 10.18 | 16.38
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.008173 | 0.0085403 | 0.010616 | 0.0084056 | 0.0080687 | 0.0084204 | 0.010014 | 0.0071619 | 0.0083049 | 0.0088118 | 0.0071609 | 0.0079627 | 0.0086548 | 0.0079595 | 0.0041811
| Total Cost ($/m2) | 5.29 | 5.05 | 4.56 | 8.19 | 5.38 | 5.08 | 6.46 | 9.28 | 5.95 | 7.73 | 9.54 | 7 | 9.77 | 9.98 | 11.16 | 7.69
Total Utility Costs
| Cost Intensity ($/m2) | 26.44 | 30.79 | 22.8 | 28.94 | 29.94 | 25.35 | 32.63 | 23.77 | 13.21 | 19.99 | 28.04 | 13.98 | 20.63 | 23.16 | 21.34 | 24.06
Energy - End Uses
Electricity (kWh)
| Heating | 69.4444 | 69.4444 | 333.3333 | 63.8889 | 0 | 261.1111 | 0 | 27.7778 | 50 | 0 | 86.1111 | 63.8889 | 177.7778 | 211.1111 | 180.5556 | 1161.1111
| Cooling | 1235130.5556 | 930930.5556 | 887316.6667 | 586511.1111 | 424572.2222 | 657605.5556 | 225611.1111 | 490936.1111 | 385763.8889 | 221144.4444 | 377238.8889 | 304708.3333 | 354316.6667 | 246408.3333 | 229011.1111 | 175558.3333
| Interior Lighting | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667 | 621566.6667
| Exterior Lighting | 51961.1111 | 51941.6667 | 51933.3333 | 51925 | 51886.1111 | 51872.2222 | 51900 | 51869.4444 | 51888.8889 | 51786.1111 | 51877.7778 | 51847.2222 | 51844.4444 | 51830.5556 | 51802.7778 | 51486.1111
| Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
| Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
| Fans | 319269.4444 | 317088.8889 | 325844.4444 | 315686.1111 | 318072.2222 | 322286.1111 | 309572.2222 | 313375 | 323975 | 316136.1111 | 314902.7778 | 321444.4444 | 315427.7778 | 319513.8889 | 319022.2222 | 329891.6667
| Pumps | 37983.3333 | 30411.1111 | 27480.5556 | 23722.2222 | 19500 | 21991.6667 | 15616.6667 | 21588.8889 | 18388.8889 | 15730.5556 | 19691.6667 | 17041.6667 | 19944.4444 | 16719.4444 | 17494.4444 | 18597.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21827.7778 | 21063.8889 | 21205.5556 | 20400 | 20583.3333 | 20688.8889 | 19980.5556 | 19952.7778 | 19961.1111 | 19583.3333 | 19613.8889 | 19580.5556 | 19475 | 19266.6667 | 19005.5556 | 18605.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3093288.8889 | 2778555.5556 | 2741158.3333 | 2425350 | 2261658.3333 | 2501752.7778 | 2049725 | 2324791.6667 | 2227072.2222 | 2051422.2222 | 2210458.3333 | 2141730.5556 | 2188230.5556 | 2080991.6667 | 2063561.1111 | 2022344.4444
Gas (MJ)
| Heating | 176020 | 913860 | 555370 | 1668470 | 376580 | 924400 | 967040 | 2661020 | 1712260 | 2292690 | 3737010 | 2579000 | 4786670 | 3842910 | 5809120 | 9580540
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3829470 | 4855150 | 4265980 | 5843000 | 5650970 | 4975990 | 6496320 | 6619460 | 6472240 | 7023360 | 7300960 | 7265410 | 7889860 | 7996780 | 8861150 | 10036920
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5244140 | 7007660 | 6060010 | 8750120 | 7266190 | 7139040 | 8702000 | 10519130 | 9423150 | 10554700 | 12276620 | 11083060 | 13915180 | 13078340 | 15908920 | 20856100
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 16379980 | 17010460 | 15928180 | 17481380 | 15408170 | 16145350 | 16081010 | 18888380 | 17440610 | 17939830 | 20234270 | 18793290 | 21792800 | 20569920 | 23337730 | 28136540
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.022036 | 0.022036 | 0.10577 | 0.020273 | 0 | 0.082854 | 0 | 0.0088142 | 0.015866 | 0 | 0.027324 | 0.020273 | 0.056411 | 0.066988 | 0.057292 | 0.36843
| Cooling (elec) | 391.9221 | 295.3957 | 281.5565 | 186.1072 | 134.722 | 208.6663 | 71.5892 | 155.7801 | 122.4076 | 70.1719 | 119.7025 | 96.6877 | 112.429 | 78.1884 | 72.668 | 55.7068
| Interior Lighting (elec) | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307 | 197.2307
| Exterior Lighting (elec) | 16.4879 | 16.4817 | 16.4791 | 16.4764 | 16.4641 | 16.4597 | 16.4685 | 16.4588 | 16.465 | 16.4324 | 16.4615 | 16.4518 | 16.4509 | 16.4465 | 16.4377 | 16.3372
| Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
| Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
| Fans (elec) | 101.3081 | 100.6162 | 103.3944 | 100.1711 | 100.9282 | 102.2653 | 98.2311 | 99.4377 | 102.8013 | 100.3139 | 99.9225 | 101.9983 | 100.0891 | 101.3857 | 101.2297 | 104.6787
| Pumps (elec) | 12.0526 | 9.6498 | 8.7199 | 7.5274 | 6.1876 | 6.9782 | 4.9554 | 6.8504 | 5.835 | 4.9915 | 6.2484 | 5.4075 | 6.3286 | 5.3053 | 5.5512 | 5.9011
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 6.9262 | 6.6838 | 6.7288 | 6.4732 | 6.5313 | 6.5648 | 6.3401 | 6.3313 | 6.3339 | 6.214 | 6.2237 | 6.2132 | 6.1797 | 6.1136 | 6.0307 | 5.9038
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 981.5386 | 881.6698 | 869.8032 | 769.5934 | 717.652 | 793.8369 | 650.4029 | 737.685 | 706.6774 | 650.9415 | 701.4056 | 679.5974 | 694.3525 | 660.3242 | 654.7933 | 641.7148
Gas (MJ/m2)
| Heating (gas) | 15.5148 | 80.5497 | 48.9516 | 147.0628 | 33.1926 | 81.4787 | 85.2371 | 234.5484 | 150.9225 | 202.083 | 329.3887 | 227.319 | 421.9081 | 338.7229 | 512.0292 | 844.4509
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 337.5383 | 427.9441 | 376.0133 | 515.0155 | 498.0895 | 438.5952 | 572.6006 | 583.4545 | 570.4781 | 619.0551 | 643.5234 | 640.39 | 695.4304 | 704.8546 | 781.0422 | 884.6773
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 462.2306 | 617.6713 | 534.1432 | 771.2557 | 640.4587 | 629.2514 | 767.0143 | 927.1804 | 830.5782 | 930.3156 | 1082.0896 | 976.8864 | 1226.516 | 1152.755 | 1402.2489 | 1838.3047
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1443.7692 | 1499.3411 | 1403.9465 | 1540.8491 | 1358.1116 | 1423.0883 | 1417.4173 | 1664.8653 | 1537.2555 | 1581.2579 | 1783.4952 | 1656.4839 | 1920.8676 | 1813.0801 | 2057.0413 | 2480.0195
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 554.3732 | 517.8973 | 439.4013 | 436.0073 | 444.4849 | 394.988 | 395.9526 | 391.2342 | 396.8415 | 390.3132 | 391.6362 | 397.0371 | 389.5244 | 391.2868 | 387.9732 | 389.0489
| Feb | 552.066 | 475.4128 | 449.6975 | 404.3225 | 428.4035 | 411.8551 | 422.2458 | 392.8009 | 400.9324 | 400.1881 | 391.1221 | 396.8757 | 390.3337 | 397.4972 | 392.9103 | 390.1696
| Mar | 573.4548 | 524.325 | 535.7544 | 458.2967 | 427.5239 | 437.364 | 398.2081 | 451.4674 | 415.5462 | 424.3345 | 423.5556 | 423.2433 | 402.2457 | 417.1932 | 394.9531 | 400.403
| Apr | 589.5138 | 580.7355 | 530.9046 | 495.3143 | 475.1535 | 514.4986 | 423.9178 | 450.8154 | 455.4235 | 417.8322 | 412.111 | 445.1539 | 447.0372 | 423.8298 | 405.2887 | 398.98
| May | 618.891 | 644.8576 | 607.4211 | 558.1794 | 473.1622 | 548.0889 | 427.1044 | 527.2995 | 487.5335 | 452.5914 | 485.8316 | 474.4136 | 559.4017 | 442.3211 | 433.5951 | 434.5583
| Jun | 672.6594 | 627.5441 | 746.0155 | 601.4065 | 468.6321 | 674.2582 | 437.5537 | 614.4891 | 517.3382 | 462.6096 | 553.4719 | 484.8321 | 577.6403 | 506.989 | 520.7997 | 482.8038
| Jul | 640.942 | 665.7689 | 716.2538 | 633.9155 | 475.2146 | 664.5946 | 496.0123 | 659.3908 | 536.3003 | 485.7876 | 595.7775 | 516.0217 | 615.7207 | 505.5066 | 550.9346 | 482.9293
| Aug | 651.058 | 694.514 | 722.3701 | 595.4144 | 500.5306 | 632.2372 | 431.808 | 658.9109 | 531.4363 | 474.9711 | 638.1243 | 496.8005 | 610.071 | 489.7905 | 545.2473 | 466.9175
| Sep | 629.2183 | 635.0036 | 638.484 | 555.5947 | 485.9952 | 573.1414 | 494.1539 | 506.1532 | 477.801 | 521.7382 | 523.8121 | 477.5183 | 490.7872 | 476.0254 | 488.5294 | 407.0179
| Oct | 624.4739 | 587.1053 | 547.9599 | 503.22 | 469.2514 | 498.1568 | 444.9682 | 516.7813 | 458.5025 | 426.7916 | 462.3647 | 435.3579 | 441.2574 | 431.2553 | 415.9385 | 400.0979
| Nov | 580.6276 | 559.6347 | 457.3263 | 430.9001 | 446.4681 | 424.3374 | 410.3477 | 461.1043 | 416.5126 | 398.7086 | 456.0857 | 400.0951 | 401.4968 | 397.6346 | 397.8564 | 389.4635
| Dec | 549.0775 | 533.9698 | 434.5163 | 427.7278 | 448.1886 | 407.9411 | 394.6011 | 389.5925 | 394.1323 | 389.4321 | 392.4338 | 393.6414 | 389.2978 | 391.4529 | 388.9599 | 386.3667
Time of Peak Electrical Demand
| Jan | 06-JAN-20:00 | 06-JAN-20:10 | 27-JAN-20:10 | 24-JAN-20:00 | 26-JAN-20:10 | 18-JAN-20:49 | 27-JAN-20:30 | 05-JAN-20:00 | 26-JAN-20:30 | 27-JAN-20:00 | 17-JAN-20:00 | 24-JAN-20:49 | 30-JAN-20:00 | 30-JAN-20:00 | 20-JAN-20:00 | 20-JAN-20:00
| Feb | 23-FEB-20:10 | 20-FEB-20:10 | 27-FEB-20:10 | 19-FEB-20:00 | 13-FEB-20:00 | 27-FEB-20:10 | 15-FEB-20:10 | 15-FEB-20:00 | 14-FEB-20:30 | 21-FEB-20:10 | 27-FEB-20:00 | 10-FEB-20:00 | 27-FEB-20:00 | 03-FEB-20:00 | 22-FEB-20:00 | 28-FEB-20:19
| Mar | 13-MAR-19:10 | 26-MAR-19:00 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:00 | 30-MAR-19:10 | 30-MAR-19:00 | 09-MAR-20:00 | 20-MAR-19:10 | 29-MAR-19:10 | 31-MAR-19:10 | 30-MAR-19:10 | 28-MAR-19:00 | 30-MAR-19:10 | 22-MAR-19:19 | 29-MAR-19:30
| Apr | 03-APR-19:00 | 30-APR-19:10 | 26-APR-19:10 | 14-APR-19:10 | 11-APR-19:10 | 21-APR-19:10 | 13-APR-19:49 | 05-APR-19:10 | 21-APR-19:10 | 14-APR-19:10 | 28-APR-19:00 | 25-APR-19:00 | 02-APR-19:00 | 06-APR-19:10 | 04-APR-19:10 | 25-APR-19:10
| May | 15-MAY-19:49 | 26-MAY-19:10 | 28-MAY-19:30 | 31-MAY-19:40 | 30-MAY-19:10 | 31-MAY-19:10 | 25-MAY-19:19 | 15-MAY-19:10 | 30-MAY-19:10 | 04-MAY-19:19 | 30-MAY-17:10 | 23-MAY-19:19 | 27-MAY-17:19 | 25-MAY-19:00 | 31-MAY-19:10 | 24-MAY-19:10
| Jun | 27-JUN-19:19 | 29-JUN-19:30 | 27-JUN-19:10 | 08-JUN-19:10 | 28-JUN-19:10 | 27-JUN-19:10 | 16-JUN-19:30 | 30-JUN-18:10 | 28-JUN-19:19 | 27-JUN-19:10 | 19-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:10 | 25-JUN-19:10 | 14-JUN-19:00 | 15-JUN-19:00
| Jul | 11-JUL-19:19 | 05-JUL-19:30 | 11-JUL-19:10 | 03-JUL-19:10 | 10-JUL-19:10 | 25-JUL-19:10 | 02-JUL-19:30 | 24-JUL-19:30 | 18-JUL-19:10 | 24-JUL-19:10 | 14-JUL-19:30 | 10-JUL-19:30 | 13-JUL-19:10 | 21-JUL-19:10 | 06-JUL-19:10 | 11-JUL-19:10
| Aug | 21-AUG-19:10 | 06-AUG-19:10 | 01-AUG-19:30 | 14-AUG-19:30 | 16-AUG-19:10 | 04-AUG-19:10 | 14-AUG-19:10 | 17-AUG-19:10 | 01-AUG-19:10 | 18-AUG-19:19 | 04-AUG-19:10 | 29-AUG-19:10 | 25-AUG-19:10 | 11-AUG-19:49 | 13-AUG-19:19 | 15-AUG-19:10
| Sep | 01-SEP-19:00 | 15-SEP-19:19 | 08-SEP-19:10 | 11-SEP-19:10 | 25-SEP-19:10 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:00 | 13-SEP-19:10 | 02-SEP-17:10 | 06-SEP-19:10 | 01-SEP-19:10 | 13-SEP-19:10 | 01-SEP-19:10 | 08-SEP-19:10 | 08-SEP-19:49
| Oct | 06-OCT-19:10 | 29-OCT-19:49 | 02-OCT-19:10 | 20-OCT-19:10 | 05-OCT-19:00 | 03-OCT-19:10 | 16-OCT-19:10 | 02-OCT-19:00 | 02-OCT-19:10 | 17-OCT-19:10 | 30-OCT-19:10 | 01-OCT-19:10 | 08-OCT-19:10 | 05-OCT-19:10 | 07-OCT-19:10 | 03-OCT-19:10
| Nov | 01-NOV-19:00 | 27-NOV-20:10 | 02-NOV-19:10 | 22-NOV-20:00 | 09-NOV-20:30 | 09-NOV-20:19 | 15-NOV-20:00 | 03-NOV-19:10 | 09-NOV-20:00 | 03-NOV-19:00 | 02-NOV-19:00 | 03-NOV-19:10 | 02-NOV-19:00 | 20-NOV-20:00 | 02-NOV-19:00 | 14-NOV-20:00
| Dec | 15-DEC-20:10 | 02-DEC-20:10 | 13-DEC-20:00 | 04-DEC-20:00 | 18-DEC-20:10 | 05-DEC-20:10 | 07-DEC-20:00 | 06-DEC-20:00 | 05-DEC-20:30 | 28-DEC-20:00 | 11-DEC-20:00 | 22-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 01-DEC-20:00 | 18-DEC-20:00
Source Energy
| Total Source Energy (GJ) | 42664.19 | 43982.52 | 37830.55 | 38927.08 | 33134.1 | 40011.41 | 32340.63 | 41415.34 | 36892.01 | 24390.62 | 41623.89 | 37685.24 | 42270.78 | 40322.26 | 42905.38 | 48780.59
| Total Source Energy (MJ/m2) | 3760.52 | 3876.72 | 3334.47 | 3431.12 | 2920.52 | 3526.7 | 2850.58 | 3650.44 | 3251.75 | 2149.85 | 3668.83 | 3321.66 | 3725.84 | 3554.1 | 3781.78 | 4299.64
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
| Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
Emissions
| Carbon Equivalent (kg) | 942899.9756 | 1053180 | 936766.7794 | 904885.0306 | 395339.9059 | 972515.1374 | 396463.5697 | 817046.4728 | 1079680 | 339743.4978 | 1399880 | 1074750 | 999944.0323 | 996310.7952 | 993223.011 | 945154.1469
| CO2 (kg) | 2237580 | 2690750 | 2261730 | 2151490 | 1084230 | 2370440 | 1092910 | 1954920 | 2610760 | 904828.9996 | 3358740 | 2616010 | 2451760 | 2450140 | 2457250 | 2512110
| NOX (kg) | 3712.4086 | 3388.317 | 3575.6993 | 3688.1028 | 947.5813 | 3615.0734 | 958.906 | 3310.4612 | 4165.0149 | 1069.5166 | 5531.9328 | 4101.0033 | 3809.2385 | 3758.3245 | 3724.018 | 2772.3854
| SO2 (kg) | 13241.923 | 13255.583 | 11024.3698 | 8515.3229 | 6583.1057 | 13763.5578 | 5966.7878 | 8489.2434 | 9727.7052 | 1588.4147 | 14900.0078 | 9355.4758 | 5168.3014 | 5560.006 | 4874.5948 | 10300.1304
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0609 | 0.038 | 0.0306 | 0.032 | 0.0037 | 0.0266 | 0.0036 | 0.0353 | 0.0389 | 0.0073 | 0.0462 | 0.0376 | 0.0392 | 0.04 | 0.0373 | 0.0371
| Water for Electricity (m3) | 1638.7 | 4521.03 | 81424.5 | 15142.9 | 39709.7 | 68633.1 | 35988.6 | 527.8154 | 10112.7 | 20959 | 3429.39 | 9725.16 | 3394.91 | 131819 | 3201.49 | 2066.19

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16379.98 | 1443.77 | 1443.77
Net Site Energy | 16379.98 | 1443.77 | 1443.77
Total Source Energy | 42664.19 | 3760.52 | 3760.52
Net Source Energy | 42664.19 | 3760.52 | 3760.52
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.25 | 176.02 | 0 | 0 | 0 | 0
Cooling | 4446.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 187.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1149.37 | 0 | 0 | 0 | 0 | 0
Pumps | 136.74 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 3829.47 | 0 | 0 | 0 | 44332.9
Refrigeration | 78.58 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11135.84 | 5244.14 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.421 | 0.457 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.251 | 0.11 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.251 | 0.11 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.251 | 0.11 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 432.93 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3722383.68 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2175332.76 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35058.93 | 24189.52 | 10869.41 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9531.98 | 6592.88 | 2939.09 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35655.65 | 24613.85 | 11041.8 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9702.45 | 6714.3 | 2988.15 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 706193.2 | 446107.78 | 260085.42 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 44876.3 | 28385.73 | 16490.57 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 706193.2 | 446107.78 | 260085.42 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28682.1 | 19660.31 | 9021.79 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28998.16 | 19883.66 | 9114.49 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 81938.55 | 51790.47 | 30148.09 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5413.95 | 3415.36 | 1998.59 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 845869.4 | 565557.23 | 280312.17 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 40640.21 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 43700.45 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18323.5 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10801.47 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4316.84 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 5550.76 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41589.88 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 14815.52 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46579.97 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 92597.23 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 482.43 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5967.8 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7267.58 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11854.72 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3138.15 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11860.03 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3144.76 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 710011.01 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 41003.95 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 710011.01 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11633.75 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 11635.92 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 618.58 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 25443.75 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 1665.96 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 113510.76 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.15 | 14.37 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.34 | 850.71 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 232.63 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.36 | 866.26 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 237.08 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.31 | 832.3 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.08 | 685.7 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.09 | 693.8 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 38.15 | 63473.28 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34110.49 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11978.31 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 168863.3999 | 274.7527 | 956.7364 | 0 | 0.0044 | 118392.0504 | 70615.5234
February | 152973.704 | 249.6717 | 872.7913 | 0 | 0.004 | 108004.883 | 64048.1751
March | 171862.7002 | 281.6782 | 989.8285 | 0 | 0.0046 | 122488.8638 | 72074.7257
April | 176994.2976 | 292.8759 | 1041.3204 | 0 | 0.0048 | 128863.2966 | 74506.0589
May | 198659.604 | 331.7282 | 1192.4151 | 0 | 0.0055 | 147563.8087 | 83926.9363
June | 200369.9442 | 336.3316 | 1216.4343 | 0 | 0.0056 | 150537.696 | 84824.5867
July | 215417.2166 | 362.7567 | 1316.9746 | 0 | 0.006 | 162980.8442 | 91311.6823
August | 213521.3376 | 359.1176 | 1301.8694 | 0 | 0.006 | 161111.1488 | 90463.3083
September | 202600.2711 | 339.5372 | 1225.7399 | 0 | 0.0056 | 151688.8405 | 85714.8624
October | 196939.8717 | 327.7105 | 1173.073 | 0 | 0.0054 | 145169.2189 | 83085.5783
November | 174007.3858 | 286.597 | 1013.2288 | 0 | 0.0047 | 125385.8181 | 73114.803
December | 165372.7035 | 269.6515 | 941.5114 | 0 | 0.0043 | 116508.5362 | 69213.7351
Annual Sum or Average | 2237580 | 3712.4086 | 13241.923 | 0 | 0.0609 | 1638700 | 942899.9756
Minimum of Months | 152973.704 | 249.6717 | 872.7913 | 0 | 0.004 | 108004.883 | 64048.1751
Maximum of Months | 215417.2166 | 362.7567 | 1316.9746 | 0 | 0.006 | 162980.8442 | 91311.6823
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 804540000000 | 554373.212 | 06-JAN-20:00 | 177438.022 | 92719.3 | 37055.57 | 0 | 178519.419 | 11888 | 5404.389 | 0 | 48888.791 | 0 | 0 | 0 | 2459.722 | 0 | 0
February | 733953000000 | 552066.035 | 23-FEB-20:10 | 177438.022 | 92719.3 | 37225.683 | 0 | 175585.344 | 11888 | 5324.069 | 0 | 48888.791 | 0 | 0 | 0 | 2996.827 | 0 | 0
March | 832380000000 | 573454.831 | 13-MAR-19:10 | 177438.022 | 92719.3 | 37319.325 | 0 | 196534.786 | 11888 | 5625.005 | 0 | 48888.791 | 0 | 0 | 0 | 3041.602 | 0 | 0
April | 875698000000 | 589513.806 | 03-APR-19:00 | 177438.022 | 92719.3 | 37581.179 | 0 | 212094.983 | 11888 | 5829.339 | 0 | 48888.791 | 0 | 0 | 0 | 3074.192 | 0 | 0
May | 1002780000000 | 618891.031 | 15-MAY-19:49 | 177438.022 | 92719.3 | 37670.305 | 0 | 240798.577 | 11888 | 6413.613 | 0 | 48888.791 | 0 | 0 | 0 | 3074.423 | 0 | 0
June | 1022990000000 | 672659.406 | 27-JUN-19:19 | 177438.022 | 92719.3 | 37923.439 | 0 | 294280.73 | 11888 | 6940.328 | 0 | 48888.791 | 0 | 0 | 0 | 2580.796 | 0 | 0
July | 1107550000000 | 640941.997 | 11-JUL-19:19 | 177438.022 | 92719.3 | 37423.999 | 0 | 263511.793 | 11888 | 6517.384 | 0 | 48888.791 | 0 | 0 | 0 | 2554.709 | 0 | 0
August | 1094840000000 | 651058.042 | 21-AUG-19:10 | 177438.022 | 92719.3 | 37769.215 | 0 | 272534.999 | 11888 | 6681.415 | 0 | 48888.791 | 0 | 0 | 0 | 3138.301 | 0 | 0
September | 1030810000000 | 629218.271 | 01-SEP-19:00 | 177438.022 | 92719.3 | 37560.78 | 0 | 251732.274 | 11888 | 6452 | 0 | 48888.791 | 0 | 0 | 0 | 2539.104 | 0 | 0
October | 986506000000 | 624473.889 | 06-OCT-19:10 | 177438.022 | 92719.3 | 37639.241 | 0 | 246977.036 | 11888 | 6386.302 | 0 | 48888.791 | 0 | 0 | 0 | 2537.197 | 0 | 0
November | 852066000000 | 580627.559 | 01-NOV-19:00 | 177438.022 | 92719.3 | 37314.178 | 0 | 203673.488 | 11888 | 5645.292 | 0 | 48888.791 | 0 | 0 | 0 | 3060.488 | 0 | 0
December | 791740000000 | 549077.487 | 15-DEC-20:10 | 177438.022 | 92719.3 | 37078.678 | 0 | 173745.71 | 11888 | 4871.816 | 0 | 48888.791 | 0 | 0 | 0 | 2447.17 | 0 | 0
Annual Sum or Average | 11135800000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 733953000000 | 549077.487 |  | 177438.022 | 92719.3 | 37055.57 | 0 | 173745.71 | 11888 | 4871.816 | 0 | 48888.791 | 0 | 0 | 0 | 2447.17 | 0 | 0
Maximum of Months | 1107550000000 | 672659.406 |  | 177438.022 | 92719.3 | 37923.439 | 0 | 294280.73 | 11888 | 6940.328 | 0 | 48888.791 | 0 | 0 | 0 | 3138.301 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 239956.95 | 60049.74 | 0 | 300006.69
Cost per Total Building Area ($/m2) | 21.15 | 5.29 | 0 | 26.44
Cost per Net Conditioned Building Area ($/m2) | 21.15 | 5.29 | 0 | 26.44

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17010.46 | 1499.34 | 1499.34
Net Site Energy | 17010.46 | 1499.34 | 1499.34
Total Source Energy | 43982.52 | 3876.72 | 3876.72
Net Source Energy | 43982.52 | 3876.72 | 3876.72
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.25 | 913.86 | 0 | 0 | 0 | 0
Cooling | 3351.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1141.52 | 0 | 0 | 0 | 0 | 0
Pumps | 109.48 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4855.15 | 0 | 0 | 0 | 44332.9
Refrigeration | 75.83 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10002.8 | 7007.66 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.375 | 0.404 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.931 | 2.715 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.251 | 0.11 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.251 | 0.11 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.251 | 0.11 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 432.93 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3546253.16 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2900214.07 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35119.32 | 24215.15 | 10904.17 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9531.47 | 6587.5 | 2943.97 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35255.11 | 24312.49 | 10942.63 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9587.38 | 6627.49 | 2959.89 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 698246.72 | 440343.37 | 257903.35 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 45489.85 | 28700.58 | 16789.28 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 698246.72 | 440343.37 | 257903.35 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28424.68 | 19470.83 | 8953.85 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28501.01 | 19527.67 | 8973.34 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 81034.02 | 51130.14 | 29903.88 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5386.95 | 3388 | 1998.96 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 858140.3 | 573671.61 | 284468.69 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 40372.85 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 42427.64 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18395.62 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10865.96 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4347.82 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 11886.67 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41340.72 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15043.42 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46417.05 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 91712.64 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 406.65 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5853.7 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7218.03 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17642.04 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4813.12 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17607.66 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4812.4 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 823599.64 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 48157.57 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 823599.64 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17182.14 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17142.09 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 616.31 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 45387.07 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2971.77 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 223210.68 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.33 | 30.4 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.36 | 865.71 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 236.24 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 869.41 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 237.75 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.34 | 849.89 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.08 | 690.58 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.09 | 692.87 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 37.98 | 63185.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32496.5 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15969.81 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 201315.4301 | 246.2284 | 889.828 | 0 | 0.0026 | 303454.0744 | 77858.7002
February | 173967.2654 | 212.2045 | 760.9015 | 0 | 0.0022 | 259483.6458 | 67207.7549
March | 198091.998 | 246.1791 | 930.1068 | 0 | 0.0027 | 317211.848 | 77113.8699
April | 210011.2027 | 264.4842 | 1034.9859 | 0 | 0.003 | 352999.0298 | 82203.9958
May | 240531.1634 | 305.6088 | 1223.0471 | 0 | 0.0035 | 417153.8301 | 94496.8462
June | 256243.0383 | 327.6163 | 1331.5752 | 0 | 0.0038 | 454180.2084 | 100933.085
July | 280008.9425 | 359.0969 | 1470.4111 | 0 | 0.0042 | 501540.2396 | 110435.5181
August | 272609.6682 | 349.2715 | 1426.8464 | 0 | 0.0041 | 486679.2513 | 107473.9068
September | 243162.511 | 310.205 | 1253.9748 | 0 | 0.0036 | 427708.6348 | 95692.1175
October | 223618.2666 | 283.0104 | 1121.5086 | 0 | 0.0032 | 382515.974 | 87709.2981
November | 197227.4979 | 246.8024 | 949.8242 | 0 | 0.0027 | 323945.3346 | 76996.1598
December | 193962.4236 | 237.6096 | 862.5736 | 0 | 0.0025 | 294161.732 | 75063.2118
Annual Sum or Average | 2690750 | 3388.317 | 13255.583 | 0 | 0.038 | 4521030 | 1053180
Minimum of Months | 173967.2654 | 212.2045 | 760.9015 | 0 | 0.0022 | 259483.6458 | 67207.7549
Maximum of Months | 280008.9425 | 359.0969 | 1470.4111 | 0 | 0.0042 | 501540.2396 | 110435.5181
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 671393000000 | 517897.288 | 06-JAN-20:10 | 177438.022 | 92719.3 | 36855.482 | 0 | 143705.145 | 11888 | 3969.596 | 0 | 48888.791 | 0 | 0 | 0 | 2432.951 | 0 | 0
February | 574108000000 | 475412.81 | 20-FEB-20:10 | 167588.533 | 91473.541 | 36830.591 | 0 | 112432.334 | 11888 | 3455.095 | 0 | 48888.791 | 0 | 0 | 0 | 2855.925 | 0 | 0
March | 701832000000 | 524324.953 | 26-MAR-19:00 | 167588.533 | 91473.541 | 37117.599 | 0 | 159434.714 | 11888 | 4972.162 | 0 | 48888.791 | 0 | 0 | 0 | 2961.613 | 0 | 0
April | 781011000000 | 580735.506 | 30-APR-19:10 | 167588.533 | 91473.541 | 37294.769 | 0 | 214694.256 | 11888 | 5908.21 | 0 | 48888.791 | 0 | 0 | 0 | 2999.405 | 0 | 0
May | 922954000000 | 644857.598 | 26-MAY-19:10 | 177438.022 | 92719.3 | 37797.341 | 0 | 267132.478 | 11888 | 6423.454 | 0 | 48888.791 | 0 | 0 | 0 | 2570.212 | 0 | 0
June | 1004870000000 | 627544.054 | 29-JUN-19:30 | 177438.022 | 92719.3 | 37691.774 | 0 | 249550.826 | 11888 | 6257.634 | 0 | 48888.791 | 0 | 0 | 0 | 3109.706 | 0 | 0
July | 1109660000000 | 665768.852 | 05-JUL-19:30 | 177438.022 | 92719.3 | 37945.048 | 92.109 | 286922.635 | 11888 | 6720.003 | 0 | 48888.791 | 0 | 0 | 0 | 3154.945 | 0 | 0
August | 1076780000000 | 694513.954 | 06-AUG-19:10 | 167588.533 | 91473.541 | 37751.174 | 458.91 | 326096.788 | 11888 | 7225.865 | 0 | 48888.791 | 0 | 0 | 0 | 3142.352 | 0 | 0
September | 946306000000 | 635003.556 | 15-SEP-19:19 | 177438.022 | 92719.3 | 37523.086 | 0 | 257591.83 | 11888 | 6411.712 | 0 | 48888.791 | 0 | 0 | 0 | 2542.815 | 0 | 0
October | 846317000000 | 587105.308 | 29-OCT-19:49 | 167588.533 | 91473.541 | 37035.389 | 0 | 221283.996 | 11888 | 5956.539 | 0 | 48888.791 | 0 | 0 | 0 | 2990.519 | 0 | 0
November | 716730000000 | 559634.726 | 27-NOV-20:10 | 177438.022 | 92719.3 | 36984.105 | 0 | 183341.171 | 11888 | 5382.581 | 0 | 48888.791 | 0 | 0 | 0 | 2992.757 | 0 | 0
December | 650833000000 | 533969.753 | 02-DEC-20:10 | 157739.045 | 88982.023 | 36830.591 | 0 | 181449.237 | 11888 | 5260.944 | 0 | 48888.791 | 0 | 0 | 0 | 2931.123 | 0 | 0
Annual Sum or Average | 10002800000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 574108000000 | 475412.81 |  | 157739.045 | 88982.023 | 36830.591 | 0 | 112432.334 | 11888 | 3455.095 | 0 | 48888.791 | 0 | 0 | 0 | 2432.951 | 0 | 0
Maximum of Months | 1109660000000 | 694513.954 |  | 177438.022 | 92719.3 | 37945.048 | 458.91 | 326096.788 | 11888 | 7225.865 | 0 | 48888.791 | 0 | 0 | 0 | 3154.945 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 292040.65 | 57273.39 | 0 | 349314.04
Cost per Total Building Area ($/m2) | 25.74 | 5.05 | 0 | 30.79
Cost per Net Conditioned Building Area ($/m2) | 25.74 | 5.05 | 0 | 30.79

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15928.18 | 1403.95 | 1403.95
Net Site Energy | 15928.18 | 1403.95 | 1403.95
Total Source Energy | 37830.55 | 3334.47 | 3334.47
Net Source Energy | 37830.55 | 3334.47 | 3334.47
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.2 | 555.37 | 0 | 0 | 0 | 0
Cooling | 3194.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1173.04 | 0 | 0 | 0 | 0 | 0
Pumps | 98.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4265.98 | 0 | 0 | 0 | 44332.9
Refrigeration | 76.34 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9868.17 | 6060.01 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.261 | 0.275 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.328 | 3.573 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.251 | 0.11 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.251 | 0.11 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.251 | 0.11 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 432.93 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3069780.71 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2454738.85 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36675.21 | 25148.91 | 11526.3 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9488.47 | 6511.73 | 2976.74 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36377.64 | 24942.53 | 11435.11 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9437.1 | 6476.7 | 2960.4 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 630988.87 | 392167.3 | 238821.57 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 43792.97 | 27555.52 | 16237.45 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 521470.29 | 330124.04 | 191346.25 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29470.5 | 20093.69 | 9376.82 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29318.52 | 19988.52 | 9329.99 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 58813.49 | 37179.99 | 21633.5 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3971.35 | 2505.99 | 1465.37 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 900919.43 | 592260.34 | 308659.1 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 42002.36 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 31470.87 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19516.49 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12252.75 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4359.76 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 7763.61 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 42949.29 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15656.29 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47001.57 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 94144.37 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 574.43 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6448.44 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7375.88 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 14982.62 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3909.42 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 14992.57 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3915.44 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 740650.98 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 44255.52 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 740650.98 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 14579.45 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 14591.57 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 594.3 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 34545.72 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2261.92 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 170209.28 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.22 | 20.34 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.58 | 1007.51 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 261.15 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.57 | 999.21 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 259.78 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.5 | 957.77 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.26 | 799.95 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.25 | 795.98 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 39.3 | 65389.31 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28130.29 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13516.84 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 162479.638 | 244.3608 | 701.4587 | 0 | 0.002 | 5180170 | 66030.7724
February | 147067.9272 | 222.1201 | 641.7062 | 0 | 0.0018 | 4738970 | 59862.3618
March | 172364.7327 | 266.8294 | 799.1274 | 0 | 0.0022 | 5901920 | 70816.7389
April | 174487.0861 | 275.117 | 845.1527 | 0 | 0.0023 | 6242140 | 72194.5405
May | 193541.0884 | 309.9432 | 972.0465 | 0 | 0.0027 | 7179620 | 80561.8927
June | 218660.7732 | 355.4414 | 1136.3369 | 0 | 0.0031 | 8393380 | 91550.9996
July | 239850.2463 | 391.9815 | 1261.6157 | 0 | 0.0035 | 9318840 | 100634.7467
August | 232452.2958 | 378.9874 | 1216.1641 | 0 | 0.0033 | 8983070 | 97439.3687
September | 210684.1973 | 340.7155 | 1082.1551 | 0 | 0.003 | 7993080 | 88033.3548
October | 184748.9883 | 293.3123 | 909.4358 | 0 | 0.0025 | 6717040 | 76644.2142
November | 162660.4343 | 252.6588 | 760.3003 | 0 | 0.0021 | 5615220 | 66915.8614
December | 162732.0298 | 244.232 | 698.8702 | 0 | 0.002 | 5161020 | 66081.9276
Annual Sum or Average | 2261730 | 3575.6993 | 11024.3698 | 0 | 0.0306 | 81424500 | 936766.7794
Minimum of Months | 147067.9272 | 222.1201 | 641.7062 | 0 | 0.0018 | 4738970 | 59862.3618
Maximum of Months | 239850.2463 | 391.9815 | 1261.6157 | 0 | 0.0035 | 9318840 | 100634.7467
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 627806000000 | 439401.289 | 27-JAN-20:10 | 177438.022 | 92719.3 | 37659.266 | 0 | 66257.54 | 11888 | 2219.985 | 0 | 48888.791 | 0 | 0 | 0 | 2330.386 | 0 | 0
February | 574335000000 | 449697.519 | 27-FEB-20:10 | 177438.022 | 92719.3 | 37659.266 | 0 | 75913.902 | 11888 | 2325.644 | 0 | 48888.791 | 0 | 0 | 0 | 2864.594 | 0 | 0
March | 715279000000 | 535754.404 | 17-MAR-19:10 | 177438.022 | 92719.3 | 38217.213 | 0 | 160316.092 | 11888 | 3773.169 | 0 | 48888.791 | 0 | 0 | 0 | 2513.817 | 0 | 0
April | 756511000000 | 530904.552 | 26-APR-19:10 | 177438.022 | 92719.3 | 38200.865 | 0 | 154972.456 | 11888 | 3718.571 | 0 | 48888.791 | 0 | 0 | 0 | 3078.546 | 0 | 0
May | 870129000000 | 607421.091 | 28-MAY-19:30 | 167588.533 | 91473.541 | 38717.392 | 0 | 240548.954 | 11888 | 5145.586 | 0 | 48888.791 | 0 | 0 | 0 | 3170.294 | 0 | 0
June | 1017230000000 | 746015.496 | 27-JUN-19:10 | 177438.022 | 92719.3 | 40100.323 | 0 | 376832.732 | 0 | 7425.295 | 0 | 48888.791 | 0 | 0 | 0 | 2611.034 | 0 | 0
July | 1129390000000 | 716253.756 | 11-JUL-19:10 | 177438.022 | 92719.3 | 39891.32 | 0 | 348594.746 | 0 | 6085.608 | 0 | 48888.791 | 0 | 0 | 0 | 2635.969 | 0 | 0
August | 1088700000000 | 722370.07 | 01-AUG-19:30 | 177438.022 | 92719.3 | 39725.749 | 0 | 342468.626 | 11888 | 6622.186 | 0 | 48888.791 | 0 | 0 | 0 | 2619.396 | 0 | 0
September | 968714000000 | 638484.024 | 08-SEP-19:10 | 177438.022 | 92719.3 | 39114.528 | 0 | 260332.268 | 11888 | 5468.099 | 0 | 48888.791 | 0 | 0 | 0 | 2635.016 | 0 | 0
October | 814066000000 | 547959.909 | 02-OCT-19:10 | 177438.022 | 92719.3 | 38404.417 | 0 | 170234.357 | 11888 | 5259.012 | 0 | 48888.791 | 0 | 0 | 0 | 3128.011 | 0 | 0
November | 680532000000 | 457326.312 | 02-NOV-19:10 | 177438.022 | 92719.3 | 37725.19 | 0 | 83320.227 | 11888 | 2461.863 | 0 | 48888.791 | 0 | 0 | 0 | 2884.919 | 0 | 0
December | 625486000000 | 434516.29 | 13-DEC-20:00 | 177438.022 | 92719.3 | 37659.266 | 0 | 60082.903 | 11888 | 3019.175 | 0 | 48888.791 | 0 | 0 | 0 | 2820.833 | 0 | 0
Annual Sum or Average | 9868170000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 574335000000 | 434516.29 |  | 167588.533 | 91473.541 | 37659.266 | 0 | 60082.903 | 0 | 2219.985 | 0 | 48888.791 | 0 | 0 | 0 | 2330.386 | 0 | 0
Maximum of Months | 1129390000000 | 746015.496 |  | 177438.022 | 92719.3 | 40100.323 | 0 | 376832.732 | 11888 | 7425.295 | 0 | 48888.791 | 0 | 0 | 0 | 3170.294 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 206862.7 | 51754.46 | 0 | 258617.17
Cost per Total Building Area ($/m2) | 18.23 | 4.56 | 0 | 22.8
Cost per Net Conditioned Building Area ($/m2) | 18.23 | 4.56 | 0 | 22.8

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17481.38 | 1540.85 | 1540.85
Net Site Energy | 17481.38 | 1540.85 | 1540.85
Total Source Energy | 38927.08 | 3431.12 | 3431.12
Net Source Energy | 38927.08 | 3431.12 | 3431.12
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.23 | 1668.47 | 0 | 0 | 0 | 0
Cooling | 2111.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1136.47 | 0 | 0 | 0 | 0 | 0
Pumps | 85.4 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5843 | 0 | 0 | 0 | 44332.9
Refrigeration | 73.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8731.26 | 8750.12 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.409 | 0.444 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.255 | 0.129 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 4.092 | 0.255 | 0.129 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.255 | 0.129 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.255 | 0.129 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.255 | 0.129 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.255 | 0.129 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 4.092 | 0.255 | 0.129 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 4.092 | 0.255 | 0.129 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.255 | 0.129 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.255 | 0.129 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.255 | 0.129 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.255 | 0.129 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.255 | 0.129 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.255 | 0.129 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.255 | 0.129 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.255 | 0.129 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 4.092 | 0.255 | 0.129 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 4.092 | 0.255 | 0.129 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 4.092 | 0.255 | 0.129 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.255 | 0.129 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.255 | 0.129 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.255 | 0.129 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.255 | 0.129 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 432.93 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 781.15 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3177899.52 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 3151631.17 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30811.75 | 21031.18 | 9780.56 | 0.68 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8487.49 | 5807.83 | 2679.66 | 0.68 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30537.42 | 20839.17 | 9698.24 | 0.68 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8418.39 | 5759.91 | 2658.47 | 0.68 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 675084.69 | 418435.83 | 256648.86 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 44925.36 | 27883.42 | 17041.94 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 675084.69 | 418435.83 | 256648.86 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25571.95 | 17356.75 | 8215.2 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25578.18 | 17361.19 | 8216.99 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 78279.62 | 48555.04 | 29724.58 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5209.6 | 3219.81 | 1989.79 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 799206.18 | 525801.91 | 273404.28 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 40300.62 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 40517.5 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18096.97 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10703.66 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4397.74 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 14186.37 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41286.93 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15271.87 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46463.43 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 91559.79 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 433.42 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5917.83 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7182.16 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18386.18 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5119.69 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18367.75 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5124.66 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 840547.16 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 49650.74 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 840547.16 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18042.9 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18048.89 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 596.01 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 51475.21 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3370.4 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 265616.24 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.4 | 37.28 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.3 | 829.83 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 229.75 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.29 | 822.06 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 227.86 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 871.61 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 681.68 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 681.86 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 38.99 | 64871.52 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29121.05 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17354.22 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 174312.6251 | 274.8101 | 572.2673 | 0 | 0.0022 | 1017400 | 71096.9972
February | 156166.524 | 249.3164 | 527.9602 | 0 | 0.002 | 938669.9852 | 63983.3476
March | 165485.5672 | 274.4551 | 609.7661 | 0 | 0.0023 | 1084250 | 68749.114
April | 166122.2771 | 283.8463 | 652.9719 | 0 | 0.0025 | 1161180 | 69783.4072
May | 183774.2494 | 322.8761 | 765.8306 | 0 | 0.0029 | 1361980 | 78017.5579
June | 193394.7406 | 345.6015 | 834.4661 | 0 | 0.0031 | 1484100 | 82639.5061
July | 213713.3005 | 385.7242 | 940.8284 | 0 | 0.0035 | 1673310 | 91673.9635
August | 209286.213 | 377.3587 | 919.5 | 0 | 0.0034 | 1635370 | 89740.2815
September | 192537.7802 | 344.4069 | 832.4197 | 0 | 0.0031 | 1480470 | 82304.427
October | 169412.1466 | 294.4598 | 690.3754 | 0 | 0.0026 | 1227750 | 71626.4339
November | 157457.6645 | 262.5061 | 586.8777 | 0 | 0.0022 | 1043570 | 65540.0892
December | 169828.5767 | 272.7415 | 582.0596 | 0 | 0.0022 | 1034880 | 69729.9055
Annual Sum or Average | 2151490 | 3688.1028 | 8515.3229 | 0 | 0.032 | 15142900 | 904885.0306
Minimum of Months | 156166.524 | 249.3164 | 527.9602 | 0 | 0.002 | 938669.9852 | 63983.3476
Maximum of Months | 213713.3005 | 385.7242 | 940.8284 | 0 | 0.0035 | 1673310 | 91673.9635
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 586622000000 | 436007.311 | 24-JAN-20:00 | 177438.022 | 92719.3 | 36878.483 | 0 | 63224.653 | 11888 | 2666.028 | 0 | 48888.791 | 0 | 0 | 0 | 2304.035 | 0 | 0
February | 541228000000 | 404322.509 | 19-FEB-20:00 | 167588.533 | 91473.541 | 36878.483 | 0 | 42382.938 | 11888 | 2525.142 | 0 | 48888.791 | 0 | 0 | 0 | 2697.08 | 0 | 0
March | 625169000000 | 458296.735 | 28-MAR-19:10 | 177438.022 | 92719.3 | 37164.622 | 0 | 84344.533 | 11888 | 3436.369 | 0 | 48888.791 | 0 | 0 | 0 | 2417.098 | 0 | 0
April | 669524000000 | 495314.258 | 14-APR-19:10 | 177438.022 | 92719.3 | 37266.445 | 0 | 120302.816 | 11888 | 4338.001 | 0 | 48888.791 | 0 | 0 | 0 | 2472.884 | 0 | 0
May | 785302000000 | 558179.42 | 31-MAY-19:40 | 177438.022 | 92719.3 | 37542.735 | 0 | 181361.234 | 11888 | 5283.768 | 0 | 48888.791 | 0 | 0 | 0 | 3057.569 | 0 | 0
June | 855719000000 | 601406.467 | 08-JUN-19:10 | 177438.022 | 92719.3 | 37709.576 | 0 | 235508.513 | 0 | 6004.424 | 0 | 48888.791 | 0 | 0 | 0 | 3137.841 | 0 | 0
July | 964813000000 | 633915.514 | 03-JUL-19:10 | 177438.022 | 92719.3 | 38318.539 | 0 | 267007.496 | 0 | 6341.001 | 0 | 48888.791 | 0 | 0 | 0 | 3202.365 | 0 | 0
August | 942939000000 | 595414.37 | 14-AUG-19:30 | 177438.022 | 92719.3 | 37759.623 | 0 | 217784.467 | 11888 | 5828.249 | 0 | 48888.791 | 0 | 0 | 0 | 3107.917 | 0 | 0
September | 853623000000 | 555594.732 | 11-SEP-19:10 | 177438.022 | 92719.3 | 37390.915 | 0 | 178812.628 | 11888 | 5458.598 | 0 | 48888.791 | 0 | 0 | 0 | 2998.477 | 0 | 0
October | 707909000000 | 503219.965 | 20-OCT-19:10 | 177438.022 | 92719.3 | 37018.612 | 0 | 129081.784 | 11888 | 3760.137 | 0 | 48888.791 | 0 | 0 | 0 | 2425.319 | 0 | 0
November | 601712000000 | 430900.098 | 22-NOV-20:00 | 177438.022 | 92719.3 | 36879.188 | 0 | 57758.436 | 11888 | 2514.757 | 0 | 48888.791 | 0 | 0 | 0 | 2813.604 | 0 | 0
December | 596700000000 | 427727.849 | 04-DEC-20:00 | 177438.022 | 92719.3 | 36878.483 | 0 | 54659.555 | 11888 | 2486.176 | 0 | 48888.791 | 0 | 0 | 0 | 2769.522 | 0 | 0
Annual Sum or Average | 8731260000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 541228000000 | 404322.509 |  | 167588.533 | 91473.541 | 36878.483 | 0 | 42382.938 | 0 | 2486.176 | 0 | 48888.791 | 0 | 0 | 0 | 2304.035 | 0 | 0
Maximum of Months | 964813000000 | 633915.514 |  | 177438.022 | 92719.3 | 38318.539 | 0 | 267007.496 | 11888 | 6341.001 | 0 | 48888.791 | 0 | 0 | 0 | 3202.365 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 235399.5 | 92889.73 | 0 | 328289.22
Cost per Total Building Area ($/m2) | 20.75 | 8.19 | 0 | 28.94
Cost per Net Conditioned Building Area ($/m2) | 20.75 | 8.19 | 0 | 28.94

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15408.17 | 1358.11 | 1358.11
Net Site Energy | 15408.17 | 1358.11 | 1358.11
Total Source Energy | 33134.1 | 2920.52 | 2920.52
Net Source Energy | 33134.1 | 2920.52 | 2920.52
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 376.58 | 0 | 0 | 0 | 0
Cooling | 1528.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1145.06 | 0 | 0 | 0 | 0 | 0
Pumps | 70.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5650.97 | 0 | 0 | 0 | 44332.9
Refrigeration | 74.1 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8141.97 | 7266.19 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.569 | 0.637 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.44 | 0.272 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.44 | 0.272 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.44 | 0.272 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.44 | 0.272 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.44 | 0.272 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.44 | 0.272 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.44 | 0.272 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.44 | 0.272 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.44 | 0.272 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.44 | 0.272 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.44 | 0.272 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.44 | 0.272 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.44 | 0.272 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.44 | 0.272 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.44 | 0.272 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.44 | 0.272 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.44 | 0.272 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.44 | 0.272 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.44 | 0.272 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.44 | 0.272 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.44 | 0.272 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.44 | 0.272 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.44 | 0.272 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 432.93 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2293641.51 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2253912.32 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 38451.15 | 26956.03 | 11495.12 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 10665.06 | 7489.51 | 3175.55 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36317.53 | 25435.02 | 10882.5 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 10124.04 | 7103.64 | 3020.39 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 564565.59 | 369231.62 | 195333.97 | 0.65 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 49751.29 | 32786.65 | 16964.64 | 0.66 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 599146.61 | 391974.9 | 207171.71 | 0.65 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 30111.36 | 20999.61 | 9111.75 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 28555.51 | 19899.79 | 8655.72 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 70396.49 | 45932.39 | 24464.1 | 0.65 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4690.85 | 3046.67 | 1644.18 | 0.65 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 855395.41 | 585136.92 | 270258.49 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37565.29 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 40226.8 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22963.03 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10775.98 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4456.48 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 7626.96 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 38558.57 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 14867 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45828.68 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 87530.48 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 351.43 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7198.47 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6900.1 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12617.88 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3573.58 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12551.8 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3559.33 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 724970.81 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 44198.49 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 724970.81 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12311.84 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 12238.17 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 616.38 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 28369.63 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 1857.54 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 126694.15 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.22 | 20.47 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.55 | 984.46 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.43 | 274.12 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.46 | 927.75 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 259.72 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.75 | 1111.03 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.2 | 762.27 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.13 | 721.81 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 37.14 | 61781.95 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21018.05 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12411 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 90866.7249 | 79.6335 | 512.4838 | 0 | 0.0003 | 3091130 | 33012.6944
February | 81734.1199 | 71.6175 | 463.1887 | 0 | 0.0003 | 2793810 | 29701.4868
March | 89897.0146 | 78.7254 | 517.4443 | 0 | 0.0003 | 3121110 | 32692.2101
April | 86677.0459 | 75.8374 | 511.1121 | 0 | 0.0003 | 3082980 | 31558.4542
May | 90324.971 | 78.9285 | 550.6161 | 0 | 0.0003 | 3321360 | 32941.5325
June | 87890.834 | 76.7328 | 548.074 | 0 | 0.0003 | 3306090 | 32091.3178
July | 94966.179 | 82.7907 | 613.5229 | 0 | 0.0003 | 3700990 | 34739.7885
August | 96957.3282 | 84.4939 | 632.2215 | 0 | 0.0003 | 3813820 | 35485.9771
September | 92830.7047 | 80.9381 | 598.0918 | 0 | 0.0003 | 3607900 | 33953.6176
October | 93256.3987 | 81.4065 | 583.4378 | 0 | 0.0003 | 3519420 | 34056.2421
November | 87671.5488 | 76.6558 | 526.2229 | 0 | 0.0003 | 3174180 | 31948.7559
December | 91160.8362 | 79.8211 | 526.6899 | 0 | 0.0003 | 3176890 | 33157.8288
Annual Sum or Average | 1084230 | 947.5813 | 6583.1057 | 0 | 0.0037 | 39709700 | 395339.9059
Minimum of Months | 81734.1199 | 71.6175 | 463.1887 | 0 | 0.0003 | 2793810 | 29701.4868
Maximum of Months | 96957.3282 | 84.4939 | 632.2215 | 0 | 0.0003 | 3813820 | 35485.9771
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 633798000000 | 444484.915 | 26-JAN-20:10 | 177438.022 | 92719.3 | 37462.733 | 0 | 71013.402 | 11888 | 2229.106 | 0 | 48888.791 | 0 | 0 | 0 | 2845.561 | 0 | 0
February | 572836000000 | 428403.513 | 13-FEB-20:00 | 177438.022 | 92719.3 | 37425.632 | 0 | 54558.877 | 11888 | 2711.655 | 0 | 48888.791 | 0 | 0 | 0 | 2773.237 | 0 | 0
March | 639944000000 | 427523.927 | 29-MAR-19:00 | 177438.022 | 92719.3 | 37482.438 | 0 | 53856.556 | 11888 | 2488.144 | 0 | 48888.791 | 0 | 0 | 0 | 2762.677 | 0 | 0
April | 632127000000 | 475153.5 | 11-APR-19:10 | 177438.022 | 92719.3 | 37774.063 | 0 | 100570.166 | 11888 | 3472.268 | 0 | 48888.791 | 0 | 0 | 0 | 2402.89 | 0 | 0
May | 681003000000 | 473162.221 | 30-MAY-19:10 | 177438.022 | 92719.3 | 37839.752 | 0 | 98755.962 | 11888 | 3226.969 | 0 | 48888.791 | 0 | 0 | 0 | 2405.425 | 0 | 0
June | 677872000000 | 468632.139 | 28-JUN-19:10 | 177438.022 | 92719.3 | 37842.587 | 0 | 93806.537 | 11888 | 3136.837 | 0 | 48888.791 | 0 | 0 | 0 | 2912.065 | 0 | 0
July | 758843000000 | 475214.579 | 10-JUL-19:10 | 177438.022 | 92719.3 | 37930.867 | 0 | 100151.936 | 11888 | 3259.758 | 0 | 48888.791 | 0 | 0 | 0 | 2937.906 | 0 | 0
August | 781976000000 | 500530.614 | 16-AUG-19:10 | 177438.022 | 92719.3 | 37817.689 | 0 | 125131.339 | 11888 | 3718.433 | 0 | 48888.791 | 0 | 0 | 0 | 2929.041 | 0 | 0
September | 739755000000 | 485995.243 | 25-SEP-19:10 | 177438.022 | 92719.3 | 37894.009 | 0 | 110630.454 | 11888 | 3594.087 | 0 | 48888.791 | 0 | 0 | 0 | 2942.58 | 0 | 0
October | 721613000000 | 469251.361 | 05-OCT-19:00 | 177438.022 | 92719.3 | 37615.382 | 0 | 94609.167 | 11888 | 3238.394 | 0 | 48888.791 | 0 | 0 | 0 | 2854.306 | 0 | 0
November | 650825000000 | 446468.128 | 09-NOV-20:30 | 177438.022 | 92719.3 | 37412.21 | 0 | 72413.857 | 11888 | 2890.108 | 0 | 48888.791 | 0 | 0 | 0 | 2817.84 | 0 | 0
December | 651381000000 | 448188.602 | 18-DEC-20:10 | 177438.022 | 92719.3 | 37362.451 | 0 | 74770.576 | 11888 | 2276.22 | 0 | 48888.791 | 0 | 0 | 0 | 2845.242 | 0 | 0
Annual Sum or Average | 8141970000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 572836000000 | 427523.927 |  | 177438.022 | 92719.3 | 37362.451 | 0 | 53856.556 | 11888 | 2229.106 | 0 | 48888.791 | 0 | 0 | 0 | 2402.89 | 0 | 0
Maximum of Months | 781976000000 | 500530.614 |  | 177438.022 | 92719.3 | 37930.867 | 0 | 125131.339 | 11888 | 3718.433 | 0 | 48888.791 | 0 | 0 | 0 | 2942.58 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 278600.48 | 61076.84 | 0 | 339677.32
Cost per Total Building Area ($/m2) | 24.56 | 5.38 | 0 | 29.94
Cost per Net Conditioned Building Area ($/m2) | 24.56 | 5.38 | 0 | 29.94

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16145.35 | 1423.09 | 1423.09
Net Site Energy | 16145.35 | 1423.09 | 1423.09
Total Source Energy | 40011.41 | 3526.7 | 3526.7
Net Source Energy | 40011.41 | 3526.7 | 3526.7
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.94 | 924.4 | 0 | 0 | 0 | 0
Cooling | 2367.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1160.23 | 0 | 0 | 0 | 0 | 0
Pumps | 79.17 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4975.99 | 0 | 0 | 0 | 44332.9
Refrigeration | 74.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9006.31 | 7139.04 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.273 | 0.288 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.647 | 2.185 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 5.835 | 0.251 | 0.11 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 5.835 | 0.251 | 0.11 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 5.835 | 0.251 | 0.11 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 5.835 | 0.251 | 0.11 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 5.835 | 0.251 | 0.11 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 5.835 | 0.251 | 0.11 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 432.93 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 781.15 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2329637.27 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2665626.39 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31835.87 | 21739.97 | 10095.9 | 0.68 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8186.58 | 5593.76 | 2592.83 | 0.68 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31477.53 | 21493.21 | 9984.33 | 0.68 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8126.47 | 5552.61 | 2573.86 | 0.68 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 568937.11 | 353209.8 | 215727.31 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 40092.78 | 25030.83 | 15061.95 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 499372.21 | 316191.2 | 183181.01 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24866.81 | 16902.77 | 7964.04 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 24524.55 | 16673.28 | 7851.27 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 56908.18 | 35891.33 | 21016.85 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4042.63 | 2523.26 | 1519.37 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 801169.37 | 529752.85 | 271416.52 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41009.44 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 28883.77 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18919.68 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11416.18 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3915.22 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 9795.76 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41986.59 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 15990.73 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46497.69 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 90673.18 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 355.94 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6020.11 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7062.3 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16410.22 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4333.64 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16405.21 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4334.45 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 757424.29 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 45227.8 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 757424.29 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15955.21 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15940.93 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 571.63 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 40987.52 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2683.71 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 208713.29 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.28 | 26.47 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.51 | 960.29 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 247.28 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.49 | 949.4 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 245.48 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.46 | 930.23 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.17 | 745.23 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.16 | 735.7 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 39.47 | 65667.67 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21347.9 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14678.07 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 182671.5846 | 262.7599 | 911.9009 | 0 | 0.0018 | 4546610 | 73299.2532
February | 161763.5919 | 237.7745 | 855.3627 | 0 | 0.0017 | 4264960 | 65438.6213
March | 178032.7486 | 263.0928 | 954.5908 | 0 | 0.0019 | 4759790 | 72166.0018
April | 183940.196 | 279.9902 | 1063.0349 | 0 | 0.0021 | 5300890 | 75409.5156
May | 199070.4768 | 307.4313 | 1191.9282 | 0 | 0.0023 | 5943810 | 82070.8148
June | 224995.9702 | 353.4438 | 1403.3157 | 0 | 0.0027 | 6998180 | 93380.1344
July | 245935.2506 | 388.763 | 1556.7175 | 0 | 0.003 | 7763270 | 102322.7155
August | 242489.5186 | 382.9114 | 1531.1025 | 0 | 0.0029 | 7635510 | 100847.0317
September | 213697.4798 | 334.4634 | 1321.2693 | 0 | 0.0025 | 6588970 | 88562.9017
October | 188897.1972 | 290.1332 | 1116.0979 | 0 | 0.0021 | 5565600 | 77711.7096
November | 169547.7425 | 253.3876 | 935.7303 | 0 | 0.0018 | 4665880 | 69021.1164
December | 179402.7422 | 260.9224 | 922.5072 | 0 | 0.0018 | 4599630 | 72285.3213
Annual Sum or Average | 2370440 | 3615.0734 | 13763.5578 | 0 | 0.0266 | 68633100 | 972515.1374
Minimum of Months | 161763.5919 | 237.7745 | 855.3627 | 0 | 0.0017 | 4264960 | 65438.6213
Maximum of Months | 245935.2506 | 388.763 | 1556.7175 | 0 | 0.003 | 7763270 | 102322.7155
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 596624000000 | 394987.998 | 18-JAN-20:49 | 177438.022 | 92719.3 | 37415.488 | 0 | 22591.917 | 11888 | 1500.691 | 0 | 48888.791 | 0 | 0 | 0 | 2545.79 | 0 | 0
February | 559666000000 | 411855.09 | 27-FEB-20:10 | 177438.022 | 92719.3 | 37415.488 | 0 | 39019.938 | 11888 | 1796.981 | 0 | 48888.791 | 0 | 0 | 0 | 2688.571 | 0 | 0
March | 624599000000 | 437363.992 | 30-MAR-19:10 | 177438.022 | 92719.3 | 37512.431 | 0 | 63923.874 | 11888 | 2178.292 | 0 | 48888.791 | 0 | 0 | 0 | 2815.283 | 0 | 0
April | 695604000000 | 514498.564 | 21-APR-19:10 | 177438.022 | 92719.3 | 38083.611 | 0 | 139566.282 | 11888 | 3414.404 | 0 | 48888.791 | 0 | 0 | 0 | 2500.154 | 0 | 0
May | 779970000000 | 548088.909 | 31-MAY-19:10 | 177438.022 | 92719.3 | 38404.512 | 0 | 171964.463 | 11888 | 3640.966 | 0 | 48888.791 | 0 | 0 | 0 | 3144.855 | 0 | 0
June | 918329000000 | 674258.202 | 27-JUN-19:10 | 177438.022 | 92719.3 | 39578.454 | 0 | 296742.034 | 11888 | 4415.126 | 0 | 48888.791 | 0 | 0 | 0 | 2588.475 | 0 | 0
July | 1018730000000 | 664594.573 | 25-JUL-19:10 | 177438.022 | 92719.3 | 39431.467 | 0 | 286330.425 | 11888 | 5303.312 | 0 | 48888.791 | 0 | 0 | 0 | 2595.257 | 0 | 0
August | 1001960000000 | 632237.193 | 04-AUG-19:10 | 177438.022 | 92719.3 | 39210.704 | 0 | 253438.412 | 11888 | 6041.121 | 0 | 48888.791 | 0 | 0 | 0 | 2612.843 | 0 | 0
September | 864632000000 | 573141.446 | 01-SEP-19:00 | 177438.022 | 92719.3 | 38989.824 | 0 | 195865.035 | 11888 | 4766.142 | 0 | 48888.791 | 0 | 0 | 0 | 2586.333 | 0 | 0
October | 730340000000 | 498156.825 | 03-OCT-19:10 | 177438.022 | 92719.3 | 37985.406 | 0 | 123440.501 | 11888 | 3331.059 | 0 | 48888.791 | 0 | 0 | 0 | 2465.746 | 0 | 0
November | 612276000000 | 424337.372 | 09-NOV-20:19 | 177438.022 | 92719.3 | 37415.488 | 0 | 51238.528 | 11888 | 1990.862 | 0 | 48888.791 | 0 | 0 | 0 | 2758.382 | 0 | 0
December | 603582000000 | 407941.12 | 05-DEC-20:10 | 177438.022 | 92719.3 | 37415.488 | 0 | 35602.192 | 11888 | 1756.86 | 0 | 48888.791 | 0 | 0 | 0 | 2232.467 | 0 | 0
Annual Sum or Average | 9006310000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 559666000000 | 394987.998 |  | 177438.022 | 92719.3 | 37415.488 | 0 | 22591.917 | 11888 | 1500.691 | 0 | 48888.791 | 0 | 0 | 0 | 2232.467 | 0 | 0
Maximum of Months | 1018730000000 | 674258.202 |  | 177438.022 | 92719.3 | 39578.454 | 0 | 296742.034 | 11888 | 6041.121 | 0 | 48888.791 | 0 | 0 | 0 | 3144.855 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 230054.02 | 57603.06 | 0 | 287657.08
Cost per Total Building Area ($/m2) | 20.28 | 5.08 | 0 | 25.35
Cost per Net Conditioned Building Area ($/m2) | 20.28 | 5.08 | 0 | 25.35

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16081.01 | 1417.42 | 1417.42
Net Site Energy | 16081.01 | 1417.42 | 1417.42
Total Source Energy | 32340.63 | 2850.58 | 2850.58
Net Source Energy | 32340.63 | 2850.58 | 2850.58
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 967.04 | 0 | 0 | 0 | 0
Cooling | 812.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1114.46 | 0 | 0 | 0 | 0 | 0
Pumps | 56.22 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6496.32 | 0 | 0 | 0 | 44332.9
Refrigeration | 71.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7379.01 | 8702 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.501 | 0.553 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 2.377 | 3.691 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.392 | 0.253 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 4.092 | 0.392 | 0.253 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.392 | 0.253 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.392 | 0.253 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 4.092 | 0.392 | 0.253 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 4.092 | 0.392 | 0.253 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 4.092 | 0.392 | 0.253 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 4.092 | 0.392 | 0.253 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 4.092 | 0.392 | 0.253 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 432.93 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 781.15 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1549714.67 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2464816.05 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33869.95 | 23775.6 | 10094.36 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9110.36 | 6400.35 | 2710.01 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 29471.11 | 20661.08 | 8810.04 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7964.22 | 5589.27 | 2374.95 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 579477.64 | 385540.19 | 193937.45 | 0.67 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 52571.76 | 35585.2 | 16986.56 | 0.68 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 493229.57 | 344991.2 | 148238.36 | 0.7 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25674.69 | 17959.45 | 7715.23 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 22127.77 | 15460.01 | 6667.76 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 54155.75 | 37490.94 | 16664.82 | 0.69 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3823.12 | 2600.57 | 1222.55 | 0.68 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 779104.11 | 544089.18 | 235014.93 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 36635.86 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 26577.92 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24153.69 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11200.47 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4060.38 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 9252.94 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 37612.34 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 13708.21 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45099.08 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 83223.61 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 352.56 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7530.66 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6531.6 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13895 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3890.84 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13716.18 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3842.34 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 767298.31 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 47919.96 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 767298.31 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13443.23 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13195.42 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 618.36 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 35365.36 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 2315.59 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 153157.82 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.26 | 24.18 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 873.4 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 235.37 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.19 | 757.75 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.32 | 205.28 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.94 | 1237.22 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.03 | 657.12 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.89 | 564.98 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 34.63 | 57606.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14200.99 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13572.32 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 98694.7411 | 86.9199 | 480.396 | 0 | 0.0003 | 2897170 | 35624.0854
February | 85394.3845 | 75.0411 | 445.222 | 0 | 0.0003 | 2685230 | 30913.495
March | 94393.6501 | 82.9904 | 484.7806 | 0 | 0.0003 | 2923770 | 34148.8478
April | 89499.9402 | 78.5817 | 478.6533 | 0 | 0.0003 | 2886930 | 32436.4322
May | 90927.4948 | 79.7297 | 505.1366 | 0 | 0.0003 | 3046770 | 33011.3108
June | 87216.3733 | 76.4048 | 497.1934 | 0 | 0.0003 | 2998930 | 31702.6509
July | 90372.7093 | 79.0856 | 530.2642 | 0 | 0.0003 | 3198490 | 32895.9621
August | 90204.0596 | 78.9354 | 529.7389 | 0 | 0.0003 | 3195320 | 32835.9892
September | 88978.9038 | 77.8356 | 527.4973 | 0 | 0.0003 | 3181830 | 32405.1219
October | 91368.6368 | 80.0125 | 526.1956 | 0 | 0.0003 | 3173900 | 33228.2411
November | 88632.7418 | 77.7755 | 482.0295 | 0 | 0.0003 | 2907340 | 32146.5942
December | 97229.6731 | 85.5937 | 479.6803 | 0 | 0.0003 | 2892890 | 35114.8392
Annual Sum or Average | 1092910 | 958.906 | 5966.7878 | 0 | 0.0036 | 35988600 | 396463.5697
Minimum of Months | 85394.3845 | 75.0411 | 445.222 | 0 | 0.0003 | 2685230 | 30913.495
Maximum of Months | 98694.7411 | 86.9199 | 530.2642 | 0 | 0.0003 | 3198490 | 35624.0854
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 594028000000 | 395952.637 | 27-JAN-20:30 | 177438.022 | 92719.3 | 36438.986 | 0 | 24517.258 | 11888 | 1888.233 | 0 | 48888.791 | 0 | 0 | 0 | 2174.047 | 0 | 0
February | 550573000000 | 422245.77 | 15-FEB-20:10 | 177438.022 | 92719.3 | 36520.017 | 0 | 49530.571 | 11888 | 2482.094 | 0 | 48888.791 | 0 | 0 | 0 | 2778.975 | 0 | 0
March | 599483000000 | 398208.122 | 30-MAR-19:00 | 177438.022 | 92719.3 | 36480.664 | 0 | 26355.658 | 11888 | 1768.616 | 0 | 48888.791 | 0 | 0 | 0 | 2669.072 | 0 | 0
April | 591930000000 | 423917.767 | 13-APR-19:49 | 177438.022 | 92719.3 | 36779.886 | 0 | 51459.734 | 11888 | 1990.489 | 0 | 48888.791 | 0 | 0 | 0 | 2753.545 | 0 | 0
May | 624703000000 | 427104.364 | 25-MAY-19:19 | 177438.022 | 92719.3 | 36768.465 | 0 | 54145.761 | 11888 | 2432.762 | 0 | 48888.791 | 0 | 0 | 0 | 2823.263 | 0 | 0
June | 614894000000 | 437553.669 | 16-JUN-19:30 | 177438.022 | 92719.3 | 37002.982 | 0 | 64247.322 | 11888 | 3019.036 | 0 | 48888.791 | 0 | 0 | 0 | 2350.216 | 0 | 0
July | 655811000000 | 496012.342 | 02-JUL-19:30 | 167588.533 | 91473.541 | 37190.646 | 0 | 131999.562 | 11888 | 3930.406 | 0 | 48888.791 | 0 | 0 | 0 | 3052.862 | 0 | 0
August | 655161000000 | 431807.95 | 14-AUG-19:10 | 177438.022 | 92719.3 | 36887.839 | 0 | 58508.988 | 11888 | 2658.5 | 0 | 48888.791 | 0 | 0 | 0 | 2818.511 | 0 | 0
September | 652395000000 | 494153.862 | 28-SEP-19:00 | 177438.022 | 92719.3 | 37202.804 | 0 | 119443.617 | 11888 | 3546.379 | 0 | 48888.791 | 0 | 0 | 0 | 3026.948 | 0 | 0
October | 650768000000 | 444968.232 | 16-OCT-19:10 | 177438.022 | 92719.3 | 36636.246 | 0 | 71570.872 | 11888 | 2941.343 | 0 | 48888.791 | 0 | 0 | 0 | 2885.658 | 0 | 0
November | 596115000000 | 410347.661 | 15-NOV-20:00 | 177438.022 | 92719.3 | 36450.558 | 0 | 38075.628 | 11888 | 2144.428 | 0 | 48888.791 | 0 | 0 | 0 | 2742.935 | 0 | 0
December | 593152000000 | 394601.081 | 07-DEC-20:00 | 177438.022 | 92719.3 | 36438.986 | 0 | 22896.109 | 11888 | 1766.628 | 0 | 48888.791 | 0 | 0 | 0 | 2565.245 | 0 | 0
Annual Sum or Average | 7379010000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 550573000000 | 394601.081 |  | 167588.533 | 91473.541 | 36438.986 | 0 | 22896.109 | 11888 | 1766.628 | 0 | 48888.791 | 0 | 0 | 0 | 2174.047 | 0 | 0
Maximum of Months | 655811000000 | 496012.342 |  | 177438.022 | 92719.3 | 37202.804 | 0 | 131999.562 | 11888 | 3930.406 | 0 | 48888.791 | 0 | 0 | 0 | 3052.862 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 296940.82 | 73274.4 | 0 | 370215.21
Cost per Total Building Area ($/m2) | 26.17 | 6.46 | 0 | 32.63
Cost per Net Conditioned Building Area ($/m2) | 26.17 | 6.46 | 0 | 32.63

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18888.38 | 1664.87 | 1664.87
Net Site Energy | 18888.38 | 1664.87 | 1664.87
Total Source Energy | 41415.34 | 3650.44 | 3650.44
Net Source Energy | 41415.34 | 3650.44 | 3650.44
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.1 | 2661.02 | 0 | 0 | 0 | 0
Cooling | 1767.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1128.15 | 0 | 0 | 0 | 0 | 0
Pumps | 77.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6619.46 | 0 | 0 | 0 | 44332.9
Refrigeration | 71.83 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8369.25 | 10519.13 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.33 | 0.352 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.681 | 0.759 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.354 | 0.355 | 0.274 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.354 | 0.355 | 0.274 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.354 | 0.355 | 0.274 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.354 | 0.355 | 0.274 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.354 | 0.355 | 0.274 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.354 | 0.355 | 0.274 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.354 | 0.355 | 0.274 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.354 | 0.355 | 0.274 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.355 | 0.274 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.355 | 0.274 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.354 | 0.355 | 0.274 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.354 | 0.355 | 0.274 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.355 | 0.274 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.355 | 0.274 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.354 | 0.355 | 0.274 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.354 | 0.355 | 0.274 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.354 | 0.355 | 0.274 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.354 | 0.355 | 0.274 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.354 | 0.355 | 0.274 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.355 | 0.274 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.355 | 0.274 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.355 | 0.274 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.355 | 0.274 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 432.93 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 781.15 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3225973.3 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 3478471.01 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33445.98 | 23014.31 | 10431.67 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9046.51 | 6238.11 | 2808.39 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33197.99 | 22838.16 | 10359.82 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8998.82 | 6204.41 | 2794.41 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 686556.49 | 433580.94 | 252975.55 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 42336.4 | 26663.18 | 15673.22 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 686556.49 | 433580.94 | 252975.55 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27911.78 | 19119.88 | 8791.9 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27740.89 | 18999.37 | 8741.52 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 79597.94 | 50306.3 | 29291.64 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5319.58 | 3347.04 | 1972.54 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 850599.52 | 569065.89 | 281533.64 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41257.28 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 39314 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17445.52 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11006.87 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3949.54 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 13190.73 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 42309.23 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16735.6 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47010.72 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 92466.51 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 364.27 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6063.97 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7040.84 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16176.88 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4485.55 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16167.18 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4488.06 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 898860.19 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 51769.5 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 898860.19 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15804.08 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 15794.63 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 615.29 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 58511.62 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3831.12 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 299164.19 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.33 | 31.17 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.3 | 826.37 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 224.65 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.29 | 819.84 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 223.39 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.25 | 792.62 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 683.34 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 678.88 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 38.11 | 63399.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29561.58 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19153.94 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 173879.8944 | 265.3982 | 594.6714 | 0 | 0.0026 | 36961.6388 | 70015.7974
February | 153417.3723 | 236.6567 | 538.4441 | 0 | 0.0023 | 33468.133 | 62003.9818
March | 158581.2119 | 255.3515 | 615.8095 | 0 | 0.0026 | 38282.344 | 65072.006
April | 145018.6159 | 242.2335 | 611.2956 | 0 | 0.0026 | 38005.7079 | 60304.162
May | 157487.8857 | 274.3643 | 726.2651 | 0 | 0.003 | 45158.3778 | 66522.8253
June | 170367.8543 | 306.7877 | 840.7938 | 0 | 0.0035 | 52283.4734 | 72876.303
July | 186456.0312 | 340.5035 | 946.3924 | 0 | 0.0039 | 58851.6614 | 80192.0426
August | 185673.1457 | 339.4821 | 944.6734 | 0 | 0.0039 | 58744.9043 | 79892.6716
September | 156205.41 | 279.8707 | 763.091 | 0 | 0.0031 | 47451.1407 | 66688.8843
October | 152515.6604 | 264.1695 | 694.8733 | 0 | 0.0029 | 43205.8777 | 64282.426
November | 149122.0427 | 246.9276 | 616.6655 | 0 | 0.0026 | 38338.6629 | 61813.0057
December | 166193.1192 | 258.7159 | 596.2682 | 0 | 0.0025 | 37063.4926 | 67382.3671
Annual Sum or Average | 1954920 | 3310.4612 | 8489.2434 | 0 | 0.0353 | 527815.4145 | 817046.4728
Minimum of Months | 145018.6159 | 236.6567 | 538.4441 | 0 | 0.0023 | 33468.133 | 60304.162
Maximum of Months | 186456.0312 | 340.5035 | 946.3924 | 0 | 0.0039 | 58851.6614 | 80192.0426
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 586079000000 | 391234.17 | 05-JAN-20:00 | 177438.022 | 92719.3 | 36655.681 | 0 | 19588.622 | 11888 | 1593.558 | 0 | 48888.791 | 0 | 0 | 0 | 2462.196 | 0 | 0
February | 530684000000 | 392800.882 | 15-FEB-20:00 | 177438.022 | 92719.3 | 36655.681 | 0 | 21160.73 | 11888 | 1517.061 | 0 | 48888.791 | 0 | 0 | 0 | 2533.298 | 0 | 0
March | 607020000000 | 451467.437 | 09-MAR-20:00 | 177438.022 | 92719.3 | 36668.944 | 0 | 78016.365 | 11888 | 2919.423 | 0 | 48888.791 | 0 | 0 | 0 | 2928.591 | 0 | 0
April | 602634000000 | 450815.39 | 05-APR-19:10 | 177438.022 | 92719.3 | 36810.825 | 0 | 76848.536 | 11888 | 3325.093 | 0 | 48888.791 | 0 | 0 | 0 | 2896.824 | 0 | 0
May | 716050000000 | 527299.464 | 15-MAY-19:10 | 177438.022 | 92719.3 | 36947.44 | 0 | 151664.482 | 11888 | 4771.645 | 0 | 48888.791 | 0 | 0 | 0 | 2981.784 | 0 | 0
June | 829028000000 | 614489.144 | 30-JUN-18:10 | 157821.345 | 80166.318 | 37365.318 | 0 | 281542.576 | 0 | 6134.125 | 0 | 48888.791 | 0 | 0 | 0 | 2570.671 | 0 | 0
July | 933176000000 | 659390.793 | 24-JUL-19:30 | 177438.022 | 92719.3 | 37340.642 | 0 | 281391.352 | 11888 | 6587.321 | 0 | 48888.791 | 0 | 0 | 0 | 3137.366 | 0 | 0
August | 931483000000 | 658910.882 | 17-AUG-19:10 | 177438.022 | 92719.3 | 37345.701 | 0 | 280886.826 | 11888 | 6608.413 | 0 | 48888.791 | 0 | 0 | 0 | 3135.829 | 0 | 0
September | 752404000000 | 506153.205 | 09-SEP-19:00 | 157739.045 | 88982.023 | 36905.964 | 0 | 153966.422 | 11888 | 4870.322 | 0 | 48888.791 | 0 | 0 | 0 | 2912.639 | 0 | 0
October | 685090000000 | 516781.252 | 02-OCT-19:00 | 177438.022 | 92719.3 | 36690.936 | 0 | 142259.915 | 11888 | 3952.741 | 0 | 48888.791 | 0 | 0 | 0 | 2943.548 | 0 | 0
November | 607913000000 | 461104.269 | 03-NOV-19:10 | 177438.022 | 92719.3 | 36655.681 | 0 | 88090.524 | 11888 | 3040.314 | 0 | 48888.791 | 0 | 0 | 0 | 2383.637 | 0 | 0
December | 587694000000 | 389592.495 | 06-DEC-20:00 | 177438.022 | 92719.3 | 36655.681 | 0 | 17945.042 | 11888 | 1619.006 | 0 | 48888.791 | 0 | 0 | 0 | 2438.653 | 0 | 0
Annual Sum or Average | 8369250000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 530684000000 | 389592.495 |  | 157739.045 | 80166.318 | 36655.681 | 0 | 17945.042 | 0 | 1517.061 | 0 | 48888.791 | 0 | 0 | 0 | 2383.637 | 0 | 0
Maximum of Months | 933176000000 | 659390.793 |  | 177438.022 | 92719.3 | 37365.318 | 0 | 281542.576 | 11888 | 6608.413 | 0 | 48888.791 | 0 | 0 | 0 | 3137.366 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 164315.66 | 105338.03 | 0 | 269653.7
Cost per Total Building Area ($/m2) | 14.48 | 9.28 | 0 | 23.77
Cost per Net Conditioned Building Area ($/m2) | 14.48 | 9.28 | 0 | 23.77

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17440.61 | 1537.26 | 1537.26
Net Site Energy | 17440.61 | 1537.26 | 1537.26
Total Source Energy | 36892.01 | 3251.75 | 3251.75
Net Source Energy | 36892.01 | 3251.75 | 3251.75
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.18 | 1712.26 | 0 | 0 | 0 | 0
Cooling | 1388.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1166.31 | 0 | 0 | 0 | 0 | 0
Pumps | 66.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6472.24 | 0 | 0 | 0 | 44332.9
Refrigeration | 71.86 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8017.46 | 9423.15 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.335 | 0.358 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 1.079 | 1.287 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.362 | 0.225 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 4.092 | 0.362 | 0.225 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.362 | 0.225 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.362 | 0.225 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.362 | 0.225 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.362 | 0.225 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 4.092 | 0.362 | 0.225 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 4.092 | 0.362 | 0.225 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.362 | 0.225 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.362 | 0.225 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.362 | 0.225 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.362 | 0.225 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.362 | 0.225 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.362 | 0.225 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.362 | 0.225 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.362 | 0.225 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 4.092 | 0.362 | 0.225 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 4.092 | 0.362 | 0.225 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 4.092 | 0.362 | 0.225 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.362 | 0.225 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.362 | 0.225 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.362 | 0.225 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.362 | 0.225 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 432.93 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 781.15 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1550239.15 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2816922.23 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 26208.45 | 16956.67 | 9251.78 | 0.65 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7048.44 | 4564.71 | 2483.73 | 0.65 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25999.61 | 16819.73 | 9179.89 | 0.65 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 7011.41 | 4540.46 | 2470.96 | 0.65 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 364749.29 | 225820.75 | 138928.54 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 31083.61 | 18641.16 | 12442.45 | 0.6 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 364749.29 | 225820.75 | 138928.54 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 20375.79 | 13124.25 | 7251.55 | 0.64 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 20358.47 | 13112.92 | 7245.55 | 0.64 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 43502.17 | 27007.17 | 16495 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3588 | 2153.38 | 1434.63 | 0.6 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 838897.04 | 533414.06 | 305482.98 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 38685.33 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 31588.11 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16285.05 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10050.68 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3296.68 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 12618.53 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 39723 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16025.8 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46181.46 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 84820.29 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 290.23 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5012.65 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6658.93 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16575.91 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4579.81 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16542.36 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 4579.59 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 730040.18 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 42838.11 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 730040.18 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16121.65 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 16103.14 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 509.05 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 46044.69 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3014.83 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 246029.54 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.41 | 38.55 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.53 | 975.01 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 262.63 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.52 | 967.1 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 261.23 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.33 | 847.44 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.19 | 758.34 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.19 | 757.69 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 42.32 | 70107.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14205.8 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15511.17 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 217659.9937 | 331.0171 | 723.2036 | 0 | 0.0029 | 751698.8836 | 88422.0445
February | 194030.9042 | 298.0711 | 660.8712 | 0 | 0.0027 | 686936.5299 | 79116.1743
March | 211658.106 | 328.7494 | 740.3912 | 0 | 0.003 | 769623.4606 | 86656.7313
April | 205154.1429 | 326.0937 | 757.9432 | 0 | 0.003 | 787930.1893 | 84724.2939
May | 223291.891 | 362.2036 | 864.3551 | 0 | 0.0034 | 898609.215 | 92928.8672
June | 227326.2299 | 373.3951 | 905.1261 | 0 | 0.0036 | 941030.7957 | 95063.7286
July | 246766.5648 | 408.4911 | 999.6565 | 0 | 0.004 | 1039330 | 103503.7028
August | 238783.586 | 394.8485 | 965.0015 | 0 | 0.0038 | 1003300 | 100113.357
September | 217923.2593 | 357.966 | 867.7722 | 0 | 0.0034 | 902195.2788 | 91133.1193
October | 209819.8545 | 338.1942 | 800.5343 | 0 | 0.0032 | 832243.1237 | 87110.6105
November | 201684.8357 | 315.7117 | 718.7803 | 0 | 0.0029 | 747179.6559 | 82814.0905
December | 216663.2562 | 330.2732 | 724.0699 | 0 | 0.0029 | 752606.0254 | 88092.8485
Annual Sum or Average | 2610760 | 4165.0149 | 9727.7052 | 0 | 0.0389 | 10112700 | 1079680
Minimum of Months | 194030.9042 | 298.0711 | 660.8712 | 0 | 0.0027 | 686936.5299 | 79116.1743
Maximum of Months | 246766.5648 | 408.4911 | 999.6565 | 0 | 0.004 | 1039330 | 103503.7028
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 595956000000 | 396841.463 | 26-JAN-20:30 | 177438.022 | 92719.3 | 37813.537 | 0 | 24019.385 | 11888 | 1535.793 | 0 | 48888.791 | 0 | 0 | 0 | 2538.635 | 0 | 0
February | 544612000000 | 400932.378 | 14-FEB-20:30 | 177438.022 | 92719.3 | 37831.759 | 0 | 28429.428 | 11888 | 1561.863 | 0 | 48888.791 | 0 | 0 | 0 | 2175.214 | 0 | 0
March | 610167000000 | 415546.166 | 20-MAR-19:10 | 177438.022 | 92719.3 | 37966.706 | 0 | 42082.603 | 11888 | 1851.165 | 0 | 48888.791 | 0 | 0 | 0 | 2711.578 | 0 | 0
April | 624681000000 | 455423.519 | 21-APR-19:10 | 177438.022 | 92719.3 | 38482.575 | 0 | 81188.183 | 11888 | 2446.592 | 0 | 48888.791 | 0 | 0 | 0 | 2372.057 | 0 | 0
May | 712428000000 | 487533.49 | 30-MAY-19:10 | 177438.022 | 92719.3 | 38694.373 | 0 | 112516.669 | 11888 | 2919.875 | 0 | 48888.791 | 0 | 0 | 0 | 2468.461 | 0 | 0
June | 746061000000 | 517338.188 | 28-JUN-19:19 | 177438.022 | 92719.3 | 39109.015 | 0 | 141092.444 | 11888 | 3110.152 | 0 | 48888.791 | 0 | 0 | 0 | 3092.464 | 0 | 0
July | 823997000000 | 536300.259 | 18-JUL-19:10 | 177438.022 | 92719.3 | 39289.451 | 0 | 170826.86 | 0 | 4542.528 | 0 | 48888.791 | 0 | 0 | 0 | 2595.308 | 0 | 0
August | 795429000000 | 531436.294 | 01-AUG-19:10 | 177438.022 | 92719.3 | 39201.657 | 0 | 154450.489 | 11888 | 4310.648 | 0 | 48888.791 | 0 | 0 | 0 | 2539.387 | 0 | 0
September | 715271000000 | 477801.017 | 13-SEP-19:10 | 177438.022 | 92719.3 | 38697.343 | 0 | 101722.174 | 11888 | 3457.401 | 0 | 48888.791 | 0 | 0 | 0 | 2989.986 | 0 | 0
October | 659812000000 | 458502.499 | 02-OCT-19:10 | 177438.022 | 92719.3 | 38337.648 | 0 | 83654.267 | 11888 | 2656.632 | 0 | 48888.791 | 0 | 0 | 0 | 2919.839 | 0 | 0
November | 592373000000 | 416512.646 | 09-NOV-20:00 | 177438.022 | 92719.3 | 37879.169 | 0 | 43099.118 | 11888 | 1868.693 | 0 | 48888.791 | 0 | 0 | 0 | 2731.553 | 0 | 0
December | 596675000000 | 394132.265 | 05-DEC-20:30 | 177438.022 | 92719.3 | 37813.537 | 0 | 21742.431 | 11888 | 1536.376 | 0 | 48888.791 | 0 | 0 | 0 | 2105.809 | 0 | 0
Annual Sum or Average | 8017460000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 544612000000 | 394132.265 |  | 177438.022 | 92719.3 | 37813.537 | 0 | 21742.431 | 0 | 1535.793 | 0 | 48888.791 | 0 | 0 | 0 | 2105.809 | 0 | 0
Maximum of Months | 823997000000 | 536300.259 |  | 177438.022 | 92719.3 | 39289.451 | 0 | 170826.86 | 11888 | 4542.528 | 0 | 48888.791 | 0 | 0 | 0 | 3092.464 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 82433.38 | 67487.81 | 0 | 149921.19
Cost per Total Building Area ($/m2) | 7.27 | 5.95 | 0 | 13.21
Cost per Net Conditioned Building Area ($/m2) | 7.27 | 5.95 | 0 | 13.21

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17939.83 | 1581.26 | 1581.26
Net Site Energy | 17939.83 | 1581.26 | 1581.26
Total Source Energy | 24390.62 | 2149.85 | 2149.85
Net Source Energy | 24390.62 | 2149.85 | 2149.85
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2292.69 | 0 | 0 | 0 | 0
Cooling | 796.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.43 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1138.09 | 0 | 0 | 0 | 0 | 0
Pumps | 56.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7023.36 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.5 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7385.12 | 10554.7 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.364 | 0.391 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.392 | 0.253 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 4.092 | 0.392 | 0.253 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 4.092 | 0.392 | 0.253 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 4.092 | 0.392 | 0.253 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 4.092 | 0.392 | 0.253 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 4.092 | 0.392 | 0.253 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.392 | 0.253 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 4.092 | 0.392 | 0.253 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 4.092 | 0.392 | 0.253 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 4.092 | 0.392 | 0.253 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 4.092 | 0.392 | 0.253 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 4.092 | 0.392 | 0.253 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 4.092 | 0.392 | 0.253 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 432.93 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 781.15 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1743871.61 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 2989115.69 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33286.81 | 23249.44 | 10037.37 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8962.82 | 6265.98 | 2696.84 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31448.08 | 21952.67 | 9495.41 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8501.33 | 5940.26 | 2561.07 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 588810.53 | 383995.74 | 204814.8 | 0.65 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 50642.16 | 33626.06 | 17016.11 | 0.66 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 508911.94 | 345522.77 | 163389.17 | 0.68 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27805.47 | 19368.33 | 8437.14 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25791.36 | 17958.95 | 7832.42 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 56670.28 | 38165.61 | 18504.66 | 0.67 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3974.48 | 2636.47 | 1338.01 | 0.66 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 831228.98 | 574298.85 | 256930.13 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 39643.55 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 30640.07 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23238.43 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11995.85 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 4233.46 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 10476.74 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 40700.22 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16191.2 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46788.05 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 89315.08 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 347.7 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7416.27 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6812.71 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13818.04 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3850.1 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13742.57 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 3836.69 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 834899.41 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 52598.99 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 834899.41 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13556.65 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 13440.62 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 609.84 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 48342.5 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3165.28 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 237373.22 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.27 | 25.43 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.39 | 886.43 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.38 | 239.19 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.31 | 836.42 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 226.63 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.85 | 1180.59 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.16 | 736.53 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.07 | 682.88 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 37.54 | 62462.98 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15980.17 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16459.34 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 90341.7682 | 101.7712 | 126.5826 | 0 | 0.0006 | 1669000 | 33384.3942
February | 76814.0655 | 87.7418 | 115.3523 | 0 | 0.0006 | 1521310 | 28515.0082
March | 83404.2075 | 95.774 | 128.47 | 0 | 0.0006 | 1694450 | 31015.4417
April | 74468.9641 | 87.2702 | 125.9222 | 0 | 0.0006 | 1661340 | 27880.8323
May | 71378.6275 | 86.0776 | 136.2053 | 0 | 0.0006 | 1797640 | 26983.9719
June | 66771.3305 | 81.9324 | 136.4219 | 0 | 0.0006 | 1800820 | 25393.3365
July | 68232.4482 | 85.167 | 148.6126 | 0 | 0.0007 | 1962050 | 26103.4191
August | 68001.251 | 85.1627 | 149.9242 | 0 | 0.0007 | 1979420 | 26045.4187
September | 66137.5255 | 81.7012 | 138.6162 | 0 | 0.0006 | 1829900 | 25210.8283
October | 71144.3074 | 85.2734 | 132.4279 | 0 | 0.0006 | 1747670 | 26839.5262
November | 78862.2195 | 90.8852 | 123.56 | 0 | 0.0006 | 1629790 | 29361.4122
December | 89272.2847 | 100.76 | 126.3196 | 0 | 0.0006 | 1665600 | 33009.9085
Annual Sum or Average | 904828.9996 | 1069.5166 | 1588.4147 | 0 | 0.0073 | 20959000 | 339743.4978
Minimum of Months | 66137.5255 | 81.7012 | 115.3523 | 0 | 0.0006 | 1521310 | 25210.8283
Maximum of Months | 90341.7682 | 101.7712 | 149.9242 | 0 | 0.0007 | 1979420 | 33384.3942
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 588092000000 | 390313.172 | 27-JAN-20:00 | 177438.022 | 92719.3 | 37114.665 | 0 | 18376.479 | 11888 | 1738.644 | 0 | 48888.791 | 0 | 0 | 0 | 2149.271 | 0 | 0
February | 536049000000 | 400188.053 | 21-FEB-20:10 | 177438.022 | 92719.3 | 37114.665 | 0 | 28318.925 | 11888 | 1602.162 | 0 | 48888.791 | 0 | 0 | 0 | 2218.188 | 0 | 0
March | 597059000000 | 424334.495 | 29-MAR-19:10 | 177438.022 | 92719.3 | 37218.295 | 0 | 50549.808 | 11888 | 2854.379 | 0 | 48888.791 | 0 | 0 | 0 | 2777.901 | 0 | 0
April | 585393000000 | 417832.234 | 14-APR-19:10 | 177438.022 | 92719.3 | 37169.504 | 0 | 45521.766 | 11888 | 1911.416 | 0 | 48888.791 | 0 | 0 | 0 | 2295.435 | 0 | 0
May | 633417000000 | 452591.395 | 04-MAY-19:19 | 177438.022 | 92719.3 | 37479.582 | 0 | 78113.543 | 11888 | 3163.356 | 0 | 48888.791 | 0 | 0 | 0 | 2900.801 | 0 | 0
June | 634538000000 | 462609.553 | 27-JUN-19:10 | 177438.022 | 92719.3 | 37696.167 | 0 | 100049.46 | 0 | 3376.357 | 0 | 48888.791 | 0 | 0 | 0 | 2441.457 | 0 | 0
July | 691348000000 | 485787.635 | 24-JUL-19:10 | 177438.022 | 92719.3 | 37754.847 | 0 | 122050.591 | 0 | 3872.87 | 0 | 48888.791 | 0 | 0 | 0 | 3063.214 | 0 | 0
August | 697470000000 | 474971.083 | 18-AUG-19:19 | 177438.022 | 92719.3 | 37525.453 | 0 | 100520.278 | 11888 | 3544.819 | 0 | 48888.791 | 0 | 0 | 0 | 2446.421 | 0 | 0
September | 644785000000 | 521738.216 | 02-SEP-17:10 | 134570.663 | 86260.044 | 37732.264 | 0 | 194843.811 | 0 | 4721.568 | 0 | 61110.989 | 0 | 0 | 0 | 2498.878 | 0 | 0
October | 615809000000 | 426791.644 | 17-OCT-19:10 | 177438.022 | 92719.3 | 37153.885 | 0 | 53948.144 | 11888 | 2440.113 | 0 | 48888.791 | 0 | 0 | 0 | 2315.388 | 0 | 0
November | 574273000000 | 398708.617 | 03-NOV-19:00 | 177438.022 | 92719.3 | 37114.665 | 0 | 26621.723 | 11888 | 1773.74 | 0 | 48888.791 | 0 | 0 | 0 | 2264.375 | 0 | 0
December | 586891000000 | 389432.069 | 28-DEC-20:00 | 177438.022 | 92719.3 | 37114.665 | 0 | 17152.94 | 11888 | 1699.606 | 0 | 48888.791 | 0 | 0 | 0 | 2530.746 | 0 | 0
Annual Sum or Average | 7385120000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 536049000000 | 389432.069 |  | 134570.663 | 86260.044 | 37114.665 | 0 | 17152.94 | 0 | 1602.162 | 0 | 48888.791 | 0 | 0 | 0 | 2149.271 | 0 | 0
Maximum of Months | 697470000000 | 521738.216 |  | 177438.022 | 92719.3 | 37754.847 | 0 | 194843.811 | 11888 | 4721.568 | 0 | 61110.989 | 0 | 0 | 0 | 3063.214 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 139180.18 | 87656.03 | 0 | 226836.21
Cost per Total Building Area ($/m2) | 12.27 | 7.73 | 0 | 19.99
Cost per Net Conditioned Building Area ($/m2) | 12.27 | 7.73 | 0 | 19.99

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20234.27 | 1783.5 | 1783.5
Net Site Energy | 20234.27 | 1783.5 | 1783.5
Total Source Energy | 41623.89 | 3668.83 | 3668.83
Net Source Energy | 41623.89 | 3668.83 | 3668.83
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.31 | 3737.01 | 0 | 0 | 0 | 0
Cooling | 1358.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1133.65 | 0 | 0 | 0 | 0 | 0
Pumps | 70.89 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7300.96 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.61 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7957.65 | 12276.62 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.296 | 0.314 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.568 | 0.621 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.354 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.354 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.354 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.354 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.354 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.354 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.354 | 0.385 | 0.305 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.354 | 0.385 | 0.305 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.354 | 0.385 | 0.305 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 432.93 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 781.15 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3200468.59 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 4092324.79 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33191.65 | 22918.94 | 10272.71 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8841.37 | 6115.07 | 2726.31 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 32856.94 | 22681.95 | 10175 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8774.78 | 6067.83 | 2706.95 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 677490.23 | 425361.55 | 252128.69 | 0.63 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 42237.06 | 26444.09 | 15792.97 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 677490.23 | 425361.55 | 252128.69 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27440.09 | 18860.88 | 8579.21 | 0.69 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27240.78 | 18720.05 | 8520.73 | 0.69 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 78555 | 49357.62 | 29197.38 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5257.47 | 3287.23 | 1970.24 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 802065.87 | 535573.9 | 266491.97 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41478.58 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 37715.02 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17653.62 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11227.76 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3740.16 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 16959.47 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 42544.8 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 17154.75 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47070.05 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 92336.35 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 344.93 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6118.48 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6996.17 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19570.58 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5434.94 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19547.25 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5438.73 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 952901.87 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 55259.59 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 952901.87 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19235.65 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19228.2 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 604.94 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 69468.24 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4548.52 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 371182.67 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.43 | 40.25 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.36 | 867.14 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 231.82 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.35 | 857.92 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.36 | 229.99 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.26 | 801.43 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.12 | 711.52 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.11 | 706.07 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 38.69 | 64366.32 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29327.87 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22534.08 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 286848.3768 | 442.072 | 1090.4252 | 0 | 0.0035 | 250924.1429 | 116650.9902
February | 254061.0066 | 395.1245 | 987.2622 | 0 | 0.0031 | 227191.3962 | 103660.0431
March | 272632.4677 | 431.4919 | 1104.2964 | 0 | 0.0035 | 254137.3023 | 111953.0166
April | 252020.4764 | 411.943 | 1099.1792 | 0 | 0.0034 | 252982.5969 | 104738.9249
May | 273488.6815 | 459.8711 | 1269.7662 | 0 | 0.0039 | 292265.1236 | 114888.3943
June | 297295.7106 | 509.7348 | 1439.2404 | 0 | 0.0044 | 331288.4373 | 125829.4299
July | 329638.1469 | 570.1453 | 1625.5297 | 0 | 0.005 | 374176.3287 | 139992.206
August | 319611.097 | 552.5684 | 1574.6808 | 0 | 0.0048 | 362471.2074 | 135711.4967
September | 275894.5269 | 472.4935 | 1332.3531 | 0 | 0.0041 | 306684.0146 | 116719.1066
October | 261248.6851 | 437.2846 | 1200.9188 | 0 | 0.0037 | 276415.2654 | 109554.8667
November | 255960.818 | 413.301 | 1085.8952 | 0 | 0.0034 | 249916.9141 | 105890.5536
December | 280040.1774 | 435.9028 | 1090.4607 | 0 | 0.0035 | 250940.387 | 114295.6784
Annual Sum or Average | 3358740 | 5531.9328 | 14900.0078 | 0 | 0.0462 | 3429390 | 1399880
Minimum of Months | 252020.4764 | 395.1245 | 987.2622 | 0 | 0.0031 | 227191.3962 | 103660.0431
Maximum of Months | 329638.1469 | 570.1453 | 1625.5297 | 0 | 0.005 | 374176.3287 | 139992.206
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 582251000000 | 391636.203 | 17-JAN-20:00 | 177438.022 | 92719.3 | 36895.75 | 0 | 20149.009 | 11888 | 1546.427 | 0 | 48888.791 | 0 | 0 | 0 | 2110.905 | 0 | 0
February | 527181000000 | 391122.059 | 27-FEB-20:00 | 177438.022 | 92719.3 | 36895.75 | 0 | 19263.97 | 11888 | 1504.314 | 0 | 48888.791 | 0 | 0 | 0 | 2523.913 | 0 | 0
March | 589706000000 | 423555.553 | 31-MAR-19:10 | 177438.022 | 92719.3 | 36895.75 | 0 | 51382.75 | 11888 | 2032.489 | 0 | 48888.791 | 0 | 0 | 0 | 2310.451 | 0 | 0
April | 587027000000 | 412111.048 | 28-APR-19:00 | 177438.022 | 92719.3 | 36989.555 | 0 | 40101.289 | 11888 | 1823.221 | 0 | 48888.791 | 0 | 0 | 0 | 2262.87 | 0 | 0
May | 678179000000 | 485831.603 | 30-MAY-17:10 | 118587.99 | 86260.044 | 36998.009 | 0 | 175534.856 | 0 | 4924.469 | 0 | 61110.989 | 0 | 0 | 0 | 2415.247 | 0 | 0
June | 768730000000 | 553471.889 | 19-JUN-19:30 | 177438.022 | 92719.3 | 37154.675 | 0 | 177182.283 | 11888 | 5150.555 | 0 | 48888.791 | 0 | 0 | 0 | 3050.263 | 0 | 0
July | 868248000000 | 595777.504 | 14-JUL-19:30 | 177438.022 | 92719.3 | 37439.176 | 0 | 219002.928 | 11888 | 5872.329 | 0 | 48888.791 | 0 | 0 | 0 | 2528.958 | 0 | 0
August | 841087000000 | 638124.337 | 04-AUG-19:10 | 177438.022 | 92719.3 | 37431.072 | 0 | 260645.757 | 11888 | 6566.247 | 0 | 48888.791 | 0 | 0 | 0 | 2547.147 | 0 | 0
September | 711637000000 | 523812.076 | 06-SEP-19:10 | 177438.022 | 92719.3 | 37226.809 | 0 | 148433.275 | 11888 | 4253.496 | 0 | 48888.791 | 0 | 0 | 0 | 2964.384 | 0 | 0
October | 641401000000 | 462364.692 | 30-OCT-19:10 | 177438.022 | 92719.3 | 36895.75 | 0 | 88595.407 | 11888 | 3066.235 | 0 | 48888.791 | 0 | 0 | 0 | 2873.187 | 0 | 0
November | 579913000000 | 456085.653 | 02-NOV-19:00 | 177438.022 | 92719.3 | 36927.518 | 0 | 82336.898 | 11888 | 2954.072 | 0 | 48888.791 | 0 | 0 | 0 | 2933.052 | 0 | 0
December | 582288000000 | 392433.797 | 11-DEC-20:00 | 177438.022 | 92719.3 | 36895.75 | 0 | 20564.66 | 11888 | 1512.275 | 0 | 48888.791 | 0 | 0 | 0 | 2526.999 | 0 | 0
Annual Sum or Average | 7957650000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 527181000000 | 391122.059 |  | 118587.99 | 86260.044 | 36895.75 | 0 | 19263.97 | 0 | 1504.314 | 0 | 48888.791 | 0 | 0 | 0 | 2110.905 | 0 | 0
Maximum of Months | 868248000000 | 638124.337 |  | 177438.022 | 92719.3 | 37439.176 | 0 | 260645.757 | 11888 | 6566.247 | 0 | 61110.989 | 0 | 0 | 0 | 3050.263 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 209948.6 | 108179.16 | 0 | 318127.76
Cost per Total Building Area ($/m2) | 18.51 | 9.54 | 0 | 28.04
Cost per Net Conditioned Building Area ($/m2) | 18.51 | 9.54 | 0 | 28.04

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18793.29 | 1656.48 | 1656.48
Net Site Energy | 18793.29 | 1656.48 | 1656.48
Total Source Energy | 37685.24 | 3321.66 | 3321.66
Net Source Energy | 37685.24 | 3321.66 | 3321.66
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.23 | 2579 | 0 | 0 | 0 | 0
Cooling | 1096.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.65 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1157.2 | 0 | 0 | 0 | 0 | 0
Pumps | 61.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7265.41 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.49 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7710.23 | 11083.06 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.285 | 0.302 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.795 | 0.902 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.354 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 3.354 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 3.354 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 3.354 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 3.354 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 3.354 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.354 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 3.354 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 3.354 | 0.385 | 0.305 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 3.354 | 0.385 | 0.305 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 3.354 | 0.385 | 0.305 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 3.354 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 3.354 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 432.93 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 781.15 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1531252.98 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 3366885.36 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25430.53 | 16214.06 | 9216.47 | 0.64 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6683.82 | 4264.71 | 2419.12 | 0.64 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 25134.9 | 16022.93 | 9111.97 | 0.64 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6620.21 | 4223.57 | 2396.65 | 0.64 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 474406.98 | 288058.67 | 186348.31 | 0.61 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 29595.12 | 17495.31 | 12099.81 | 0.59 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 474406.98 | 288058.67 | 186348.31 | 0.61 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 19804.75 | 12571.39 | 7233.36 | 0.63 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 19613.33 | 12447.75 | 7165.57 | 0.63 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 54590.08 | 33261.37 | 21328.71 | 0.61 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3507.3 | 2081.47 | 1425.83 | 0.59 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 829484.91 | 521947.41 | 307537.49 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 39176.26 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 31272.83 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15095.52 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10068.12 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3420.37 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 15322.55 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 40232 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16408.27 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46354.98 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 84840.47 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 352.02 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5098.94 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6615.99 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18389.24 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5088.41 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18400.43 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5094.29 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 789447.48 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 45906.4 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 789447.48 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17965.62 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 17972.99 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 508.11 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 56417.29 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 3693.99 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 312499.83 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.48 | 45.22 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.48 | 940.87 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 247.67 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.46 | 929.75 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 245.27 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.27 | 809.89 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.15 | 734.14 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.14 | 726.96 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 42.36 | 70174.45 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14031.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18539.5 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 226859.2436 | 339.3693 | 723.2533 | 0 | 0.003 | 751701.2986 | 91606.1068
February | 202393.3873 | 304.3195 | 653.6418 | 0 | 0.0027 | 679365.8356 | 81878.7788
March | 219894.216 | 335.0476 | 734.0514 | 0 | 0.003 | 762979.5581 | 89391.7301
April | 207500.315 | 323.6738 | 733.3288 | 0 | 0.003 | 762293.6662 | 85090.045
May | 215291.5282 | 341.933 | 793.912 | 0 | 0.0032 | 825319.9087 | 88883.9274
June | 215633.4069 | 348.3388 | 826.9051 | 0 | 0.0033 | 859664.2917 | 89600.1503
July | 240394.7864 | 393.5402 | 950.0114 | 0 | 0.0038 | 987686.9914 | 100399.2092
August | 230050.0127 | 375.965 | 905.6654 | 0 | 0.0036 | 941577.5895 | 96015.9962
September | 212135.8881 | 343.6549 | 818.7215 | 0 | 0.0033 | 851163.8168 | 88241.6156
October | 212712.6058 | 337.9839 | 785.1966 | 0 | 0.0031 | 816260.8218 | 87833.6101
November | 207886.0741 | 319.8484 | 710.7299 | 0 | 0.0029 | 738765.8681 | 84813.9734
December | 225260.2245 | 337.3289 | 720.0588 | 0 | 0.0029 | 748384.334 | 90994.9143
Annual Sum or Average | 2616010 | 4101.0033 | 9355.4758 | 0 | 0.0376 | 9725160 | 1074750
Minimum of Months | 202393.3873 | 304.3195 | 653.6418 | 0 | 0.0027 | 679365.8356 | 81878.7788
Maximum of Months | 240394.7864 | 393.5402 | 950.0114 | 0 | 0.0038 | 987686.9914 | 100399.2092
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 595958000000 | 397037.133 | 24-JAN-20:49 | 177438.022 | 92719.3 | 37636.684 | 0 | 24784.885 | 11888 | 1527.867 | 0 | 48888.791 | 0 | 0 | 0 | 2153.584 | 0 | 0
February | 538609000000 | 396875.654 | 10-FEB-20:00 | 177438.022 | 92719.3 | 37636.684 | 0 | 24628.357 | 11888 | 1532.701 | 0 | 48888.791 | 0 | 0 | 0 | 2143.798 | 0 | 0
March | 604899000000 | 423243.292 | 30-MAR-19:10 | 177438.022 | 92719.3 | 37870.977 | 0 | 49726.015 | 11888 | 1964.607 | 0 | 48888.791 | 0 | 0 | 0 | 2747.58 | 0 | 0
April | 604356000000 | 445153.915 | 25-APR-19:00 | 177438.022 | 92719.3 | 38093.803 | 0 | 70887.025 | 11888 | 2864.718 | 0 | 48888.791 | 0 | 0 | 0 | 2374.257 | 0 | 0
May | 654324000000 | 474413.646 | 23-MAY-19:19 | 177438.022 | 92719.3 | 38403.279 | 0 | 99792.47 | 11888 | 2839.136 | 0 | 48888.791 | 0 | 0 | 0 | 2444.649 | 0 | 0
June | 681552000000 | 484832.08 | 27-JUN-19:30 | 177438.022 | 92719.3 | 38574.014 | 0 | 109369.221 | 11888 | 3488.456 | 0 | 48888.791 | 0 | 0 | 0 | 2466.277 | 0 | 0
July | 783050000000 | 516021.7 | 10-JUL-19:30 | 177438.022 | 92719.3 | 38726.531 | 0 | 140194.866 | 11888 | 3070.771 | 0 | 48888.791 | 0 | 0 | 0 | 3095.42 | 0 | 0
August | 746494000000 | 496800.54 | 29-AUG-19:10 | 177438.022 | 92719.3 | 38595.678 | 0 | 120255.382 | 11888 | 4511.457 | 0 | 48888.791 | 0 | 0 | 0 | 2503.909 | 0 | 0
September | 674813000000 | 477518.258 | 01-SEP-19:10 | 177438.022 | 92719.3 | 38360.146 | 0 | 102320.834 | 11888 | 3452.101 | 0 | 48888.791 | 0 | 0 | 0 | 2451.064 | 0 | 0
October | 647141000000 | 435357.891 | 01-OCT-19:10 | 167588.533 | 91473.541 | 37814.598 | 0 | 71328.521 | 11888 | 3547.216 | 0 | 48888.791 | 0 | 0 | 0 | 2828.691 | 0 | 0
November | 585702000000 | 400095.129 | 03-NOV-19:10 | 177438.022 | 92719.3 | 37636.684 | 0 | 27787.067 | 11888 | 1536.821 | 0 | 48888.791 | 0 | 0 | 0 | 2200.443 | 0 | 0
December | 593328000000 | 393641.415 | 22-DEC-20:00 | 177438.022 | 92719.3 | 37636.684 | 0 | 21416.715 | 11888 | 1584.886 | 0 | 48888.791 | 0 | 0 | 0 | 2069.016 | 0 | 0
Annual Sum or Average | 7710230000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 538609000000 | 393641.415 |  | 167588.533 | 91473.541 | 37636.684 | 0 | 21416.715 | 11888 | 1527.867 | 0 | 48888.791 | 0 | 0 | 0 | 2069.016 | 0 | 0
Maximum of Months | 783050000000 | 516021.7 |  | 177438.022 | 92719.3 | 38726.531 | 0 | 140194.866 | 11888 | 4511.457 | 0 | 48888.791 | 0 | 0 | 0 | 3095.42 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 79281.87 | 79364.48 | 0 | 158646.34
Cost per Total Building Area ($/m2) | 6.99 | 7 | 0 | 13.98
Cost per Net Conditioned Building Area ($/m2) | 6.99 | 7 | 0 | 13.98

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21792.8 | 1920.87 | 1920.87
Net Site Energy | 21792.8 | 1920.87 | 1920.87
Total Source Energy | 42270.78 | 3725.84 | 3725.84
Net Source Energy | 42270.78 | 3725.84 | 3725.84
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.64 | 4786.67 | 0 | 0 | 0 | 0
Cooling | 1275.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1135.54 | 0 | 0 | 0 | 0 | 0
Pumps | 71.8 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7889.86 | 0 | 0 | 0 | 44332.9
Refrigeration | 70.11 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7877.63 | 13915.18 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.252 | 0.265 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.403 | 0.429 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 2.956 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 2.956 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 2.956 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 2.956 | 0.385 | 0.305 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 2.956 | 0.385 | 0.305 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 2.956 | 0.385 | 0.305 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 432.93 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 781.15 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3032444.97 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 4430756.17 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 32383.09 | 22056.9 | 10326.19 | 0.68 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8409.57 | 5733.82 | 2675.75 | 0.68 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 31963.34 | 21764.38 | 10198.95 | 0.68 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8324.45 | 5674.46 | 2649.99 | 0.68 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 670916.42 | 416855.26 | 254061.16 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 42614.14 | 26399.36 | 16214.78 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 670916.42 | 416855.26 | 254061.16 | 0.62 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27274.57 | 18499.91 | 8774.65 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27067.88 | 18356.15 | 8711.73 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 77754.58 | 48351.27 | 29403.31 | 0.62 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5216.61 | 3226.71 | 1989.9 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 809023.77 | 533114.47 | 275909.29 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41918.18 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 37051.98 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17813.59 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11180.49 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3587.29 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 17461.27 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 42979.7 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 17227 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47193.93 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 92373.27 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 342.25 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6153.41 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6956.05 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19756.75 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5441.03 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19737.26 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5445.46 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 978860.92 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 57226.57 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 978860.92 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19492.79 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19478.05 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 600.28 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 74682.8 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4889.94 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 411157.8 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.43 | 40.15 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.35 | 857.47 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 223.2 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.33 | 845.88 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.35 | 220.83 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.28 | 815.8 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.13 | 717.14 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.12 | 711.43 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 39.02 | 64921.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27788.16 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24397.63 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 234550.779 | 329.8218 | 381.7877 | 0 | 0.003 | 250604.2899 | 92354.3019
February | 203879.8506 | 291.1841 | 346.4879 | 0 | 0.0027 | 227464.0171 | 80706.943
March | 206581.0148 | 306.7793 | 389.2971 | 0 | 0.003 | 255643.7673 | 82898.1454
April | 186258.6674 | 289.5325 | 393.1107 | 0 | 0.003 | 258223.7824 | 75979.2475
May | 197747.8047 | 319.6764 | 457.3592 | 0 | 0.0034 | 300491.104 | 81840.1589
June | 204257.2082 | 338.4458 | 499.2662 | 0 | 0.0037 | 328063.8542 | 85322.3985
July | 219793.8137 | 368.526 | 551.363 | 0 | 0.0041 | 362315.8547 | 92226.8776
August | 215193.7811 | 361.242 | 541.2202 | 0 | 0.004 | 355652.6289 | 90337.6728
September | 182190.2014 | 300.1324 | 439.6317 | 0 | 0.0033 | 288870.6353 | 75937.3493
October | 184316.0224 | 292.474 | 408.4213 | 0 | 0.0031 | 268312.0885 | 75756.6115
November | 193318.353 | 291.176 | 377.6286 | 0 | 0.0029 | 248005.2767 | 77967.1758
December | 223668.9569 | 320.2484 | 382.7277 | 0 | 0.003 | 251260.089 | 88617.1503
Annual Sum or Average | 2451760 | 3809.2385 | 5168.3014 | 0 | 0.0392 | 3394910 | 999944.0323
Minimum of Months | 182190.2014 | 289.5325 | 346.4879 | 0 | 0.0027 | 227464.0171 | 75756.6115
Maximum of Months | 234550.779 | 368.526 | 551.363 | 0 | 0.0041 | 362315.8547 | 92354.3019
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 581508000000 | 389524.43 | 30-JAN-20:00 | 177438.022 | 92719.3 | 36931.409 | 0 | 17617.195 | 11888 | 1592.321 | 0 | 48888.791 | 0 | 0 | 0 | 2449.391 | 0 | 0
February | 527813000000 | 390333.694 | 27-FEB-20:00 | 177438.022 | 92719.3 | 36931.409 | 0 | 18440.189 | 11888 | 1551.56 | 0 | 48888.791 | 0 | 0 | 0 | 2476.423 | 0 | 0
March | 593202000000 | 402245.716 | 28-MAR-19:00 | 177438.022 | 92719.3 | 36931.409 | 0 | 29936.01 | 11888 | 2201.267 | 0 | 48888.791 | 0 | 0 | 0 | 2242.917 | 0 | 0
April | 599189000000 | 447037.244 | 02-APR-19:00 | 167588.533 | 91473.541 | 36931.409 | 0 | 84411.452 | 11888 | 3022.088 | 0 | 48888.791 | 0 | 0 | 0 | 2833.429 | 0 | 0
May | 697267000000 | 559401.723 | 27-MAY-17:19 | 134570.663 | 86260.044 | 37359.804 | 0 | 232240.611 | 0 | 5363.119 | 0 | 61110.989 | 0 | 0 | 0 | 2496.494 | 0 | 0
June | 761247000000 | 577640.327 | 29-JUN-19:10 | 177438.022 | 92719.3 | 37482.573 | 0 | 212450.594 | 0 | 5546.468 | 0 | 48888.791 | 0 | 0 | 0 | 3114.578 | 0 | 0
July | 840727000000 | 615720.68 | 13-JUL-19:10 | 177438.022 | 92719.3 | 37312.007 | 0 | 250146.673 | 0 | 6073.867 | 0 | 48888.791 | 0 | 0 | 0 | 3142.019 | 0 | 0
August | 825265000000 | 610070.993 | 25-AUG-19:10 | 177438.022 | 92719.3 | 37324.783 | 0 | 233235.068 | 11888 | 6044.693 | 0 | 48888.791 | 0 | 0 | 0 | 2532.337 | 0 | 0
September | 670303000000 | 490787.221 | 13-SEP-19:10 | 177438.022 | 92719.3 | 37067.557 | 0 | 115571.404 | 11888 | 4231.724 | 0 | 48888.791 | 0 | 0 | 0 | 2982.423 | 0 | 0
October | 622598000000 | 441257.406 | 08-OCT-19:10 | 167588.533 | 91473.541 | 36931.409 | 0 | 78694.606 | 11888 | 2947.46 | 0 | 48888.791 | 0 | 0 | 0 | 2845.065 | 0 | 0
November | 575478000000 | 401496.78 | 02-NOV-19:00 | 177438.022 | 92719.3 | 36931.409 | 0 | 29002.179 | 11888 | 1993.865 | 0 | 48888.791 | 0 | 0 | 0 | 2635.214 | 0 | 0
December | 583030000000 | 389297.752 | 01-DEC-20:00 | 177438.022 | 92719.3 | 36931.409 | 0 | 17786.44 | 11888 | 1625.649 | 0 | 48888.791 | 0 | 0 | 0 | 2020.141 | 0 | 0
Annual Sum or Average | 7877630000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 527813000000 | 389297.752 |  | 134570.663 | 86260.044 | 36931.409 | 0 | 17617.195 | 0 | 1551.56 | 0 | 48888.791 | 0 | 0 | 0 | 2020.141 | 0 | 0
Maximum of Months | 840727000000 | 615720.68 |  | 177438.022 | 92719.3 | 37482.573 | 0 | 250146.673 | 11888 | 6073.867 | 0 | 61110.989 | 0 | 0 | 0 | 3142.019 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 123289.81 | 110801.72 | 0 | 234091.53
Cost per Total Building Area ($/m2) | 10.87 | 9.77 | 0 | 20.63
Cost per Net Conditioned Building Area ($/m2) | 10.87 | 9.77 | 0 | 20.63

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20569.92 | 1813.08 | 1813.08
Net Site Energy | 20569.92 | 1813.08 | 1813.08
Total Source Energy | 40322.26 | 3554.1 | 3554.1
Net Source Energy | 40322.26 | 3554.1 | 3554.1
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.76 | 3842.91 | 0 | 0 | 0 | 0
Cooling | 887.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.59 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1150.25 | 0 | 0 | 0 | 0 | 0
Pumps | 60.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7996.78 | 0 | 0 | 0 | 44332.9
Refrigeration | 69.36 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7491.57 | 13078.34 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.274 | 0.289 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.449 | 0.481 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.385 | 0.305 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 2.956 | 0.385 | 0.305 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.385 | 0.305 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 2.956 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 2.956 | 0.385 | 0.305 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.385 | 0.305 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.385 | 0.305 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 2.956 | 0.385 | 0.305 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 2.956 | 0.385 | 0.305 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 2.956 | 0.385 | 0.305 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.385 | 0.305 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 432.93 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 781.15 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1450373.04 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 4070176.02 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 26548.73 | 17516.46 | 9032.26 | 0.66 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6937.91 | 4580.93 | 2356.99 | 0.66 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 26042.13 | 17180.86 | 8861.27 | 0.66 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6821.65 | 4504.4 | 2317.25 | 0.66 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 457489.59 | 283139.7 | 174349.89 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 30287.05 | 18873.99 | 11413.06 | 0.62 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 317500.98 | 207223.1 | 110277.88 | 0.65 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 21581.8 | 14200.31 | 7381.49 | 0.66 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 21332.16 | 14034.15 | 7298.01 | 0.66 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 41725.82 | 26618.88 | 15106.94 | 0.64 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3063.94 | 1924.43 | 1139.51 | 0.63 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 672733.97 | 437847.83 | 234886.15 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 39973.39 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 30923.09 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17281.99 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10541.63 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3836.16 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 17906.13 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41037.54 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 16636.44 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46808.23 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 87052.21 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 317.19 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5340.39 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6679.73 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19298.91 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5420.58 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19252.75 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5414.25 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 881855.12 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 52947.58 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 881855.12 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 19007.24 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 18967.08 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 536.56 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 67921.02 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4447.21 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 385907.34 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.51 | 48.03 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.42 | 906.32 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 237.27 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.4 | 889.14 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.37 | 233.41 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.38 | 880.07 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.16 | 736.33 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.14 | 727.69 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 41.1 | 68087.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13290.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22412.12 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 228394.6562 | 327.4496 | 435.5059 | 0 | 0.0032 | 10320700 | 90660.3939
February | 201462.1645 | 292.0323 | 395.7085 | 0 | 0.0029 | 9378300 | 80278.5652
March | 209643.0754 | 313.8976 | 447.9659 | 0 | 0.0032 | 10619100 | 84505.7607
April | 194576.4359 | 296.6189 | 434.8683 | 0 | 0.0031 | 10309700 | 78942.9267
May | 196757.5288 | 307.6598 | 467.6479 | 0 | 0.0033 | 11088300 | 80573.6915
June | 197651.8066 | 316.1431 | 495.3961 | 0 | 0.0035 | 11747600 | 81624.7621
July | 211094.6781 | 342.4696 | 546.5379 | 0 | 0.0039 | 12961200 | 87642.6709
August | 204561.9164 | 331.5111 | 528.322 | 0 | 0.0037 | 12529100 | 84895.5839
September | 190652.7918 | 305.5724 | 480.111 | 0 | 0.0034 | 11385200 | 78794.6967
October | 194944.5664 | 304.2669 | 461.3205 | 0 | 0.0033 | 10938200 | 79777.3211
November | 197924.6623 | 298.2606 | 429.8294 | 0 | 0.0031 | 10189500 | 79966.663
December | 222478.0504 | 322.4423 | 436.7926 | 0 | 0.0032 | 10352000 | 88647.7595
Annual Sum or Average | 2450140 | 3758.3245 | 5560.006 | 0 | 0.04 | 131819000 | 996310.7952
Minimum of Months | 190652.7918 | 292.0323 | 395.7085 | 0 | 0.0029 | 9378300 | 78794.6967
Maximum of Months | 228394.6562 | 342.4696 | 546.5379 | 0 | 0.0039 | 12961200 | 90660.3939
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 586549000000 | 391286.819 | 30-JAN-20:00 | 177438.022 | 92719.3 | 37435.432 | 0 | 18849.723 | 11888 | 1645.884 | 0 | 48888.791 | 0 | 0 | 0 | 2421.667 | 0 | 0
February | 532991000000 | 397497.231 | 03-FEB-20:00 | 177438.022 | 92719.3 | 37435.432 | 0 | 25435.9 | 11888 | 1545.331 | 0 | 48888.791 | 0 | 0 | 0 | 2146.455 | 0 | 0
March | 603506000000 | 417193.239 | 30-MAR-19:10 | 177438.022 | 92719.3 | 37469.615 | 0 | 44182.061 | 11888 | 1886.935 | 0 | 48888.791 | 0 | 0 | 0 | 2720.516 | 0 | 0
April | 585923000000 | 423829.847 | 06-APR-19:10 | 177438.022 | 92719.3 | 37469.646 | 0 | 50672.866 | 11888 | 1993.912 | 0 | 48888.791 | 0 | 0 | 0 | 2759.308 | 0 | 0
May | 630175000000 | 442321.107 | 25-MAY-19:00 | 177438.022 | 92719.3 | 37780.482 | 0 | 67895.152 | 11888 | 2855.083 | 0 | 48888.791 | 0 | 0 | 0 | 2856.278 | 0 | 0
June | 667642000000 | 506989.02 | 25-JUN-19:10 | 167588.533 | 91473.541 | 38001.037 | 0 | 152648.071 | 0 | 5276.13 | 0 | 48888.791 | 0 | 0 | 0 | 3112.916 | 0 | 0
July | 736614000000 | 505506.636 | 21-JUL-19:10 | 177438.022 | 92719.3 | 38302.192 | 0 | 141696.893 | 0 | 3926.497 | 0 | 48888.791 | 0 | 0 | 0 | 2534.941 | 0 | 0
August | 712060000000 | 489790.529 | 11-AUG-19:49 | 177438.022 | 92719.3 | 38089.247 | 0 | 114678.568 | 11888 | 3594.745 | 0 | 48888.791 | 0 | 0 | 0 | 2493.856 | 0 | 0
September | 647049000000 | 476025.44 | 01-SEP-19:10 | 177438.022 | 92719.3 | 37854.458 | 0 | 101771.019 | 11888 | 3010.682 | 0 | 48888.791 | 0 | 0 | 0 | 2455.168 | 0 | 0
October | 621643000000 | 431255.278 | 05-OCT-19:10 | 177438.022 | 92719.3 | 37478.992 | 0 | 57872.41 | 11888 | 2162.403 | 0 | 48888.791 | 0 | 0 | 0 | 2807.36 | 0 | 0
November | 579095000000 | 397634.638 | 20-NOV-20:00 | 177438.022 | 92719.3 | 37435.432 | 0 | 25175.937 | 11888 | 1489.545 | 0 | 48888.791 | 0 | 0 | 0 | 2599.612 | 0 | 0
December | 588328000000 | 391452.885 | 01-DEC-20:00 | 177438.022 | 92719.3 | 37435.432 | 0 | 19441.613 | 11888 | 1584.587 | 0 | 48888.791 | 0 | 0 | 0 | 2057.14 | 0 | 0
Annual Sum or Average | 7491570000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 532991000000 | 391286.819 |  | 167588.533 | 91473.541 | 37435.432 | 0 | 18849.723 | 0 | 1489.545 | 0 | 48888.791 | 0 | 0 | 0 | 2057.14 | 0 | 0
Maximum of Months | 736614000000 | 506989.02 |  | 177438.022 | 92719.3 | 38302.192 | 0 | 152648.071 | 11888 | 5276.13 | 0 | 48888.791 | 0 | 0 | 0 | 3112.916 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 149543.66 | 113190.48 | 0 | 262734.15
Cost per Total Building Area ($/m2) | 13.18 | 9.98 | 0 | 23.16
Cost per Net Conditioned Building Area ($/m2) | 13.18 | 9.98 | 0 | 23.16

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 23337.73 | 2057.04 | 2057.04
Net Site Energy | 23337.73 | 2057.04 | 2057.04
Total Source Energy | 42905.38 | 3781.78 | 3781.78
Net Source Energy | 42905.38 | 3781.78 | 3781.78
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.65 | 5809.12 | 0 | 0 | 0 | 0
Cooling | 824.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 186.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1148.48 | 0 | 0 | 0 | 0 | 0
Pumps | 62.98 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 8861.15 | 0 | 0 | 0 | 44332.9
Refrigeration | 68.42 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7428.82 | 15908.92 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.227 | 0.237 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.346 | 0.365 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.487 | 0.409 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 2.956 | 0.487 | 0.409 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.487 | 0.409 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.487 | 0.409 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.487 | 0.409 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.487 | 0.409 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 2.956 | 0.487 | 0.409 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 2.956 | 0.487 | 0.409 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.487 | 0.409 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.487 | 0.409 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.487 | 0.409 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.487 | 0.409 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.487 | 0.409 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.487 | 0.409 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.487 | 0.409 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.487 | 0.409 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 2.956 | 0.487 | 0.409 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 2.956 | 0.487 | 0.409 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 2.956 | 0.487 | 0.409 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.487 | 0.409 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.487 | 0.409 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.487 | 0.409 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.487 | 0.409 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 432.93 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 781.15 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2484522.09 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 4534194.51 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 33476.88 | 23004.01 | 10472.87 | 0.69 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8690.5 | 5976.07 | 2714.43 | 0.69 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 32687.57 | 22449.69 | 10237.88 | 0.69 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 8513.32 | 5853.3 | 2660.03 | 0.69 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 643048.34 | 399508.21 | 243540.14 | 0.62 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 45941.06 | 28862.37 | 17078.68 | 0.63 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 611116.3 | 384501.26 | 226615.05 | 0.63 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27716.68 | 18968.94 | 8747.73 | 0.68 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 27269.94 | 18659.66 | 8610.28 | 0.68 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 72494.07 | 45385.92 | 27108.15 | 0.63 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4836.03 | 3013.74 | 1822.28 | 0.62 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 753351.58 | 503492.31 | 249859.28 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 41477.01 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 29672.07 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19743.83 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11584.95 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 3607.04 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 17781.14 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 42565.15 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 17610.25 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46998.71 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 90140.2 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 335.1 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5872.85 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6788.51 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20552.17 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5611.42 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20487.14 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 5614.45 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 975135.2 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 60553.09 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 975135.2 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20212.58 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 20188.52 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 587.74 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 76011.74 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 4976.96 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 421107.33 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.44 | 41.23 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.5 | 952.1 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.39 | 247.55 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.46 | 928.82 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.38 | 242.49 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.53 | 973.21 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.23 | 783.94 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.21 | 771.25 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 38.84 | 64610.07 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22767.21 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24967.2 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 238522.4056 | 333.784 | 382.969 | 0 | 0.003 | 251368.6526 | 93763.027
February | 211107.889 | 298.0021 | 347.3583 | 0 | 0.0027 | 228012.6723 | 83233.1523
March | 219912.3532 | 318.4256 | 387.8783 | 0 | 0.003 | 254664.382 | 87468.6914
April | 195602.1589 | 294.2968 | 381.0511 | 0 | 0.0029 | 250251.1618 | 78857.7646
May | 191687.6698 | 299.0682 | 408.1391 | 0 | 0.0031 | 268101.2755 | 78298.6685
June | 188268.4517 | 302.8828 | 430.6503 | 0 | 0.0032 | 282935.9793 | 77776.5643
July | 208503.4065 | 341.9653 | 498.1956 | 0 | 0.0037 | 327344.5071 | 86760.0123
August | 198418.6346 | 323.9085 | 469.1602 | 0 | 0.0035 | 308259.5233 | 82418.669
September | 180958.4588 | 289.3272 | 408.0831 | 0 | 0.0031 | 268100.7245 | 74585.0775
October | 191256.0358 | 296.6386 | 401.5018 | 0 | 0.003 | 263732.1912 | 77954.4942
November | 201967.095 | 298.5968 | 376.2695 | 0 | 0.0029 | 247081.0569 | 80919.453
December | 231046.4146 | 327.1221 | 383.3386 | 0 | 0.003 | 251637.3862 | 91187.4369
Annual Sum or Average | 2457250 | 3724.018 | 4874.5948 | 0 | 0.0373 | 3201490 | 993223.011
Minimum of Months | 180958.4588 | 289.3272 | 347.3583 | 0 | 0.0027 | 228012.6723 | 74585.0775
Maximum of Months | 238522.4056 | 341.9653 | 498.1956 | 0 | 0.0037 | 327344.5071 | 93763.027
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 583282000000 | 387973.189 | 20-JAN-20:00 | 177438.022 | 92719.3 | 37410.935 | 0 | 15811.766 | 11888 | 1816.968 | 0 | 48888.791 | 0 | 0 | 0 | 1999.407 | 0 | 0
February | 529086000000 | 392910.342 | 22-FEB-20:00 | 177438.022 | 92719.3 | 37410.935 | 0 | 20470.02 | 11888 | 1662.046 | 0 | 48888.791 | 0 | 0 | 0 | 2433.228 | 0 | 0
March | 590930000000 | 394953.119 | 22-MAR-19:19 | 177438.022 | 92719.3 | 37410.935 | 0 | 22508.152 | 11888 | 1650.953 | 0 | 48888.791 | 0 | 0 | 0 | 2448.968 | 0 | 0
April | 580689000000 | 405288.689 | 04-APR-19:10 | 177438.022 | 92719.3 | 37410.935 | 0 | 33061.322 | 11888 | 1661.066 | 0 | 48888.791 | 0 | 0 | 0 | 2221.253 | 0 | 0
May | 622109000000 | 433595.134 | 31-MAY-19:10 | 177438.022 | 92719.3 | 37647.68 | 0 | 71696.89 | 0 | 2367.207 | 0 | 48888.791 | 0 | 0 | 0 | 2837.244 | 0 | 0
June | 656532000000 | 520799.711 | 14-JUN-19:00 | 177438.022 | 92719.3 | 37769.163 | 0 | 144601.218 | 11888 | 4455.754 | 0 | 48888.791 | 0 | 0 | 0 | 3039.464 | 0 | 0
July | 759578000000 | 550934.577 | 06-JUL-19:10 | 177438.022 | 92719.3 | 37933.775 | 0 | 185865.3 | 0 | 4974.293 | 0 | 48888.791 | 0 | 0 | 0 | 3115.097 | 0 | 0
August | 715293000000 | 545247.321 | 13-AUG-19:19 | 167588.533 | 91473.541 | 37606.983 | 0 | 179838.363 | 11888 | 4921.442 | 0 | 48888.791 | 0 | 0 | 0 | 3041.668 | 0 | 0
September | 622108000000 | 488529.36 | 08-SEP-19:10 | 177438.022 | 92719.3 | 37501.786 | 0 | 114163.259 | 11888 | 3519.568 | 0 | 48888.791 | 0 | 0 | 0 | 2410.634 | 0 | 0
October | 611971000000 | 415938.545 | 07-OCT-19:10 | 157739.045 | 88982.023 | 37410.935 | 0 | 65371.591 | 11888 | 2892.463 | 0 | 48888.791 | 0 | 0 | 0 | 2765.697 | 0 | 0
November | 573333000000 | 397856.393 | 02-NOV-19:00 | 177438.022 | 92719.3 | 37410.935 | 0 | 25409.389 | 11888 | 1556.79 | 0 | 48888.791 | 0 | 0 | 0 | 2545.167 | 0 | 0
December | 583906000000 | 388959.883 | 01-DEC-20:00 | 177438.022 | 92719.3 | 37410.935 | 0 | 16969.205 | 11888 | 1628.337 | 0 | 48888.791 | 0 | 0 | 0 | 2017.294 | 0 | 0
Annual Sum or Average | 7428820000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 529086000000 | 387973.189 |  | 157739.045 | 88982.023 | 37410.935 | 0 | 15811.766 | 0 | 1556.79 | 0 | 48888.791 | 0 | 0 | 0 | 1999.407 | 0 | 0
Maximum of Months | 759578000000 | 550934.577 |  | 177438.022 | 92719.3 | 37933.775 | 0 | 185865.3 | 11888 | 4974.293 | 0 | 48888.791 | 0 | 0 | 0 | 3115.097 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 115530.27 | 126626.85 | 0 | 242157.12
Cost per Total Building Area ($/m2) | 10.18 | 11.16 | 0 | 21.34
Cost per Net Conditioned Building Area ($/m2) | 10.18 | 11.16 | 0 | 21.34

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 28136.54 | 2480.02 | 2480.02
Net Site Energy | 28136.54 | 2480.02 | 2480.02
Total Source Energy | 48780.59 | 4299.64 | 4299.64
Net Source Energy | 48780.59 | 4299.64 | 4299.64
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 4.18 | 9580.54 | 0 | 0 | 0 | 0
Cooling | 632.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 2237.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 185.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1952.18 | 1238.65 | 0 | 0 | 0 | 0
Exterior Equipment | 947.54 | 0 | 0 | 0 | 0 | 0
Fans | 1187.61 | 0 | 0 | 0 | 0 | 0
Pumps | 66.95 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10036.92 | 0 | 0 | 0 | 44332.9
Refrigeration | 66.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7280.44 | 20856.1 | 0 | 0 | 0 | 44332.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 7.53 | 37.16 | 5.38
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 15.74 | 1.39 | 5.38
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 13.11 | 92.9 | 0
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 13.11 | 92.9 | 0
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 27.55 | 1.39 | 67.817
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 16.83 | 18.58 | 2127.546
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 12.23 | 23.23 | 598.6458
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 20.28 | 3.1 | 8.07
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 8.6 |  | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 38.09 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 38.09 | 6.19 | 10.76
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 19.09 | 26.01 | 14.3
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 19.09 | 16.35 | 14.3
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 19.09 | 16.35 | 14.3
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 19.09 | 26.01 | 14.3
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 3.96 | 46.45 | 2.69
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 16.508 | 8.03 | 35.5139
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 331.66 | 180 | 0
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.401 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.401 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1978.83 | 0 | 180
CAFE_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 188.86 | 180 | 0
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 70.6 | 180 | 90 | S
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 167.42 | 270 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 103.3 | 270 | 0
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 67.63 | 90 | 90 | E
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 18.12 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_CEILING_2 | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 245.35 | 180 | 0
MECH_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 62.8 | 0 | 90 | N
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.57 | 270 | 90 | W
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 104.06 | 270 | 90 | W
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 39.02 | 180 | 0
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 104.05 | 270 | 90 | W
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 39.02 | 180 | 0
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 847.14 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOF-IEAD-RES | 0.3 | 0.174 | 0.18 | 220.77 | 180 | 0
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 104.05 | 90 | 90 | E
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS-MASS-RES | 0.08 | 0.267 | 0.278 | 55.74 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 36.23 | 0 | 90 | N
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.616 | 0.541 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.62 | 65.62 | 2.956 | 0.616 | 0.541 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.58 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.15 | 8.59 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 5.82 | 23.29 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.83 | 5.83 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW-NONRES-FIXED | 5.21 | 5.21 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 32.21 | 32.21 | 2.956 | 0.616 | 0.541 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.616 | 0.541 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 17.18 | 17.18 | 2.956 | 0.616 | 0.541 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.6 | 4.6 | 2.956 | 0.616 | 0.541 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 85.24 | 85.24 | 2.956 | 0.616 | 0.541 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 23.3 | 23.3 | 2.956 | 0.616 | 0.541 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.616 | 0.541 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.616 | 0.541 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.616 | 0.541 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.616 | 0.541 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.616 | 0.541 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.616 | 0.541 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 4.6 | 2.956 | 0.616 | 0.541 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW-RES-OPER | 8.59 | 8.59 | 2.956 | 0.616 | 0.541 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.51 | 2.956 | 0.616 | 0.541 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 6.75 | 60.74 | 2.956 | 0.616 | 0.541 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 3.68 | 279.6 | 2.956 | 0.616 | 0.541 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.616 | 0.541 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.616 | 0.541 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-OPER | 8.58 | 34.33 | 2.956 | 0.616 | 0.541 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-OPER | 4.6 | 18.39 | 2.956 | 0.616 | 0.541 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
Total or Average |  |  | 1214.08 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 432.93 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 781.15 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1345852.41 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 5637179.73 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 39406.17 | 27628.88 | 11777.3 | 0.7 | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 10259.61 | 7195.84 | 3063.77 | 0.7 | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 36573.05 | 25639.41 | 10933.64 | 0.7 | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 9658.71 | 6775.25 | 2883.46 | 0.7 | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 519386.41 | 352595.02 | 166791.4 | 0.68 | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 62218.38 | 42889.55 | 19328.83 | 0.69 | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 361656.15 | 279431.49 | 82224.66 | 0.77 | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 35016.91 | 24510.92 | 10505.99 | 0.7 | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 32206.72 | 22540.06 | 9666.66 | 0.7 | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 46216.19 | 33277.3 | 12938.89 | 0.72 | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 3406.89 | 2373.17 | 1033.72 | 0.7 | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 822357.54 | 578451.39 | 243906.15 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 42271.6 | -
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 24125.98 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28828.6 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14736.36 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 5304.71 | -
CORRIDOR_FLR_6 UNIT HEATER COIL | Coil:Heating:Electric | 21484.5 | 1
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 43391.81 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | 18241.53 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47028.64 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 90649.78 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 513.08 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9383.97 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6776.89 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 24804.41 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6690.96 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 24664.23 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 6664.38 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 1077309.31 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | 77704.95 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 1077309.31 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 24575.27 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | 24389.66 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 608.69 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | 90416.75 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | 5920.14 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | 528746.24 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDOR_FLR_6 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 50 | 0.49 | 45.69 | 1 | Unit Heater Fans
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.84 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.04 | 0 | 1 | Zone Exhaust Fans
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.24 | 86.76 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.68 | 1068.3 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.44 | 278.36 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.56 | 991.48 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 0.41 | 262.27 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 2.54 | 1619.36 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 20.45 | 13015.33 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.49 | 945.98 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 331 | 1.37 | 870.16 | 1 | General
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2601.61 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.67 | 1 | Fan Energy
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 39.24 | 65290.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12332.87 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31040.71 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.59 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.33 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 263474.5416 | 278.6426 | 826.528 | 0 | 0.0031 | 165736.1731 | 97262.7273
February | 229499.4258 | 243.8817 | 744.4278 | 0 | 0.0028 | 149281.429 | 84900.7417
March | 226577.9114 | 245.5774 | 835.3785 | 0 | 0.0031 | 167551.916 | 84558.6586
April | 197611.8854 | 219.1089 | 831.649 | 0 | 0.003 | 166832.7585 | 74506.6764
May | 184299.6265 | 210.087 | 895.6805 | 0 | 0.0032 | 179707.2608 | 70370.5637
June | 181344.2786 | 209.1202 | 931.5707 | 0 | 0.0033 | 186918.8799 | 69611.7711
July | 187682.9733 | 217.6808 | 990.3068 | 0 | 0.0035 | 198709.4967 | 72237.5008
August | 180326.4722 | 208.234 | 932.3574 | 0 | 0.0033 | 187077.9388 | 69265.3157
September | 176226.6991 | 200.4273 | 846.8812 | 0 | 0.003 | 169914.257 | 67217.7427
October | 203344.018 | 224.9439 | 844.878 | 0 | 0.003 | 169483.8959 | 76587.7574
November | 229029.0925 | 245.9703 | 797.0545 | 0 | 0.0029 | 159851.9859 | 85125.0673
December | 252696.0191 | 268.7111 | 823.4179 | 0 | 0.0031 | 165122.6407 | 93509.6244
Annual Sum or Average | 2512110 | 2772.3854 | 10300.1304 | 0 | 0.0371 | 2066190 | 945154.1469
Minimum of Months | 176226.6991 | 200.4273 | 744.4278 | 0 | 0.0028 | 149281.429 | 67217.7427
Maximum of Months | 263474.5416 | 278.6426 | 990.3068 | 0 | 0.0035 | 198709.4967 | 97262.7273
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 583989000000 | 389048.86 | 20-JAN-20:00 | 177438.022 | 92719.3 | 38608.297 | 0 | 15930.478 | 11888 | 1502.168 | 0 | 48888.791 | 0 | 0 | 0 | 2073.803 | 0 | 0
February | 526009000000 | 390169.571 | 28-FEB-20:19 | 177438.022 | 92719.3 | 38608.297 | 0 | 16755.458 | 11888 | 1862.733 | 0 | 48888.791 | 0 | 0 | 0 | 2008.969 | 0 | 0
March | 590387000000 | 400403.047 | 29-MAR-19:30 | 177438.022 | 92719.3 | 38608.297 | 0 | 26703.487 | 11888 | 1694.057 | 0 | 48888.791 | 0 | 0 | 0 | 2463.093 | 0 | 0
April | 587853000000 | 398980.048 | 25-APR-19:10 | 177438.022 | 92719.3 | 38608.297 | 0 | 37439.348 | 0 | 1714.256 | 0 | 48888.791 | 0 | 0 | 0 | 2172.033 | 0 | 0
May | 633218000000 | 434558.315 | 24-MAY-19:10 | 177438.022 | 92719.3 | 38790.753 | 0 | 71593.007 | 0 | 2324.856 | 0 | 48888.791 | 0 | 0 | 0 | 2803.586 | 0 | 0
June | 658629000000 | 482803.802 | 15-JUN-19:00 | 177438.022 | 92719.3 | 39061.306 | 0 | 118725.852 | 0 | 2990.546 | 0 | 48888.791 | 0 | 0 | 0 | 2979.986 | 0 | 0
July | 700174000000 | 482929.267 | 11-JUL-19:10 | 177438.022 | 92719.3 | 38950.223 | 0 | 118251.521 | 0 | 4209.365 | 0 | 48888.791 | 0 | 0 | 0 | 2472.046 | 0 | 0
August | 659189000000 | 466917.517 | 15-AUG-19:10 | 177438.022 | 92719.3 | 38836.741 | 0 | 102950.476 | 0 | 3629.675 | 0 | 48888.791 | 0 | 0 | 0 | 2454.512 | 0 | 0
September | 598711000000 | 407017.904 | 08-SEP-19:49 | 177438.022 | 92719.3 | 38608.297 | 0 | 33569.985 | 11888 | 1732.8 | 0 | 48888.791 | 0 | 0 | 0 | 2172.709 | 0 | 0
October | 597195000000 | 400097.88 | 03-OCT-19:10 | 177438.022 | 92719.3 | 38608.297 | 0 | 26818.623 | 11888 | 1610.042 | 0 | 48888.791 | 0 | 0 | 0 | 2126.805 | 0 | 0
November | 563256000000 | 389463.465 | 14-NOV-20:00 | 177438.022 | 92719.3 | 38608.297 | 0 | 16284.388 | 11888 | 1610.742 | 0 | 48888.791 | 0 | 0 | 0 | 2025.924 | 0 | 0
December | 581827000000 | 386366.663 | 18-DEC-20:00 | 177438.022 | 92719.3 | 38608.297 | 0 | 12708.84 | 11888 | 1711.423 | 0 | 48888.791 | 0 | 0 | 0 | 2403.99 | 0 | 0
Annual Sum or Average | 7280440000000 | [9 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 526009000000 | 386366.663 |  | 177438.022 | 92719.3 | 38608.297 | 0 | 12708.84 | 0 | 1502.168 | 0 | 48888.791 | 0 | 0 | 0 | 2008.969 | 0 | 0
Maximum of Months | 700174000000 | 482929.267 |  | 177438.022 | 92719.3 | 39061.306 | 0 | 118725.852 | 11888 | 4209.365 | 0 | 48888.791 | 0 | 0 | 0 | 2979.986 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 185806.69 | 87200.74 | 0 | 273007.43
Cost per Total Building Area ($/m2) | 16.38 | 7.69 | 0 | 24.06
Cost per Net Conditioned Building Area ($/m2) | 16.38 | 7.69 | 0 | 24.06

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
UnitHeater_HtgSP_Sch | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
UnitHeater_ClgSP_Sch | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laundry_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Laundry_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Laundry_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_5_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
FLR_3_DOAS_OAminOAFracSchedule | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FLR_6_DOAS_OAminOAFracSchedule | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720