## BuildingSummary
Building Summary Large Office post-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Large Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 46320 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 12 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.38
| East | 0.38
| North | 0.38
| West | 0.38
| Total | 0.38
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11589.72
| Net Dimensions - Total Area (m2) | 6953.64
| Wall to Skin Ratio | 0.765
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3563
| Net Dimensions - Total Area (m2) | 3563
| Roof to Skin Ratio | 0.235
Window Dimensions (m2)
| South | 1390.85
| East | 927.23
| North | 1390.85
| West | 927.23
| Total Area (m2) | 4636.16
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 3563
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 8523.53
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 92640.76
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.36496 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Water cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | boiler
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 1504.13

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 7.5347 | 4.842 |  |  | 10.001 |  | 958.9195 |  | 0
Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 8.07 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 8.07 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 8.07 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 3.6267
Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 2397.06 |  |  |  | 967.5482 |  |  | 23972.9872
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 4356.1748 | 4216.5829 | 4292.5563 | 4104.9365 | 3859.047 | 3789.0185 | 3311.8779 | 4079.4104 | 3251.8325 | 3534.3936 | 4097.2666 | 3142.2411 | 4063.5817 | 3137.4166 | 3795.5443 | 4085.485
Heating (kW)
| HEATSYS1 BOILER | 2888.7161 | 3174.7451 | 3184.6341 | 3243.3723 | 2984.2545 | 3137.6765 | 2932.3785 | 3407.1883 | 3005.6631 | 3263.6831 | 3691.9002 | 3183.5625 | 3838.8658 | 3540.6501 | 3926.618 | 4923.4118
HVAC Efficiency
| Air Conditioning (COP) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
| Heating Efficiency (%) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 16.57 | 17.39 | 18.19 | 17.46 | 17.65 | 17.92 | 16.5 | 16.96 | 18.89 | 17.3 | 16.62 | 18.43 | 16.76 | 17.94 | 17.78 | 20.97
| VAV_2_FAN | 192.06 | 192.98 | 216.71 | 195.6 | 200.2 | 213.53 | 189.42 | 192.39 | 216.73 | 200.65 | 199.03 | 212.7 | 200.84 | 209.08 | 209.32 | 247.54
| VAV_3_FAN | 18.72 | 18.49 | 21.76 | 18.76 | 17.82 | 20.54 | 16.16 | 18.34 | 18.91 | 17.87 | 18.86 | 18.04 | 18.97 | 17.96 | 18.58 | 21.82
| VAV_5_FAN | 5.58 | 5.39 | 3.97 | 5.96 | 5.09 | 3.72 | 3.73 | 5.57 | 5.49 | 4.32 | 5.4 | 5.45 | 5.38 | 5.07 | 4.44 | 4.12
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.084859 | 0.10832 | 0.078592 | 0.096666 | 0.056953 | 0.097422 | 0.15059 | 0.070362 | 0.036966 | 0.072587 | 0.08735 | 0.036967 | 0.062032 | 0.078105 | 0.061996 | 0.10004
| Total Cost ($/m2) | 11.77 | 14.32 | 9.95 | 11.89 | 6.62 | 11.51 | 15.74 | 8.45 | 4.03 | 7.49 | 9.61 | 3.9 | 6.74 | 8.03 | 6.41 | 10.28
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011381 | 0.0080506 | 0.0081765 | 0.0095748 | 0.0085738 | 0.0076496 | 0.0085685 | 0.0096895 | 0.006872 | 0.0084098 | 0.0083451 | 0.0069027 | 0.0078861 | 0.0080675 | 0.0078726 | 0.0041276
| Total Cost ($/m2) | 0.14 | 0.64 | 0.51 | 1.22 | 0.49 | 0.72 | 0.87 | 1.67 | 0.85 | 1.57 | 1.97 | 1.14 | 2.29 | 1.83 | 2.72 | 2.53
Total Utility Costs
| Cost Intensity ($/m2) | 11.91 | 14.96 | 10.46 | 13.12 | 7.12 | 12.22 | 16.61 | 10.12 | 4.88 | 9.06 | 11.58 | 5.04 | 9.03 | 9.86 | 9.13 | 12.81
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1456005.5556 | 1165750 | 906147.2222 | 781838.8889 | 555172.2222 | 638291.6667 | 199722.2222 | 669625 | 365944.4444 | 179463.8889 | 414247.2222 | 257983.3333 | 362566.6667 | 179816.6667 | 185933.3333 | 118811.1111
| Interior Lighting | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222
| Exterior Lighting | 13458.3333 | 13452.7778 | 13450 | 13447.2222 | 13438.8889 | 13436.1111 | 13441.6667 | 13433.3333 | 13438.8889 | 13413.8889 | 13436.1111 | 13427.7778 | 13427.7778 | 13425 | 13416.6667 | 13333.3333
| Interior Equipment | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222
| Exterior Equipment | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111
| Fans | 180652.7778 | 179883.3333 | 218322.2222 | 179875 | 170122.2222 | 215861.1111 | 154905.5556 | 182372.2222 | 216269.4444 | 179811.1111 | 195619.4444 | 207236.1111 | 200811.1111 | 202697.2222 | 213330.5556 | 264358.3333
| Pumps | 327266.6667 | 331247.2222 | 301061.1111 | 319144.4444 | 254258.3333 | 237211.1111 | 163158.3333 | 321716.6667 | 157519.4444 | 130300 | 177888.8889 | 130327.7778 | 169211.1111 | 113113.8889 | 124391.6667 | 122897.2222
| Heat Rejection | 263925 | 248558.3333 | 243069.4444 | 220441.6667 | 210822.2222 | 181827.7778 | 125150 | 188441.6667 | 115777.7778 | 93041.6667 | 111413.8889 | 88052.7778 | 104108.3333 | 71038.8889 | 66833.3333 | 57263.8889
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 6425611.1111 | 6123197.2222 | 5866355.5556 | 5699055.5556 | 5388119.4444 | 5470930.5556 | 4840683.3333 | 5559894.4444 | 5053252.7778 | 4780333.3333 | 5096911.1111 | 4881333.3333 | 5034433.3333 | 4764394.4444 | 4788211.1111 | 4760969.4444
Gas (MJ)
| Heating | 388680 | 3490100 | 2692520 | 5673690 | 2435370 | 4118020 | 4457180 | 7732160 | 5451890 | 8366060 | 10651290 | 7354550 | 13128800 | 10190350 | 15668140 | 27991890
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 176820 | 211580 | 191500 | 245150 | 238720 | 215610 | 267430 | 271530 | 266560 | 285330 | 294720 | 293510 | 314720 | 318390 | 347740 | 387670
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 565490 | 3701690 | 2884020 | 5918840 | 2674090 | 4333630 | 4724600 | 8003690 | 5718450 | 8651380 | 10946010 | 7648060 | 13443510 | 10508740 | 16015880 | 28379550
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 23697700 | 25745190 | 24002890 | 26435440 | 22071320 | 24028980 | 22151060 | 28019310 | 23910160 | 25860580 | 29294900 | 25220860 | 31567470 | 27660560 | 33253430 | 45519040
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 113.1601 | 90.6016 | 70.4254 | 60.7642 | 43.1477 | 49.6078 | 15.5223 | 52.043 | 28.441 | 13.9479 | 32.1951 | 20.0504 | 28.1785 | 13.9753 | 14.4507 | 9.2339
| Interior Lighting (elec) | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367
| Exterior Lighting (elec) | 1.046 | 1.0455 | 1.0453 | 1.0451 | 1.0445 | 1.0442 | 1.0447 | 1.044 | 1.0445 | 1.0425 | 1.0442 | 1.0436 | 1.0436 | 1.0434 | 1.0427 | 1.0363
| Interior Equipment (elec) | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533
| Exterior Equipment (elec) | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124
| Fans (elec) | 14.0403 | 13.9805 | 16.9679 | 13.9798 | 13.2218 | 16.7766 | 12.0392 | 14.1739 | 16.8084 | 13.9748 | 15.2035 | 16.1063 | 15.607 | 15.7535 | 16.58 | 20.5458
| Pumps (elec) | 25.435 | 25.7444 | 23.3983 | 24.8038 | 19.7608 | 18.4359 | 12.6806 | 25.0037 | 12.2423 | 10.1269 | 13.8254 | 10.129 | 13.151 | 8.7912 | 9.6677 | 9.5515
| Heat Rejection (elec) | 20.5121 | 19.3178 | 18.8913 | 17.1326 | 16.385 | 14.1316 | 9.7266 | 14.6456 | 8.9982 | 7.2312 | 8.659 | 6.8434 | 8.0913 | 5.5211 | 5.1943 | 4.4505
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 499.3957 | 475.8923 | 455.9306 | 442.9281 | 418.7623 | 425.1984 | 376.2158 | 432.1126 | 392.7366 | 371.5254 | 396.1297 | 379.3751 | 391.274 | 370.2867 | 372.1377 | 370.0205
Gas (MJ/m2)
| Heating (gas) | 8.3911 | 75.347 | 58.1282 | 122.488 | 52.5766 | 88.903 | 96.225 | 166.9278 | 117.6996 | 180.6129 | 229.9482 | 158.7757 | 283.4346 | 219.9971 | 338.2559 | 604.3105
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.8173 | 4.5678 | 4.1342 | 5.2925 | 5.1537 | 4.6548 | 5.7735 | 5.862 | 5.7547 | 6.1599 | 6.3626 | 6.3365 | 6.7944 | 6.8736 | 7.5073 | 8.3693
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 12.2082 | 79.9149 | 62.2624 | 127.7805 | 57.7303 | 93.5577 | 101.9983 | 172.7898 | 123.4543 | 186.7726 | 236.3109 | 165.1122 | 290.2288 | 226.8708 | 345.7631 | 612.6796
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 511.6042 | 555.807 | 518.1929 | 570.7086 | 476.4926 | 518.7561 | 478.2141 | 604.9024 | 516.1909 | 558.2981 | 632.4408 | 544.4873 | 681.5028 | 597.1574 | 717.9006 | 982.7001
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1562.1328 | 1502.1224 | 1381.2793 | 1368.25 | 1374.377 | 1290.8996 | 1221.5564 | 1320.3541 | 1243.5536 | 1176.4526 | 1183.9737 | 1236.5676 | 1183.8331 | 1172.1543 | 1182.8974 | 1201.1837
| Feb | 1594.0919 | 1448.0539 | 1404.8485 | 1372.8594 | 1352.8469 | 1332.885 | 1330.112 | 1298.9887 | 1311.6831 | 1251.673 | 1184.5725 | 1173.136 | 1184.0856 | 1194.7759 | 1168.5691 | 1162.4969
| Mar | 1600.8118 | 1489.2262 | 1467.1607 | 1398.3198 | 1376.9704 | 1356.8238 | 1275.2802 | 1409.9499 | 1311.9453 | 1312.251 | 1345.2207 | 1301.226 | 1221.9715 | 1301.0557 | 1181.04 | 1191.2792
| Apr | 1648.2455 | 1539.4992 | 1465.0666 | 1451.5834 | 1423.086 | 1443.3578 | 1317.5341 | 1401.9051 | 1359.7626 | 1280.4344 | 1367.4087 | 1334.6132 | 1350.5162 | 1281.8494 | 1220.4096 | 1191.4469
| May | 1754.7046 | 1721.627 | 1570.1127 | 1577.4014 | 1514.7375 | 1516.1805 | 1336.3754 | 1552.1711 | 1437.6613 | 1378.7382 | 1566.9504 | 1389.9965 | 1485.5087 | 1324.3121 | 1365.9458 | 1355.8503
| Jun | 1834.4639 | 1715.1806 | 1742.9481 | 1628.4183 | 1462.9089 | 1667.4183 | 1367.9604 | 1690.3465 | 1545.3199 | 1388.9213 | 1624.832 | 1442.1378 | 1636.4532 | 1473.7664 | 1523.3417 | 1459.4675
| Jul | 1794.3874 | 1836.301 | 1780.6096 | 1721.2065 | 1521.4511 | 1677.5228 | 1407.8222 | 1738.2996 | 1553.1003 | 1448.4368 | 1650.8192 | 1503.8585 | 1673.4232 | 1463.8652 | 1650.0169 | 1460.3002
| Aug | 1834.2906 | 1782.5485 | 1740.9325 | 1660.3037 | 1663.2391 | 1681.7411 | 1348.9773 | 1795.2126 | 1573.3003 | 1422.7919 | 1742.9294 | 1496.0688 | 1643.5768 | 1438.2097 | 1543.5109 | 1449.664
| Sep | 1755.7349 | 1756.6738 | 1709.5528 | 1616.5452 | 1532.7532 | 1630.6015 | 1465.0287 | 1512.2266 | 1462.3543 | 1434.5271 | 1545.3698 | 1415.9016 | 1544.1181 | 1378.3852 | 1520.2385 | 1295.5012
| Oct | 1732.0501 | 1624.8322 | 1546.5913 | 1474.6129 | 1461.5316 | 1465.4663 | 1360.0052 | 1481.5247 | 1380.6324 | 1335.7877 | 1452.2791 | 1366.4387 | 1375.5178 | 1334.9928 | 1303.6469 | 1195.5475
| Nov | 1611.0635 | 1550.3631 | 1448.0068 | 1382.3424 | 1382.9616 | 1338.804 | 1305.5391 | 1429.8353 | 1295.4765 | 1258.4671 | 1464.1431 | 1258.5969 | 1325.7948 | 1187.0149 | 1181.1193 | 1195.4181
| Dec | 1556.0342 | 1484.7258 | 1383.4312 | 1391.5469 | 1356.7115 | 1321.8266 | 1212.2821 | 1275.57 | 1209.8262 | 1176.4291 | 1185.4257 | 1172.9225 | 1183.5974 | 1163.8279 | 1158.5775 | 1199.4369
Time of Peak Electrical Demand
| Jan | 23-JAN-16:10 | 03-JAN-08:00 | 26-JAN-16:10 | 24-JAN-16:00 | 25-JAN-16:10 | 18-JAN-16:10 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:10 | 17-JAN-08:50 | 03-JAN-08:00 | 27-JAN-16:10 | 31-JAN-08:09 | 10-JAN-08:20 | 11-JAN-08:30 | 13-JAN-08:30
| Feb | 21-FEB-16:10 | 15-FEB-16:10 | 28-FEB-16:10 | 22-FEB-08:09 | 13-FEB-11:00 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:10 | 21-FEB-16:10 | 09-FEB-08:50 | 13-FEB-08:50 | 13-FEB-08:00 | 03-FEB-16:19 | 01-FEB-08:20 | 02-FEB-09:39
| Mar | 13-MAR-15:09 | 29-MAR-07:00 | 17-MAR-15:00 | 29-MAR-15:09 | 31-MAR-15:09 | 31-MAR-15:20 | 20-MAR-15:09 | 09-MAR-16:10 | 02-MAR-16:10 | 29-MAR-15:30 | 31-MAR-15:50 | 30-MAR-15:09 | 23-MAR-15:00 | 30-MAR-15:09 | 28-MAR-07:49 | 10-MAR-08:00
| Apr | 03-APR-15:09 | 25-APR-15:20 | 17-APR-15:00 | 20-APR-15:00 | 11-APR-15:00 | 21-APR-15:30 | 13-APR-15:09 | 04-APR-07:00 | 21-APR-15:00 | 14-APR-15:09 | 10-APR-08:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:39 | 04-APR-15:09 | 17-APR-07:10
| May | 15-MAY-15:00 | 18-MAY-15:30 | 30-MAY-15:00 | 31-MAY-15:00 | 30-MAY-07:00 | 31-MAY-15:00 | 25-MAY-15:50 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-08:00 | 24-MAY-15:00 | 31-MAY-15:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:09
| Jun | 27-JUN-15:39 | 29-JUN-15:00 | 28-JUN-15:00 | 08-JUN-15:00 | 29-JUN-07:00 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:09 | 08-JUN-12:00 | 27-JUN-15:30 | 29-JUN-15:00 | 26-JUN-15:30 | 14-JUN-15:20 | 21-JUN-15:39
| Jul | 13-JUL-15:39 | 18-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 24-JUL-15:09 | 07-JUL-15:00 | 03-JUL-15:09 | 25-JUL-15:50 | 03-JUL-15:30 | 31-JUL-15:00 | 13-JUL-15:09 | 18-JUL-15:09 | 13-JUL-15:00 | 21-JUL-15:00 | 07-JUL-07:00 | 03-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 11-AUG-15:50 | 14-AUG-15:00 | 16-AUG-15:00 | 02-AUG-15:09 | 14-AUG-15:09 | 09-AUG-15:09 | 01-AUG-15:30 | 18-AUG-15:30 | 04-AUG-15:00 | 30-AUG-15:30 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-15:09
| Sep | 11-SEP-15:09 | 15-SEP-15:20 | 12-SEP-15:09 | 05-SEP-15:00 | 07-SEP-08:00 | 01-SEP-15:09 | 28-SEP-15:20 | 27-SEP-15:09 | 05-SEP-15:09 | 01-SEP-15:50 | 07-SEP-12:00 | 01-SEP-15:00 | 22-SEP-15:00 | 01-SEP-15:00 | 07-SEP-15:30 | 07-SEP-15:00
| Oct | 06-OCT-15:30 | 30-OCT-15:09 | 03-OCT-13:09 | 20-OCT-15:00 | 05-OCT-15:00 | 03-OCT-15:09 | 13-OCT-15:20 | 03-OCT-07:00 | 11-OCT-15:50 | 17-OCT-15:09 | 31-OCT-07:00 | 05-OCT-15:30 | 06-OCT-15:09 | 06-OCT-15:20 | 27-OCT-15:09 | 23-OCT-07:00
| Nov | 01-NOV-15:09 | 27-NOV-16:00 | 13-NOV-16:10 | 22-NOV-08:00 | 09-NOV-16:10 | 10-NOV-16:10 | 16-NOV-16:10 | 03-NOV-15:09 | 08-NOV-16:10 | 03-NOV-15:09 | 02-NOV-07:00 | 10-NOV-13:00 | 02-NOV-15:09 | 21-NOV-16:10 | 30-NOV-08:30 | 28-NOV-08:39
| Dec | 15-DEC-16:10 | 06-DEC-16:10 | 11-DEC-16:10 | 26-DEC-08:00 | 18-DEC-08:00 | 05-DEC-16:10 | 20-DEC-08:09 | 08-DEC-08:00 | 05-DEC-16:10 | 13-DEC-08:30 | 26-DEC-08:30 | 20-DEC-08:09 | 08-DEC-08:50 | 11-DEC-08:20 | 11-DEC-08:09 | 28-DEC-08:39
Source Energy
| Total Source Energy (GJ) | 77347.04 | 84104.27 | 69948.36 | 75481.22 | 62954.52 | 75182.59 | 59094.16 | 80315.88 | 66604.63 | 39425.74 | 77018.19 | 66658.22 | 76972.37 | 71095.28 | 76734.82 | 92212.71
| Total Source Energy (MJ/m2) | 1669.83 | 1815.71 | 1510.1 | 1629.55 | 1359.11 | 1623.1 | 1275.77 | 1733.92 | 1437.91 | 851.15 | 1662.73 | 1439.07 | 1661.74 | 1534.86 | 1656.61 | 1990.76
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 22471.43 | 18691.78 | 29529.34 | 14917.88 | 11338.47 | 23579.48 | 5323.04 | 13031.18 | 12465.64 | 4659.95 | 8216.89 | 8865.32 | 7216.54 | 6161.09 | 4042.69 | 3516.34
| Water Systems | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13
| Total Building | 23975.56 | 20195.91 | 31033.47 | 16422.01 | 12842.6 | 25083.61 | 6827.17 | 14535.32 | 13969.78 | 6164.08 | 9721.02 | 10369.45 | 8720.67 | 7665.22 | 5546.82 | 5020.47
Emissions
| Carbon Equivalent (kg) | 1772420 | 2109210 | 1822920 | 1862250 | 677907.9479 | 1923360 | 650907.8362 | 1644700 | 2167360 | 504179.1951 | 2914800 | 2131930 | 1965670 | 1930590 | 1927780 | 1851440
| CO2 (kg) | 4109980 | 5317970 | 4314900 | 4292700 | 1820480 | 4596180 | 1756500 | 3781620 | 5107820 | 1277810 | 6840100 | 5044710 | 4673180 | 4597050 | 4612900 | 4834490
| NOX (kg) | 7223.1767 | 6911.586 | 7175.3363 | 7973.6865 | 1565.1768 | 7372.1189 | 1515.9944 | 7105.8234 | 8709.6155 | 1738.1048 | 11934.4221 | 8513.7737 | 7885.4621 | 7685.3926 | 7652.5731 | 5546.6685
| SO2 (kg) | 27504.3426 | 29208.6413 | 23590.5608 | 20005.2723 | 15679.4943 | 30095.6577 | 14087.0749 | 20297.9804 | 22068.0727 | 3697.1334 | 34352.0447 | 21317.8524 | 11885.671 | 12724.324 | 11305.2335 | 24242.8376
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1254 | 0.0825 | 0.0643 | 0.0736 | 0.0073 | 0.0568 | 0.0068 | 0.0826 | 0.0865 | 0.0153 | 0.1047 | 0.0838 | 0.0881 | 0.0893 | 0.0841 | 0.085
| Water for Electricity (m3) | 3404.02 | 9963.16 | 174257 | 35582.6 | 94603.3 | 150090 | 84991.6 | 1262.3 | 22945.8 | 48839.7 | 7907.55 | 22165.1 | 7810.62 | 301797 | 7428.62 | 4864.19

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 23697.7 | 511.6 | 511.6
Net Site Energy | 23697.7 | 511.6 | 511.6
Total Source Energy | 77347.04 | 1669.83 | 1669.83
Net Source Energy | 77347.04 | 1669.83 | 1669.83
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 388.68 | 0 | 0 | 0 | 0
Cooling | 5241.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.45 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 650.35 | 0 | 0 | 0 | 0 | 0
Pumps | 1178.16 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 950.13 | 0 | 0 | 0 | 0 | 22471.43
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 176.82 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 23132.2 | 565.49 | 0 | 0 | 0 | 23975.56
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 1390.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4356174.81 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 2888716.07 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4155120.59
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 389305.88 | 270481.61 | 118824.27 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 4480918.36 | 3128437.69 | 1352480.67 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 437816.81 | 305283.09 | 132533.72 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 130887.86 | 90286.79 | 40601.07 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 68464.78 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 120713.91 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1523557.25 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 143802.96 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17846.2 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21475.6 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18734.75 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24605.67 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 184311.4 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 216058.45 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 182329.69 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 250406.51 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19334.37 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20239.81 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 20704.28 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25669.66 | -
VAV_1_HEATC | Coil:Heating:Water | 4280.96 | -
VAV_2_HEATC | Coil:Heating:Water | 1920.2 | -
VAV_3_HEATC | Coil:Heating:Water | 945.34 | -
VAV_5_HEATC | Coil:Heating:Water | 22520.83 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.57 | 27900.46 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 192.06 | 316496.04 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.72 | 31518.75 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.58 | 10467.23 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 39918.31 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16360.97 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 58643.73 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 324796.4149 | 565.638 | 2132.776 | 0 | 0.0097 | 263954.8365 | 139548.3688
February | 293395.6269 | 513.4454 | 1946.1992 | 0 | 0.0089 | 240865.7808 | 126306.7941
March | 339899.6742 | 596.1875 | 2265.3777 | 0 | 0.0103 | 280369.0233 | 146463.0069
April | 320294.3936 | 563.9988 | 2152.0206 | 0 | 0.0098 | 266341.3072 | 138235.4351
May | 361892.6801 | 637.4535 | 2433.1302 | 0 | 0.0111 | 301132.538 | 156209.3531
June | 367893.4009 | 648.2091 | 2474.9362 | 0 | 0.0113 | 306306.7259 | 158818.1375
July | 368795.7316 | 649.844 | 2481.3614 | 0 | 0.0113 | 307101.959 | 159212.1881
August | 391989.7391 | 690.6808 | 2637.1597 | 0 | 0.012 | 326384.0848 | 169221.9569
September | 356404.8778 | 627.8619 | 2396.8231 | 0 | 0.0109 | 296639.0954 | 153848.0694
October | 347598.4611 | 612.1598 | 2336.118 | 0 | 0.0106 | 289125.8885 | 150027.7681
November | 324038.0591 | 570.2372 | 2174.3896 | 0 | 0.0099 | 269109.5119 | 139815.7136
December | 312984.0542 | 547.4604 | 2074.0509 | 0 | 0.0095 | 256688.787 | 134713.0621
Annual Sum or Average | 4109980 | 7223.1767 | 27504.3426 | 0 | 0.1254 | 3404020 | 1772420
Minimum of Months | 293395.6269 | 513.4454 | 1946.1992 | 0 | 0.0089 | 240865.7808 | 126306.7941
Maximum of Months | 391989.7391 | 690.6808 | 2637.1597 | 0 | 0.012 | 326384.0848 | 169221.9569
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1793720000000 | 1562132.823 | 23-JAN-16:10 | 645239.307 | 326066.958 | 44110.229 | 0 | 337581.059 | 0 | 69043.926 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1636820000000 | 1594091.889 | 21-FEB-16:10 | 645239.307 | 326066.958 | 46772.926 | 0 | 366062.695 | 0 | 69858.661 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1905260000000 | 1600811.774 | 13-MAR-15:09 | 645239.307 | 326066.958 | 41838.799 | 0 | 378045.947 | 0 | 69529.42 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1809940000000 | 1648245.452 | 03-APR-15:09 | 645239.307 | 326066.958 | 53744.743 | 0 | 411925.421 | 0 | 71177.679 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 2046360000000 | 1754704.613 | 15-MAY-15:00 | 645239.307 | 326066.958 | 57846.75 | 0 | 511952.749 | 0 | 73507.507 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2081520000000 | 1834463.918 | 27-JUN-15:39 | 645239.307 | 326066.958 | 57622.613 | 0 | 590852.405 | 0 | 74591.292 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2086930000000 | 1794387.377 | 13-JUL-15:39 | 645239.307 | 326066.958 | 57456.934 | 0 | 551570.297 | 0 | 73962.538 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2217960000000 | 1834290.611 | 21-AUG-15:09 | 645239.307 | 326066.958 | 62240.643 | 0 | 585798.761 | 0 | 74853.599 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 2015830000000 | 1755734.883 | 11-SEP-15:09 | 645239.307 | 326066.958 | 60057.961 | 0 | 510802.715 | 0 | 73476.6 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1964770000000 | 1732050.079 | 06-OCT-15:30 | 645239.307 | 326066.958 | 54995.043 | 0 | 492798.642 | 0 | 72858.786 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1828750000000 | 1611063.493 | 01-NOV-15:09 | 645239.307 | 326066.958 | 40137.513 | 0 | 389930.121 | 0 | 69598.251 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1744340000000 | 1556034.161 | 15-DEC-16:10 | 645239.307 | 326066.958 | 37998.666 | 0 | 338132.735 | 0 | 68505.152 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 23132200000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1636820000000 | 1556034.161 |  | 645239.307 | 326066.958 | 37998.666 | 0 | 337581.059 | 0 | 68505.152 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2217960000000 | 1834463.918 |  | 645239.307 | 326066.958 | 62240.643 | 0 | 590852.405 | 0 | 74853.599 | 54535.958 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 545268.18 | 6435.71 | 0 | 551703.89
Cost per Total Building Area ($/m2) | 11.77 | 0.14 | 0 | 11.91
Cost per Net Conditioned Building Area ($/m2) | 11.77 | 0.14 | 0 | 11.91

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25745.19 | 555.81 | 555.81
Net Site Energy | 25745.19 | 555.81 | 555.81
Total Source Energy | 84104.27 | 1815.71 | 1815.71
Net Source Energy | 84104.27 | 1815.71 | 1815.71
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3490.1 | 0 | 0 | 0 | 0
Cooling | 4196.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.43 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 647.58 | 0 | 0 | 0 | 0 | 0
Pumps | 1192.49 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 894.81 | 0 | 0 | 0 | 0 | 18691.78
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 211.58 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 22043.51 | 3701.69 | 0 | 0 | 0 | 20195.91
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 1390.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4216582.87 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3174745.12 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4021971.36
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 399553.78 | 278253.97 | 121299.81 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 4421785.36 | 3090429.04 | 1331356.32 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 424717.45 | 296408.46 | 128308.99 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 122583.35 | 85069.86 | 37513.48 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 65857.21 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 128848 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1501530.39 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 139328.57 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19209.61 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21168.84 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18285.85 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25035.82 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 198604.11 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 215198.22 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 189468.18 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 254510.46 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20249.04 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19972.35 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 20528.11 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26017.55 | -
VAV_1_HEATC | Coil:Heating:Water | 26280.92 | -
VAV_2_HEATC | Coil:Heating:Water | 235398.9 | -
VAV_3_HEATC | Coil:Heating:Water | 24698.61 | -
VAV_5_HEATC | Coil:Heating:Water | 17497.09 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.39 | 29265.8 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 192.98 | 318015.11 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.49 | 31131.16 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.39 | 10105.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 38639.15 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17980.97 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 56764.51 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 439044.8914 | 556.9558 | 2220.1732 | 0 | 0.0063 | 757246.8871 | 172373.4718
February | 391006.0054 | 495.7153 | 1973.0448 | 0 | 0.0056 | 672955.9561 | 153474.2257
March | 438668.6142 | 568.0304 | 2380.0607 | 0 | 0.0067 | 811836.7999 | 173714.7655
April | 405785.1501 | 530.5096 | 2272.513 | 0 | 0.0064 | 775175.2771 | 161344.9762
May | 455936.3754 | 598.52 | 2587.6088 | 0 | 0.0073 | 882668.1231 | 181600.7722
June | 481123.0237 | 632.0654 | 2737.3067 | 0 | 0.0077 | 933734.192 | 191694.8497
July | 485111.2145 | 637.3303 | 2760.354 | 0 | 0.0078 | 941596.0657 | 193287.1571
August | 512975.4447 | 673.9068 | 2918.471 | 0 | 0.0082 | 995531.8985 | 204385.3499
September | 439745.5607 | 577.629 | 2500.8059 | 0 | 0.007 | 853060.0673 | 175198.7328
October | 429107.7188 | 562.2737 | 2420.9539 | 0 | 0.0068 | 825815.4509 | 170782.3829
November | 406170.7402 | 528.5474 | 2240.1306 | 0 | 0.0063 | 764118.5076 | 161180.3886
December | 433298.8977 | 550.1023 | 2197.2187 | 0 | 0.0063 | 749419.7783 | 170173.6954
Annual Sum or Average | 5317970 | 6911.586 | 29208.6413 | 0 | 0.0825 | 9963160 | 2109210
Minimum of Months | 391006.0054 | 495.7153 | 1973.0448 | 0 | 0.0056 | 672955.9561 | 153474.2257
Maximum of Months | 512975.4447 | 673.9068 | 2918.471 | 0 | 0.0082 | 995531.8985 | 204385.3499
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1675410000000 | 1502122.393 | 03-JAN-08:00 | 645239.307 | 326066.958 | 33447.873 | 0 | 257685.119 | 0 | 64672.784 | 52788.374 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1488920000000 | 1448053.916 | 15-FEB-16:10 | 645239.307 | 326066.958 | 33479.877 | 0 | 240747.801 | 0 | 64176.215 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1796190000000 | 1489226.163 | 29-MAR-07:00 | 645239.307 | 326066.958 | 33447.873 | 0 | 245067.064 | 0 | 64394.608 | 52788.374 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1715080000000 | 1539499.22 | 25-APR-15:20 | 645239.307 | 326066.958 | 37382.47 | 0 | 326068.965 | 0 | 66397.761 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1952900000000 | 1721626.971 | 18-MAY-15:30 | 645239.307 | 326066.958 | 53707.516 | 0 | 487455.934 | 0 | 70813.498 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2065890000000 | 1715180.634 | 29-JUN-15:00 | 645239.307 | 326066.958 | 51157.103 | 0 | 483931.061 | 0 | 70442.446 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2083280000000 | 1836300.989 | 18-JUL-15:00 | 645239.307 | 326066.958 | 61425.559 | 0 | 591961.733 | 0 | 73263.673 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2202620000000 | 1782548.513 | 31-AUG-15:00 | 645239.307 | 326066.958 | 61360.919 | 0 | 539173.481 | 0 | 72364.089 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1887400000000 | 1756673.826 | 15-SEP-15:20 | 645239.307 | 326066.958 | 46491.732 | 0 | 529943.601 | 0 | 70588.469 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1827120000000 | 1624832.216 | 30-OCT-15:09 | 645239.307 | 326066.958 | 38209.716 | 0 | 409113.287 | 0 | 67859.189 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1690610000000 | 1550363.113 | 27-NOV-16:00 | 645239.307 | 326066.958 | 34604.258 | 0 | 339685.892 | 0 | 66422.939 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1658090000000 | 1484725.792 | 06-DEC-16:10 | 645239.307 | 326066.958 | 33447.873 | 0 | 276625.642 | 0 | 65002.253 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 22043500000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1488920000000 | 1448053.916 |  | 645239.307 | 326066.958 | 33447.873 | 0 | 240747.801 | 0 | 64176.215 | 52788.374 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2202620000000 | 1836300.989 |  | 645239.307 | 326066.958 | 61425.559 | 0 | 591961.733 | 0 | 73263.673 | 52788.374 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 663289.61 | 29800.86 | 0 | 693090.47
Cost per Total Building Area ($/m2) | 14.32 | 0.64 | 0 | 14.96
Cost per Net Conditioned Building Area ($/m2) | 14.32 | 0.64 | 0 | 14.96

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 24002.89 | 518.19 | 518.19
Net Site Energy | 24002.89 | 518.19 | 518.19
Total Source Energy | 69948.36 | 1510.1 | 1510.1
Net Source Energy | 69948.36 | 1510.1 | 1510.1
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2692.52 | 0 | 0 | 0 | 0
Cooling | 3262.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 785.96 | 0 | 0 | 0 | 0 | 0
Pumps | 1083.82 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 875.05 | 0 | 0 | 0 | 0 | 29529.34
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 191.5 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21118.88 | 2884.02 | 0 | 0 | 0 | 31033.47
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 1390.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4292556.3 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3184634.11 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4094438.31
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 390063.54 | 267025.92 | 123037.62 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 4615032.34 | 3173006.52 | 1442025.82 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 462817.91 | 318324.96 | 144492.95 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 85012.8 | 57142.81 | 27869.99 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 46790.51 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 121171.03 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1575161.36 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 157730.44 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23278.57 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22655.35 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 20424.24 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26897.61 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 246475.69 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 238062.3 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 219049.87 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 276142.07 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24902.66 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23184.34 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 22856.04 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27862.49 | -
VAV_1_HEATC | Coil:Heating:Water | 12905.94 | -
VAV_2_HEATC | Coil:Heating:Water | 78184.85 | -
VAV_3_HEATC | Coil:Heating:Water | 7687.81 | -
VAV_5_HEATC | Coil:Heating:Water | 13269.5 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.19 | 30616.34 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 216.71 | 357113.27 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.76 | 36628.78 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.97 | 7570.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 39335.34 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18036.98 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 57787.28 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 329169.2868 | 526.734 | 1650.2728 | 0 | 0.0046 | 12189000 | 136976.0888
February | 297858.7555 | 480.1845 | 1519.0047 | 0 | 0.0042 | 11219700 | 124306.273
March | 352007.8568 | 584.3966 | 1917.5313 | 0 | 0.0052 | 14164200 | 148615.1795
April | 330429.3601 | 555.4049 | 1849.4115 | 0 | 0.005 | 13661400 | 140195.8161
May | 368987.602 | 622.712 | 2083.2786 | 0 | 0.0056 | 15389000 | 156807.8628
June | 401587.0359 | 678.2295 | 2270.964 | 0 | 0.0062 | 16775500 | 170712.3335
July | 416490.7477 | 703.4955 | 2355.935 | 0 | 0.0064 | 17403200 | 177057.4725
August | 430997.077 | 727.9587 | 2437.7064 | 0 | 0.0066 | 18007200 | 183220.3739
September | 377459.5547 | 637.439 | 2134.2185 | 0 | 0.0058 | 15765300 | 160451.6125
October | 352352.6404 | 592.9466 | 1977.1199 | 0 | 0.0054 | 14604800 | 149567.4567
November | 324780.4061 | 539.0001 | 1767.8083 | 0 | 0.0048 | 13058200 | 137100.3214
December | 332779.8451 | 526.835 | 1627.3097 | 0 | 0.0045 | 12019100 | 137904.5135
Annual Sum or Average | 4314900 | 7175.3363 | 23590.5608 | 0 | 0.0643 | 174257000 | 1822920
Minimum of Months | 297858.7555 | 480.1845 | 1519.0047 | 0 | 0.0042 | 11219700 | 124306.273
Maximum of Months | 430997.077 | 727.9587 | 2437.7064 | 0 | 0.0066 | 18007200 | 183220.3739
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1477240000000 | 1381279.331 | 26-JAN-16:10 | 645239.307 | 326066.958 | 40790.944 | 0 | 167308.845 | 0 | 62578.389 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1359760000000 | 1404848.492 | 28-FEB-16:10 | 645239.307 | 326066.958 | 42468.969 | 0 | 188714.498 | 0 | 63063.872 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1716620000000 | 1467160.672 | 17-MAR-15:00 | 645239.307 | 326066.958 | 48322.592 | 0 | 243912.069 | 0 | 64324.857 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1655680000000 | 1465066.613 | 17-APR-15:00 | 645239.307 | 326066.958 | 47188.754 | 0 | 243092.571 | 0 | 64184.135 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1865060000000 | 1570112.668 | 30-MAY-15:00 | 645239.307 | 326066.958 | 64690.59 | 0 | 328038.967 | 0 | 66781.958 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2033090000000 | 1742948.103 | 28-JUN-15:00 | 645239.307 | 326066.958 | 90309.617 | 0 | 463403.309 | 0 | 78634.025 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2109160000000 | 1780609.579 | 11-JUL-15:00 | 645239.307 | 326066.958 | 85359.182 | 0 | 509710.524 | 0 | 74938.72 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2182370000000 | 1740932.502 | 11-AUG-15:50 | 645239.307 | 326066.958 | 72258 | 0 | 484568.653 | 0 | 73504.696 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1910670000000 | 1709552.806 | 12-SEP-15:09 | 645239.307 | 326066.958 | 79463.451 | 0 | 446315.081 | 0 | 73173.121 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1770010000000 | 1546591.348 | 03-OCT-13:09 | 645239.307 | 326066.958 | 41955.445 | 0 | 373092.177 | 0 | 69831.364 | 53739.503 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
November | 1582580000000 | 1448006.794 | 13-NOV-16:10 | 645239.307 | 326066.958 | 46115.057 | 0 | 227402.978 | 0 | 63887.606 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1456650000000 | 1383431.233 | 11-DEC-16:10 | 645239.307 | 326066.958 | 40527.999 | 0 | 169751.922 | 0 | 62550.159 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 21118900000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1359760000000 | 1381279.331 |  | 645239.307 | 326066.958 | 40527.999 | 0 | 167308.845 | 0 | 62550.159 | 53739.503 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2182370000000 | 1780609.579 |  | 645239.307 | 326066.958 | 90309.617 | 0 | 509710.524 | 0 | 78634.025 | 53739.503 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 461048.24 | 23581.15 | 0 | 484629.39
Cost per Total Building Area ($/m2) | 9.95 | 0.51 | 0 | 10.46
Cost per Net Conditioned Building Area ($/m2) | 9.95 | 0.51 | 0 | 10.46

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 26435.44 | 570.71 | 570.71
Net Site Energy | 26435.44 | 570.71 | 570.71
Total Source Energy | 75481.22 | 1629.55 | 1629.55
Net Source Energy | 75481.22 | 1629.55 | 1629.55
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5673.69 | 0 | 0 | 0 | 0
Cooling | 2814.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.41 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 647.55 | 0 | 0 | 0 | 0 | 0
Pumps | 1148.92 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 793.59 | 0 | 0 | 0 | 0 | 14917.88
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 245.15 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20516.6 | 5918.84 | 0 | 0 | 0 | 16422.01
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 1390.85 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 3245.31 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4104936.47 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3243372.34 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3915477.86
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 373846.36 | 255587.13 | 118259.23 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 4174481.59 | 2865769.5 | 1308712.09 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 401916.23 | 275392.39 | 126523.84 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 126216.68 | 85873.08 | 40343.6 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 70477.53 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 129131.66 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1507580.17 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 139859.57 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18353.09 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19667.79 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16848.73 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 22430.06 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 192221.01 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 205855.37 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 175180.64 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 231795.47 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19717.12 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19346.32 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18799.39 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24070.4 | -
VAV_1_HEATC | Coil:Heating:Water | 35511.72 | -
VAV_2_HEATC | Coil:Heating:Water | 327359.76 | -
VAV_3_HEATC | Coil:Heating:Water | 33801.25 | -
VAV_5_HEATC | Coil:Heating:Water | 21074.77 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.46 | 29390.64 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 195.6 | 322329 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.76 | 31577.72 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.96 | 11182.45 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37616.06 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18369.66 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 55261.51 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 392427.513 | 670.7631 | 1543.6714 | 0 | 0.0058 | 2745110 | 164870.0313
February | 334455.204 | 586.0276 | 1385.9964 | 0 | 0.0052 | 2464880 | 141839.8998
March | 362536.5166 | 668.2095 | 1664.0278 | 0 | 0.0061 | 2959690 | 156794.5954
April | 331857.5849 | 625.2958 | 1590.039 | 0 | 0.0058 | 2828230 | 144785.1415
May | 351798.7141 | 675.1557 | 1745.8114 | 0 | 0.0064 | 3105420 | 154619.8625
June | 365675.7427 | 705.0479 | 1830.6578 | 0 | 0.0067 | 3256370 | 161020.0667
July | 370055.6738 | 713.3918 | 1852.0901 | 0 | 0.0068 | 3294490 | 162939.3864
August | 392571.229 | 756.9901 | 1965.7236 | 0 | 0.0072 | 3496630 | 172871.0347
September | 349615.5243 | 673.2979 | 1746.4093 | 0 | 0.0064 | 3106500 | 153875.6968
October | 336869.5043 | 639.3033 | 1636.4252 | 0 | 0.006 | 2910780 | 147393.2622
November | 336674.7921 | 616.5906 | 1525.9515 | 0 | 0.0056 | 2714070 | 145244.6128
December | 368157.4207 | 643.6132 | 1518.4687 | 0 | 0.0057 | 2700450 | 155997.2748
Annual Sum or Average | 4292700 | 7973.6865 | 20005.2723 | 0 | 0.0736 | 35582600 | 1862250
Minimum of Months | 331857.5849 | 586.0276 | 1385.9964 | 0 | 0.0052 | 2464880 | 141839.8998
Maximum of Months | 392571.229 | 756.9901 | 1965.7236 | 0 | 0.0072 | 3496630 | 172871.0347
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1582800000000 | 1368249.976 | 24-JAN-16:00 | 645239.307 | 326066.958 | 33961.166 | 0 | 164933.193 | 0 | 61103.32 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1421230000000 | 1372859.427 | 22-FEB-08:09 | 645239.307 | 326066.958 | 33961.166 | 0 | 133930.679 | 0 | 60048.692 | 51390.647 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1706530000000 | 1398319.813 | 29-MAR-15:09 | 645239.307 | 326066.958 | 33961.166 | 0 | 194267.977 | 0 | 61838.373 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1630730000000 | 1451583.407 | 20-APR-15:00 | 645239.307 | 326066.958 | 38863.527 | 0 | 241160.648 | 0 | 63306.935 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1790550000000 | 1577401.42 | 31-MAY-15:00 | 645239.307 | 326066.958 | 46710.282 | 0 | 355816.132 | 0 | 66622.709 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1877590000000 | 1628418.264 | 08-JUN-15:00 | 645239.307 | 326066.958 | 44535.438 | 0 | 408281.396 | 0 | 67349.133 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1899570000000 | 1721206.471 | 03-JUL-15:00 | 645239.307 | 326066.958 | 62345.169 | 0 | 480136.611 | 0 | 70472.394 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2016120000000 | 1660303.719 | 14-AUG-15:00 | 645239.307 | 326066.958 | 54014.331 | 0 | 429385.414 | 0 | 68651.677 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1791180000000 | 1616545.202 | 05-SEP-15:00 | 645239.307 | 326066.958 | 53245.019 | 0 | 387117.904 | 0 | 67929.982 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1678330000000 | 1474612.907 | 20-OCT-15:00 | 645239.307 | 326066.958 | 36224.317 | 0 | 266432.806 | 0 | 63703.486 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1564910000000 | 1382342.397 | 22-NOV-08:00 | 645239.307 | 326066.958 | 33961.166 | 0 | 143132.355 | 0 | 60329.986 | 51390.647 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1557060000000 | 1391546.922 | 26-DEC-08:00 | 645239.307 | 326066.958 | 33961.166 | 0 | 151614.854 | 0 | 61052.012 | 51390.647 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 20516600000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1421230000000 | 1368249.976 |  | 645239.307 | 326066.958 | 33961.166 | 0 | 133930.679 | 0 | 60048.692 | 51390.647 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2016120000000 | 1721206.471 |  | 645239.307 | 326066.958 | 62345.169 | 0 | 480136.611 | 0 | 70472.394 | 51390.647 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 550902.28 | 56671.52 | 0 | 607573.8
Cost per Total Building Area ($/m2) | 11.89 | 1.22 | 0 | 13.12
Cost per Net Conditioned Building Area ($/m2) | 11.89 | 1.22 | 0 | 13.12

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22071.32 | 476.49 | 476.49
Net Site Energy | 22071.32 | 476.49 | 476.49
Total Source Energy | 62954.52 | 1359.11 | 1359.11
Net Source Energy | 62954.52 | 1359.11 | 1359.11
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2435.37 | 0 | 0 | 0 | 0
Cooling | 1998.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 612.44 | 0 | 0 | 0 | 0 | 0
Pumps | 915.33 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 758.96 | 0 | 0 | 0 | 0 | 11338.47
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 238.72 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19397.23 | 2674.09 | 0 | 0 | 0 | 12842.6
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 1390.85 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3859047.04 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 2984254.51 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3680937.18
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 394555.03 | 279201.44 | 115353.6 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 4458945.4 | 3163490.93 | 1295454.47 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 398452.25 | 281947.23 | 116505.02 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 113234.13 | 79571.38 | 33662.75 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 62255.72 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 117525.79 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1444805.58 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 120357.05 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27092.93 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25247.61 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15313.61 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30629.31 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 275654.59 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 257561.69 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 157100.15 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 312697.91 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26785.59 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23314.45 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16275.94 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 31128.1 | -
VAV_1_HEATC | Coil:Heating:Water | 5817.32 | -
VAV_2_HEATC | Coil:Heating:Water | 21637.1 | -
VAV_3_HEATC | Coil:Heating:Water | 5561.11 | -
VAV_5_HEATC | Coil:Heating:Water | 8443.82 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.65 | 29711.31 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 200.2 | 329906.29 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.82 | 29993.8 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.09 | 9551.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35362.83 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16902.08 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 51951.29 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 153779.9104 | 132.9019 | 1201.4078 | 0 | 0.0006 | 7248330 | 56888.9332
February | 135606.98 | 117.0373 | 1087.8764 | 0 | 0.0005 | 6563490 | 50252.8717
March | 156659.9011 | 135.0054 | 1292.8864 | 0 | 0.0006 | 7800510 | 58164.8005
April | 142121.3623 | 122.2206 | 1218.6816 | 0 | 0.0006 | 7352980 | 52906.5917
May | 153509.6631 | 131.8174 | 1351.5463 | 0 | 0.0006 | 8154750 | 57253.4666
June | 152818.9431 | 131.0869 | 1370.0489 | 0 | 0.0006 | 8266480 | 57070.8581
July | 152897.4307 | 130.9904 | 1400.066 | 0 | 0.0006 | 8447690 | 57189.6039
August | 168979.9958 | 144.7659 | 1547.8317 | 0 | 0.0007 | 9339280 | 63206.6338
September | 151627.5831 | 129.9643 | 1377.3814 | 0 | 0.0006 | 8310780 | 56680.8974
October | 153646.2579 | 131.8711 | 1364.1316 | 0 | 0.0006 | 8230730 | 57339.1398
November | 148132.6304 | 127.4465 | 1260.1365 | 0 | 0.0006 | 7603060 | 55113.5791
December | 150697.1532 | 130.069 | 1207.4998 | 0 | 0.0006 | 7285200 | 55840.5722
Annual Sum or Average | 1820480 | 1565.1768 | 15679.4943 | 0 | 0.0073 | 94603300 | 677907.9479
Minimum of Months | 135606.98 | 117.0373 | 1087.8764 | 0 | 0.0005 | 6563490 | 50252.8717
Maximum of Months | 168979.9958 | 144.7659 | 1547.8317 | 0 | 0.0007 | 9339280 | 63206.6338
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1486180000000 | 1374377.045 | 25-JAN-16:10 | 645239.307 | 326066.958 | 39493.726 | 0 | 172926.085 | 0 | 56783.283 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1345760000000 | 1352846.851 | 13-FEB-11:00 | 645239.307 | 326066.958 | 45772.029 | 0 | 193247.959 | 0 | 57541.703 | 48312.301 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
March | 1599400000000 | 1376970.374 | 31-MAR-15:09 | 645239.307 | 326066.958 | 42240.146 | 0 | 172579.345 | 0 | 56976.933 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1507640000000 | 1423086.02 | 11-APR-15:00 | 645239.307 | 326066.958 | 41771.961 | 0 | 215072.252 | 0 | 61067.856 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1672030000000 | 1514737.485 | 30-MAY-07:00 | 645239.307 | 326066.958 | 38315.281 | 0 | 273196.408 | 0 | 61385.252 | 48312.301 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
June | 1694940000000 | 1462908.922 | 29-JUN-07:00 | 645239.307 | 326066.958 | 37522.795 | 0 | 223635.612 | 0 | 59909.971 | 48312.301 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
July | 1732090000000 | 1521451.137 | 24-JUL-15:09 | 645239.307 | 326066.958 | 42939.667 | 0 | 310824.044 | 0 | 62513.475 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1914900000000 | 1663239.148 | 16-AUG-15:00 | 645239.307 | 326066.958 | 46074.291 | 0 | 445926.29 | 0 | 66064.617 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1704020000000 | 1532753.206 | 07-SEP-08:00 | 645239.307 | 326066.958 | 39971.97 | 0 | 324740.747 | 0 | 62866.538 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1687610000000 | 1461531.578 | 05-OCT-15:00 | 645239.307 | 326066.958 | 43984.591 | 0 | 251174.508 | 0 | 61198.529 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1558910000000 | 1382961.596 | 09-NOV-16:10 | 645239.307 | 326066.958 | 38249.529 | 0 | 180880.708 | 0 | 58657.408 | 48312.301 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1493740000000 | 1356711.54 | 18-DEC-08:00 | 645239.307 | 326066.958 | 37502.148 | 0 | 121577.752 | 0 | 55791.096 | 48312.301 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 19397200000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1345760000000 | 1352846.851 |  | 645239.307 | 326066.958 | 37502.148 | 0 | 121577.752 | 0 | 55791.096 | 48312.301 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1914900000000 | 1663239.148 |  | 645239.307 | 326066.958 | 46074.291 | 0 | 445926.29 | 0 | 66064.617 | 48312.301 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 306867.7 | 22927.24 | 0 | 329794.94
Cost per Total Building Area ($/m2) | 6.62 | 0.49 | 0 | 7.12
Cost per Net Conditioned Building Area ($/m2) | 6.62 | 0.49 | 0 | 7.12

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 24028.98 | 518.76 | 518.76
Net Site Energy | 24028.98 | 518.76 | 518.76
Total Source Energy | 75182.59 | 1623.1 | 1623.1
Net Source Energy | 75182.59 | 1623.1 | 1623.1
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4118.02 | 0 | 0 | 0 | 0
Cooling | 2297.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 777.1 | 0 | 0 | 0 | 0 | 0
Pumps | 853.96 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 654.58 | 0 | 0 | 0 | 0 | 23579.48
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 215.61 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19695.35 | 4333.63 | 0 | 0 | 0 | 25083.61
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 1390.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3789018.48 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3137676.5 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3614140.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 348718.11 | 238160.86 | 110557.25 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 4130014.94 | 2831426.52 | 1298588.42 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 397950.18 | 272583.98 | 125366.2 | 0.68 | -
VAV_5_COOLC | Coil:Cooling:Water | 71027.98 | 47800.08 | 23227.9 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 42130.87 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 116260.41 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1515500.3 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 143057.79 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22372.99 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20459.26 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18709.32 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25412.92 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 234558.21 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 214293.83 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 199175.8 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 258028.57 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23074.39 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20234.88 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 20850.95 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25745.3 | -
VAV_1_HEATC | Coil:Heating:Water | 22245.78 | -
VAV_2_HEATC | Coil:Heating:Water | 175934.99 | -
VAV_3_HEATC | Coil:Heating:Water | 18703.48 | -
VAV_5_HEATC | Coil:Heating:Water | 16809.68 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.92 | 30164.67 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 213.53 | 351881.96 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.54 | 34580.44 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.72 | 7086.22 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34721.11 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17771.02 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 51008.55 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 376796.8475 | 568.4385 | 2129.5284 | 0 | 0.0041 | 10618800 | 153942.9092
February | 321250.5398 | 505.3826 | 2010.5571 | 0 | 0.0038 | 10026400 | 133404.937
March | 373982.7855 | 591.0421 | 2365.986 | 0 | 0.0045 | 11799000 | 155583.8305
April | 354088.5865 | 575.7099 | 2391.535 | 0 | 0.0045 | 11927100 | 148981.7554
May | 389340.0281 | 636.2171 | 2659.6297 | 0 | 0.005 | 13264200 | 164145.4874
June | 421634.0184 | 690.8546 | 2897.7748 | 0 | 0.0054 | 14452000 | 177954.5795
July | 432113.3139 | 708.1556 | 2971.0225 | 0 | 0.0056 | 14817300 | 182391.026
August | 454723.841 | 745.1892 | 3126.2861 | 0 | 0.0059 | 15591600 | 191932.5463
September | 392719.9751 | 643.4531 | 2698.8183 | 0 | 0.0051 | 13459700 | 165748.5031
October | 371628.8432 | 604.9901 | 2517.1619 | 0 | 0.0047 | 12553600 | 156440.9319
November | 345662.5948 | 549.0455 | 2212.7669 | 0 | 0.0042 | 11035100 | 144089.0283
December | 362239.1152 | 553.6407 | 2114.5909 | 0 | 0.0041 | 10544600 | 148739.8738
Annual Sum or Average | 4596180 | 7372.1189 | 30095.6577 | 0 | 0.0568 | 150090000 | 1923360
Minimum of Months | 321250.5398 | 505.3826 | 2010.5571 | 0 | 0.0038 | 10026400 | 133404.937
Maximum of Months | 454723.841 | 745.1892 | 3126.2861 | 0 | 0.0059 | 15591600 | 191932.5463
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1393440000000 | 1290899.578 | 18-JAN-16:10 | 645239.307 | 326066.958 | 36477.905 | 0 | 95966.554 | 0 | 54157.872 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1315710000000 | 1332885.048 | 08-FEB-16:10 | 645239.307 | 326066.958 | 37417.473 | 0 | 136084.303 | 0 | 55086.025 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1548320000000 | 1356823.833 | 31-MAR-15:20 | 645239.307 | 326066.958 | 38103.494 | 0 | 158831.061 | 0 | 55592.032 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1565120000000 | 1443357.762 | 21-APR-15:30 | 645239.307 | 326066.958 | 48122.945 | 0 | 233365.024 | 0 | 57572.545 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1740580000000 | 1516180.504 | 31-MAY-15:00 | 645239.307 | 326066.958 | 63669.821 | 0 | 288262.322 | 0 | 59951.114 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1896450000000 | 1667418.28 | 27-JUN-15:00 | 645239.307 | 326066.958 | 93322.209 | 0 | 405145.472 | 0 | 64653.352 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1944380000000 | 1677522.809 | 07-JUL-15:00 | 645239.307 | 326066.958 | 109286.006 | 0 | 391004.375 | 0 | 72935.182 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2046000000000 | 1681741.073 | 02-AUG-15:09 | 645239.307 | 326066.958 | 81328.672 | 0 | 428987.212 | 0 | 67127.942 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1766240000000 | 1630601.493 | 01-SEP-15:09 | 645239.307 | 326066.958 | 81971.925 | 0 | 370318.456 | 0 | 74013.865 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1647340000000 | 1465466.255 | 03-OCT-15:09 | 645239.307 | 326066.958 | 54611.884 | 0 | 248121.437 | 0 | 58435.688 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1448060000000 | 1338804.043 | 10-NOV-16:10 | 645239.307 | 326066.958 | 37814.094 | 0 | 141526.948 | 0 | 55165.754 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1383710000000 | 1321826.626 | 05-DEC-16:10 | 645239.307 | 326066.958 | 36503.658 | 0 | 126258.073 | 0 | 54767.648 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 19695400000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1315710000000 | 1290899.578 |  | 645239.307 | 326066.958 | 36477.905 | 0 | 95966.554 | 0 | 54157.872 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2046000000000 | 1681741.073 |  | 645239.307 | 326066.958 | 109286.006 | 0 | 428987.212 | 0 | 74013.865 | 47435.597 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 532990.46 | 33150.41 | 0 | 566140.87
Cost per Total Building Area ($/m2) | 11.51 | 0.72 | 0 | 12.22
Cost per Net Conditioned Building Area ($/m2) | 11.51 | 0.72 | 0 | 12.22

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22151.06 | 478.21 | 478.21
Net Site Energy | 22151.06 | 478.21 | 478.21
Total Source Energy | 59094.16 | 1275.77 | 1275.77
Net Source Energy | 59094.16 | 1275.77 | 1275.77
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4457.18 | 0 | 0 | 0 | 0
Cooling | 719 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 557.66 | 0 | 0 | 0 | 0 | 0
Pumps | 587.37 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 450.54 | 0 | 0 | 0 | 0 | 5323.04
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 267.43 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17426.46 | 4724.6 | 0 | 0 | 0 | 6827.17
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.65 | 0.721 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 1390.85 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 3245.31 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3311877.93 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 2932378.51 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3159022.02
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 360104.48 | 257504.12 | 102600.36 | 0.72 | -
VAV_2_COOLC | Coil:Cooling:Water | 4126587.39 | 2955467.09 | 1171120.29 | 0.72 | -
VAV_3_COOLC | Coil:Cooling:Water | 353059.79 | 252335.17 | 100724.62 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 78323.07 | 56227.47 | 22095.6 | 0.72 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 45707.35 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 114055.81 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1399251.24 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 111309.38 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31519.34 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19409.9 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12847.59 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24502.58 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 336774.49 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 199552.25 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 134642.47 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 253213.83 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31955.28 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17174.65 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12993.15 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24745.25 | -
VAV_1_HEATC | Coil:Heating:Water | 15285.31 | -
VAV_2_HEATC | Coil:Heating:Water | 116138 | -
VAV_3_HEATC | Coil:Heating:Water | 15788.82 | -
VAV_5_HEATC | Coil:Heating:Water | 13777.64 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.5 | 27767.51 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 189.42 | 312144.1 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.16 | 27196.95 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.73 | 7107.6 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30348.78 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16608.26 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 44585.19 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 163321.2621 | 142.1957 | 1088.4632 | 0 | 0.0006 | 6566170 | 59846.6218
February | 133893.8741 | 115.8141 | 1028.4428 | 0 | 0.0005 | 6204730 | 49478.6332
March | 155825.2602 | 134.8909 | 1177.7794 | 0 | 0.0006 | 7105620 | 57524.7429
April | 140183.5063 | 121.0234 | 1118.0992 | 0 | 0.0005 | 6745800 | 51929.0236
May | 147126.8593 | 126.6764 | 1234.549 | 0 | 0.0006 | 7448620 | 54687.4134
June | 144139.026 | 123.9564 | 1235.8614 | 0 | 0.0006 | 7456630 | 53657.3236
July | 139434.2962 | 119.7538 | 1223.5577 | 0 | 0.0006 | 7382500 | 51991.4704
August | 150535.8468 | 129.296 | 1319.6119 | 0 | 0.0006 | 7962050 | 56126.7933
September | 138499.906 | 118.8877 | 1226.7311 | 0 | 0.0006 | 7401690 | 51677.7583
October | 142465.6999 | 122.4861 | 1227.1185 | 0 | 0.0006 | 7403900 | 53051.5083
November | 144181.8148 | 124.5176 | 1142.4053 | 0 | 0.0006 | 6892420 | 53387.0019
December | 156895.8961 | 136.4963 | 1064.4556 | 0 | 0.0006 | 6421430 | 57549.5454
Annual Sum or Average | 1756500 | 1515.9944 | 14087.0749 | 0 | 0.0068 | 84991600 | 650907.8362
Minimum of Months | 133893.8741 | 115.8141 | 1028.4428 | 0 | 0.0005 | 6204730 | 49478.6332
Maximum of Months | 163321.2621 | 142.1957 | 1319.6119 | 0 | 0.0006 | 7962050 | 59846.6218
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1346310000000 | 1221556.427 | 06-JAN-16:10 | 645239.307 | 326066.958 | 32216.647 | 0 | 44002.991 | 0 | 47012.976 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1272200000000 | 1330112.049 | 15-FEB-16:10 | 645239.307 | 326066.958 | 35316.093 | 0 | 146054.463 | 0 | 50417.679 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1456920000000 | 1275280.237 | 20-MAR-15:09 | 645239.307 | 326066.958 | 32392.916 | 0 | 94546.895 | 0 | 50016.612 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1383140000000 | 1317534.122 | 13-APR-15:09 | 645239.307 | 326066.958 | 34732.353 | 0 | 135942.918 | 0 | 48535.037 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1527250000000 | 1336375.408 | 25-MAY-15:50 | 645239.307 | 326066.958 | 34105.172 | 0 | 153695.794 | 0 | 50250.628 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1528890000000 | 1367960.39 | 16-JUN-15:00 | 645239.307 | 326066.958 | 38248.227 | 0 | 179394.966 | 0 | 51993.383 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1513690000000 | 1407822.156 | 03-JUL-15:09 | 645239.307 | 326066.958 | 41787.603 | 0 | 215436.348 | 0 | 52274.391 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1632520000000 | 1348977.295 | 14-AUG-15:09 | 645239.307 | 326066.958 | 34219.132 | 0 | 165405.364 | 0 | 51028.985 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1517620000000 | 1465028.667 | 28-SEP-15:20 | 645239.307 | 326066.958 | 50722.563 | 0 | 259792.98 | 0 | 56189.31 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1518080000000 | 1360005.167 | 13-OCT-15:20 | 645239.307 | 326066.958 | 38022.038 | 0 | 172370.054 | 0 | 51289.26 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1413210000000 | 1305539.052 | 16-NOV-16:10 | 645239.307 | 326066.958 | 32216.647 | 0 | 125516.259 | 0 | 49482.332 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1316630000000 | 1212282.053 | 20-DEC-08:09 | 645239.307 | 326066.958 | 32216.647 | 0 | 0 | 0 | 45074.999 | 41462.164 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17426500000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1272200000000 | 1212282.053 |  | 645239.307 | 326066.958 | 32216.647 | 0 | 0 | 0 | 45074.999 | 41462.164 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1632520000000 | 1465028.667 |  | 645239.307 | 326066.958 | 50722.563 | 0 | 259792.98 | 0 | 56189.31 | 41462.164 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 728963.88 | 40482.55 | 0 | 769446.43
Cost per Total Building Area ($/m2) | 15.74 | 0.87 | 0 | 16.61
Cost per Net Conditioned Building Area ($/m2) | 15.74 | 0.87 | 0 | 16.61

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 28019.31 | 604.9 | 604.9
Net Site Energy | 28019.31 | 604.9 | 604.9
Total Source Energy | 80315.88 | 1733.92 | 1733.92
Net Source Energy | 80315.88 | 1733.92 | 1733.92
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7732.16 | 0 | 0 | 0 | 0
Cooling | 2410.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 656.54 | 0 | 0 | 0 | 0 | 0
Pumps | 1158.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 678.39 | 0 | 0 | 0 | 0 | 13031.18
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 271.53 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20015.62 | 8003.69 | 0 | 0 | 0 | 14535.32
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 1390.85 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 3245.31 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4079410.36 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3407188.25 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3891129.88
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 389413.36 | 270551.62 | 118861.74 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 4389337.27 | 3064871.17 | 1324466.09 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 420627.79 | 292964.03 | 127663.77 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 126652.39 | 87766.55 | 38885.83 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 68026.29 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 128121.58 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1493700.32 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 138954.99 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17578.43 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20936.1 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16476.51 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 23864.52 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 191653.75 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 225807.34 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 180951.4 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 256057.6 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19431.64 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21353.15 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17979.03 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26141.84 | -
VAV_1_HEATC | Coil:Heating:Water | 45090.25 | -
VAV_2_HEATC | Coil:Heating:Water | 421345.94 | -
VAV_3_HEATC | Coil:Heating:Water | 43309.62 | -
VAV_5_HEATC | Coil:Heating:Water | 25374.62 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.96 | 28545.97 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 192.39 | 317038 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.34 | 30874.51 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.57 | 10455.68 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37382.15 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19297.47 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 54917.87 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 362565.204 | 609.5399 | 1549.9889 | 0 | 0.0065 | 96368.1566 | 151127.041
February | 310515.4529 | 537.6219 | 1413.5395 | 0 | 0.0059 | 87891.0749 | 130856.5505
March | 322454.6857 | 593.669 | 1663.2192 | 0 | 0.0068 | 103429.396 | 139122.6023
April | 285397.6237 | 542.9322 | 1568.6435 | 0 | 0.0064 | 97554.0821 | 124733.4931
May | 300349.5092 | 589.5259 | 1751.0387 | 0 | 0.0071 | 108903.093 | 132927.7898
June | 314116.6999 | 625.5555 | 1881.0362 | 0 | 0.0076 | 116990.8168 | 139844.4395
July | 316462.3001 | 631.4021 | 1901.5726 | 0 | 0.0077 | 118268.4243 | 140996.1757
August | 340933.8859 | 679.7946 | 2046.228 | 0 | 0.0082 | 127265.1473 | 151859.6246
September | 289925.6918 | 573.5044 | 1714.7747 | 0 | 0.0069 | 106649.0565 | 128720.2817
October | 295319.1045 | 571.3861 | 1676.0696 | 0 | 0.0068 | 104238.001 | 129945.62
November | 304150.8386 | 564.3386 | 1592.9298 | 0 | 0.0065 | 99059.8606 | 131624.8906
December | 339426.5309 | 586.5534 | 1538.9398 | 0 | 0.0064 | 95687.7775 | 142937.3421
Annual Sum or Average | 3781620 | 7105.8234 | 20297.9804 | 0 | 0.0826 | 1262300 | 1644700
Minimum of Months | 285397.6237 | 537.6219 | 1413.5395 | 0 | 0.0059 | 87891.0749 | 124733.4931
Maximum of Months | 362565.204 | 679.7946 | 2046.228 | 0 | 0.0082 | 127265.1473 | 151859.6246
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1528050000000 | 1320354.099 | 09-JAN-08:00 | 645239.307 | 326066.958 | 33309.83 | 0 | 82507.538 | 0 | 59937.408 | 51071.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1393640000000 | 1298988.727 | 15-FEB-16:10 | 645239.307 | 326066.958 | 33309.83 | 0 | 99644.509 | 0 | 58101.658 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1640020000000 | 1409949.862 | 09-MAR-16:10 | 645239.307 | 326066.958 | 33719.151 | 0 | 206730.217 | 0 | 61567.764 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1546860000000 | 1401905.127 | 04-APR-07:00 | 645239.307 | 326066.958 | 33309.83 | 0 | 163452.241 | 0 | 60543.733 | 51071.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
May | 1726810000000 | 1552171.146 | 31-MAY-15:00 | 645239.307 | 326066.958 | 35410.581 | 0 | 344085.255 | 0 | 64742.58 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1855050000000 | 1690346.49 | 30-JUN-15:00 | 645239.307 | 326066.958 | 47183.55 | 0 | 467456.535 | 0 | 67773.675 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1875310000000 | 1738299.587 | 25-JUL-15:50 | 645239.307 | 326066.958 | 50777.249 | 0 | 510672.494 | 0 | 68917.115 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2017970000000 | 1795212.598 | 09-AUG-15:09 | 645239.307 | 326066.958 | 48202.346 | 0 | 569468.736 | 0 | 69608.786 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1691070000000 | 1512226.598 | 27-SEP-15:09 | 645239.307 | 326066.958 | 33613.782 | 0 | 306912.861 | 0 | 63767.225 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1652840000000 | 1481524.726 | 03-OCT-07:00 | 645239.307 | 326066.958 | 33309.83 | 0 | 241074.193 | 0 | 62541.379 | 51071.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1570730000000 | 1429835.252 | 03-NOV-15:09 | 645239.307 | 326066.958 | 36831.918 | 0 | 222847.377 | 0 | 62223.226 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1517260000000 | 1275569.95 | 08-DEC-08:00 | 645239.307 | 326066.958 | 33309.83 | 0 | 40579.852 | 0 | 57080.945 | 51071.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 20015600000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1393640000000 | 1275569.95 |  | 645239.307 | 326066.958 | 33309.83 | 0 | 40579.852 | 0 | 57080.945 | 51071.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2017970000000 | 1795212.598 |  | 645239.307 | 326066.958 | 50777.249 | 0 | 569468.736 | 0 | 69608.786 | 51071.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 391205.65 | 77551.76 | 0 | 468757.41
Cost per Total Building Area ($/m2) | 8.45 | 1.67 | 0 | 10.12
Cost per Net Conditioned Building Area ($/m2) | 8.45 | 1.67 | 0 | 10.12

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 23910.16 | 516.19 | 516.19
Net Site Energy | 23910.16 | 516.19 | 516.19
Total Source Energy | 66604.63 | 1437.91 | 1437.91
Net Source Energy | 66604.63 | 1437.91 | 1437.91
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5451.89 | 0 | 0 | 0 | 0
Cooling | 1317.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 778.57 | 0 | 0 | 0 | 0 | 0
Pumps | 567.07 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 416.8 | 0 | 0 | 0 | 0 | 12465.64
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 266.56 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18191.71 | 5718.45 | 0 | 0 | 0 | 13969.78
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.584 | 0.639 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.584 | 0.639 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.584 | 0.639 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.584 | 0.639 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 1390.85 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 3245.31 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3251832.49 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3005663.15 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3101747.92
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 292848.02 | 189518 | 103330.01 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water | 3362297.63 | 2181480.93 | 1180816.7 | 0.65 | -
VAV_3_COOLC | Coil:Cooling:Water | 292850.01 | 189562.56 | 103287.45 | 0.65 | -
VAV_5_COOLC | Coil:Cooling:Water | 80524.05 | 51876.7 | 28647.35 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 55492.45 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 115551.33 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1400836.28 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 116583.76 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16276.54 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19769.12 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14756.43 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24394.96 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 171418.86 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 206704.89 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 154551.08 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 255613.72 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15946.98 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18137.34 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15014.61 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25318.32 | -
VAV_1_HEATC | Coil:Heating:Water | 31723.16 | -
VAV_2_HEATC | Coil:Heating:Water | 285457.02 | -
VAV_3_HEATC | Coil:Heating:Water | 31690.57 | -
VAV_5_HEATC | Coil:Heating:Water | 19562.43 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.89 | 31790.31 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 216.73 | 357160.76 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.91 | 31832.41 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.49 | 10306.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29798.54 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17023.33 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 43776.84 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 433955.7493 | 700.6528 | 1662.1269 | 0 | 0.0066 | 1727970 | 180281.4587
February | 374294.1277 | 617.3601 | 1504.166 | 0 | 0.006 | 1563850 | 156774.4131
March | 423429.7994 | 713.0096 | 1780.6769 | 0 | 0.007 | 1851440 | 178787.676
April | 385261.7428 | 664.2619 | 1704.1856 | 0 | 0.0067 | 1772020 | 164194.3751
May | 436387.4207 | 762.47 | 1984.7764 | 0 | 0.0077 | 2063840 | 186970.1678
June | 454835.1049 | 796.6977 | 2079.4799 | 0 | 0.0081 | 2162330 | 195069.7981
July | 461251.0313 | 808.3988 | 2111.318 | 0 | 0.0082 | 2195440 | 197866.858
August | 487038.065 | 853.3953 | 2228.2813 | 0 | 0.0087 | 2317060 | 208909.4896
September | 424333.8833 | 742.4033 | 1935.3328 | 0 | 0.0075 | 2012430 | 181903.2993
October | 404379.7401 | 698.3059 | 1794.6042 | 0 | 0.007 | 1866040 | 172448.2962
November | 399379.2715 | 668.1943 | 1656.1706 | 0 | 0.0065 | 1721960 | 168209.2175
December | 423272.6111 | 684.4657 | 1626.9542 | 0 | 0.0065 | 1691410 | 175947.4092
Annual Sum or Average | 5107820 | 8709.6155 | 22068.0727 | 0 | 0.0865 | 22945800 | 2167360
Minimum of Months | 374294.1277 | 617.3601 | 1504.166 | 0 | 0.006 | 1563850 | 156774.4131
Maximum of Months | 487038.065 | 853.3953 | 2228.2813 | 0 | 0.0087 | 2317060 | 208909.4896
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1369960000000 | 1243553.584 | 26-JAN-16:10 | 645239.307 | 326066.958 | 42933.441 | 0 | 56741.828 | 0 | 46306.223 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1239840000000 | 1311683.133 | 14-FEB-16:10 | 645239.307 | 326066.958 | 44673.535 | 0 | 121036.102 | 0 | 48401.405 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1467840000000 | 1311945.306 | 02-MAR-16:10 | 645239.307 | 326066.958 | 44477.035 | 0 | 121521.86 | 0 | 48374.319 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1404880000000 | 1359762.649 | 21-APR-15:00 | 645239.307 | 326066.958 | 48634.73 | 0 | 163384.101 | 0 | 50171.727 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1636240000000 | 1437661.304 | 31-MAY-15:00 | 645239.307 | 326066.958 | 62876.054 | 0 | 224075.829 | 0 | 53137.329 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1714320000000 | 1545319.926 | 29-JUN-15:30 | 645239.307 | 326066.958 | 96536.903 | 0 | 280421.663 | 0 | 70789.269 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1740570000000 | 1553100.286 | 03-JUL-15:30 | 645239.307 | 326066.958 | 100441.068 | 0 | 293045.226 | 0 | 62041.902 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1836990000000 | 1573300.308 | 01-AUG-15:30 | 645239.307 | 326066.958 | 96666.808 | 0 | 319410.098 | 0 | 59651.31 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1595480000000 | 1462354.273 | 05-SEP-15:09 | 645239.307 | 326066.958 | 50090.789 | 0 | 259741.588 | 0 | 54949.805 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1479420000000 | 1380632.406 | 11-OCT-15:50 | 645239.307 | 326066.958 | 48340.892 | 0 | 177646.311 | 0 | 57073.112 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1365190000000 | 1295476.464 | 08-NOV-16:10 | 645239.307 | 326066.958 | 41600.463 | 0 | 108733.494 | 0 | 47570.416 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1340970000000 | 1209826.233 | 05-DEC-16:10 | 645239.307 | 326066.958 | 39817.858 | 0 | 27097.348 | 0 | 45338.936 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18191700000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1239840000000 | 1209826.233 |  | 645239.307 | 326066.958 | 39817.858 | 0 | 27097.348 | 0 | 45338.936 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1836990000000 | 1573300.308 |  | 645239.307 | 326066.958 | 100441.068 | 0 | 319410.098 | 0 | 70789.269 | 40710.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 186797.84 | 39297.02 | 0 | 226094.86
Cost per Total Building Area ($/m2) | 4.03 | 0.85 | 0 | 4.88
Cost per Net Conditioned Building Area ($/m2) | 4.03 | 0.85 | 0 | 4.88

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25860.58 | 558.3 | 558.3
Net Site Energy | 25860.58 | 558.3 | 558.3
Total Source Energy | 39425.74 | 851.15 | 851.15
Net Source Energy | 39425.74 | 851.15 | 851.15
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8366.06 | 0 | 0 | 0 | 0
Cooling | 646.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 647.32 | 0 | 0 | 0 | 0 | 0
Pumps | 469.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 334.95 | 0 | 0 | 0 | 0 | 4659.95
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 285.33 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17209.2 | 8651.38 | 0 | 0 | 0 | 6164.08
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.529 | 0.575 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 1390.85 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 3245.31 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3534393.57 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3263683.12 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3371267.72
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 370612.26 | 262305.73 | 108306.53 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 4286720.19 | 3039919.55 | 1246800.64 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 382848.99 | 271063.73 | 111785.26 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 90187.73 | 63884.96 | 26302.77 | 0.71 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 52274.31 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 115986.39 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1436999.53 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 121507.7 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30998.79 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21741.56 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14923.09 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25591.73 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 333929.19 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 227125.92 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 159045.12 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 270304.81 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31959.83 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20392.85 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15526.81 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26849.45 | -
VAV_1_HEATC | Coil:Heating:Water | 30626.13 | -
VAV_2_HEATC | Coil:Heating:Water | 267616.06 | -
VAV_3_HEATC | Coil:Heating:Water | 29829.99 | -
VAV_5_HEATC | Coil:Heating:Water | 20093.21 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.3 | 29115.69 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 200.65 | 330659.19 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.87 | 30089.04 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.32 | 8242.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32387.83 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18484.69 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 47580.74 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 146452.813 | 178.1351 | 289.1887 | 0 | 0.0013 | 3817060 | 55528.1627
February | 111749.8762 | 142.535 | 262.8683 | 0 | 0.0011 | 3471110 | 43078.3615
March | 122241.6233 | 158.9457 | 306.886 | 0 | 0.0013 | 4052910 | 47447.1981
April | 100051.7485 | 135.4451 | 285.3502 | 0 | 0.0012 | 3769420 | 39407.5632
May | 90252.9203 | 132.4052 | 322.6904 | 0 | 0.0013 | 4264240 | 36643.2184
June | 86243.3835 | 130.5122 | 333.8246 | 0 | 0.0013 | 4411860 | 35442.5631
July | 82585.9816 | 128.0353 | 339.1921 | 0 | 0.0013 | 4483140 | 34267.0241
August | 89051.8625 | 138.1185 | 366.1243 | 0 | 0.0014 | 4839110 | 36956.1892
September | 86778.3574 | 128.8522 | 320.1275 | 0 | 0.0013 | 4230560 | 35397.922
October | 98856.408 | 137.1213 | 302.9748 | 0 | 0.0012 | 4002740 | 39289.5788
November | 120672.4035 | 154.1175 | 285.1466 | 0 | 0.0012 | 3765330 | 46539.5359
December | 142873.8226 | 173.8818 | 282.7597 | 0 | 0.0013 | 3732230 | 54181.8781
Annual Sum or Average | 1277810 | 1738.1048 | 3697.1334 | 0 | 0.0153 | 48839700 | 504179.1951
Minimum of Months | 82585.9816 | 128.0353 | 262.8683 | 0 | 0.0011 | 3471110 | 34267.0241
Maximum of Months | 146452.813 | 178.1351 | 366.1243 | 0 | 0.0014 | 4839110 | 55528.1627
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1344980000000 | 1176452.636 | 17-JAN-08:50 | 645239.307 | 326066.958 | 34273.351 | 0 | 0 | 0 | 48651.042 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1223080000000 | 1251673.031 | 21-FEB-16:10 | 645239.307 | 326066.958 | 34273.351 | 0 | 66174.618 | 0 | 50115.524 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1428090000000 | 1312251.032 | 29-MAR-15:30 | 645239.307 | 326066.958 | 35068.86 | 0 | 124890.449 | 0 | 51182.184 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1328200000000 | 1280434.408 | 14-APR-15:09 | 645239.307 | 326066.958 | 34273.351 | 0 | 94455.185 | 0 | 50596.334 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1502550000000 | 1378738.233 | 05-MAY-15:00 | 645239.307 | 326066.958 | 34975.16 | 0 | 188492.35 | 0 | 54161.184 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1554570000000 | 1388921.296 | 28-JUN-15:09 | 645239.307 | 326066.958 | 38618.372 | 0 | 194306.692 | 0 | 54886.693 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1579680000000 | 1448436.794 | 31-JUL-15:00 | 645239.307 | 326066.958 | 41726.647 | 0 | 249521.005 | 0 | 56079.603 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1705110000000 | 1422791.902 | 18-AUG-15:30 | 645239.307 | 326066.958 | 39802.076 | 0 | 226444.558 | 0 | 55435.729 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1490680000000 | 1434527.109 | 01-SEP-15:50 | 645239.307 | 326066.958 | 40223.406 | 0 | 237549.907 | 0 | 55644.257 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1410410000000 | 1335787.716 | 17-OCT-15:09 | 645239.307 | 326066.958 | 36999.504 | 0 | 145977.723 | 0 | 51700.95 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1326750000000 | 1258467.106 | 03-NOV-15:09 | 645239.307 | 326066.958 | 34273.351 | 0 | 72290.426 | 0 | 50793.79 | 44247.889 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1315090000000 | 1176429.108 | 13-DEC-08:30 | 645239.307 | 326066.958 | 34273.351 | 0 | 0.568 | 0 | 48626.946 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17209200000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1223080000000 | 1176429.108 |  | 645239.307 | 326066.958 | 34273.351 | 0 | 0 | 0 | 48626.946 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1705110000000 | 1448436.794 |  | 645239.307 | 326066.958 | 41726.647 | 0 | 249521.005 | 0 | 56079.603 | 44247.889 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 346990.47 | 72756.24 | 0 | 419746.71
Cost per Total Building Area ($/m2) | 7.49 | 1.57 | 0 | 9.06
Cost per Net Conditioned Building Area ($/m2) | 7.49 | 1.57 | 0 | 9.06

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 29294.9 | 632.44 | 632.44
Net Site Energy | 29294.9 | 632.44 | 632.44
Total Source Energy | 77018.19 | 1662.73 | 1662.73
Net Source Energy | 77018.19 | 1662.73 | 1662.73
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10651.29 | 0 | 0 | 0 | 0
Cooling | 1491.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 704.23 | 0 | 0 | 0 | 0 | 0
Pumps | 640.4 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 401.09 | 0 | 0 | 0 | 0 | 8216.89
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 294.72 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18348.88 | 10946.01 | 0 | 0 | 0 | 9721.02
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4097266.6 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3691900.17 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3908161.99
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 365036.34 | 253285.56 | 111750.78 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 4332918.06 | 3025287.33 | 1307630.74 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 412748.05 | 287380.88 | 125367.17 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 116613.04 | 80686.15 | 35926.88 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 64837.43 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 117179.23 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1493366.68 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 138796.21 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18973.21 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21777.26 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16616.07 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24913.78 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 208320.87 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 235901.29 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 182601.92 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 268301.84 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20314.65 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22336.61 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17805.08 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27077.83 | -
VAV_1_HEATC | Coil:Heating:Water | 63683.7 | -
VAV_2_HEATC | Coil:Heating:Water | 602349.04 | -
VAV_3_HEATC | Coil:Heating:Water | 61429.29 | -
VAV_5_HEATC | Coil:Heating:Water | 32740.12 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.62 | 27979.26 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 199.03 | 327993.07 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.86 | 31748.58 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.4 | 10135.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37545.78 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20910.01 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 55158.25 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 601760.4133 | 973.8136 | 2565.8054 | 0 | 0.008 | 590519.3082 | 249152.689
February | 521015.2776 | 859.7065 | 2320.7984 | 0 | 0.0072 | 534158.6383 | 217304.3754
March | 569219.4408 | 966.1919 | 2697.0498 | 0 | 0.0083 | 620800.2278 | 239985.5946
April | 498951.4377 | 876.0712 | 2538.8681 | 0 | 0.0077 | 584434.0844 | 213147.5251
May | 560838.6061 | 1009.0294 | 2999.4184 | 0 | 0.0091 | 690484.2577 | 241908.0406
June | 617242.133 | 1121.1626 | 3364.9444 | 0 | 0.0101 | 774644.7101 | 267255.4697
July | 623200.8907 | 1133.1454 | 3404.3786 | 0 | 0.0103 | 783724.3882 | 269946.3516
August | 662753.9534 | 1204.2906 | 3615.8137 | 0 | 0.0109 | 832398.0029 | 287005.3112
September | 564148.0681 | 1020.3491 | 3049.2821 | 0 | 0.0092 | 701970.3138 | 243848.5133
October | 529981.2247 | 942.0565 | 2765.7142 | 0 | 0.0084 | 636668.9283 | 227502.9223
November | 519741.8381 | 890.8522 | 2514.4329 | 0 | 0.0077 | 578778.8922 | 219952.0185
December | 571247.6279 | 937.753 | 2515.5387 | 0 | 0.0078 | 578972.6403 | 237792.4779
Annual Sum or Average | 6840100 | 11934.4221 | 34352.0447 | 0 | 0.1047 | 7907550 | 2914800
Minimum of Months | 498951.4377 | 859.7065 | 2320.7984 | 0 | 0.0072 | 534158.6383 | 213147.5251
Maximum of Months | 662753.9534 | 1204.2906 | 3615.8137 | 0 | 0.0109 | 832398.0029 | 287005.3112
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1370260000000 | 1183973.697 | 03-JAN-08:00 | 645239.307 | 326066.958 | 34251.89 | 0 | 0 | 0 | 56193.564 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1239470000000 | 1184572.543 | 09-FEB-08:50 | 645239.307 | 326066.958 | 34251.89 | 0 | 0 | 0 | 56792.41 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1440520000000 | 1345220.682 | 31-MAR-15:50 | 645239.307 | 326066.958 | 34251.89 | 0 | 143814.378 | 0 | 58998.137 | 51294.626 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1356140000000 | 1367408.672 | 10-APR-08:00 | 645239.307 | 326066.958 | 34251.89 | 0 | 163539.567 | 0 | 61460.938 | 51294.626 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1602220000000 | 1566950.446 | 30-MAY-08:00 | 645239.307 | 326066.958 | 34251.89 | 0 | 358347.45 | 0 | 66194.83 | 51294.626 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1797500000000 | 1624831.966 | 08-JUN-12:00 | 645239.307 | 326066.958 | 42300.79 | 0 | 455717.366 | 0 | 67546.324 | 51294.626 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
July | 1818570000000 | 1650819.223 | 13-JUL-15:09 | 645239.307 | 326066.958 | 48000.595 | 0 | 427135.988 | 0 | 67526.364 | 51294.626 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1931520000000 | 1742929.359 | 04-AUG-15:00 | 645239.307 | 326066.958 | 47834.142 | 0 | 517593.814 | 0 | 69345.127 | 51294.626 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1628870000000 | 1545369.801 | 07-SEP-12:00 | 645239.307 | 326066.958 | 36816.265 | 0 | 382173.608 | 0 | 67112.443 | 51294.626 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
October | 1477340000000 | 1452279.062 | 31-OCT-07:00 | 645239.307 | 326066.958 | 34251.89 | 0 | 210665.903 | 0 | 62538.4 | 51294.626 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1343010000000 | 1464143.14 | 02-NOV-07:00 | 645239.307 | 326066.958 | 34251.89 | 0 | 221998.924 | 0 | 63069.456 | 51294.626 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1343460000000 | 1185425.734 | 26-DEC-08:30 | 645239.307 | 326066.958 | 34251.89 | 0 | 0 | 0 | 57645.601 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18348900000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1239470000000 | 1183973.697 |  | 645239.307 | 326066.958 | 34251.89 | 0 | 0 | 0 | 56193.564 | 0 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1931520000000 | 1742929.359 |  | 645239.307 | 326066.958 | 48000.595 | 0 | 517593.814 | 0 | 69345.127 | 51294.626 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 445216.82 | 91345.82 | 0 | 536562.64
Cost per Total Building Area ($/m2) | 9.61 | 1.97 | 0 | 11.58
Cost per Net Conditioned Building Area ($/m2) | 9.61 | 1.97 | 0 | 11.58

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25220.86 | 544.49 | 544.49
Net Site Energy | 25220.86 | 544.49 | 544.49
Total Source Energy | 66658.22 | 1439.07 | 1439.07
Net Source Energy | 66658.22 | 1439.07 | 1439.07
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7354.55 | 0 | 0 | 0 | 0
Cooling | 928.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 746.05 | 0 | 0 | 0 | 0 | 0
Pumps | 469.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 316.99 | 0 | 0 | 0 | 0 | 8865.32
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 293.51 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17572.8 | 7648.06 | 0 | 0 | 0 | 10369.45
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.484 | 0.522 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3142241.05 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3183562.51 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2997214.54
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 284368.9 | 181816.51 | 102552.39 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water | 3289209.88 | 2108366.35 | 1180843.53 | 0.64 | -
VAV_3_COOLC | Coil:Cooling:Water | 278403.55 | 177919.16 | 100484.38 | 0.64 | -
VAV_5_COOLC | Coil:Cooling:Water | 78512.83 | 50165.17 | 28347.67 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 54949.5 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 115040.64 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1386048.24 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 112172.4 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15298.04 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18632.74 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13898.6 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 22922.66 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 166838.08 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 197422.56 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 147190.66 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 246909.83 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15510.51 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16946.43 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15472.85 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24030.9 | -
VAV_1_HEATC | Coil:Heating:Water | 48648.56 | -
VAV_2_HEATC | Coil:Heating:Water | 457737.64 | -
VAV_3_HEATC | Coil:Heating:Water | 49010.34 | -
VAV_5_HEATC | Coil:Heating:Water | 26198.68 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.43 | 31021.38 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 212.7 | 350509.33 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.04 | 30373.51 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.45 | 10224.67 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28794.29 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18030.91 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 42301.5 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 449098.8212 | 713.8987 | 1659.4876 | 0 | 0.0066 | 1725140 | 185473.4966
February | 388158.7949 | 628.4364 | 1496.0587 | 0 | 0.006 | 1555340 | 161424.9973
March | 430848.7875 | 715.3831 | 1757.106 | 0 | 0.0069 | 1826860 | 180927.6569
April | 382876.2363 | 653.3631 | 1656.9054 | 0 | 0.0065 | 1722810 | 162512.0862
May | 411397.7516 | 712.0812 | 1834.7136 | 0 | 0.0072 | 1907760 | 175603.5902
June | 426853.4934 | 744.7709 | 1935.779 | 0 | 0.0075 | 2012890 | 182783.2319
July | 445428.9249 | 780.0712 | 2035.6607 | 0 | 0.0079 | 2116760 | 191020.91
August | 464327.8958 | 812.7484 | 2119.7572 | 0 | 0.0083 | 2204210 | 199084.4677
September | 401589.7864 | 699.3352 | 1813.8701 | 0 | 0.0071 | 1886110 | 171832.0554
October | 404250.9907 | 692.8097 | 1765.4878 | 0 | 0.0069 | 1835730 | 171876.0769
November | 402662.7297 | 665.6201 | 1626.1202 | 0 | 0.0064 | 1690660 | 168800.7787
December | 437217.1948 | 695.2558 | 1616.906 | 0 | 0.0065 | 1680880 | 180590.4709
Annual Sum or Average | 5044710 | 8513.7737 | 21317.8524 | 0 | 0.0838 | 22165100 | 2131930
Minimum of Months | 382876.2363 | 628.4364 | 1496.0587 | 0 | 0.006 | 1555340 | 161424.9973
Maximum of Months | 464327.8958 | 812.7484 | 2119.7572 | 0 | 0.0083 | 2204210 | 199084.4677
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1367710000000 | 1236567.581 | 27-JAN-16:10 | 645239.307 | 326066.958 | 36549.615 | 0 | 59090.256 | 0 | 44727.619 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1233090000000 | 1173136.047 | 13-FEB-08:50 | 645239.307 | 326066.958 | 36375.09 | 0 | 0 | 0 | 43232.714 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1448360000000 | 1301226.016 | 30-MAR-15:09 | 645239.307 | 326066.958 | 39224.48 | 0 | 119116.998 | 0 | 46684.446 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1365860000000 | 1334613.233 | 26-APR-15:00 | 645239.307 | 326066.958 | 43747.756 | 0 | 146977.218 | 0 | 47688.168 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1512490000000 | 1389996.547 | 24-MAY-15:00 | 645239.307 | 326066.958 | 50811.605 | 0 | 190320.7 | 0 | 52664.151 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1595840000000 | 1442137.807 | 27-JUN-15:30 | 645239.307 | 326066.958 | 59087.761 | 0 | 225426.561 | 0 | 61423.394 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1678200000000 | 1503858.516 | 18-JUL-15:09 | 645239.307 | 326066.958 | 88022.128 | 0 | 260949.225 | 0 | 58687.072 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1747520000000 | 1496068.758 | 30-AUG-15:30 | 645239.307 | 326066.958 | 88698.184 | 0 | 251301.428 | 0 | 59869.055 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1495330000000 | 1415901.573 | 01-SEP-15:00 | 645239.307 | 326066.958 | 57621.317 | 0 | 211363.465 | 0 | 50716.701 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1455390000000 | 1366438.67 | 05-OCT-15:30 | 645239.307 | 326066.958 | 49551.994 | 0 | 171742.195 | 0 | 48944.391 | 39338.441 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1340370000000 | 1258596.856 | 10-NOV-13:00 | 645239.307 | 326066.958 | 44136.164 | 0 | 120155.666 | 0 | 46993.727 | 39338.441 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
December | 1332620000000 | 1172922.467 | 20-DEC-08:09 | 645239.307 | 326066.958 | 36375.09 | 0 | 0.328 | 0 | 43018.807 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17572800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1233090000000 | 1172922.467 |  | 645239.307 | 326066.958 | 36375.09 | 0 | 0 | 0 | 43018.807 | 0 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1747520000000 | 1503858.516 |  | 645239.307 | 326066.958 | 88698.184 | 0 | 260949.225 | 0 | 61423.394 | 39338.441 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 180449.24 | 52792.28 | 0 | 233241.52
Cost per Total Building Area ($/m2) | 3.9 | 1.14 | 0 | 5.04
Cost per Net Conditioned Building Area ($/m2) | 3.9 | 1.14 | 0 | 5.04

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 31567.47 | 681.5 | 681.5
Net Site Energy | 31567.47 | 681.5 | 681.5
Total Source Energy | 76972.37 | 1661.74 | 1661.74
Net Source Energy | 76972.37 | 1661.74 | 1661.74
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13128.8 | 0 | 0 | 0 | 0
Cooling | 1305.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 722.92 | 0 | 0 | 0 | 0 | 0
Pumps | 609.16 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 374.79 | 0 | 0 | 0 | 0 | 7216.54
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 314.72 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18123.96 | 13443.51 | 0 | 0 | 0 | 8720.67
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.414 | 0.441 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.414 | 0.441 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.414 | 0.441 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.414 | 0.441 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4063581.72 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3838865.81 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3876031.8
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 363226.85 | 248498.99 | 114727.85 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 4332642.95 | 2978168.89 | 1354474.06 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 409936.38 | 281342.1 | 128594.28 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 115032.75 | 78295.15 | 36737.6 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 64122.55 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 117587.16 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1488469.41 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 138985.56 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20333.54 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21685.74 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15576.51 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24360.13 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 223814.62 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 233755.45 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 182255.7 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 263315.43 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21697.22 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22196.21 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 19077.73 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26254.96 | -
VAV_1_HEATC | Coil:Heating:Water | 72568.54 | -
VAV_2_HEATC | Coil:Heating:Water | 702451.68 | -
VAV_3_HEATC | Coil:Heating:Water | 71260.99 | -
VAV_5_HEATC | Coil:Heating:Water | 36448.2 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.76 | 28207.91 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 200.84 | 330966.48 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.97 | 31926.27 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.38 | 10101.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37237.1 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21742.38 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 54704.78 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 484980.0049 | 716.0711 | 900.4549 | 0 | 0.0069 | 591286.8597 | 194220.1937
February | 397431.5585 | 610.2728 | 814.3165 | 0 | 0.0062 | 534863.1666 | 161402.7276
March | 391216.0477 | 643.3714 | 940.4329 | 0 | 0.007 | 617929.0954 | 162954.5969
April | 327749.5619 | 569.0846 | 885.8342 | 0 | 0.0065 | 582192.0111 | 139394.5465
May | 365761.5992 | 656.7518 | 1059.1183 | 0 | 0.0077 | 696167.0322 | 157632.2985
June | 390317.7787 | 709.0707 | 1157.0113 | 0 | 0.0084 | 760544.2201 | 169001.6211
July | 394636.2808 | 718.4817 | 1174.911 | 0 | 0.0086 | 772316.1772 | 171021.1359
August | 423668.3187 | 770.5331 | 1258.7247 | 0 | 0.0092 | 827407.261 | 183525.6467
September | 347498.0522 | 625.6873 | 1011.8636 | 0 | 0.0074 | 665112.6955 | 149926.5327
October | 339972.9109 | 590.189 | 918.4822 | 0 | 0.0068 | 603648.6178 | 144581.818
November | 373143.3685 | 609.448 | 883.3059 | 0 | 0.0066 | 580373.4302 | 155025.0578
December | 436803.5449 | 666.5007 | 881.2157 | 0 | 0.0067 | 578781.4822 | 176987.9807
Annual Sum or Average | 4673180 | 7885.4621 | 11885.671 | 0 | 0.0881 | 7810620 | 1965670
Minimum of Months | 327749.5619 | 569.0846 | 814.3165 | 0 | 0.0062 | 534863.1666 | 139394.5465
Maximum of Months | 484980.0049 | 770.5331 | 1258.7247 | 0 | 0.0092 | 827407.261 | 194220.1937
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1372040000000 | 1183833.097 | 31-JAN-08:09 | 645239.307 | 326066.958 | 34570.165 | 0 | 0 | 0 | 55734.688 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1241110000000 | 1184085.625 | 13-FEB-08:00 | 645239.307 | 326066.958 | 34570.165 | 0 | 0 | 0 | 55987.217 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1433860000000 | 1221971.548 | 23-MAR-15:00 | 645239.307 | 326066.958 | 34980.24 | 0 | 72500.345 | 0 | 57629.313 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1350930000000 | 1350516.213 | 14-APR-15:00 | 645239.307 | 326066.958 | 35029.992 | 0 | 149047.837 | 0 | 58703.816 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1615400000000 | 1485508.745 | 31-MAY-15:09 | 645239.307 | 326066.958 | 37433.26 | 0 | 276413.311 | 0 | 63927.607 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1764790000000 | 1636453.193 | 29-JUN-15:00 | 645239.307 | 326066.958 | 47745.774 | 0 | 413970.604 | 0 | 67002.247 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1792100000000 | 1673423.209 | 13-JUL-15:00 | 645239.307 | 326066.958 | 44013.12 | 0 | 454259.114 | 0 | 67416.408 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1919940000000 | 1643576.835 | 25-AUG-15:00 | 645239.307 | 326066.958 | 43477.009 | 0 | 425504.071 | 0 | 66861.188 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1543340000000 | 1544118.117 | 22-SEP-15:00 | 645239.307 | 326066.958 | 34570.165 | 0 | 336546.608 | 0 | 65266.776 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1400720000000 | 1375517.775 | 06-OCT-15:09 | 645239.307 | 326066.958 | 38333.872 | 0 | 165796.332 | 0 | 63653.003 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1346710000000 | 1325794.752 | 02-NOV-15:09 | 645239.307 | 326066.958 | 38627.941 | 0 | 121108.793 | 0 | 58323.451 | 50872.917 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1343020000000 | 1183597.363 | 08-DEC-08:50 | 645239.307 | 326066.958 | 34570.165 | 0 | 0.48 | 0 | 55498.475 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18124000000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1241110000000 | 1183597.363 |  | 645239.307 | 326066.958 | 34570.165 | 0 | 0 | 0 | 55498.475 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1919940000000 | 1673423.209 |  | 645239.307 | 326066.958 | 47745.774 | 0 | 454259.114 | 0 | 67416.408 | 50872.917 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 312294.73 | 106016.69 | 0 | 418311.43
Cost per Total Building Area ($/m2) | 6.74 | 2.29 | 0 | 9.03
Cost per Net Conditioned Building Area ($/m2) | 6.74 | 2.29 | 0 | 9.03

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 27660.56 | 597.16 | 597.16
Net Site Energy | 27660.56 | 597.16 | 597.16
Total Source Energy | 71095.28 | 1534.86 | 1534.86
Net Source Energy | 71095.28 | 1534.86 | 1534.86
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10190.35 | 0 | 0 | 0 | 0
Cooling | 647.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.33 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 729.71 | 0 | 0 | 0 | 0 | 0
Pumps | 407.21 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 255.74 | 0 | 0 | 0 | 0 | 6161.09
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 318.39 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17151.82 | 10508.74 | 0 | 0 | 0 | 7665.22
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.446 | 0.478 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.446 | 0.478 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.446 | 0.478 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.446 | 0.478 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3137416.6 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3540650.11 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2992612.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 300900.17 | 199869.53 | 101030.64 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water | 3510200.63 | 2335220.99 | 1174979.64 | 0.67 | -
VAV_3_COOLC | Coil:Cooling:Water | 301386.63 | 200153.29 | 101233.34 | 0.66 | -
VAV_5_COOLC | Coil:Cooling:Water | 79519.36 | 53030.91 | 26488.44 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 53960.17 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 115208.09 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1402452.72 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 114976.33 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19289.17 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19284.3 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14328.13 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 22923.07 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 212546.42 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 208215.65 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 153583.88 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 249031.69 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19379.59 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18303.48 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18406.66 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24345.11 | -
VAV_1_HEATC | Coil:Heating:Water | 66311.32 | -
VAV_2_HEATC | Coil:Heating:Water | 642497.04 | -
VAV_3_HEATC | Coil:Heating:Water | 66291.21 | -
VAV_5_HEATC | Coil:Heating:Water | 33199.67 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.94 | 30207.16 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 209.08 | 344550.93 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.96 | 30234.36 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.07 | 9508.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28750.08 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20053.36 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 42236.55 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 451535.2301 | 689.4142 | 1013.0587 | 0 | 0.0073 | 24017400 | 183299.6855
February | 381783.484 | 598.2959 | 912.1872 | 0 | 0.0065 | 21629000 | 156470.8349
March | 396838.2525 | 655.209 | 1068.6614 | 0 | 0.0075 | 25345300 | 165861.8101
April | 339180.2053 | 574.5483 | 965.9645 | 0 | 0.0068 | 22912000 | 143168.3477
May | 361535.5262 | 628.7714 | 1088.778 | 0 | 0.0076 | 25827600 | 154185.4622
June | 377534.4334 | 663.6375 | 1162.4242 | 0 | 0.0081 | 27575700 | 161689.2179
July | 381028.308 | 674.7069 | 1191.0032 | 0 | 0.0083 | 28254300 | 163661.9028
August | 397774.0499 | 703.0466 | 1238.5983 | 0 | 0.0086 | 29383300 | 170727.7418
September | 351281.7982 | 615.2727 | 1073.5733 | 0 | 0.0075 | 25467600 | 150231.4807
October | 357074.5757 | 609.3123 | 1033.0279 | 0 | 0.0072 | 24503400 | 151151.9457
November | 374581.2405 | 612.1941 | 986.0602 | 0 | 0.007 | 23385200 | 155953.5212
December | 426903.6661 | 660.984 | 990.9872 | 0 | 0.0071 | 23495900 | 174187.7206
Annual Sum or Average | 4597050 | 7685.3926 | 12724.324 | 0 | 0.0893 | 301797000 | 1930590
Minimum of Months | 339180.2053 | 574.5483 | 912.1872 | 0 | 0.0065 | 21629000 | 143168.3477
Maximum of Months | 451535.2301 | 703.0466 | 1238.5983 | 0 | 0.0086 | 29383300 | 183299.6855
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1364960000000 | 1172154.252 | 10-JAN-08:20 | 645239.307 | 326066.958 | 35745.549 | 0 | 0.162 | 0 | 42880.298 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1229220000000 | 1194775.851 | 03-FEB-16:19 | 645239.307 | 326066.958 | 37376.763 | 0 | 17860.22 | 0 | 43399.176 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1440430000000 | 1301055.741 | 30-MAR-15:09 | 645239.307 | 326066.958 | 39503.446 | 0 | 119075.967 | 0 | 46336.635 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1302150000000 | 1281849.442 | 06-APR-15:39 | 645239.307 | 326066.958 | 36356.337 | 0 | 103628.555 | 0 | 45724.858 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1467850000000 | 1324312.065 | 16-MAY-15:00 | 645239.307 | 326066.958 | 38283.979 | 0 | 143118.783 | 0 | 46769.61 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1567190000000 | 1473766.419 | 26-JUN-15:30 | 645239.307 | 326066.958 | 77166.01 | 0 | 244738.29 | 0 | 55722.427 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1605760000000 | 1463865.153 | 21-JUL-15:00 | 645239.307 | 326066.958 | 59377.251 | 0 | 249276.08 | 0 | 59072.13 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1669920000000 | 1438209.71 | 09-AUG-15:00 | 645239.307 | 326066.958 | 53832.061 | 0 | 229997.361 | 0 | 58240.595 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1447380000000 | 1378385.209 | 01-SEP-15:00 | 645239.307 | 326066.958 | 44313.1 | 0 | 189749.99 | 0 | 48182.427 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1392590000000 | 1334992.848 | 06-OCT-15:20 | 645239.307 | 326066.958 | 43089.941 | 0 | 148545.285 | 0 | 47217.929 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1329040000000 | 1187014.875 | 21-NOV-16:10 | 645239.307 | 326066.958 | 35745.549 | 0 | 12006.645 | 0 | 43122.988 | 39278.042 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1335330000000 | 1163827.864 | 11-DEC-08:20 | 645239.307 | 326066.958 | 35745.549 | 0 | 0 | 0 | 34554.071 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17151800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1229220000000 | 1163827.864 |  | 645239.307 | 326066.958 | 35745.549 | 0 | 0 | 0 | 34554.071 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1669920000000 | 1473766.419 |  | 645239.307 | 326066.958 | 77166.01 | 0 | 249276.08 | 0 | 59072.13 | 39278.042 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 372123.88 | 84779.71 | 0 | 456903.58
Cost per Total Building Area ($/m2) | 8.03 | 1.83 | 0 | 9.86
Cost per Net Conditioned Building Area ($/m2) | 8.03 | 1.83 | 0 | 9.86

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 33253.43 | 717.9 | 717.9
Net Site Energy | 33253.43 | 717.9 | 717.9
Total Source Energy | 76734.82 | 1656.61 | 1656.61
Net Source Energy | 76734.82 | 1656.61 | 1656.61
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15668.14 | 0 | 0 | 0 | 0
Cooling | 669.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 767.99 | 0 | 0 | 0 | 0 | 0
Pumps | 447.81 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 240.6 | 0 | 0 | 0 | 0 | 4042.69
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 347.74 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17237.56 | 16015.88 | 0 | 0 | 0 | 5546.82
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.385 | 0.409 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.385 | 0.409 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.385 | 0.409 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.385 | 0.409 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 1390.85 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 3245.31 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3795544.34 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3926617.97 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3620365.37
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 358132.8 | 247669.37 | 110463.44 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 4204071.55 | 2918181.71 | 1285889.84 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 373914.99 | 258847.65 | 115067.34 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 85570.27 | 59114.71 | 26455.56 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 51804.56 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 116560.37 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1447150.58 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 123144.59 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24535.18 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23552.78 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15469.81 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27180.47 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 270725.46 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 257099.55 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 167486.76 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 298115.95 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25255.24 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23687.11 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 20097.78 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29011.41 | -
VAV_1_HEATC | Coil:Heating:Water | 75609.52 | -
VAV_2_HEATC | Coil:Heating:Water | 736255.26 | -
VAV_3_HEATC | Coil:Heating:Water | 75193.42 | -
VAV_5_HEATC | Coil:Heating:Water | 36791.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.78 | 29928.51 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 209.32 | 344937.84 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.58 | 31268.82 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.44 | 8474.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34780.91 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22239.39 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 51096.41 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 482843.7067 | 714.4895 | 901.6095 | 0 | 0.007 | 592054.3888 | 193515.001
February | 411635.0808 | 623.1513 | 814.3359 | 0 | 0.0062 | 534827.8857 | 166317.2407
March | 417341.3223 | 667.2402 | 941.0573 | 0 | 0.0071 | 618251.7692 | 172011.3937
April | 334869.5013 | 565.4687 | 853.0493 | 0 | 0.0063 | 560579.768 | 140895.385
May | 343039.3794 | 602.7693 | 950.3967 | 0 | 0.007 | 624653.1947 | 146579.5819
June | 356365.899 | 643.2449 | 1042.8646 | 0 | 0.0076 | 685496.1386 | 153904.5638
July | 377632.2007 | 684.6705 | 1114.9959 | 0 | 0.0081 | 732920.9902 | 163379.4498
August | 382549.2565 | 690.9885 | 1121.0577 | 0 | 0.0082 | 736895.8895 | 165258.5334
September | 324737.3539 | 574.5934 | 912.6609 | 0 | 0.0067 | 599866.9989 | 139139.9383
October | 340849.1378 | 582.9713 | 892.3946 | 0 | 0.0066 | 586467.5307 | 144119.1446
November | 389303.6792 | 622.2628 | 877.3434 | 0 | 0.0066 | 576392.5297 | 160440.9496
December | 451732.8325 | 680.7226 | 883.4678 | 0 | 0.0068 | 580213.8719 | 182219.1241
Annual Sum or Average | 4612900 | 7652.5731 | 11305.2335 | 0 | 0.0841 | 7428620 | 1927780
Minimum of Months | 324737.3539 | 565.4687 | 814.3359 | 0 | 0.0062 | 534827.8857 | 139139.9383
Maximum of Months | 482843.7067 | 714.4895 | 1121.0577 | 0 | 0.0082 | 736895.8895 | 193515.001
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1373820000000 | 1182897.407 | 11-JAN-08:30 | 645239.307 | 326066.958 | 35754.96 | 0 | 0 | 0 | 53614.203 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1241030000000 | 1168569.062 | 01-FEB-08:20 | 645239.307 | 326066.958 | 35754.96 | 0 | 0 | 0 | 39285.859 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1434610000000 | 1181040.048 | 28-MAR-07:49 | 645239.307 | 326066.958 | 35754.96 | 0 | 0.086 | 0 | 51756.759 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1300780000000 | 1220409.577 | 04-APR-15:09 | 645239.307 | 326066.958 | 37691.181 | 0 | 71710.202 | 0 | 54146.545 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1449460000000 | 1365945.843 | 31-MAY-15:00 | 645239.307 | 326066.958 | 39856.386 | 0 | 165801.732 | 0 | 55908.779 | 47517.295 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1590640000000 | 1523341.73 | 14-JUN-15:20 | 645239.307 | 326066.958 | 41569.281 | 0 | 316177.562 | 0 | 61215.941 | 47517.295 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1700690000000 | 1650016.856 | 07-JUL-07:00 | 645239.307 | 326066.958 | 42400.262 | 0 | 401984.226 | 0 | 64586.83 | 47517.295 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
August | 1709910000000 | 1543510.879 | 11-AUG-15:39 | 645239.307 | 326066.958 | 44375.175 | 0 | 332962.978 | 0 | 61793.78 | 47517.295 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1391950000000 | 1520238.502 | 07-SEP-15:30 | 645239.307 | 326066.958 | 41781.336 | 0 | 312153.467 | 0 | 61924.753 | 47517.295 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1360850000000 | 1303646.891 | 27-OCT-15:09 | 645239.307 | 326066.958 | 36848.539 | 0 | 108028.423 | 0 | 54390.983 | 47517.295 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1337480000000 | 1181119.336 | 30-NOV-08:30 | 645239.307 | 326066.958 | 35754.96 | 0 | 0 | 0 | 51836.132 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1346340000000 | 1158577.523 | 11-DEC-08:09 | 645239.307 | 326066.958 | 35754.96 | 0 | 0 | 0 | 29294.319 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17237600000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1241030000000 | 1158577.523 |  | 645239.307 | 326066.958 | 35754.96 | 0 | 0 | 0 | 29294.319 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1709910000000 | 1650016.856 |  | 645239.307 | 326066.958 | 44375.175 | 0 | 401984.226 | 0 | 64586.83 | 47517.295 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 296850.67 | 126086.27 | 0 | 422936.94
Cost per Total Building Area ($/m2) | 6.41 | 2.72 | 0 | 9.13
Cost per Net Conditioned Building Area ($/m2) | 6.41 | 2.72 | 0 | 9.13

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 45519.04 | 982.7 | 982.7
Net Site Energy | 45519.04 | 982.7 | 982.7
Total Source Energy | 92212.71 | 1990.76 | 1990.76
Net Source Energy | 92212.71 | 1990.76 | 1990.76
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 27991.89 | 0 | 0 | 0 | 0
Cooling | 427.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 951.69 | 0 | 0 | 0 | 0 | 0
Pumps | 442.43 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 206.15 | 0 | 0 | 0 | 0 | 3516.34
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 387.67 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17139.49 | 28379.55 | 0 | 0 | 0 | 5020.47
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.32 | 0.336 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.32 | 0.336 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.32 | 0.336 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.32 | 0.336 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 1390.85 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 3245.31 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4085484.97 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 4923411.77 | 0.7
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3896924.12
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 436827.92 | 311810.03 | 125017.89 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 5163446.64 | 3686923.41 | 1476523.23 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 455148.4 | 324772.32 | 130376.09 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 81562.09 | 58646.82 | 22915.27 | 0.72 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 49806.07 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 133894.09 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1644599.67 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 137947.29 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43409.22 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28031.46 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17589.59 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30394.42 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 494106.54 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 309959.8 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 198309.16 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 341996.79 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46998 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28518.02 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 25763.05 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 32850.1 | -
VAV_1_HEATC | Coil:Heating:Water | 100132.81 | -
VAV_2_HEATC | Coil:Heating:Water | 982377.05 | -
VAV_3_HEATC | Coil:Heating:Water | 99779.42 | -
VAV_5_HEATC | Coil:Heating:Water | 45697.32 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.97 | 35297.38 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 247.54 | 407928.34 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.82 | 36729.66 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.12 | 7867.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37437.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27884.98 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 54999.65 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.78 | 0.88 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 582161.0682 | 622.6282 | 1971.7104 | 0 | 0.0073 | 395417.1178 | 215977.0749
February | 478682.9346 | 519.7966 | 1785.2526 | 0 | 0.0065 | 358073.9315 | 178793.9078
March | 452444.623 | 509.2891 | 2063.649 | 0 | 0.0073 | 414017.0279 | 171761.1264
April | 334853.5909 | 392.5783 | 1854.8072 | 0 | 0.0064 | 372192.5758 | 129529.1264
May | 311670.6675 | 381.2114 | 2057.2072 | 0 | 0.007 | 412868.6283 | 122994.7566
June | 325960.5656 | 404.4638 | 2272.3297 | 0 | 0.0077 | 456061.2884 | 129522.5451
July | 324347.6057 | 403.0155 | 2272.6579 | 0 | 0.0077 | 456128.8695 | 128966.7466
August | 333985.2198 | 411.4509 | 2266.1319 | 0 | 0.0077 | 454808.1676 | 132254.1255
September | 304437.7705 | 366.0642 | 1877.654 | 0 | 0.0064 | 376812.7874 | 119170.8842
October | 386506.7682 | 443.9337 | 1948.4021 | 0 | 0.0068 | 390937.7726 | 148093.6776
November | 474734.9221 | 523.3237 | 1934.0098 | 0 | 0.007 | 387955.9178 | 178521.7735
December | 524700.1363 | 568.9131 | 1939.0259 | 0 | 0.0071 | 388911.7857 | 195850.6086
Annual Sum or Average | 4834490 | 5546.6685 | 24242.8376 | 0 | 0.085 | 4864190 | 1851440
Minimum of Months | 304437.7705 | 366.0642 | 1785.2526 | 0 | 0.0064 | 358073.9315 | 119170.8842
Maximum of Months | 582161.0682 | 622.6282 | 2272.6579 | 0 | 0.0077 | 456128.8695 | 215977.0749
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1393290000000 | 1201183.712 | 13-JAN-08:30 | 645239.307 | 326066.958 | 42109.425 | 0 | 0 | 3079 | 62467.044 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1261710000000 | 1162496.935 | 02-FEB-09:39 | 645239.307 | 326066.958 | 42109.425 | 0 | 0 | 3079 | 60446.86 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1458830000000 | 1191279.179 | 10-MAR-08:00 | 645239.307 | 326066.958 | 42109.425 | 0 | 0.048 | 0 | 55641.462 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1311460000000 | 1191446.903 | 17-APR-07:10 | 645239.307 | 326066.958 | 42109.425 | 0 | 0 | 0 | 55809.234 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
May | 1454790000000 | 1355850.337 | 24-MAY-15:09 | 645239.307 | 326066.958 | 47124.409 | 0 | 141053.177 | 0 | 59663.972 | 51147.129 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1606980000000 | 1459467.453 | 21-JUN-15:39 | 645239.307 | 326066.958 | 49430.951 | 0 | 238187.26 | 0 | 63840.463 | 51147.129 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1607220000000 | 1460300.176 | 03-JUL-15:00 | 645239.307 | 326066.958 | 42818.595 | 0 | 244233.694 | 0 | 65239.108 | 51147.129 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1602570000000 | 1449663.966 | 15-AUG-15:09 | 645239.307 | 326066.958 | 48731.059 | 0 | 227815.021 | 0 | 65109.107 | 51147.129 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1327740000000 | 1295501.2 | 07-SEP-15:00 | 645239.307 | 326066.958 | 44017.215 | 0 | 85216.597 | 0 | 58258.609 | 51147.129 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1377510000000 | 1195547.513 | 23-OCT-07:00 | 645239.307 | 326066.958 | 42109.425 | 0 | 0 | 3079 | 56830.845 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1367000000000 | 1195418.134 | 28-NOV-08:39 | 645239.307 | 326066.958 | 42109.425 | 0 | 0 | 3079 | 56701.466 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1370370000000 | 1199436.943 | 28-DEC-08:39 | 645239.307 | 326066.958 | 42109.425 | 0 | 0 | 3079 | 60720.275 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17139500000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1261710000000 | 1162496.935 |  | 645239.307 | 326066.958 | 42109.425 | 0 | 0 | 0 | 55641.462 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1607220000000 | 1460300.176 |  | 645239.307 | 326066.958 | 49430.951 | 0 | 244233.694 | 3079 | 65239.108 | 51147.129 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 476274.69 | 117140.55 | 0 | 593415.25
Cost per Total Building Area ($/m2) | 10.28 | 2.53 | 0 | 12.81
Cost per Net Conditioned Building Area ($/m2) | 10.28 | 2.53 | 0 | 12.81

## Picture
DOE Commercial Building Benchmark - Large Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720