## BuildingSummary
Building Summary Medium Office post-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Medium Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.75222 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.59

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0702 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0701 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 8.07 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0702 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0701 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 8.07 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0702 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0701 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 8.07 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 3.7565
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.7218 | 652.8006 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_1_COOLC DXCOIL | 166.4249 | 149.7212 | 145.9057 | 138.9539 | 137.7669 | 126.7533 | 105.6865 | 131.2957 | 121.9824 | 113.8837 | 133.0172 | 116.2657 | 131.0072 | 112.8801 | 122.1512 | 123.0359
| VAV_2_COOLC DXCOIL | 173.4283 | 155.2557 | 170.2388 | 148.6065 | 152.1242 | 153.2034 | 135.376 | 151.3928 | 139.9203 | 142.4991 | 154.432 | 134.7626 | 153.1915 | 132.9962 | 145.0971 | 164.8552
| VAV_3_COOLC DXCOIL | 176.8282 | 158.4257 | 174.4084 | 151.3554 | 150.0825 | 155.9135 | 126.622 | 153.5072 | 131.8285 | 136.1832 | 152.5649 | 124.2383 | 151.3565 | 122.3784 | 138.8277 | 154.1404
Heating (kW)
| HEATSYS1 BOILER | 317.9997 | 280.9208 | 320.5341 | 267.0596 | 311.3227 | 293.83 | 272.3375 | 276.714 | 239.975 | 286.6241 | 281.3476 | 231.5176 | 282.1552 | 243.841 | 285.3234 | 335.8319
HVAC Efficiency
Air Conditioning (COP)
| VAV_1_COOLC DXCOIL | 3.07 | 3.05 | 3.13 | 3.09 | 3.21 | 3.24 | 3.32 | 3.05 | 3.32 | 3.32 | 3.07 | 3.32 | 3.09 | 3.32 | 3.21 | 3.32
| VAV_2_COOLC DXCOIL | 3.09 | 3.08 | 3.11 | 3.12 | 3.3 | 3.32 | 3.32 | 3.16 | 3.32 | 3.32 | 3.18 | 3.32 | 3.2 | 3.32 | 3.32 | 3.2
| VAV_3_COOLC DXCOIL | 3.09 | 3.08 | 3.13 | 3.12 | 3.27 | 3.32 | 3.32 | 3.14 | 3.32 | 3.32 | 3.18 | 3.32 | 3.19 | 3.32 | 3.31 | 3.32
| Heating Efficiency (%) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 8.27 | 7.25 | 7.67 | 7.01 | 7.67 | 7.25 | 6.38 | 6.4 | 7.37 | 6.87 | 6.6 | 7.02 | 6.59 | 6.82 | 6.82 | 7.43
| VAV_2_FAN | 8.73 | 7.81 | 9.58 | 7.72 | 9.03 | 9.26 | 8.18 | 8.15 | 8.45 | 8.61 | 8.44 | 8.14 | 8.5 | 8.03 | 8.77 | 9.96
| VAV_3_FAN | 8.93 | 7.93 | 9.96 | 7.87 | 8.77 | 9.42 | 7.65 | 8.14 | 7.96 | 8.23 | 8.29 | 7.51 | 8.35 | 7.39 | 8.33 | 9.31
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.091538 | 0.12453 | 0.10241 | 0.098511 | 0.13513 | 0.10282 | 0.15212 | 0.08087 | 0.037259 | 0.078923 | 0.084901 | 0.037277 | 0.065464 | 0.08125 | 0.065192 | 0.10484
| Total Cost ($/m2) | 15.06 | 18.09 | 14.89 | 12.75 | 16.65 | 13.5 | 16.42 | 10.06 | 4.34 | 8.47 | 9.87 | 4.13 | 7.48 | 8.73 | 7.01 | 11.1
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01138 | 0.0080526 | 0.0082117 | 0.0096 | 0.0085521 | 0.0076777 | 0.0085414 | 0.0096877 | 0.0068811 | 0.0084024 | 0.0083394 | 0.0069091 | 0.0078777 | 0.0080918 | 0.0078705 | 0.0041241
| Total Cost ($/m2) | 0.28 | 0.82 | 0.8 | 1.62 | 0.8 | 1.03 | 1.25 | 2.48 | 1.21 | 2.23 | 2.94 | 1.7 | 3.49 | 2.88 | 4.21 | 3.74
Total Utility Costs
| Cost Intensity ($/m2) | 15.34 | 18.91 | 15.69 | 14.37 | 17.44 | 14.53 | 17.68 | 12.55 | 5.55 | 10.7 | 12.81 | 5.82 | 10.97 | 11.61 | 11.22 | 14.84
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 318677.7778 | 227002.7778 | 222880.5556 | 149222.2222 | 117561.1111 | 151783.3333 | 45125 | 123686.1111 | 81605.5556 | 38619.4444 | 81480.5556 | 54358.3333 | 70641.6667 | 37608.3333 | 35813.8889 | 23219.4444
| Interior Lighting | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111
| Exterior Lighting | 9525 | 9519.4444 | 9519.4444 | 9516.6667 | 9511.1111 | 9508.3333 | 9513.8889 | 9508.3333 | 9511.1111 | 9491.6667 | 9508.3333 | 9502.7778 | 9502.7778 | 9500 | 9494.4444 | 9436.1111
| Interior Equipment | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 26741.6667 | 22080.5556 | 27188.8889 | 20769.4444 | 21663.8889 | 27872.2222 | 18227.7778 | 21472.2222 | 24391.6667 | 21247.2222 | 22844.4444 | 22486.1111 | 23277.7778 | 22361.1111 | 24588.8889 | 28255.5556
| Pumps | 94.4444 | 216.6667 | 188.8889 | 330.5556 | 175 | 255.5556 | 258.3333 | 458.3333 | 366.6667 | 422.2222 | 627.7778 | 513.8889 | 819.4444 | 716.6667 | 986.1111 | 1702.7778
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 819872.2222 | 723652.7778 | 724611.1111 | 644675 | 613741.6667 | 654252.7778 | 537958.3333 | 619958.3333 | 580711.1111 | 534616.6667 | 579300 | 551697.2222 | 569075 | 535019.4444 | 535719.4444 | 527450
Gas (MJ)
| Heating | 93390 | 474830 | 453340 | 806410 | 428270 | 634860 | 692920 | 1237100 | 838530 | 1280810 | 1711480 | 1180410 | 2165780 | 1728790 | 2615970 | 4470720
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 28430 | 32470 | 30130 | 36360 | 35610 | 32930 | 38950 | 39420 | 38840 | 41030 | 42110 | 41980 | 44440 | 44860 | 48270 | 52910
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 121820 | 507290 | 483480 | 842770 | 463880 | 667790 | 731870 | 1276520 | 877380 | 1321830 | 1753590 | 1222390 | 2210220 | 1773650 | 2664250 | 4523620
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3073360 | 3112440 | 3092080 | 3163600 | 2673350 | 3023100 | 2668530 | 3508370 | 2967930 | 3246460 | 3839070 | 3208490 | 4258890 | 3699720 | 4592840 | 6422440
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 230.2682 | 164.0263 | 161.0477 | 107.8241 | 84.9466 | 109.6747 | 32.6061 | 89.3723 | 58.966 | 27.9054 | 58.8757 | 39.2779 | 51.0438 | 27.1748 | 25.8782 | 16.7778
| Interior Lighting (elec) | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941
| Exterior Lighting (elec) | 6.8825 | 6.8785 | 6.8785 | 6.8765 | 6.8725 | 6.8705 | 6.8745 | 6.8705 | 6.8725 | 6.8584 | 6.8705 | 6.8665 | 6.8665 | 6.8645 | 6.8604 | 6.8183
| Interior Equipment (elec) | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 19.3228 | 15.9548 | 19.646 | 15.0075 | 15.6538 | 20.1397 | 13.1709 | 15.5153 | 17.6248 | 15.3527 | 16.5068 | 16.2479 | 16.8199 | 16.1576 | 17.7673 | 20.4167
| Pumps (elec) | 0.068243 | 0.15656 | 0.13649 | 0.23885 | 0.12645 | 0.18466 | 0.18666 | 0.33118 | 0.26494 | 0.30509 | 0.45362 | 0.37132 | 0.59211 | 0.51784 | 0.71254 | 1.2304
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 592.4182 | 522.8925 | 523.585 | 465.8253 | 443.4737 | 472.7459 | 388.7146 | 447.9657 | 419.6066 | 386.3 | 418.587 | 398.642 | 411.1987 | 386.591 | 387.0968 | 381.1216
Gas (MJ/m2)
| Heating (gas) | 18.7448 | 95.3055 | 90.9921 | 161.8585 | 85.9602 | 127.4259 | 139.0794 | 248.3045 | 168.3055 | 257.0777 | 343.5196 | 236.9259 | 434.7044 | 346.994 | 525.0643 | 897.3403
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 5.7063 | 6.5172 | 6.0475 | 7.298 | 7.1475 | 6.6095 | 7.8178 | 7.9122 | 7.7958 | 8.2353 | 8.4521 | 8.426 | 8.9198 | 9.0041 | 9.6885 | 10.6198
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 24.4511 | 101.8207 | 97.0417 | 169.1565 | 93.1076 | 134.0354 | 146.8972 | 256.2166 | 176.1033 | 265.311 | 351.9717 | 245.3519 | 443.6242 | 355.9981 | 534.7548 | 907.9581
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 616.8693 | 624.7132 | 620.6267 | 634.9818 | 536.5813 | 606.7814 | 535.6139 | 704.1823 | 595.7079 | 651.613 | 770.5587 | 643.9919 | 854.8229 | 742.5891 | 921.8516 | 1289.0797
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 217.9936 | 184.6765 | 170.3746 | 159.9673 | 179.7836 | 154.8498 | 142.6808 | 156.8339 | 142.5556 | 138.3305 | 138.7502 | 146.1057 | 139.2159 | 140.8902 | 139.1045 | 142.5064
| Feb | 224.8119 | 185.0165 | 176.7613 | 162.7539 | 177.5635 | 158.8964 | 161.5522 | 150.7318 | 153.9557 | 147.4082 | 138.3429 | 140.2181 | 138.7731 | 144.6185 | 138.9655 | 141.7637
| Mar | 229.6066 | 185.2305 | 201.2589 | 166.5696 | 173.6939 | 164.6773 | 154.1665 | 170.2243 | 156.2837 | 153.6228 | 159.0508 | 153.8111 | 148.5731 | 151.7722 | 138.7335 | 141.6337
| Apr | 239.7733 | 203.533 | 201.2821 | 185.4592 | 183.0007 | 194.0171 | 157.541 | 169.4942 | 173.6832 | 148.4719 | 164.0116 | 161.2665 | 158.3257 | 148.1523 | 147.471 | 138.9095
| May | 253.5929 | 248.566 | 245.1273 | 213.6686 | 194.2632 | 222.3166 | 164.259 | 192.2127 | 196.0306 | 171.3824 | 191.7962 | 179.6797 | 191.0105 | 159.4364 | 162.0191 | 157.5222
| Jun | 284.9814 | 248.7445 | 321.0208 | 231.6996 | 188.0412 | 292.876 | 171.3767 | 238.8685 | 220.3623 | 174.215 | 228.193 | 196.4066 | 222.932 | 201.1458 | 192.0665 | 185.0546
| Jul | 277.289 | 274.2559 | 313.4621 | 269.149 | 198.4591 | 285.0841 | 187.1918 | 252.2683 | 230.6045 | 191.0039 | 236.2976 | 215.5293 | 224.1531 | 202.9042 | 212.7449 | 182.3487
| Aug | 289.7941 | 271.0086 | 317.0443 | 234.3203 | 230.7799 | 279.9172 | 176.2866 | 262.4099 | 228.7538 | 187.4945 | 237.3969 | 209.052 | 219.4211 | 193.7371 | 197.5412 | 181.9675
| Sep | 267.8219 | 248.1019 | 272.8717 | 221.5154 | 219.5817 | 261.8235 | 203.2431 | 202.0343 | 194.0344 | 184.7638 | 196.8291 | 187.5199 | 190.6255 | 177.5693 | 188.9445 | 147.2426
| Oct | 257.6539 | 217.358 | 217.1671 | 190.7108 | 195.8611 | 200.3341 | 176.0359 | 184.7978 | 175.3423 | 160.801 | 180.7921 | 171.7307 | 163.1459 | 159.6065 | 153.9938 | 141.1473
| Nov | 231.2355 | 192.9986 | 190.7929 | 167.1434 | 184.3453 | 162.6138 | 151.8305 | 173.4287 | 151.5961 | 148.2085 | 178.137 | 155.6008 | 154.238 | 140.1101 | 138.7207 | 141.608
| Dec | 209.3098 | 183.5955 | 174.4196 | 165.1429 | 183.5058 | 161.2078 | 141.8095 | 145.0984 | 141.4436 | 138.2478 | 138.4472 | 139.668 | 138.6497 | 140.836 | 138.9174 | 141.705
Time of Peak Electrical Demand
| Jan | 23-JAN-16:10 | 03-JAN-13:00 | 27-JAN-13:39 | 24-JAN-16:00 | 26-JAN-13:09 | 18-JAN-13:00 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:10 | 02-JAN-08:09 | 30-JAN-08:09 | 24-JAN-13:00 | 02-JAN-08:09 | 17-JAN-08:09 | 09-JAN-08:09 | 02-JAN-08:09
| Feb | 22-FEB-16:10 | 23-FEB-13:00 | 28-FEB-16:19 | 22-FEB-08:09 | 13-FEB-11:00 | 08-FEB-13:00 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:10 | 21-FEB-13:00 | 06-FEB-08:09 | 07-FEB-13:00 | 07-FEB-08:09 | 02-FEB-14:00 | 02-FEB-08:09 | 03-FEB-08:09
| Mar | 27-MAR-15:20 | 29-MAR-11:00 | 17-MAR-15:30 | 28-MAR-15:00 | 03-MAR-13:00 | 31-MAR-15:20 | 01-MAR-13:09 | 09-MAR-13:00 | 02-MAR-13:00 | 29-MAR-15:00 | 31-MAR-15:09 | 30-MAR-12:00 | 23-MAR-15:00 | 30-MAR-15:09 | 07-MAR-08:09 | 14-MAR-07:10
| Apr | 03-APR-15:09 | 21-APR-15:30 | 26-APR-15:00 | 20-APR-15:00 | 11-APR-15:50 | 21-APR-15:30 | 28-APR-12:09 | 04-APR-15:00 | 21-APR-15:00 | 18-APR-15:00 | 10-APR-07:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:09 | 10-APR-07:10
| May | 15-MAY-15:00 | 18-MAY-15:30 | 30-MAY-15:00 | 15-MAY-15:09 | 30-MAY-07:00 | 31-MAY-15:00 | 26-MAY-12:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:50 | 30-MAY-15:00 | 24-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 30-MAY-12:39
| Jun | 27-JUN-15:20 | 13-JUN-15:00 | 28-JUN-15:00 | 19-JUN-15:39 | 28-JUN-12:00 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:20 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 26-JUN-15:20 | 14-JUN-15:00 | 21-JUN-15:39
| Jul | 03-JUL-15:30 | 05-JUL-15:00 | 11-JUL-15:50 | 03-JUL-15:00 | 24-JUL-15:09 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-15:00 | 03-JUL-15:30 | 24-JUL-15:09 | 03-JUL-15:30 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 11-JUL-15:00 | 11-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 01-AUG-15:00 | 14-AUG-15:00 | 08-AUG-15:39 | 04-AUG-15:30 | 15-AUG-12:09 | 09-AUG-15:09 | 01-AUG-15:20 | 07-AUG-15:09 | 04-AUG-15:50 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-12:00
| Sep | 11-SEP-15:09 | 15-SEP-15:09 | 11-SEP-15:30 | 11-SEP-12:00 | 25-SEP-15:09 | 01-SEP-15:09 | 28-SEP-15:09 | 08-SEP-15:00 | 05-SEP-12:00 | 01-SEP-15:00 | 06-SEP-12:30 | 01-SEP-15:00 | 14-SEP-15:09 | 12-SEP-12:00 | 07-SEP-15:09 | 07-SEP-15:00
| Oct | 06-OCT-15:09 | 06-OCT-15:00 | 03-OCT-15:30 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-15:09 | 31-OCT-12:00 | 03-OCT-12:00 | 11-OCT-15:00 | 17-OCT-12:00 | 30-OCT-12:09 | 05-OCT-15:20 | 06-OCT-15:20 | 06-OCT-15:09 | 27-OCT-12:39 | 30-OCT-07:10
| Nov | 07-NOV-15:09 | 03-NOV-15:09 | 13-NOV-13:00 | 22-NOV-13:30 | 20-NOV-13:09 | 10-NOV-13:09 | 14-NOV-13:09 | 03-NOV-13:00 | 08-NOV-13:00 | 03-NOV-12:00 | 02-NOV-15:09 | 10-NOV-13:00 | 02-NOV-15:09 | 03-NOV-07:10 | 27-NOV-08:09 | 06-NOV-08:09
| Dec | 19-DEC-13:00 | 19-DEC-13:00 | 13-DEC-13:09 | 26-DEC-08:00 | 19-DEC-13:09 | 05-DEC-13:00 | 01-DEC-13:00 | 08-DEC-08:00 | 05-DEC-13:00 | 11-DEC-08:09 | 26-DEC-08:09 | 21-DEC-13:00 | 20-DEC-08:09 | 18-DEC-08:09 | 21-DEC-08:09 | 29-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 9923.28 | 10015.88 | 8778.96 | 8727.57 | 7344.87 | 9154.17 | 6793.15 | 9375.05 | 7894.56 | 4796.14 | 9310.02 | 7924.74 | 9454.84 | 8631.86 | 9537.92 | 11722.37
| Total Source Energy (MJ/m2) | 1991.75 | 2010.34 | 1762.07 | 1751.76 | 1474.23 | 1837.38 | 1363.49 | 1881.72 | 1584.56 | 962.66 | 1868.66 | 1590.62 | 1897.73 | 1732.54 | 1914.4 | 2352.86
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
| Total Building | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
Emissions
| Carbon Equivalent (kg) | 227046.3472 | 250530.4725 | 227460.7375 | 213780.8501 | 80090.531 | 232705.2409 | 76066.7405 | 190318.2137 | 253040.4627 | 62774.6374 | 340474.6716 | 247409.6279 | 234646.6623 | 227500.2748 | 231416.4619 | 229990.6987
| CO2 (kg) | 526998.1912 | 632128.0786 | 539605.1242 | 494613.2756 | 215663.1884 | 557435.3046 | 205980.435 | 441680.6316 | 598454.5957 | 161364.9328 | 803968.9903 | 588812.5767 | 564220.9759 | 547153.2176 | 561553.888 | 607469.1098
| NOX (kg) | 923.9856 | 820.1298 | 892.315 | 910.1737 | 185.8182 | 888.6839 | 178.2593 | 810.5039 | 1011.3092 | 211.1421 | 1380.5276 | 979.1732 | 924.0115 | 891.1112 | 897.4542 | 679.7472
| SO2 (kg) | 3509.4109 | 3451.9646 | 2913.9363 | 2263.0332 | 1786.0405 | 3599.0928 | 1565.594 | 2263.4365 | 2536.0804 | 413.5706 | 3904.4797 | 2409.4735 | 1343.7006 | 1429.0444 | 1265.0963 | 2686.1397
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.016 | 0.0098 | 0.008 | 0.0083 | 0.0008 | 0.0068 | 0.0008 | 0.0093 | 0.01 | 0.0018 | 0.012 | 0.0095 | 0.01 | 0.0101 | 0.0095 | 0.0096
| Water for Electricity (m3) | 434.3335 | 1177.47 | 21524.1 | 4025.09 | 10775.9 | 17948.8 | 9445.36 | 140.7538 | 2636.89 | 5462.08 | 898.7473 | 2505.14 | 882.886 | 33890.4 | 831.1358 | 538.8843

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3073.36 | 616.87 | 616.87
Net Site Energy | 3073.36 | 616.87 | 616.87
Total Source Energy | 9923.28 | 1991.75 | 1991.75
Net Source Energy | 9923.28 | 1991.75 | 1991.75
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 93.39 | 0 | 0 | 0 | 0
Cooling | 1147.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 96.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 28.43 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2951.54 | 121.82 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 195.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 317999.66 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 166424.91 | 122071.38 | 44353.52 | 0.73 | 3.07
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 173428.34 | 127855.23 | 45573.1 | 0.74 | 3.09
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 176828.2 | 130553.6 | 46274.6 | 0.74 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 45789.99 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 44550.8 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 43586.63 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10868.33 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15219.24 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11468.05 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 18154.52 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12998.28 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16499.99 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13615.12 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 19411.49 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14131.46 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.91 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15386.11 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 20443.61 | -
VAV_1_HEATC | Coil:Heating:Gas | 1150.37 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 441.86 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 125.91 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.27 | 15517.84 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.73 | 16370.25 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.93 | 16750.33 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1854.04 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39917.277 | 68.9767 | 257.8676 | 0 | 0.0012 | 31913.5784 | 17096.311
February | 36285.0933 | 63.1605 | 238.0254 | 0 | 0.0011 | 29458.2806 | 15586.7805
March | 42250.2634 | 73.7137 | 278.4924 | 0 | 0.0013 | 34466.6482 | 18166.2162
April | 40724.2186 | 71.5568 | 272.4127 | 0 | 0.0012 | 33714.6005 | 17560.7261
May | 46909.1937 | 82.5406 | 314.6999 | 0 | 0.0014 | 38948.268 | 20239.3977
June | 48811.1701 | 85.9652 | 328.0729 | 0 | 0.0015 | 40603.4207 | 21067.8302
July | 49165.257 | 86.5997 | 330.5382 | 0 | 0.0015 | 40908.536 | 21221.7472
August | 52610.0341 | 92.6626 | 353.6602 | 0 | 0.0016 | 43770.1905 | 22708.1806
September | 46672.474 | 82.1591 | 313.3877 | 0 | 0.0014 | 38785.8979 | 20140.7757
October | 44850.0353 | 78.8675 | 300.4928 | 0 | 0.0014 | 37189.919 | 19345.9548
November | 40646.4728 | 71.374 | 271.5296 | 0 | 0.0012 | 33605.2714 | 17522.5795
December | 38156.702 | 66.4093 | 250.2315 | 0 | 0.0011 | 30968.9123 | 16389.8475
Annual Sum or Average | 526998.1912 | 923.9856 | 3509.4109 | 0 | 0.016 | 434333.5236 | 227046.3472
Minimum of Months | 36285.0933 | 63.1605 | 238.0254 | 0 | 0.0011 | 29458.2806 | 15586.7805
Maximum of Months | 52610.0341 | 92.6626 | 353.6602 | 0 | 0.0016 | 43770.1905 | 22708.1806
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 216870000000 | 217993.579 | 23-JAN-16:10 | 75734.208 | 50956.166 | 7939.382 | 0 | 83355.383 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 200185000000 | 224811.944 | 22-FEB-16:10 | 75734.208 | 50956.166 | 8537.575 | 0 | 89575.555 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 234220000000 | 229606.582 | 27-MAR-15:20 | 75734.208 | 50956.166 | 8975.07 | 0 | 93932.699 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 229109000000 | 239773.26 | 03-APR-15:09 | 75734.208 | 50956.166 | 9886.598 | 0 | 103187.849 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 264675000000 | 253592.911 | 15-MAY-15:00 | 75734.208 | 50956.166 | 10271.458 | 0 | 116622.639 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 275923000000 | 284981.387 | 27-JUN-15:20 | 75734.208 | 50956.166 | 22836.214 | 0 | 135446.36 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 277996000000 | 277289.024 | 03-JUL-15:30 | 75734.208 | 50956.166 | 21187.802 | 0 | 129402.409 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 297443000000 | 289794.139 | 21-AUG-15:09 | 75734.208 | 50956.166 | 23293.312 | 0 | 139802.013 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 263572000000 | 267821.882 | 11-SEP-15:09 | 75734.208 | 50956.166 | 12440.493 | 0 | 128682.575 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 252726000000 | 257653.881 | 06-OCT-15:09 | 75734.208 | 50956.166 | 10957.748 | 0 | 119997.319 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 228366000000 | 231235.468 | 07-NOV-15:09 | 75734.208 | 48066.275 | 9226.309 | 0 | 98200.236 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 210451000000 | 209309.8 | 19-DEC-13:00 | 75734.208 | 51598.363 | 6599.749 | 0 | 75369.04 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2951540000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 200185000000 | 209309.8 |  | 75734.208 | 48066.275 | 6599.749 | 0 | 75369.04 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 297443000000 | 289794.139 |  | 75734.208 | 51598.363 | 23293.312 | 0 | 139802.013 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 75049.65 | 1386.31 | 0 | 76435.95
Cost per Total Building Area ($/m2) | 15.06 | 0.28 | 0 | 15.34
Cost per Net Conditioned Building Area ($/m2) | 15.06 | 0.28 | 0 | 15.34

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3112.44 | 624.71 | 624.71
Net Site Energy | 3112.44 | 624.71 | 624.71
Total Source Energy | 10015.88 | 2010.34 | 2010.34
Net Source Energy | 10015.88 | 2010.34 | 2010.34
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 474.83 | 0 | 0 | 0 | 0
Cooling | 817.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 79.49 | 0 | 0 | 0 | 0 | 0
Pumps | 0.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 32.47 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2605.15 | 507.29 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 195.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 280920.82 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 149721.24 | 108665.76 | 41055.48 | 0.73 | 3.05
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 155255.65 | 114419.98 | 40835.67 | 0.74 | 3.08
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 158425.69 | 116546.34 | 41879.35 | 0.74 | 3.08
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 44415.33 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 44040.63 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 42334.79 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9897.72 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11300.79 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9055.11 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13992.38 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12084.79 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12810.4 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11162.68 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15330.36 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13000.01 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12311.7 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12932.57 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16376.64 | -
VAV_1_HEATC | Coil:Heating:Gas | 13944.6 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 13085.4 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 12890.63 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.25 | 13604.75 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.81 | 14643.2 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.93 | 14877.49 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1637.86 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 49072.604 | 61.7905 | 241.6932 | 0 | 0.0007 | 82433.4015 | 19206.9621
February | 43374.542 | 54.5615 | 212.8701 | 0 | 0.0006 | 72602.563 | 16969.763
March | 49874.0019 | 64.3635 | 267.5433 | 0 | 0.0008 | 91257.8226 | 19722.2116
April | 46977.0977 | 61.3663 | 262.3859 | 0 | 0.0007 | 89502.0423 | 18672.2138
May | 55193.2367 | 72.4249 | 312.84 | 0 | 0.0009 | 106713.8163 | 21979.9242
June | 60733.1529 | 79.7714 | 345.3185 | 0 | 0.001 | 117792.9859 | 24196.0364
July | 62187.9673 | 81.6899 | 353.6972 | 0 | 0.001 | 120651.1126 | 24776.6168
August | 65288.9562 | 85.7554 | 371.2234 | 0 | 0.001 | 126629.5017 | 26011.0769
September | 54110.3485 | 71.0539 | 307.4022 | 0 | 0.0009 | 104859.1149 | 21555.1223
October | 50793.6349 | 66.4759 | 285.4396 | 0 | 0.0008 | 97366.4016 | 20205.1759
November | 46526.9384 | 60.3826 | 254.3304 | 0 | 0.0007 | 86752.5116 | 18442.2893
December | 47995.5982 | 60.4938 | 237.2207 | 0 | 0.0007 | 80908.2775 | 18793.0803
Annual Sum or Average | 632128.0786 | 820.1298 | 3451.9646 | 0 | 0.0098 | 1177470 | 250530.4725
Minimum of Months | 43374.542 | 54.5615 | 212.8701 | 0 | 0.0006 | 72602.563 | 16969.763
Maximum of Months | 65288.9562 | 85.7554 | 371.2234 | 0 | 0.001 | 126629.5017 | 26011.0769
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 182384000000 | 184676.514 | 03-JAN-13:00 | 75734.208 | 51598.363 | 3980.722 | 0 | 53354.781 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 160633000000 | 185016.524 | 23-FEB-13:00 | 75734.208 | 51598.363 | 4707.245 | 0 | 52968.268 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 201908000000 | 185230.507 | 29-MAR-11:00 | 75734.208 | 50788.728 | 4084.618 | 0 | 54614.513 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 198023000000 | 203533.039 | 21-APR-15:30 | 75734.208 | 50956.166 | 5848.686 | 0 | 70985.54 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 236105000000 | 248565.977 | 18-MAY-15:30 | 75734.208 | 50956.166 | 9209.014 | 0 | 112658.149 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 260617000000 | 248744.508 | 13-JUN-15:00 | 75734.208 | 50956.166 | 9632.325 | 0 | 112413.37 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 266941000000 | 274255.892 | 05-JUL-15:00 | 75734.208 | 50956.166 | 21243.053 | 0 | 126314.026 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 280168000000 | 271008.64 | 31-AUG-15:00 | 75734.208 | 50956.166 | 20128.986 | 0 | 124180.841 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 232001000000 | 248101.879 | 15-SEP-15:09 | 75734.208 | 50956.166 | 7589.741 | 0 | 113813.324 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 215423000000 | 217358.018 | 06-OCT-15:00 | 75734.208 | 50956.166 | 6863.369 | 0 | 83795.836 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 191940000000 | 192998.556 | 03-NOV-15:09 | 75734.208 | 50956.166 | 4557.479 | 0 | 61742.263 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 179010000000 | 183595.474 | 19-DEC-13:00 | 75734.208 | 51598.363 | 4217.097 | 0 | 52037.366 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2605150000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 160633000000 | 183595.474 |  | 75734.208 | 50788.728 | 3980.722 | 0 | 52037.366 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 280168000000 | 274255.892 |  | 75734.208 | 51598.363 | 21243.053 | 0 | 126314.026 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 90119.57 | 4085 | 0 | 94204.57
Cost per Total Building Area ($/m2) | 18.09 | 0.82 | 0 | 18.91
Cost per Net Conditioned Building Area ($/m2) | 18.09 | 0.82 | 0 | 18.91

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3092.08 | 620.63 | 620.63
Net Site Energy | 3092.08 | 620.63 | 620.63
Total Source Energy | 8778.96 | 1762.07 | 1762.07
Net Source Energy | 8778.96 | 1762.07 | 1762.07
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 453.34 | 0 | 0 | 0 | 0
Cooling | 802.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 97.88 | 0 | 0 | 0 | 0 | 0
Pumps | 0.68 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 30.13 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2608.6 | 483.48 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 195.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 320534.1 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 145905.72 | 109558.92 | 36346.8 | 0.75 | 3.13
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 170238.76 | 131665.45 | 38573.31 | 0.77 | 3.11
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 174408.43 | 135761.04 | 38647.38 | 0.78 | 3.13
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 40510.47 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 51697.42 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 52794.8 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12177.7 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12422.03 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9825.16 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15479.97 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15630.56 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14836.07 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13151.24 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 17608.18 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16518.97 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14888.64 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14711.01 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 18462.61 | -
VAV_1_HEATC | Coil:Heating:Gas | 7310.97 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 4450.93 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 3885.03 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.67 | 14386.97 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.58 | 16477.83 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.96 | 17127.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1868.82 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 38030.6729 | 59.6126 | 181.6672 | 0 | 0.0005 | 1341740 | 15699.7995
February | 34414.0882 | 54.3767 | 167.5242 | 0 | 0.0005 | 1237310 | 14250.5983
March | 41230.0821 | 67.7591 | 219.6039 | 0 | 0.0006 | 1622110 | 17337.2447
April | 39124.5379 | 65.3183 | 215.7645 | 0 | 0.0006 | 1593800 | 16554.9601
May | 45438.6419 | 76.5359 | 255.477 | 0 | 0.0007 | 1887180 | 19295.054
June | 55472.7263 | 93.6512 | 313.442 | 0 | 0.0008 | 2315380 | 23577.575
July | 57816.725 | 97.6383 | 326.9027 | 0 | 0.0009 | 2414810 | 24576.866
August | 59324.7946 | 100.181 | 335.4002 | 0 | 0.0009 | 2477580 | 25217.5111
September | 49977.835 | 84.3484 | 282.2049 | 0 | 0.0008 | 2084630 | 21239.4408
October | 42537.5119 | 71.232 | 236.1469 | 0 | 0.0006 | 1744370 | 18020.9231
November | 37835.6117 | 62.0907 | 200.8742 | 0 | 0.0005 | 1483760 | 15900.7877
December | 38401.8968 | 59.5708 | 178.9285 | 0 | 0.0005 | 1321480 | 15789.9771
Annual Sum or Average | 539605.1242 | 892.315 | 2913.9363 | 0 | 0.008 | 21524100 | 227460.7375
Minimum of Months | 34414.0882 | 54.3767 | 167.5242 | 0 | 0.0005 | 1237310 | 14250.5983
Maximum of Months | 59324.7946 | 100.181 | 335.4002 | 0 | 0.0009 | 2477580 | 25217.5111
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 162611000000 | 170374.599 | 27-JAN-13:39 | 75734.208 | 51598.363 | 5038.394 | 0 | 37995.193 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 149955000000 | 176761.323 | 28-FEB-16:19 | 75734.208 | 50956.166 | 5067.944 | 0 | 44994.565 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 196590000000 | 201258.908 | 17-MAR-15:30 | 75734.208 | 50956.166 | 6706.221 | 0 | 67853.874 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 193159000000 | 201282.13 | 26-APR-15:00 | 75734.208 | 50956.166 | 6409.504 | 0 | 68173.813 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 228716000000 | 245127.252 | 30-MAY-15:00 | 75734.208 | 50956.166 | 10684.151 | 0 | 107744.287 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 280610000000 | 321020.826 | 28-JUN-15:00 | 75734.208 | 50956.166 | 26354.512 | 0 | 167967.501 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 292661000000 | 313462.124 | 11-JUL-15:50 | 75734.208 | 50956.166 | 23406.98 | 0 | 163356.33 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 300268000000 | 317044.305 | 01-AUG-15:00 | 75734.208 | 50956.166 | 26210.244 | 0 | 164135.248 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 252645000000 | 272871.694 | 11-SEP-15:30 | 75734.208 | 50956.166 | 13732.049 | 0 | 132440.831 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 211408000000 | 217167.098 | 03-OCT-15:30 | 75734.208 | 50956.166 | 6146.45 | 0 | 84321.834 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 179823000000 | 190792.947 | 13-NOV-13:00 | 75734.208 | 51598.363 | 5987.273 | 0 | 57464.662 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 160155000000 | 174419.649 | 13-DEC-13:09 | 75734.208 | 51598.363 | 5090.817 | 0 | 41983.806 | 0 | 12.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2608600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 149955000000 | 170374.599 |  | 75734.208 | 50956.166 | 5038.394 | 0 | 37995.193 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 300268000000 | 321020.826 |  | 75734.208 | 51598.363 | 26354.512 | 0 | 167967.501 | 0 | 12.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 74205.84 | 3970.17 | 0 | 78176.02
Cost per Total Building Area ($/m2) | 14.89 | 0.8 | 0 | 15.69
Cost per Net Conditioned Building Area ($/m2) | 14.89 | 0.8 | 0 | 15.69

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3163.6 | 634.98 | 634.98
Net Site Energy | 3163.6 | 634.98 | 634.98
Total Source Energy | 8727.57 | 1751.76 | 1751.76
Net Source Energy | 8727.57 | 1751.76 | 1751.76
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 806.41 | 0 | 0 | 0 | 0
Cooling | 537.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 74.77 | 0 | 0 | 0 | 0 | 0
Pumps | 1.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 36.36 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2320.83 | 842.77 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.255 | 0.129 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.255 | 0.129 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.255 | 0.129 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 195.85 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 456.98 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 267059.62 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 138953.89 | 102551.58 | 36402.31 | 0.74 | 3.09
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 148606.48 | 111061.71 | 37544.77 | 0.75 | 3.12
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 151355.4 | 113101.89 | 38253.51 | 0.75 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 43798.11 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 44216.79 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 42595.85 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9081.57 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10026.24 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7863.2 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12112.43 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11490.22 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11769.59 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10243.63 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13611.92 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12513.54 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11351.2 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11746.94 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14786.43 | -
VAV_1_HEATC | Coil:Heating:Gas | 18955.55 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 17883.09 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 17670.43 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.01 | 13150.56 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.72 | 14491.39 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.87 | 14755.07 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1557.05 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43724.5543 | 72.5075 | 161.0684 | 0 | 0.0006 | 286402.3216 | 18164.0474
February | 37534.9203 | 63.9419 | 146.5937 | 0 | 0.0006 | 260684.9651 | 15749.6105
March | 40594.4144 | 73.7071 | 180.8634 | 0 | 0.0007 | 321678.4865 | 17453.8836
April | 37410.5417 | 69.9015 | 176.3612 | 0 | 0.0006 | 313690.9022 | 16267.379
May | 40682.6196 | 77.9759 | 201.397 | 0 | 0.0007 | 358240.3559 | 17871.2481
June | 44130.0433 | 85.0405 | 220.7035 | 0 | 0.0008 | 392586.49 | 19427.8533
July | 44976.979 | 86.6809 | 224.9798 | 0 | 0.0008 | 400193.2268 | 19801.474
August | 47835.8171 | 92.1952 | 239.303 | 0 | 0.0009 | 425671.3874 | 21060.5338
September | 41268.0402 | 79.4401 | 205.9725 | 0 | 0.0008 | 366382.3712 | 18160.0172
October | 38069.6663 | 71.7314 | 182.4015 | 0 | 0.0007 | 324440.4523 | 16609.2468
November | 37678.4456 | 67.777 | 164.7557 | 0 | 0.0006 | 293023.3647 | 16141.4367
December | 40707.2337 | 69.2746 | 158.6335 | 0 | 0.0006 | 282094.2512 | 17074.1197
Annual Sum or Average | 494613.2756 | 910.1737 | 2263.0332 | 0 | 0.0083 | 4025090 | 213780.8501
Minimum of Months | 37410.5417 | 63.9419 | 146.5937 | 0 | 0.0006 | 260684.9651 | 15749.6105
Maximum of Months | 47835.8171 | 92.1952 | 239.303 | 0 | 0.0009 | 425671.3874 | 21060.5338
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 165137000000 | 159967.345 | 24-JAN-16:00 | 75734.208 | 50956.166 | 3650.003 | 0 | 29600.591 | 0 | 26.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 150308000000 | 162753.876 | 22-FEB-08:09 | 75734.208 | 58341.44 | 3650.003 | 0 | 24987.184 | 0 | 41.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 185477000000 | 166569.562 | 28-MAR-15:00 | 75734.208 | 50956.166 | 4120.688 | 0 | 35750.06 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 180871000000 | 185459.203 | 20-APR-15:00 | 75734.208 | 50956.166 | 4923.087 | 0 | 53837.302 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 206558000000 | 213668.562 | 15-MAY-15:09 | 75734.208 | 50956.166 | 7421.971 | 0 | 79547.778 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 226362000000 | 231699.603 | 19-JUN-15:39 | 75734.208 | 50956.166 | 9282.995 | 0 | 95717.794 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 230748000000 | 269149.05 | 03-JUL-15:00 | 75734.208 | 50956.166 | 21421.592 | 0 | 121028.645 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 245438000000 | 234320.324 | 14-AUG-15:00 | 75734.208 | 50956.166 | 8787.386 | 0 | 98834.125 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 211253000000 | 221515.443 | 11-SEP-12:00 | 75734.208 | 51598.363 | 7782.736 | 0 | 86391.696 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 187069000000 | 190710.785 | 12-OCT-15:00 | 75734.208 | 50956.166 | 4934.4 | 0 | 59077.571 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 168954000000 | 167143.371 | 22-NOV-13:30 | 75734.208 | 51598.363 | 4061.519 | 0 | 35740.42 | 0 | 8.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 162653000000 | 165142.919 | 26-DEC-08:00 | 75734.208 | 58341.44 | 3650.003 | 0 | 27340.899 | 0 | 76.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2320830000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 150308000000 | 159967.345 |  | 75734.208 | 50956.166 | 3650.003 | 0 | 24987.184 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 245438000000 | 269149.05 |  | 75734.208 | 58341.44 | 21421.592 | 0 | 121028.645 | 0 | 76.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63507.44 | 8090.59 | 0 | 71598.03
Cost per Total Building Area ($/m2) | 12.75 | 1.62 | 0 | 14.37
Cost per Net Conditioned Building Area ($/m2) | 12.75 | 1.62 | 0 | 14.37

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2673.35 | 536.58 | 536.58
Net Site Energy | 2673.35 | 536.58 | 536.58
Total Source Energy | 7344.87 | 1474.23 | 1474.23
Net Source Energy | 7344.87 | 1474.23 | 1474.23
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 428.27 | 0 | 0 | 0 | 0
Cooling | 423.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 77.99 | 0 | 0 | 0 | 0 | 0
Pumps | 0.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 35.61 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2209.47 | 463.88 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.44 | 0.272 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.44 | 0.272 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.44 | 0.272 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 195.85 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 311322.71 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 137766.9 | 106071.01 | 31695.89 | 0.77 | 3.21
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 152124.17 | 120525.56 | 31598.61 | 0.79 | 3.3
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 150082.51 | 118060.12 | 32022.39 | 0.79 | 3.27
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 39119.62 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 49013.03 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 44240.91 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15044.21 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14238.12 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7501.73 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 17906.48 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17072.68 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15667.8 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9503.05 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 19161.64 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17610.46 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14629.01 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10805.35 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 19947.14 | -
VAV_1_HEATC | Coil:Heating:Gas | 3588.14 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 1476.79 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 1882.07 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.67 | 14393.11 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.03 | 16941.25 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.77 | 16452.53 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1815.11 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18347.9994 | 15.9186 | 132.3226 | 0 | 0.0001 | 798284.687 | 6753.9845
February | 15980.3091 | 13.8424 | 119.1842 | 0 | 0.0001 | 719039.1747 | 5894.4381
March | 18576.9683 | 16.0606 | 144.1015 | 0 | 0.0001 | 869388.5542 | 6869.1679
April | 16742.9359 | 14.4406 | 136.0421 | 0 | 0.0001 | 820789.689 | 6209.8174
May | 18111.4127 | 15.584 | 153.7589 | 0 | 0.0001 | 927706.8095 | 6737.5028
June | 18011.5824 | 15.4722 | 157.5448 | 0 | 0.0001 | 950565.7351 | 6714.5019
July | 17982.4066 | 15.4138 | 163.2448 | 0 | 0.0001 | 984978.8095 | 6721.7947
August | 20399.0456 | 17.484 | 185.4083 | 0 | 0.0001 | 1118710 | 7625.8172
September | 18040.9349 | 15.4724 | 162.2725 | 0 | 0.0001 | 979106.759 | 6739.0848
October | 18025.0521 | 15.4899 | 156.5568 | 0 | 0.0001 | 944600.7705 | 6716.1495
November | 17550.7284 | 15.1412 | 141.9083 | 0 | 0.0001 | 856180.0975 | 6507.2934
December | 17893.8129 | 15.4985 | 133.6956 | 0 | 0.0001 | 806587.9635 | 6600.9788
Annual Sum or Average | 215663.1884 | 185.8182 | 1786.0405 | 0 | 0.0008 | 10775900 | 80090.531
Minimum of Months | 15980.3091 | 13.8424 | 119.1842 | 0 | 0.0001 | 719039.1747 | 5894.4381
Maximum of Months | 20399.0456 | 17.484 | 185.4083 | 0 | 0.0001 | 1118710 | 7625.8172
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 163678000000 | 179783.616 | 26-JAN-13:09 | 75734.208 | 51598.363 | 5976.843 | 0 | 46465.762 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 147430000000 | 177563.478 | 13-FEB-11:00 | 75734.208 | 49992.869 | 6215.161 | 0 | 45612.593 | 0 | 8.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 178257000000 | 173693.86 | 03-MAR-13:00 | 75734.208 | 51598.363 | 5675.353 | 0 | 40677.496 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 168293000000 | 183000.677 | 11-APR-15:50 | 75734.208 | 50956.166 | 5561.065 | 0 | 50740.799 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 190215000000 | 194263.208 | 30-MAY-07:00 | 75734.208 | 58341.44 | 5008.404 | 0 | 55169.521 | 0 | 9.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 194902000000 | 188041.227 | 28-JUN-12:00 | 75734.208 | 51598.363 | 4662.925 | 0 | 56037.291 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 201958000000 | 198459.093 | 24-JUL-15:09 | 75734.208 | 50956.166 | 6341.518 | 0 | 65418.761 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 229377000000 | 230779.942 | 08-AUG-15:39 | 75734.208 | 50956.166 | 7477.758 | 0 | 96603.37 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 200754000000 | 219581.651 | 25-SEP-15:09 | 75734.208 | 50956.166 | 9837.872 | 0 | 83044.965 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 193679000000 | 195861.082 | 05-OCT-14:09 | 75734.208 | 48066.275 | 7439.076 | 0 | 64613.083 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 175549000000 | 184345.337 | 20-NOV-13:09 | 75734.208 | 51598.363 | 6439.59 | 0 | 50564.735 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 165381000000 | 183505.779 | 19-DEC-13:09 | 75734.208 | 51598.363 | 6501.142 | 0 | 49663.626 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2209470000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 147430000000 | 173693.86 |  | 75734.208 | 48066.275 | 4662.925 | 0 | 40677.496 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 229377000000 | 230779.942 |  | 75734.208 | 58341.44 | 9837.872 | 0 | 96603.37 | 0 | 9.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 82932.44 | 3967.16 | 0 | 86899.6
Cost per Total Building Area ($/m2) | 16.65 | 0.8 | 0 | 17.44
Cost per Net Conditioned Building Area ($/m2) | 16.65 | 0.8 | 0 | 17.44

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3023.1 | 606.78 | 606.78
Net Site Energy | 3023.1 | 606.78 | 606.78
Total Source Energy | 9154.17 | 1837.38 | 1837.38
Net Source Energy | 9154.17 | 1837.38 | 1837.38
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 634.86 | 0 | 0 | 0 | 0
Cooling | 546.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 100.34 | 0 | 0 | 0 | 0 | 0
Pumps | 0.92 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 32.93 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2355.31 | 667.79 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 195.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 293830.01 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 126753.25 | 98778.08 | 27975.18 | 0.78 | 3.24
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 153203.43 | 122356.73 | 30846.7 | 0.8 | 3.32
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 155913.49 | 124521.13 | 31392.36 | 0.8 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38640.05 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 50332.68 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 49979.59 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10994.79 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10225.86 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8600.78 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13802.13 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14347.1 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12616.01 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11825.78 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15835.51 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14821.05 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12345.52 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13178.25 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16489.27 | -
VAV_1_HEATC | Coil:Heating:Gas | 12228.77 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 9346.91 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 9110.2 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.25 | 13608.3 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.26 | 17362.32 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.42 | 17669.45 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1713.13 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44000.1088 | 65.1034 | 236.6848 | 0 | 0.0005 | 1180160 | 17843.969
February | 36534.0536 | 56.5482 | 219.9445 | 0 | 0.0004 | 1096810 | 15075.1477
March | 42862.4115 | 66.7077 | 261.467 | 0 | 0.0005 | 1303880 | 17724.2988
April | 40276.419 | 65.0928 | 268.3416 | 0 | 0.0005 | 1338260 | 16905.4093
May | 45891.6041 | 74.82 | 311.8836 | 0 | 0.0006 | 1555430 | 19330.0921
June | 55710.5285 | 91.2543 | 382.6163 | 0 | 0.0007 | 1908210 | 23510.198
July | 58182.119 | 95.3328 | 399.8738 | 0 | 0.0007 | 1994280 | 24556.3529
August | 60775.2943 | 99.5736 | 417.6194 | 0 | 0.0008 | 2082780 | 25649.9789
September | 49039.0832 | 80.2963 | 336.514 | 0 | 0.0006 | 1678280 | 20691.6738
October | 43056.6459 | 69.717 | 288.0961 | 0 | 0.0005 | 1436780 | 18085.9818
November | 39246.8554 | 61.4472 | 242.856 | 0 | 0.0005 | 1211090 | 16267.2966
December | 41860.1813 | 62.7906 | 233.1957 | 0 | 0.0005 | 1162810 | 17064.8419
Annual Sum or Average | 557435.3046 | 888.6839 | 3599.0928 | 0 | 0.0068 | 17948800 | 232705.2409
Minimum of Months | 36534.0536 | 56.5482 | 219.9445 | 0 | 0.0004 | 1096810 | 15075.1477
Maximum of Months | 60775.2943 | 99.5736 | 417.6194 | 0 | 0.0008 | 2082780 | 25649.9789
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 154866000000 | 154849.835 | 18-JAN-13:00 | 75734.208 | 51598.363 | 4644.626 | 0 | 22856.187 | 0 | 16.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 143927000000 | 158896.414 | 08-FEB-13:00 | 75734.208 | 51598.363 | 4852.255 | 0 | 26702.26 | 0 | 9.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 171101000000 | 164677.267 | 31-MAR-15:20 | 75734.208 | 50956.166 | 4490.061 | 0 | 33488.392 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 175612000000 | 194017.129 | 21-APR-15:30 | 75734.208 | 50956.166 | 6647.728 | 0 | 60670.587 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 204110000000 | 222316.612 | 31-MAY-15:00 | 75734.208 | 50956.166 | 9579.069 | 0 | 86038.729 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 250403000000 | 292876.014 | 27-JUN-15:00 | 75734.208 | 50956.166 | 27386.399 | 0 | 138790.802 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 261697000000 | 285084.096 | 24-JUL-15:00 | 75734.208 | 50956.166 | 26565.324 | 0 | 131819.958 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 273311000000 | 279917.181 | 04-AUG-15:30 | 75734.208 | 50956.166 | 25748.886 | 0 | 127469.481 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 220231000000 | 261823.546 | 01-SEP-15:09 | 75734.208 | 50956.166 | 19822.601 | 0 | 115302.131 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 188540000000 | 200334.078 | 03-OCT-15:09 | 75734.208 | 50956.166 | 7791.386 | 0 | 65843.879 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 158924000000 | 162613.761 | 10-NOV-13:09 | 75734.208 | 51598.363 | 5271.926 | 0 | 30000.824 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 152588000000 | 161207.781 | 05-DEC-13:00 | 75734.208 | 51598.363 | 4781.36 | 0 | 29081.256 | 0 | 12.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2355310000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 143927000000 | 154849.835 |  | 75734.208 | 50956.166 | 4490.061 | 0 | 22856.187 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 273311000000 | 292876.014 |  | 75734.208 | 51598.363 | 27386.399 | 0 | 138790.802 | 0 | 16.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 67268.23 | 5127.07 | 0 | 72395.3
Cost per Total Building Area ($/m2) | 13.5 | 1.03 | 0 | 14.53
Cost per Net Conditioned Building Area ($/m2) | 13.5 | 1.03 | 0 | 14.53

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2668.53 | 535.61 | 535.61
Net Site Energy | 2668.53 | 535.61 | 535.61
Total Source Energy | 6793.15 | 1363.49 | 1363.49
Net Source Energy | 6793.15 | 1363.49 | 1363.49
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 692.92 | 0 | 0 | 0 | 0
Cooling | 162.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 65.62 | 0 | 0 | 0 | 0 | 0
Pumps | 0.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.95 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1936.65 | 731.87 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 195.85 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 456.98 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 272337.46 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 105686.5 | 84407.08 | 21279.42 | 0.8 | 3.32
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 135376.03 | 108118.78 | 27257.25 | 0.8 | 3.32
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 126621.97 | 101127.31 | 25494.67 | 0.8 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 35693.91 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 47158.24 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 41057.92 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15530.74 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9160.58 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 5178.54 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12750.4 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18914.72 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11438.8 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8081.6 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14720.87 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18757.51 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10208.69 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8685.7 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15117.62 | -
VAV_1_HEATC | Coil:Heating:Gas | 9285.24 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 6489.25 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 7313.92 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.38 | 11977.3 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.18 | 15341.97 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.65 | 14349.88 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1587.82 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19774.5266 | 17.273 | 121.7187 | 0 | 0.0001 | 734222.9895 | 7215.356
February | 15722.545 | 13.6402 | 113.4935 | 0 | 0.0001 | 684691.7484 | 5787.8635
March | 18349.3015 | 15.9284 | 130.7751 | 0 | 0.0001 | 788941.852 | 6749.7137
April | 16290.8627 | 14.1055 | 122.5617 | 0 | 0.0001 | 739420.082 | 6012.2258
May | 17061.8412 | 14.7282 | 136.3808 | 0 | 0.0001 | 822824.4788 | 6321.2243
June | 16664.5611 | 14.3631 | 137.1715 | 0 | 0.0001 | 827610.7868 | 6186.1376
July | 16043.6204 | 13.8075 | 135.7108 | 0 | 0.0001 | 818811.012 | 5966.7722
August | 17649.1866 | 15.1912 | 148.9422 | 0 | 0.0001 | 898641.5884 | 6562.8299
September | 16260.528 | 13.9873 | 138.7682 | 0 | 0.0001 | 837262.4366 | 6051.1723
October | 16666.5071 | 14.369 | 136.4334 | 0 | 0.0001 | 823154.3244 | 6184.559
November | 16829.3498 | 14.5798 | 125.1558 | 0 | 0.0001 | 755064.7571 | 6206.5118
December | 18667.6051 | 16.2861 | 118.4823 | 0 | 0.0001 | 714718.5767 | 6822.3745
Annual Sum or Average | 205980.435 | 178.2593 | 1565.594 | 0 | 0.0008 | 9445360 | 76066.7405
Minimum of Months | 15722.545 | 13.6402 | 113.4935 | 0 | 0.0001 | 684691.7484 | 5787.8635
Maximum of Months | 19774.5266 | 17.273 | 148.9422 | 0 | 0.0001 | 898641.5884 | 7215.356
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 150543000000 | 142680.765 | 06-JAN-16:10 | 75734.208 | 50956.166 | 3679.007 | 0 | 12300.291 | 0 | 11.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 140388000000 | 161552.152 | 15-FEB-16:10 | 75734.208 | 50956.166 | 4104.982 | 0 | 30748.357 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 161763000000 | 154166.536 | 01-MAR-13:09 | 75734.208 | 51598.363 | 4180.521 | 0 | 22641.606 | 0 | 11.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 151609000000 | 157541.032 | 28-APR-12:09 | 75734.208 | 51598.363 | 3682.511 | 0 | 26517.114 | 0 | 8.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 168710000000 | 164259.031 | 26-MAY-12:00 | 75734.208 | 51598.363 | 3762.333 | 0 | 33155.687 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 169691000000 | 171376.664 | 16-JUN-15:00 | 75734.208 | 50956.166 | 5000.803 | 0 | 39677.048 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 167887000000 | 187191.827 | 03-JUL-12:00 | 75734.208 | 51598.363 | 5276.759 | 0 | 54574.056 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 184255000000 | 176286.643 | 15-AUG-12:09 | 75734.208 | 51598.363 | 4131.463 | 0 | 44814.169 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 171670000000 | 203243.114 | 28-SEP-15:09 | 75734.208 | 50956.166 | 7734.315 | 0 | 68809.986 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 168778000000 | 176035.946 | 31-OCT-12:00 | 75734.208 | 51598.363 | 4959.161 | 0 | 43735.773 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 154817000000 | 151830.501 | 14-NOV-13:09 | 75734.208 | 51598.363 | 4335.969 | 0 | 20151.659 | 0 | 10.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 146544000000 | 141809.491 | 01-DEC-13:00 | 75734.208 | 51598.363 | 3646.412 | 0 | 10813.665 | 0 | 16.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1936650000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 140388000000 | 141809.491 |  | 75734.208 | 50956.166 | 3646.412 | 0 | 10813.665 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 184255000000 | 203243.114 |  | 75734.208 | 51598.363 | 7734.315 | 0 | 68809.986 | 0 | 16.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 81832.13 | 6251.22 | 0 | 88083.35
Cost per Total Building Area ($/m2) | 16.42 | 1.25 | 0 | 17.68
Cost per Net Conditioned Building Area ($/m2) | 16.42 | 1.25 | 0 | 17.68

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3508.37 | 704.18 | 704.18
Net Site Energy | 3508.37 | 704.18 | 704.18
Total Source Energy | 9375.05 | 1881.72 | 1881.72
Net Source Energy | 9375.05 | 1881.72 | 1881.72
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1237.1 | 0 | 0 | 0 | 0
Cooling | 445.27 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 77.3 | 0 | 0 | 0 | 0 | 0
Pumps | 1.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 39.42 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2231.85 | 1276.52 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.355 | 0.274 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.355 | 0.274 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.355 | 0.274 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 195.85 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 456.98 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 276713.99 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 131295.68 | 95513.22 | 35782.47 | 0.73 | 3.05
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 151392.84 | 114827.14 | 36565.7 | 0.76 | 3.16
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 153507.22 | 115699.61 | 37807.61 | 0.75 | 3.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 39783.7 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 51400.66 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 49774.5 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8422.58 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10092.06 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7268.36 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12497 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10757.35 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12124.47 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10932.07 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14211.87 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11897.52 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11671.54 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11002.54 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15002.45 | -
VAV_1_HEATC | Coil:Heating:Gas | 24503.22 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 21792.11 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 21799.64 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.4 | 11998.44 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.15 | 15281.9 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.14 | 15269.93 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1613.33 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43417.2986 | 68.7147 | 161.9912 | 0 | 0.0007 | 10069.784 | 17706.3569
February | 36562.9314 | 59.7794 | 146.9791 | 0 | 0.0006 | 9137.4971 | 15085.9241
March | 37036.3666 | 65.6291 | 176.9076 | 0 | 0.0007 | 11000.3476 | 15745.3642
April | 32092.9509 | 59.6094 | 168.4247 | 0 | 0.0007 | 10473.8832 | 13894.3063
May | 34194.9018 | 66.4919 | 195.9011 | 0 | 0.0008 | 12183.5697 | 15076.6577
June | 37360.1036 | 74.3839 | 223.6266 | 0 | 0.0009 | 13908.4233 | 16631.0537
July | 38053.1021 | 75.8986 | 228.5196 | 0 | 0.0009 | 14212.7824 | 16951.8815
August | 41478.9015 | 82.7037 | 248.9393 | 0 | 0.001 | 15482.7776 | 18475.4683
September | 33438.5685 | 66.0588 | 197.297 | 0 | 0.0008 | 12270.7049 | 14838.0583
October | 33694.6115 | 64.0892 | 185.1392 | 0 | 0.0008 | 11513.8208 | 14725.3245
November | 34668.4074 | 62.3557 | 170.6916 | 0 | 0.0007 | 10614.1696 | 14823.0371
December | 39682.4878 | 64.7893 | 159.0195 | 0 | 0.0007 | 9885.9977 | 16364.7811
Annual Sum or Average | 441680.6316 | 810.5039 | 2263.4365 | 0 | 0.0093 | 140753.758 | 190318.2137
Minimum of Months | 32092.9509 | 59.6094 | 146.9791 | 0 | 0.0006 | 9137.4971 | 13894.3063
Maximum of Months | 43417.2986 | 82.7037 | 248.9393 | 0 | 0.001 | 15482.7776 | 18475.4683
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 159671000000 | 156833.926 | 09-JAN-08:00 | 75734.208 | 58341.44 | 3663.195 | 0 | 19025.972 | 0 | 69.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 144888000000 | 150731.777 | 15-FEB-16:10 | 75734.208 | 50956.166 | 3663.195 | 0 | 20356.426 | 0 | 21.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 174426000000 | 170224.274 | 09-MAR-13:00 | 75734.208 | 51598.363 | 3693.865 | 0 | 39184.504 | 0 | 13.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 166078000000 | 169494.25 | 04-APR-15:00 | 75734.208 | 50956.166 | 3718.79 | 0 | 39076.647 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 193188000000 | 192212.711 | 31-MAY-15:00 | 75734.208 | 50956.166 | 3996.691 | 0 | 61517.207 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 220538000000 | 238868.471 | 30-JUN-15:00 | 75734.208 | 50956.166 | 7334.713 | 0 | 104834.945 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 225364000000 | 252268.332 | 25-JUL-15:00 | 75734.208 | 50956.166 | 11514.047 | 0 | 114055.471 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 245501000000 | 262409.885 | 09-AUG-15:09 | 75734.208 | 50956.166 | 19917.276 | 0 | 115793.796 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 194569000000 | 202034.278 | 08-SEP-15:00 | 75734.208 | 50956.166 | 5977.892 | 0 | 69357.572 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 182568000000 | 184797.807 | 03-OCT-12:00 | 75734.208 | 51598.363 | 4331.872 | 0 | 53124.924 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 168303000000 | 173428.704 | 03-NOV-13:00 | 75734.208 | 48066.275 | 4276.353 | 0 | 45343.428 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 156756000000 | 145098.436 | 08-DEC-08:00 | 75734.208 | 58341.44 | 3663.195 | 0 | 7299.451 | 0 | 60.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2231850000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 144888000000 | 145098.436 |  | 75734.208 | 48066.275 | 3663.195 | 0 | 7299.451 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 245501000000 | 262409.885 |  | 75734.208 | 58341.44 | 19917.276 | 0 | 115793.796 | 0 | 69.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 50135.91 | 12366.57 | 0 | 62502.48
Cost per Total Building Area ($/m2) | 10.06 | 2.48 | 0 | 12.55
Cost per Net Conditioned Building Area ($/m2) | 10.06 | 2.48 | 0 | 12.55

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2967.93 | 595.71 | 595.71
Net Site Energy | 2967.93 | 595.71 | 595.71
Total Source Energy | 7894.56 | 1584.56 | 1584.56
Net Source Energy | 7894.56 | 1584.56 | 1584.56
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 838.53 | 0 | 0 | 0 | 0
Cooling | 293.78 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 87.81 | 0 | 0 | 0 | 0 | 0
Pumps | 1.32 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.84 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2090.56 | 877.38 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.362 | 0.225 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.362 | 0.225 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.362 | 0.225 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 195.85 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 456.98 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 239975 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 121982.35 | 97421.84 | 24560.5 | 0.8 | 3.32
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 139920.31 | 111748.09 | 28172.22 | 0.8 | 3.32
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 131828.5 | 105285.53 | 26542.98 | 0.8 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38790.59 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41102.55 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 36487.01 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7332.97 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9302.25 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6345.71 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12658.7 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9881.08 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11212.22 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8829.22 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14350.4 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9806.46 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10090.97 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9290.41 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14763.23 | -
VAV_1_HEATC | Coil:Heating:Gas | 17236.23 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 15847.7 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 16472.27 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.37 | 13824.08 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.45 | 15856.97 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.96 | 14939.93 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1399.13 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50833.647 | 80.3335 | 185.2783 | 0 | 0.0007 | 192604.8875 | 20947.419
February | 43503.9139 | 70.4418 | 167.7191 | 0 | 0.0007 | 174364.7673 | 18092.9333
March | 48859.2115 | 80.9503 | 198.3087 | 0 | 0.0008 | 206180.3319 | 20500.3641
April | 43152.6678 | 73.647 | 186.791 | 0 | 0.0007 | 194220.7571 | 18317.0288
May | 49783.5984 | 86.7006 | 224.8943 | 0 | 0.0009 | 233851.2814 | 21302.027
June | 54448.4479 | 95.3269 | 248.6861 | 0 | 0.001 | 258593.8714 | 23347.3501
July | 57215.8163 | 100.2496 | 261.7463 | 0 | 0.001 | 272174.8968 | 24541.6131
August | 59870.3564 | 104.873 | 273.7397 | 0 | 0.0011 | 284645.9541 | 25677.501
September | 49553.1779 | 86.6448 | 225.7233 | 0 | 0.0009 | 234715.5607 | 21237.3205
October | 45563.2061 | 78.0549 | 198.8164 | 0 | 0.0008 | 206726.4755 | 19369.067
November | 45944.7342 | 75.6019 | 183.6667 | 0 | 0.0007 | 190953.3672 | 19226.5304
December | 49725.8183 | 78.4849 | 180.7108 | 0 | 0.0007 | 187856.0255 | 20481.3085
Annual Sum or Average | 598454.5957 | 1011.3092 | 2536.0804 | 0 | 0.01 | 2636890 | 253040.4627
Minimum of Months | 43152.6678 | 70.4418 | 167.7191 | 0 | 0.0007 | 174364.7673 | 18092.9333
Maximum of Months | 59870.3564 | 104.873 | 273.7397 | 0 | 0.0011 | 284645.9541 | 25677.501
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 152699000000 | 142555.581 | 26-JAN-16:10 | 75734.208 | 50956.166 | 4411.79 | 0 | 11442.216 | 0 | 11.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 138238000000 | 153955.723 | 14-FEB-16:10 | 75734.208 | 50956.166 | 4658.424 | 0 | 22598.485 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 163462000000 | 156283.736 | 02-MAR-13:00 | 75734.208 | 51598.363 | 4969.303 | 0 | 23973.422 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 153981000000 | 173683.235 | 21-APR-15:00 | 75734.208 | 50956.166 | 6277.492 | 0 | 40706.929 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 185400000000 | 196030.573 | 31-MAY-15:00 | 75734.208 | 50956.166 | 9430.905 | 0 | 59900.854 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 205016000000 | 220362.341 | 29-JUN-15:30 | 75734.208 | 50956.166 | 13747.024 | 0 | 79916.504 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 215784000000 | 230604.547 | 03-JUL-15:30 | 75734.208 | 50956.166 | 15608.679 | 0 | 88297.054 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 225671000000 | 228753.808 | 01-AUG-15:20 | 75734.208 | 50956.166 | 13542.253 | 0 | 88512.741 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 186085000000 | 194034.395 | 05-SEP-12:00 | 75734.208 | 51598.363 | 7056.338 | 0 | 59637.046 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 163895000000 | 175342.278 | 11-OCT-15:00 | 75734.208 | 50956.166 | 5745.092 | 0 | 42898.372 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 151390000000 | 151596.058 | 08-NOV-13:00 | 75734.208 | 51598.363 | 5076.7 | 0 | 19178.304 | 0 | 8.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 148935000000 | 141443.576 | 05-DEC-13:00 | 75734.208 | 51598.363 | 4749.506 | 0 | 9343.071 | 0 | 18.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2090560000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 138238000000 | 141443.576 |  | 75734.208 | 50956.166 | 4411.79 | 0 | 9343.071 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 225671000000 | 230604.547 |  | 75734.208 | 51598.363 | 15608.679 | 0 | 88512.741 | 0 | 18.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21636.92 | 6037.33 | 0 | 27674.25
Cost per Total Building Area ($/m2) | 4.34 | 1.21 | 0 | 5.55
Cost per Net Conditioned Building Area ($/m2) | 4.34 | 1.21 | 0 | 5.55

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3246.46 | 651.61 | 651.61
Net Site Energy | 3246.46 | 651.61 | 651.61
Total Source Energy | 4796.14 | 962.66 | 962.66
Net Source Energy | 4796.14 | 962.66 | 962.66
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1280.81 | 0 | 0 | 0 | 0
Cooling | 139.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 76.49 | 0 | 0 | 0 | 0 | 0
Pumps | 1.52 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.03 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1924.62 | 1321.83 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 4.092 | 0.392 | 0.253 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 195.85 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 456.98 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 286624.1 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 113883.74 | 90887.73 | 22996.01 | 0.8 | 3.32
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 142499.08 | 113807.64 | 28691.44 | 0.8 | 3.32
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 136183.17 | 108763.41 | 27419.77 | 0.8 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38411.59 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 49069.78 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 44677.68 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15194.38 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10149.7 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6212.29 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13128.49 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18473.99 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12385.85 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9091.51 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15119.26 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18272.67 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11450.08 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9567.5 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15556.7 | -
VAV_1_HEATC | Coil:Heating:Gas | 16626.43 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 13954.38 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 14539.5 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.87 | 12885.9 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.61 | 16149.21 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.23 | 15433.44 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1671.11 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19449.6971 | 22.7604 | 32.6795 | 0 | 0.0002 | 431146.236 | 7278.3756
February | 14620.3874 | 17.8839 | 29.5124 | 0 | 0.0001 | 389562.5472 | 5554.1583
March | 15990.9258 | 19.9319 | 34.651 | 0 | 0.0002 | 457471.7917 | 6114.6035
April | 12704.9609 | 16.4702 | 31.5796 | 0 | 0.0001 | 417050.1757 | 4926.0377
May | 10998.2847 | 15.5368 | 35.5039 | 0 | 0.0001 | 469098.5989 | 4401.3011
June | 10197.1611 | 15.0364 | 36.9486 | 0 | 0.0001 | 488271.6331 | 4148.321
July | 9626.1908 | 14.6943 | 38.0711 | 0 | 0.0002 | 503165.6064 | 3969.5771
August | 10356.2541 | 15.921 | 41.6752 | 0 | 0.0002 | 550811.7761 | 4282.6583
September | 10430.6737 | 15.038 | 35.6063 | 0 | 0.0001 | 470492.3915 | 4206.6078
October | 12315.8511 | 16.3934 | 33.3428 | 0 | 0.0001 | 440410.1608 | 4820.9699
November | 15755.4181 | 19.3245 | 32.1371 | 0 | 0.0001 | 424219.6804 | 5990.9416
December | 18919.1281 | 22.1513 | 31.863 | 0 | 0.0001 | 420376.7463 | 7081.0856
Annual Sum or Average | 161364.9328 | 211.1421 | 413.5706 | 0 | 0.0018 | 5462080 | 62774.6374
Minimum of Months | 9626.1908 | 14.6943 | 29.5124 | 0 | 0.0001 | 389562.5472 | 3969.5771
Maximum of Months | 19449.6971 | 22.7604 | 41.6752 | 0 | 0.0002 | 550811.7761 | 7278.3756
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 151919000000 | 138330.471 | 02-JAN-08:09 | 75734.208 | 58341.44 | 3828.343 | 0 | 0 | 0 | 426.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 137267000000 | 147408.164 | 21-FEB-13:00 | 75734.208 | 51598.363 | 3828.343 | 0 | 16216.845 | 0 | 30.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 161195000000 | 153622.812 | 29-MAR-15:00 | 75734.208 | 50956.166 | 3931.47 | 0 | 22992.529 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 146952000000 | 148471.89 | 18-APR-15:00 | 75734.208 | 50956.166 | 3999.756 | 0 | 17773.321 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 165292000000 | 171382.445 | 05-MAY-15:50 | 75734.208 | 50956.166 | 4035.474 | 0 | 40648.158 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 172048000000 | 174214.992 | 28-JUN-15:20 | 75734.208 | 50956.166 | 4788.363 | 0 | 42727.815 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 177296000000 | 191003.919 | 24-JUL-15:09 | 75734.208 | 50956.166 | 5724.185 | 0 | 58580.921 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 194084000000 | 187494.456 | 07-AUG-15:09 | 75734.208 | 50956.166 | 5888.187 | 0 | 54907.456 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 165783000000 | 184763.803 | 01-SEP-15:00 | 75734.208 | 50956.166 | 5006.258 | 0 | 53058.731 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 155183000000 | 160800.963 | 17-OCT-12:00 | 75734.208 | 51598.363 | 4465.852 | 0 | 28992.707 | 0 | 9.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 149478000000 | 148208.549 | 03-NOV-12:00 | 75734.208 | 51598.363 | 3828.343 | 0 | 17024.91 | 0 | 22.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 148124000000 | 138247.823 | 11-DEC-08:09 | 75734.208 | 58341.44 | 3828.343 | 0 | 0 | 0 | 343.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1924620000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 137267000000 | 138247.823 |  | 75734.208 | 50956.166 | 3828.343 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 194084000000 | 191003.919 |  | 75734.208 | 58341.44 | 5888.187 | 0 | 58580.921 | 0 | 426.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 42193.49 | 11106.58 | 0 | 53300.07
Cost per Total Building Area ($/m2) | 8.47 | 2.23 | 0 | 10.7
Cost per Net Conditioned Building Area ($/m2) | 8.47 | 2.23 | 0 | 10.7

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3839.07 | 770.56 | 770.56
Net Site Energy | 3839.07 | 770.56 | 770.56
Total Source Energy | 9310.02 | 1868.66 | 1868.66
Net Source Energy | 9310.02 | 1868.66 | 1868.66
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1711.48 | 0 | 0 | 0 | 0
Cooling | 293.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 82.24 | 0 | 0 | 0 | 0 | 0
Pumps | 2.26 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 42.11 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2085.48 | 1753.59 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 281347.6 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 133017.18 | 97508.34 | 35508.84 | 0.73 | 3.07
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 154431.95 | 117954.76 | 36477.19 | 0.76 | 3.18
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 152564.85 | 116224.3 | 36340.55 | 0.76 | 3.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 39936.2 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 51369.08 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 49832.2 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8837.34 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10352.03 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7696.31 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12903 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11700.24 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12534.6 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11018.42 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14717.77 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11868.93 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12083.24 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11336.08 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15304.37 | -
VAV_1_HEATC | Coil:Heating:Gas | 33932.35 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 31127.35 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 31354.38 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.6 | 12384.72 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.44 | 15842.22 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.29 | 15556.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1640.35 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 73418.9824 | 114.3455 | 286.2701 | 0 | 0.0009 | 65877.528 | 29971.3165
February | 62781.2336 | 100.0584 | 258.4634 | 0 | 0.0008 | 59482.7095 | 25846.7877
March | 67709.2358 | 111.9398 | 302.8946 | 0 | 0.0009 | 69715.0354 | 28260.688
April | 56858.2397 | 98.3083 | 280.1771 | 0 | 0.0009 | 64493.1626 | 24143.5364
May | 63385.236 | 113.2622 | 334.3325 | 0 | 0.001 | 76964.3242 | 27265.838
June | 72445.3071 | 131.5514 | 394.7089 | 0 | 0.0012 | 90865.9921 | 31363.8937
July | 74406.904 | 135.2877 | 406.4418 | 0 | 0.0012 | 93567.2495 | 32229.8047
August | 78026.2412 | 141.7935 | 425.7624 | 0 | 0.0013 | 98014.9524 | 33790.3692
September | 64171.3189 | 115.8744 | 345.7181 | 0 | 0.001 | 79586.9618 | 27719.4415
October | 60462.7208 | 106.2458 | 308.1619 | 0 | 0.0009 | 70937.364 | 25837.147
November | 61234.1044 | 102.6399 | 282.3513 | 0 | 0.0009 | 64988.9655 | 25692.4163
December | 69069.4663 | 109.2206 | 279.1977 | 0 | 0.0009 | 64253.0167 | 28353.4324
Annual Sum or Average | 803968.9903 | 1380.5276 | 3904.4797 | 0 | 0.012 | 898747.2616 | 340474.6716
Minimum of Months | 56858.2397 | 98.3083 | 258.4634 | 0 | 0.0008 | 59482.7095 | 24143.5364
Maximum of Months | 78026.2412 | 141.7935 | 425.7624 | 0 | 0.0013 | 98014.9524 | 33790.3692
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 152864000000 | 138750.17 | 30-JAN-08:09 | 75734.208 | 58341.44 | 3789.322 | 0 | 0 | 0 | 885.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 138025000000 | 138342.935 | 06-FEB-08:09 | 75734.208 | 58341.44 | 3789.322 | 0 | 0 | 0 | 477.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 161768000000 | 159050.775 | 31-MAR-15:09 | 75734.208 | 50956.166 | 3789.322 | 0 | 28562.347 | 0 | 8.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 149652000000 | 164011.627 | 10-APR-07:00 | 75734.208 | 58341.44 | 3789.322 | 0 | 26099.918 | 0 | 46.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 178590000000 | 191796.158 | 30-MAY-15:00 | 75734.208 | 50956.166 | 4319.337 | 0 | 60778.008 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 210848000000 | 228192.952 | 08-JUN-12:00 | 75734.208 | 51598.363 | 5886.879 | 0 | 94965.062 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 217116000000 | 236297.589 | 03-JUL-15:30 | 75734.208 | 50956.166 | 8759.472 | 0 | 100839.303 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 227436000000 | 237396.915 | 04-AUG-15:50 | 75734.208 | 50956.166 | 7248.825 | 0 | 103449.276 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 184676000000 | 196829.065 | 06-SEP-12:30 | 75734.208 | 51598.363 | 5389.184 | 0 | 64098.87 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 164605000000 | 180792.128 | 30-OCT-12:09 | 75734.208 | 51598.363 | 4403.432 | 0 | 49045.824 | 0 | 10.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 150802000000 | 178136.964 | 02-NOV-15:09 | 75734.208 | 50956.166 | 3862.917 | 0 | 47575.234 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 149094000000 | 138447.193 | 26-DEC-08:09 | 75734.208 | 58341.44 | 3789.322 | 0 | 0 | 0 | 582.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2085480000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 138025000000 | 138342.935 |  | 75734.208 | 50956.166 | 3789.322 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 227436000000 | 237396.915 |  | 75734.208 | 58341.44 | 8759.472 | 0 | 103449.276 | 0 | 885.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 49183.25 | 14623.94 | 0 | 63807.19
Cost per Total Building Area ($/m2) | 9.87 | 2.94 | 0 | 12.81
Cost per Net Conditioned Building Area ($/m2) | 9.87 | 2.94 | 0 | 12.81

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3208.49 | 643.99 | 643.99
Net Site Energy | 3208.49 | 643.99 | 643.99
Total Source Energy | 7924.74 | 1590.62 | 1590.62
Net Source Energy | 7924.74 | 1590.62 | 1590.62
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1180.41 | 0 | 0 | 0 | 0
Cooling | 195.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 80.95 | 0 | 0 | 0 | 0 | 0
Pumps | 1.85 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.98 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1986.11 | 1222.39 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.354 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 231517.59 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116265.75 | 92856.25 | 23409.5 | 0.8 | 3.32
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 134762.55 | 107628.82 | 27133.73 | 0.8 | 3.32
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124238.28 | 99223.55 | 25014.72 | 0.8 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38522.55 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 40981.13 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 36068.54 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6647.85 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8349.98 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6612.22 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11537.4 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9196.96 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10331.23 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8267.78 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13300.18 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9766.16 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9085.07 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9758.65 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13352.84 | -
VAV_1_HEATC | Coil:Heating:Gas | 26173.53 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 24745.22 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 25554.91 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.02 | 13176.23 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.14 | 15272.44 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.51 | 14079.74 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1349.82 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 53934.0229 | 83.187 | 185.5039 | 0 | 0.0008 | 192823.1704 | 22024.313
February | 46192.6678 | 72.7348 | 166.9315 | 0 | 0.0007 | 173530.5375 | 19009.0348
March | 50680.9677 | 82.2826 | 196.577 | 0 | 0.0008 | 204367.8601 | 21099.3527
April | 43593.0962 | 73.2956 | 182.727 | 0 | 0.0007 | 189987.7197 | 18395.7769
May | 46626.006 | 79.991 | 204.0785 | 0 | 0.0008 | 212198.7409 | 19832.1858
June | 49005.9587 | 85.3111 | 221.1911 | 0 | 0.0009 | 230000.4161 | 20965.8337
July | 52637.5769 | 92.1775 | 240.5291 | 0 | 0.0009 | 250112.0515 | 22572.9183
August | 55066.633 | 96.3789 | 251.3455 | 0 | 0.001 | 261359.1088 | 23609.454
September | 45563.2608 | 79.0157 | 204.0162 | 0 | 0.0008 | 212139.4903 | 19463.3197
October | 45752.3683 | 77.4735 | 194.7409 | 0 | 0.0008 | 202482.8583 | 19360.6632
November | 47255.9699 | 76.3837 | 181.4614 | 0 | 0.0007 | 188650.6502 | 19640.2844
December | 52504.0483 | 80.9418 | 180.3713 | 0 | 0.0007 | 187487.7727 | 21436.4913
Annual Sum or Average | 588812.5767 | 979.1732 | 2409.4735 | 0 | 0.0095 | 2505140 | 247409.6279
Minimum of Months | 43593.0962 | 72.7348 | 166.9315 | 0 | 0.0007 | 173530.5375 | 18395.7769
Maximum of Months | 55066.633 | 96.3789 | 251.3455 | 0 | 0.001 | 261359.1088 | 23609.454
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 152873000000 | 146105.677 | 24-JAN-13:00 | 75734.208 | 51598.363 | 3867.329 | 0 | 14894.001 | 0 | 11.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 137577000000 | 140218.144 | 07-FEB-13:00 | 75734.208 | 51598.363 | 4444.142 | 0 | 8421.551 | 0 | 19.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 162025000000 | 153811.092 | 30-MAR-12:00 | 75734.208 | 51598.363 | 4294.615 | 0 | 22175.114 | 0 | 8.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 150625000000 | 161266.471 | 26-APR-15:00 | 75734.208 | 50956.166 | 4996.526 | 0 | 29571.131 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 168234000000 | 179679.692 | 24-MAY-15:00 | 75734.208 | 50956.166 | 6512.432 | 0 | 46468.447 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 182347000000 | 196406.577 | 27-JUN-15:00 | 75734.208 | 50956.166 | 8905.199 | 0 | 60802.565 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 198292000000 | 215529.298 | 17-JUL-15:30 | 75734.208 | 50956.166 | 12793.012 | 0 | 76037.473 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 207209000000 | 209051.967 | 30-AUG-13:00 | 75734.208 | 48066.275 | 10610.116 | 0 | 74632.928 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 168187000000 | 187519.865 | 01-SEP-15:00 | 75734.208 | 50956.166 | 8146.025 | 0 | 52675.026 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 160531000000 | 171730.689 | 05-OCT-15:20 | 75734.208 | 50956.166 | 5783.746 | 0 | 39248.13 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 149565000000 | 155600.794 | 10-NOV-13:00 | 75734.208 | 51598.363 | 4610.04 | 0 | 23649.28 | 0 | 8.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 148643000000 | 139668.017 | 21-DEC-13:00 | 75734.208 | 51598.363 | 4404.931 | 0 | 7911.091 | 0 | 19.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1986110000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 137577000000 | 139668.017 |  | 75734.208 | 48066.275 | 3867.329 | 0 | 7911.091 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 207209000000 | 215529.298 |  | 75734.208 | 51598.363 | 12793.012 | 0 | 76037.473 | 0 | 19.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20565.49 | 8445.57 | 0 | 29011.06
Cost per Total Building Area ($/m2) | 4.13 | 1.7 | 0 | 5.82
Cost per Net Conditioned Building Area ($/m2) | 4.13 | 1.7 | 0 | 5.82

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4258.89 | 854.82 | 854.82
Net Site Energy | 4258.89 | 854.82 | 854.82
Total Source Energy | 9454.84 | 1897.73 | 1897.73
Net Source Energy | 9454.84 | 1897.73 | 1897.73
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2165.78 | 0 | 0 | 0 | 0
Cooling | 254.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 83.8 | 0 | 0 | 0 | 0 | 0
Pumps | 2.95 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 44.44 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2048.67 | 2210.22 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 282155.17 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 131007.18 | 96599.25 | 34407.92 | 0.74 | 3.09
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 153191.47 | 117750.7 | 35440.77 | 0.77 | 3.2
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 151356.55 | 116070.14 | 35286.41 | 0.77 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 39598.35 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 51318.96 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 50112.53 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9274.92 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10183.69 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8344.85 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12324.98 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12249.6 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12378.8 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11089.35 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14170.9 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12396.36 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11991.2 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12366.95 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14503.48 | -
VAV_1_HEATC | Coil:Heating:Gas | 39349.05 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 36473.48 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 36688.96 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.59 | 12371.53 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.5 | 15944.12 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.35 | 15669.87 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1645.06 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 62692.8087 | 87.7785 | 100.8129 | 0 | 0.0008 | 66170.7089 | 24649.0299
February | 51017.4796 | 74.1636 | 90.9348 | 0 | 0.0007 | 59705.7778 | 20319.7822
March | 48541.6402 | 76.4261 | 105.6083 | 0 | 0.0008 | 69376.2778 | 19893.9722
April | 38260.4856 | 64.8005 | 98.0934 | 0 | 0.0007 | 64462.725 | 16116.4345
May | 41608.7272 | 74.0045 | 118.1823 | 0 | 0.0009 | 77679.4778 | 17864.5357
June | 45303.0733 | 82.2119 | 134.0047 | 0 | 0.001 | 88085.6549 | 19607.1314
July | 46041.0122 | 83.7998 | 136.9974 | 0 | 0.001 | 90053.8099 | 19950.2872
August | 49781.9016 | 90.5644 | 147.9846 | 0 | 0.0011 | 97275.9304 | 21567.0437
September | 39254.9766 | 70.2064 | 112.7608 | 0 | 0.0008 | 74117.5443 | 16891.067
October | 39614.9369 | 67.1187 | 101.6447 | 0 | 0.0008 | 66796.5919 | 16689.2799
November | 45745.7134 | 71.6851 | 98.4216 | 0 | 0.0007 | 64653.4642 | 18715.7053
December | 56358.2206 | 81.252 | 98.2552 | 0 | 0.0008 | 64507.989 | 22382.3931
Annual Sum or Average | 564220.9759 | 924.0115 | 1343.7006 | 0 | 0.01 | 882885.9519 | 234646.6623
Minimum of Months | 38260.4856 | 64.8005 | 90.9348 | 0 | 0.0007 | 59705.7778 | 16116.4345
Maximum of Months | 62692.8087 | 90.5644 | 147.9846 | 0 | 0.0011 | 97275.9304 | 24649.0299
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 153544000000 | 139215.937 | 02-JAN-08:09 | 75734.208 | 58341.44 | 3831.191 | 0 | 0 | 0 | 1309.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 138543000000 | 138773.101 | 07-FEB-08:09 | 75734.208 | 58341.44 | 3831.191 | 0 | 0 | 0 | 866.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 160982000000 | 148573.144 | 23-MAR-15:00 | 75734.208 | 50956.166 | 3831.191 | 0 | 18038.628 | 0 | 12.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 149581000000 | 158325.664 | 14-APR-15:00 | 75734.208 | 50956.166 | 3858.234 | 0 | 27768.616 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 180249000000 | 191010.543 | 31-MAY-12:09 | 75734.208 | 51598.363 | 4734.3 | 0 | 58935.231 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 204396000000 | 222931.976 | 29-JUN-15:00 | 75734.208 | 50956.166 | 6775.413 | 0 | 89457.75 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 208963000000 | 224153.086 | 13-JUL-15:00 | 75734.208 | 50956.166 | 6135.508 | 0 | 91318.764 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 225721000000 | 219421.074 | 25-AUG-15:00 | 75734.208 | 50956.166 | 6110.171 | 0 | 86612.089 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 171984000000 | 190625.511 | 14-SEP-15:09 | 75734.208 | 50956.166 | 5058.316 | 0 | 58868.381 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 154996000000 | 163145.906 | 06-OCT-15:20 | 75734.208 | 50956.166 | 4126.16 | 0 | 32320.813 | 0 | 8.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 150023000000 | 154237.981 | 02-NOV-15:09 | 75734.208 | 50956.166 | 4125.701 | 0 | 23410.725 | 0 | 11.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 149686000000 | 138649.662 | 20-DEC-08:09 | 75734.208 | 58341.44 | 3831.191 | 0 | 0 | 0 | 742.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2048670000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 138543000000 | 138649.662 |  | 75734.208 | 50956.166 | 3831.191 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 225721000000 | 224153.086 |  | 75734.208 | 58341.44 | 6775.413 | 0 | 91318.764 | 0 | 1309.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37253.93 | 17411.36 | 0 | 54665.28
Cost per Total Building Area ($/m2) | 7.48 | 3.49 | 0 | 10.97
Cost per Net Conditioned Building Area ($/m2) | 7.48 | 3.49 | 0 | 10.97

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3699.72 | 742.59 | 742.59
Net Site Energy | 3699.72 | 742.59 | 742.59
Total Source Energy | 8631.86 | 1732.54 | 1732.54
Net Source Energy | 8631.86 | 1732.54 | 1732.54
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1728.79 | 0 | 0 | 0 | 0
Cooling | 135.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 80.5 | 0 | 0 | 0 | 0 | 0
Pumps | 2.58 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 44.86 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1926.07 | 1773.65 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 243840.99 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 112880.09 | 90152.27 | 22727.81 | 0.8 | 3.32
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 132996.2 | 106218.11 | 26778.08 | 0.8 | 3.32
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122378.42 | 97738.17 | 24640.25 | 0.8 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38379.58 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41614.81 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 36616.73 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8406.75 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8586.7 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8047.29 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11375.77 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11370.14 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10744.01 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8586.75 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13276.7 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12068.79 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9621.99 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12017.72 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13351.86 | -
VAV_1_HEATC | Coil:Heating:Gas | 36079.86 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 34439.57 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 35301.32 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.82 | 12792.54 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.03 | 15072.27 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.39 | 13868.97 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1421.67 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 56989.983 | 83.0196 | 113.4178 | 0 | 0.0008 | 2688090 | 22748.8786
February | 47808.6215 | 71.6593 | 102.4313 | 0 | 0.0007 | 2428160 | 19278.6614
March | 48034.2742 | 76.715 | 119.9753 | 0 | 0.0009 | 2845010 | 19825.6577
April | 39995.5489 | 65.9763 | 107.4913 | 0 | 0.0008 | 2549350 | 16710.7405
May | 41236.9159 | 70.6236 | 120.2287 | 0 | 0.0008 | 2851860 | 17480.6815
June | 43462.8617 | 75.9239 | 132.1004 | 0 | 0.0009 | 3133690 | 18568.1265
July | 43812.5622 | 77.5243 | 136.7416 | 0 | 0.0009 | 3243930 | 18813.1691
August | 45699.9341 | 80.6229 | 141.7605 | 0 | 0.001 | 3362960 | 19600.31
September | 39732.7275 | 68.9475 | 119.098 | 0 | 0.0008 | 2825180 | 16930.0411
October | 41469.7116 | 69.2637 | 114.5474 | 0 | 0.0008 | 2716840 | 17409.3711
November | 45397.9488 | 71.7401 | 110.626 | 0 | 0.0008 | 2623170 | 18663.6491
December | 53512.1283 | 79.0951 | 110.6259 | 0 | 0.0008 | 2622180 | 21470.9883
Annual Sum or Average | 547153.2176 | 891.1112 | 1429.0444 | 0 | 0.0101 | 33890400 | 227500.2748
Minimum of Months | 39732.7275 | 65.9763 | 102.4313 | 0 | 0.0007 | 2428160 | 16710.7405
Maximum of Months | 56989.983 | 83.0196 | 141.7605 | 0 | 0.001 | 3362960 | 22748.8786
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 152771000000 | 140890.214 | 17-JAN-08:09 | 75734.208 | 58341.44 | 3712.142 | 0 | 0 | 2179 | 923.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 137998000000 | 144618.496 | 02-FEB-14:00 | 75734.208 | 48066.275 | 3717.655 | 0 | 17085.864 | 0 | 14.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 161689000000 | 151772.156 | 30-MAR-15:09 | 75734.208 | 50956.166 | 4008.565 | 0 | 21064.778 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 144885000000 | 148152.312 | 06-APR-15:00 | 75734.208 | 50956.166 | 3725.329 | 0 | 17728.17 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 162078000000 | 159436.42 | 16-MAY-15:00 | 75734.208 | 50956.166 | 4028.829 | 0 | 28708.777 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 178095000000 | 201145.797 | 26-JUN-15:20 | 75734.208 | 50956.166 | 8550.934 | 0 | 65896.05 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 184360000000 | 202904.171 | 21-JUL-15:00 | 75734.208 | 50956.166 | 9318.991 | 0 | 66886.366 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 191125000000 | 193737.074 | 09-AUG-15:00 | 75734.208 | 50956.166 | 7858.189 | 0 | 59180.072 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 160562000000 | 177569.328 | 12-SEP-12:00 | 75734.208 | 51598.363 | 5229.469 | 0 | 44998.848 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 154404000000 | 159606.541 | 06-OCT-15:09 | 75734.208 | 50956.166 | 4641.391 | 0 | 28266.336 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 149081000000 | 140110.124 | 03-NOV-07:10 | 75734.208 | 58341.44 | 3712.142 | 0 | 0 | 2179 | 143.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 149025000000 | 140836.015 | 18-DEC-08:09 | 75734.208 | 58341.44 | 3712.142 | 0 | 0 | 2179 | 869.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1926070000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 137998000000 | 140110.124 |  | 75734.208 | 48066.275 | 3712.142 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 191125000000 | 202904.171 |  | 75734.208 | 58341.44 | 9318.991 | 0 | 66886.366 | 2179 | 923.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43470.48 | 14352.02 | 0 | 57822.49
Cost per Total Building Area ($/m2) | 8.73 | 2.88 | 0 | 11.61
Cost per Net Conditioned Building Area ($/m2) | 8.73 | 2.88 | 0 | 11.61

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4592.84 | 921.85 | 921.85
Net Site Energy | 4592.84 | 921.85 | 921.85
Total Source Energy | 9537.92 | 1914.4 | 1914.4
Net Source Energy | 9537.92 | 1914.4 | 1914.4
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2615.97 | 0 | 0 | 0 | 0
Cooling | 128.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 88.52 | 0 | 0 | 0 | 0 | 0
Pumps | 3.55 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 48.27 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1928.59 | 2664.25 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 195.85 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 456.98 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 285323.37 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122151.23 | 94161.95 | 27989.29 | 0.77 | 3.21
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 145097.1 | 115882.56 | 29214.54 | 0.8 | 3.32
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 138827.73 | 110548.08 | 28279.66 | 0.8 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38553.8 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 49638.53 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 46529.29 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10794.16 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10666.05 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8790.02 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13324.9 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14291.44 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13274.29 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9428.63 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15568.36 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13684 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12466.37 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13014.13 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15470.84 | -
VAV_1_HEATC | Coil:Heating:Gas | 41273.32 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 38399.41 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 39033.42 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.82 | 12796.79 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.77 | 16443.64 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.33 | 15632.22 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1663.53 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 63081.2386 | 88.2064 | 101.0599 | 0 | 0.0008 | 66332.0433 | 24790.6648
February | 53583.3703 | 76.5782 | 91.225 | 0 | 0.0007 | 59888.1375 | 21216.0114
March | 52850.6567 | 80.3877 | 105.7917 | 0 | 0.0008 | 69482.4692 | 21390.1318
April | 40535.5148 | 66.0188 | 95.3467 | 0 | 0.0007 | 62646.3759 | 16822.8869
May | 39552.5368 | 68.0141 | 104.7444 | 0 | 0.0008 | 68837.8822 | 16758.685
June | 40034.71 | 71.8225 | 115.7221 | 0 | 0.0008 | 76064.853 | 17247.7594
July | 43002.2364 | 77.8366 | 126.5478 | 0 | 0.0009 | 83183.2711 | 18592.2183
August | 43634.9361 | 78.4308 | 126.6157 | 0 | 0.0009 | 83225.8242 | 18813.1038
September | 37179.3317 | 64.7873 | 101.2409 | 0 | 0.0007 | 66538.9841 | 15834.7902
October | 40546.0356 | 67.4198 | 99.8775 | 0 | 0.0007 | 65629.7664 | 16959.531
November | 48624.7854 | 74.2613 | 98.3138 | 0 | 0.0007 | 64572.7668 | 19708.6046
December | 58928.5357 | 83.6907 | 98.6108 | 0 | 0.0008 | 64733.4422 | 23282.0748
Annual Sum or Average | 561553.888 | 897.4542 | 1265.0963 | 0 | 0.0095 | 831135.8159 | 231416.4619
Minimum of Months | 37179.3317 | 64.7873 | 91.225 | 0 | 0.0007 | 59888.1375 | 15834.7902
Maximum of Months | 63081.2386 | 88.2064 | 126.6157 | 0 | 0.0009 | 83225.8242 | 24790.6648
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 153919000000 | 139104.474 | 09-JAN-08:09 | 75734.208 | 58341.44 | 3961.27 | 0 | 0 | 0 | 1067.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 138966000000 | 138965.514 | 02-FEB-08:09 | 75734.208 | 58341.44 | 3961.27 | 0 | 0 | 0 | 928.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 161229000000 | 138733.481 | 07-MAR-08:09 | 75734.208 | 58341.44 | 3961.27 | 0 | 0 | 0 | 696.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 145366000000 | 147470.972 | 04-APR-15:09 | 75734.208 | 50956.166 | 4004.647 | 0 | 16762.821 | 0 | 13.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 159733000000 | 162019.071 | 31-MAY-15:00 | 75734.208 | 50956.166 | 4426.256 | 0 | 30894.001 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 176503000000 | 192066.486 | 14-JUN-15:00 | 75734.208 | 50956.166 | 5032.383 | 0 | 60335.29 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 193021000000 | 212744.892 | 11-JUL-15:00 | 75734.208 | 50956.166 | 6062.957 | 0 | 79983.121 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 193119000000 | 197541.233 | 11-AUG-15:39 | 75734.208 | 50956.166 | 5463.932 | 0 | 65378.487 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 154399000000 | 188944.518 | 07-SEP-15:09 | 75734.208 | 50956.166 | 4758.034 | 0 | 57487.671 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 152289000000 | 153993.786 | 27-OCT-12:39 | 75734.208 | 51598.363 | 4707.966 | 0 | 21936.366 | 0 | 16.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 149836000000 | 138720.68 | 27-NOV-08:09 | 75734.208 | 58341.44 | 3961.27 | 0 | 0 | 0 | 683.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 150209000000 | 138917.386 | 21-DEC-08:09 | 75734.208 | 58341.44 | 3961.27 | 0 | 0 | 0 | 880.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1928590000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 138966000000 | 138720.68 |  | 75734.208 | 50956.166 | 3961.27 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 193119000000 | 212744.892 |  | 75734.208 | 58341.44 | 6062.957 | 0 | 79983.121 | 0 | 1067.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34924.65 | 20969.01 | 0 | 55893.65
Cost per Total Building Area ($/m2) | 7.01 | 4.21 | 0 | 11.22
Cost per Net Conditioned Building Area ($/m2) | 7.01 | 4.21 | 0 | 11.22

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6422.44 | 1289.08 | 1289.08
Net Site Energy | 6422.44 | 1289.08 | 1289.08
Total Source Energy | 11722.37 | 2352.86 | 2352.86
Net Source Energy | 11722.37 | 2352.86 | 2352.86
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4470.72 | 0 | 0 | 0 | 0
Cooling | 83.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 33.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 101.72 | 0 | 0 | 0 | 0 | 0
Pumps | 6.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 52.91 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1898.82 | 4523.62 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.616 | 0.541 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.616 | 0.541 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 2.956 | 0.616 | 0.541 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 195.85 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 456.98 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 335831.86 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 123035.93 | 98263.29 | 24772.64 | 0.8 | 3.32
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 164855.16 | 131662.44 | 33192.72 | 0.8 | 3.2
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 154140.36 | 123105.01 | 31035.35 | 0.8 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 35902.62 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 51080.21 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 46889.3 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20092.08 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12601.36 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11643.22 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14493.16 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24895.63 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15894.18 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12283.46 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 17392 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24010.76 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14889.28 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16985.32 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16942.3 | -
VAV_1_HEATC | Coil:Heating:Gas | 56179.95 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 52312.43 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 53295.12 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.43 | 13943.48 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.96 | 17132.88 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.31 | 17468.5 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1958.01 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.78 | 1.76 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 77436.7108 | 80.8699 | 221.4817 | 0 | 0.0008 | 44404.6612 | 28428.3841
February | 65334.1805 | 68.8305 | 199.4136 | 0 | 0.0008 | 39984.7693 | 24077.6222
March | 59751.084 | 65.2516 | 230.5536 | 0 | 0.0008 | 46245.0274 | 22374.4794
April | 41708.4164 | 47.7176 | 206.3245 | 0 | 0.0007 | 41397.2478 | 15952.0625
May | 35199.9903 | 42.6381 | 223.6417 | 0 | 0.0008 | 44882.1213 | 13827.0066
June | 35970.5985 | 44.5319 | 248.6281 | 0 | 0.0008 | 49899.8581 | 14277.4876
July | 35882.019 | 44.5063 | 249.7762 | 0 | 0.0008 | 50130.5392 | 14255.2767
August | 37470.2667 | 45.9318 | 249.4396 | 0 | 0.0008 | 50061.2909 | 14802.4608
September | 35524.9627 | 42.1518 | 207.2968 | 0 | 0.0007 | 41598.9215 | 13819.2475
October | 48315.6234 | 54.2239 | 216.9834 | 0 | 0.0008 | 43531.2633 | 18317.0839
November | 63570.4783 | 68.0334 | 216.2272 | 0 | 0.0008 | 43363.6169 | 23590.9148
December | 71304.7791 | 75.0603 | 216.3733 | 0 | 0.0008 | 43384.9701 | 26268.6727
Annual Sum or Average | 607469.1098 | 679.7472 | 2686.1397 | 0 | 0.0096 | 538884.2871 | 229990.6987
Minimum of Months | 35199.9903 | 42.1518 | 199.4136 | 0 | 0.0007 | 39984.7693 | 13819.2475
Maximum of Months | 77436.7108 | 80.8699 | 249.7762 | 0 | 0.0008 | 50130.5392 | 28428.3841
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 156465000000 | 142506.42 | 02-JAN-08:09 | 75734.208 | 58341.44 | 4375.323 | 0 | 0 | 2179 | 1876.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 140891000000 | 141763.675 | 03-FEB-08:09 | 75734.208 | 58341.44 | 4375.323 | 0 | 0 | 2179 | 1133.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 162949000000 | 141633.703 | 14-MAR-07:10 | 75734.208 | 58341.44 | 4375.323 | 0 | 0 | 2179 | 1003.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 145868000000 | 138909.486 | 10-APR-07:10 | 75734.208 | 58341.44 | 4375.323 | 0 | 0 | 0 | 458.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 158147000000 | 157522.227 | 30-MAY-12:39 | 75734.208 | 51598.363 | 4914.671 | 0 | 25266.545 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 175828000000 | 185054.551 | 21-JUN-15:39 | 75734.208 | 50956.166 | 5505.315 | 0 | 52850.422 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 176640000000 | 182348.709 | 11-JUL-15:00 | 75734.208 | 50956.166 | 5773.695 | 0 | 49876.2 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 176396000000 | 181967.511 | 15-AUG-12:00 | 75734.208 | 51598.363 | 5987.649 | 0 | 48638.851 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 146578000000 | 147242.574 | 07-SEP-15:00 | 75734.208 | 50956.166 | 4475.584 | 0 | 16065.097 | 0 | 11.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 153387000000 | 141147.3 | 30-OCT-07:10 | 75734.208 | 58341.44 | 4375.323 | 0 | 0 | 2179 | 517.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 152796000000 | 141608.022 | 06-NOV-08:09 | 75734.208 | 58341.44 | 4375.323 | 0 | 0 | 2179 | 978.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 152872000000 | 141704.951 | 29-DEC-08:09 | 75734.208 | 58341.44 | 4375.323 | 0 | 0 | 2179 | 1074.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1898820000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 140891000000 | 138909.486 |  | 75734.208 | 50956.166 | 4375.323 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 176640000000 | 185054.551 |  | 75734.208 | 58341.44 | 5987.649 | 0 | 52850.422 | 2179 | 1876.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 55298.58 | 18655.77 | 0 | 73954.35
Cost per Total Building Area ($/m2) | 11.1 | 3.74 | 0 | 14.84
Cost per Net Conditioned Building Area ($/m2) | 11.1 | 3.74 | 0 | 14.84

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720