## BuildingSummary
Building Summary Medium Office pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Medium Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.75222 | See Benchmark Technical Report
HVAC
| System Type | SZ-CAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.59

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0702 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0701 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 8.07 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0702 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0701 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 8.07 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0702 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 8.0701 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 8.0698 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 8.07 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 3.7565
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.7218 | 652.8006 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ_1:1_COOLC DXCOIL | 79.2487 | 76.9145 | 68.9888 | 74.1329 | 62.2596 | 62.0809 | 48.8721 | 66.4926 | 64.3513 | 53.9159 | 66.4768 | 62.6821 | 65.751 | 59.0983 | 58.869 | 46.6789
| PSZ_1:2_COOLC DXCOIL | 20.6518 | 23.2659 | 25.2939 | 24.2701 | 23.7892 | 23.6667 | 31.1898 | 26.8135 | 20.8189 | 31.2438 | 22.5511 | 18.0643 | 24.3651 | 21.4616 | 24.4804 | 27.2174
| PSZ_1:3_COOLC DXCOIL | 24.918 | 24.5559 | 25.2219 | 24.6274 | 21.829 | 24.0517 | 18.0754 | 22.883 | 23.4705 | 20.2662 | 17.1573 | 15.888 | 16.9158 | 15.3289 | 14.2355 | 18.0293
| PSZ_1:4_COOLC DXCOIL | 21.6007 | 21.172 | 20.262 | 19.5393 | 13.0819 | 18.161 | 9.5432 | 18.9271 | 15.6305 | 13.2227 | 24.584 | 18.9066 | 27.2591 | 21.7838 | 28.3159 | 26.9849
| PSZ_1:5_COOLC DXCOIL | 29.1027 | 29.7489 | 31.1153 | 29.9752 | 27.2292 | 31.3939 | 24.5676 | 28.1721 | 31.2925 | 25.8417 | 21.186 | 21.7577 | 20.4 | 20.4218 | 18.3815 | 18.0291
| PSZ_2:1_COOLC DXCOIL | 76.0657 | 71.9307 | 77.6034 | 72.8101 | 69.814 | 66.3468 | 64.4886 | 77.2439 | 67.6217 | 67.3761 | 76.3335 | 67.4097 | 76.0583 | 65.3582 | 68.5757 | 67.6609
| PSZ_2:2_COOLC DXCOIL | 23.409 | 26.0937 | 29.7623 | 27.2982 | 26.5166 | 28.584 | 35.6356 | 29.8496 | 24.946 | 35.7482 | 22.8263 | 19.4414 | 24.7358 | 23.017 | 24.6802 | 28.8802
| PSZ_2:3_COOLC DXCOIL | 26.722 | 26.4656 | 28.9648 | 27.1541 | 23.8667 | 27.9109 | 20.9322 | 25.3573 | 26.477 | 23.1631 | 19.5675 | 18.8739 | 19.2396 | 18.4695 | 17.495 | 19.0874
| PSZ_2:4_COOLC DXCOIL | 24.2984 | 23.9757 | 24.5392 | 22.48 | 15.5452 | 22.4535 | 12.9489 | 21.8934 | 19.3871 | 15.1674 | 22.2122 | 19.3675 | 24.9926 | 22.7694 | 27.2568 | 28.6762
| PSZ_2:5_COOLC DXCOIL | 30.8311 | 31.6316 | 34.4967 | 32.2708 | 29.065 | 34.7484 | 27.0606 | 30.4071 | 34.0559 | 28.5488 | 23.2656 | 24.5351 | 22.442 | 23.2678 | 21.2537 | 19.3271
| PSZ_3:1_COOLC DXCOIL | 75.5021 | 85.2749 | 78.6003 | 81.9798 | 65.4937 | 79.9882 | 54.247 | 73.7821 | 66.3859 | 59.7693 | 73.432 | 58.3101 | 73.6431 | 55.4967 | 61.6455 | 68.6152
| PSZ_3:2_COOLC DXCOIL | 25.6006 | 28.4459 | 32.838 | 29.4801 | 27.2364 | 31.2711 | 35.6549 | 31.1278 | 25.8652 | 36.1273 | 30.3304 | 26.5159 | 33.0474 | 31.2177 | 33.4039 | 39.1521
| PSZ_3:3_COOLC DXCOIL | 26.2196 | 25.8245 | 28.7128 | 26.4033 | 22.4224 | 27.0422 | 19.0938 | 24.4054 | 24.1534 | 21.5879 | 18.8453 | 17.3403 | 19.1543 | 20.4211 | 20.336 | 25.5822
| PSZ_3:4_COOLC DXCOIL | 26.8857 | 26.8886 | 28.1316 | 25.2052 | 17.0373 | 26.2395 | 13.8342 | 24.1892 | 22.2472 | 17.2942 | 31.5077 | 26.4861 | 35.2277 | 31.0339 | 36.1192 | 39.0244
| PSZ_3:5_COOLC DXCOIL | 32.6894 | 33.9182 | 37.4331 | 34.481 | 30.122 | 37.2483 | 27.5709 | 32.0514 | 35.6173 | 29.5073 | 24.4051 | 25.5114 | 23.2167 | 23.7934 | 21.7356 | 25.5816
Heating (kW)
| PSZ_1:1_HEATC | 95.2815 | 100.1746 | 89.008 | 101.4599 | 83.2864 | 88.1583 | 78.9376 | 95.3893 | 89.3132 | 89.0588 | 100.5536 | 92.2934 | 102.6743 | 97.9906 | 101.0509 | 103.8004
| PSZ_1:2_HEATC | 23.457 | 28.7353 | 32.2868 | 31.9411 | 34.6388 | 32.7733 | 45.7079 | 36.7953 | 27.1216 | 46.1826 | 29.3228 | 24.9957 | 33.0547 | 31.5121 | 34.7492 | 45.6493
| PSZ_1:3_HEATC | 34.6494 | 35.2559 | 35.1409 | 35.2929 | 31.4356 | 32.6619 | 26.6178 | 34.2342 | 28.9298 | 29.9037 | 25.5929 | 20.9031 | 25.8431 | 22.0489 | 22.852 | 29.992
| PSZ_1:4_HEATC | 25.5513 | 26.5702 | 26.0086 | 25.7778 | 17.1729 | 25.0152 | 14.2397 | 25.4238 | 21.1926 | 19.7104 | 29.1097 | 24.8803 | 32.7165 | 31.189 | 34.3998 | 45.3314
| PSZ_1:5_HEATC | 40.8902 | 42.8137 | 43.0046 | 42.4507 | 38.909 | 42.0853 | 35.6321 | 41.6521 | 37.8683 | 37.5396 | 31.0025 | 27.5989 | 30.7159 | 28.1852 | 28.325 | 29.9915
| PSZ_2:1_HEATC | 92.8309 | 98.7425 | 108.5984 | 101.2141 | 101.8983 | 98.2866 | 100.9178 | 117.4786 | 93.0489 | 108.3404 | 122.2283 | 97.6838 | 125.012 | 105.5287 | 120.8966 | 132.4708
| PSZ_2:2_HEATC | 27.749 | 33.1615 | 39.1871 | 36.7065 | 38.6335 | 39.5174 | 51.8808 | 41.6491 | 31.8377 | 52.3514 | 31.3663 | 26.5665 | 35.1665 | 33.386 | 36.9209 | 47.9226
| PSZ_2:3_HEATC | 37.6241 | 38.4086 | 40.1352 | 38.6748 | 34.2556 | 37.6151 | 30.5845 | 37.7622 | 32.3654 | 33.8712 | 29.5547 | 24.3092 | 29.6527 | 25.833 | 27.1549 | 31.4387
| PSZ_2:4_HEATC | 29.8247 | 31.0104 | 32.71 | 30.4304 | 21.0754 | 31.6492 | 19.6275 | 30.1314 | 25.4854 | 23.3118 | 31.1938 | 26.4823 | 34.9123 | 33.0877 | 36.6721 | 47.6436
| PSZ_2:5_HEATC | 43.724 | 45.7718 | 47.5166 | 45.5231 | 41.4496 | 46.3907 | 39.0934 | 44.7407 | 41.0262 | 41.247 | 34.3699 | 30.7671 | 34.0327 | 31.6141 | 32.1166 | 31.7661
| PSZ_3:1_HEATC | 90.3578 | 106.6658 | 107.6526 | 108.0345 | 92.8749 | 107.2711 | 85.5624 | 111.7671 | 91.6374 | 97.9265 | 117.3811 | 87.3086 | 121.0653 | 93.6536 | 111.7535 | 133.7748
| PSZ_3:2_HEATC | 31.1624 | 36.8046 | 43.8636 | 40.1305 | 39.6297 | 42.9661 | 51.9076 | 43.6241 | 32.8879 | 52.8706 | 40.195 | 34.6364 | 44.9993 | 43.266 | 47.4286 | 61.966
| PSZ_3:3_HEATC | 36.7283 | 37.2465 | 39.799 | 37.6697 | 32.257 | 36.5001 | 28.032 | 36.4465 | 29.7099 | 31.7138 | 28.3651 | 22.5594 | 29.3224 | 28.1839 | 30.9048 | 40.3182
| PSZ_3:4_HEATC | 33.9649 | 35.6724 | 38.3896 | 34.7055 | 23.4971 | 36.5084 | 21.1083 | 33.7668 | 28.7535 | 26.5513 | 40.092 | 34.6023 | 44.8591 | 43.0447 | 47.3074 | 61.7915
| PSZ_3:5_HEATC | 46.5098 | 48.9365 | 51.4349 | 48.4812 | 42.9125 | 49.5992 | 39.8022 | 47.0126 | 42.8101 | 42.5597 | 36.2199 | 31.8805 | 35.2003 | 32.2468 | 32.7521 | 40.3171
HVAC Efficiency
Air Conditioning (COP)
| PSZ_1:1_COOLC DXCOIL | 3.52 | 3.54 | 3.82 | 3.62 | 3.24 | 4.02 | 3.35 | 3.21 | 4.17 | 3.34 | 3.22 | 4.17 | 3.22 | 4.17 | 3.28 | 3.35
| PSZ_1:2_COOLC DXCOIL | 3.37 | 3.4 | 3.49 | 3.47 | 3.59 | 3.58 | 3.56 | 3.48 | 3.6 | 3.56 | 3.39 | 3.61 | 3.43 | 3.6 | 3.48 | 3.6
| PSZ_1:3_COOLC DXCOIL | 3.57 | 3.58 | 3.6 | 3.6 | 3.6 | 3.6 | 3.61 | 3.59 | 3.6 | 3.6 | 3.56 | 3.61 | 3.57 | 3.61 | 3.63 | 3.61
| PSZ_1:4_COOLC DXCOIL | 3.4 | 3.41 | 3.48 | 3.45 | 3.47 | 3.56 | 3.52 | 3.43 | 3.61 | 3.53 | 3.33 | 3.56 | 3.34 | 3.57 | 3.36 | 3.6
| PSZ_1:5_COOLC DXCOIL | 3.58 | 3.55 | 3.56 | 3.56 | 3.6 | 3.56 | 3.6 | 3.6 | 3.56 | 3.6 | 3.55 | 3.6 | 3.57 | 3.6 | 3.61 | 3.61
| PSZ_2:1_COOLC DXCOIL | 3.54 | 3.61 | 3.8 | 3.64 | 4.07 | 4.16 | 4.17 | 3.74 | 4.17 | 4.17 | 3.77 | 4.17 | 3.79 | 4.17 | 4.17 | 4.17
| PSZ_2:2_COOLC DXCOIL | 3.41 | 3.44 | 3.53 | 3.5 | 3.6 | 3.6 | 3.56 | 3.5 | 3.6 | 3.56 | 3.44 | 3.6 | 3.47 | 3.6 | 3.53 | 3.6
| PSZ_2:3_COOLC DXCOIL | 3.58 | 3.59 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.58 | 3.61 | 3.59 | 3.61 | 3.61 | 3.61
| PSZ_2:4_COOLC DXCOIL | 3.44 | 3.44 | 3.53 | 3.49 | 3.52 | 3.6 | 3.59 | 3.46 | 3.6 | 3.59 | 3.45 | 3.6 | 3.46 | 3.6 | 3.45 | 3.6
| PSZ_2:5_COOLC DXCOIL | 3.55 | 3.56 | 3.56 | 3.56 | 3.6 | 3.56 | 3.6 | 3.56 | 3.56 | 3.6 | 3.57 | 3.6 | 3.59 | 3.6 | 3.6 | 3.6
| PSZ_3:1_COOLC DXCOIL | 3.51 | 3.5 | 3.76 | 3.58 | 3.99 | 3.75 | 3.34 | 3.71 | 4.17 | 4.17 | 3.75 | 4.17 | 3.77 | 3.35 | 4.17 | 4.17
| PSZ_3:2_COOLC DXCOIL | 3.43 | 3.46 | 3.51 | 3.52 | 3.6 | 3.56 | 3.56 | 3.51 | 3.6 | 3.56 | 3.45 | 3.6 | 3.47 | 3.56 | 3.49 | 3.56
| PSZ_3:3_COOLC DXCOIL | 3.58 | 3.58 | 3.6 | 3.6 | 3.6 | 3.6 | 3.61 | 3.6 | 3.6 | 3.6 | 3.58 | 3.61 | 3.58 | 3.6 | 3.6 | 3.6
| PSZ_3:4_COOLC DXCOIL | 3.46 | 3.48 | 3.56 | 3.52 | 3.53 | 3.6 | 3.6 | 3.48 | 3.6 | 3.59 | 3.42 | 3.6 | 3.42 | 3.56 | 3.43 | 3.56
| PSZ_3:5_COOLC DXCOIL | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.56 | 3.6 | 3.56 | 3.56 | 3.56 | 3.58 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
Heating Efficiency (%)
| PSZ_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ_1:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ_1:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_1:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ_1:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_1:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_2:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ_2:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_2:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ_2:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_2:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ_3:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ_1:1_FAN | 3.78 | 3.72 | 3.53 | 3.79 | 3.23 | 3.52 | 2.94 | 3.28 | 3.89 | 3.22 | 3.31 | 3.79 | 3.29 | 3.57 | 3.23 | 2.82
| PSZ_1:2_FAN | 0.94 | 1.12 | 1.36 | 1.28 | 1.43 | 1.41 | 1.88 | 1.42 | 1.26 | 1.89 | 1.06 | 1.09 | 1.21 | 1.3 | 1.3 | 1.64
| PSZ_1:3_FAN | 1.46 | 1.45 | 1.52 | 1.49 | 1.32 | 1.45 | 1.09 | 1.38 | 1.42 | 1.22 | 0.98 | 0.96 | 0.98 | 0.93 | 0.86 | 1.09
| PSZ_1:4_FAN | 1.04 | 1.02 | 1.07 | 1 | 0.67 | 1.04 | 0.52 | 0.92 | 0.94 | 0.72 | 1.05 | 1.09 | 1.19 | 1.28 | 1.28 | 1.63
| PSZ_1:5_FAN | 1.73 | 1.78 | 1.88 | 1.81 | 1.64 | 1.9 | 1.48 | 1.7 | 1.89 | 1.56 | 1.22 | 1.31 | 1.2 | 1.23 | 1.11 | 1.09
| PSZ_2:1_FAN | 3.68 | 3.66 | 4.41 | 3.78 | 4.05 | 4 | 3.9 | 4.25 | 4.09 | 4.07 | 4.28 | 4.07 | 4.29 | 3.95 | 4.14 | 4.09
| PSZ_2:2_FAN | 1.13 | 1.31 | 1.67 | 1.49 | 1.6 | 1.73 | 2.15 | 1.63 | 1.51 | 2.16 | 1.15 | 1.17 | 1.3 | 1.39 | 1.4 | 1.74
| PSZ_2:3_FAN | 1.59 | 1.59 | 1.75 | 1.64 | 1.44 | 1.69 | 1.26 | 1.53 | 1.6 | 1.4 | 1.16 | 1.14 | 1.15 | 1.12 | 1.06 | 1.15
| PSZ_2:4_FAN | 1.22 | 1.22 | 1.37 | 1.21 | 0.84 | 1.36 | 0.75 | 1.13 | 1.17 | 0.88 | 1.14 | 1.17 | 1.29 | 1.38 | 1.38 | 1.73
| PSZ_2:5_FAN | 1.85 | 1.91 | 2.08 | 1.95 | 1.76 | 2.1 | 1.63 | 1.84 | 2.06 | 1.72 | 1.37 | 1.48 | 1.35 | 1.41 | 1.28 | 1.17
| PSZ_3:1_FAN | 3.57 | 4.01 | 4.37 | 4.09 | 3.65 | 4.42 | 3.23 | 4 | 4.01 | 3.61 | 4.06 | 3.52 | 4.12 | 3.35 | 3.72 | 4.15
| PSZ_3:2_FAN | 1.28 | 1.47 | 1.88 | 1.65 | 1.65 | 1.89 | 2.15 | 1.72 | 1.56 | 2.18 | 1.54 | 1.6 | 1.74 | 1.89 | 1.88 | 2.37
| PSZ_3:3_FAN | 1.55 | 1.54 | 1.73 | 1.6 | 1.35 | 1.63 | 1.15 | 1.47 | 1.46 | 1.3 | 1.11 | 1.05 | 1.14 | 1.23 | 1.23 | 1.55
| PSZ_3:4_FAN | 1.4 | 1.42 | 1.63 | 1.4 | 0.94 | 1.59 | 0.81 | 1.29 | 1.34 | 1.02 | 1.54 | 1.6 | 1.73 | 1.87 | 1.87 | 2.36
| PSZ_3:5_FAN | 1.97 | 2.05 | 2.26 | 2.08 | 1.82 | 2.25 | 1.67 | 1.94 | 2.15 | 1.78 | 1.46 | 1.54 | 1.4 | 1.44 | 1.31 | 1.55
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.089305 | 0.12202 | 0.095672 | 0.098036 | 0.13679 | 0.10107 | 0.1516 | 0.079058 | 0.037173 | 0.077703 | 0.087332 | 0.037192 | 0.062944 | 0.079149 | 0.062249 | 0.099767
| Total Cost ($/m2) | 17.55 | 22.46 | 18.43 | 16.87 | 19.35 | 17.77 | 19.91 | 12.85 | 5.86 | 10.82 | 13.05 | 5.44 | 9.42 | 11.14 | 8.89 | 14.73
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011456 | 0.0080827 | 0.0082416 | 0.0095369 | 0.0086286 | 0.0076874 | 0.0086678 | 0.0096637 | 0.0068649 | 0.0084554 | 0.0082609 | 0.0068691 | 0.0079184 | 0.0079715 | 0.0078818 | 0.0041061
| Total Cost ($/m2) | 0.07 | 0.27 | 0.16 | 0.71 | 0.13 | 0.26 | 0.38 | 1.37 | 0.58 | 0.97 | 1.64 | 0.93 | 2.33 | 1.83 | 2.98 | 2.94
Total Utility Costs
| Cost Intensity ($/m2) | 17.62 | 22.73 | 18.59 | 17.58 | 19.49 | 18.03 | 20.29 | 14.22 | 6.44 | 11.79 | 14.7 | 6.37 | 11.75 | 12.97 | 11.87 | 17.67
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 311869.4444 | 239219.4444 | 255547.2222 | 167269.4444 | 55822.2222 | 175313.8889 | 20880.5556 | 126688.8889 | 89033.3333 | 19883.3333 | 74519.4444 | 51422.2222 | 64986.1111 | 29811.1111 | 29008.3333 | 18622.2222
| Interior Lighting | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111 | 240936.1111
| Exterior Lighting | 9525 | 9519.4444 | 9519.4444 | 9516.6667 | 9511.1111 | 9508.3333 | 9513.8889 | 9508.3333 | 9511.1111 | 9491.6667 | 9508.3333 | 9502.7778 | 9502.7778 | 9500 | 9494.4444 | 9436.1111
| Interior Equipment | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 192747.2222 | 203413.8889 | 229622.2222 | 215511.1111 | 174688.8889 | 226144.4444 | 158986.1111 | 208988.8889 | 222372.2222 | 199677.7778 | 195725 | 202830.5556 | 206158.3333 | 196880.5556 | 207936.1111 | 242441.6667
| Pumps | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 979050 | 917063.8889 | 959597.2222 | 857208.3333 | 704927.7778 | 875875 | 654291.6667 | 810094.4444 | 785825 | 693963.8889 | 744663.8889 | 728666.6667 | 745555.5556 | 701100 | 711347.2222 | 735408.3333
Gas (MJ)
| Heating | 4580 | 136870 | 69570 | 335300 | 41110 | 139050 | 180270 | 665480 | 379720 | 529770 | 949730 | 636120 | 1425630 | 1098480 | 1836630 | 3516600
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 27740 | 31670 | 29400 | 35470 | 34740 | 32130 | 37990 | 38460 | 37890 | 40020 | 41080 | 40940 | 43340 | 43750 | 47080 | 51600
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 32320 | 168530 | 98970 | 370770 | 75850 | 171170 | 218260 | 703940 | 417610 | 569790 | 990810 | 677060 | 1468970 | 1142240 | 1883710 | 3568200
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3556900 | 3469960 | 3553520 | 3456720 | 2613600 | 3324330 | 2573710 | 3620280 | 3246580 | 3068060 | 3671600 | 3300260 | 4152980 | 3666190 | 4444560 | 6215670
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 225.3487 | 172.8537 | 184.6517 | 120.8645 | 40.3357 | 126.6772 | 15.0877 | 91.5421 | 64.3332 | 14.3672 | 53.8458 | 37.1564 | 46.9573 | 21.5407 | 20.9607 | 13.4559
| Interior Lighting (elec) | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941 | 174.0941
| Exterior Lighting (elec) | 6.8825 | 6.8785 | 6.8785 | 6.8765 | 6.8725 | 6.8705 | 6.8745 | 6.8705 | 6.8725 | 6.8584 | 6.8705 | 6.8665 | 6.8665 | 6.8645 | 6.8604 | 6.8183
| Interior Equipment (elec) | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 139.2741 | 146.9815 | 165.919 | 155.7227 | 126.2256 | 163.4061 | 114.8792 | 151.0099 | 160.6803 | 144.2819 | 141.4258 | 146.56 | 148.9646 | 142.2607 | 150.2492 | 175.182
| Pumps (elec) | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 707.4359 | 662.6463 | 693.3798 | 619.3963 | 509.3623 | 632.8843 | 472.774 | 585.353 | 567.8166 | 501.4401 | 538.0746 | 526.5154 | 538.7189 | 506.5965 | 514.0009 | 531.3868
Gas (MJ/m2)
| Heating (gas) | 0.91927 | 27.4719 | 13.9637 | 67.2997 | 8.2514 | 27.9094 | 36.1829 | 133.5718 | 76.2155 | 106.3328 | 190.625 | 127.6788 | 286.1452 | 220.4814 | 368.6391 | 705.8342
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 5.5678 | 6.3566 | 5.901 | 7.1194 | 6.9728 | 6.449 | 7.6252 | 7.7195 | 7.6051 | 8.0326 | 8.2454 | 8.2173 | 8.699 | 8.7813 | 9.4497 | 10.3569
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 6.4871 | 33.8265 | 19.8648 | 74.4191 | 15.2242 | 34.3564 | 43.808 | 141.2913 | 83.8206 | 114.3654 | 198.8704 | 135.8961 | 294.8442 | 229.2646 | 378.0888 | 716.1911
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 713.923 | 696.4728 | 713.2446 | 693.8154 | 524.5886 | 667.2427 | 516.5821 | 726.6443 | 651.6371 | 615.8055 | 736.945 | 662.4115 | 833.5652 | 735.8591 | 892.0896 | 1247.5779
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 257.921 | 240.4373 | 230.9204 | 214.8406 | 225.7838 | 185.3639 | 168.1788 | 185.1004 | 177.5809 | 172.2528 | 170.574 | 174.3194 | 171.6051 | 172.8449 | 170.6541 | 176.5518
| Feb | 262.2327 | 249.4247 | 244.9915 | 210.3137 | 220.4924 | 199.9501 | 192.8308 | 183.6956 | 196.5496 | 172.3486 | 170.6827 | 175.3464 | 171.6608 | 170.7829 | 170.7662 | 176.5518
| Mar | 267.6749 | 247.4243 | 269.2609 | 236.2188 | 221.3697 | 233.1781 | 170.9901 | 218.7087 | 200.9711 | 179.4769 | 189.9163 | 197.812 | 176.138 | 179.1173 | 170.7812 | 176.5518
| Apr | 273.9444 | 261.5639 | 269.2012 | 252.6125 | 231.5565 | 264.4643 | 200.0394 | 228.1856 | 236.5604 | 172.3389 | 192.5641 | 211.8184 | 192.9886 | 172.0874 | 174.2755 | 175.8043
| May | 278.1098 | 287.1706 | 300.6151 | 271.4711 | 237.3333 | 282.0864 | 211.8168 | 247.8759 | 250.3188 | 220.3603 | 236.1378 | 225.7488 | 238.4247 | 206.5374 | 204.19 | 192.7318
| Jun | 289.9084 | 291.0705 | 339.8718 | 285.1896 | 232.2575 | 324.6019 | 218.129 | 282.8105 | 266.7389 | 231.6546 | 262.9013 | 238.0217 | 260.0016 | 244.1233 | 232.0705 | 224.334
| Jul | 287.4552 | 299.5236 | 336.1284 | 305.0031 | 241.2256 | 321.1143 | 236.5672 | 291.4923 | 277.2769 | 246.1953 | 269.3648 | 250.1452 | 259.4695 | 241.7059 | 244.1825 | 224.0791
| Aug | 295.2228 | 300.4092 | 336.7468 | 283.973 | 258.3268 | 310.979 | 225.4311 | 290.4369 | 272.8167 | 242.9928 | 263.495 | 246.4952 | 257.9131 | 235.0037 | 236.6496 | 220.6821
| Sep | 287.7681 | 285.777 | 318.208 | 274.346 | 250.3895 | 302.351 | 251.1606 | 265.9605 | 251.7969 | 239.9756 | 240.6772 | 230.7013 | 239.2309 | 222.3534 | 223.4944 | 180.6354
| Oct | 279.2104 | 270.5547 | 278.3468 | 259.6249 | 236.985 | 268.116 | 219.0674 | 244.9257 | 235.5443 | 193.5667 | 219.3986 | 222.92 | 199.9509 | 198.9646 | 178.5274 | 176.5518
| Nov | 265.3591 | 253.4195 | 259.4984 | 226.5705 | 226.6414 | 214.5164 | 170.2713 | 227.6585 | 185.0708 | 172.2528 | 214.4194 | 187.0688 | 181.3557 | 172.8449 | 170.9945 | 176.5518
| Dec | 254.6916 | 241.494 | 226.9122 | 207.508 | 227.5163 | 207.0459 | 167.764 | 180.2548 | 177.5809 | 172.2528 | 170.5081 | 173.3246 | 171.6051 | 172.8449 | 170.6541 | 176.5518
Time of Peak Electrical Demand
| Jan | 23-JAN-16:10 | 03-JAN-13:00 | 26-JAN-16:10 | 23-JAN-16:10 | 26-JAN-13:09 | 18-JAN-13:30 | 27-JAN-08:00 | 05-JAN-13:00 | 02-JAN-08:09 | 02-JAN-08:09 | 17-JAN-08:00 | 25-JAN-08:00 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09
| Feb | 22-FEB-13:00 | 23-FEB-13:00 | 28-FEB-16:10 | 22-FEB-13:00 | 13-FEB-11:00 | 08-FEB-13:00 | 15-FEB-16:10 | 16-FEB-13:00 | 14-FEB-16:10 | 22-FEB-08:50 | 28-FEB-08:00 | 23-FEB-08:00 | 16-FEB-08:00 | 03-FEB-08:39 | 28-FEB-08:00 | 01-FEB-08:09
| Mar | 13-MAR-15:39 | 27-MAR-15:30 | 17-MAR-15:20 | 28-MAR-15:39 | 30-MAR-12:39 | 31-MAR-15:09 | 01-MAR-08:00 | 09-MAR-16:10 | 02-MAR-14:00 | 29-MAR-15:30 | 31-MAR-15:09 | 30-MAR-15:00 | 23-MAR-15:30 | 30-MAR-15:00 | 22-MAR-07:40 | 01-MAR-08:09
| Apr | 03-APR-15:09 | 17-APR-15:39 | 26-APR-15:30 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-15:09 | 05-APR-15:39 | 21-APR-15:30 | 27-APR-07:49 | 07-APR-14:00 | 26-APR-15:00 | 14-APR-15:00 | 14-APR-07:00 | 04-APR-15:30 | 25-APR-15:00
| May | 15-MAY-15:00 | 18-MAY-15:30 | 30-MAY-15:00 | 15-MAY-15:09 | 30-MAY-10:20 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:39 | 31-MAY-15:00 | 04-MAY-15:09 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:09
| Jun | 27-JUN-15:20 | 13-JUN-15:20 | 28-JUN-15:00 | 19-JUN-15:09 | 28-JUN-12:00 | 27-JUN-15:00 | 16-JUN-15:09 | 30-JUN-15:00 | 29-JUN-15:20 | 28-JUN-15:09 | 08-JUN-12:00 | 27-JUN-15:39 | 29-JUN-15:00 | 26-JUN-15:09 | 14-JUN-15:00 | 21-JUN-15:00
| Jul | 03-JUL-15:20 | 31-JUL-15:09 | 11-JUL-15:00 | 03-JUL-15:30 | 24-JUL-15:09 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:09 | 24-JUL-15:09 | 03-JUL-15:09 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-15:09 | 28-AUG-15:30 | 01-AUG-15:00 | 14-AUG-15:30 | 09-AUG-14:09 | 04-AUG-15:20 | 15-AUG-12:09 | 17-AUG-15:09 | 01-AUG-15:09 | 07-AUG-15:09 | 04-AUG-15:39 | 30-AUG-12:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-15:09
| Sep | 11-SEP-15:09 | 15-SEP-15:09 | 11-SEP-15:00 | 11-SEP-12:00 | 25-SEP-12:00 | 01-SEP-15:09 | 28-SEP-15:09 | 08-SEP-15:09 | 05-SEP-13:50 | 01-SEP-15:30 | 05-SEP-15:09 | 06-SEP-15:09 | 14-SEP-15:09 | 01-SEP-15:00 | 07-SEP-15:09 | 07-SEP-15:00
| Oct | 06-OCT-15:30 | 06-OCT-15:00 | 02-OCT-15:09 | 12-OCT-15:00 | 05-OCT-12:00 | 03-OCT-15:09 | 31-OCT-12:00 | 12-OCT-15:09 | 13-OCT-15:09 | 17-OCT-12:00 | 31-OCT-12:00 | 05-OCT-15:09 | 06-OCT-15:09 | 06-OCT-15:00 | 06-OCT-15:09 | 03-OCT-07:10
| Nov | 07-NOV-13:00 | 01-NOV-15:09 | 13-NOV-13:00 | 22-NOV-13:00 | 20-NOV-13:50 | 10-NOV-13:00 | 08-NOV-08:00 | 03-NOV-13:00 | 08-NOV-14:00 | 01-NOV-07:10 | 02-NOV-15:09 | 10-NOV-13:00 | 02-NOV-15:09 | 01-NOV-07:10 | 09-NOV-08:30 | 01-NOV-07:10
| Dec | 19-DEC-13:00 | 19-DEC-15:20 | 11-DEC-16:10 | 05-DEC-13:00 | 19-DEC-13:09 | 05-DEC-13:00 | 15-DEC-08:00 | 06-DEC-13:00 | 01-DEC-08:09 | 01-DEC-08:09 | 12-DEC-08:00 | 22-DEC-08:39 | 01-DEC-08:09 | 15-DEC-08:09 | 01-DEC-08:09 | 01-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 11726.34 | 12174.82 | 11034.83 | 10786.02 | 7937.15 | 11465.74 | 7528.45 | 11197.54 | 9842.55 | 4974.19 | 10588.03 | 9443.12 | 10829.04 | 10020.6 | 10858.66 | 13353.23
| Total Source Energy (MJ/m2) | 2353.65 | 2443.67 | 2214.86 | 2164.92 | 1593.11 | 2301.35 | 1511.07 | 2247.51 | 1975.55 | 998.4 | 2125.18 | 1895.38 | 2173.55 | 2011.29 | 2179.5 | 2680.2
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
| Total Building | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
Emissions
| Carbon Equivalent (kg) | 269087.3123 | 308935.4982 | 291463.7928 | 270737.6512 | 83749.9107 | 298497.5814 | 80400.1297 | 231302.3726 | 328538.4896 | 60819.0237 | 414883.3463 | 309867.7077 | 281688.4063 | 276805.5493 | 277457.6802 | 271278.781
| CO2 (kg) | 623420.4804 | 776362.2961 | 686394.1789 | 618608.7673 | 223898.1889 | 708602.3784 | 215518.1706 | 526912.0839 | 769736.9328 | 149752.7028 | 967645.658 | 728848.0189 | 664867.2109 | 655416.8246 | 659479.8641 | 704277.5339
| NOX (kg) | 1098.0268 | 1016.8876 | 1156.0838 | 1174.769 | 191.8123 | 1155.5282 | 185.0274 | 1013.4784 | 1332.1118 | 219.8673 | 1714.8501 | 1248.9257 | 1143.0842 | 1111.8182 | 1113.4401 | 818.1999
| SO2 (kg) | 4190.7386 | 4374.4351 | 3858.7622 | 3008.9013 | 2051.279 | 4818.0603 | 1903.9672 | 2957.3578 | 3431.6517 | 536.5313 | 5018.6961 | 3182.1181 | 1760.0273 | 1872.3251 | 1679.3993 | 3744.4773
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0191 | 0.0123 | 0.0105 | 0.011 | 0.0009 | 0.009 | 0.0009 | 0.012 | 0.0134 | 0.0021 | 0.0152 | 0.0125 | 0.013 | 0.0131 | 0.0124 | 0.013
| Water for Electricity (m3) | 518.6601 | 1492.17 | 28504.3 | 5352.07 | 12377 | 24028.8 | 11487.9 | 183.9219 | 3568.27 | 7090.09 | 1155.3 | 3308.72 | 1156.69 | 44410.5 | 1103.61 | 751.3517

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3556.9 | 713.92 | 713.92
Net Site Energy | 3556.9 | 713.92 | 713.92
Total Source Energy | 11726.34 | 2353.65 | 2353.65
Net Source Energy | 11726.34 | 2353.65 | 2353.65
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4.58 | 0 | 0 | 0 | 0
Cooling | 1122.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 693.89 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.74 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3524.58 | 32.32 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 79248.74 | 57178.14 | 22070.6 | 0.72 | 3.52
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20651.83 | 14646.15 | 6005.68 | 0.71 | 3.37
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24918 | 19618.3 | 5299.7 | 0.79 | 3.57
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21600.72 | 15609.55 | 5991.17 | 0.72 | 3.4
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29102.73 | 23074.06 | 6028.67 | 0.79 | 3.58
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76065.73 | 55157.26 | 20908.47 | 0.73 | 3.54
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23408.97 | 16970.7 | 6438.27 | 0.72 | 3.41
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26721.96 | 21183.27 | 5538.69 | 0.79 | 3.58
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24298.4 | 17903.55 | 6394.86 | 0.74 | 3.44
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30831.14 | 24569.18 | 6261.96 | 0.8 | 3.55
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75502.08 | 54259.57 | 21242.52 | 0.72 | 3.51
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25600.64 | 18818.91 | 6781.73 | 0.74 | 3.43
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26219.56 | 20729.59 | 5489.97 | 0.79 | 3.58
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26885.65 | 20114.66 | 6770.98 | 0.75 | 3.46
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32689.38 | 26107.55 | 6581.84 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 95281.52 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 23457 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 34649.43 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 25551.3 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 40890.21 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 92830.93 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 27749.03 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 37624.08 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 29824.72 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 43723.99 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 90357.84 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 31162.36 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 36728.35 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 33964.9 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 46509.83 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.78 | 7215.37 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.94 | 1075.4 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.46 | 1661.93 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.04 | 1179.18 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1971.18 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.68 | 7011.97 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.13 | 1288.09 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.59 | 1809.33 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.22 | 1390.94 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.85 | 2027.14 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.57 | 6806.76 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.28 | 1457.22 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.55 | 1764.94 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.4 | 1596.1 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.97 | 2159.66 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 46690.2393 | 82.0964 | 312.7672 | 0 | 0.0014 | 38709.0365 | 20139.0243
February | 43434.0232 | 76.4816 | 291.8251 | 0 | 0.0013 | 36117.2553 | 18745.5943
March | 51579.8601 | 90.8262 | 346.5624 | 0 | 0.0016 | 42891.7253 | 22261.3261
April | 49825.961 | 87.7692 | 335.0255 | 0 | 0.0015 | 41463.9078 | 21507.5125
May | 55674.6244 | 98.0839 | 374.4474 | 0 | 0.0017 | 46342.9044 | 24033.3258
June | 57210.1812 | 100.7987 | 384.8503 | 0 | 0.0018 | 47630.4173 | 24697.1461
July | 56396.8022 | 99.366 | 379.3814 | 0 | 0.0017 | 46953.5593 | 24346.0504
August | 60745.7392 | 107.0301 | 408.6502 | 0 | 0.0019 | 50575.9746 | 26223.6243
September | 54145.882 | 95.3938 | 364.1899 | 0 | 0.0017 | 45073.4078 | 23373.7159
October | 52995.3919 | 93.3576 | 356.3787 | 0 | 0.0016 | 44106.6511 | 22876.1428
November | 49026.8289 | 86.3571 | 329.6175 | 0 | 0.0015 | 40794.5898 | 21162.1229
December | 45694.9469 | 80.4662 | 307.043 | 0 | 0.0014 | 38000.672 | 19721.7268
Annual Sum or Average | 623420.4804 | 1098.0268 | 4190.7386 | 0 | 0.0191 | 518660.1014 | 269087.3123
Minimum of Months | 43434.0232 | 76.4816 | 291.8251 | 0 | 0.0013 | 36117.2553 | 18745.5943
Maximum of Months | 60745.7392 | 107.0301 | 408.6502 | 0 | 0.0019 | 50575.9746 | 26223.6243
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 263049000000 | 257920.994 | 23-JAN-16:10 | 75734.208 | 50956.166 | 40415.196 | 0 | 90806.984 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 245437000000 | 262232.748 | 22-FEB-13:00 | 75734.208 | 51598.363 | 40415.196 | 0 | 94476.54 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 291473000000 | 267674.911 | 13-MAR-15:39 | 75734.208 | 50956.166 | 40415.196 | 0 | 100560.901 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 281770000000 | 273944.431 | 03-APR-15:09 | 75734.208 | 50956.166 | 40415.196 | 0 | 106830.422 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 314926000000 | 278109.819 | 15-MAY-15:00 | 75734.208 | 50956.166 | 40415.196 | 0 | 110995.809 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 323675000000 | 289908.424 | 27-JUN-15:20 | 75734.208 | 50956.166 | 40415.196 | 0 | 122794.414 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 319076000000 | 287455.222 | 03-JUL-15:20 | 75734.208 | 50956.166 | 40415.196 | 0 | 120341.213 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 343692000000 | 295222.818 | 21-AUG-15:09 | 75734.208 | 50956.166 | 40415.196 | 0 | 128108.808 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 306299000000 | 287768.131 | 11-SEP-15:09 | 75734.208 | 50956.166 | 40415.196 | 0 | 120654.121 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 299729000000 | 279210.375 | 06-OCT-15:30 | 75734.208 | 50956.166 | 40415.196 | 0 | 112096.365 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 277222000000 | 265359.088 | 07-NOV-13:00 | 75734.208 | 51598.363 | 40415.196 | 0 | 97602.881 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 258236000000 | 254691.56 | 19-DEC-13:00 | 75734.208 | 51598.363 | 40415.196 | 0 | 86935.352 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3524580000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 245437000000 | 254691.56 |  | 75734.208 | 50956.166 | 40415.196 | 0 | 86935.352 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 343692000000 | 295222.818 |  | 75734.208 | 51598.363 | 40415.196 | 0 | 128108.808 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 87434.51 | 370.26 | 0 | 87804.77
Cost per Total Building Area ($/m2) | 17.55 | 0.07 | 0 | 17.62
Cost per Net Conditioned Building Area ($/m2) | 17.55 | 0.07 | 0 | 17.62

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3469.96 | 696.47 | 696.47
Net Site Energy | 3469.96 | 696.47 | 696.47
Total Source Energy | 12174.82 | 2443.67 | 2443.67
Net Source Energy | 12174.82 | 2443.67 | 2443.67
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 136.87 | 0 | 0 | 0 | 0
Cooling | 861.19 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 732.29 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 31.67 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3301.43 | 168.53 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76914.54 | 55801.62 | 21112.92 | 0.73 | 3.54
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23265.93 | 16824.93 | 6441 | 0.72 | 3.4
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24555.89 | 19419.67 | 5136.22 | 0.79 | 3.58
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21172 | 15347.31 | 5824.69 | 0.72 | 3.41
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29748.88 | 23665.5 | 6083.38 | 0.8 | 3.55
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 71930.68 | 53273.03 | 18657.65 | 0.74 | 3.61
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26093.7 | 19219.49 | 6874.21 | 0.74 | 3.44
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26465.59 | 21080.24 | 5385.36 | 0.8 | 3.59
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23975.71 | 17735.22 | 6240.5 | 0.74 | 3.44
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31631.58 | 25262.73 | 6368.85 | 0.8 | 3.56
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 85274.88 | 61129.8 | 24145.08 | 0.72 | 3.5
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28445.95 | 21201.07 | 7244.87 | 0.75 | 3.46
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25824.45 | 20495.2 | 5329.25 | 0.79 | 3.58
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26888.58 | 20229.08 | 6659.5 | 0.75 | 3.48
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33918.16 | 27088.92 | 6829.24 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 100174.59 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 28735.28 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 35255.91 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 26570.18 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 42813.67 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 98742.5 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 33161.51 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 38408.63 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 31010.4 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 45771.75 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 106665.8 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 36804.62 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 37246.49 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 35672.4 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 48936.46 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.72 | 7099.26 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.12 | 1272.34 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.45 | 1653.96 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.02 | 1164.68 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.78 | 1948.57 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.66 | 6979.99 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.31 | 1492.43 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.59 | 1810.72 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.22 | 1385.47 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.91 | 2089.77 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.01 | 7639.86 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.47 | 1673.58 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.54 | 1752.94 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.42 | 1617.28 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.05 | 2240.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 57075.6843 | 73.9241 | 309.9102 | 0 | 0.0009 | 105710.1879 | 22604.4181
February | 50161.1911 | 65.1192 | 274.4767 | 0 | 0.0008 | 93624.5268 | 19885.4099
March | 60842.5242 | 79.7274 | 343.3121 | 0 | 0.001 | 117107.7406 | 24215.4201
April | 60040.8477 | 78.8406 | 341.0815 | 0 | 0.001 | 116347.5764 | 23917.4549
May | 70515.1251 | 92.6276 | 401.0468 | 0 | 0.0011 | 136802.6994 | 28094.1742
June | 76071.5201 | 99.9379 | 432.8097 | 0 | 0.0012 | 147637.5271 | 30309.4035
July | 75904.319 | 99.7208 | 431.8941 | 0 | 0.0012 | 147325.214 | 30243.1136
August | 80462.7813 | 105.7091 | 457.8248 | 0 | 0.0013 | 156170.5372 | 32059.3118
September | 69006.5572 | 90.6527 | 392.5617 | 0 | 0.0011 | 133908.3646 | 27494.0128
October | 64597.5186 | 84.8332 | 367.0947 | 0 | 0.001 | 125221.0943 | 25733.7932
November | 57384.8406 | 75.247 | 324.5095 | 0 | 0.0009 | 110694.1894 | 22845.7716
December | 54299.3869 | 70.548 | 297.9135 | 0 | 0.0008 | 101619.1287 | 21533.2144
Annual Sum or Average | 776362.2961 | 1016.8876 | 4374.4351 | 0 | 0.0123 | 1492170 | 308935.4982
Minimum of Months | 50161.1911 | 65.1192 | 274.4767 | 0 | 0.0008 | 93624.5268 | 19885.4099
Maximum of Months | 80462.7813 | 105.7091 | 457.8248 | 0 | 0.0013 | 156170.5372 | 32059.3118
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 233884000000 | 240437.296 | 03-JAN-13:00 | 75734.208 | 51598.363 | 41821.683 | 0 | 71274.602 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 207144000000 | 249424.677 | 23-FEB-13:00 | 75734.208 | 51598.363 | 41821.683 | 0 | 80261.983 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 259101000000 | 247424.264 | 27-MAR-15:30 | 75734.208 | 50956.166 | 41821.683 | 0 | 78903.768 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 257419000000 | 261563.91 | 17-APR-15:39 | 75734.208 | 50956.166 | 41821.683 | 0 | 93043.414 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 302676000000 | 287170.63 | 18-MAY-15:30 | 75734.208 | 50956.166 | 41821.683 | 0 | 118650.134 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 326648000000 | 291070.525 | 13-JUN-15:20 | 75734.208 | 50956.166 | 41821.683 | 0 | 122550.029 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 325957000000 | 299523.616 | 31-JUL-15:09 | 75734.208 | 50956.166 | 41821.683 | 0 | 131003.12 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 345528000000 | 300409.212 | 28-AUG-15:30 | 75734.208 | 50956.166 | 41821.683 | 0 | 131888.715 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 296273000000 | 285776.965 | 15-SEP-15:09 | 75734.208 | 50956.166 | 41821.683 | 0 | 117256.468 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 277052000000 | 270554.676 | 06-OCT-15:00 | 75734.208 | 50956.166 | 41821.683 | 0 | 102034.18 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 244911000000 | 253419.465 | 01-NOV-15:09 | 75734.208 | 50956.166 | 41821.683 | 0 | 84898.969 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 224833000000 | 241493.955 | 19-DEC-15:20 | 75734.208 | 48066.275 | 41821.683 | 0 | 75863.349 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3301430000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 207144000000 | 240437.296 |  | 75734.208 | 48066.275 | 41821.683 | 0 | 71274.602 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 345528000000 | 300409.212 |  | 75734.208 | 51598.363 | 41821.683 | 0 | 131888.715 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 111896.26 | 1362.17 | 0 | 113258.43
Cost per Total Building Area ($/m2) | 22.46 | 0.27 | 0 | 22.73
Cost per Net Conditioned Building Area ($/m2) | 22.46 | 0.27 | 0 | 22.73

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3553.52 | 713.25 | 713.25
Net Site Energy | 3553.52 | 713.25 | 713.25
Total Source Energy | 11034.83 | 2214.86 | 2214.86
Net Source Energy | 11034.83 | 2214.86 | 2214.86
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 69.57 | 0 | 0 | 0 | 0
Cooling | 919.97 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 826.64 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 29.4 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3454.55 | 98.97 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 68988.76 | 51194.59 | 17794.17 | 0.74 | 3.82
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25293.9 | 19151.03 | 6142.88 | 0.76 | 3.49
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25221.9 | 20143.6 | 5078.3 | 0.8 | 3.6
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20262.02 | 15252.43 | 5009.59 | 0.75 | 3.48
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31115.26 | 24850.36 | 6264.89 | 0.8 | 3.56
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 77603.38 | 60306.39 | 17297 | 0.78 | 3.8
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29762.25 | 22978.12 | 6784.13 | 0.77 | 3.53
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28964.76 | 23132.86 | 5831.9 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24539.18 | 18942.34 | 5596.84 | 0.77 | 3.53
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34496.68 | 27550.96 | 6945.73 | 0.8 | 3.56
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 78600.34 | 60475.4 | 18124.94 | 0.77 | 3.76
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32838 | 25592.27 | 7245.73 | 0.78 | 3.51
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28712.8 | 22931.63 | 5781.17 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28131.57 | 22055.54 | 6076.03 | 0.78 | 3.56
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37433.07 | 29896.12 | 7536.95 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 89007.97 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 32286.82 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 35140.85 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 26008.6 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 43004.58 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 108598.42 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 39187.06 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 40135.18 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 32710.01 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 47516.62 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 107652.64 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 43863.55 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 39799.04 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 38389.57 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 51434.9 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.53 | 6725.98 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.36 | 1544.14 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.52 | 1735.74 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1220.34 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.88 | 2055.66 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.41 | 8418.06 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.67 | 1900.02 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.75 | 1993.32 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.37 | 1565.96 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.08 | 2279.06 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.37 | 8336.36 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.88 | 2055.55 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1975.98 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.63 | 1858.88 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.26 | 2473.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 45600.2256 | 76.1305 | 251.4837 | 0 | 0.0007 | 1857650 | 19295.1489
February | 41843.6595 | 69.9766 | 231.619 | 0 | 0.0006 | 1710920 | 17717.524
March | 53225.3313 | 89.6913 | 299.5442 | 0 | 0.0008 | 2212700 | 22605.6009
April | 52638.8456 | 88.8449 | 297.2702 | 0 | 0.0008 | 2195910 | 22370.8639
May | 61639.3658 | 104.0778 | 348.4005 | 0 | 0.0009 | 2573610 | 26200.1834
June | 71357.2219 | 120.5156 | 403.5401 | 0 | 0.0011 | 2980930 | 30333.7799
July | 72421.8497 | 122.3199 | 409.6057 | 0 | 0.0011 | 3025730 | 30786.9786
August | 74706.2905 | 126.1777 | 422.5217 | 0 | 0.0011 | 3121140 | 31758.0472
September | 64413.5491 | 108.78 | 364.2113 | 0 | 0.001 | 2690410 | 27381.1909
October | 55450.3796 | 93.6132 | 313.3143 | 0 | 0.0008 | 2314430 | 23568.0568
November | 47736.207 | 80.4551 | 268.7515 | 0 | 0.0007 | 1985240 | 20275.6752
December | 45361.2533 | 75.5012 | 248.4999 | 0 | 0.0007 | 1835600 | 19170.743
Annual Sum or Average | 686394.1789 | 1156.0838 | 3858.7622 | 0 | 0.0105 | 28504300 | 291463.7928
Minimum of Months | 41843.6595 | 69.9766 | 231.619 | 0 | 0.0006 | 1710920 | 17717.524
Maximum of Months | 74706.2905 | 126.1777 | 422.5217 | 0 | 0.0011 | 3121140 | 31758.0472
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 225137000000 | 230920.412 | 26-JAN-16:10 | 75734.208 | 50956.166 | 46138.088 | 0 | 58083.511 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 207354000000 | 244991.465 | 28-FEB-16:10 | 75734.208 | 50956.166 | 46138.088 | 0 | 72154.564 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 268167000000 | 269260.877 | 17-MAR-15:20 | 75734.208 | 50956.166 | 46138.088 | 0 | 96423.976 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 266132000000 | 269201.22 | 26-APR-15:30 | 75734.208 | 50956.166 | 46138.088 | 0 | 96364.319 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 311907000000 | 300615.057 | 30-MAY-15:00 | 75734.208 | 50956.166 | 46138.088 | 0 | 127778.156 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 361271000000 | 339871.834 | 28-JUN-15:00 | 75734.208 | 50956.166 | 46138.088 | 0 | 167034.932 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 366701000000 | 336128.353 | 11-JUL-15:00 | 75734.208 | 50956.166 | 46138.088 | 0 | 163291.452 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 378264000000 | 336746.822 | 01-AUG-15:00 | 75734.208 | 50956.166 | 46138.088 | 0 | 163909.921 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 326062000000 | 318207.998 | 11-SEP-15:00 | 75734.208 | 50956.166 | 46138.088 | 0 | 145371.096 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 280496000000 | 278346.787 | 02-OCT-15:09 | 75734.208 | 50956.166 | 46138.088 | 0 | 105509.886 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 240600000000 | 259498.413 | 13-NOV-13:00 | 75734.208 | 51598.363 | 46138.088 | 0 | 86019.314 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 222464000000 | 226912.169 | 11-DEC-16:10 | 75734.208 | 50956.166 | 46138.088 | 0 | 54075.267 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3454550000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 207354000000 | 226912.169 |  | 75734.208 | 50956.166 | 46138.088 | 0 | 54075.267 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 378264000000 | 339871.834 |  | 75734.208 | 51598.363 | 46138.088 | 0 | 167034.932 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 91806.39 | 815.67 | 0 | 92622.06
Cost per Total Building Area ($/m2) | 18.43 | 0.16 | 0 | 18.59
Cost per Net Conditioned Building Area ($/m2) | 18.43 | 0.16 | 0 | 18.59

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3456.72 | 693.82 | 693.82
Net Site Energy | 3456.72 | 693.82 | 693.82
Total Source Energy | 10786.02 | 2164.92 | 2164.92
Net Source Energy | 10786.02 | 2164.92 | 2164.92
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 335.3 | 0 | 0 | 0 | 0
Cooling | 602.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 775.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 35.47 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3085.95 | 370.77 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74132.9 | 55033.75 | 19099.15 | 0.74 | 3.62
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24270.11 | 18223.32 | 6046.79 | 0.75 | 3.47
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24627.42 | 19668.82 | 4958.6 | 0.8 | 3.6
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19539.27 | 14491.36 | 5047.91 | 0.74 | 3.45
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29975.22 | 23939.87 | 6035.35 | 0.8 | 3.56
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 72810.05 | 54396.04 | 18414 | 0.75 | 3.64
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27298.24 | 20837.47 | 6460.77 | 0.76 | 3.5
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27154.14 | 21686.8 | 5467.34 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22480.02 | 17036.85 | 5443.18 | 0.76 | 3.49
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32270.78 | 25773.23 | 6497.55 | 0.8 | 3.56
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 81979.79 | 60222.42 | 21757.37 | 0.73 | 3.58
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29480.06 | 22718.41 | 6761.65 | 0.77 | 3.52
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26403.34 | 21087.17 | 5316.17 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25205.22 | 19385.75 | 5819.47 | 0.77 | 3.52
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34481.01 | 27538.44 | 6942.57 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 101459.9 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 31941.07 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 35292.94 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 25777.81 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 42450.65 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 101214.06 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 36706.52 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 38674.8 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 30430.41 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 45523.11 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 108034.46 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 40130.52 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 37669.71 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 34705.49 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 48481.21 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.79 | 7234.34 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.28 | 1453.08 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.49 | 1694.83 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1 | 1136.19 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.81 | 1980.34 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.78 | 7213.17 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.49 | 1698.11 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.64 | 1868.71 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.21 | 1375.41 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.95 | 2132 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.09 | 7800.57 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.65 | 1874.17 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1817.04 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.4 | 1595.23 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.08 | 2278.02 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50179.5785 | 90.5612 | 220.8741 | 0 | 0.0008 | 392834.9047 | 21524.3309
February | 43750.1702 | 80.1534 | 198.4352 | 0 | 0.0007 | 352938.5041 | 18876.8855
March | 48952.8348 | 93.1303 | 238.9212 | 0 | 0.0009 | 424981.3368 | 21439.8521
April | 47528.9395 | 91.1397 | 235.4933 | 0 | 0.0009 | 418890.4478 | 20882.5739
May | 54193.3008 | 104.4763 | 271.245 | 0 | 0.001 | 482489.9571 | 23862.1263
June | 58854.9222 | 113.5016 | 294.7654 | 0 | 0.0011 | 524328.3422 | 25918.2567
July | 58537.9997 | 112.8989 | 293.2194 | 0 | 0.0011 | 521578.3964 | 25779.4691
August | 62635.2193 | 120.8043 | 313.7591 | 0 | 0.0011 | 558114.3223 | 27584.1486
September | 54311.4969 | 104.7351 | 271.988 | 0 | 0.001 | 483811.8875 | 23917.0224
October | 48427.1196 | 93.1085 | 241.1515 | 0 | 0.0009 | 428957.4277 | 21299.9612
November | 44560.2965 | 84.4268 | 215.7822 | 0 | 0.0008 | 383819.5741 | 19484.015
December | 46676.8892 | 85.833 | 213.2668 | 0 | 0.0008 | 379321.1139 | 20169.0095
Annual Sum or Average | 618608.7673 | 1174.769 | 3008.9013 | 0 | 0.011 | 5352070 | 270737.6512
Minimum of Months | 43750.1702 | 80.1534 | 198.4352 | 0 | 0.0007 | 352938.5041 | 18876.8855
Maximum of Months | 62635.2193 | 120.8043 | 313.7591 | 0 | 0.0011 | 558114.3223 | 27584.1486
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 226505000000 | 214840.62 | 23-JAN-16:10 | 75734.208 | 50956.166 | 43151.221 | 0 | 44990.586 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 203501000000 | 210313.653 | 22-FEB-13:00 | 75734.208 | 51598.363 | 43151.221 | 0 | 39821.421 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 245040000000 | 236218.827 | 28-MAR-15:39 | 75734.208 | 50956.166 | 43151.221 | 0 | 66368.792 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 241528000000 | 252612.468 | 14-APR-15:00 | 75734.208 | 50956.166 | 43151.221 | 0 | 82762.433 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 278199000000 | 271471.125 | 15-MAY-15:09 | 75734.208 | 50956.166 | 43151.221 | 0 | 101621.09 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 302323000000 | 285189.625 | 19-JUN-15:09 | 75734.208 | 50956.166 | 43151.221 | 0 | 115339.591 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 300737000000 | 305003.117 | 03-JUL-15:30 | 75734.208 | 50956.166 | 43151.221 | 0 | 135153.083 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 321803000000 | 283973.03 | 14-AUG-15:30 | 75734.208 | 50956.166 | 43151.221 | 0 | 114122.996 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 278961000000 | 274346.011 | 11-SEP-12:00 | 75734.208 | 51598.363 | 43151.221 | 0 | 103853.779 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 247333000000 | 259624.881 | 12-OCT-15:00 | 75734.208 | 50956.166 | 43151.221 | 0 | 89774.846 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 221307000000 | 226570.528 | 22-NOV-13:00 | 75734.208 | 51598.363 | 43151.221 | 0 | 56078.296 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 218713000000 | 207508.021 | 05-DEC-13:00 | 75734.208 | 51598.363 | 43151.221 | 0 | 37015.789 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3085950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 203501000000 | 207508.021 |  | 75734.208 | 50956.166 | 43151.221 | 0 | 37015.789 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 321803000000 | 305003.117 |  | 75734.208 | 51598.363 | 43151.221 | 0 | 135153.083 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 84037.68 | 3536.01 | 0 | 87573.68
Cost per Total Building Area ($/m2) | 16.87 | 0.71 | 0 | 17.58
Cost per Net Conditioned Building Area ($/m2) | 16.87 | 0.71 | 0 | 17.58

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2613.6 | 524.59 | 524.59
Net Site Energy | 2613.6 | 524.59 | 524.59
Total Source Energy | 7937.15 | 1593.11 | 1593.11
Net Source Energy | 7937.15 | 1593.11 | 1593.11
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 41.11 | 0 | 0 | 0 | 0
Cooling | 200.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 628.88 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 34.74 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2537.74 | 75.85 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 62259.58 | 46521.1 | 15738.47 | 0.75 | 3.24
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23789.22 | 18940.88 | 4848.34 | 0.8 | 3.59
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21828.98 | 17433.83 | 4395.15 | 0.8 | 3.6
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13081.85 | 9685.93 | 3395.92 | 0.74 | 3.47
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27229.21 | 21746.75 | 5482.46 | 0.8 | 3.6
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 69813.96 | 54722.16 | 15091.81 | 0.78 | 4.07
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26516.61 | 21177.63 | 5338.98 | 0.8 | 3.6
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23866.65 | 19061.23 | 4805.43 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15545.17 | 11784.37 | 3760.79 | 0.76 | 3.52
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29065.02 | 23212.93 | 5852.09 | 0.8 | 3.6
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 65493.68 | 50462.6 | 15031.08 | 0.77 | 3.99
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27236.39 | 21752.49 | 5483.9 | 0.8 | 3.6
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22422.38 | 17907.75 | 4514.63 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17037.35 | 13070.84 | 3966.51 | 0.77 | 3.53
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30121.96 | 24057.06 | 6064.9 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 83286.43 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 34638.8 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 31435.64 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 17172.9 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 38909 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 101898.3 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 38633.5 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 34255.63 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 21075.41 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 41449.64 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 92874.9 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 39629.71 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 32256.96 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 23497.07 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 42912.46 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.23 | 3537.7 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.43 | 1626.19 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.32 | 1502.24 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 771.43 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.64 | 1873.88 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.05 | 7720.09 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1824.84 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.44 | 1642.47 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.84 | 969.02 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.76 | 2000.22 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.65 | 6968.68 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.65 | 1874.37 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.35 | 1543.08 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.94 | 1072.13 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.82 | 1990.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18228.7532 | 15.6412 | 162.5759 | 0 | 0.0001 | 980932.7709 | 6805.0148
February | 16256.1125 | 13.9403 | 146.4714 | 0 | 0.0001 | 883768.1868 | 6073.1463
March | 19032.1146 | 16.3117 | 173.116 | 0 | 0.0001 | 1044540 | 7115.217
April | 17339.7513 | 14.8533 | 159.138 | 0 | 0.0001 | 960205.0182 | 6486.8408
May | 18576.5463 | 15.9073 | 171.472 | 0 | 0.0001 | 1034630 | 6952.5282
June | 18797.3709 | 16.0945 | 173.8474 | 0 | 0.0001 | 1048960 | 7036.2031
July | 19596.923 | 16.7782 | 181.3957 | 0 | 0.0001 | 1094510 | 7335.959
August | 22484.2077 | 19.2495 | 208.2406 | 0 | 0.0001 | 1256490 | 8417.1559
September | 19455.2454 | 16.6569 | 180.0806 | 0 | 0.0001 | 1086570 | 7282.9119
October | 18596.5161 | 15.9233 | 171.8428 | 0 | 0.0001 | 1036870 | 6960.5712
November | 17754.4479 | 15.2093 | 162.8046 | 0 | 0.0001 | 982328.3683 | 6641.5548
December | 17780.1999 | 15.2467 | 160.2941 | 0 | 0.0001 | 967170.6811 | 6642.8079
Annual Sum or Average | 223898.1889 | 191.8123 | 2051.279 | 0 | 0.0009 | 12377000 | 83749.9107
Minimum of Months | 16256.1125 | 13.9403 | 146.4714 | 0 | 0.0001 | 883768.1868 | 6073.1463
Maximum of Months | 22484.2077 | 19.2495 | 208.2406 | 0 | 0.0001 | 1256490 | 8417.1559
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 201128000000 | 225783.752 | 26-JAN-13:09 | 75734.208 | 51598.363 | 36916.39 | 0 | 61526.351 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 181206000000 | 220492.433 | 13-FEB-11:00 | 75734.208 | 49992.869 | 36916.39 | 0 | 57840.526 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 214170000000 | 221369.73 | 30-MAR-12:39 | 75734.208 | 51598.363 | 36916.39 | 0 | 57112.329 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 196878000000 | 231556.526 | 11-APR-15:00 | 75734.208 | 50956.166 | 36916.39 | 0 | 67941.323 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 212138000000 | 237333.326 | 30-MAY-10:20 | 75734.208 | 49992.869 | 36916.39 | 0 | 74681.419 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 215077000000 | 232257.452 | 28-JUN-12:00 | 75734.208 | 51598.363 | 36916.39 | 0 | 68000.051 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 224415000000 | 241225.569 | 24-JUL-15:09 | 75734.208 | 50956.166 | 36916.39 | 0 | 77610.366 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 257627000000 | 258326.786 | 09-AUG-14:09 | 75734.208 | 48066.275 | 36916.39 | 0 | 97601.473 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 222788000000 | 250389.464 | 25-SEP-12:00 | 75734.208 | 51598.363 | 36916.39 | 0 | 86132.063 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 212597000000 | 236984.999 | 05-OCT-12:00 | 75734.208 | 51598.363 | 36916.39 | 0 | 72727.598 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 201414000000 | 226641.366 | 20-NOV-13:50 | 75734.208 | 51598.363 | 36916.39 | 0 | 62383.965 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 198306000000 | 227516.338 | 19-DEC-13:09 | 75734.208 | 51598.363 | 36916.39 | 0 | 63258.937 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2537740000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 181206000000 | 220492.433 |  | 75734.208 | 48066.275 | 36916.39 | 0 | 57112.329 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 257627000000 | 258326.786 |  | 75734.208 | 51598.363 | 36916.39 | 0 | 97601.473 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 96426.9 | 654.48 | 0 | 97081.39
Cost per Total Building Area ($/m2) | 19.35 | 0.13 | 0 | 19.49
Cost per Net Conditioned Building Area ($/m2) | 19.35 | 0.13 | 0 | 19.49

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3324.33 | 667.24 | 667.24
Net Site Energy | 3324.33 | 667.24 | 667.24
Total Source Energy | 11465.74 | 2301.35 | 2301.35
Net Source Energy | 11465.74 | 2301.35 | 2301.35
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 139.05 | 0 | 0 | 0 | 0
Cooling | 631.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 814.12 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 32.13 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3153.15 | 171.17 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 62080.87 | 48168.71 | 13912.16 | 0.78 | 4.02
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23666.72 | 18777.53 | 4889.19 | 0.79 | 3.58
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24051.71 | 19209.03 | 4842.69 | 0.8 | 3.6
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18160.98 | 14182.17 | 3978.8 | 0.78 | 3.56
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31393.92 | 25072.92 | 6321 | 0.8 | 3.56
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 66346.8 | 52909.5 | 13437.3 | 0.8 | 4.16
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28584.02 | 22828.78 | 5755.24 | 0.8 | 3.6
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27910.92 | 22291.2 | 5619.72 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22453.53 | 17932.63 | 4520.9 | 0.8 | 3.6
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34748.41 | 27752 | 6996.41 | 0.8 | 3.56
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 79988.16 | 61363.32 | 18624.85 | 0.77 | 3.75
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31271.06 | 24974.8 | 6296.26 | 0.8 | 3.56
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27042.16 | 21597.36 | 5444.8 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26239.54 | 20956.34 | 5283.19 | 0.8 | 3.6
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37248.32 | 29748.57 | 7499.75 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 88158.29 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 32773.33 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 32661.94 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 25015.17 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 42085.32 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 98286.61 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 39517.41 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 37615.11 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 31649.2 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 46390.71 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 107271.07 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 42966.09 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 36500.06 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 36508.36 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 49599.23 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.52 | 6710.75 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.41 | 1605.5 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.45 | 1655.21 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.04 | 1189.51 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.9 | 2074.07 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4 | 7620.33 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1967.12 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.69 | 1920.79 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.36 | 1545.22 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.1 | 2295.69 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.42 | 8427.18 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.89 | 2065.95 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.63 | 1861.01 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.59 | 1805.77 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.25 | 2460.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 51375.4324 | 82.0561 | 333.1308 | 0 | 0.0006 | 1661340 | 21462.7809
February | 43561.1145 | 70.7399 | 293.408 | 0 | 0.0006 | 1463280 | 18319.2975
March | 51653.3996 | 83.9583 | 348.639 | 0 | 0.0007 | 1738730 | 21730.4637
April | 52169.7015 | 85.3949 | 357.739 | 0 | 0.0007 | 1784140 | 22009.7643
May | 62081.4031 | 101.6952 | 426.4217 | 0 | 0.0008 | 2126680 | 26199.3086
June | 73926.8314 | 121.144 | 508.207 | 0 | 0.001 | 2534560 | 31202.9285
July | 76267.7878 | 124.988 | 524.3733 | 0 | 0.001 | 2615190 | 32191.8083
August | 79892.6259 | 130.9288 | 549.2997 | 0 | 0.001 | 2739500 | 33721.8581
September | 66278.7007 | 108.6022 | 455.5471 | 0 | 0.0009 | 2271930 | 27973.8964
October | 55376.7369 | 90.6745 | 380.0131 | 0 | 0.0007 | 1895220 | 23365.9003
November | 46853.3711 | 76.2846 | 317.4472 | 0 | 0.0006 | 1583180 | 19724.4443
December | 49165.2734 | 79.0617 | 323.8343 | 0 | 0.0006 | 1615000 | 20595.1306
Annual Sum or Average | 708602.3784 | 1155.5282 | 4818.0603 | 0 | 0.009 | 24028800 | 298497.5814
Minimum of Months | 43561.1145 | 70.7399 | 293.408 | 0 | 0.0006 | 1463280 | 18319.2975
Maximum of Months | 79892.6259 | 130.9288 | 549.2997 | 0 | 0.001 | 2739500 | 33721.8581
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 218007000000 | 185363.921 | 18-JAN-13:30 | 75734.208 | 51598.363 | 45204.943 | 0 | 12817.967 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 192018000000 | 199950.094 | 08-FEB-13:00 | 75734.208 | 51598.363 | 45204.943 | 0 | 27404.139 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 228163000000 | 233178.064 | 31-MAR-15:09 | 75734.208 | 50956.166 | 45204.943 | 0 | 61274.308 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 234122000000 | 264464.313 | 21-APR-15:09 | 75734.208 | 50956.166 | 45204.943 | 0 | 92560.556 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 279071000000 | 282086.388 | 31-MAY-15:00 | 75734.208 | 50956.166 | 45204.943 | 0 | 110182.631 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 332596000000 | 324601.873 | 27-JUN-15:00 | 75734.208 | 50956.166 | 45204.943 | 0 | 152698.117 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 343176000000 | 321114.3 | 24-JUL-15:00 | 75734.208 | 50956.166 | 45204.943 | 0 | 149210.544 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 359489000000 | 310978.969 | 04-AUG-15:20 | 75734.208 | 50956.166 | 45204.943 | 0 | 139075.212 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 298132000000 | 302351.017 | 01-SEP-15:09 | 75734.208 | 50956.166 | 45204.943 | 0 | 130447.26 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 248699000000 | 268116.022 | 03-OCT-15:09 | 75734.208 | 50956.166 | 45204.943 | 0 | 96212.265 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 207751000000 | 214516.371 | 10-NOV-13:00 | 75734.208 | 51598.363 | 45204.943 | 0 | 41970.416 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 211926000000 | 207045.89 | 05-DEC-13:00 | 75734.208 | 51598.363 | 45204.943 | 0 | 34499.935 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3153150000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 192018000000 | 185363.921 |  | 75734.208 | 50956.166 | 45204.943 | 0 | 12817.967 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 359489000000 | 324601.873 |  | 75734.208 | 51598.363 | 45204.943 | 0 | 152698.117 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 88522.75 | 1315.85 | 0 | 89838.61
Cost per Total Building Area ($/m2) | 17.77 | 0.26 | 0 | 18.03
Cost per Net Conditioned Building Area ($/m2) | 17.77 | 0.26 | 0 | 18.03

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2573.71 | 516.58 | 516.58
Net Site Energy | 2573.71 | 516.58 | 516.58
Total Source Energy | 7528.45 | 1511.07 | 1511.07
Net Source Energy | 7528.45 | 1511.07 | 1511.07
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 180.27 | 0 | 0 | 0 | 0
Cooling | 75.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 572.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 37.99 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2355.45 | 218.26 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 48872.09 | 38952.05 | 9920.04 | 0.8 | 3.35
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31189.84 | 24909.93 | 6279.91 | 0.8 | 3.56
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18075.38 | 14436 | 3639.38 | 0.8 | 3.61
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9543.21 | 7247.71 | 2295.5 | 0.76 | 3.52
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24567.64 | 19621.08 | 4946.57 | 0.8 | 3.6
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64488.59 | 51504.15 | 12984.44 | 0.8 | 4.17
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35635.63 | 28460.58 | 7175.05 | 0.8 | 3.56
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20932.2 | 16717.61 | 4214.59 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12948.9 | 10142.18 | 2806.72 | 0.78 | 3.59
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27060.56 | 21612.06 | 5448.5 | 0.8 | 3.6
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54247.03 | 43023.19 | 11223.84 | 0.79 | 3.34
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35654.86 | 28475.94 | 7178.92 | 0.8 | 3.56
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19093.8 | 15249.37 | 3844.44 | 0.8 | 3.61
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13834.23 | 10915.86 | 2918.36 | 0.79 | 3.6
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27570.95 | 22019.69 | 5551.27 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 78937.59 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 45707.9 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 26617.81 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 14239.74 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 35632.07 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 100917.77 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 51880.76 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 30584.46 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 19627.47 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 39093.45 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 85562.37 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 51907.59 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 28031.95 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 21108.31 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 39802.22 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.94 | 3214.42 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.88 | 2060.59 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.09 | 1243.92 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 597.41 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.48 | 1690.71 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.9 | 7430.88 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.15 | 2354.3 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.26 | 1440.53 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 869.3 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.63 | 1862.27 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.23 | 3529.71 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.15 | 2355.57 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.15 | 1314.01 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.81 | 944.03 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.67 | 1897.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19750.6821 | 17.0522 | 157.347 | 0 | 0.0001 | 949317.9039 | 7315.8039
February | 16226.4444 | 13.9427 | 141.2267 | 0 | 0.0001 | 852106.1395 | 6046.8768
March | 19098.1836 | 16.4168 | 165.0452 | 0 | 0.0001 | 995813.2992 | 7113.4599
April | 17173.8364 | 14.7433 | 151.8666 | 0 | 0.0001 | 916311.583 | 6407.2327
May | 18052.6237 | 15.4762 | 163.4953 | 0 | 0.0001 | 986488.6816 | 6746.8611
June | 17900.4995 | 15.3359 | 163.8766 | 0 | 0.0001 | 988795.4136 | 6695.374
July | 17297.9434 | 14.8159 | 159.0345 | 0 | 0.0001 | 959581.719 | 6472.0553
August | 18893.8188 | 16.1829 | 173.686 | 0 | 0.0001 | 1047990 | 7069.0916
September | 17695.4737 | 15.1563 | 162.7082 | 0 | 0.0001 | 981748.0066 | 6620.8495
October | 17653.0732 | 15.1282 | 160.8607 | 0 | 0.0001 | 970595.8476 | 6600.5381
November | 17125.6904 | 14.7005 | 151.7081 | 0 | 0.0001 | 915356.0926 | 6390.0856
December | 18649.9015 | 16.0765 | 153.1121 | 0 | 0.0001 | 923785.0768 | 6921.9013
Annual Sum or Average | 215518.1706 | 185.0274 | 1903.9672 | 0 | 0.0009 | 11487900 | 80400.1297
Minimum of Months | 16226.4444 | 13.9427 | 141.2267 | 0 | 0.0001 | 852106.1395 | 6046.8768
Maximum of Months | 19750.6821 | 17.0522 | 173.686 | 0 | 0.0001 | 1047990 | 7315.8039
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 194646000000 | 168178.809 | 27-JAN-08:00 | 75734.208 | 58341.44 | 32805.068 | 0 | 1289.653 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 174714000000 | 192830.796 | 15-FEB-16:10 | 75734.208 | 50956.166 | 32805.068 | 0 | 33326.914 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 204179000000 | 170990.117 | 01-MAR-08:00 | 75734.208 | 58341.44 | 32805.068 | 0 | 4100.96 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 187878000000 | 200039.424 | 13-APR-15:09 | 75734.208 | 50956.166 | 32805.068 | 0 | 40535.543 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 202267000000 | 211816.752 | 17-MAY-13:00 | 75734.208 | 48066.275 | 32805.068 | 0 | 55202.761 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 202740000000 | 218129.002 | 16-JUN-15:09 | 75734.208 | 50956.166 | 32805.068 | 0 | 58625.12 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 196750000000 | 236567.221 | 03-JUL-12:00 | 75734.208 | 51598.363 | 32805.068 | 0 | 76421.141 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 214876000000 | 225431.068 | 15-AUG-12:09 | 75734.208 | 51598.363 | 32805.068 | 0 | 65284.989 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 201295000000 | 251160.621 | 28-SEP-15:09 | 75734.208 | 50956.166 | 32805.068 | 0 | 91656.739 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 199009000000 | 219067.393 | 31-OCT-12:00 | 75734.208 | 51598.363 | 32805.068 | 0 | 58921.314 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 187682000000 | 170271.273 | 08-NOV-08:00 | 75734.208 | 58341.44 | 32805.068 | 0 | 3382.117 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 189411000000 | 167764.001 | 15-DEC-08:00 | 75734.208 | 58341.44 | 32805.068 | 0 | 874.845 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2355450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 174714000000 | 167764.001 |  | 75734.208 | 48066.275 | 32805.068 | 0 | 874.845 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 214876000000 | 251160.621 |  | 75734.208 | 58341.44 | 32805.068 | 0 | 91656.739 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 99190.42 | 1891.84 | 0 | 101082.25
Cost per Total Building Area ($/m2) | 19.91 | 0.38 | 0 | 20.29
Cost per Net Conditioned Building Area ($/m2) | 19.91 | 0.38 | 0 | 20.29

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3620.28 | 726.64 | 726.64
Net Site Energy | 3620.28 | 726.64 | 726.64
Total Source Energy | 11197.54 | 2247.51 | 2247.51
Net Source Energy | 11197.54 | 2247.51 | 2247.51
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 665.48 | 0 | 0 | 0 | 0
Cooling | 456.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 752.36 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.46 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2916.34 | 703.94 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 66492.57 | 48622.08 | 17870.49 | 0.73 | 3.21
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26813.51 | 20202.87 | 6610.64 | 0.75 | 3.48
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22882.99 | 18246.69 | 4636.3 | 0.8 | 3.59
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18927.06 | 13778.48 | 5148.58 | 0.73 | 3.43
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28172.14 | 22499.83 | 5672.31 | 0.8 | 3.6
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 77243.91 | 59135.43 | 18108.48 | 0.77 | 3.74
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29849.63 | 22802.8 | 7046.83 | 0.76 | 3.5
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25357.29 | 20251.74 | 5105.56 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21893.43 | 16309.43 | 5584 | 0.74 | 3.46
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30407.14 | 24284.82 | 6122.32 | 0.8 | 3.56
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73782.14 | 56123.15 | 17658.99 | 0.76 | 3.71
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31127.81 | 23879.19 | 7248.62 | 0.77 | 3.51
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24405.39 | 19491.49 | 4913.9 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24189.2 | 18266.13 | 5923.07 | 0.76 | 3.48
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32051.4 | 25598.02 | 6453.38 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 95389.27 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 36795.33 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 34234.21 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 25423.85 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 41652.12 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 117478.64 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 41649.12 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 37762.22 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 30131.4 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 44740.65 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 111767.12 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 43624.06 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 36446.49 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 33766.78 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 47012.6 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.28 | 3587.4 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.42 | 1618.43 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.38 | 1569.36 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.92 | 1052.14 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.7 | 1938.77 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.25 | 8099.62 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.63 | 1860.15 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.53 | 1745.06 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.13 | 1286.57 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.84 | 2008.88 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4 | 7623.16 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.72 | 1958.51 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.47 | 1679.55 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.29 | 1467.62 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.94 | 2117.51 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 48998.9602 | 85.481 | 226.6161 | 0 | 0.0009 | 14090.7874 | 20707.9788
February | 41252.6167 | 74.3563 | 203.9816 | 0 | 0.0008 | 12684.3084 | 17652.6676
March | 41970.2459 | 80.1482 | 232.3683 | 0 | 0.0009 | 14451.1017 | 18371.0734
April | 36915.4539 | 72.4541 | 215.1977 | 0 | 0.0009 | 13383.884 | 16337.609
May | 41769.1299 | 83.1059 | 249.7064 | 0 | 0.001 | 15530.4337 | 18588.5994
June | 48315.7176 | 96.4269 | 290.4755 | 0 | 0.0012 | 18066.1498 | 21529.0665
July | 48776.6906 | 97.3632 | 293.3369 | 0 | 0.0012 | 18244.1201 | 21735.9628
August | 52656.229 | 105.1129 | 316.7 | 0 | 0.0013 | 19697.1903 | 23465.3003
September | 42215.4071 | 84.212 | 253.5788 | 0 | 0.001 | 15771.3447 | 18807.1536
October | 40206.1927 | 79.2704 | 236.3553 | 0 | 0.001 | 14699.8559 | 17826.6802
November | 38909.104 | 74.9473 | 218.9806 | 0 | 0.0009 | 13618.7206 | 17090.1197
December | 44926.3363 | 80.6002 | 220.0606 | 0 | 0.0009 | 13684.0249 | 19190.1614
Annual Sum or Average | 526912.0839 | 1013.4784 | 2957.3578 | 0 | 0.012 | 183921.9215 | 231302.3726
Minimum of Months | 36915.4539 | 72.4541 | 203.9816 | 0 | 0.0008 | 12684.3084 | 16337.609
Maximum of Months | 52656.229 | 105.1129 | 316.7 | 0 | 0.0013 | 19697.1903 | 23465.3003
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 223429000000 | 185100.362 | 05-JAN-13:00 | 75734.208 | 51598.363 | 39612.729 | 0 | 18146.622 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 201128000000 | 183695.578 | 16-FEB-13:00 | 75734.208 | 51598.363 | 39612.729 | 0 | 16741.838 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 229143000000 | 218708.721 | 09-MAR-16:10 | 75734.208 | 50956.166 | 39612.729 | 0 | 52397.179 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 212220000000 | 228185.564 | 05-APR-15:39 | 75734.208 | 50956.166 | 39612.729 | 0 | 61874.022 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 246257000000 | 247875.895 | 31-MAY-15:39 | 75734.208 | 50956.166 | 39612.729 | 0 | 81564.353 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 286464000000 | 282810.452 | 30-JUN-15:00 | 75734.208 | 50956.166 | 39612.729 | 0 | 116498.91 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 289286000000 | 291492.322 | 25-JUL-12:00 | 75734.208 | 51598.363 | 39612.729 | 0 | 124538.582 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 312327000000 | 290436.902 | 17-AUG-15:09 | 75734.208 | 50956.166 | 39612.729 | 0 | 124125.36 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 250077000000 | 265960.542 | 08-SEP-15:09 | 75734.208 | 50956.166 | 39612.729 | 0 | 99649 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 233087000000 | 244925.704 | 12-OCT-15:09 | 75734.208 | 50956.166 | 39612.729 | 0 | 78614.162 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 215944000000 | 227658.48 | 03-NOV-13:00 | 75734.208 | 48066.275 | 39612.729 | 0 | 64236.828 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 216979000000 | 180254.78 | 06-DEC-13:00 | 75734.208 | 51598.363 | 39612.729 | 0 | 13301.04 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2916340000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 201128000000 | 180254.78 |  | 75734.208 | 48066.275 | 39612.729 | 0 | 13301.04 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 312327000000 | 291492.322 |  | 75734.208 | 51598.363 | 39612.729 | 0 | 124538.582 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 64044.68 | 6802.66 | 0 | 70847.35
Cost per Total Building Area ($/m2) | 12.85 | 1.37 | 0 | 14.22
Cost per Net Conditioned Building Area ($/m2) | 12.85 | 1.37 | 0 | 14.22

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3246.58 | 651.64 | 651.64
Net Site Energy | 3246.58 | 651.64 | 651.64
Total Source Energy | 9842.55 | 1975.55 | 1975.55
Net Source Energy | 9842.55 | 1975.55 | 1975.55
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 379.72 | 0 | 0 | 0 | 0
Cooling | 320.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 800.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 37.89 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2828.97 | 417.61 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64351.33 | 51394.53 | 12956.8 | 0.8 | 4.17
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20818.92 | 16627.14 | 4191.78 | 0.8 | 3.6
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23470.46 | 18744.8 | 4725.65 | 0.8 | 3.6
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15630.48 | 12483.37 | 3147.11 | 0.8 | 3.61
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31292.5 | 24991.92 | 6300.58 | 0.8 | 3.56
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 67621.66 | 54006.4 | 13615.27 | 0.8 | 4.17
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24945.97 | 19923.23 | 5022.74 | 0.8 | 3.6
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26476.95 | 21145.95 | 5330.99 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19387.12 | 15483.62 | 3903.49 | 0.8 | 3.6
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34055.94 | 27198.95 | 6856.98 | 0.8 | 3.56
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 66385.91 | 53019.45 | 13366.45 | 0.8 | 4.17
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25865.15 | 20657.34 | 5207.81 | 0.8 | 3.6
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24153.38 | 19290.22 | 4863.16 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22247.18 | 17767.82 | 4479.35 | 0.8 | 3.6
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35617.3 | 28445.94 | 7171.36 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 89313.22 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 27121.59 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 28929.77 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 21192.55 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 37868.33 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 93048.92 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 31837.69 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 32365.39 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 25485.37 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 41026.18 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 91637.39 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 32887.85 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 29709.93 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 28753.5 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 42810.14 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.89 | 7415.07 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.26 | 1432.73 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.42 | 1615.21 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.94 | 1075.67 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.89 | 2067.37 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.09 | 7791.9 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.51 | 1716.75 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1822.11 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.17 | 1334.2 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.06 | 2249.94 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.01 | 7649.51 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.56 | 1780.01 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.46 | 1662.2 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.34 | 1531.02 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.15 | 2353.09 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 64279.7995 | 108.0522 | 269.3028 | 0 | 0.0011 | 280003.5275 | 27122.8671
February | 55091.0708 | 93.8759 | 237.6782 | 0 | 0.0009 | 247131.0685 | 23370.22
March | 61827.8943 | 106.3972 | 272.3805 | 0 | 0.0011 | 283220.6074 | 26330.2254
April | 55527.5779 | 96.7831 | 251.2706 | 0 | 0.001 | 261278.6742 | 23767.5948
May | 66145.7481 | 115.8462 | 302.3282 | 0 | 0.0012 | 314373.3822 | 28367.0405
June | 71823.5856 | 125.8834 | 328.7837 | 0 | 0.0013 | 341883.4993 | 30811.1555
July | 74504.0375 | 130.5971 | 341.1395 | 0 | 0.0013 | 354731.6615 | 31962.5769
August | 77156.4462 | 135.2441 | 353.2714 | 0 | 0.0014 | 367346.9304 | 33100.2377
September | 64322.7819 | 112.7305 | 294.413 | 0 | 0.0011 | 306143.371 | 27592.806
October | 58281.9038 | 101.6512 | 264.0991 | 0 | 0.001 | 274618.5357 | 24953.1452
November | 57893.7684 | 99.3842 | 253.7343 | 0 | 0.001 | 263830.6848 | 24631.0018
December | 62882.3186 | 105.6666 | 263.2504 | 0 | 0.001 | 273710.3724 | 26529.6187
Annual Sum or Average | 769736.9328 | 1332.1118 | 3431.6517 | 0 | 0.0134 | 3568270 | 328538.4896
Minimum of Months | 55091.0708 | 93.8759 | 237.6782 | 0 | 0.0009 | 247131.0685 | 23370.22
Maximum of Months | 77156.4462 | 135.2441 | 353.2714 | 0 | 0.0014 | 367346.9304 | 33100.2377
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 221990000000 | 177580.865 | 02-JAN-08:09 | 75734.208 | 58341.44 | 43496.777 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 195928000000 | 196549.599 | 14-FEB-16:10 | 75734.208 | 50956.166 | 43496.777 | 0 | 26354.009 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 224541000000 | 200971.056 | 02-MAR-14:00 | 75734.208 | 48066.275 | 43496.777 | 0 | 33665.355 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 207145000000 | 236560.433 | 21-APR-15:30 | 75734.208 | 50956.166 | 43496.777 | 0 | 66364.842 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 249239000000 | 250318.79 | 31-MAY-15:00 | 75734.208 | 50956.166 | 43496.777 | 0 | 80123.199 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 271049000000 | 266738.862 | 29-JUN-15:20 | 75734.208 | 50956.166 | 43496.777 | 0 | 96543.271 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 281236000000 | 277276.937 | 31-JUL-15:09 | 75734.208 | 50956.166 | 43496.777 | 0 | 107081.347 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 291237000000 | 272816.748 | 01-AUG-15:09 | 75734.208 | 50956.166 | 43496.777 | 0 | 102621.158 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 242714000000 | 251796.903 | 05-SEP-13:50 | 75734.208 | 48066.275 | 43496.777 | 0 | 84491.203 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 217721000000 | 235544.339 | 13-OCT-15:09 | 75734.208 | 50956.166 | 43496.777 | 0 | 65348.748 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 209168000000 | 185070.842 | 08-NOV-14:00 | 75734.208 | 48066.275 | 43496.777 | 0 | 17765.142 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 217001000000 | 177580.865 | 01-DEC-08:09 | 75734.208 | 58341.44 | 43496.777 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2828970000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 195928000000 | 177580.865 |  | 75734.208 | 48066.275 | 43496.777 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 291237000000 | 277276.937 |  | 75734.208 | 58341.44 | 43496.777 | 0 | 107081.347 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29211.34 | 2866.86 | 0 | 32078.21
Cost per Total Building Area ($/m2) | 5.86 | 0.58 | 0 | 6.44
Cost per Net Conditioned Building Area ($/m2) | 5.86 | 0.58 | 0 | 6.44

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3068.06 | 615.81 | 615.81
Net Site Energy | 3068.06 | 615.81 | 615.81
Total Source Energy | 4974.19 | 998.4 | 998.4
Net Source Energy | 4974.19 | 998.4 | 998.4
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 529.77 | 0 | 0 | 0 | 0
Cooling | 71.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 718.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.02 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2498.27 | 569.79 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 195.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53915.89 | 42830.82 | 11085.07 | 0.79 | 3.34
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31243.84 | 24953.06 | 6290.78 | 0.8 | 3.56
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20266.18 | 16185.69 | 4080.49 | 0.8 | 3.6
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13222.66 | 10079.38 | 3143.28 | 0.76 | 3.53
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25841.73 | 20638.63 | 5203.1 | 0.8 | 3.6
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 67376.1 | 53810.28 | 13565.82 | 0.8 | 4.17
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35748.15 | 28550.45 | 7197.7 | 0.8 | 3.56
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23163.13 | 18499.36 | 4663.77 | 0.8 | 3.6
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15167.44 | 11884.4 | 3283.04 | 0.78 | 3.59
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28548.83 | 22800.68 | 5748.16 | 0.8 | 3.6
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 59769.33 | 47735.09 | 12034.24 | 0.8 | 4.17
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36127.32 | 28853.27 | 7274.05 | 0.8 | 3.56
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21587.91 | 17241.29 | 4346.61 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17294.22 | 13670.69 | 3623.53 | 0.79 | 3.59
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29507.33 | 23566.19 | 5941.15 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 89058.79 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 46182.63 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 29903.7 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 19710.42 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 37539.55 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 108340.38 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 52351.38 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 33871.19 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 23311.85 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 41247.03 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 97926.54 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 52870.56 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 31713.78 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 26551.3 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 42559.66 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.22 | 3520.79 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.89 | 2064.15 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.22 | 1394.69 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.72 | 834.85 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.56 | 1778.39 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.07 | 7763.61 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.16 | 2361.74 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.4 | 1594.06 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.88 | 1019.11 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.72 | 1964.69 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.61 | 6887.09 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.18 | 2386.79 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.3 | 1485.65 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.02 | 1163.69 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.78 | 1949.43 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16962.2556 | 22.6346 | 46.2823 | 0 | 0.0002 | 611330.4089 | 6645.8204
February | 12784.2226 | 17.9391 | 40.4987 | 0 | 0.0002 | 535077.2959 | 5103.0763
March | 14306.0676 | 20.3341 | 46.9769 | 0 | 0.0002 | 620703.3569 | 5738.3482
April | 11382.114 | 16.8825 | 41.8733 | 0 | 0.0002 | 553362.9881 | 4640.96
May | 10684.6875 | 16.7191 | 44.8686 | 0 | 0.0002 | 593049.4003 | 4449.8729
June | 10401.1497 | 16.4987 | 45.1037 | 0 | 0.0002 | 596179.3549 | 4355.7029
July | 10449.6163 | 16.6573 | 45.8354 | 0 | 0.0002 | 605859.6528 | 4384.7483
August | 11251.106 | 17.9471 | 49.4291 | 0 | 0.0002 | 653362.8936 | 4722.3703
September | 10288.8677 | 16.2323 | 44.0529 | 0 | 0.0002 | 582281.168 | 4299.2236
October | 10813.8503 | 16.5313 | 42.9221 | 0 | 0.0002 | 567280.8968 | 4461.9157
November | 13642.4536 | 19.2247 | 43.7368 | 0 | 0.0002 | 577869.5711 | 5454.3661
December | 16786.3118 | 22.2666 | 44.9517 | 0 | 0.0002 | 593734.2359 | 6562.6192
Annual Sum or Average | 149752.7028 | 219.8673 | 536.5313 | 0 | 0.0021 | 7090090 | 60819.0237
Minimum of Months | 10288.8677 | 16.2323 | 40.4987 | 0 | 0.0002 | 535077.2959 | 4299.2236
Maximum of Months | 16962.2556 | 22.6346 | 49.4291 | 0 | 0.0002 | 653362.8936 | 6645.8204
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 215409000000 | 172252.822 | 02-JAN-08:09 | 75734.208 | 58341.44 | 38168.734 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 188540000000 | 172348.601 | 22-FEB-08:50 | 75734.208 | 58341.44 | 38168.734 | 0 | 95.779 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 218712000000 | 179476.877 | 29-MAR-15:30 | 75734.208 | 50956.166 | 38168.734 | 0 | 14609.33 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 194983000000 | 172338.887 | 27-APR-07:49 | 75734.208 | 58341.44 | 38168.734 | 0 | 86.065 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 208967000000 | 220360.321 | 04-MAY-15:09 | 75734.208 | 50956.166 | 38168.734 | 0 | 55492.774 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 210070000000 | 231654.555 | 28-JUN-15:09 | 75734.208 | 50956.166 | 38168.734 | 0 | 66787.008 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 213481000000 | 246195.289 | 24-JUL-15:09 | 75734.208 | 50956.166 | 38168.734 | 0 | 81327.742 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 230219000000 | 242992.805 | 07-AUG-15:09 | 75734.208 | 50956.166 | 38168.734 | 0 | 78125.258 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 205173000000 | 239975.581 | 01-SEP-15:30 | 75734.208 | 50956.166 | 38168.734 | 0 | 75108.034 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 199888000000 | 193566.65 | 17-OCT-12:00 | 75734.208 | 51598.363 | 38168.734 | 0 | 28056.905 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 203619000000 | 172252.822 | 01-NOV-07:10 | 75734.208 | 58341.44 | 38168.734 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 209209000000 | 172252.822 | 01-DEC-08:09 | 75734.208 | 58341.44 | 38168.734 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2498270000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 188540000000 | 172252.822 |  | 75734.208 | 50956.166 | 38168.734 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 230219000000 | 246195.289 |  | 75734.208 | 58341.44 | 38168.734 | 0 | 81327.742 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 53923 | 4817.82 | 0 | 58740.82
Cost per Total Building Area ($/m2) | 10.82 | 0.97 | 0 | 11.79
Cost per Net Conditioned Building Area ($/m2) | 10.82 | 0.97 | 0 | 11.79

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3671.6 | 736.94 | 736.94
Net Site Energy | 3671.6 | 736.94 | 736.94
Total Source Energy | 10588.03 | 2125.18 | 2125.18
Net Source Energy | 10588.03 | 2125.18 | 2125.18
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 949.73 | 0 | 0 | 0 | 0
Cooling | 268.27 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 704.61 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.08 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2680.79 | 990.81 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 195.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 456.98 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 66476.81 | 48820.98 | 17655.83 | 0.73 | 3.22
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22551.1 | 16168.02 | 6383.08 | 0.72 | 3.39
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17157.25 | 13379.06 | 3778.19 | 0.78 | 3.56
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24583.97 | 16986.51 | 7597.46 | 0.69 | 3.33
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21186.04 | 16579.26 | 4606.78 | 0.78 | 3.55
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76333.5 | 58937.27 | 17396.24 | 0.77 | 3.77
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22826.27 | 16839.58 | 5986.69 | 0.74 | 3.44
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19567.48 | 15489.88 | 4077.6 | 0.79 | 3.58
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22212.21 | 16528.24 | 5683.97 | 0.74 | 3.45
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23265.55 | 18386.72 | 4878.83 | 0.79 | 3.57
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73431.95 | 56374.37 | 17057.59 | 0.77 | 3.75
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30330.44 | 22462.93 | 7867.52 | 0.74 | 3.45
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18845.27 | 14856.83 | 3988.44 | 0.79 | 3.58
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31507.65 | 22942.42 | 8565.23 | 0.73 | 3.42
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24405.11 | 19378.56 | 5026.55 | 0.79 | 3.58
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 100553.65 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 29322.83 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 25592.91 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 29109.69 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 31002.55 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 122228.33 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 31366.29 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 29554.68 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 31193.8 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 34369.94 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 117381.08 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 40195.03 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 28365.12 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 40092 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 36219.92 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.31 | 3624.36 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.06 | 1207.05 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.98 | 1120.16 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.05 | 1196.25 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.22 | 1394.15 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.28 | 8160.5 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.15 | 1310.55 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.16 | 1320.82 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.14 | 1301.81 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.37 | 1564.71 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.06 | 7749.2 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.54 | 1757.74 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.11 | 1260.58 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.54 | 1752.52 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.46 | 1658.43 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 88723.3203 | 148.159 | 405.7593 | 0 | 0.0013 | 93393.0056 | 37172.9049
February | 76228.2466 | 129.8193 | 363.7567 | 0 | 0.0011 | 83729.2685 | 32179.2646
March | 82188.1447 | 143.7246 | 414.7098 | 0 | 0.0013 | 95463.2008 | 35054.2562
April | 68720.814 | 123.4723 | 366.5285 | 0 | 0.0011 | 84376.8613 | 29625.635
May | 76505.538 | 138.8408 | 416.3306 | 0 | 0.0013 | 95843.4061 | 33113.7232
June | 87753.9366 | 159.6322 | 479.8085 | 0 | 0.0014 | 110457.1342 | 38018.4825
July | 89656.5766 | 163.1104 | 490.3144 | 0 | 0.0015 | 112875.7431 | 38844.424
August | 92813.9324 | 168.8529 | 507.5717 | 0 | 0.0015 | 116848.5593 | 40212.2192
September | 75607.9026 | 137.4783 | 413.0434 | 0 | 0.0012 | 95087.0167 | 32750.6823
October | 71438.821 | 128.9978 | 384.8734 | 0 | 0.0012 | 88600.8065 | 30858.746
November | 73975.7382 | 130.4784 | 379.9554 | 0 | 0.0012 | 87464.5559 | 31658.1712
December | 84032.687 | 142.284 | 396.0444 | 0 | 0.0012 | 91159.9983 | 35394.837
Annual Sum or Average | 967645.658 | 1714.8501 | 5018.6961 | 0 | 0.0152 | 1155300 | 414883.3463
Minimum of Months | 68720.814 | 123.4723 | 363.7567 | 0 | 0.0011 | 83729.2685 | 29625.635
Maximum of Months | 92813.9324 | 168.8529 | 507.5717 | 0 | 0.0015 | 116848.5593 | 40212.2192
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 216711000000 | 170573.988 | 17-JAN-08:00 | 75734.208 | 58341.44 | 36378.832 | 0 | 111.068 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 194287000000 | 170682.727 | 28-FEB-08:00 | 75734.208 | 58341.44 | 36378.832 | 0 | 219.806 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 221515000000 | 189916.294 | 31-MAR-15:09 | 75734.208 | 50956.166 | 36378.832 | 0 | 26838.648 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 195790000000 | 192564.089 | 07-APR-14:00 | 75734.208 | 48066.275 | 36378.832 | 0 | 32376.333 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 222397000000 | 236137.847 | 30-MAY-15:00 | 75734.208 | 50956.166 | 36378.832 | 0 | 73060.202 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 256307000000 | 262901.269 | 08-JUN-12:00 | 75734.208 | 51598.363 | 36378.832 | 0 | 99181.426 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 261920000000 | 269364.831 | 03-JUL-15:09 | 75734.208 | 50956.166 | 36378.832 | 0 | 106287.185 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 271138000000 | 263495.03 | 04-AUG-15:39 | 75734.208 | 50956.166 | 36378.832 | 0 | 100417.384 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 220642000000 | 240677.186 | 05-SEP-15:09 | 75734.208 | 50956.166 | 36378.832 | 0 | 77599.541 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 205591000000 | 219398.594 | 31-OCT-12:00 | 75734.208 | 51598.363 | 36378.832 | 0 | 55678.751 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 202955000000 | 214419.382 | 02-NOV-15:09 | 75734.208 | 50956.166 | 36378.832 | 0 | 51341.736 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 211530000000 | 170508.083 | 12-DEC-08:00 | 75734.208 | 58341.44 | 36378.832 | 0 | 45.163 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2680790000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 194287000000 | 170508.083 |  | 75734.208 | 48066.275 | 36378.832 | 0 | 45.163 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 271138000000 | 269364.831 |  | 75734.208 | 58341.44 | 36378.832 | 0 | 106287.185 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 65032.87 | 8185.03 | 0 | 73217.9
Cost per Total Building Area ($/m2) | 13.05 | 1.64 | 0 | 14.7
Cost per Net Conditioned Building Area ($/m2) | 13.05 | 1.64 | 0 | 14.7

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3300.26 | 662.41 | 662.41
Net Site Energy | 3300.26 | 662.41 | 662.41
Total Source Energy | 9443.12 | 1895.38 | 1895.38
Net Source Energy | 9443.12 | 1895.38 | 1895.38
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 636.12 | 0 | 0 | 0 | 0
Cooling | 185.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 730.19 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.94 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2623.2 | 677.06 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 195.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 456.98 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 62682.13 | 50061.41 | 12620.72 | 0.8 | 4.17
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18064.29 | 14427.14 | 3637.15 | 0.8 | 3.61
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15888.04 | 12689.07 | 3198.97 | 0.8 | 3.61
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18906.62 | 14752.99 | 4153.63 | 0.78 | 3.56
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21757.72 | 17376.92 | 4380.8 | 0.8 | 3.6
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 67409.71 | 53837.12 | 13572.59 | 0.8 | 4.17
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19441.4 | 15526.98 | 3914.42 | 0.8 | 3.6
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18873.88 | 15073.72 | 3800.16 | 0.8 | 3.61
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19367.52 | 15467.97 | 3899.55 | 0.8 | 3.6
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24535.1 | 19595.09 | 4940.01 | 0.8 | 3.6
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58310.12 | 46569.68 | 11740.44 | 0.8 | 4.17
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26515.94 | 21177.09 | 5338.84 | 0.8 | 3.6
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17340.29 | 13848.92 | 3491.38 | 0.8 | 3.61
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26486.08 | 21153.25 | 5332.83 | 0.8 | 3.6
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25511.45 | 20374.86 | 5136.6 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 92293.44 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 24995.67 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 20903.09 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 24880.28 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 27598.88 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 97683.81 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 26566.53 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 24309.16 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 26482.25 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 30767.11 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 87308.58 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 34636.38 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 22559.42 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 34602.34 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 31880.5 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.79 | 7222.73 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.09 | 1243.16 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.96 | 1093.39 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.09 | 1236.2 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.31 | 1497.34 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.07 | 7767.48 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.17 | 1337.93 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.14 | 1298.88 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.17 | 1332.85 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.48 | 1688.47 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.52 | 6718.95 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1824.79 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.05 | 1193.34 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1822.74 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.54 | 1755.67 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 65906.9894 | 108.0952 | 261.548 | 0 | 0.001 | 271921.9273 | 27545.3753
February | 56643.8114 | 94.5078 | 233.4761 | 0 | 0.0009 | 242748.3419 | 23831.3527
March | 62686.6282 | 106.563 | 269.0625 | 0 | 0.0011 | 279761.9175 | 26567.2367
April | 54213.9994 | 93.8675 | 241.9377 | 0 | 0.0009 | 251569.9531 | 23143.9257
May | 58187.8799 | 101.4909 | 263.6928 | 0 | 0.001 | 274196.0107 | 24913.2462
June | 61479.3878 | 107.665 | 280.9535 | 0 | 0.0011 | 292147.0063 | 26364.9987
July | 64567.2257 | 113.1502 | 295.4848 | 0 | 0.0012 | 307257.7933 | 27696.813
August | 68632.4422 | 120.2752 | 314.0937 | 0 | 0.0012 | 326608.156 | 29440.7207
September | 57406.5869 | 100.4486 | 261.8865 | 0 | 0.001 | 272319.8417 | 24610.1654
October | 56676.7991 | 98.4107 | 254.439 | 0 | 0.001 | 264570.8641 | 24222.6731
November | 58025.2972 | 98.5292 | 248.4611 | 0 | 0.001 | 258340.5276 | 24580.9494
December | 64420.9718 | 105.9225 | 257.0825 | 0 | 0.001 | 267281.28 | 26950.2508
Annual Sum or Average | 728848.0189 | 1248.9257 | 3182.1181 | 0 | 0.0125 | 3308720 | 309867.7077
Minimum of Months | 54213.9994 | 93.8675 | 233.4761 | 0 | 0.0009 | 242748.3419 | 23143.9257
Maximum of Months | 68632.4422 | 120.2752 | 314.0937 | 0 | 0.0012 | 326608.156 | 29440.7207
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 215583000000 | 174319.363 | 25-JAN-08:00 | 75734.208 | 58341.44 | 39033.921 | 0 | 1201.354 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 192454000000 | 175346.443 | 23-FEB-08:00 | 75734.208 | 58341.44 | 39033.921 | 0 | 2228.435 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 221799000000 | 197812.03 | 30-MAR-15:00 | 75734.208 | 50956.166 | 39033.921 | 0 | 32079.296 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 199448000000 | 211818.393 | 26-APR-15:00 | 75734.208 | 50956.166 | 39033.921 | 0 | 46085.659 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 217386000000 | 225748.756 | 23-MAY-15:00 | 75734.208 | 50956.166 | 39033.921 | 0 | 60016.022 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 231618000000 | 238021.716 | 27-JUN-15:39 | 75734.208 | 50956.166 | 39033.921 | 0 | 72288.982 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 243598000000 | 250145.154 | 17-JUL-15:30 | 75734.208 | 50956.166 | 39033.921 | 0 | 84412.42 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 258939000000 | 246495.164 | 30-AUG-12:00 | 75734.208 | 51598.363 | 39033.921 | 0 | 80120.232 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 215898000000 | 230701.264 | 06-SEP-15:09 | 75734.208 | 50956.166 | 39033.921 | 0 | 64968.53 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 209755000000 | 222919.976 | 05-OCT-15:09 | 75734.208 | 50956.166 | 39033.921 | 0 | 57187.242 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 204815000000 | 187068.837 | 10-NOV-13:00 | 75734.208 | 51598.363 | 39033.921 | 0 | 20693.905 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 211904000000 | 173324.571 | 22-DEC-08:39 | 75734.208 | 58341.44 | 39033.921 | 0 | 206.562 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2623200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 192454000000 | 173324.571 |  | 75734.208 | 50956.166 | 39033.921 | 0 | 206.562 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 258939000000 | 250145.154 |  | 75734.208 | 58341.44 | 39033.921 | 0 | 84412.42 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27100.58 | 4650.76 | 0 | 31751.34
Cost per Total Building Area ($/m2) | 5.44 | 0.93 | 0 | 6.37
Cost per Net Conditioned Building Area ($/m2) | 5.44 | 0.93 | 0 | 6.37

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4152.98 | 833.56 | 833.56
Net Site Energy | 4152.98 | 833.56 | 833.56
Total Source Energy | 10829.04 | 2173.55 | 2173.55
Net Source Energy | 10829.04 | 2173.55 | 2173.55
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1425.63 | 0 | 0 | 0 | 0
Cooling | 233.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 742.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.34 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2684 | 1468.97 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 195.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 456.98 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 65751.04 | 48382.8 | 17368.24 | 0.74 | 3.22
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24365.14 | 17836.08 | 6529.06 | 0.73 | 3.43
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16915.84 | 13274.77 | 3641.07 | 0.78 | 3.57
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27259.13 | 18991.14 | 8267.99 | 0.7 | 3.34
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20400.02 | 16105.2 | 4294.82 | 0.79 | 3.57
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76058.29 | 58919.82 | 17138.47 | 0.77 | 3.79
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24735.81 | 18571.72 | 6164.09 | 0.75 | 3.47
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19239.59 | 15315.12 | 3924.47 | 0.8 | 3.59
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24992.64 | 18613.09 | 6379.55 | 0.74 | 3.46
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22442.03 | 17889.76 | 4552.26 | 0.8 | 3.59
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73643.05 | 56802.02 | 16841.03 | 0.77 | 3.77
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33047.43 | 24835.41 | 8212.02 | 0.75 | 3.47
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19154.32 | 15188.43 | 3965.88 | 0.79 | 3.58
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35227.73 | 25736.88 | 9490.85 | 0.73 | 3.42
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23216.74 | 18542.17 | 4674.57 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 102674.25 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 33054.74 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 25843.12 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 32716.45 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 30715.9 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 125012.03 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 35166.53 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 29652.71 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 34912.31 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 34032.71 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 121065.32 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 44999.28 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 29322.43 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 44859.05 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 35200.25 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.29 | 3601.83 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.21 | 1372.93 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.98 | 1120.11 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.19 | 1355.66 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.2 | 1368.83 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.29 | 8192.21 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.3 | 1480.73 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.15 | 1314.56 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.29 | 1467.75 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.35 | 1538.13 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.12 | 7854.71 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.74 | 1982.63 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.14 | 1297.72 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1975.48 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.4 | 1597.75 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 71776.3841 | 109.7438 | 145.5296 | 0 | 0.0011 | 95584.897 | 29104.3284
February | 58783.9898 | 93.3899 | 130.6195 | 0 | 0.001 | 85810.9354 | 24171.7015
March | 56713.0848 | 96.2295 | 145.9772 | 0 | 0.0011 | 95930.6399 | 23906.0723
April | 45141.9734 | 80.6329 | 129.3386 | 0 | 0.0009 | 85013.7302 | 19414.4223
May | 49915.7259 | 90.6335 | 147.8149 | 0 | 0.0011 | 97163.738 | 21608.361
June | 55018.6327 | 100.2291 | 164.0008 | 0 | 0.0012 | 107804.504 | 23848.9422
July | 55849.6175 | 101.7612 | 166.5371 | 0 | 0.0012 | 109471.8489 | 24210.8924
August | 60070.4353 | 109.4585 | 179.1454 | 0 | 0.0013 | 117759.7839 | 26041.2756
September | 46270.918 | 84.1706 | 137.5265 | 0 | 0.001 | 90401.4371 | 20045.3592
October | 46669.0297 | 83.4032 | 133.8528 | 0 | 0.001 | 87981.0359 | 20075.2486
November | 53532.8288 | 90.7134 | 137.4009 | 0 | 0.001 | 90294.1065 | 22554.0479
December | 65124.591 | 102.7186 | 142.284 | 0 | 0.0011 | 93470.2689 | 26707.7549
Annual Sum or Average | 664867.2109 | 1143.0842 | 1760.0273 | 0 | 0.013 | 1156690 | 281688.4063
Minimum of Months | 45141.9734 | 80.6329 | 129.3386 | 0 | 0.0009 | 85013.7302 | 19414.4223
Maximum of Months | 71776.3841 | 109.7438 | 179.1454 | 0 | 0.0013 | 117759.7839 | 29104.3284
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 221798000000 | 171605.106 | 02-JAN-08:09 | 75734.208 | 58341.44 | 37521.018 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 199118000000 | 171660.769 | 16-FEB-08:00 | 75734.208 | 58341.44 | 37521.018 | 0 | 55.662 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 222600000000 | 176137.954 | 23-MAR-15:30 | 75734.208 | 50956.166 | 37521.018 | 0 | 11918.122 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 197268000000 | 192988.59 | 14-APR-15:00 | 75734.208 | 50956.166 | 37521.018 | 0 | 28768.758 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 225461000000 | 238424.654 | 31-MAY-12:09 | 75734.208 | 51598.363 | 37521.018 | 0 | 73562.624 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 250152000000 | 260001.605 | 29-JUN-15:00 | 75734.208 | 50956.166 | 37521.018 | 0 | 95781.773 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 254021000000 | 259469.472 | 13-JUL-15:00 | 75734.208 | 50956.166 | 37521.018 | 0 | 95249.641 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 273253000000 | 257913.081 | 25-AUG-15:00 | 75734.208 | 50956.166 | 37521.018 | 0 | 93693.249 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 209770000000 | 239230.865 | 14-SEP-15:09 | 75734.208 | 50956.166 | 37521.018 | 0 | 75011.033 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 204153000000 | 199950.92 | 06-OCT-15:09 | 75734.208 | 50956.166 | 37521.018 | 0 | 35731.088 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 209521000000 | 181355.707 | 02-NOV-15:09 | 75734.208 | 50956.166 | 37521.018 | 0 | 17135.875 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 216891000000 | 171605.106 | 01-DEC-08:09 | 75734.208 | 58341.44 | 37521.018 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2684000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 197268000000 | 171605.106 |  | 75734.208 | 50956.166 | 37521.018 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 273253000000 | 260001.605 |  | 75734.208 | 58341.44 | 37521.018 | 0 | 95781.773 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 46928.37 | 11631.95 | 0 | 58560.31
Cost per Total Building Area ($/m2) | 9.42 | 2.33 | 0 | 11.75
Cost per Net Conditioned Building Area ($/m2) | 9.42 | 2.33 | 0 | 11.75

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3666.19 | 735.86 | 735.86
Net Site Energy | 3666.19 | 735.86 | 735.86
Total Source Energy | 10020.6 | 2011.29 | 2011.29
Net Source Energy | 10020.6 | 2011.29 | 2011.29
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1098.48 | 0 | 0 | 0 | 0
Cooling | 107.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 708.77 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.75 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2523.96 | 1142.24 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 195.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 456.98 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 59098.34 | 47199.2 | 11899.14 | 0.8 | 4.17
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21461.61 | 17140.43 | 4321.18 | 0.8 | 3.6
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15328.87 | 12242.48 | 3086.39 | 0.8 | 3.61
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21783.78 | 17180.67 | 4603.11 | 0.79 | 3.57
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20421.82 | 16309.99 | 4111.83 | 0.8 | 3.6
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 65358.16 | 52198.64 | 13159.52 | 0.8 | 4.17
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23016.96 | 18382.61 | 4634.34 | 0.8 | 3.6
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18469.54 | 14750.8 | 3718.75 | 0.8 | 3.61
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22769.43 | 18184.92 | 4584.5 | 0.8 | 3.6
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23267.78 | 18582.94 | 4684.85 | 0.8 | 3.6
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55496.7 | 44322.73 | 11173.97 | 0.8 | 3.35
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31217.67 | 24932.16 | 6285.51 | 0.8 | 3.56
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20421.1 | 16309.42 | 4111.68 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31033.91 | 24785.39 | 6248.51 | 0.8 | 3.56
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23793.37 | 19002.7 | 4790.67 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 97990.57 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 31512.14 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 22048.9 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 31188.99 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 28185.17 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 105528.67 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 33385.97 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 25832.96 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 33087.75 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 31614.09 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 93653.56 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 43266.03 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 28183.9 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 43044.66 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 32246.81 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.57 | 6809.78 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.3 | 1476.96 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.93 | 1054.91 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.28 | 1458.5 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.23 | 1405.4 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.95 | 7531.08 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.39 | 1584 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.12 | 1271.05 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.38 | 1566.96 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.41 | 1601.26 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.35 | 3666.44 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.89 | 2062.43 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.23 | 1405.35 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.87 | 2050.29 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.44 | 1637.43 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 67282.2335 | 105.297 | 160.2441 | 0 | 0.0011 | 3799540 | 27561.3905
February | 56523.5274 | 90.7609 | 142.9433 | 0 | 0.001 | 3389740 | 23376.6685
March | 57400.5742 | 96.6681 | 161.4317 | 0 | 0.0011 | 3828960 | 24174.2768
April | 48121.6886 | 83.1951 | 143.1243 | 0 | 0.001 | 3395070 | 20474.6391
May | 49594.6349 | 87.1873 | 152.7333 | 0 | 0.0011 | 3623220 | 21241.0832
June | 52764.377 | 93.331 | 164.5612 | 0 | 0.0011 | 3903890 | 22653.8925
July | 53788.6685 | 95.3265 | 168.4202 | 0 | 0.0012 | 3995470 | 23111.4241
August | 55663.9601 | 98.6355 | 174.2395 | 0 | 0.0012 | 4133520 | 23915.7766
September | 47691.6586 | 84.2255 | 148.2601 | 0 | 0.001 | 3517160 | 20463.1313
October | 49306.2499 | 85.7804 | 148.5909 | 0 | 0.001 | 3524830 | 21030.5879
November | 54048.8348 | 90.9677 | 151.8037 | 0 | 0.0011 | 3600590 | 22757.3018
December | 63230.4173 | 100.4431 | 155.9728 | 0 | 0.0011 | 3698540 | 26045.3771
Annual Sum or Average | 655416.8246 | 1111.8182 | 1872.3251 | 0 | 0.0131 | 44410500 | 276805.5493
Minimum of Months | 47691.6586 | 83.1951 | 142.9433 | 0 | 0.001 | 3389740 | 20463.1313
Maximum of Months | 67282.2335 | 105.297 | 174.2395 | 0 | 0.0012 | 4133520 | 27561.3905
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 215937000000 | 172844.937 | 02-JAN-08:09 | 75734.208 | 58341.44 | 36581.849 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 192647000000 | 170782.871 | 03-FEB-08:39 | 75734.208 | 58341.44 | 36581.849 | 0 | 116.934 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 217609000000 | 179117.333 | 30-MAR-15:00 | 75734.208 | 50956.166 | 36581.849 | 0 | 15836.67 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 192950000000 | 172087.357 | 14-APR-07:00 | 75734.208 | 58341.44 | 36581.849 | 0 | 1421.42 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 205916000000 | 206537.363 | 16-MAY-15:00 | 75734.208 | 50956.166 | 36581.849 | 0 | 43256.701 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 221868000000 | 244123.321 | 26-JUN-15:09 | 75734.208 | 50956.166 | 36581.849 | 0 | 80842.659 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 227072000000 | 241705.86 | 21-JUL-15:00 | 75734.208 | 50956.166 | 36581.849 | 0 | 78425.198 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 234918000000 | 235003.679 | 09-AUG-15:00 | 75734.208 | 50956.166 | 36581.849 | 0 | 71723.017 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 199889000000 | 222353.353 | 01-SEP-15:00 | 75734.208 | 50956.166 | 36581.849 | 0 | 59072.691 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 200324000000 | 198964.621 | 06-OCT-15:00 | 75734.208 | 50956.166 | 36581.849 | 0 | 35683.959 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 204630000000 | 172844.937 | 01-NOV-07:10 | 75734.208 | 58341.44 | 36581.849 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 210197000000 | 172844.937 | 15-DEC-08:09 | 75734.208 | 58341.44 | 36581.849 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2523960000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 192647000000 | 170782.871 |  | 75734.208 | 50956.166 | 36581.849 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 234918000000 | 244123.321 |  | 75734.208 | 58341.44 | 36581.849 | 0 | 80842.659 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 55491.18 | 9105.33 | 0 | 64596.51
Cost per Total Building Area ($/m2) | 11.14 | 1.83 | 0 | 12.97
Cost per Net Conditioned Building Area ($/m2) | 11.14 | 1.83 | 0 | 12.97

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4444.56 | 892.09 | 892.09
Net Site Energy | 4444.56 | 892.09 | 892.09
Total Source Energy | 10858.66 | 2179.5 | 2179.5
Net Source Energy | 10858.66 | 2179.5 | 2179.5
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1836.63 | 0 | 0 | 0 | 0
Cooling | 104.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 34.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 748.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 47.08 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2560.85 | 1883.71 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 195.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 456.98 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58868.98 | 45054.33 | 13814.65 | 0.77 | 3.28
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24480.38 | 18443.09 | 6037.3 | 0.75 | 3.48
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14235.46 | 11369.22 | 2866.23 | 0.8 | 3.63
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28315.87 | 19998.84 | 8317.03 | 0.71 | 3.36
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18381.46 | 14680.45 | 3701.01 | 0.8 | 3.61
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 68575.71 | 54768.35 | 13807.36 | 0.8 | 4.17
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24680.18 | 19134.07 | 5546.11 | 0.78 | 3.53
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17495 | 13972.47 | 3522.53 | 0.8 | 3.61
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27256.8 | 20175.29 | 7081.51 | 0.74 | 3.45
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21253.74 | 16974.42 | 4279.33 | 0.8 | 3.6
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 61645.49 | 49233.5 | 12412 | 0.8 | 4.17
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 33403.87 | 25820.65 | 7583.22 | 0.77 | 3.49
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20335.99 | 16241.44 | 4094.54 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36119.15 | 26957.19 | 9161.96 | 0.75 | 3.43
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21735.56 | 17359.22 | 4376.34 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 101050.85 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 34749.24 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 22852.02 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 34399.76 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 28325.04 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 120896.64 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 36920.9 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 27154.9 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 36672.07 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 32116.64 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 111753.53 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 47428.56 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 30904.83 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 47307.41 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 32752.14 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.23 | 3536.73 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.3 | 1477.25 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.86 | 997.48 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.28 | 1459.03 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.11 | 1264.99 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.14 | 7901.84 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.4 | 1590.48 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.06 | 1203.98 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.38 | 1577.5 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.28 | 1462.66 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.72 | 7103.28 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.88 | 2052.77 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.23 | 1399.5 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.87 | 2046.7 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.31 | 1495.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 72486.6744 | 110.1565 | 144.7775 | 0 | 0.0011 | 95087.2392 | 29327.9861
February | 62045.5761 | 96.1566 | 130.0035 | 0 | 0.001 | 85394.2719 | 25282.0179
March | 62221.5278 | 101.9344 | 148.2975 | 0 | 0.0011 | 97439.8482 | 25879.9222
April | 48593.3652 | 84.3809 | 131.3576 | 0 | 0.001 | 86331.4925 | 20667.7562
May | 47084.0913 | 84.403 | 135.8836 | 0 | 0.001 | 89316.8601 | 20278.4611
June | 48294.7609 | 87.8536 | 143.5464 | 0 | 0.001 | 94358.5608 | 20922.2591
July | 50021.163 | 91.0837 | 148.9694 | 0 | 0.0011 | 97923.638 | 21678.7318
August | 51856.9433 | 94.327 | 154.1128 | 0 | 0.0011 | 101304.184 | 22464.8355
September | 44089.6367 | 79.6756 | 129.3269 | 0 | 0.0009 | 85009.5688 | 19050.0048
October | 48117.5092 | 84.8058 | 134.1453 | 0 | 0.001 | 88168.7165 | 20584.9595
November | 56688.6246 | 93.5515 | 137.3292 | 0 | 0.001 | 90236.1971 | 23643.742
December | 67979.9917 | 105.1116 | 141.6496 | 0 | 0.0011 | 93042.8515 | 27677.004
Annual Sum or Average | 659479.8641 | 1113.4401 | 1679.3993 | 0 | 0.0124 | 1103610 | 277457.6802
Minimum of Months | 44089.6367 | 79.6756 | 129.3269 | 0 | 0.0009 | 85009.5688 | 19050.0048
Maximum of Months | 72486.6744 | 110.1565 | 154.1128 | 0 | 0.0011 | 101304.184 | 29327.9861
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 220643000000 | 170654.084 | 02-JAN-08:09 | 75734.208 | 58341.44 | 36569.995 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 198151000000 | 170766.226 | 28-FEB-08:00 | 75734.208 | 58341.44 | 36569.995 | 0 | 112.143 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 226102000000 | 170781.182 | 22-MAR-07:40 | 75734.208 | 58341.44 | 36569.995 | 0 | 127.098 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 200326000000 | 174275.483 | 04-APR-15:30 | 75734.208 | 50956.166 | 36569.995 | 0 | 11006.674 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 207253000000 | 204190.003 | 31-MAY-15:00 | 75734.208 | 50956.166 | 36569.995 | 0 | 40921.194 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 218952000000 | 232070.509 | 14-JUN-15:00 | 75734.208 | 50956.166 | 36569.995 | 0 | 68801.7 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 227224000000 | 244182.548 | 06-JUL-15:00 | 75734.208 | 50956.166 | 36569.995 | 0 | 80913.739 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 235069000000 | 236649.605 | 11-AUG-15:30 | 75734.208 | 50956.166 | 36569.995 | 0 | 73380.796 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 197258000000 | 223494.429 | 07-SEP-15:09 | 75734.208 | 50956.166 | 36569.995 | 0 | 60225.62 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 204589000000 | 178527.35 | 06-OCT-15:09 | 75734.208 | 50956.166 | 36569.995 | 0 | 15258.541 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 209386000000 | 170994.525 | 09-NOV-08:30 | 75734.208 | 58341.44 | 36569.995 | 0 | 340.442 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 215899000000 | 170654.084 | 01-DEC-08:09 | 75734.208 | 58341.44 | 36569.995 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2560850000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 197258000000 | 170654.084 |  | 75734.208 | 50956.166 | 36569.995 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 235069000000 | 244182.548 |  | 75734.208 | 58341.44 | 36569.995 | 0 | 80913.739 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 44280.58 | 14847.01 | 0 | 59127.59
Cost per Total Building Area ($/m2) | 8.89 | 2.98 | 0 | 11.87
Cost per Net Conditioned Building Area ($/m2) | 8.89 | 2.98 | 0 | 11.87

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6215.67 | 1247.58 | 1247.58
Net Site Energy | 6215.67 | 1247.58 | 1247.58
Total Source Energy | 13353.23 | 2680.2 | 2680.2
Net Source Energy | 13353.23 | 2680.2 | 2680.2
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3516.6 | 0 | 0 | 0 | 0
Cooling | 67.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 867.37 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 33.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 872.79 | 0 | 0 | 0 | 0 | 0
Pumps | 0.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 51.6 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2647.47 | 3568.2 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 16.89 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 16.89 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 16.89 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | No | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 8.445 | 37.16 | 7.2575
Conditioned Total | 4982.19 |  | 13667.13 |  | 1369.16 | 652.83 | 16.89 | 18.58 | 14.5149
Unconditioned Total | 4982.19 |  | 6074.28 |  | 608.51 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 65.28 | 65.28 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 43.52 | 43.52 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 195.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 456.98 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46678.87 | 37280.32 | 9398.54 | 0.8 | 3.35
PSZ_1:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27217.36 | 21737.29 | 5480.07 | 0.8 | 3.6
PSZ_1:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18029.26 | 14399.17 | 3630.1 | 0.8 | 3.61
PSZ_1:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26984.89 | 21551.63 | 5433.27 | 0.8 | 3.6
PSZ_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18029.14 | 14399.07 | 3630.07 | 0.8 | 3.61
PSZ_2:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 67660.86 | 54037.7 | 13623.16 | 0.8 | 4.17
PSZ_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28880.24 | 23065.35 | 5814.88 | 0.8 | 3.6
PSZ_2:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19087.4 | 15244.26 | 3843.15 | 0.8 | 3.61
PSZ_2:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28676.15 | 22902.35 | 5773.79 | 0.8 | 3.6
PSZ_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19327.13 | 15435.71 | 3891.42 | 0.8 | 3.6
PSZ_3:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 68615.16 | 54799.86 | 13815.3 | 0.8 | 4.17
PSZ_3:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39152.08 | 31269.01 | 7883.06 | 0.8 | 3.56
PSZ_3:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25582.15 | 20431.32 | 5150.83 | 0.8 | 3.6
PSZ_3:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39024.44 | 31167.07 | 7857.37 | 0.8 | 3.56
PSZ_3:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25581.56 | 20430.85 | 5150.71 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ_1:1_HEATC | Coil:Heating:Gas | 103800.36 | 0.78
PSZ_1:2_HEATC | Coil:Heating:Gas | 45649.25 | 0.78
PSZ_1:3_HEATC | Coil:Heating:Gas | 29992.01 | 0.78
PSZ_1:4_HEATC | Coil:Heating:Gas | 45331.43 | 0.78
PSZ_1:5_HEATC | Coil:Heating:Gas | 29991.49 | 0.78
PSZ_2:1_HEATC | Coil:Heating:Gas | 132470.79 | 0.78
PSZ_2:2_HEATC | Coil:Heating:Gas | 47922.62 | 0.78
PSZ_2:3_HEATC | Coil:Heating:Gas | 31438.65 | 0.78
PSZ_2:4_HEATC | Coil:Heating:Gas | 47643.61 | 0.78
PSZ_2:5_HEATC | Coil:Heating:Gas | 31766.09 | 0.78
PSZ_3:1_HEATC | Coil:Heating:Gas | 133774.84 | 0.78
PSZ_3:2_HEATC | Coil:Heating:Gas | 61965.97 | 0.78
PSZ_3:3_HEATC | Coil:Heating:Gas | 40318.24 | 0.78
PSZ_3:4_HEATC | Coil:Heating:Gas | 61791.51 | 0.78
PSZ_3:5_HEATC | Coil:Heating:Gas | 40317.08 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.82 | 3083.88 | 1 | Fan Energy
PSZ_1:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.64 | 1873.06 | 1 | Fan Energy
PSZ_1:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.09 | 1240.75 | 1 | Fan Energy
PSZ_1:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.63 | 1857.07 | 1 | Fan Energy
PSZ_1:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.09 | 1240.74 | 1 | Fan Energy
PSZ_2:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.09 | 7796.42 | 1 | Fan Energy
PSZ_2:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.74 | 1987.5 | 1 | Fan Energy
PSZ_2:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.15 | 1313.57 | 1 | Fan Energy
PSZ_2:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1973.46 | 1 | Fan Energy
PSZ_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.17 | 1330.07 | 1 | Fan Energy
PSZ_3:1_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.15 | 7906.38 | 1 | Fan Energy
PSZ_3:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.37 | 2586.62 | 1 | Fan Energy
PSZ_3:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.55 | 1760.53 | 1 | Fan Energy
PSZ_3:4_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.36 | 2578.19 | 1 | Fan Energy
PSZ_3:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.55 | 1760.49 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 87174.9376 | 94.819 | 328.3968 | 0 | 0.0012 | 65868.5227 | 32585.0056
February | 73885.8682 | 81.2433 | 296.7189 | 0 | 0.0011 | 59519.7286 | 27752.9215
March | 69150.197 | 78.9099 | 337.8245 | 0 | 0.0012 | 67780.6964 | 26416.3574
April | 50099.7493 | 59.679 | 297.2321 | 0 | 0.001 | 59647.3806 | 19524.8071
May | 43080.2648 | 53.4891 | 301.0219 | 0 | 0.001 | 60415.8211 | 17123.3834
June | 43946.4839 | 54.9211 | 314.5319 | 0 | 0.0011 | 63128.4207 | 17522.5381
July | 42880.1499 | 53.6243 | 307.6503 | 0 | 0.001 | 61747.3508 | 17102.8836
August | 44586.0712 | 55.6722 | 318.1026 | 0 | 0.0011 | 63844.9258 | 17770.1503
September | 42022.3371 | 51.7222 | 284.1445 | 0 | 0.001 | 57027.0855 | 16633.1136
October | 55754.3066 | 65.6691 | 315.1794 | 0 | 0.0011 | 63246.261 | 21613.7463
November | 71733.4555 | 80.4087 | 320.1284 | 0 | 0.0011 | 64223.7564 | 27180.2054
December | 79963.7126 | 88.042 | 323.5461 | 0 | 0.0012 | 64901.7152 | 30053.6688
Annual Sum or Average | 704277.5339 | 818.1999 | 3744.4773 | 0 | 0.013 | 751351.6648 | 271278.781
Minimum of Months | 42022.3371 | 51.7222 | 284.1445 | 0 | 0.001 | 57027.0855 | 16633.1136
Maximum of Months | 87174.9376 | 94.819 | 337.8245 | 0 | 0.0012 | 67780.6964 | 32585.0056
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 232095000000 | 176551.819 | 02-JAN-08:09 | 75734.208 | 58341.44 | 40288.731 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 209724000000 | 176551.819 | 01-FEB-08:09 | 75734.208 | 58341.44 | 40288.731 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 238833000000 | 176551.819 | 01-MAR-08:09 | 75734.208 | 58341.44 | 40288.731 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 210174000000 | 175804.297 | 25-APR-15:00 | 75734.208 | 50956.166 | 40288.731 | 0 | 8816.753 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 212882000000 | 192731.755 | 24-MAY-15:09 | 75734.208 | 50956.166 | 40288.731 | 0 | 25744.211 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 222440000000 | 224334.019 | 21-JUN-15:00 | 75734.208 | 50956.166 | 40288.731 | 0 | 57346.474 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 217573000000 | 224079.052 | 21-JUL-15:00 | 75734.208 | 50956.166 | 40288.731 | 0 | 57091.507 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 224965000000 | 220682.137 | 15-AUG-15:09 | 75734.208 | 50956.166 | 40288.731 | 0 | 53694.593 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 200941000000 | 180635.418 | 07-SEP-15:00 | 75734.208 | 50956.166 | 40288.731 | 0 | 13647.873 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 222855000000 | 176551.819 | 03-OCT-07:10 | 75734.208 | 58341.44 | 40288.731 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 226299000000 | 176551.819 | 01-NOV-07:10 | 75734.208 | 58341.44 | 40288.731 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 228688000000 | 176551.819 | 01-DEC-08:09 | 75734.208 | 58341.44 | 40288.731 | 0 | 0 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2647470000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 200941000000 | 175804.297 |  | 75734.208 | 50956.166 | 40288.731 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 238833000000 | 224334.019 |  | 75734.208 | 58341.44 | 40288.731 | 0 | 57346.474 | 2179 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 73369.17 | 14651.34 | 0 | 88020.51
Cost per Total Building Area ($/m2) | 14.73 | 2.94 | 0 | 17.67
Cost per Net Conditioned Building Area ($/m2) | 14.73 | 2.94 | 0 | 17.67

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720