## BuildingSummary
Building Summary Primary School post-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Primary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 6871 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.35
| Total | 0.35
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2512
| Net Dimensions - Total Area (m2) | 1619.42
| Wall to Skin Ratio | 0.27
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6871
| Net Dimensions - Total Area (m2) | 6871
| Roof to Skin Ratio | 0.73
Window Dimensions (m2)
| South | 324.79 | Pless, et al. 2007
| East | 114.8
| North | 324.79
| West | 114.8
| Total Area (m2) | 879.18
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab-on-grade
| Dimensions - Total Area (m2) | 6871
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 2932
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 13742
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.3934 | See Benchmark Technical Report
HVAC
| System Type | CAV, PSZ-AC (gym, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | gas boiler, gas furnace (gym, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 971.75

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 21.5278 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140.0001 | 49 | 4 | 78.75 | 21.5278 | 15 |  |  | 8 |  | 630 |  | 1.4738
COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72.0001 | 25.2 | 3.33 | 48.6486 | 21.5278 | 20 |  |  | 8 |  | 389.1892 |  | 1.4738
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 |  | 0 | 11.1486 | 4 |  |  |  | 0.5 | 273 |  | 1.0876
LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76.0001 | 26.6 |  | 0 | 12.2682 | 4 |  |  |  | 0.5 | 85.5 |  | 1.4738
MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 8.263 | 4 |  |  |  | 0.25 | 63 |  | 1.0203
BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 10 | 19 | 9.7047 | 4 |  | 213.9574 | 25 |  | 300 | 283.1682 | 1.2352
OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168.0002 | 58.8001 | 20 | 22.05 | 20.3418 | 10.8 |  |  | 10 |  | 220.5 |  | 1.409
GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68.0001 | 37.18 | 3.33 | 107.2072 | 11.4717 | 5 |  |  | 10 |  | 1072.0721 |  | 1.2147
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 17.2091 | 190.521 | 954.3991 | 378.54 | 8 |  | 201.4993 | 1557.4251 | 1.2147
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144.0001 | 50.4 | 1.3935 | 226.0419 | 15.0583 | 25.4028 |  |  | 10 |  | 2260.419 |  | 1.4868
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160.0001 | 56.0001 | 4.35 | 91.7241 | 22.7584 | 15 |  |  | 8 |  | 733.7931 |  | 1.4295
Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:6_COOLC DXCOIL | 20.3735 | 17.349 | 16.1967 | 17.7502 | 19.589 | 14.2647 | 19.2773 | 15.3059 | 14.0282 | 11.3643 | 14.7511 | 12.6494 | 13.9288 | 10.0323 | 11.9709 | 8.1098
| PSZ-AC_2:5_COOLC DXCOIL | 29.9717 | 26.6221 | 26.6221 | 26.6221 | 28.7484 | 26.6221 | 23.2845 | 26.6221 | 23.4218 | 23.0614 | 26.6221 | 23.6122 | 26.6221 | 19.6685 | 26.6221 | 17.7466
| PSZ-AC_2:7_COOLC DXCOIL | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 44.0264 | 56.2748 | 53.2715 | 51.3622 | 56.2748 | 53.9233 | 56.2748 | 46.1168 | 56.2748 | 37.5134
| VAV_OTHER_COOLC DXCOIL | 204.1606 | 170.182 | 142.801 | 171.1157 | 150.6621 | 116.8392 | 135.8443 | 138.1345 | 90.8582 | 89.5716 | 127.537 | 78.1508 | 114.2679 | 82.4328 | 110.9127 | 95.5597
| VAV_POD_1_COOLC DXCOIL | 200.0203 | 161.6548 | 157.6402 | 158.3788 | 152.62 | 132.1073 | 151.6489 | 134.7401 | 94.9381 | 99.95 | 129.3662 | 84.143 | 114.1034 | 74.3111 | 104.5656 | 89.3542
| VAV_POD_2_COOLC DXCOIL | 152.2049 | 125.2158 | 118.3121 | 124.2688 | 120.1191 | 103.712 | 121.1088 | 103.7882 | 73.9692 | 77.7406 | 98.1744 | 65.4826 | 86.097 | 58.6558 | 81.8661 | 70.1546
| VAV_POD_3_COOLC DXCOIL | 158.5065 | 128.8879 | 124.9553 | 126.806 | 123.1068 | 105.2872 | 123.2241 | 107.4691 | 75.5155 | 81.0652 | 102.8647 | 66.8535 | 90.7054 | 58.6926 | 82.3983 | 70.4765
Heating (kW)
| PSZ-AC_1:6_HEATC | 31.7642 | 35.708 | 28.1256 | 39.4106 | 31.7639 | 26.7777 | 44.1633 | 37.8297 | 29.855 | 27.2249 | 42.5909 | 31.7909 | 43.4623 | 36.075 | 38.2337 | 48.1169
| PSZ-AC_2:5_HEATC | 44.6071 | 54.794 | 46.2294 | 59.1086 | 45.1298 | 49.9752 | 51.9136 | 65.7984 | 52.2805 | 56.9032 | 76.8662 | 62.4079 | 83.0697 | 75.6966 | 85.0282 | 105.2941
| PSZ-AC_2:7_HEATC | 87.7376 | 115.8256 | 97.7215 | 124.946 | 91.2508 | 105.6395 | 100.8623 | 139.0873 | 110.5125 | 120.2841 | 162.4826 | 131.9201 | 175.596 | 160.0105 | 179.7358 | 222.5747
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:6_COOLC DXCOIL | 2.98 | 2.95 | 2.95 | 2.95 | 2.98 | 2.95 | 3.1 | 2.95 | 2.98 | 3 | 2.95 | 2.98 | 2.95 | 3.07 | 2.95 | 3.19
| PSZ-AC_2:5_COOLC DXCOIL | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 3.13 | 2.98 | 3.04 | 3.05 | 2.98 | 3.03 | 2.98 | 3.14 | 2.98 | 3.17
| PSZ-AC_2:7_COOLC DXCOIL | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.72 | 2.62 | 2.64 | 2.66 | 2.62 | 2.64 | 2.62 | 2.7 | 2.62 | 3.19
| VAV_OTHER_COOLC DXCOIL | 2.89 | 2.89 | 2.89 | 2.89 | 3.15 | 2.97 | 3.31 | 2.89 | 3.32 | 3.2 | 2.89 | 3.25 | 2.9 | 3.32 | 2.9 | 3.32
| VAV_POD_1_COOLC DXCOIL | 2.89 | 2.89 | 2.89 | 2.89 | 3.1 | 2.96 | 3.3 | 2.89 | 3.27 | 3.19 | 2.89 | 3.2 | 2.9 | 3.35 | 2.9 | 3.32
| VAV_POD_2_COOLC DXCOIL | 2.89 | 2.89 | 2.9 | 2.89 | 3.07 | 2.94 | 3.29 | 2.9 | 3.24 | 3.18 | 2.9 | 2.73 | 2.62 | 3.35 | 2.62 | 3.35
| VAV_POD_3_COOLC DXCOIL | 2.89 | 2.89 | 2.89 | 2.89 | 3.1 | 2.97 | 3.3 | 2.9 | 3.29 | 3.21 | 2.9 | 3.2 | 2.9 | 3.35 | 2.62 | 3.35
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| PSZ-AC_1:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_2:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:6 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_2:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_2:7 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
| VAV_OTHER | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| PSZ-AC_1:6_FAN | 0.82 | 0.7 | 0.65 | 0.71 | 0.79 | 0.57 | 0.99 | 0.62 | 0.61 | 0.51 | 0.59 | 0.55 | 0.56 | 0.51 | 0.48 | 0.49
| PSZ-AC_2:5_FAN | 1.21 | 1.07 | 1.07 | 1.07 | 1.16 | 1.07 | 1.25 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07
| PSZ-AC_2:7_FAN | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
| VAV_OTHER_FAN | 8.22 | 6.85 | 5.75 | 6.89 | 8.02 | 5.22 | 8.15 | 5.56 | 5.48 | 4.97 | 5.14 | 4.42 | 4.6 | 4.98 | 4.47 | 5.77
| VAV_POD_1_FAN | 8.05 | 6.51 | 6.35 | 6.38 | 7.77 | 5.82 | 9.04 | 5.43 | 5.52 | 5.5 | 5.21 | 4.6 | 4.59 | 4.49 | 4.21 | 5.4
| VAV_POD_2_FAN | 6.13 | 5.04 | 4.76 | 5 | 5.96 | 4.37 | 7.14 | 4.18 | 4.14 | 4.17 | 3.95 | 3.43 | 3.47 | 3.54 | 3.3 | 4.24
| VAV_POD_3_FAN | 6.38 | 5.19 | 5.03 | 5.11 | 6.3 | 4.62 | 7.36 | 4.33 | 4.38 | 4.46 | 4.14 | 3.65 | 3.65 | 3.55 | 3.32 | 4.26
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.09075 | 0.122 | 0.091272 | 0.097534 | 0.1313 | 0.10005 | 0.1472 | 0.078306 | 0.037109 | 0.075198 | 0.088165 | 0.037118 | 0.061464 | 0.07575 | 0.05973 | 0.094958
| Total Cost ($/m2) | 20.29 | 23.51 | 17.42 | 16.5 | 21.43 | 17.39 | 21.69 | 12.5 | 5.75 | 10.72 | 13.54 | 5.47 | 9.2 | 10.85 | 8.49 | 13.43
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011441 | 0.0081067 | 0.0083683 | 0.0098556 | 0.0084995 | 0.0078309 | 0.0085337 | 0.0097455 | 0.0069569 | 0.0083939 | 0.0083903 | 0.0069644 | 0.0079006 | 0.00817 | 0.0078851 | 0.0041226
| Total Cost ($/m2) | 0.61 | 0.98 | 0.78 | 1.92 | 0.85 | 0.97 | 1.52 | 2.67 | 1.42 | 2.09 | 3.05 | 1.84 | 3.62 | 3.08 | 4.27 | 4.26
Total Utility Costs
| Cost Intensity ($/m2) | 20.9 | 24.49 | 18.2 | 18.42 | 22.28 | 18.36 | 23.21 | 15.17 | 7.17 | 12.81 | 16.59 | 7.31 | 12.81 | 13.92 | 12.75 | 17.69
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 555550 | 359850 | 337972.2222 | 205708.3333 | 162361.1111 | 228172.2222 | 61408.3333 | 146363.8889 | 105366.6667 | 36427.7778 | 105002.7778 | 63825 | 80747.2222 | 37066.6667 | 33391.6667 | 17550
| Interior Lighting | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556
| Exterior Lighting | 34400 | 34386.1111 | 34380.5556 | 34375 | 34350 | 34341.6667 | 34358.3333 | 34338.8889 | 34350 | 34283.3333 | 34344.4444 | 34325 | 34322.2222 | 34313.8889 | 34294.4444 | 34083.3333
| Interior Equipment | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 68608.3333 | 52980.5556 | 62352.7778 | 46216.6667 | 48744.4444 | 55255.5556 | 41483.3333 | 40983.3333 | 49772.2222 | 33700 | 40472.2222 | 38922.2222 | 37594.4444 | 37638.8889 | 33608.3333 | 43980.5556
| Pumps | 13.8889 | 158.3333 | 97.2222 | 311.1111 | 91.6667 | 169.4444 | 213.8889 | 452.7778 | 325 | 341.6667 | 616.6667 | 480.5556 | 952.7778 | 738.8889 | 1191.6667 | 3069.4444
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21780.5556 | 20788.8889 | 20825 | 19844.4444 | 19855.5556 | 20147.2222 | 18986.1111 | 19233.3333 | 19227.7778 | 18597.2222 | 18794.4444 | 18691.6667 | 18583.3333 | 18238.8889 | 17927.7778 | 17397.2222
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1536213.8889 | 1324025 | 1311488.8889 | 1162319.4444 | 1121261.1111 | 1193947.2222 | 1012311.1111 | 1097230.5556 | 1064905.5556 | 979211.1111 | 1055091.6667 | 1012105.5556 | 1028058.3333 | 983855.5556 | 976272.2222 | 971941.6667
Gas (MJ)
| Heating | 54950 | 496080 | 320820 | 983850 | 342070 | 517780 | 856920 | 1509780 | 1034110 | 1335020 | 2109440 | 1427500 | 2746600 | 2185510 | 3296160 | 6648940
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 74790 | 98790 | 86910 | 120670 | 114310 | 102890 | 132910 | 138020 | 134700 | 145090 | 152950 | 151750 | 166100 | 167700 | 186430 | 210690
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 364080 | 829210 | 642070 | 1338860 | 690720 | 855020 | 1224170 | 1882140 | 1403160 | 1714450 | 2496730 | 1813590 | 3147040 | 2587550 | 3716930 | 7093970
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 5894450 | 5595700 | 5363440 | 5523210 | 4727260 | 5153220 | 4868500 | 5832180 | 5236810 | 5239610 | 6295060 | 5457160 | 6848050 | 6129420 | 7231510 | 10592960
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 291.0755 | 188.5402 | 177.0776 | 107.7791 | 85.0677 | 119.5488 | 32.1744 | 76.6861 | 55.2059 | 19.086 | 55.0153 | 33.4405 | 42.3068 | 19.4208 | 17.4953 | 9.1952
| Interior Lighting (elec) | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742
| Exterior Lighting (elec) | 18.0236 | 18.0163 | 18.0134 | 18.0105 | 17.9974 | 17.993 | 18.0017 | 17.9916 | 17.9974 | 17.9625 | 17.9945 | 17.9843 | 17.9828 | 17.9785 | 17.9683 | 17.8577
| Interior Equipment (elec) | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 35.9467 | 27.7587 | 32.6692 | 24.2148 | 25.5392 | 28.9507 | 21.7348 | 21.4729 | 26.0777 | 17.6568 | 21.2051 | 20.393 | 19.6973 | 19.7206 | 17.6088 | 23.0432
| Pumps (elec) | 0.007277 | 0.082957 | 0.050939 | 0.163 | 0.048028 | 0.088779 | 0.11207 | 0.23723 | 0.17028 | 0.17901 | 0.3231 | 0.25178 | 0.4992 | 0.38713 | 0.62436 | 1.6082
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 11.4117 | 10.8922 | 10.9111 | 10.3973 | 10.4031 | 10.556 | 9.9476 | 10.0771 | 10.0742 | 9.7439 | 9.8472 | 9.7933 | 9.7366 | 9.5561 | 9.3931 | 9.1151
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 804.8858 | 693.7113 | 687.1431 | 608.987 | 587.4749 | 625.5581 | 530.3915 | 574.8843 | 557.9479 | 513.049 | 552.806 | 530.2838 | 538.6421 | 515.4825 | 511.5092 | 509.2403
Gas (MJ/m2)
| Heating (gas) | 7.9974 | 72.1991 | 46.6919 | 143.1888 | 49.7846 | 75.3573 | 124.7155 | 219.7322 | 150.5036 | 194.2978 | 307.0063 | 207.7572 | 399.738 | 318.0774 | 479.7206 | 967.6816
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 10.8849 | 14.3778 | 12.6488 | 17.5622 | 16.6366 | 14.9745 | 19.3436 | 20.0873 | 19.6041 | 21.1163 | 22.2602 | 22.0856 | 24.1741 | 24.4069 | 27.1329 | 30.6637
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 52.9879 | 120.6826 | 93.4464 | 194.8566 | 100.5269 | 124.4389 | 178.1648 | 273.9252 | 204.2148 | 249.5197 | 363.3721 | 263.9485 | 458.0178 | 376.59 | 540.9591 | 1032.4509
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 857.8737 | 814.3938 | 780.5909 | 803.8437 | 688.0017 | 749.9956 | 708.5577 | 848.8109 | 762.1613 | 762.5688 | 916.1781 | 794.2308 | 996.6599 | 892.071 | 1052.4683 | 1541.6912
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 417.1397 | 361.3479 | 285.0408 | 256.6987 | 335.3239 | 246.6856 | 229.135 | 228.746 | 230.2223 | 211.433 | 212.3089 | 234.8718 | 212.2295 | 214.9737 | 211.8044 | 222.556
| Feb | 432.8362 | 343.9542 | 310.2743 | 249.5371 | 326.2351 | 258.0038 | 275.2826 | 221.5354 | 255.7898 | 227.5725 | 211.742 | 223.6431 | 211.2214 | 230.5035 | 211.629 | 217.1032
| Mar | 438.7881 | 355.1982 | 370.0964 | 296.6766 | 323.1333 | 285.5414 | 253.4746 | 290.2123 | 261.3696 | 250.1752 | 252.8107 | 259.8901 | 228.1219 | 244.5724 | 210.4292 | 216.9858
| Apr | 467.0576 | 396.1407 | 380.2042 | 346.3755 | 340.8966 | 365.346 | 278.4859 | 289.4117 | 299.2411 | 239.0111 | 259.1142 | 277.697 | 247.442 | 235.441 | 232.4854 | 212.8785
| May | 502.2282 | 462.6412 | 433.4651 | 412.0218 | 364.2388 | 401.0719 | 300.9638 | 373.0695 | 331.5561 | 292.9862 | 347.5218 | 301.6343 | 359.2787 | 272.0679 | 267.5395 | 253.7449
| Jun | 517.072 | 466.1176 | 511.3474 | 447.3894 | 364.0675 | 461.7284 | 306.7263 | 431.0546 | 361.175 | 309.5298 | 417.4321 | 342.3548 | 397.0943 | 329.6071 | 354.0128 | 300.3888
| Jul | 368.1924 | 372.4745 | 403.2997 | 360.4417 | 239.0427 | 356.1026 | 210.8419 | 343.7586 | 267.049 | 214.831 | 314.0762 | 246.8729 | 295.2535 | 230.5348 | 247.273 | 167.6572
| Aug | 397.1115 | 361.3269 | 404.4378 | 322.7414 | 272.7241 | 344.753 | 203.7594 | 337.8177 | 263.2381 | 201.2646 | 316.5499 | 251.6463 | 291.0839 | 204.8073 | 224.4802 | 171.9409
| Sep | 503.9752 | 465.4691 | 471.3033 | 436.1304 | 411.2517 | 409.5734 | 381.0167 | 391.5159 | 327.7009 | 329.0534 | 378.7933 | 321.0955 | 350.8324 | 299.845 | 325.5707 | 225.3629
| Oct | 493.7286 | 428.1239 | 386.3721 | 360.6711 | 377.2462 | 367.6017 | 299.59 | 349.9453 | 299.4482 | 262.8254 | 315.6217 | 298.8214 | 263.3041 | 260.4102 | 238.7184 | 214.9337
| Nov | 452.9757 | 384.2515 | 347.3322 | 280.2119 | 347.7783 | 270.0655 | 248.3777 | 311.0122 | 248.8189 | 227.3527 | 305.8213 | 247.8831 | 241.0443 | 219.0033 | 212.6582 | 218.4662
| Dec | 402.4379 | 358.7772 | 279.2986 | 251.4834 | 343.4932 | 261.7309 | 234.3638 | 211.7392 | 225.3715 | 211.4432 | 211.4674 | 219.8804 | 211.1306 | 214.5381 | 210.8932 | 222.558
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:00 | 26-JAN-15:00 | 23-JAN-15:00 | 26-JAN-12:00 | 18-JAN-14:00 | 27-JAN-14:00 | 09-JAN-11:50 | 25-JAN-14:00 | 27-JAN-16:00 | 27-JAN-16:00 | 24-JAN-12:00 | 04-JAN-16:00 | 05-JAN-08:09 | 09-JAN-11:09 | 04-JAN-11:09
| Feb | 23-FEB-12:50 | 23-FEB-14:00 | 28-FEB-15:00 | 27-FEB-15:00 | 13-FEB-11:00 | 08-FEB-14:00 | 15-FEB-15:00 | 15-FEB-12:00 | 14-FEB-15:00 | 21-FEB-13:00 | 28-FEB-11:20 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 02-FEB-09:39
| Mar | 13-MAR-14:00 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-13:00 | 31-MAR-14:50 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 01-MAR-11:20 | 14-MAR-07:10
| Apr | 03-APR-13:00 | 21-APR-14:00 | 26-APR-14:00 | 21-APR-13:00 | 11-APR-13:00 | 21-APR-14:00 | 14-APR-13:00 | 04-APR-14:00 | 21-APR-14:00 | 18-APR-13:00 | 07-APR-13:00 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 24-APR-11:00
| May | 24-MAY-14:00 | 18-MAY-13:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-11:39 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-14:00 | 31-MAY-14:00 | 04-MAY-13:00 | 30-MAY-14:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-13:50 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-11:00 | 29-JUN-13:00 | 28-JUN-13:00 | 08-JUN-12:00 | 28-JUN-11:00 | 30-JUN-11:00 | 30-JUN-14:00 | 14-JUN-15:09 | 21-JUN-14:50
| Jul | 13-JUL-14:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-15:00 | 24-JUL-13:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-11:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 17-JUL-15:30 | 13-JUL-15:50 | 21-JUL-15:00 | 06-JUL-15:00 | 11-JUL-13:30
| Aug | 21-AUG-13:00 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-15:00 | 15-AUG-11:00 | 17-AUG-13:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-13:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-14:00 | 08-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-14:00 | 13-SEP-14:00 | 06-SEP-11:00 | 05-SEP-13:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 07-SEP-14:00
| Oct | 06-OCT-13:00 | 30-OCT-10:50 | 13-OCT-14:00 | 12-OCT-15:00 | 05-OCT-13:00 | 03-OCT-14:00 | 31-OCT-13:20 | 03-OCT-11:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 27-OCT-11:00 | 31-OCT-07:10
| Nov | 01-NOV-11:00 | 27-NOV-12:00 | 13-NOV-14:00 | 22-NOV-14:00 | 20-NOV-12:00 | 10-NOV-12:00 | 08-NOV-12:00 | 03-NOV-13:00 | 08-NOV-14:00 | 03-NOV-11:00 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:50 | 09-NOV-11:50 | 30-NOV-10:20
| Dec | 15-DEC-12:00 | 19-DEC-14:00 | 13-DEC-12:00 | 13-DEC-12:00 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 06-DEC-11:20 | 08-DEC-14:00 | 28-DEC-16:19 | 12-DEC-16:19 | 21-DEC-14:00 | 29-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 28-DEC-11:20
Source Energy
| Total Source Energy (GJ) | 18741.82 | 18217.37 | 15634.81 | 15538.18 | 13247.37 | 16308.36 | 12615.98 | 16180.61 | 14252.32 | 8013.01 | 16195.32 | 14069.82 | 16156.94 | 15137.17 | 16138.51 | 20245.01
| Total Source Energy (MJ/m2) | 2727.67 | 2651.34 | 2275.48 | 2261.41 | 1928.01 | 2373.51 | 1836.12 | 2354.91 | 2074.27 | 1166.21 | 2357.05 | 2047.71 | 2351.47 | 2203.05 | 2348.79 | 2946.44
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
| Total Building | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
Emissions
| Carbon Equivalent (kg) | 427871.7312 | 456595.5139 | 407484.8571 | 382180.0675 | 143492.7155 | 418106.44 | 140379.8744 | 330033.8866 | 460314.1862 | 102236.1968 | 607544.5986 | 446146.5531 | 408646.8362 | 406197.9535 | 401197.6936 | 401415.7716
| CO2 (kg) | 994526.1739 | 1151410 | 964504.7452 | 882354.9353 | 385833.6271 | 998318.196 | 379633.0533 | 762059.9319 | 1086720 | 258742.1841 | 1427970 | 1057850 | 975222.2244 | 971048.5285 | 964048.5118 | 1054700
| NOX (kg) | 1737.7196 | 1495.8596 | 1604.0003 | 1632.4583 | 332.0614 | 1604.5594 | 328.203 | 1416.6308 | 1844.8029 | 353.3064 | 2481.4182 | 1776.0376 | 1629.2591 | 1606.792 | 1581.6438 | 1193.8477
| SO2 (kg) | 6575.7089 | 6315.8153 | 5273.9343 | 4080.0968 | 3262.9228 | 6567.8879 | 2946.035 | 4005.8357 | 4650.6023 | 757.3111 | 7111.1494 | 4420.1439 | 2427.2257 | 2627.7044 | 2305.1567 | 4949.478
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.03 | 0.0178 | 0.0144 | 0.015 | 0.0015 | 0.0124 | 0.0015 | 0.0163 | 0.0183 | 0.0031 | 0.0217 | 0.0174 | 0.018 | 0.0185 | 0.0172 | 0.0175
| Water for Electricity (m3) | 813.8218 | 2154.34 | 38957 | 7257.05 | 19686.8 | 32754.7 | 17773.9 | 249.1126 | 4835.52 | 10004.4 | 1636.91 | 4595.76 | 1594.97 | 62321.5 | 1514.63 | 993.0144

## Miami
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5894.45 | 857.87 | 857.87
Net Site Energy | 5894.45 | 857.87 | 857.87
Total Source Energy | 18741.82 | 2727.67 | 2727.67
Net Source Energy | 18741.82 | 2727.67 | 2727.67
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 54.95 | 0 | 0 | 0 | 0
Cooling | 1999.98 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 246.99 | 0 | 0 | 0 | 0 | 0
Pumps | 0.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 74.79 | 0 | 0 | 0 | 971.75
Refrigeration | 78.41 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5530.37 | 364.08 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.251 | 0.11 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 324.79 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 440469.98 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20373.51 | 13774.19 | 6599.32 | 0.68 | 2.98
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29971.68 | 20263.35 | 9708.33 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 204160.59 | 138029.55 | 66131.04 | 0.68 | 2.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 200020.3 | 135230.37 | 64789.93 | 0.68 | 2.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 152204.85 | 102903.15 | 49301.71 | 0.68 | 2.89
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 158506.47 | 107163.57 | 51342.91 | 0.68 | 2.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11425.22 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10089 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11660.48 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11549.14 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11559.54 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12144.13 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12151.82 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12246.79 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9638.37 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9606.71 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9661.26 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22168.78 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7312.67 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22002.4 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6087.91 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26664.91 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26236.49 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26338.75 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27180.45 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27215.07 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18517.61 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21797.38 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 31764.16 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 44607.08 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 87737.56 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 21289.14 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 23964.73 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 18235.89 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 18990.89 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.82 | 951.64 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.21 | 1374.96 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.22 | 15423.54 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.05 | 15110.76 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.13 | 11498.48 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.38 | 11974.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2425.41 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 75826.8438 | 131.3769 | 492.5908 | 0 | 0.0022 | 60963.0958 | 32511.1004
February | 69861.431 | 121.7314 | 459.2697 | 0 | 0.0021 | 56839.8081 | 30022.5538
March | 81530.4927 | 141.9879 | 535.3801 | 0 | 0.0024 | 66259.2612 | 35029.6004
April | 80761.8421 | 141.2067 | 534.7198 | 0 | 0.0024 | 66177.9717 | 34755.2018
May | 96009.3779 | 168.1003 | 637.5175 | 0 | 0.0029 | 78900.5946 | 41340.3379
June | 100718.5727 | 176.456 | 669.6566 | 0 | 0.0031 | 82878.2836 | 43379.1201
July | 74160.7303 | 129.9256 | 493.0651 | 0 | 0.0022 | 61022.8981 | 31940.5763
August | 77633.5415 | 135.9832 | 515.9445 | 0 | 0.0024 | 63854.4913 | 33433.6228
September | 92886.4446 | 162.7047 | 617.3496 | 0 | 0.0028 | 76404.621 | 40002.8869
October | 90551.9361 | 158.4741 | 600.7206 | 0 | 0.0027 | 74346.4751 | 38983.3257
November | 81804.9358 | 142.9871 | 541.2847 | 0 | 0.0025 | 66990.4226 | 35199.7426
December | 72780.0255 | 126.7856 | 478.2099 | 0 | 0.0022 | 59183.842 | 31273.6624
Annual Sum or Average | 994526.1739 | 1737.7196 | 6575.7089 | 0 | 0.03 | 813821.7651 | 427871.7312
Minimum of Months | 69861.431 | 121.7314 | 459.2697 | 0 | 0.0021 | 56839.8081 | 30022.5538
Maximum of Months | 100718.5727 | 176.456 | 669.6566 | 0 | 0.0031 | 82878.2836 | 43379.1201
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 414278000000 | 417139.733 | 06-JAN-12:00 | 120876.129 | 79091.122 | 23388.198 | 0 | 191170.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2613.507 | 0 | 0
February | 386258000000 | 432836.245 | 23-FEB-12:50 | 120876.129 | 79091.122 | 26949.203 | 0 | 203305.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2614.778 | 0 | 0
March | 450269000000 | 438788.076 | 13-MAR-14:00 | 120876.129 | 73092.045 | 29137.165 | 0 | 213042.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2640.735 | 0 | 0
April | 449716000000 | 467057.59 | 03-APR-13:00 | 120876.129 | 75091.738 | 33943.893 | 0 | 234497.704 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2648.12 | 0 | 0
May | 536173000000 | 502228.21 | 24-MAY-14:00 | 120876.129 | 73092.045 | 39504.15 | 0 | 266045.383 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2710.496 | 0 | 0
June | 563204000000 | 517071.974 | 27-JUN-14:00 | 120876.129 | 73092.045 | 46563.965 | 0 | 273843.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2696.07 | 0 | 0
July | 414685000000 | 368192.365 | 13-JUL-14:00 | 67153.405 | 40636.785 | 20156.119 | 0 | 237688.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2557.953 | 0 | 0
August | 433927000000 | 397111.487 | 21-AUG-13:00 | 67153.405 | 41836.601 | 23669.828 | 0 | 261868.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2583.272 | 0 | 0
September | 519212000000 | 503975.213 | 07-SEP-13:00 | 120876.129 | 75091.738 | 40671.371 | 0 | 264649.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2686.388 | 0 | 0
October | 505226000000 | 493728.6 | 06-OCT-13:00 | 120876.129 | 75091.738 | 39929.531 | 0 | 255165.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2665.935 | 0 | 0
November | 455237000000 | 452975.73 | 01-NOV-11:00 | 120876.129 | 79091.122 | 27918.401 | 0 | 222457.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2632.118 | 0 | 0
December | 402187000000 | 402437.881 | 15-DEC-12:00 | 120876.129 | 79091.122 | 23405.666 | 0 | 176460.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2604.216 | 0 | 0
Annual Sum or Average | 5530370000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 386258000000 | 368192.365 |  | 67153.405 | 40636.785 | 20156.119 | 0 | 176460.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2557.953 | 0 | 0
Maximum of Months | 563204000000 | 517071.974 |  | 120876.129 | 79091.122 | 46563.965 | 0 | 273843.765 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2710.496 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 139411.96 | 4165.57 | 0 | 143577.52
Cost per Total Building Area ($/m2) | 20.29 | 0.61 | 0 | 20.9
Cost per Net Conditioned Building Area ($/m2) | 20.29 | 0.61 | 0 | 20.9

## Houston
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5595.7 | 814.39 | 814.39
Net Site Energy | 5595.7 | 814.39 | 814.39
Total Source Energy | 18217.37 | 2651.34 | 2651.34
Net Source Energy | 18217.37 | 2651.34 | 2651.34
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 496.08 | 0 | 0 | 0 | 0
Cooling | 1295.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 190.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0.57 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 98.79 | 0 | 0 | 0 | 971.75
Refrigeration | 74.84 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4766.49 | 829.21 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.251 | 0.11 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 324.79 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 451326.79 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17349.02 | 11729.38 | 5619.64 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 170181.97 | 115057.17 | 55124.8 | 0.68 | 2.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 161654.8 | 109292.1 | 52362.7 | 0.68 | 2.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 125215.76 | 84656.28 | 40559.49 | 0.68 | 2.89
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 128887.95 | 87138.98 | 41748.97 | 0.68 | 2.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8456.81 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8315.22 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8822.63 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8745.56 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8752.47 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8739.09 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8744.18 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8813.95 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7998.63 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7974.22 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8020.3 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18801.6 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5989.43 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18329.57 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5278.76 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23129.54 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22754.01 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22834.9 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22151.98 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22175 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15033.72 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18614.21 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 35707.99 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 54793.98 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 115825.61 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 40277.88 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 38259.71 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 29635.49 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 30504.6 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.7 | 810.36 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.85 | 12856.59 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.51 | 12212.39 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.04 | 9459.56 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.19 | 9736.98 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2485.2 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 88923.5606 | 113.0322 | 452.8523 | 0 | 0.0013 | 154457.9537 | 34941.5701
February | 78542.0157 | 99.816 | 399.702 | 0 | 0.0011 | 136329.4639 | 30859.664
March | 89561.1936 | 116.1186 | 487.9736 | 0 | 0.0014 | 166448.0498 | 35485.4719
April | 89741.8739 | 117.1799 | 500.5411 | 0 | 0.0014 | 170738.5633 | 35663.6639
May | 112545.0429 | 147.2789 | 632.2638 | 0 | 0.0018 | 215671.6787 | 44767.4574
June | 126626.2987 | 165.854 | 713.4446 | 0 | 0.002 | 243363.9219 | 50387.699
July | 91859.9062 | 120.3238 | 517.6531 | 0 | 0.0015 | 176577.2865 | 36554.1407
August | 93304.6255 | 122.1886 | 525.4083 | 0 | 0.0015 | 179222.5693 | 37125.4896
September | 108244.4611 | 141.723 | 609.1111 | 0 | 0.0017 | 207774.3705 | 43066.0709
October | 101128.4097 | 132.1436 | 565.3924 | 0 | 0.0016 | 192860.2967 | 40201.0569
November | 87382.8805 | 113.5566 | 479.7782 | 0 | 0.0014 | 163653.7928 | 34656.1976
December | 83549.4507 | 106.6446 | 431.6949 | 0 | 0.0012 | 147243.7981 | 32887.0319
Annual Sum or Average | 1151410 | 1495.8596 | 6315.8153 | 0 | 0.0178 | 2154340 | 456595.5139
Minimum of Months | 78542.0157 | 99.816 | 399.702 | 0 | 0.0011 | 136329.4639 | 30859.664
Maximum of Months | 126626.2987 | 165.854 | 713.4446 | 0 | 0.002 | 243363.9219 | 50387.699
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 341739000000 | 361347.872 | 03-JAN-12:00 | 120876.129 | 79091.122 | 16265.052 | 0 | 142509.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2605.576 | 0 | 0
February | 301629000000 | 343954.235 | 23-FEB-14:00 | 120876.129 | 75091.738 | 22727.243 | 0 | 122624.15 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 2634.956 | 0 | 0
March | 368267000000 | 355198.227 | 29-MAR-11:00 | 120876.129 | 79091.122 | 16184.036 | 0 | 136434.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2612.607 | 0 | 0
April | 377759000000 | 396140.68 | 21-APR-14:00 | 120876.129 | 73092.045 | 27182.253 | 0 | 172351.914 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2638.338 | 0 | 0
May | 477174000000 | 462641.211 | 18-MAY-13:00 | 120876.129 | 75091.738 | 36370.218 | 0 | 227598.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2704.22 | 0 | 0
June | 538443000000 | 466117.572 | 13-JUN-14:00 | 120876.129 | 73092.045 | 37580.743 | 0 | 231833.247 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2735.402 | 0 | 0
July | 390678000000 | 372474.508 | 18-JUL-11:00 | 67153.405 | 44636.17 | 27297.896 | 0 | 230802.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2584.478 | 0 | 0
August | 396530000000 | 361326.867 | 31-AUG-15:00 | 67153.405 | 40636.785 | 26670.888 | 0 | 224267.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2597.971 | 0 | 0
September | 459701000000 | 465469.121 | 15-SEP-14:00 | 120876.129 | 73092.045 | 39038.792 | 0 | 229755.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2706.185 | 0 | 0
October | 426704000000 | 428123.918 | 30-OCT-10:50 | 120876.129 | 79091.122 | 22948.524 | 0 | 201262.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3945.918 | 0 | 0
November | 362084000000 | 384251.47 | 27-NOV-12:00 | 120876.129 | 79091.122 | 16989.176 | 0 | 164689.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2605.738 | 0 | 0
December | 325777000000 | 358777.209 | 19-DEC-14:00 | 120876.129 | 75091.738 | 19901.543 | 0 | 140297.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2610.191 | 0 | 0
Annual Sum or Average | 4766490000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 301629000000 | 343954.235 |  | 67153.405 | 40636.785 | 16184.036 | 0 | 122624.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2584.478 | 0 | 0
Maximum of Months | 538443000000 | 466117.572 |  | 120876.129 | 79091.122 | 39038.792 | 0 | 231833.247 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 3945.918 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 161526.6 | 6722.15 | 0 | 168248.76
Cost per Total Building Area ($/m2) | 23.51 | 0.98 | 0 | 24.49
Cost per Net Conditioned Building Area ($/m2) | 23.51 | 0.98 | 0 | 24.49

## Phoenix
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5363.44 | 780.59 | 780.59
Net Site Energy | 5363.44 | 780.59 | 780.59
Total Source Energy | 15634.81 | 2275.48 | 2275.48
Net Source Energy | 15634.81 | 2275.48 | 2275.48
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 320.82 | 0 | 0 | 0 | 0
Cooling | 1216.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 224.47 | 0 | 0 | 0 | 0 | 0
Pumps | 0.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 86.91 | 0 | 0 | 0 | 971.75
Refrigeration | 74.97 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4721.36 | 642.07 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.251 | 0.11 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 324.79 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 363350.25 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16196.69 | 10950.31 | 5246.38 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 142800.98 | 96545.35 | 46255.63 | 0.68 | 2.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157640.21 | 106577.9 | 51062.31 | 0.68 | 2.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 118312.09 | 79988.82 | 38323.27 | 0.68 | 2.9
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124955.34 | 84480.21 | 40475.13 | 0.68 | 2.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7117.29 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7248.77 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9231.25 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9151.11 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9159.05 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8989.75 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8995.11 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9069.73 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5998.92 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5972.82 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6028.99 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16338.51 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5668.19 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12565.73 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2501.67 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22209.74 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21903.03 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22011.22 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19262.33 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19300.26 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13056.27 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16357.71 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 28125.62 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 46229.41 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 97721.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 24903.48 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 27491.34 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 20632.79 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 21791.33 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.65 | 756.54 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.75 | 10788.06 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.35 | 11909.1 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.76 | 9087.82 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.03 | 9439.89 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2000.76 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 68850.0636 | 111.659 | 355.9241 | 0 | 0.001 | 2628960 | 28800.5835
February | 62511.9991 | 101.6449 | 325.0746 | 0 | 0.0009 | 2401110 | 26176.0912
March | 77106.6183 | 127.9473 | 419.5712 | 0 | 0.0011 | 3099240 | 32547.4246
April | 75684.9186 | 126.5044 | 418.4629 | 0 | 0.0011 | 3091100 | 32039.9594
May | 89948.0278 | 150.8723 | 501.1408 | 0 | 0.0014 | 3701850 | 38131.368
June | 109631.3031 | 184.2568 | 613.4764 | 0 | 0.0017 | 4531670 | 46512.9742
July | 81076.5652 | 136.2641 | 453.6829 | 0 | 0.0012 | 3351290 | 34398.0415
August | 81594.7427 | 137.0803 | 456.1867 | 0 | 0.0012 | 3369790 | 34612.3547
September | 95980.8476 | 161.2234 | 536.4318 | 0 | 0.0015 | 3962550 | 40712.3177
October | 82108.8462 | 137.4346 | 455.3764 | 0 | 0.0012 | 3363780 | 34778.9304
November | 71447.9419 | 118.4929 | 388.312 | 0 | 0.0011 | 2868330 | 30152.3059
December | 68562.8711 | 110.6203 | 350.2944 | 0 | 0.001 | 2587350 | 28622.5059
Annual Sum or Average | 964504.7452 | 1604.0003 | 5273.9343 | 0 | 0.0144 | 38957000 | 407484.8571
Minimum of Months | 62511.9991 | 101.6449 | 325.0746 | 0 | 0.0009 | 2401110 | 26176.0912
Maximum of Months | 109631.3031 | 184.2568 | 613.4764 | 0 | 0.0017 | 4531670 | 46512.9742
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 318615000000 | 285040.775 | 26-JAN-15:00 | 120876.129 | 73092.045 | 18086.624 | 0 | 70479.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2506.723 | 0 | 0
February | 291001000000 | 310274.315 | 28-FEB-15:00 | 120876.129 | 73092.045 | 21873.852 | 0 | 91873.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2558.517 | 0 | 0
March | 375609000000 | 370096.4 | 17-MAR-14:00 | 120876.129 | 73092.045 | 29857.977 | 0 | 143604.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2665.957 | 0 | 0
April | 374623000000 | 380204.201 | 26-APR-14:00 | 120876.129 | 73092.045 | 30896.26 | 0 | 152652.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2687.296 | 0 | 0
May | 448642000000 | 433465.098 | 30-MAY-14:00 | 120876.129 | 73092.045 | 34893.038 | 0 | 201878.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2725.111 | 0 | 0
June | 549212000000 | 511347.378 | 28-JUN-15:00 | 120876.129 | 73092.045 | 40886.648 | 0 | 273865.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2627.381 | 0 | 0
July | 406157000000 | 403299.735 | 11-JUL-15:00 | 67153.405 | 40636.785 | 34372.347 | 0 | 258623.072 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2514.122 | 0 | 0
August | 408399000000 | 404437.807 | 01-AUG-15:00 | 67153.405 | 40636.785 | 34485.115 | 0 | 259671.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2491.013 | 0 | 0
September | 480237000000 | 471303.322 | 08-SEP-13:00 | 120876.129 | 75091.738 | 36596.597 | 0 | 236007.379 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2731.477 | 0 | 0
October | 407670000000 | 386372.054 | 13-OCT-14:00 | 120876.129 | 73092.045 | 33173.11 | 0 | 156532.688 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 2698.062 | 0 | 0
November | 347625000000 | 347332.151 | 13-NOV-14:00 | 120876.129 | 75091.738 | 25487.656 | 0 | 123222.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2654.145 | 0 | 0
December | 313572000000 | 279298.571 | 13-DEC-12:00 | 120876.129 | 79091.122 | 15835.932 | 0 | 60997.731 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2497.651 | 0 | 0
Annual Sum or Average | 4721360000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 291001000000 | 279298.571 |  | 67153.405 | 40636.785 | 15835.932 | 0 | 60997.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2491.013 | 0 | 0
Maximum of Months | 549212000000 | 511347.378 |  | 120876.129 | 79091.122 | 40886.648 | 0 | 273865.175 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 2731.477 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 119701.99 | 5373.04 | 0 | 125075.03
Cost per Total Building Area ($/m2) | 17.42 | 0.78 | 0 | 18.2
Cost per Net Conditioned Building Area ($/m2) | 17.42 | 0.78 | 0 | 18.2

## Atlanta
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5523.21 | 803.84 | 803.84
Net Site Energy | 5523.21 | 803.84 | 803.84
Total Source Energy | 15538.18 | 2261.41 | 2261.41
Net Source Energy | 15538.18 | 2261.41 | 2261.41
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 983.85 | 0 | 0 | 0 | 0
Cooling | 740.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 166.38 | 0 | 0 | 0 | 0 | 0
Pumps | 1.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 120.67 | 0 | 0 | 0 | 971.75
Refrigeration | 71.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4184.35 | 1338.86 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 4.092 | 0.255 | 0.129 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.255 | 0.129 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.255 | 0.129 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.255 | 0.129 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.255 | 0.129 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 4.092 | 0.255 | 0.129 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.255 | 0.129 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.255 | 0.129 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.255 | 0.129 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.255 | 0.129 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.255 | 0.129 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 324.79 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 554.39 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 472488.91 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17750.24 | 12000.64 | 5749.6 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 171115.7 | 115688.46 | 55427.25 | 0.68 | 2.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 158378.77 | 107077.23 | 51301.54 | 0.68 | 2.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124268.77 | 84016.03 | 40252.74 | 0.68 | 2.89
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 126805.97 | 85731.39 | 41074.58 | 0.68 | 2.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7823.05 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7999.98 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7984.3 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7919.16 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7925.19 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7746.49 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7750.88 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7812.41 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7808.65 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7785.53 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7829.94 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18234.87 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5818.69 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17959.38 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5424.75 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22671.35 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22333.76 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22408.23 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21278.94 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21297.93 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14400.37 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18212.61 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 39410.55 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 59108.58 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 124945.98 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 46939.96 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 43446 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 34089.05 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 34785.05 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.71 | 829.1 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.89 | 12927.13 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.38 | 11964.9 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5 | 9388.02 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.11 | 9579.7 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2601.72 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 76911.8854 | 132.4448 | 307.3578 | 0 | 0.0012 | 546585.3202 | 32403.5708
February | 68917.387 | 119.2126 | 278.0306 | 0 | 0.001 | 494437.6007 | 29084.798
March | 71687.143 | 131.8976 | 327.9009 | 0 | 0.0012 | 583212.7968 | 30982.7259
April | 68752.8001 | 129.5619 | 329.4952 | 0 | 0.0012 | 586078.4111 | 29997.4178
May | 79621.7945 | 151.7843 | 390.115 | 0 | 0.0014 | 693920.1848 | 34900.3627
June | 90698.733 | 173.5417 | 447.531 | 0 | 0.0016 | 796055.3007 | 39814.9027
July | 63633.6729 | 121.7742 | 314.0752 | 0 | 0.0011 | 558668.0219 | 27935.5891
August | 66364.8029 | 126.9651 | 327.3808 | 0 | 0.0012 | 582335.3102 | 29131.2874
September | 82877.8294 | 158.5445 | 408.78 | 0 | 0.0015 | 727125.7895 | 36378.6579
October | 71146.18 | 134.121 | 341.205 | 0 | 0.0013 | 606907.3741 | 31046.1846
November | 68677.0557 | 124.7608 | 306.2965 | 0 | 0.0011 | 544770.8378 | 29534.1553
December | 73065.6515 | 127.8495 | 301.9288 | 0 | 0.0011 | 536953.5382 | 30970.4153
Annual Sum or Average | 882354.9353 | 1632.4583 | 4080.0968 | 0 | 0.015 | 7257050 | 382180.0675
Minimum of Months | 63633.6729 | 119.2126 | 278.0306 | 0 | 0.001 | 494437.6007 | 27935.5891
Maximum of Months | 90698.733 | 173.5417 | 447.531 | 0 | 0.0016 | 796055.3007 | 39814.9027
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 315156000000 | 256698.713 | 23-JAN-15:00 | 120876.129 | 73092.045 | 15630.56 | 0 | 44710.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2389.281 | 0 | 0
February | 285088000000 | 249537.103 | 27-FEB-15:00 | 120876.129 | 73092.045 | 15320.275 | 0 | 37914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2334.653 | 0 | 0
March | 336275000000 | 296676.564 | 28-MAR-14:00 | 120876.129 | 73092.045 | 21425.784 | 0 | 78744.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2538.419 | 0 | 0
April | 337927000000 | 346375.535 | 21-APR-13:00 | 120876.129 | 75091.738 | 22144.877 | 0 | 125672.034 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2590.75 | 0 | 0
May | 400108000000 | 412021.804 | 15-MAY-14:00 | 120876.129 | 73092.045 | 31145.496 | 0 | 184252.07 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2656.055 | 0 | 0
June | 458998000000 | 447389.387 | 19-JUN-14:00 | 120876.129 | 73092.045 | 35023.536 | 0 | 215680.85 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2716.825 | 0 | 0
July | 322123000000 | 360441.693 | 03-JUL-15:00 | 67153.405 | 40636.785 | 25636.4 | 0 | 224410.812 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2604.286 | 0 | 0
August | 335769000000 | 322741.373 | 17-AUG-13:00 | 67153.405 | 41836.601 | 16516.241 | 0 | 194661.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2573.673 | 0 | 0
September | 419254000000 | 436130.402 | 11-SEP-13:00 | 120876.129 | 75091.738 | 32083.288 | 0 | 205421.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2658.055 | 0 | 0
October | 349937000000 | 360671.071 | 12-OCT-15:00 | 120876.129 | 73092.045 | 21497.582 | 0 | 142619.968 | 0 | 0.017 | 0 | 0 | 0 | 0 | 0 | 2585.33 | 0 | 0
November | 314110000000 | 280211.877 | 22-NOV-14:00 | 120876.129 | 75091.738 | 15955.745 | 0 | 65766.678 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2521.58 | 0 | 0
December | 309602000000 | 251483.428 | 13-DEC-12:00 | 120876.129 | 79091.122 | 9957.472 | 0 | 39104.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2453.773 | 0 | 0
Annual Sum or Average | 4184350000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 285088000000 | 249537.103 |  | 67153.405 | 40636.785 | 9957.472 | 0 | 37914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2334.653 | 0 | 0
Maximum of Months | 458998000000 | 447389.387 |  | 120876.129 | 79091.122 | 35023.536 | 0 | 224410.812 | 0 | 0.017 | 0 | 0 | 0 | 0 | 0 | 2716.825 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 113365.82 | 13195.31 | 0 | 126561.12
Cost per Total Building Area ($/m2) | 16.5 | 1.92 | 0 | 18.42
Cost per Net Conditioned Building Area ($/m2) | 16.5 | 1.92 | 0 | 18.42

## LosAngeles
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4727.26 | 688 | 688
Net Site Energy | 4727.26 | 688 | 688
Total Source Energy | 13247.37 | 1928.01 | 1928.01
Net Source Energy | 13247.37 | 1928.01 | 1928.01
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 342.07 | 0 | 0 | 0 | 0
Cooling | 584.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 175.48 | 0 | 0 | 0 | 0 | 0
Pumps | 0.33 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 114.31 | 0 | 0 | 0 | 971.75
Refrigeration | 71.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4036.54 | 690.72 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.44 | 0.272 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.44 | 0.272 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.44 | 0.272 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.44 | 0.272 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.44 | 0.272 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.44 | 0.272 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.44 | 0.272 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.44 | 0.272 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.44 | 0.272 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.44 | 0.272 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.44 | 0.272 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 324.79 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 442551.12 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19588.96 | 13243.77 | 6345.19 | 0.68 | 2.98
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28748.44 | 19436.34 | 9312.1 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 150662.08 | 113743.68 | 36918.4 | 0.75 | 3.15
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 152619.96 | 113096.08 | 39523.88 | 0.74 | 3.1
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 120119.15 | 88055.52 | 32063.63 | 0.73 | 3.07
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 123106.76 | 91400.18 | 31706.58 | 0.74 | 3.1
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10450.15 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8308.38 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10831.59 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10706.46 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10717.4 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9831.51 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9839.62 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9954.21 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9511.44 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9466.35 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9538.1 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19409.72 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9248.6 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21354.85 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6436.32 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 32384.52 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31761.51 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31872.69 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21797.07 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21829.71 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14947.43 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22851 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 31763.91 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 45129.75 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 91250.81 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 24868.47 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 26524.65 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 20339.99 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 21493.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.79 | 914.99 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.16 | 1318.84 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.02 | 15045.01 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.77 | 14585.27 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.96 | 11184.48 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.3 | 11818.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2436.87 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 33405.0857 | 28.8531 | 263.9735 | 0 | 0.0001 | 1592620 | 12366.9292
February | 29767.9799 | 25.6998 | 237.3516 | 0 | 0.0001 | 1432010 | 11026.8982
March | 34531.186 | 29.7824 | 280.6206 | 0 | 0.0001 | 1693080 | 12807.4638
April | 31482.1832 | 27.0997 | 265.3369 | 0 | 0.0001 | 1600910 | 11705.5689
May | 34402.943 | 29.5767 | 296.6066 | 0 | 0.0001 | 1789600 | 12811.8514
June | 34595.9561 | 29.7202 | 302.2718 | 0 | 0.0001 | 1823790 | 12895.9379
July | 24624.4465 | 21.141 | 217.4814 | 0 | 0.0001 | 1312210 | 9186.0893
August | 27402.7558 | 23.5236 | 242.4943 | 0 | 0.0001 | 1463130 | 10223.9803
September | 34907.2297 | 29.9601 | 309.9201 | 0 | 0.0001 | 1869960 | 13027.0048
October | 34809.0958 | 29.9028 | 304.2335 | 0 | 0.0001 | 1835630 | 12975.6909
November | 33238.4788 | 28.6203 | 278.5634 | 0 | 0.0001 | 1680700 | 12353.7794
December | 32666.2865 | 28.1818 | 264.0692 | 0 | 0.0001 | 1593220 | 12111.5214
Annual Sum or Average | 385833.6271 | 332.0614 | 3262.9228 | 0 | 0.0015 | 19686800 | 143492.7155
Minimum of Months | 24624.4465 | 21.141 | 217.4814 | 0 | 0.0001 | 1312210 | 9186.0893
Maximum of Months | 34907.2297 | 29.9601 | 309.9201 | 0 | 0.0001 | 1869960 | 13027.0048
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 326546000000 | 335323.857 | 26-JAN-12:00 | 120876.129 | 79091.122 | 24368.092 | 0 | 108416.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2572.342 | 0 | 0
February | 293615000000 | 326235.109 | 13-FEB-11:00 | 120876.129 | 79091.122 | 23341.724 | 0 | 99874.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3051.181 | 0 | 0
March | 347146000000 | 323133.308 | 31-MAR-13:00 | 120876.129 | 75091.738 | 29203.365 | 0 | 95405.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.419 | 0 | 0
April | 328246000000 | 340896.579 | 11-APR-13:00 | 120876.129 | 75091.738 | 24295.611 | 0 | 118098.305 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2534.793 | 0 | 0
May | 366935000000 | 364238.778 | 30-MAY-11:39 | 120876.129 | 79091.122 | 20480.983 | 0 | 141238.474 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 2552.052 | 0 | 0
June | 373946000000 | 364067.55 | 28-JUN-13:50 | 120876.129 | 75091.738 | 25425.657 | 0 | 140116.255 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2557.764 | 0 | 0
July | 269052000000 | 239042.703 | 24-JUL-13:00 | 67153.405 | 41836.601 | 15321.581 | 0 | 112304.112 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2426.991 | 0 | 0
August | 299996000000 | 272724.146 | 08-AUG-12:00 | 67153.405 | 41836.601 | 18008.281 | 0 | 143233.08 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2492.766 | 0 | 0
September | 383411000000 | 411251.662 | 25-SEP-14:00 | 120876.129 | 73092.045 | 42078.055 | 0 | 172588.019 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2617.411 | 0 | 0
October | 376373000000 | 377246.205 | 05-OCT-13:00 | 120876.129 | 75091.738 | 37274.025 | 0 | 141423.789 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2580.518 | 0 | 0
November | 344607000000 | 347778.276 | 20-NOV-12:00 | 120876.129 | 79091.122 | 27348.634 | 0 | 117863.044 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2599.335 | 0 | 0
December | 326669000000 | 343493.244 | 19-DEC-12:00 | 120876.129 | 79091.122 | 25800.777 | 0 | 115144.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2580.749 | 0 | 0
Annual Sum or Average | 4036540000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 269052000000 | 239042.703 |  | 67153.405 | 41836.601 | 15321.581 | 0 | 95405.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2426.991 | 0 | 0
Maximum of Months | 383411000000 | 411251.662 |  | 120876.129 | 79091.122 | 42078.055 | 0 | 172588.019 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 3051.181 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 147216.43 | 5870.78 | 0 | 153087.21
Cost per Total Building Area ($/m2) | 21.43 | 0.85 | 0 | 22.28
Cost per Net Conditioned Building Area ($/m2) | 21.43 | 0.85 | 0 | 22.28

## LasVegas
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5153.22 | 750 | 750
Net Site Energy | 5153.22 | 750 | 750
Total Source Energy | 16308.36 | 2373.51 | 2373.51
Net Source Energy | 16308.36 | 2373.51 | 2373.51
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 517.78 | 0 | 0 | 0 | 0
Cooling | 821.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.63 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 198.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0.61 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 102.89 | 0 | 0 | 0 | 971.75
Refrigeration | 72.53 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4298.21 | 855.02 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.251 | 0.11 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 324.79 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 350533.55 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14264.67 | 9644.1 | 4620.57 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116839.24 | 82125.04 | 34714.19 | 0.7 | 2.97
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 132107.29 | 92349.84 | 39757.45 | 0.7 | 2.96
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 103712.04 | 71303.13 | 32408.92 | 0.69 | 2.94
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 105287.23 | 73478.76 | 31808.46 | 0.7 | 2.97
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6048.83 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6529.88 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8085.61 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8017.09 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8024.21 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7907.35 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7911.59 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7974.06 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5428.16 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5404.55 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5459.56 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14379.04 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4658.21 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11336.98 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2084.48 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19475.66 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19166.28 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19267.94 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17071.54 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17089.63 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11635.27 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14157.32 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 26777.74 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 49975.2 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 105639.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 27600.56 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 30766.83 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 23113.82 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 24414.23 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 666.29 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.22 | 9792.18 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.82 | 10915.51 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.37 | 8337.8 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.62 | 8806.89 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1930.19 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 79254.1483 | 122.2437 | 473.1108 | 0 | 0.0009 | 2359260 | 32658.4063
February | 68044.6098 | 107.9008 | 433.8946 | 0 | 0.0008 | 2163820 | 28345.5745
March | 79204.9777 | 125.9235 | 508.1178 | 0 | 0.001 | 2533980 | 33028.4993
April | 77352.0749 | 125.2779 | 517.8514 | 0 | 0.001 | 2582610 | 32494.9174
May | 91528.7647 | 148.8759 | 618.7546 | 0 | 0.0012 | 3085860 | 38516.7015
June | 110626.0437 | 180.3893 | 752.0931 | 0 | 0.0014 | 3750860 | 46599.9771
July | 80359.7502 | 131.0466 | 546.4234 | 0 | 0.001 | 2725140 | 33851.705
August | 82863.0853 | 135.0971 | 563.1459 | 0 | 0.0011 | 2808540 | 34902.9288
September | 95191.1209 | 155.1341 | 646.3444 | 0 | 0.0012 | 3223460 | 40089.1866
October | 83980.8014 | 136.2296 | 564.2588 | 0 | 0.0011 | 2814060 | 35302.0325
November | 73978.6737 | 118.0602 | 478.7793 | 0 | 0.0009 | 2387690 | 30895.4562
December | 75934.1455 | 118.3806 | 465.1139 | 0 | 0.0009 | 2319440 | 31421.0548
Annual Sum or Average | 998318.196 | 1604.5594 | 6567.8879 | 0 | 0.0124 | 32754700 | 418106.44
Minimum of Months | 68044.6098 | 107.9008 | 433.8946 | 0 | 0.0008 | 2163820 | 28345.5745
Maximum of Months | 110626.0437 | 180.3893 | 752.0931 | 0 | 0.0014 | 3750860 | 46599.9771
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 309592000000 | 246685.642 | 18-JAN-14:00 | 120876.129 | 75091.738 | 13894.842 | 0 | 34395.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2427.178 | 0 | 0
February | 283945000000 | 258003.803 | 08-FEB-14:00 | 120876.129 | 75091.738 | 16270.713 | 0 | 43297.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2467.931 | 0 | 0
March | 332520000000 | 285541.387 | 31-MAR-14:50 | 120876.129 | 73092.045 | 20166.507 | 0 | 68888.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2518.375 | 0 | 0
April | 338901000000 | 365345.98 | 21-APR-14:00 | 120876.129 | 73092.045 | 30820.419 | 0 | 137867.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2689.425 | 0 | 0
May | 404938000000 | 401071.903 | 31-MAY-15:00 | 120876.129 | 73092.045 | 32177.538 | 0 | 172318.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.03 | 0 | 0
June | 492203000000 | 461728.373 | 27-JUN-15:00 | 120876.129 | 73092.045 | 41806.097 | 0 | 223345.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.213 | 0 | 0
July | 357604000000 | 356102.566 | 24-JUL-15:00 | 67153.405 | 40636.785 | 32214.907 | 0 | 213635.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2462.393 | 0 | 0
August | 368547000000 | 344753.026 | 04-AUG-15:00 | 67153.405 | 40636.785 | 29500.599 | 0 | 204972.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.614 | 0 | 0
September | 422996000000 | 409573.429 | 08-SEP-14:00 | 120876.129 | 73092.045 | 34287.601 | 0 | 178605.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.877 | 0 | 0
October | 369272000000 | 367601.671 | 03-OCT-14:00 | 120876.129 | 73092.045 | 31624.927 | 0 | 139326.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2682.458 | 0 | 0
November | 313322000000 | 270065.455 | 10-NOV-12:00 | 120876.129 | 79091.122 | 16737.73 | 0 | 50892.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2468.187 | 0 | 0
December | 304366000000 | 261730.941 | 05-DEC-12:00 | 120876.129 | 79091.122 | 14332.359 | 0 | 44982.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2449.267 | 0 | 0
Annual Sum or Average | 4298210000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 283945000000 | 246685.642 |  | 67153.405 | 40636.785 | 13894.842 | 0 | 34395.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2427.178 | 0 | 0
Maximum of Months | 492203000000 | 461728.373 |  | 120876.129 | 79091.122 | 41806.097 | 0 | 223345.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.877 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 119459.49 | 6695.54 | 0 | 126155.03
Cost per Total Building Area ($/m2) | 17.39 | 0.97 | 0 | 18.36
Cost per Net Conditioned Building Area ($/m2) | 17.39 | 0.97 | 0 | 18.36

## SanFrancisco
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4868.5 | 708.56 | 708.56
Net Site Energy | 4868.5 | 708.56 | 708.56
Total Source Energy | 12615.98 | 1836.12 | 1836.12
Net Source Energy | 12615.98 | 1836.12 | 1836.12
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 856.92 | 0 | 0 | 0 | 0
Cooling | 221.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 149.34 | 0 | 0 | 0 | 0 | 0
Pumps | 0.77 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 132.91 | 0 | 0 | 0 | 971.75
Refrigeration | 68.35 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3644.32 | 1224.17 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 4.092 | 0.392 | 0.253 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.392 | 0.253 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.392 | 0.253 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 4.092 | 0.392 | 0.253 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.392 | 0.253 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 324.79 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 554.39 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 534018.79 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19277.26 | 14347.43 | 4929.83 | 0.74 | 3.1
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23284.52 | 17672.1 | 5612.42 | 0.76 | 3.13
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44026.36 | 32767.37 | 11258.98 | 0.74 | 2.72
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 135844.3 | 108146.96 | 27697.34 | 0.8 | 3.31
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 151648.89 | 120353.04 | 31295.85 | 0.79 | 3.3
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 121108.75 | 95643.46 | 25465.29 | 0.79 | 3.29
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 123224.07 | 97875.36 | 25348.72 | 0.79 | 3.3
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8009.69 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10974.76 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11408.39 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11333.81 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11341.74 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9268.46 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9273.1 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9342.52 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9815.78 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9783.84 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9866.1 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23760.93 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8686.9 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20741.38 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4542.63 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41509.64 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 40987.38 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41111 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27500.33 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27519.71 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18563.49 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23247.97 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 44163.3 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 51913.6 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 100862.31 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 32679.74 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 38100.08 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 31575.84 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 30364.52 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.99 | 1130.38 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.25 | 1429.42 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.15 | 15288.44 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.04 | 16951.22 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.14 | 13391.96 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.36 | 13798.91 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2940.53 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37730.0438 | 32.8569 | 250.1663 | 0 | 0.0001 | 1509130 | 13821.679
February | 30329.7272 | 26.2513 | 229.9217 | 0 | 0.0001 | 1387130 | 11198.6516
March | 35649.6313 | 30.8994 | 262.4468 | 0 | 0.0001 | 1583330 | 13139.1121
April | 31347.699 | 27.0864 | 245.8559 | 0 | 0.0001 | 1483300 | 11599.5879
May | 33073.4988 | 28.5127 | 271.0086 | 0 | 0.0001 | 1635100 | 12273.6301
June | 32345.521 | 27.8622 | 269.139 | 0 | 0.0001 | 1623830 | 12015.9717
July | 22587.0682 | 19.4795 | 183.8022 | 0 | 0.0001 | 1108940 | 8378.1956
August | 24384.9542 | 21.0419 | 196.3093 | 0 | 0.0001 | 1184400 | 9038.6056
September | 31637.2117 | 27.2197 | 269.0358 | 0 | 0.0001 | 1623230 | 11770.5099
October | 32826.741 | 28.2866 | 271.381 | 0 | 0.0001 | 1637350 | 12189.363
November | 32513.0651 | 28.1046 | 252.9921 | 0 | 0.0001 | 1526350 | 12024.6954
December | 35207.8921 | 30.6016 | 243.9763 | 0 | 0.0001 | 1471830 | 12929.8726
Annual Sum or Average | 379633.0533 | 328.203 | 2946.035 | 0 | 0.0015 | 17773900 | 140379.8744
Minimum of Months | 22587.0682 | 19.4795 | 183.8022 | 0 | 0.0001 | 1108940 | 8378.1956
Maximum of Months | 37730.0438 | 32.8569 | 271.381 | 0 | 0.0001 | 1637350 | 13821.679
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 309427000000 | 229134.996 | 27-JAN-14:00 | 120876.129 | 75091.738 | 13200.806 | 0 | 17656.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2309.998 | 0 | 0
February | 284415000000 | 275282.568 | 15-FEB-15:00 | 120876.129 | 73092.045 | 15284.636 | 0 | 63529.1 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2500.65 | 0 | 0
March | 324642000000 | 253474.591 | 01-MAR-12:00 | 120876.129 | 79091.122 | 12784.603 | 0 | 38301.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2420.996 | 0 | 0
April | 304132000000 | 278485.87 | 14-APR-13:00 | 120876.129 | 75091.738 | 15644.645 | 0 | 64361.311 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2512.043 | 0 | 0
May | 335257000000 | 300963.821 | 17-MAY-13:00 | 120876.129 | 75091.738 | 16097.035 | 0 | 86311.265 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2587.647 | 0 | 0
June | 332947000000 | 306726.287 | 15-JUN-12:00 | 120876.129 | 75091.738 | 16091.621 | 0 | 92068.391 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2598.396 | 0 | 0
July | 227375000000 | 210841.918 | 03-JUL-12:00 | 67153.405 | 41836.601 | 10993.579 | 0 | 88335.015 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2523.312 | 0 | 0
August | 242846000000 | 203759.352 | 15-AUG-11:00 | 67153.405 | 44636.17 | 10303.582 | 0 | 79198.236 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2467.957 | 0 | 0
September | 332824000000 | 381016.682 | 28-SEP-14:00 | 120876.129 | 73092.045 | 28460.208 | 0 | 155877.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.294 | 0 | 0
October | 335719000000 | 299589.967 | 31-OCT-13:20 | 120876.129 | 75091.738 | 16750.178 | 0 | 84318.405 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2553.512 | 0 | 0
November | 312959000000 | 248377.715 | 08-NOV-12:00 | 120876.129 | 79091.122 | 12837.924 | 0 | 33170.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2402.481 | 0 | 0
December | 301781000000 | 234363.8 | 07-DEC-14:00 | 120876.129 | 75091.738 | 12280.543 | 0 | 23763.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2351.862 | 0 | 0
Annual Sum or Average | 3644320000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 227375000000 | 203759.352 |  | 67153.405 | 41836.601 | 10303.582 | 0 | 17656.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2309.998 | 0 | 0
Maximum of Months | 335719000000 | 381016.682 |  | 120876.129 | 79091.122 | 28460.208 | 0 | 155877.006 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2711.294 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 149015.03 | 10446.67 | 0 | 159461.7
Cost per Total Building Area ($/m2) | 21.69 | 1.52 | 0 | 23.21
Cost per Net Conditioned Building Area ($/m2) | 21.69 | 1.52 | 0 | 23.21

## Baltimore
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5832.18 | 848.81 | 848.81
Net Site Energy | 5832.18 | 848.81 | 848.81
Total Source Energy | 16180.61 | 2354.91 | 2354.91
Net Source Energy | 16180.61 | 2354.91 | 2354.91
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1509.78 | 0 | 0 | 0 | 0
Cooling | 526.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.62 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 147.54 | 0 | 0 | 0 | 0 | 0
Pumps | 1.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 138.02 | 0 | 0 | 0 | 971.75
Refrigeration | 69.24 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3950.03 | 1882.14 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.354 | 0.355 | 0.274 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.355 | 0.274 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.355 | 0.274 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.355 | 0.274 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.355 | 0.274 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.354 | 0.355 | 0.274 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.355 | 0.274 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.354 | 0.355 | 0.274 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.354 | 0.355 | 0.274 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.355 | 0.274 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.355 | 0.274 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 324.79 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 554.39 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 432820.8 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15305.91 | 10348.07 | 4957.84 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 138134.47 | 93390.4 | 44744.07 | 0.68 | 2.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 134740.11 | 91095.53 | 43644.58 | 0.68 | 2.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 103788.18 | 70169.44 | 33618.73 | 0.68 | 2.9
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 107469.1 | 72658.05 | 34811.04 | 0.68 | 2.9
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6637.65 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6877.68 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7434.39 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7360.86 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7367.94 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7156.99 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7161.33 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7229.62 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6601.68 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6566.67 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6624.23 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15596.92 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4723.26 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14724.51 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3943.16 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19660.43 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19254.49 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19337.46 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18012.42 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18030.94 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12263.42 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15391.96 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 37829.65 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 65798.44 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 139087.27 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 43669.72 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 42596.63 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 32811.51 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 33975.19 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 714.93 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.56 | 10435.52 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.43 | 10179.09 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.18 | 7972.2 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.33 | 8254.94 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2383.3 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 76351.4813 | 127.006 | 318.9248 | 0 | 0.0013 | 19828.0949 | 31701.4637
February | 64656.0656 | 110.3673 | 285.6208 | 0 | 0.0012 | 17758.7209 | 27102.9593
March | 65855.677 | 119.0696 | 327.6639 | 0 | 0.0013 | 20375.4527 | 28214.2976
April | 55827.387 | 105.9489 | 305.4358 | 0 | 0.0012 | 18995.0012 | 24376.0891
May | 62052.8976 | 120.8681 | 356.6376 | 0 | 0.0014 | 22180.2322 | 27378.2169
June | 74903.4085 | 147.9002 | 441.5452 | 0 | 0.0018 | 27461.4765 | 33230.9771
July | 52229.9863 | 103.2246 | 308.4079 | 0 | 0.0012 | 19181.1567 | 23180.4894
August | 55668.3463 | 109.9853 | 328.5193 | 0 | 0.0013 | 20431.9559 | 24703.3169
September | 62588.4402 | 123.2402 | 367.0535 | 0 | 0.0015 | 22828.4321 | 27736.0188
October | 61341.2731 | 117.5695 | 341.9876 | 0 | 0.0014 | 21268.5215 | 26889.3679
November | 60858.6821 | 112.1068 | 314.2419 | 0 | 0.0013 | 19541.5506 | 26262.9069
December | 69726.2868 | 119.3443 | 309.7974 | 0 | 0.0013 | 19262.0495 | 29257.7831
Annual Sum or Average | 762059.9319 | 1416.6308 | 4005.8357 | 0 | 0.0163 | 249112.6447 | 330033.8866
Minimum of Months | 52229.9863 | 103.2246 | 285.6208 | 0 | 0.0012 | 17758.7209 | 23180.4894
Maximum of Months | 76351.4813 | 147.9002 | 441.5452 | 0 | 0.0018 | 27461.4765 | 33230.9771
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 314402000000 | 228745.99 | 09-JAN-11:50 | 120876.129 | 79091.122 | 7946.367 | 0 | 17391.979 | 0 | 0.391 | 0 | 0 | 0 | 0 | 0 | 3440.002 | 0 | 0
February | 281589000000 | 221535.367 | 15-FEB-12:00 | 120876.129 | 79091.122 | 8204.765 | 0 | 11082.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2280.821 | 0 | 0
March | 323081000000 | 290212.263 | 09-MAR-15:00 | 120876.129 | 73092.045 | 13265.713 | 0 | 80399.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2578.418 | 0 | 0
April | 301192000000 | 289411.69 | 04-APR-14:00 | 120876.129 | 73092.045 | 15661.461 | 0 | 77223.864 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2558.191 | 0 | 0
May | 351699000000 | 373069.49 | 15-MAY-14:00 | 120876.129 | 73092.045 | 22323.492 | 0 | 154175.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2602.587 | 0 | 0
June | 435440000000 | 431054.644 | 30-JUN-11:00 | 120876.129 | 79091.122 | 30192.166 | 0 | 198182.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2712.927 | 0 | 0
July | 304144000000 | 343758.579 | 25-JUL-11:00 | 67153.405 | 44636.17 | 27528.629 | 0 | 201831.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.46 | 0 | 0
August | 323977000000 | 337817.715 | 17-AUG-13:00 | 67153.405 | 41836.601 | 27597.097 | 0 | 198630.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2599.904 | 0 | 0
September | 361977000000 | 391515.906 | 08-SEP-14:00 | 120876.129 | 73092.045 | 28526.071 | 0 | 166316.06 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2705.588 | 0 | 0
October | 337242000000 | 349945.276 | 03-OCT-11:00 | 120876.129 | 79091.122 | 17610.593 | 0 | 129762.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2604.469 | 0 | 0
November | 309859000000 | 311012.172 | 03-NOV-13:00 | 120876.129 | 75091.738 | 17213.019 | 0 | 95270.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2561.271 | 0 | 0
December | 305427000000 | 211739.2 | 06-DEC-11:20 | 120876.129 | 79091.122 | 8233.209 | 0 | 0 | 0 | 58.385 | 0 | 0 | 0 | 0 | 0 | 3480.354 | 0 | 0
Annual Sum or Average | 3950030000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 281589000000 | 211739.2 |  | 67153.405 | 41836.601 | 7946.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2280.821 | 0 | 0
Maximum of Months | 435440000000 | 431054.644 |  | 120876.129 | 79091.122 | 30192.166 | 0 | 201831.916 | 0 | 58.385 | 0 | 0 | 0 | 0 | 0 | 3480.354 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 85919.7 | 18342.37 | 0 | 104262.08
Cost per Total Building Area ($/m2) | 12.5 | 2.67 | 0 | 15.17
Cost per Net Conditioned Building Area ($/m2) | 12.5 | 2.67 | 0 | 15.17

## Albuquerque
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5236.81 | 762.16 | 762.16
Net Site Energy | 5236.81 | 762.16 | 762.16
Total Source Energy | 14252.32 | 2074.27 | 2074.27
Net Source Energy | 14252.32 | 2074.27 | 2074.27
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1034.11 | 0 | 0 | 0 | 0
Cooling | 379.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 179.18 | 0 | 0 | 0 | 0 | 0
Pumps | 1.17 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 134.7 | 0 | 0 | 0 | 971.75
Refrigeration | 69.22 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3833.66 | 1403.16 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 4.092 | 0.362 | 0.225 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.362 | 0.225 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.362 | 0.225 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.362 | 0.225 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.362 | 0.225 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 4.092 | 0.362 | 0.225 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.362 | 0.225 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.362 | 0.225 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.362 | 0.225 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.362 | 0.225 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.362 | 0.225 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 324.79 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 554.39 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 348056.26 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14028.2 | 9772.08 | 4256.12 | 0.7 | 2.98
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23421.79 | 16619.42 | 6802.37 | 0.71 | 3.04
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53271.5 | 36752.03 | 16519.47 | 0.69 | 2.64
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 90858.21 | 72536.79 | 18321.42 | 0.8 | 3.32
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 94938.06 | 74507.69 | 20430.38 | 0.78 | 3.27
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 73969.23 | 57097.69 | 16871.54 | 0.77 | 3.24
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 75515.47 | 59220.48 | 16294.99 | 0.78 | 3.29
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5805.73 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5703.38 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6755.78 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6665.55 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6674.58 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6488.66 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6494.36 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6579.56 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5601.3 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5565.54 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5635.9 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12969.97 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3813.11 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12380.15 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3507.75 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15807.16 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15339.69 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15428.17 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14427.52 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14451.25 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9949.65 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12380.61 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 29855.02 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 52280.48 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 110512.48 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 33630.47 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 33844.57 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 25408.54 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 26875.96 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 710.11 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.48 | 10288.32 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.52 | 10353.82 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.14 | 7903.32 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.38 | 8359.76 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1916.55 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 95722.986 | 155.9164 | 374.0225 | 0 | 0.0015 | 388849.6709 | 39900.7757
February | 83758.4995 | 138.3892 | 337.8865 | 0 | 0.0013 | 351295.7435 | 35105.892
March | 94775.9713 | 158.4949 | 392.6276 | 0 | 0.0015 | 408222.921 | 39910.2615
April | 85272.5313 | 145.8511 | 370.8423 | 0 | 0.0015 | 385595.0093 | 36227.0321
May | 99849.3839 | 173.2993 | 447.8522 | 0 | 0.0017 | 465685.2867 | 42666.6057
June | 107775.064 | 187.6726 | 486.7432 | 0 | 0.0019 | 506128.8877 | 46113.8938
July | 74132.706 | 129.1426 | 335.0895 | 0 | 0.0013 | 348435.558 | 31724.4453
August | 74878.0945 | 130.37 | 338.0737 | 0 | 0.0013 | 351538.1658 | 32036.4498
September | 96374.116 | 167.7293 | 434.7639 | 0 | 0.0017 | 452078.8428 | 41226.8839
October | 90583.3383 | 155.3191 | 396.0187 | 0 | 0.0016 | 411775.5234 | 38520.9647
November | 89405.0945 | 149.6042 | 370.8707 | 0 | 0.0015 | 385602.4628 | 37657.5138
December | 94195.6188 | 153.0142 | 365.8117 | 0 | 0.0015 | 380310.3191 | 39223.4679
Annual Sum or Average | 1086720 | 1844.8029 | 4650.6023 | 0 | 0.0183 | 4835520 | 460314.1862
Minimum of Months | 74132.706 | 129.1426 | 335.0895 | 0 | 0.0013 | 348435.558 | 31724.4453
Maximum of Months | 107775.064 | 187.6726 | 486.7432 | 0 | 0.0019 | 506128.8877 | 46113.8938
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 308285000000 | 230222.289 | 25-JAN-14:00 | 120876.129 | 75091.738 | 15218.281 | 0 | 16725.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2310.669 | 0 | 0
February | 278511000000 | 255789.846 | 14-FEB-15:00 | 120876.129 | 73092.045 | 20606.722 | 0 | 38775.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2439.433 | 0 | 0
March | 323644000000 | 261369.575 | 02-MAR-14:00 | 120876.129 | 75091.738 | 20404.164 | 0 | 42514.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2483.425 | 0 | 0
April | 305704000000 | 299241.06 | 21-APR-14:00 | 120876.129 | 73092.045 | 27190.921 | 0 | 75512.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2569.252 | 0 | 0
May | 369201000000 | 331556.065 | 31-MAY-14:00 | 120876.129 | 73092.045 | 29674.93 | 0 | 105243.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2669.166 | 0 | 0
June | 401265000000 | 361174.956 | 29-JUN-13:00 | 120876.129 | 75091.738 | 33534.677 | 0 | 128946.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2726.213 | 0 | 0
July | 276244000000 | 267048.986 | 31-JUL-14:00 | 67153.405 | 40636.785 | 29416.168 | 0 | 127286.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.267 | 0 | 0
August | 278704000000 | 263238.149 | 01-AUG-13:00 | 67153.405 | 41836.601 | 24907.083 | 0 | 126742.473 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2598.585 | 0 | 0
September | 358414000000 | 327700.93 | 20-SEP-14:00 | 120876.129 | 73092.045 | 31390.225 | 0 | 99684.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2657.738 | 0 | 0
October | 326461000000 | 299448.156 | 13-OCT-14:00 | 120876.129 | 73092.045 | 27987.524 | 0 | 74933.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2559.326 | 0 | 0
November | 305710000000 | 248818.944 | 08-NOV-14:00 | 120876.129 | 75091.738 | 19407.991 | 0 | 31017.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2425.121 | 0 | 0
December | 301515000000 | 225371.514 | 08-DEC-14:00 | 120876.129 | 75091.738 | 14200.572 | 0 | 12914.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2288.398 | 0 | 0
Annual Sum or Average | 3833660000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 276244000000 | 225371.514 |  | 67153.405 | 40636.785 | 14200.572 | 0 | 12914.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2288.398 | 0 | 0
Maximum of Months | 401265000000 | 361174.956 |  | 120876.129 | 75091.738 | 33534.677 | 0 | 128946.199 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2726.213 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 39517.14 | 9761.59 | 0 | 49278.72
Cost per Total Building Area ($/m2) | 5.75 | 1.42 | 0 | 7.17
Cost per Net Conditioned Building Area ($/m2) | 5.75 | 1.42 | 0 | 7.17

## Seattle
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5239.61 | 762.57 | 762.57
Net Site Energy | 5239.61 | 762.57 | 762.57
Total Source Energy | 8013.01 | 1166.21 | 1166.21
Net Source Energy | 8013.01 | 1166.21 | 1166.21
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1335.02 | 0 | 0 | 0 | 0
Cooling | 131.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 121.32 | 0 | 0 | 0 | 0 | 0
Pumps | 1.23 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 145.09 | 0 | 0 | 0 | 971.75
Refrigeration | 66.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3525.16 | 1714.45 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 4.092 | 0.392 | 0.253 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.392 | 0.253 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.392 | 0.253 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 4.092 | 0.392 | 0.253 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 4.092 | 0.392 | 0.253 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 324.79 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 554.39 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 375911.21 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11364.31 | 8019.68 | 3344.63 | 0.71 | 3
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23061.37 | 16464.08 | 6597.29 | 0.71 | 3.05
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51362.23 | 35929.14 | 15433.1 | 0.7 | 2.66
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 89571.56 | 68881.28 | 20690.27 | 0.77 | 3.2
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 99950.04 | 76524.34 | 23425.71 | 0.77 | 3.19
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 77740.6 | 58876.42 | 18864.18 | 0.76 | 3.18
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 81065.21 | 62110.33 | 18954.88 | 0.77 | 3.21
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5746.35 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5540.51 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7767.05 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7677.96 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7686.92 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6655.65 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6660.7 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6741.65 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5800.42 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5761.01 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5834.32 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12714.16 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6334.09 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11865.28 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2671.95 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24573.8 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23980.09 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24096.8 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14007.84 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14028.38 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9650.48 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15309.3 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 27224.93 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 56903.15 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 120284.05 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 31451.8 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 34744.83 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 26355.54 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 28226.49 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 594.95 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 4.97 | 9332.46 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.5 | 10309.58 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.17 | 7951.35 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.46 | 8515.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2069.93 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29895.7498 | 37.442 | 65.921 | 0 | 0.0003 | 870343.1043 | 11450.6378
February | 23582.5604 | 30.6767 | 59.2882 | 0 | 0.0003 | 782995.9959 | 9154.8168
March | 26685.0243 | 34.9414 | 68.55 | 0 | 0.0003 | 905351.968 | 10383.7252
April | 21251.6189 | 29.1036 | 62.744 | 0 | 0.0003 | 828887.678 | 8406.2072
May | 19854.7368 | 28.8547 | 69.2447 | 0 | 0.0003 | 915010.5413 | 8031.8866
June | 18754.349 | 28.0561 | 70.519 | 0 | 0.0003 | 931949.7705 | 7672.4945
July | 12425.4562 | 18.7522 | 47.7683 | 0 | 0.0002 | 631304.8815 | 5100.8738
August | 13119.2162 | 19.7921 | 50.3903 | 0 | 0.0002 | 665956.644 | 5384.9188
September | 18134.2759 | 26.9894 | 67.2994 | 0 | 0.0003 | 889384.2071 | 7403.9227
October | 20386.9927 | 28.9223 | 66.5936 | 0 | 0.0003 | 879890.5515 | 8171.5935
November | 25471.5176 | 33.2153 | 64.5573 | 0 | 0.0003 | 852596.8332 | 9896.8399
December | 29180.6863 | 36.5607 | 64.4352 | 0 | 0.0003 | 850728.925 | 11178.28
Annual Sum or Average | 258742.1841 | 353.3064 | 757.3111 | 0 | 0.0031 | 10004400 | 102236.1968
Minimum of Months | 12425.4562 | 18.7522 | 47.7683 | 0 | 0.0002 | 631304.8815 | 5100.8738
Maximum of Months | 29895.7498 | 37.442 | 70.519 | 0 | 0.0003 | 931949.7705 | 11450.6378
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 306675000000 | 211432.986 | 27-JAN-16:00 | 120876.129 | 73092.045 | 7508.018 | 0 | 0 | 7870 | 18.002 | 0 | 0 | 0 | 0 | 0 | 2068.792 | 0 | 0
February | 275897000000 | 227572.544 | 21-FEB-13:00 | 120876.129 | 75091.738 | 10152.295 | 0 | 19106.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2345.893 | 0 | 0
March | 319011000000 | 250175.19 | 29-MAR-14:00 | 120876.129 | 73092.045 | 18033.78 | 0 | 35759.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2413.779 | 0 | 0
April | 292068000000 | 239011.053 | 18-APR-13:00 | 120876.129 | 75091.738 | 14965.053 | 0 | 25710.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2367.862 | 0 | 0
May | 322414000000 | 292986.22 | 04-MAY-13:00 | 120876.129 | 75091.738 | 22999.634 | 0 | 71469.225 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2549.484 | 0 | 0
June | 328383000000 | 309529.802 | 28-JUN-13:00 | 120876.129 | 75091.738 | 22343.773 | 0 | 88630.091 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2588.065 | 0 | 0
July | 222447000000 | 214831.016 | 24-JUL-14:00 | 67153.405 | 40636.785 | 13048.956 | 0 | 91487.263 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2504.596 | 0 | 0
August | 234657000000 | 201264.554 | 07-AUG-14:00 | 67153.405 | 40636.785 | 12637.293 | 0 | 78376.262 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2460.805 | 0 | 0
September | 313384000000 | 329053.409 | 13-SEP-14:00 | 120876.129 | 73092.045 | 27670.401 | 0 | 104792.23 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2622.595 | 0 | 0
October | 310039000000 | 262825.396 | 17-OCT-14:00 | 120876.129 | 73092.045 | 19477.355 | 0 | 46913.89 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2465.977 | 0 | 0
November | 300422000000 | 227352.744 | 03-NOV-11:00 | 120876.129 | 79091.122 | 8670.916 | 0 | 16365.593 | 0 | 0.175 | 0 | 0 | 0 | 0 | 0 | 2348.808 | 0 | 0
December | 299764000000 | 211443.192 | 28-DEC-16:19 | 120876.129 | 73092.045 | 7508.018 | 0 | 0 | 7870 | 37.45 | 0 | 0 | 0 | 0 | 0 | 2059.549 | 0 | 0
Annual Sum or Average | 3525160000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 222447000000 | 201264.554 |  | 67153.405 | 40636.785 | 7508.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2059.549 | 0 | 0
Maximum of Months | 328383000000 | 329053.409 |  | 120876.129 | 79091.122 | 27670.401 | 0 | 104792.23 | 7870 | 37.45 | 0 | 0 | 0 | 0 | 0 | 2622.595 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 73634.89 | 14391 | 0 | 88025.89
Cost per Total Building Area ($/m2) | 10.72 | 2.09 | 0 | 12.81
Cost per Net Conditioned Building Area ($/m2) | 10.72 | 2.09 | 0 | 12.81

## Chicago
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6295.06 | 916.18 | 916.18
Net Site Energy | 6295.06 | 916.18 | 916.18
Total Source Energy | 16195.32 | 2357.05 | 2357.05
Net Source Energy | 16195.32 | 2357.05 | 2357.05
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2109.44 | 0 | 0 | 0 | 0
Cooling | 378.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 145.7 | 0 | 0 | 0 | 0 | 0
Pumps | 2.22 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 152.95 | 0 | 0 | 0 | 971.75
Refrigeration | 67.66 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3798.33 | 2496.73 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.354 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.354 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.354 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 324.79 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 554.39 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 467157.25 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14751.07 | 9972.95 | 4778.12 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 127537.01 | 86225.63 | 41311.38 | 0.68 | 2.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129366.23 | 87462.34 | 41903.89 | 0.68 | 2.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 98174.44 | 66374.09 | 31800.35 | 0.68 | 2.9
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 102864.68 | 69545.08 | 33319.6 | 0.68 | 2.9
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6139.05 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6363.04 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7337.64 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7256.35 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7264.27 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7006.9 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7011.55 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7088.02 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6020.63 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5981.17 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6045.52 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14375.96 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5258.16 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13141.91 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4022.16 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18399.67 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17935.17 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18023.83 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16495.86 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16515.54 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11288.36 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14146.75 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 42590.86 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 76866.16 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 162482.64 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 49273.97 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 49980.69 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 37929.73 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 39741.8 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 689.01 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.14 | 9634.93 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.21 | 9773.12 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.95 | 7541 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.14 | 7901.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2572.37 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 135387.4907 | 219.4649 | 579.4922 | 0 | 0.0018 | 133370.5708 | 56091.2432
February | 117308.3678 | 193.1191 | 519.8575 | 0 | 0.0016 | 119650.5181 | 48884.1074
March | 127077.656 | 214.927 | 597.4714 | 0 | 0.0018 | 137523.3234 | 53502.4988
April | 107745.8628 | 190.0077 | 553.1998 | 0 | 0.0017 | 127344.8239 | 46106.9216
May | 120866.0965 | 217.0579 | 644.0199 | 0 | 0.0019 | 148256.7538 | 52095.4873
June | 143441.3142 | 259.5042 | 775.726 | 0 | 0.0023 | 178578.7292 | 62007.9061
July | 97656.3428 | 176.7821 | 528.7756 | 0 | 0.0016 | 121728.7884 | 42226.048
August | 97608.8995 | 176.59 | 527.8817 | 0 | 0.0016 | 121522.8613 | 42195.3738
September | 120333.283 | 217.2439 | 648.0317 | 0 | 0.002 | 149181.8197 | 51975.1
October | 115331.2767 | 205.1897 | 602.9676 | 0 | 0.0018 | 138803.7337 | 49525.4967
November | 117612.2085 | 201.3837 | 567.7495 | 0 | 0.0017 | 130685.7868 | 49753.081
December | 127601.1682 | 210.148 | 565.9764 | 0 | 0.0018 | 130265.375 | 53181.3347
Annual Sum or Average | 1427970 | 2481.4182 | 7111.1494 | 0 | 0.0217 | 1636910 | 607544.5986
Minimum of Months | 97608.8995 | 176.59 | 519.8575 | 0 | 0.0016 | 119650.5181 | 42195.3738
Maximum of Months | 143441.3142 | 259.5042 | 775.726 | 0 | 0.0023 | 178578.7292 | 62007.9061
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 309476000000 | 212308.919 | 27-JAN-16:00 | 120876.129 | 73092.045 | 7519.741 | 0 | 0 | 7870 | 1108.27 | 0 | 0 | 0 | 0 | 0 | 1842.735 | 0 | 0
February | 277640000000 | 211741.969 | 28-FEB-11:20 | 120876.129 | 79091.122 | 8246.138 | 0 | 0 | 0 | 7.221 | 0 | 0 | 0 | 0 | 0 | 3521.358 | 0 | 0
March | 319113000000 | 252810.743 | 31-MAR-14:00 | 120876.129 | 73092.045 | 13064.982 | 0 | 43301.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2475.712 | 0 | 0
April | 295494000000 | 259114.22 | 07-APR-13:00 | 120876.129 | 75091.738 | 14799.955 | 0 | 45830.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2515.938 | 0 | 0
May | 344019000000 | 347521.799 | 30-MAY-14:00 | 120876.129 | 73092.045 | 19519.113 | 0 | 131415.863 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2618.639 | 0 | 0
June | 414378000000 | 417432.075 | 08-JUN-12:00 | 120876.129 | 75091.738 | 31477.815 | 0 | 187273.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2712.93 | 0 | 0
July | 282462000000 | 314076.208 | 14-JUL-11:00 | 67153.405 | 44636.17 | 16467.638 | 0 | 183221.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2597.984 | 0 | 0
August | 281985000000 | 316549.925 | 04-AUG-15:00 | 67153.405 | 40636.785 | 26956.483 | 0 | 179255.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2548.019 | 0 | 0
September | 346165000000 | 378793.268 | 06-SEP-11:00 | 120876.129 | 79091.122 | 23380.776 | 0 | 152797.481 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2647.755 | 0 | 0
October | 322084000000 | 315621.684 | 31-OCT-11:00 | 120876.129 | 79091.122 | 15195.223 | 0 | 97903.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.044 | 0 | 0
November | 303247000000 | 305821.306 | 02-NOV-14:39 | 120876.129 | 73092.045 | 15913.322 | 0 | 93387.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2552.33 | 0 | 0
December | 302271000000 | 211467.378 | 12-DEC-16:19 | 120876.129 | 73092.045 | 7519.741 | 0 | 0 | 7870 | 15.67 | 0 | 0 | 0 | 0 | 0 | 2093.793 | 0 | 0
Annual Sum or Average | 3798330000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 277640000000 | 211467.378 |  | 67153.405 | 40636.785 | 7519.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1842.735 | 0 | 0
Maximum of Months | 414378000000 | 417432.075 |  | 120876.129 | 79091.122 | 31477.815 | 0 | 187273.463 | 7870 | 1108.27 | 0 | 0 | 0 | 0 | 0 | 3521.358 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 93022.25 | 20948.37 | 0 | 113970.62
Cost per Total Building Area ($/m2) | 13.54 | 3.05 | 0 | 16.59
Cost per Net Conditioned Building Area ($/m2) | 13.54 | 3.05 | 0 | 16.59

## Boulder
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5457.16 | 794.23 | 794.23
Net Site Energy | 5457.16 | 794.23 | 794.23
Total Source Energy | 14069.82 | 2047.71 | 2047.71
Net Source Energy | 14069.82 | 2047.71 | 2047.71
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1427.5 | 0 | 0 | 0 | 0
Cooling | 229.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 140.12 | 0 | 0 | 0 | 0 | 0
Pumps | 1.73 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 151.75 | 0 | 0 | 0 | 971.75
Refrigeration | 67.29 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3643.58 | 1813.59 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.354 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.354 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.354 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 324.79 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 554.39 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 334749.93 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12649.37 | 8775.56 | 3873.82 | 0.69 | 2.98
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23612.24 | 16701.5 | 6910.73 | 0.71 | 3.03
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53923.29 | 37032.95 | 16890.34 | 0.69 | 2.64
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 78150.79 | 60580.24 | 17570.55 | 0.78 | 3.25
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 84143 | 64239.54 | 19903.46 | 0.76 | 3.2
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 65482.64 | 49096.52 | 16386.12 | 0.75 | 2.73
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 66853.49 | 51030.22 | 15823.27 | 0.76 | 3.2
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4788.93 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4760.62 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5707.45 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5623.4 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5632.45 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5413.88 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5418.69 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5497.99 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4527.63 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4490.98 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4557.57 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10774.84 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4602.45 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9728.23 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3137.74 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13311.53 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12892.63 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12978.62 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11757.18 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11776.38 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8136.59 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10090.16 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 31790.86 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 62407.86 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 131920.13 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 34238.41 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 35608.93 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 26570.58 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 28279.96 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 633.45 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.42 | 8429.95 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.6 | 8767.38 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.43 | 3750.87 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.65 | 6962.9 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1843.28 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 98781.3662 | 158.6926 | 374.0359 | 0 | 0.0015 | 388847.3348 | 40959.2936
February | 86907.4851 | 140.6473 | 334.6514 | 0 | 0.0013 | 347911.1082 | 36136.8884
March | 96606.7301 | 159.5457 | 389.3281 | 0 | 0.0015 | 404778.304 | 40483.9525
April | 85345.564 | 144.7081 | 364.2973 | 0 | 0.0014 | 378781.2469 | 36133.6909
May | 91829.3531 | 157.3482 | 400.8848 | 0 | 0.0016 | 416834.5328 | 39040.3031
June | 96401.0951 | 167.0946 | 431.1957 | 0 | 0.0017 | 448364.1781 | 41171.5541
July | 66890.9059 | 116.39 | 301.6136 | 0 | 0.0012 | 313625.5447 | 28611.9337
August | 69280.9659 | 120.4914 | 312.0806 | 0 | 0.0012 | 324508.9794 | 29628.6419
September | 88388.5553 | 152.7193 | 392.7209 | 0 | 0.0015 | 408354.2894 | 37701.7527
October | 89740.9722 | 153.3299 | 389.387 | 0 | 0.0015 | 404876.3835 | 38109.3018
November | 90579.4636 | 149.6265 | 365.2263 | 0 | 0.0014 | 379720.3494 | 37961.5831
December | 97096.9624 | 155.4442 | 364.7221 | 0 | 0.0015 | 379160.545 | 40207.6573
Annual Sum or Average | 1057850 | 1776.0376 | 4420.1439 | 0 | 0.0174 | 4595760 | 446146.5531
Minimum of Months | 66890.9059 | 116.39 | 301.6136 | 0 | 0.0012 | 313625.5447 | 28611.9337
Maximum of Months | 98781.3662 | 167.0946 | 431.1957 | 0 | 0.0017 | 448364.1781 | 41171.5541
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 308283000000 | 234871.83 | 24-JAN-12:00 | 120876.129 | 79091.122 | 12317.111 | 0 | 20209.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2377.949 | 0 | 0
February | 275828000000 | 223643.145 | 07-FEB-14:00 | 120876.129 | 75091.738 | 12820.299 | 0 | 12565.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2289.546 | 0 | 0
March | 320913000000 | 259890.063 | 30-MAR-14:00 | 120876.129 | 73092.045 | 19315.752 | 0 | 44131.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2474.387 | 0 | 0
April | 300302000000 | 277697.006 | 25-APR-14:00 | 120876.129 | 73092.045 | 20725.903 | 0 | 60456.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2546.828 | 0 | 0
May | 330471000000 | 301634.274 | 23-MAY-15:00 | 120876.129 | 73092.045 | 22193.794 | 0 | 82968.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2503.821 | 0 | 0
June | 355469000000 | 342354.808 | 28-JUN-11:00 | 120876.129 | 79091.122 | 21460.852 | 0 | 118241.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2685.578 | 0 | 0
July | 248646000000 | 246872.896 | 17-JUL-15:30 | 67153.405 | 40636.785 | 21570.82 | 0 | 115061.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2450.723 | 0 | 0
August | 257275000000 | 251646.275 | 30-AUG-13:00 | 67153.405 | 41836.601 | 20066.186 | 0 | 120002.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2587.287 | 0 | 0
September | 323748000000 | 321095.49 | 05-SEP-13:00 | 120876.129 | 75091.738 | 22645.995 | 0 | 99791.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.511 | 0 | 0
October | 320991000000 | 298821.396 | 05-OCT-14:00 | 120876.129 | 73092.045 | 23177.026 | 0 | 79082.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2594.102 | 0 | 0
November | 301047000000 | 247883.061 | 10-NOV-13:00 | 120876.129 | 75091.738 | 15279.746 | 0 | 34171.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2463.91 | 0 | 0
December | 300603000000 | 219880.402 | 21-DEC-14:00 | 120876.129 | 75091.738 | 11660.338 | 0 | 9972.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2279.326 | 0 | 0
Annual Sum or Average | 3643580000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 248646000000 | 219880.402 |  | 67153.405 | 40636.785 | 11660.338 | 0 | 9972.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2279.326 | 0 | 0
Maximum of Months | 355469000000 | 342354.808 |  | 120876.129 | 79091.122 | 23177.026 | 0 | 120002.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.511 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37567.34 | 12630.52 | 0 | 50197.86
Cost per Total Building Area ($/m2) | 5.47 | 1.84 | 0 | 7.31
Cost per Net Conditioned Building Area ($/m2) | 5.47 | 1.84 | 0 | 7.31

## Minneapolis
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6848.05 | 996.66 | 996.66
Net Site Energy | 6848.05 | 996.66 | 996.66
Total Source Energy | 16156.94 | 2351.47 | 2351.47
Net Source Energy | 16156.94 | 2351.47 | 2351.47
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2746.6 | 0 | 0 | 0 | 0
Cooling | 290.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 135.34 | 0 | 0 | 0 | 0 | 0
Pumps | 3.43 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 166.1 | 0 | 0 | 0 | 971.75
Refrigeration | 66.9 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3701.01 | 3147.04 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 2.956 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 2.956 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 324.79 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 554.39 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 442984.18 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13928.75 | 9416.99 | 4511.76 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 114267.92 | 77254.62 | 37013.3 | 0.68 | 2.9
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 114103.43 | 77143.41 | 36960.02 | 0.68 | 2.9
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 86096.97 | 58208.72 | 27888.25 | 0.68 | 2.62
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 90705.45 | 61324.43 | 29381.02 | 0.68 | 2.9
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6138.96 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5576.94 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6514.53 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6431.99 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6440.11 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6133.93 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6138.5 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6215.17 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5086.55 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5045.55 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5112.39 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12653.05 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5615.41 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11581.61 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4029.63 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16336.32 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15869.96 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15957.74 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14340.21 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14343.77 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9771.49 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12370.9 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 43462.28 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 83069.72 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 175595.96 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 48483.63 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 48413.84 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 36530.76 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 38486.12 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 650.6 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.6 | 8777.18 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.59 | 8764.54 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.47 | 3791.74 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.65 | 6967.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2439.26 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 108147.7596 | 160.5052 | 203.4841 | 0 | 0.0016 | 133623.4571 | 43388.8923
February | 90587.5044 | 138.0595 | 182.2182 | 0 | 0.0014 | 119679.8066 | 36689.3603
March | 89057.6016 | 144.6877 | 208.3152 | 0 | 0.0016 | 136869.2677 | 36926.1584
April | 71614.8144 | 124.0077 | 192.4519 | 0 | 0.0014 | 126482.7281 | 30425.8638
May | 78586.5172 | 140.1023 | 224.2849 | 0 | 0.0016 | 147420.4723 | 33772.3178
June | 87894.1952 | 158.5958 | 257.0356 | 0 | 0.0019 | 168954.5288 | 37953.8776
July | 58510.6955 | 105.6953 | 171.4943 | 0 | 0.0013 | 112727.0228 | 25277.0568
August | 61936.17 | 111.878 | 181.5176 | 0 | 0.0013 | 119315.5517 | 26756.3966
September | 72385.7818 | 129.7397 | 208.8411 | 0 | 0.0015 | 137272.0743 | 31173.7093
October | 75040.4009 | 129.9462 | 201.6797 | 0 | 0.0015 | 132547.4141 | 31881.8889
November | 83283.8498 | 136.091 | 197.3614 | 0 | 0.0015 | 129676.0129 | 34607.0798
December | 98176.934 | 149.9509 | 198.5417 | 0 | 0.0015 | 130402.7682 | 39794.2346
Annual Sum or Average | 975222.2244 | 1629.2591 | 2427.2257 | 0 | 0.018 | 1594970 | 408646.8362
Minimum of Months | 58510.6955 | 105.6953 | 171.4943 | 0 | 0.0013 | 112727.0228 | 25277.0568
Maximum of Months | 108147.7596 | 160.5052 | 257.0356 | 0 | 0.0019 | 168954.5288 | 43388.8923
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 310063000000 | 212229.484 | 04-JAN-16:00 | 120876.129 | 73092.045 | 6941.838 | 0 | 0 | 7870 | 1607.997 | 0 | 0 | 0 | 0 | 0 | 1841.476 | 0 | 0
February | 277708000000 | 211221.415 | 03-FEB-11:09 | 120876.129 | 79091.122 | 6941.838 | 0 | 0 | 0 | 892.279 | 0 | 0 | 0 | 0 | 0 | 3420.047 | 0 | 0
March | 317595000000 | 228121.936 | 23-MAR-14:00 | 120876.129 | 73092.045 | 11241.551 | 0 | 20594.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2318.184 | 0 | 0
April | 293494000000 | 247441.992 | 14-APR-14:00 | 120876.129 | 73092.045 | 13194.132 | 0 | 37836.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2442.785 | 0 | 0
May | 342078000000 | 359278.687 | 31-MAY-11:00 | 120876.129 | 79091.122 | 18952.084 | 0 | 137711.891 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2647.456 | 0 | 0
June | 392046000000 | 397094.252 | 30-JUN-11:00 | 120876.129 | 79091.122 | 25062.686 | 0 | 169370.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2694.067 | 0 | 0
July | 261575000000 | 295253.491 | 13-JUL-15:50 | 67153.405 | 40636.785 | 21905.609 | 0 | 163000.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2557.405 | 0 | 0
August | 276863000000 | 291083.864 | 25-AUG-15:00 | 67153.405 | 40636.785 | 21403.756 | 0 | 159344.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2544.968 | 0 | 0
September | 318530000000 | 350832.444 | 14-SEP-14:00 | 120876.129 | 73092.045 | 22003.714 | 0 | 132224.984 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2635.558 | 0 | 0
October | 307566000000 | 263304.13 | 06-OCT-14:00 | 120876.129 | 73092.045 | 15506.187 | 0 | 51329.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500.656 | 0 | 0
November | 300903000000 | 241044.311 | 02-NOV-14:00 | 120876.129 | 73092.045 | 13680.641 | 0 | 31022.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2372.988 | 0 | 0
December | 302590000000 | 211130.559 | 29-DEC-16:00 | 120876.129 | 73092.045 | 6941.838 | 0 | 0 | 7870 | 500.528 | 0 | 0 | 0 | 0 | 0 | 1850.019 | 0 | 0
Annual Sum or Average | 3701010000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 261575000000 | 211130.559 |  | 67153.405 | 40636.785 | 6941.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1841.476 | 0 | 0
Maximum of Months | 392046000000 | 397094.252 |  | 120876.129 | 79091.122 | 25062.686 | 0 | 169370.248 | 7870 | 1607.997 | 0 | 0 | 0 | 0 | 0 | 3420.047 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63188.28 | 24863.58 | 0 | 88051.86
Cost per Total Building Area ($/m2) | 9.2 | 3.62 | 0 | 12.81
Cost per Net Conditioned Building Area ($/m2) | 9.2 | 3.62 | 0 | 12.81

## Helena
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6129.42 | 892.07 | 892.07
Net Site Energy | 6129.42 | 892.07 | 892.07
Total Source Energy | 15137.17 | 2203.05 | 2203.05
Net Source Energy | 15137.17 | 2203.05 | 2203.05
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2185.51 | 0 | 0 | 0 | 0
Cooling | 133.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.53 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 135.5 | 0 | 0 | 0 | 0 | 0
Pumps | 2.66 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 167.7 | 0 | 0 | 0 | 971.75
Refrigeration | 65.66 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3541.88 | 2587.55 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 2.956 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 2.956 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 324.79 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 554.39 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 409028.42 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10032.27 | 7433.38 | 2598.9 | 0.74 | 3.07
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19668.51 | 15001.76 | 4666.75 | 0.76 | 3.14
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46116.8 | 33668.35 | 12448.44 | 0.73 | 2.7
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 82432.78 | 65835.37 | 16597.41 | 0.8 | 3.32
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 74311.12 | 59348.97 | 14962.15 | 0.8 | 3.35
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 58655.78 | 46845.74 | 11810.03 | 0.8 | 3.35
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 58692.55 | 46875.11 | 11817.44 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5463.86 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4779.06 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5604.42 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5519.85 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5529.14 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5126.72 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5131.48 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5211.47 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4346.7 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4310.28 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4374.67 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10987.79 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5647.42 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10399.07 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3874.38 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14478.27 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14483.07 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14405.22 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14413.53 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14417.5 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9521.55 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11861.63 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 36075.03 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 75696.65 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 160010.48 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 47939.22 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 43216.03 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 34111.58 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 34132.96 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 592.62 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 4.98 | 9341.99 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.49 | 8562.72 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.54 | 6758.78 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.55 | 6763.02 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2252.28 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 101724.7027 | 155.6774 | 229.5369 | 0 | 0.0017 | 5441880 | 41329.8869
February | 86717.8732 | 135.6661 | 206.3609 | 0 | 0.0015 | 4893000 | 35518.364
March | 90103.5991 | 147.359 | 237.5492 | 0 | 0.0017 | 5633690 | 37523.3753
April | 77583.8437 | 129.8448 | 215.251 | 0 | 0.0015 | 5105360 | 32595.7926
May | 80571.9793 | 138.5997 | 237.1176 | 0 | 0.0017 | 5624600 | 34214.09
June | 83956.6649 | 146.4106 | 254.2702 | 0 | 0.0018 | 6031770 | 35843.587
July | 55572.9911 | 97.5715 | 170.6898 | 0 | 0.0012 | 4049180 | 23789.4248
August | 56573.6894 | 98.8976 | 172.2051 | 0 | 0.0012 | 4085060 | 24176.1488
September | 76081.1917 | 132.0009 | 227.9746 | 0 | 0.0016 | 5407890 | 32415.989
October | 79986.0541 | 135.9378 | 229.4113 | 0 | 0.0016 | 5441550 | 33805.3941
November | 85400.1923 | 139.1232 | 223.183 | 0 | 0.0016 | 5292890 | 35512.1049
December | 96775.747 | 149.7033 | 224.155 | 0 | 0.0016 | 5314600 | 39473.7961
Annual Sum or Average | 971048.5285 | 1606.792 | 2627.7044 | 0 | 0.0185 | 62321500 | 406197.9535
Minimum of Months | 55572.9911 | 97.5715 | 170.6898 | 0 | 0.0012 | 4049180 | 23789.4248
Maximum of Months | 101724.7027 | 155.6774 | 254.2702 | 0 | 0.0018 | 6031770 | 41329.8869
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 309275000000 | 214973.713 | 05-JAN-08:09 | 120876.129 | 75091.738 | 7162.15 | 0 | 0 | 7870 | 2073.174 | 0 | 0 | 0 | 0 | 0 | 1900.523 | 0 | 0
February | 278081000000 | 230503.545 | 02-FEB-14:00 | 120876.129 | 75091.738 | 11963.717 | 0 | 20203.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2368.621 | 0 | 0
March | 320176000000 | 244572.351 | 30-MAR-14:00 | 120876.129 | 73092.045 | 17174.574 | 0 | 31008.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2421.492 | 0 | 0
April | 290150000000 | 235440.961 | 06-APR-14:00 | 120876.129 | 73092.045 | 14478.651 | 0 | 24610.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2383.528 | 0 | 0
May | 319659000000 | 272067.926 | 16-MAY-14:00 | 120876.129 | 73092.045 | 21483.832 | 0 | 54092.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2523.692 | 0 | 0
June | 342800000000 | 329607.134 | 30-JUN-14:00 | 120876.129 | 73092.045 | 30128.063 | 0 | 102783.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2727.472 | 0 | 0
July | 230125000000 | 230534.818 | 21-JUL-15:00 | 67153.405 | 40636.785 | 26188.144 | 0 | 94115.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2441.089 | 0 | 0
August | 232164000000 | 204807.262 | 09-AUG-15:00 | 67153.405 | 40636.785 | 13181.919 | 0 | 81421.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2414.111 | 0 | 0
September | 307343000000 | 299845.012 | 12-SEP-13:00 | 120876.129 | 75091.738 | 24173.277 | 0 | 77106.284 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2597.581 | 0 | 0
October | 309256000000 | 260410.177 | 06-OCT-14:00 | 120876.129 | 73092.045 | 20344.389 | 0 | 43608.727 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2488.886 | 0 | 0
November | 300808000000 | 219003.282 | 21-NOV-11:50 | 120876.129 | 79091.122 | 8907.028 | 0 | 6793.76 | 0 | 0.357 | 0 | 0 | 0 | 0 | 0 | 3334.886 | 0 | 0
December | 302041000000 | 214538.14 | 18-DEC-08:09 | 120876.129 | 75091.738 | 7162.15 | 0 | 0 | 7870 | 1635.461 | 0 | 0 | 0 | 0 | 0 | 1902.663 | 0 | 0
Annual Sum or Average | 3541880000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 230125000000 | 204807.262 |  | 67153.405 | 40636.785 | 7162.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900.523 | 0 | 0
Maximum of Months | 342800000000 | 329607.134 |  | 120876.129 | 79091.122 | 30128.063 | 0 | 102783.425 | 7870 | 2073.174 | 0 | 0 | 0 | 0 | 0 | 3334.886 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 74526.78 | 21140.3 | 0 | 95667.09
Cost per Total Building Area ($/m2) | 10.85 | 3.08 | 0 | 13.92
Cost per Net Conditioned Building Area ($/m2) | 10.85 | 3.08 | 0 | 13.92

## Duluth
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7231.51 | 1052.47 | 1052.47
Net Site Energy | 7231.51 | 1052.47 | 1052.47
Total Source Energy | 16138.51 | 2348.79 | 2348.79
Net Source Energy | 16138.51 | 2348.79 | 2348.79
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3296.16 | 0 | 0 | 0 | 0
Cooling | 120.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.46 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 120.99 | 0 | 0 | 0 | 0 | 0
Pumps | 4.29 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 186.43 | 0 | 0 | 0 | 971.75
Refrigeration | 64.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3514.58 | 3716.93 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 2.956 | 0.487 | 0.409 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.487 | 0.409 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 2.956 | 0.487 | 0.409 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.487 | 0.409 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 324.79 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 554.39 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 426082.64 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11970.87 | 8093.3 | 3877.56 | 0.68 | 2.95
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 2.98
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 2.62
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 110912.7 | 74986.22 | 35926.48 | 0.68 | 2.9
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 104565.59 | 70695.04 | 33870.55 | 0.68 | 2.9
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 81866.12 | 55348.31 | 26517.81 | 0.68 | 2.62
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 82398.28 | 55708.1 | 26690.19 | 0.68 | 2.62
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5538.37 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4941.36 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6212.75 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6097.05 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6109.39 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5651.51 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5657.77 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5768.83 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4094.62 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4039.3 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4136.33 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11328.09 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5811.91 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9211.58 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3064.08 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15585.24 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15004.72 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15140.94 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14892.77 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14896.13 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9839.22 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12182.28 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 38233.68 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 85028.19 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 179735.84 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 48431.31 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 45659.77 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 35747.78 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 35980.16 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 559.15 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.47 | 8519.45 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.21 | 8031.92 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.3 | 3605.41 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.57 | 622 | 3.32 | 3628.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2346.19 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 107827.6682 | 160.0722 | 203.0187 | 0 | 0.0016 | 133318.097 | 43264.4898
February | 93238.5202 | 140.5362 | 182.4592 | 0 | 0.0014 | 119829.5492 | 37613.5986
March | 95254.3505 | 150.241 | 208.1111 | 0 | 0.0016 | 136713.9189 | 39064.0353
April | 75248.4182 | 126.365 | 189.4048 | 0 | 0.0014 | 124464.0076 | 31593.5206
May | 75470.5978 | 131.2692 | 204.718 | 0 | 0.0015 | 134546.6396 | 32119.915
June | 76563.77 | 137.1702 | 220.7069 | 0 | 0.0016 | 145071.2601 | 32967.4795
July | 53298.9226 | 95.944 | 155.1228 | 0 | 0.0011 | 101964.4016 | 22993.3628
August | 52906.0613 | 94.3767 | 151.1787 | 0 | 0.0011 | 99368.6016 | 22741.6632
September | 70073.1012 | 123.4533 | 195.1963 | 0 | 0.0014 | 128295.0999 | 29973.0475
October | 76688.4749 | 130.7749 | 199.5147 | 0 | 0.0015 | 131116.2739 | 32388.5142
November | 86306.6426 | 138.7788 | 197.193 | 0 | 0.0015 | 129554.9052 | 35647.9218
December | 101171.9843 | 152.6624 | 198.5323 | 0 | 0.0015 | 130386.4288 | 40830.1452
Annual Sum or Average | 964048.5118 | 1581.6438 | 2305.1567 | 0 | 0.0172 | 1514630 | 401197.6936
Minimum of Months | 52906.0613 | 94.3767 | 151.1787 | 0 | 0.0011 | 99368.6016 | 22741.6632
Maximum of Months | 107827.6682 | 160.0722 | 220.7069 | 0 | 0.0016 | 145071.2601 | 43264.4898
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 309355000000 | 211804.432 | 09-JAN-11:09 | 120876.129 | 79091.122 | 6494.847 | 0 | 0 | 0 | 1925.514 | 0 | 0 | 0 | 0 | 0 | 3416.819 | 0 | 0
February | 278055000000 | 211628.965 | 01-FEB-11:09 | 120876.129 | 79091.122 | 6494.847 | 0 | 0 | 0 | 1743.198 | 0 | 0 | 0 | 0 | 0 | 3423.668 | 0 | 0
March | 317234000000 | 210429.242 | 01-MAR-11:20 | 120876.129 | 79091.122 | 6789.59 | 0 | 0 | 0 | 222.396 | 0 | 0 | 0 | 0 | 0 | 3450.004 | 0 | 0
April | 288809000000 | 232485.373 | 04-APR-14:00 | 120876.129 | 73092.045 | 12433.392 | 0 | 23757.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2326.211 | 0 | 0
May | 312205000000 | 267539.45 | 31-MAY-14:00 | 120876.129 | 73092.045 | 17708.235 | 0 | 53375.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2487.969 | 0 | 0
June | 336627000000 | 354012.832 | 14-JUN-15:09 | 120876.129 | 73092.045 | 20826.521 | 0 | 136598.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2619.639 | 0 | 0
July | 236601000000 | 247273.017 | 06-JUL-15:00 | 67153.405 | 40636.785 | 11378.834 | 0 | 125669.752 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2434.236 | 0 | 0
August | 230577000000 | 224480.15 | 11-AUG-15:30 | 67153.405 | 40636.785 | 9176.687 | 0 | 105106.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2406.4 | 0 | 0
September | 297699000000 | 325570.725 | 07-SEP-14:00 | 120876.129 | 73092.045 | 18910.452 | 0 | 110120.999 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2571.096 | 0 | 0
October | 304245000000 | 238718.447 | 27-OCT-11:00 | 120876.129 | 79091.122 | 11468.468 | 0 | 24896.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2385.735 | 0 | 0
November | 300622000000 | 212658.195 | 09-NOV-11:50 | 120876.129 | 79091.122 | 7575.363 | 0 | 1833.47 | 0 | 0.586 | 0 | 0 | 0 | 0 | 0 | 3281.524 | 0 | 0
December | 302552000000 | 210893.221 | 20-DEC-16:00 | 120876.129 | 73092.045 | 6494.847 | 0 | 0 | 7870 | 705.943 | 0 | 0 | 0 | 0 | 0 | 1854.257 | 0 | 0
Annual Sum or Average | 3514580000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 230577000000 | 210429.242 |  | 67153.405 | 40636.785 | 6494.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1854.257 | 0 | 0
Maximum of Months | 336627000000 | 354012.832 |  | 120876.129 | 79091.122 | 20826.521 | 0 | 136598.498 | 7870 | 1925.514 | 0 | 0 | 0 | 0 | 0 | 3450.004 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 58312.59 | 29308.35 | 0 | 87620.94
Cost per Total Building Area ($/m2) | 8.49 | 4.27 | 0 | 12.75
Cost per Net Conditioned Building Area ($/m2) | 8.49 | 4.27 | 0 | 12.75

## Fairbanks
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10592.96 | 1541.69 | 1541.69
Net Site Energy | 10592.96 | 1541.69 | 1541.69
Total Source Energy | 20245.01 | 2946.44 | 2946.44
Net Source Energy | 20245.01 | 2946.44 | 2946.44
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6648.94 | 0 | 0 | 0 | 0
Cooling | 63.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 122.7 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 158.33 | 0 | 0 | 0 | 0 | 0
Pumps | 11.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 210.69 | 0 | 0 | 0 | 971.75
Refrigeration | 62.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3498.99 | 7093.97 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 2.956 | 0.616 | 0.541 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.616 | 0.541 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.616 | 0.541 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.616 | 0.541 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.616 | 0.541 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 2.956 | 0.616 | 0.541 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.616 | 0.541 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.616 | 0.541 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 2.956 | 0.616 | 0.541 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.616 | 0.541 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 2.956 | 0.616 | 0.541 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 324.79 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 554.39 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 670675.74 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8109.77 | 6476.91 | 1632.86 | 0.8 | 3.19
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17746.6 | 14173.41 | 3573.18 | 0.8 | 3.17
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37513.44 | 29960.31 | 7553.13 | 0.8 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 95559.67 | 76319.23 | 19240.44 | 0.8 | 3.32
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 89354.2 | 71363.2 | 17991 | 0.8 | 3.32
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 70154.65 | 56029.38 | 14125.27 | 0.8 | 3.35
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 70476.47 | 56286.4 | 14190.07 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7182.08 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6524.78 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7258.45 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7098.78 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7120.59 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6997.31 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6998.11 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7003.98 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4987.07 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4987.36 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4936.15 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14818.04 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7471.97 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13326.21 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4525.19 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26006.33 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24802.8 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25046.59 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19562.38 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19565.9 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12919.42 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15855.79 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 48116.86 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 105294.08 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 222574.67 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 77776.65 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 72725.98 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 57099.34 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 57361.27 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 568.25 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.77 | 10829.64 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.4 | 10126.38 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.24 | 8083.77 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.26 | 8120.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3693.03 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.78 | 0.67 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 133450.6022 | 142.674 | 450.8728 | 0 | 0.0017 | 90420.042 | 49500.946
February | 115577.248 | 124.1912 | 403.5797 | 0 | 0.0015 | 80939.6946 | 42967.4771
March | 108442.4901 | 120.272 | 457.0629 | 0 | 0.0016 | 91689.1633 | 40891.6816
April | 78380.1693 | 90.7793 | 410.8813 | 0 | 0.0014 | 82444.634 | 30148.0356
May | 67960.6541 | 82.6303 | 438.2461 | 0 | 0.0015 | 87951.6326 | 26743.3382
June | 67190.7918 | 82.9634 | 459.8332 | 0 | 0.0016 | 92288.1992 | 26635.6897
July | 43980.4403 | 54.3027 | 300.9508 | 0 | 0.001 | 60400.6172 | 17434.393
August | 46796.056 | 57.0479 | 304.9176 | 0 | 0.001 | 61194.4462 | 18437.9982
September | 65925.2651 | 79.2128 | 405.3984 | 0 | 0.0014 | 81356.2662 | 25797.3185
October | 87654.9699 | 100.3987 | 436.0169 | 0 | 0.0015 | 87483.5553 | 33542.7412
November | 114204.912 | 124.6272 | 438.7603 | 0 | 0.0016 | 88007.1313 | 42751.3122
December | 125134.9159 | 134.7482 | 442.9581 | 0 | 0.0016 | 88838.9711 | 46564.8403
Annual Sum or Average | 1054700 | 1193.8477 | 4949.478 | 0 | 0.0175 | 993014.3531 | 401415.7716
Minimum of Months | 43980.4403 | 54.3027 | 300.9508 | 0 | 0.001 | 60400.6172 | 17434.393
Maximum of Months | 133450.6022 | 142.674 | 459.8332 | 0 | 0.0017 | 92288.1992 | 49500.946
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 318605000000 | 222555.991 | 04-JAN-11:09 | 120876.129 | 79091.122 | 7839.684 | 0 | 0 | 7870 | 3474.491 | 0 | 0 | 0 | 0 | 0 | 3404.564 | 0 | 0
February | 285200000000 | 217103.215 | 02-FEB-09:39 | 120876.129 | 75091.738 | 7839.684 | 0 | 0 | 7870 | 3474.641 | 0 | 0 | 0 | 0 | 0 | 1951.023 | 0 | 0
March | 323077000000 | 216985.766 | 14-MAR-07:10 | 120876.129 | 75091.738 | 7839.684 | 0 | 0 | 7870 | 3405.056 | 0 | 0 | 0 | 0 | 0 | 1903.159 | 0 | 0
April | 290503000000 | 212878.482 | 24-APR-11:00 | 120876.129 | 79091.122 | 10729.641 | 0 | 0 | 0 | 44.277 | 0 | 0 | 0 | 0 | 0 | 2137.312 | 0 | 0
May | 309907000000 | 253744.945 | 24-MAY-14:00 | 120876.129 | 73092.045 | 20510.415 | 0 | 36874.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2392.005 | 0 | 0
June | 325187000000 | 300388.847 | 21-JUN-14:50 | 120876.129 | 73092.045 | 24681.065 | 0 | 79173.7 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2565.897 | 0 | 0
July | 212828000000 | 167657.193 | 11-JUL-13:30 | 67153.405 | 41836.601 | 9845.002 | 0 | 46411.425 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2410.756 | 0 | 0
August | 215625000000 | 171940.862 | 15-AUG-13:00 | 67153.405 | 41836.601 | 10535.178 | 0 | 49991.46 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2424.213 | 0 | 0
September | 286668000000 | 225362.886 | 07-SEP-14:00 | 120876.129 | 73092.045 | 13296.928 | 0 | 15818.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2278.862 | 0 | 0
October | 308258000000 | 214933.657 | 31-OCT-07:10 | 120876.129 | 75091.738 | 7839.684 | 0 | 0 | 7870 | 1339.883 | 0 | 0 | 0 | 0 | 0 | 1916.224 | 0 | 0
November | 310103000000 | 218466.236 | 30-NOV-10:20 | 120876.129 | 79091.122 | 7839.684 | 0 | 0 | 7870 | 826.475 | 0 | 0 | 0 | 0 | 0 | 1962.826 | 0 | 0
December | 313034000000 | 222557.974 | 28-DEC-11:20 | 120876.129 | 79091.122 | 7839.684 | 0 | 0 | 7870 | 3473.782 | 0 | 0 | 0 | 0 | 0 | 3407.256 | 0 | 0
Annual Sum or Average | 3498990000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 212828000000 | 167657.193 |  | 67153.405 | 41836.601 | 7839.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1903.159 | 0 | 0
Maximum of Months | 325187000000 | 300388.847 |  | 120876.129 | 79091.122 | 24681.065 | 0 | 79173.7 | 7870 | 3474.641 | 0 | 0 | 0 | 0 | 0 | 3407.256 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 92293.7 | 29245.62 | 0 | 121539.32
Cost per Total Building Area ($/m2) | 13.43 | 4.26 | 0 | 17.69
Cost per Net Conditioned Building Area ($/m2) | 13.43 | 4.26 | 0 | 17.69

## Picture
DOE Commercial Building Benchmark - Primary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75 | 1444.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75 | 2395.71
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 2607.14
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720