## BuildingSummary
Building Summary Primary School pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Primary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 6871 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.35
| Total | 0.35
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2512
| Net Dimensions - Total Area (m2) | 1619.42
| Wall to Skin Ratio | 0.27
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6871
| Net Dimensions - Total Area (m2) | 6871
| Roof to Skin Ratio | 0.73
Window Dimensions (m2)
| South | 324.79 | Pless, et al. 2007
| East | 114.8
| North | 324.79
| West | 114.8
| Total Area (m2) | 879.18
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab-on-grade
| Dimensions - Total Area (m2) | 6871
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 2932
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 13742
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.3934 | See Benchmark Technical Report
HVAC
| System Type | CAV, PSZ-AC (gym, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | gas boiler, gas furnace (gym, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 971.75

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 21.5278 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 15 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 9.6942 | 4 |  |  |  | 0.5 | 96 |  | 1.0841
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 15 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140.0001 | 49 | 4 | 78.75 | 21.5278 | 15 |  |  | 8 |  | 630 |  | 1.4738
COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72.0001 | 25.2 | 3.33 | 48.6486 | 21.5278 | 20 |  |  | 8 |  | 389.1892 |  | 1.4738
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 |  | 0 | 11.1486 | 4 |  |  |  | 0.5 | 273 |  | 1.0876
LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76.0001 | 26.6 |  | 0 | 12.2682 | 4 |  |  |  | 0.5 | 85.5 |  | 1.4738
MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 8.263 | 4 |  |  |  | 0.25 | 63 |  | 1.0203
BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 10 | 19 | 9.7047 | 4 |  | 213.9574 | 25 |  | 300 | 283.1682 | 1.2352
OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168.0002 | 58.8001 | 20 | 22.05 | 20.3418 | 10.8 |  |  | 10 |  | 220.5 |  | 1.409
GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68.0001 | 37.18 | 3.33 | 107.2072 | 11.4717 | 5 |  |  | 10 |  | 1072.0721 |  | 1.2147
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 17.2091 | 190.521 | 954.3991 | 378.54 | 8 |  | 201.4993 | 1557.4251 | 1.2147
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144.0001 | 50.4 | 1.3935 | 226.0419 | 15.0583 | 25.4028 |  |  | 10 |  | 2260.419 |  | 1.4868
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160.0001 | 56.0001 | 4.35 | 91.7241 | 22.7584 | 15 |  |  | 8 |  | 733.7931 |  | 1.4295
Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512.0023 | 892.5808 |  | 1423.4793
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:6_COOLC DXCOIL | 23.4807 | 23.6653 | 23.7578 | 24.0281 | 20.1546 | 22.7502 | 20.8158 | 20.6367 | 19.4203 | 14.4292 | 17.2067 | 15.4141 | 15.5677 | 10.9773 | 12.9013 | 9.8446
| PSZ-AC_2:5_COOLC DXCOIL | 35.7662 | 36.9354 | 36.9499 | 36.7411 | 29.6459 | 34.6041 | 24.814 | 30.9903 | 27.6875 | 23.8618 | 26.6221 | 24.1542 | 26.6221 | 19.6685 | 26.6221 | 17.7466
| PSZ-AC_2:7_COOLC DXCOIL | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 44.0264 | 56.2748 | 53.2715 | 51.3622 | 56.2748 | 53.9233 | 56.2748 | 46.1168 | 56.2748 | 37.5134
| VAV_OTHER_COOLC DXCOIL | 229.9677 | 237.1923 | 219.0465 | 220.758 | 157.4943 | 184.0506 | 161.8369 | 207.1095 | 144.496 | 122.8677 | 164.6787 | 104.0621 | 142.6562 | 100.1565 | 130.2603 | 121.288
| VAV_POD_1_COOLC DXCOIL | 222.0643 | 233.5585 | 226.1297 | 224.4905 | 162.1571 | 191.7943 | 186.5476 | 217.3256 | 143.0707 | 139.4689 | 161.5463 | 104.7886 | 146.2914 | 89.5327 | 125.7111 | 109.6567
| VAV_POD_2_COOLC DXCOIL | 169.9506 | 178.8618 | 179.374 | 178.7041 | 126.4415 | 150.2517 | 143.3127 | 165.7395 | 107.3478 | 105.9852 | 123.2242 | 82.3899 | 110.653 | 69.1789 | 100.0968 | 86.8459
| VAV_POD_3_COOLC DXCOIL | 176.8782 | 186.71 | 180.8733 | 179.7885 | 130.7837 | 153.3758 | 151.9081 | 174.6223 | 114.7006 | 113.0983 | 129.0282 | 83.9056 | 116.954 | 71.6683 | 99.4609 | 86.8962
Heating (kW)
| PSZ-AC_1:6_HEATC | 36.6086 | 48.7082 | 41.2555 | 53.3492 | 32.6811 | 42.7068 | 47.6881 | 51.0051 | 41.3306 | 34.5673 | 49.681 | 38.7394 | 48.5763 | 39.4733 | 41.2054 | 58.4099
| PSZ-AC_2:5_HEATC | 49.9712 | 64.3072 | 55.4147 | 68.1346 | 45.9576 | 56.803 | 53.9163 | 69.8212 | 56.1 | 56.9032 | 76.8662 | 62.4079 | 83.0697 | 75.6966 | 85.0282 | 105.2941
| PSZ-AC_2:7_HEATC | 87.7376 | 115.8256 | 97.7215 | 124.946 | 91.2508 | 105.6395 | 100.8623 | 139.0873 | 110.5125 | 120.2841 | 162.4826 | 131.9201 | 175.596 | 160.0105 | 179.7358 | 222.5747
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:6_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.31 | 3.3 | 3.46 | 3.31 | 3.35 | 3.39 | 3.32 | 3.36 | 3.32 | 3.47 | 3.32 | 3.63
| PSZ-AC_2:5_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.49 | 3.3 | 3.38 | 3.36 | 3.3 | 3.35 | 3.3 | 3.5 | 3.3 | 3.61
| PSZ-AC_2:7_COOLC DXCOIL | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.24 | 3.1 | 3.13 | 3.15 | 3.1 | 3.12 | 3.1 | 3.21 | 3.1 | 3.56
| VAV_OTHER_COOLC DXCOIL | 3.13 | 3.14 | 3.38 | 3.35 | 3.68 | 3.52 | 3.72 | 3.37 | 3.89 | 3.85 | 3.31 | 3.89 | 3.31 | 3.89 | 3.35 | 3.89
| VAV_POD_1_COOLC DXCOIL | 3.31 | 3.17 | 3.19 | 3.15 | 3.62 | 3.48 | 3.7 | 3.31 | 3.89 | 3.84 | 3.31 | 3.85 | 3.31 | 3.89 | 3.32 | 3.89
| VAV_POD_2_COOLC DXCOIL | 3.31 | 3.31 | 3.38 | 3.33 | 3.58 | 3.55 | 3.89 | 3.31 | 3.89 | 3.8 | 3.31 | 3.8 | 3.33 | 4.17 | 3.33 | 3.89
| VAV_POD_3_COOLC DXCOIL | 3.31 | 3.31 | 3.42 | 3.37 | 3.63 | 3.6 | 3.89 | 3.31 | 3.89 | 3.85 | 3.31 | 3.84 | 3.33 | 3.93 | 3.33 | 3.89
Heating Efficiency (%)
| PSZ-AC_1:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:6 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_2:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_2:7 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
| VAV_OTHER | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| PSZ-AC_1:6_FAN | 0.95 | 0.95 | 0.96 | 0.97 | 0.81 | 0.92 | 1.07 | 0.83 | 0.85 | 0.65 | 0.69 | 0.67 | 0.63 | 0.56 | 0.52 | 0.59
| PSZ-AC_2:5_FAN | 1.44 | 1.49 | 1.49 | 1.48 | 1.19 | 1.39 | 1.34 | 1.25 | 1.27 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07
| PSZ-AC_2:7_FAN | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
| VAV_OTHER_FAN | 9.55 | 10.01 | 10.31 | 10.11 | 8.5 | 9.77 | 9.78 | 8.83 | 8.73 | 7.28 | 6.63 | 6.29 | 5.74 | 6.05 | 5.45 | 7.33
| VAV_POD_1_FAN | 8.94 | 9.41 | 10.13 | 9.6 | 8.44 | 9.85 | 11.27 | 8.75 | 8.64 | 8.23 | 6.51 | 6.2 | 5.89 | 5.41 | 5.11 | 6.62
| VAV_POD_2_FAN | 6.84 | 7.2 | 7.74 | 7.37 | 6.4 | 7.47 | 8.66 | 6.67 | 6.48 | 6.11 | 4.96 | 4.67 | 4.46 | 4.18 | 4.03 | 5.25
| VAV_POD_3_FAN | 7.12 | 7.52 | 8.11 | 7.71 | 6.84 | 7.89 | 9.18 | 7.05 | 6.93 | 6.7 | 5.2 | 4.95 | 4.71 | 4.33 | 4.03 | 5.25
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.090578 | 0.12247 | 0.092168 | 0.097335 | 0.13049 | 0.10077 | 0.14739 | 0.078966 | 0.037102 | 0.075324 | 0.088491 | 0.037116 | 0.061295 | 0.075627 | 0.059568 | 0.094325
| Total Cost ($/m2) | 19.95 | 24.61 | 18.6 | 17.32 | 21.12 | 18.45 | 22.02 | 13.22 | 5.97 | 10.95 | 13.68 | 5.53 | 9.24 | 10.88 | 8.52 | 13.4
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011442 | 0.0080985 | 0.0083511 | 0.0097955 | 0.0084989 | 0.0077894 | 0.0085336 | 0.0097166 | 0.0069335 | 0.0084074 | 0.0083743 | 0.0069503 | 0.0078934 | 0.0081505 | 0.0078787 | 0.0041245
| Total Cost ($/m2) | 0.6 | 1.14 | 0.96 | 2.39 | 0.86 | 1.28 | 1.68 | 3.81 | 1.91 | 2.93 | 3.64 | 2.31 | 4.34 | 3.59 | 5.11 | 4.97
Total Utility Costs
| Cost Intensity ($/m2) | 20.55 | 25.75 | 19.57 | 19.71 | 21.98 | 19.73 | 23.7 | 17.03 | 7.88 | 13.88 | 17.32 | 7.84 | 13.58 | 14.47 | 13.62 | 18.37
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 527863.8889 | 405050 | 397147.2222 | 252319.4444 | 150583.3333 | 273341.6667 | 69147.2222 | 185363.8889 | 127780.5556 | 45280.5556 | 106369.4444 | 65633.3333 | 81455.5556 | 36861.1111 | 31947.2222 | 16075
| Interior Lighting | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556 | 514130.5556
| Exterior Lighting | 34400 | 34386.1111 | 34380.5556 | 34375 | 34350 | 34341.6667 | 34358.3333 | 34338.8889 | 34350 | 34283.3333 | 34344.4444 | 34325 | 34322.2222 | 34313.8889 | 34294.4444 | 34083.3333
| Interior Equipment | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 73394.4444 | 64186.1111 | 78519.4444 | 59613.8889 | 51425 | 74347.2222 | 47719.4444 | 54886.1111 | 67283.3333 | 43888.8889 | 45655.5556 | 48138.8889 | 44052.7778 | 42150 | 40763.8889 | 48419.4444
| Pumps | 13.8889 | 208.3333 | 150 | 450 | 91.6667 | 275 | 266.6667 | 788.8889 | 561.1111 | 569.4444 | 858.3333 | 750 | 1347.2222 | 1022.2222 | 1747.2222 | 4219.4444
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21769.4444 | 20766.6667 | 20763.8889 | 19819.4444 | 19872.2222 | 20091.6667 | 18986.1111 | 19172.2222 | 19180.5556 | 18558.3333 | 18741.6667 | 18636.1111 | 18519.4444 | 18188.8889 | 17811.1111 | 17230.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1513302.7778 | 1380458.3333 | 1386819.4444 | 1222436.1111 | 1112183.3333 | 1258255.5556 | 1026341.6667 | 1150408.3333 | 1105019.4444 | 998441.6667 | 1061830.5556 | 1023341.6667 | 1035555.5556 | 988394.4444 | 982425 | 975888.8889
Gas (MJ)
| Heating | 51640 | 640570 | 472970 | 1325650 | 345720 | 795630 | 989160 | 2327740 | 1530240 | 2020140 | 2603220 | 1899930 | 3384840 | 2626130 | 4036520 | 7842590
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 72940 | 96330 | 84750 | 117670 | 111470 | 100330 | 129600 | 134580 | 131350 | 141490 | 149140 | 147980 | 161970 | 163520 | 181790 | 205450
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 358920 | 971240 | 792060 | 1677660 | 691530 | 1130310 | 1353110 | 2696660 | 1895940 | 2395970 | 2986690 | 2282250 | 3781160 | 3023990 | 4452650 | 8282380
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 5806810 | 5940880 | 5784610 | 6078430 | 4695390 | 5660030 | 5047940 | 6838140 | 5874010 | 5990360 | 6809280 | 5966280 | 7509160 | 6582210 | 7989380 | 11795580
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 276.5696 | 212.2224 | 208.0818 | 132.2006 | 78.8968 | 143.215 | 36.2291 | 97.1198 | 66.9495 | 23.7243 | 55.7313 | 34.388 | 42.6779 | 19.3131 | 16.7385 | 8.4224
| Interior Lighting (elec) | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742 | 269.3742
| Exterior Lighting (elec) | 18.0236 | 18.0163 | 18.0134 | 18.0105 | 17.9974 | 17.993 | 18.0017 | 17.9916 | 17.9974 | 17.9625 | 17.9945 | 17.9843 | 17.9828 | 17.9785 | 17.9683 | 17.8577
| Interior Equipment (elec) | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 38.4544 | 33.6297 | 41.1396 | 31.2342 | 26.9437 | 38.9536 | 25.0022 | 28.7571 | 35.2525 | 22.9952 | 23.9208 | 25.2219 | 23.0811 | 22.0841 | 21.3579 | 25.3689
| Pumps (elec) | 0.007277 | 0.10915 | 0.078591 | 0.23577 | 0.048028 | 0.14408 | 0.13972 | 0.41333 | 0.29399 | 0.29836 | 0.44972 | 0.39296 | 0.70587 | 0.53558 | 0.91544 | 2.2107
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 11.4059 | 10.8805 | 10.8791 | 10.3842 | 10.4119 | 10.5269 | 9.9476 | 10.0451 | 10.0495 | 9.7235 | 9.8195 | 9.7642 | 9.7031 | 9.5299 | 9.332 | 9.0278
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 792.8817 | 723.279 | 726.6118 | 640.4846 | 582.7187 | 659.2519 | 537.7427 | 602.7463 | 578.9652 | 523.1247 | 556.3368 | 536.1709 | 542.5702 | 517.8606 | 514.7329 | 511.3084
Gas (MJ/m2)
| Heating (gas) | 7.5156 | 93.2281 | 68.8357 | 192.9341 | 50.3158 | 115.7954 | 143.9616 | 338.7775 | 222.7099 | 294.0096 | 378.8706 | 276.5143 | 492.627 | 382.2049 | 587.472 | 1141.4045
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 10.6156 | 14.0198 | 12.3344 | 17.1256 | 16.2233 | 14.602 | 18.8619 | 19.5867 | 19.1166 | 20.5923 | 21.7057 | 21.5369 | 23.573 | 23.7986 | 26.4576 | 29.901
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 52.2369 | 141.3535 | 115.2758 | 244.1653 | 100.6447 | 164.5044 | 196.9306 | 392.4698 | 275.9336 | 348.7076 | 434.6805 | 332.1569 | 550.3071 | 440.1092 | 648.0352 | 1205.4111
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 845.1186 | 864.6311 | 841.8876 | 884.65 | 683.3634 | 823.7564 | 734.6733 | 995.2176 | 854.8989 | 871.8323 | 991.0173 | 868.3278 | 1092.8773 | 957.9697 | 1162.7682 | 1716.7195
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 407.2265 | 366.6219 | 312.8554 | 281.8482 | 325.9474 | 261.2252 | 232.2832 | 237.4225 | 240.6233 | 213.1072 | 213.3894 | 233.2022 | 213.8706 | 216.0273 | 213.4441 | 223.873
| Feb | 424.721 | 371.77 | 341.7259 | 273.3226 | 318.907 | 283.6225 | 280.1874 | 229.6958 | 272.8307 | 231.2833 | 212.4238 | 227.0005 | 212.5507 | 228.9332 | 213.264 | 218.5155
| Mar | 430.3643 | 360.4936 | 405.6289 | 325.3796 | 315.7726 | 310.3172 | 259.9732 | 300.9346 | 280.3895 | 254.0457 | 253.9141 | 269.1979 | 228.39 | 245.5705 | 211.6279 | 218.0529
| Apr | 459.619 | 410.3504 | 417.9926 | 370.6435 | 331.5954 | 407.8488 | 284.1483 | 307.4061 | 329.5554 | 244.8329 | 264.1592 | 289.2031 | 250.2114 | 233.7102 | 230.0908 | 212.3147
| May | 494.5175 | 509.1274 | 478.2427 | 433.1481 | 351.6334 | 439.1047 | 305.6692 | 380.5033 | 358.5055 | 310.0946 | 340.5357 | 310.2269 | 353.9303 | 274.6517 | 269.4892 | 242.8017
| Jun | 512.7423 | 511.7185 | 584.7506 | 476.3816 | 350.9348 | 521.7794 | 312.1731 | 493.6717 | 400.4128 | 321.3744 | 433.4382 | 345.46 | 407.0301 | 331.8384 | 356.1279 | 281.7672
| Jul | 354.6467 | 385.2206 | 432.5678 | 377.9251 | 231.1743 | 384.8761 | 217.9048 | 367.6611 | 292.7765 | 226.8155 | 306.8165 | 251.1288 | 285.5191 | 232.8483 | 245.7622 | 164.5251
| Aug | 379.3599 | 380.2426 | 436.2842 | 348.6414 | 259.3547 | 371.6758 | 208.4055 | 374.0301 | 295.2549 | 215.0626 | 315.0846 | 255.8307 | 284.6451 | 201.6489 | 225.3782 | 165.0256
| Sep | 498.3979 | 513.0646 | 533.6303 | 466.4292 | 396.4354 | 458.1253 | 386.4456 | 435.9208 | 362.6515 | 339.5514 | 376.0685 | 328.6086 | 355.069 | 298.9921 | 321.8068 | 219.3453
| Oct | 486.7835 | 446.2503 | 424.3245 | 380.5852 | 365.8081 | 404.8383 | 309.4112 | 364.3234 | 324.8591 | 268.2094 | 306.9657 | 309.8265 | 266.6349 | 261.5518 | 237.7265 | 215.9224
| Nov | 441.0323 | 385.8641 | 377.8994 | 299.2398 | 339.1689 | 295.2137 | 253.0365 | 325.5157 | 263.1192 | 229.3497 | 299.0505 | 252.9238 | 243.3386 | 217.7979 | 212.4295 | 219.5834
| Dec | 396.7375 | 370.2726 | 304.4246 | 269.8342 | 334.5085 | 282.7236 | 237.3608 | 214.1917 | 232.9554 | 213.1625 | 212.426 | 222.006 | 212.2945 | 215.5973 | 212.1375 | 223.8503
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:00 | 26-JAN-15:39 | 23-JAN-14:00 | 26-JAN-12:00 | 18-JAN-14:09 | 27-JAN-14:00 | 09-JAN-11:50 | 25-JAN-14:00 | 10-JAN-16:49 | 27-JAN-16:00 | 27-JAN-12:00 | 04-JAN-16:00 | 05-JAN-08:09 | 09-JAN-11:09 | 02-JAN-11:09
| Feb | 23-FEB-12:00 | 23-FEB-14:00 | 28-FEB-15:39 | 27-FEB-14:00 | 13-FEB-11:00 | 27-FEB-14:30 | 15-FEB-15:00 | 15-FEB-14:50 | 14-FEB-15:00 | 21-FEB-12:00 | 28-FEB-11:20 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-08:30
| Mar | 27-MAR-14:00 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-13:00 | 31-MAR-13:00 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-13:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 07-MAR-11:09 | 14-MAR-07:10
| Apr | 03-APR-13:00 | 17-APR-14:00 | 26-APR-14:00 | 21-APR-13:00 | 11-APR-13:00 | 21-APR-14:00 | 14-APR-13:00 | 04-APR-14:00 | 21-APR-14:00 | 18-APR-13:00 | 07-APR-13:00 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 10-APR-10:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-11:30 | 31-MAY-14:00 | 17-MAY-13:00 | 15-MAY-12:00 | 31-MAY-14:00 | 04-MAY-13:00 | 30-MAY-14:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-13:50 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:00 | 29-JUN-13:00 | 28-JUN-13:50 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 21-JUN-14:00
| Jul | 13-JUL-14:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-15:09 | 24-JUL-13:50 | 24-JUL-15:30 | 03-JUL-12:00 | 25-JUL-13:30 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-12:00 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-13:00 | 31-AUG-13:00 | 01-AUG-15:50 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-14:00 | 15-AUG-11:00 | 09-AUG-14:39 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:50 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-13:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-14:30 | 11-SEP-13:00 | 25-SEP-14:00 | 08-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 05-SEP-13:00 | 13-SEP-14:00 | 06-SEP-11:00 | 05-SEP-13:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 07-SEP-14:00
| Oct | 06-OCT-14:00 | 13-OCT-14:00 | 13-OCT-14:00 | 12-OCT-15:00 | 05-OCT-13:00 | 03-OCT-14:00 | 31-OCT-13:20 | 12-OCT-14:50 | 13-OCT-14:00 | 17-OCT-13:39 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 27-OCT-07:30
| Nov | 01-NOV-11:00 | 03-NOV-14:30 | 13-NOV-14:00 | 22-NOV-14:00 | 20-NOV-12:00 | 10-NOV-12:00 | 08-NOV-12:00 | 03-NOV-13:00 | 08-NOV-14:00 | 03-NOV-11:00 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:50 | 09-NOV-11:50 | 30-NOV-10:09
| Dec | 14-DEC-12:00 | 19-DEC-14:00 | 13-DEC-12:00 | 01-DEC-14:30 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 06-DEC-11:20 | 05-DEC-14:50 | 14-DEC-16:19 | 13-DEC-16:19 | 21-DEC-14:30 | 29-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 29-DEC-11:09
Source Energy
| Total Source Energy (GJ) | 18462.58 | 19110.35 | 16656.37 | 16636.19 | 13147.1 | 17437.12 | 12913.1 | 17754.67 | 15269.61 | 8877.83 | 16816.37 | 14715.83 | 16942.16 | 15670.56 | 17018.04 | 21593.51
| Total Source Energy (MJ/m2) | 2687.03 | 2781.31 | 2424.16 | 2421.22 | 1913.42 | 2537.78 | 1879.36 | 2584 | 2222.33 | 1292.07 | 2447.44 | 2141.73 | 2465.75 | 2280.68 | 2476.79 | 3142.7
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
| Total Building | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
Emissions
| Carbon Equivalent (kg) | 421494.8459 | 477980.734 | 432929.9172 | 406807.903 | 142446.3837 | 444761.0933 | 144344.5541 | 359072.439 | 485587.387 | 115926.5244 | 619972.3969 | 459188.2732 | 422647.9884 | 415726.9422 | 416570.7315 | 423956.4983
| CO2 (kg) | 979706.7585 | 1206040 | 1025800 | 942035.6111 | 383043.3137 | 1064030 | 390728.0994 | 836678.0035 | 1150580 | 297576.6388 | 1461790 | 1092960 | 1014180 | 997645.2328 | 1007230 | 1119400
| NOX (kg) | 1711.8141 | 1564.6636 | 1701.4821 | 1729.6421 | 329.6757 | 1701.8303 | 338.0478 | 1519.5016 | 1935.1055 | 390.8884 | 2519.6862 | 1816.9722 | 1670.049 | 1634.284 | 1625.3031 | 1253.5444
| SO2 (kg) | 6477.6319 | 6585.0425 | 5576.893 | 4291.2005 | 3236.505 | 6921.7219 | 2986.8961 | 4200.1774 | 4825.9095 | 772.3579 | 7156.6891 | 4469.3403 | 2445.0905 | 2639.9409 | 2319.8748 | 4969.8828
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0296 | 0.0186 | 0.0152 | 0.0158 | 0.0015 | 0.0131 | 0.0015 | 0.0172 | 0.019 | 0.0033 | 0.0219 | 0.0176 | 0.0182 | 0.0186 | 0.0174 | 0.0177
| Water for Electricity (m3) | 801.6836 | 2246.17 | 41194.7 | 7632.4 | 19527.4 | 34519 | 18020.3 | 261.1862 | 5017.67 | 10200.9 | 1647.37 | 4646.79 | 1606.6 | 62609 | 1524.17 | 997.0458

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5806.81 | 845.12 | 845.12
Net Site Energy | 5806.81 | 845.12 | 845.12
Total Source Energy | 18462.58 | 2687.03 | 2687.03
Net Source Energy | 18462.58 | 2687.03 | 2687.03
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 51.64 | 0 | 0 | 0 | 0
Cooling | 1900.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 264.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 72.94 | 0 | 0 | 0 | 971.75
Refrigeration | 78.37 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5447.89 | 358.92 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 488554.56 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23480.72 | 15874.92 | 7605.8 | 0.68 | 3.3
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 35766.15 | 24180.89 | 11585.26 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 229967.66 | 157227.5 | 72740.15 | 0.68 | 3.13
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 222064.26 | 150133.92 | 71930.34 | 0.68 | 3.31
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 169950.64 | 114900.78 | 55049.86 | 0.68 | 3.31
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 176878.23 | 119584.41 | 57293.83 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12812.11 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11148.84 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12604.16 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12432.92 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12447.54 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12955.27 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12965.67 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13116.14 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11271.4 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11208.7 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11295.24 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25174.25 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8707.88 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25712.17 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8037.17 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30569.66 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29859.44 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29990.02 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29896.82 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29945.14 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20553.18 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25571.98 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 36608.57 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 49971.2 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 87737.56 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 19578.47 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 25418.41 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 20362.04 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 20339.75 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.95 | 1077.19 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.44 | 1640.78 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.55 | 16426.64 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.94 | 16776.09 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.84 | 12839.11 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.12 | 13362.46 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2690.19 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 75551.2802 | 130.9885 | 491.5016 | 0 | 0.0022 | 60828.3594 | 32401.8741
February | 69704.2843 | 121.4815 | 458.425 | 0 | 0.0021 | 56735.2795 | 29957.4186
March | 81331.4826 | 141.6793 | 534.372 | 0 | 0.0024 | 66134.5277 | 34947.8988
April | 80093.3049 | 140.0358 | 530.2776 | 0 | 0.0024 | 65628.1939 | 34467.3003
May | 94099.7434 | 164.7394 | 624.7003 | 0 | 0.0028 | 77314.2952 | 40516.3319
June | 97979.1755 | 171.6307 | 651.239 | 0 | 0.003 | 80598.8536 | 42196.6752
July | 72330.4509 | 126.6989 | 480.7371 | 0 | 0.0022 | 59497.1378 | 31150.259
August | 75646.1162 | 132.4792 | 502.5572 | 0 | 0.0023 | 62197.6336 | 32575.4398
September | 90531.2278 | 158.5565 | 601.517 | 0 | 0.0027 | 74445.1268 | 38986.2982
October | 88992.9616 | 155.7287 | 590.2445 | 0 | 0.0027 | 73049.9163 | 38310.4704
November | 80740.8913 | 141.1179 | 534.1707 | 0 | 0.0024 | 66109.9725 | 34740.961
December | 72705.8399 | 126.6777 | 477.8901 | 0 | 0.0022 | 59144.2768 | 31243.9187
Annual Sum or Average | 979706.7585 | 1711.8141 | 6477.6319 | 0 | 0.0296 | 801683.573 | 421494.8459
Minimum of Months | 69704.2843 | 121.4815 | 458.425 | 0 | 0.0021 | 56735.2795 | 29957.4186
Maximum of Months | 97979.1755 | 171.6307 | 651.239 | 0 | 0.003 | 80598.8536 | 42196.6752
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 413363000000 | 407226.454 | 06-JAN-12:00 | 120876.129 | 79091.122 | 25140.342 | 0 | 179505.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2613.297 | 0 | 0
February | 385548000000 | 424720.979 | 23-FEB-12:00 | 120876.129 | 79091.122 | 29606.395 | 0 | 192534.507 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2612.824 | 0 | 0
March | 449421000000 | 430364.34 | 27-MAR-14:00 | 120876.129 | 73092.045 | 36466.112 | 0 | 197308.887 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2621.159 | 0 | 0
April | 445980000000 | 459619.001 | 03-APR-13:00 | 120876.129 | 75091.738 | 37370.627 | 0 | 223632.8 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 2647.684 | 0 | 0
May | 525394000000 | 494517.468 | 24-MAY-14:00 | 120876.129 | 73092.045 | 41019.838 | 0 | 256819.27 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 2710.166 | 0 | 0
June | 547714000000 | 512742.299 | 27-JUN-14:00 | 120876.129 | 73092.045 | 49791.956 | 0 | 266286.518 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2695.643 | 0 | 0
July | 404316000000 | 354646.702 | 13-JUL-14:00 | 67153.405 | 40636.785 | 21873.507 | 0 | 222425.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2557.505 | 0 | 0
August | 422667000000 | 379359.917 | 21-AUG-13:00 | 67153.405 | 41836.601 | 23527.354 | 0 | 244259.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2582.856 | 0 | 0
September | 505896000000 | 498397.899 | 07-SEP-13:00 | 120876.129 | 75091.738 | 41985.555 | 0 | 257758.457 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2686.017 | 0 | 0
October | 496415000000 | 486783.464 | 06-OCT-14:00 | 120876.129 | 73092.045 | 43615.524 | 0 | 246537.466 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2662.296 | 0 | 0
November | 449254000000 | 441032.335 | 01-NOV-11:00 | 120876.129 | 79091.122 | 29654.939 | 0 | 208778.247 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2631.892 | 0 | 0
December | 401918000000 | 396737.455 | 14-DEC-12:00 | 120876.129 | 79091.122 | 28553.748 | 0 | 165613.244 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2603.199 | 0 | 0
Annual Sum or Average | 5447890000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 385548000000 | 354646.702 |  | 67153.405 | 40636.785 | 21873.507 | 0 | 165613.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2557.505 | 0 | 0
Maximum of Months | 547714000000 | 512742.299 |  | 120876.129 | 79091.122 | 49791.956 | 0 | 266286.518 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 2710.166 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 137071.71 | 4106.64 | 0 | 141178.35
Cost per Total Building Area ($/m2) | 19.95 | 0.6 | 0 | 20.55
Cost per Net Conditioned Building Area ($/m2) | 19.95 | 0.6 | 0 | 20.55

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5940.88 | 864.63 | 864.63
Net Site Energy | 5940.88 | 864.63 | 864.63
Total Source Energy | 19110.35 | 2781.31 | 2781.31
Net Source Energy | 19110.35 | 2781.31 | 2781.31
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 640.57 | 0 | 0 | 0 | 0
Cooling | 1458.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 231.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0.75 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 96.33 | 0 | 0 | 0 | 971.75
Refrigeration | 74.76 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4969.65 | 971.24 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 620184.9 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23665.25 | 15999.68 | 7665.57 | 0.68 | 3.3
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36935.42 | 24971.42 | 11964 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 237192.31 | 163121.63 | 74070.68 | 0.69 | 3.14
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 233558.52 | 157905 | 75653.52 | 0.68 | 3.17
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 178861.81 | 120925.47 | 57936.34 | 0.68 | 3.31
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 186710.01 | 126231.5 | 60478.5 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13267.15 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11209.57 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13191.11 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13017.38 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13032.25 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13176.7 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13187.35 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13341.32 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11570.43 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11506.65 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11596.73 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26080.35 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9869.55 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26345.12 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8195.69 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33918.64 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33211.22 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33350.5 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30113.5 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30153.73 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20602.04 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27353.48 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 48708.15 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 64307.2 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 115825.61 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 43302.75 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 50871.73 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 42332.19 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 40651.05 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.95 | 1085.65 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.49 | 1694.43 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.01 | 17212.56 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.41 | 17644.44 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.2 | 13512.31 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.52 | 14105.22 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3415 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 93935.7911 | 118.8273 | 470.3101 | 0 | 0.0013 | 160409.6718 | 36836.8252
February | 83424.7078 | 105.5221 | 417.5595 | 0 | 0.0012 | 142417.8442 | 32713.7675
March | 94484.2173 | 122.3003 | 511.9807 | 0 | 0.0014 | 174635.9842 | 37410.1305
April | 94037.0388 | 122.7335 | 523.731 | 0 | 0.0015 | 178648.6073 | 37363.5188
May | 115774.2265 | 151.4928 | 650.2393 | 0 | 0.0018 | 221803.2543 | 46050.4172
June | 129337.4215 | 169.4141 | 728.8474 | 0 | 0.0021 | 248618.0505 | 51467.6964
July | 97597.8207 | 127.8626 | 550.3085 | 0 | 0.0015 | 187716.5229 | 38840.4028
August | 99462.9206 | 130.2649 | 560.2489 | 0 | 0.0016 | 191107.1221 | 39577.3435
September | 112093.3109 | 146.764 | 630.7943 | 0 | 0.0018 | 215170.7642 | 44597.6024
October | 105498.707 | 137.7784 | 588.7636 | 0 | 0.0017 | 200832.0929 | 41928.5811
November | 91865.1746 | 119.2319 | 502.2932 | 0 | 0.0014 | 171333.0718 | 36414.6007
December | 88533.0121 | 112.4717 | 449.9658 | 0 | 0.0013 | 153473.1454 | 34779.8479
Annual Sum or Average | 1206040 | 1564.6636 | 6585.0425 | 0 | 0.0186 | 2246170 | 477980.734
Minimum of Months | 83424.7078 | 105.5221 | 417.5595 | 0 | 0.0012 | 142417.8442 | 32713.7675
Maximum of Months | 129337.4215 | 169.4141 | 728.8474 | 0 | 0.0021 | 248618.0505 | 51467.6964
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 354907000000 | 366621.86 | 03-JAN-12:00 | 120876.129 | 79091.122 | 17817.334 | 0 | 146232.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2605.13 | 0 | 0
February | 315100000000 | 371769.977 | 23-FEB-14:00 | 120876.129 | 75091.738 | 29358.734 | 0 | 143807.543 | 0 | 0.017 | 0 | 0 | 0 | 0 | 0 | 2635.817 | 0 | 0
March | 386382000000 | 360493.621 | 29-MAR-11:00 | 120876.129 | 79091.122 | 17464.292 | 0 | 140449.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2612.084 | 0 | 0
April | 395260000000 | 410350.397 | 17-APR-14:00 | 120876.129 | 73092.045 | 31716.018 | 0 | 182028.105 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2638.089 | 0 | 0
May | 490740000000 | 509127.436 | 26-MAY-14:00 | 120876.129 | 73092.045 | 43248.622 | 0 | 269191.668 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2718.964 | 0 | 0
June | 550068000000 | 511718.459 | 13-JUN-14:00 | 120876.129 | 73092.045 | 43349.19 | 0 | 271666.278 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2734.806 | 0 | 0
July | 415323000000 | 385220.55 | 18-JUL-11:00 | 67153.405 | 44636.17 | 18380.205 | 0 | 252467.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2583.459 | 0 | 0
August | 422825000000 | 380242.562 | 31-AUG-13:00 | 67153.405 | 41836.601 | 25979.81 | 0 | 242667.41 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 2605.318 | 0 | 0
September | 476066000000 | 513064.554 | 15-SEP-14:00 | 120876.129 | 73092.045 | 42004.992 | 0 | 274385.971 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2705.416 | 0 | 0
October | 444341000000 | 446250.302 | 13-OCT-14:00 | 120876.129 | 73092.045 | 38364.873 | 0 | 211261.344 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 2655.899 | 0 | 0
November | 379075000000 | 385864.133 | 03-NOV-14:30 | 120876.129 | 73092.045 | 24863.161 | 0 | 164421.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2611.442 | 0 | 0
December | 339560000000 | 370272.598 | 19-DEC-14:00 | 120876.129 | 75091.738 | 22767.055 | 0 | 148926.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2610.846 | 0 | 0
Annual Sum or Average | 4969650000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 315100000000 | 360493.621 |  | 67153.405 | 41836.601 | 17464.292 | 0 | 140449.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2583.459 | 0 | 0
Maximum of Months | 550068000000 | 513064.554 |  | 120876.129 | 79091.122 | 43349.19 | 0 | 274385.971 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 2734.806 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 169070.8 | 7865.6 | 0 | 176936.4
Cost per Total Building Area ($/m2) | 24.61 | 1.14 | 0 | 25.75
Cost per Net Conditioned Building Area ($/m2) | 24.61 | 1.14 | 0 | 25.75

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5784.61 | 841.89 | 841.89
Net Site Energy | 5784.61 | 841.89 | 841.89
Total Source Energy | 16656.37 | 2424.16 | 2424.16
Net Source Energy | 16656.37 | 2424.16 | 2424.16
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 472.97 | 0 | 0 | 0 | 0
Cooling | 1429.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 282.67 | 0 | 0 | 0 | 0 | 0
Pumps | 0.54 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 84.75 | 0 | 0 | 0 | 971.75
Refrigeration | 74.75 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4992.55 | 792.06 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 565324.37 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23757.76 | 16062.22 | 7695.54 | 0.68 | 3.3
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36949.88 | 24981.19 | 11968.68 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 219046.45 | 157184.46 | 61861.99 | 0.72 | 3.38
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 226129.74 | 159125.44 | 67004.31 | 0.7 | 3.19
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 179374 | 124424.31 | 54949.69 | 0.69 | 3.38
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 180873.31 | 127316.03 | 53557.28 | 0.7 | 3.42
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12915.74 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11373.32 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13804.14 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13632.09 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13647.11 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13447.73 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13458.44 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13615.67 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11100.41 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11036.66 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11133.17 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26339.64 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10914.7 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24463.41 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7169.24 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 36865.43 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 36130.46 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 36292.51 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30603.87 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30643.23 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20930.31 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28431.61 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 41255.47 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 55414.71 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 97721.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 30018.65 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 36635.58 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 31585.23 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 29261.87 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.96 | 1089.9 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.49 | 1695.09 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.31 | 17745.03 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.13 | 17430.72 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.74 | 14522.77 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.11 | 15214.95 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3112.92 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 72621.3018 | 116.7472 | 367.984 | 0 | 0.001 | 2717990 | 30274.1834
February | 66235.3053 | 106.9044 | 338.6883 | 0 | 0.0009 | 2501630 | 27654.8241
March | 81873.8763 | 135.3618 | 441.9236 | 0 | 0.0012 | 3264320 | 34509.5695
April | 81175.9939 | 135.3747 | 446.5967 | 0 | 0.0012 | 3298900 | 34333.394
May | 95380.7556 | 159.9028 | 530.8161 | 0 | 0.0014 | 3921050 | 40426.1592
June | 114960.5527 | 193.2466 | 643.5363 | 0 | 0.0017 | 4753720 | 48777.3325
July | 88372.7999 | 148.592 | 494.983 | 0 | 0.0013 | 3656380 | 37500.1903
August | 88638.7349 | 148.9823 | 496.0606 | 0 | 0.0013 | 3664330 | 37607.279
September | 101097.6039 | 169.8398 | 565.185 | 0 | 0.0015 | 4174940 | 42884.8783
October | 87181.3317 | 145.6552 | 481.5567 | 0 | 0.0013 | 3557150 | 36900.2057
November | 75473.3776 | 124.7346 | 407.0481 | 0 | 0.0011 | 3006710 | 31807.1941
December | 72785.9593 | 116.1406 | 362.5145 | 0 | 0.001 | 2677540 | 30254.7071
Annual Sum or Average | 1025800 | 1701.4821 | 5576.893 | 0 | 0.0152 | 41194700 | 432929.9172
Minimum of Months | 66235.3053 | 106.9044 | 338.6883 | 0 | 0.0009 | 2501630 | 27654.8241
Maximum of Months | 114960.5527 | 193.2466 | 643.5363 | 0 | 0.0017 | 4753720 | 48777.3325
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 329404000000 | 312855.406 | 26-JAN-15:39 | 120876.129 | 73092.045 | 25023.541 | 0 | 91343.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2520.49 | 0 | 0
February | 303183000000 | 341725.948 | 28-FEB-15:39 | 120876.129 | 73092.045 | 29792.574 | 0 | 115382.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2582.644 | 0 | 0
March | 395617000000 | 405628.883 | 17-MAR-14:00 | 120876.129 | 73092.045 | 38676.282 | 0 | 170310.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2674.112 | 0 | 0
April | 399807000000 | 417992.646 | 26-APR-14:00 | 120876.129 | 73092.045 | 40705.034 | 0 | 180632.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2687.313 | 0 | 0
May | 475208000000 | 478242.747 | 30-MAY-14:00 | 120876.129 | 73092.045 | 47547.645 | 0 | 234001.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2725.132 | 0 | 0
June | 576123000000 | 584750.631 | 28-JUN-15:00 | 120876.129 | 73092.045 | 56732.106 | 0 | 331422.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2627.592 | 0 | 0
July | 443132000000 | 432567.805 | 11-JUL-15:00 | 67153.405 | 40636.785 | 32074.036 | 0 | 290191.864 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 2511.692 | 0 | 0
August | 444096000000 | 436284.213 | 01-AUG-15:50 | 67153.405 | 40636.785 | 36928.908 | 0 | 289074.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2490.709 | 0 | 0
September | 505979000000 | 533630.308 | 08-SEP-14:30 | 120876.129 | 73092.045 | 50885.508 | 0 | 286045.66 | 0 | 0.023 | 0 | 0 | 0 | 0 | 0 | 2730.944 | 0 | 0
October | 431106000000 | 424324.546 | 13-OCT-14:00 | 120876.129 | 73092.045 | 41456.453 | 0 | 186201.71 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 2698.189 | 0 | 0
November | 364395000000 | 377899.388 | 13-NOV-14:00 | 120876.129 | 75091.738 | 32736.586 | 0 | 146531.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2663.699 | 0 | 0
December | 324503000000 | 304424.628 | 13-DEC-12:00 | 120876.129 | 79091.122 | 19649.08 | 0 | 82300.442 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2507.854 | 0 | 0
Annual Sum or Average | 4992550000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 303183000000 | 304424.628 |  | 67153.405 | 40636.785 | 19649.08 | 0 | 82300.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2490.709 | 0 | 0
Maximum of Months | 576123000000 | 584750.631 |  | 120876.129 | 79091.122 | 56732.106 | 0 | 331422.759 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 2730.944 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 127820.9 | 6614.6 | 0 | 134435.5
Cost per Total Building Area ($/m2) | 18.6 | 0.96 | 0 | 19.57
Cost per Net Conditioned Building Area ($/m2) | 18.6 | 0.96 | 0 | 19.57

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6078.43 | 884.65 | 884.65
Net Site Energy | 6078.43 | 884.65 | 884.65
Total Source Energy | 16636.19 | 2421.22 | 2421.22
Net Source Energy | 16636.19 | 2421.22 | 2421.22
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1325.65 | 0 | 0 | 0 | 0
Cooling | 908.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 214.61 | 0 | 0 | 0 | 0 | 0
Pumps | 1.62 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 117.67 | 0 | 0 | 0 | 971.75
Refrigeration | 71.35 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4400.77 | 1677.66 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 659823.99 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24028.1 | 16245 | 7783.1 | 0.68 | 3.3
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36741.13 | 24840.06 | 11901.07 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 220758.01 | 156676.7 | 64081.32 | 0.71 | 3.35
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 224490.5 | 155192.79 | 69297.7 | 0.69 | 3.15
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 178704.11 | 121895.83 | 56808.28 | 0.68 | 3.33
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 179788.55 | 124409.41 | 55379.14 | 0.69 | 3.37
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12786.57 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10810.17 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12891.55 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12719.38 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12734.13 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12505.49 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12516.42 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12674.71 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11240.61 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11176.56 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11268.07 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25134.29 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10335.89 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25373.79 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7808.92 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 35234.95 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34508.41 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34651.39 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28935.99 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28977.3 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19825.56 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27286.43 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 53349.16 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 68134.61 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 124945.98 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 51399.73 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 59394.92 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 50018.87 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 47473.71 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.97 | 1102.3 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.48 | 1685.51 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.11 | 17392.97 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.6 | 16518.77 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.37 | 13832.38 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.71 | 14463.11 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3633.27 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 84204.3789 | 141.5456 | 319.5531 | 0 | 0.0012 | 568233.7211 | 35156.6758
February | 74972.1558 | 127.2092 | 290.315 | 0 | 0.0011 | 516256.1705 | 31411.3055
March | 76379.4982 | 139.4798 | 344.2102 | 0 | 0.0013 | 612210.603 | 32913.6367
April | 73089.9677 | 137.1827 | 347.5727 | 0 | 0.0013 | 618228.0999 | 31838.7399
May | 83917.6743 | 159.7718 | 410.1736 | 0 | 0.0015 | 729597.7404 | 36764.7203
June | 93663.1042 | 179.2194 | 462.1861 | 0 | 0.0017 | 822123.3625 | 41116.7307
July | 69209.7397 | 132.4715 | 341.727 | 0 | 0.0012 | 607854.4731 | 30385.9696
August | 72084.7379 | 137.897 | 355.5428 | 0 | 0.0013 | 632429.0434 | 31641.0625
September | 85819.9819 | 164.1339 | 423.101 | 0 | 0.0015 | 752599.162 | 37666.5037
October | 75719.6868 | 142.3491 | 361.2091 | 0 | 0.0013 | 642485.2176 | 33005.5787
November | 73574.5401 | 132.2883 | 321.4262 | 0 | 0.0012 | 571666.443 | 31513.823
December | 79400.1456 | 136.0937 | 314.1837 | 0 | 0.0012 | 558716.9287 | 33393.1568
Annual Sum or Average | 942035.6111 | 1729.6421 | 4291.2005 | 0 | 0.0158 | 7632400 | 406807.903
Minimum of Months | 69209.7397 | 127.2092 | 290.315 | 0 | 0.0011 | 516256.1705 | 30385.9696
Maximum of Months | 93663.1042 | 179.2194 | 462.1861 | 0 | 0.0017 | 822123.3625 | 41116.7307
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 327638000000 | 281848.166 | 23-JAN-14:00 | 120876.129 | 75091.738 | 21109.366 | 0 | 62343.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2427.41 | 0 | 0
February | 297668000000 | 273322.636 | 27-FEB-14:00 | 120876.129 | 75091.738 | 20140.397 | 0 | 54821.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2393.184 | 0 | 0
March | 352995000000 | 325379.623 | 28-MAR-14:00 | 120876.129 | 73092.045 | 28383.201 | 0 | 100462.082 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2566.155 | 0 | 0
April | 356464000000 | 370643.488 | 21-APR-13:00 | 120876.129 | 75091.738 | 27422.999 | 0 | 144661.386 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2591.228 | 0 | 0
May | 420679000000 | 433148.141 | 15-MAY-14:00 | 120876.129 | 73092.045 | 36784.894 | 0 | 199739.575 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 2655.479 | 0 | 0
June | 474029000000 | 476381.59 | 19-JUN-14:00 | 120876.129 | 73092.045 | 42485.187 | 0 | 237211.838 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2716.383 | 0 | 0
July | 350483000000 | 377925.1 | 03-JUL-15:09 | 67153.405 | 40636.785 | 28413.993 | 0 | 239117.125 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2603.782 | 0 | 0
August | 364653000000 | 348641.415 | 17-AUG-13:00 | 67153.405 | 41836.601 | 23720.762 | 0 | 213357.793 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2572.851 | 0 | 0
September | 433942000000 | 466429.169 | 11-SEP-13:00 | 120876.129 | 75091.738 | 40079.694 | 0 | 227724.388 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2657.206 | 0 | 0
October | 370451000000 | 380585.219 | 12-OCT-15:00 | 120876.129 | 73092.045 | 26099.779 | 0 | 157920.953 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 2596.298 | 0 | 0
November | 329617000000 | 299239.784 | 22-NOV-14:00 | 120876.129 | 75091.738 | 19065.112 | 0 | 81684.444 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2522.353 | 0 | 0
December | 322151000000 | 269834.217 | 01-DEC-14:30 | 120876.129 | 75091.738 | 17702.55 | 0 | 53734.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2429.061 | 0 | 0
Annual Sum or Average | 4400770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 297668000000 | 269834.217 |  | 67153.405 | 40636.785 | 17702.55 | 0 | 53734.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2393.184 | 0 | 0
Maximum of Months | 474029000000 | 476381.59 |  | 120876.129 | 75091.738 | 42485.187 | 0 | 239117.125 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 2716.383 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 118986.1 | 16433.45 | 0 | 135419.54
Cost per Total Building Area ($/m2) | 17.32 | 2.39 | 0 | 19.71
Cost per Net Conditioned Building Area ($/m2) | 17.32 | 2.39 | 0 | 19.71

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4695.39 | 683.36 | 683.36
Net Site Energy | 4695.39 | 683.36 | 683.36
Total Source Energy | 13147.1 | 1913.42 | 1913.42
Net Source Energy | 13147.1 | 1913.42 | 1913.42
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 345.72 | 0 | 0 | 0 | 0
Cooling | 542.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 185.13 | 0 | 0 | 0 | 0 | 0
Pumps | 0.33 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 111.47 | 0 | 0 | 0 | 971.75
Refrigeration | 71.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4003.86 | 691.53 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 473775.35 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20154.61 | 13626.19 | 6528.42 | 0.68 | 3.31
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29645.86 | 20043.07 | 9602.79 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 157494.35 | 119608.85 | 37885.5 | 0.76 | 3.68
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 162157.08 | 121247.04 | 40910.04 | 0.75 | 3.62
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 126441.54 | 93460.36 | 32981.18 | 0.74 | 3.58
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 130783.74 | 97980.59 | 32803.15 | 0.75 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11247.1 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8616.83 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12117.51 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11962.33 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11975.83 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10712.41 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10722.29 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10865.73 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10033.95 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9973.81 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10063.01 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20226.74 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10477.52 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22097.41 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6547.55 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 35822.97 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 35014.45 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 35148.31 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22530.99 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22570.7 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15549.88 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24713.25 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 32681.12 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 45957.58 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 91250.81 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 24323.02 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 28789.64 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 21842.27 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 23327.09 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.81 | 941.41 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.19 | 1360.01 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.5 | 15945.23 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.44 | 15830.73 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.4 | 12010.54 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.84 | 12827.01 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2608.81 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 33364.359 | 28.8181 | 263.6109 | 0 | 0.0001 | 1590430 | 12351.7272
February | 29747.0831 | 25.6808 | 237.3552 | 0 | 0.0001 | 1432030 | 11019.6767
March | 34436.0996 | 29.6999 | 279.9373 | 0 | 0.0001 | 1688960 | 12772.4696
April | 31341.1974 | 26.9787 | 264.0853 | 0 | 0.0001 | 1593360 | 11652.955
May | 34140.0669 | 29.3517 | 294.1601 | 0 | 0.0001 | 1774840 | 12713.4055
June | 34226.7146 | 29.4051 | 298.6804 | 0 | 0.0001 | 1802120 | 12757.1856
July | 24361.5036 | 20.9174 | 214.7754 | 0 | 0.0001 | 1295880 | 9086.8285
August | 26956.8498 | 23.1429 | 238.1864 | 0 | 0.0001 | 1437140 | 10056.5083
September | 34356.2888 | 29.4893 | 304.6556 | 0 | 0.0001 | 1838190 | 12820.2614
October | 34450.8095 | 29.5967 | 300.7882 | 0 | 0.0001 | 1814840 | 12841.176
November | 33072.2096 | 28.4784 | 276.9382 | 0 | 0.0001 | 1670900 | 12291.2749
December | 32590.1317 | 28.1168 | 263.332 | 0 | 0.0001 | 1588770 | 12082.9148
Annual Sum or Average | 383043.3137 | 329.6757 | 3236.505 | 0 | 0.0015 | 19527400 | 142446.3837
Minimum of Months | 24361.5036 | 20.9174 | 214.7754 | 0 | 0.0001 | 1295880 | 9086.8285
Maximum of Months | 34450.8095 | 29.6999 | 304.6556 | 0 | 0.0001 | 1838190 | 12841.176
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 326098000000 | 325947.441 | 26-JAN-12:00 | 120876.129 | 79091.122 | 25516.037 | 0 | 97892.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2571.495 | 0 | 0
February | 293620000000 | 318906.954 | 13-FEB-11:00 | 120876.129 | 79091.122 | 24826.891 | 0 | 91055.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3056.841 | 0 | 0
March | 346300000000 | 315772.6 | 31-MAR-13:00 | 120876.129 | 75091.738 | 30428.232 | 0 | 86819.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.609 | 0 | 0
April | 326698000000 | 331595.369 | 11-APR-13:00 | 120876.129 | 75091.738 | 25335.28 | 0 | 107757.302 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2534.917 | 0 | 0
May | 363908000000 | 351633.356 | 30-MAY-11:30 | 120876.129 | 79091.122 | 20859.846 | 0 | 128251.285 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 2554.95 | 0 | 0
June | 369503000000 | 350934.814 | 28-JUN-13:50 | 120876.129 | 75091.738 | 26037.434 | 0 | 126371.799 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2557.706 | 0 | 0
July | 265704000000 | 231174.303 | 24-JUL-13:50 | 67153.405 | 41836.601 | 16274.804 | 0 | 103481.045 | 0 | 0.019 | 0 | 0 | 0 | 0 | 0 | 2428.429 | 0 | 0
August | 294667000000 | 259354.721 | 08-AUG-12:00 | 67153.405 | 41836.601 | 19153.269 | 0 | 128718.558 | 0 | 0.017 | 0 | 0 | 0 | 0 | 0 | 2492.872 | 0 | 0
September | 376898000000 | 396435.399 | 25-SEP-14:00 | 120876.129 | 73092.045 | 44609.752 | 0 | 155240.093 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2617.378 | 0 | 0
October | 372110000000 | 365808.122 | 05-OCT-13:00 | 120876.129 | 75091.738 | 39395.926 | 0 | 127863.827 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2580.496 | 0 | 0
November | 342597000000 | 339168.901 | 20-NOV-12:00 | 120876.129 | 79091.122 | 29167.135 | 0 | 107435.267 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2599.233 | 0 | 0
December | 325757000000 | 334508.482 | 19-DEC-12:00 | 120876.129 | 79091.122 | 27476.691 | 0 | 104483.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2580.755 | 0 | 0
Annual Sum or Average | 4003860000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 265704000000 | 231174.303 |  | 67153.405 | 41836.601 | 16274.804 | 0 | 86819.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2428.429 | 0 | 0
Maximum of Months | 376898000000 | 396435.399 |  | 120876.129 | 79091.122 | 44609.752 | 0 | 155240.093 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 3056.841 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 145127.72 | 5877.26 | 0 | 151004.98
Cost per Total Building Area ($/m2) | 21.12 | 0.86 | 0 | 21.98
Cost per Net Conditioned Building Area ($/m2) | 21.12 | 0.86 | 0 | 21.98

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5660.03 | 823.76 | 823.76
Net Site Energy | 5660.03 | 823.76 | 823.76
Total Source Energy | 17437.12 | 2537.78 | 2537.78
Net Source Energy | 17437.12 | 2537.78 | 2537.78
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 795.63 | 0 | 0 | 0 | 0
Cooling | 984.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.63 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 267.65 | 0 | 0 | 0 | 0 | 0
Pumps | 0.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 100.33 | 0 | 0 | 0 | 971.75
Refrigeration | 72.33 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4529.72 | 1130.31 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 577563.62 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22750.16 | 15381 | 7369.16 | 0.68 | 3.3
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34604.07 | 23395.23 | 11208.84 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 184050.59 | 138775.05 | 45275.54 | 0.75 | 3.52
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 191794.26 | 142593.25 | 49201.01 | 0.74 | 3.48
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 150251.7 | 110235 | 40016.7 | 0.73 | 3.55
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 153375.82 | 114150.09 | 39225.73 | 0.74 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11938.92 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10335.59 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13156.49 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12986.69 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13001.89 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12822.69 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12832.58 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12981.17 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10174.15 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10109.04 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10211.98 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23906.29 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10193.52 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22073 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6159.77 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 35013.77 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34238.28 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34406.25 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27518.69 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27560.32 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18925.21 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26169.69 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 42706.76 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 56803 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 105639.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 38963.35 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 45627.84 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 38809.46 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 36455.99 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.92 | 1043.67 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.39 | 1587.47 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.77 | 16804.8 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.85 | 16940.67 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.47 | 14017.99 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.89 | 14809.75 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3180.31 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 85548.409 | 129.3507 | 486.2328 | 0 | 0.0009 | 2424590 | 34981.7056
February | 71756.733 | 112.7339 | 447.6645 | 0 | 0.0009 | 2232450 | 29782.4615
March | 83409.3015 | 131.5891 | 525.5152 | 0 | 0.001 | 2620710 | 34675.8309
April | 82114.7043 | 132.6937 | 546.9377 | 0 | 0.001 | 2727660 | 34464.7125
May | 96539.47 | 156.9399 | 651.8181 | 0 | 0.0012 | 3250750 | 40616.3254
June | 116369.1352 | 189.7857 | 791.4349 | 0 | 0.0015 | 3947070 | 49022.477
July | 88484.3839 | 144.3708 | 602.3731 | 0 | 0.0011 | 3004170 | 37282.014
August | 90577.8145 | 147.7225 | 616.0233 | 0 | 0.0012 | 3072250 | 38157.4121
September | 101083.3048 | 164.7292 | 686.2813 | 0 | 0.0013 | 3422640 | 42569.8633
October | 88760.967 | 143.6763 | 593.4864 | 0 | 0.0011 | 2959810 | 37279.4594
November | 77906.7946 | 123.4246 | 495.7007 | 0 | 0.0009 | 2472040 | 32441.9407
December | 81483.8489 | 124.8139 | 478.2539 | 0 | 0.0009 | 2384870 | 33486.8909
Annual Sum or Average | 1064030 | 1701.8303 | 6921.7219 | 0 | 0.0131 | 34519000 | 444761.0933
Minimum of Months | 71756.733 | 112.7339 | 447.6645 | 0 | 0.0009 | 2232450 | 29782.4615
Maximum of Months | 116369.1352 | 189.7857 | 791.4349 | 0 | 0.0015 | 3947070 | 49022.477
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 318165000000 | 261225.187 | 18-JAN-14:09 | 120876.129 | 75091.738 | 18837.882 | 0 | 43977.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2442.437 | 0 | 0
February | 292951000000 | 283622.525 | 27-FEB-14:30 | 120876.129 | 75091.738 | 26248.399 | 0 | 58929.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2476.955 | 0 | 0
March | 343900000000 | 310317.178 | 31-MAR-13:00 | 120876.129 | 75091.738 | 25430.239 | 0 | 86356.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2562.38 | 0 | 0
April | 357934000000 | 407848.797 | 21-APR-14:00 | 120876.129 | 73092.045 | 44776.722 | 0 | 166412.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2691.084 | 0 | 0
May | 426576000000 | 439104.727 | 31-MAY-14:00 | 120876.129 | 73092.045 | 46648.879 | 0 | 195781.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2706.425 | 0 | 0
June | 517950000000 | 521779.361 | 27-JUN-15:00 | 120876.129 | 73092.045 | 62625.676 | 0 | 262577.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.271 | 0 | 0
July | 394220000000 | 384876.07 | 24-JUL-15:30 | 67153.405 | 40636.785 | 36204.581 | 0 | 238417.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2463.55 | 0 | 0
August | 403153000000 | 371675.767 | 04-AUG-14:00 | 67153.405 | 40636.785 | 34164.554 | 0 | 227124.571 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2596.447 | 0 | 0
September | 449132000000 | 458125.261 | 08-SEP-14:00 | 120876.129 | 73092.045 | 50995.285 | 0 | 210449.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.855 | 0 | 0
October | 388399000000 | 404838.346 | 03-OCT-14:00 | 120876.129 | 73092.045 | 43287.167 | 0 | 164896.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2686.458 | 0 | 0
November | 324391000000 | 295213.687 | 10-NOV-12:00 | 120876.129 | 79091.122 | 23746.183 | 0 | 69014.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2485.433 | 0 | 0
December | 312953000000 | 282723.648 | 05-DEC-12:00 | 120876.129 | 79091.122 | 19795.435 | 0 | 60499.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2461.592 | 0 | 0
Annual Sum or Average | 4529720000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 292951000000 | 261225.187 |  | 67153.405 | 40636.785 | 18837.882 | 0 | 43977.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2442.437 | 0 | 0
Maximum of Months | 517950000000 | 521779.361 |  | 120876.129 | 79091.122 | 62625.676 | 0 | 262577.239 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2711.855 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 126793.58 | 8804.4 | 0 | 135597.98
Cost per Total Building Area ($/m2) | 18.45 | 1.28 | 0 | 19.73
Cost per Net Conditioned Building Area ($/m2) | 18.45 | 1.28 | 0 | 19.73

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5047.94 | 734.67 | 734.67
Net Site Energy | 5047.94 | 734.67 | 734.67
Total Source Energy | 12913.1 | 1879.36 | 1879.36
Net Source Energy | 12913.1 | 1879.36 | 1879.36
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 989.16 | 0 | 0 | 0 | 0
Cooling | 248.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 171.79 | 0 | 0 | 0 | 0 | 0
Pumps | 0.96 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 129.6 | 0 | 0 | 0 | 971.75
Refrigeration | 68.35 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3694.83 | 1353.11 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 612640.17 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20815.83 | 15492.54 | 5323.29 | 0.74 | 3.46
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24814.03 | 18861.69 | 5952.34 | 0.76 | 3.49
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44026.36 | 32767.37 | 11258.98 | 0.74 | 3.24
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 161836.88 | 129251.88 | 32585 | 0.8 | 3.72
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 186547.56 | 148987.19 | 37560.37 | 0.8 | 3.7
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 143312.68 | 114457.42 | 28855.25 | 0.8 | 3.89
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 151908.06 | 121322.17 | 30585.89 | 0.8 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10249.8 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11848.36 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15618.37 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15489.46 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15501.43 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11680.96 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11688.9 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11808.08 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11572.57 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11518.83 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11622.49 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26071.66 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13235.13 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23642.04 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5233.34 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 54136.48 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53219.49 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53374.22 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29734.74 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29768.11 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20258.32 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29641.52 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 47688.08 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 53916.33 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 100862.31 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 31207.48 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 36002.83 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 31540.93 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 28568.12 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1220.6 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.34 | 1528.69 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.78 | 16819.2 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.27 | 19093.55 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.66 | 16241.42 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.18 | 17215.52 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3373.46 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39205.5555 | 34.1831 | 252.5552 | 0 | 0.0001 | 1523500 | 14339.6445
February | 31019.5107 | 26.8661 | 231.96 | 0 | 0.0001 | 1399420 | 11443.6057
March | 36571.1002 | 31.7232 | 264.7492 | 0 | 0.0001 | 1597200 | 13465.0585
April | 31981.3526 | 27.647 | 248.4998 | 0 | 0.0001 | 1499240 | 11826.9631
May | 33753.468 | 29.1132 | 274.0249 | 0 | 0.0001 | 1653290 | 12518.171
June | 33048.8669 | 28.4812 | 272.6383 | 0 | 0.0001 | 1644940 | 12270.077
July | 23359.3469 | 20.1534 | 188.6859 | 0 | 0.0001 | 1138400 | 8660.3824
August | 25298.3694 | 21.8414 | 201.6448 | 0 | 0.0001 | 1216580 | 9371.0186
September | 32673.2668 | 28.126 | 275.1782 | 0 | 0.0001 | 1660280 | 12147.8303
October | 33733.1165 | 29.0858 | 275.6192 | 0 | 0.0001 | 1662910 | 12515.9915
November | 33628.1324 | 29.1038 | 255.356 | 0 | 0.0001 | 1540580 | 12417.8343
December | 36456.0135 | 31.7236 | 245.9847 | 0 | 0.0001 | 1483920 | 13367.9773
Annual Sum or Average | 390728.0994 | 338.0478 | 2986.8961 | 0 | 0.0015 | 18020300 | 144344.5541
Minimum of Months | 23359.3469 | 20.1534 | 188.6859 | 0 | 0.0001 | 1138400 | 8660.3824
Maximum of Months | 39205.5555 | 34.1831 | 275.6192 | 0 | 0.0001 | 1662910 | 14339.6445
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 312375000000 | 232283.179 | 27-JAN-14:00 | 120876.129 | 75091.738 | 15002.192 | 0 | 18999.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2313.18 | 0 | 0
February | 286934000000 | 280187.362 | 15-FEB-15:00 | 120876.129 | 73092.045 | 16806.328 | 0 | 66906.066 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2506.784 | 0 | 0
March | 327486000000 | 259973.173 | 01-MAR-12:00 | 120876.129 | 79091.122 | 14936.47 | 0 | 42640.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2428.829 | 0 | 0
April | 307401000000 | 284148.288 | 14-APR-13:00 | 120876.129 | 75091.738 | 17354.07 | 0 | 68313.677 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2512.668 | 0 | 0
May | 338986000000 | 305669.195 | 17-MAY-13:00 | 120876.129 | 75091.738 | 18002.561 | 0 | 89110.414 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2588.345 | 0 | 0
June | 337274000000 | 312173.134 | 15-JUN-12:00 | 120876.129 | 75091.738 | 18245.613 | 0 | 95361.508 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2598.133 | 0 | 0
July | 233416000000 | 217904.804 | 03-JUL-12:00 | 67153.405 | 41836.601 | 13095.633 | 0 | 93294.931 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2524.225 | 0 | 0
August | 249444000000 | 208405.484 | 15-AUG-11:00 | 67153.405 | 44636.17 | 11804.274 | 0 | 82332.226 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2479.403 | 0 | 0
September | 340420000000 | 386445.558 | 28-SEP-14:00 | 120876.129 | 73092.045 | 32865.436 | 0 | 156900.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.299 | 0 | 0
October | 340960000000 | 309411.159 | 31-OCT-13:20 | 120876.129 | 75091.738 | 19656.665 | 0 | 91232.638 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2553.98 | 0 | 0
November | 315878000000 | 253036.542 | 08-NOV-12:00 | 120876.129 | 79091.122 | 14699.393 | 0 | 35961.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2408.227 | 0 | 0
December | 304259000000 | 237360.802 | 07-DEC-14:00 | 120876.129 | 75091.738 | 13731.903 | 0 | 25307.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2353.763 | 0 | 0
Annual Sum or Average | 3694830000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 233416000000 | 208405.484 |  | 67153.405 | 41836.601 | 11804.274 | 0 | 18999.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2313.18 | 0 | 0
Maximum of Months | 340960000000 | 386445.558 |  | 120876.129 | 79091.122 | 32865.436 | 0 | 156900.649 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2711.299 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 151272.22 | 11546.92 | 0 | 162819.14
Cost per Total Building Area ($/m2) | 22.02 | 1.68 | 0 | 23.7
Cost per Net Conditioned Building Area ($/m2) | 22.02 | 1.68 | 0 | 23.7

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6838.14 | 995.22 | 995.22
Net Site Energy | 6838.14 | 995.22 | 995.22
Total Source Energy | 17754.67 | 2584 | 2584
Net Source Energy | 17754.67 | 2584 | 2584
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2327.74 | 0 | 0 | 0 | 0
Cooling | 667.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.62 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 197.59 | 0 | 0 | 0 | 0 | 0
Pumps | 2.84 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 134.58 | 0 | 0 | 0 | 971.75
Refrigeration | 69.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4141.47 | 2696.66 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 676864.27 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20636.68 | 13952.12 | 6684.57 | 0.68 | 3.31
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30990.3 | 20952.02 | 10038.28 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 207109.52 | 143002.77 | 64106.75 | 0.69 | 3.37
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 217325.56 | 146930.16 | 70395.39 | 0.68 | 3.31
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 165739.45 | 112053.66 | 53685.79 | 0.68 | 3.31
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 174622.26 | 118195.82 | 56426.43 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11510.42 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9645.57 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12351.32 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12181.61 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12196.31 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11674.01 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11684.62 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11841.62 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10059.99 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9993.64 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10089.41 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22375.43 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10229.4 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22249.84 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6361.52 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 35041.36 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34230.75 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34379.65 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25510.45 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25554.38 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17596.48 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25400.62 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 51005.05 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 69821.2 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 139087.27 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 59649.39 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 68075.52 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 52396.73 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 54456.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.83 | 963.93 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.25 | 1421.69 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.83 | 16564.74 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.75 | 16418.1 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.67 | 12520.97 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.05 | 13234.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3727.1 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 89309.4324 | 140.7874 | 330.1304 | 0 | 0.0014 | 20521.474 | 36370.8962
February | 74456.4082 | 121.186 | 296.2795 | 0 | 0.0012 | 18419.0711 | 30670.7019
March | 72722.2811 | 127.4856 | 339.747 | 0 | 0.0014 | 21125.4041 | 30790.4589
April | 59286.4228 | 111.0844 | 316.4697 | 0 | 0.0013 | 19680.7305 | 25755.7468
May | 65258.6836 | 126.5643 | 372.0356 | 0 | 0.0015 | 23137.7057 | 28742.5128
June | 77544.046 | 153.0373 | 456.6863 | 0 | 0.0018 | 28403.1368 | 34395.4585
July | 57722.5262 | 114.1463 | 341.2077 | 0 | 0.0014 | 21221.1348 | 25624.2504
August | 60921.8686 | 120.3606 | 359.499 | 0 | 0.0015 | 22358.7126 | 27034.2294
September | 65638.986 | 128.9772 | 383.4543 | 0 | 0.0015 | 23848.378 | 29063.203
October | 65381.9746 | 123.9878 | 357.192 | 0 | 0.0015 | 22213.6796 | 28539.3663
November | 66795.6883 | 119.552 | 325.6198 | 0 | 0.0013 | 20247.9097 | 28505.7214
December | 81639.6857 | 132.3329 | 321.856 | 0 | 0.0014 | 20008.8638 | 33579.8933
Annual Sum or Average | 836678.0035 | 1519.5016 | 4200.1774 | 0 | 0.0172 | 261186.2008 | 359072.439
Minimum of Months | 57722.5262 | 111.0844 | 296.2795 | 0 | 0.0012 | 18419.0711 | 25624.2504
Maximum of Months | 89309.4324 | 153.0373 | 456.6863 | 0 | 0.0018 | 28403.1368 | 36370.8962
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 325397000000 | 237422.462 | 09-JAN-11:50 | 120876.129 | 79091.122 | 10025.525 | 0 | 23987.152 | 0 | 1.906 | 0 | 0 | 0 | 0 | 0 | 3440.628 | 0 | 0
February | 292060000000 | 229695.77 | 15-FEB-14:50 | 120876.129 | 75091.738 | 10656.637 | 0 | 20753.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2317.632 | 0 | 0
March | 334973000000 | 300934.645 | 09-MAR-15:00 | 120876.129 | 73092.045 | 15062.529 | 0 | 89324.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2578.987 | 0 | 0
April | 312066000000 | 307406.078 | 04-APR-14:00 | 120876.129 | 73092.045 | 18818.276 | 0 | 92060.72 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2558.9 | 0 | 0
May | 366881000000 | 380503.267 | 15-MAY-12:00 | 120876.129 | 75091.738 | 21781.634 | 0 | 160131.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2622.243 | 0 | 0
June | 450372000000 | 493671.689 | 30-JUN-14:00 | 120876.129 | 73092.045 | 44571.201 | 0 | 252404.266 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2728.047 | 0 | 0
July | 336491000000 | 367661.141 | 25-JUL-13:30 | 67153.405 | 41836.601 | 22515.12 | 0 | 233548.902 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2607.111 | 0 | 0
August | 354529000000 | 374030.111 | 09-AUG-14:39 | 67153.405 | 40636.785 | 22825.505 | 0 | 240833.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2580.713 | 0 | 0
September | 378150000000 | 435920.785 | 08-SEP-14:00 | 120876.129 | 73092.045 | 42111.526 | 0 | 197135.653 | 0 | 0.028 | 0 | 0 | 0 | 0 | 0 | 2705.404 | 0 | 0
October | 352229000000 | 364323.407 | 12-OCT-14:50 | 120876.129 | 73092.045 | 30394.083 | 0 | 137363.147 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2597.995 | 0 | 0
November | 321059000000 | 325515.691 | 03-NOV-13:00 | 120876.129 | 75091.738 | 19986.974 | 0 | 106999.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2561.807 | 0 | 0
December | 317269000000 | 214191.651 | 06-DEC-11:20 | 120876.129 | 79091.122 | 10674.817 | 0 | 0 | 0 | 66.133 | 0 | 0 | 0 | 0 | 0 | 3483.449 | 0 | 0
Annual Sum or Average | 4141470000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 292060000000 | 214191.651 |  | 67153.405 | 40636.785 | 10025.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2317.632 | 0 | 0
Maximum of Months | 450372000000 | 493671.689 |  | 120876.129 | 79091.122 | 44571.201 | 0 | 252404.266 | 0 | 66.133 | 0 | 0 | 0 | 0 | 0 | 3483.449 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 90842.7 | 26202.31 | 0 | 117045.01
Cost per Total Building Area ($/m2) | 13.22 | 3.81 | 0 | 17.03
Cost per Net Conditioned Building Area ($/m2) | 13.22 | 3.81 | 0 | 17.03

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5874.01 | 854.9 | 854.9
Net Site Energy | 5874.01 | 854.9 | 854.9
Total Source Energy | 15269.61 | 2222.33 | 2222.33
Net Source Energy | 15269.61 | 2222.33 | 2222.33
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1530.24 | 0 | 0 | 0 | 0
Cooling | 460.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 242.22 | 0 | 0 | 0 | 0 | 0
Pumps | 2.02 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 131.35 | 0 | 0 | 0 | 971.75
Refrigeration | 69.05 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3978.07 | 1895.94 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 535619.47 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19420.33 | 13528.25 | 5892.08 | 0.7 | 3.35
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27687.48 | 19687.11 | 8000.38 | 0.71 | 3.38
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53271.5 | 36752.03 | 16519.47 | 0.69 | 3.13
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 144495.99 | 115402.48 | 29093.51 | 0.8 | 3.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 143070.68 | 114264.15 | 28806.53 | 0.8 | 3.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 107347.75 | 85733.85 | 21613.91 | 0.8 | 3.89
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 114700.61 | 91606.24 | 23094.36 | 0.8 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9923.11 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8074.62 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10585.65 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10411.41 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10427.22 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10249.73 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10260.37 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10419.59 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8578.52 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8509.61 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8618.44 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18812.68 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7127.78 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19030.46 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5159.63 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26659.86 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25873.02 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26022.54 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20812.57 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20857.6 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14499.32 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20121.08 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 41330.64 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 56100 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 110512.48 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 46393.98 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 53000.31 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 39766.81 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 42440.93 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.85 | 983.06 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.27 | 1451.38 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.73 | 16375.52 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.64 | 16213.99 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.48 | 12165.56 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.93 | 12998.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2949.35 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 103389.4809 | 164.3613 | 382.0981 | 0 | 0.0015 | 397215.478 | 42699.9211
February | 89450.8695 | 144.9483 | 345.4459 | 0 | 0.0014 | 359134.6729 | 37212.5862
March | 99868.0326 | 164.7275 | 401.3658 | 0 | 0.0016 | 417292.2928 | 41830.5988
April | 88616.7211 | 150.8166 | 381.3026 | 0 | 0.0015 | 396466.402 | 37573.7717
May | 103838.8657 | 179.9737 | 464.3944 | 0 | 0.0018 | 482884.5489 | 44346.8523
June | 112133.9701 | 195.2209 | 506.2019 | 0 | 0.002 | 526362.2751 | 47974.825
July | 80515.9804 | 140.3147 | 364.2248 | 0 | 0.0014 | 378731.5668 | 34461.2232
August | 81318.0582 | 141.5766 | 367.1178 | 0 | 0.0014 | 381738.9708 | 34791.1914
September | 100670.4101 | 175.0882 | 453.5046 | 0 | 0.0018 | 471565.0942 | 43053.1372
October | 94340.9821 | 160.944 | 408.0186 | 0 | 0.0016 | 424247.4577 | 40038.6713
November | 94149.6821 | 155.2786 | 378.2935 | 0 | 0.0015 | 393304.3136 | 39433.7776
December | 102287.613 | 161.855 | 373.9417 | 0 | 0.0015 | 388730.4206 | 42170.8312
Annual Sum or Average | 1150580 | 1935.1055 | 4825.9095 | 0 | 0.019 | 5017670 | 485587.387
Minimum of Months | 80515.9804 | 140.3147 | 345.4459 | 0 | 0.0014 | 359134.6729 | 34461.2232
Maximum of Months | 112133.9701 | 195.2209 | 506.2019 | 0 | 0.002 | 526362.2751 | 47974.825
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 314917000000 | 240623.266 | 25-JAN-14:00 | 120876.129 | 75091.738 | 20824.89 | 0 | 21508.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2321.631 | 0 | 0
February | 284726000000 | 272830.706 | 14-FEB-15:00 | 120876.129 | 73092.045 | 27296.684 | 0 | 49105.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2460.112 | 0 | 0
March | 330834000000 | 280389.475 | 02-MAR-14:00 | 120876.129 | 75091.738 | 27660.73 | 0 | 54260.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2499.972 | 0 | 0
April | 314323000000 | 329555.406 | 21-APR-14:00 | 120876.129 | 73092.045 | 39985.772 | 0 | 93012.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2588.582 | 0 | 0
May | 382837000000 | 358505.484 | 31-MAY-14:00 | 120876.129 | 73092.045 | 41726.999 | 0 | 120140.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2669.34 | 0 | 0
June | 417306000000 | 400412.777 | 29-JUN-13:00 | 120876.129 | 75091.738 | 48644.159 | 0 | 153074.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2726.163 | 0 | 0
July | 300263000000 | 292776.549 | 31-JUL-14:00 | 67153.405 | 40636.785 | 37083.917 | 0 | 145344.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2557.836 | 0 | 0
August | 302647000000 | 295254.852 | 01-AUG-13:00 | 67153.405 | 41836.601 | 36069.888 | 0 | 147596.59 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2598.355 | 0 | 0
September | 373862000000 | 362651.474 | 05-SEP-13:00 | 120876.129 | 75091.738 | 40260.851 | 0 | 123860.265 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2562.49 | 0 | 0
October | 336348000000 | 324859.086 | 13-OCT-14:00 | 120876.129 | 73092.045 | 38129.481 | 0 | 90183.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2578.215 | 0 | 0
November | 311816000000 | 263119.231 | 08-NOV-14:00 | 120876.129 | 75091.738 | 25446.061 | 0 | 39261.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2443.709 | 0 | 0
December | 308190000000 | 232955.387 | 05-DEC-14:50 | 120876.129 | 75091.738 | 18982.783 | 0 | 15712.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2292.274 | 0 | 0
Annual Sum or Average | 3978070000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 284726000000 | 232955.387 |  | 67153.405 | 40636.785 | 18982.783 | 0 | 15712.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2292.274 | 0 | 0
Maximum of Months | 417306000000 | 400412.777 |  | 120876.129 | 75091.738 | 48644.159 | 0 | 153074.589 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2726.163 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40998.5 | 13145.51 | 0 | 54144.02
Cost per Total Building Area ($/m2) | 5.97 | 1.91 | 0 | 7.88
Cost per Net Conditioned Building Area ($/m2) | 5.97 | 1.91 | 0 | 7.88

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5990.36 | 871.83 | 871.83
Net Site Energy | 5990.36 | 871.83 | 871.83
Total Source Energy | 8877.83 | 1292.07 | 1292.07
Net Source Energy | 8877.83 | 1292.07 | 1292.07
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2020.14 | 0 | 0 | 0 | 0
Cooling | 163.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 158 | 0 | 0 | 0 | 0 | 0
Pumps | 2.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 141.49 | 0 | 0 | 0 | 971.75
Refrigeration | 66.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3594.39 | 2395.97 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 5.835 | 0.54 | 0.384 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 324.79 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 554.39 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 557305.45 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14429.18 | 10182.54 | 4246.65 | 0.71 | 3.39
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23861.78 | 16809.06 | 7052.72 | 0.7 | 3.36
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51362.23 | 35929.14 | 15433.1 | 0.7 | 3.15
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122867.71 | 97234.32 | 25633.39 | 0.79 | 3.85
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 139468.87 | 110220.09 | 29248.78 | 0.79 | 3.84
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 105985.16 | 82873.63 | 23111.52 | 0.78 | 3.8
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 113098.28 | 89529.54 | 23568.74 | 0.79 | 3.85
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8730.78 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7133.01 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12387.68 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12232.98 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12247.23 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9616.09 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9625.17 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9764.85 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8206.61 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8141.62 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8245.07 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16723.98 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11517.78 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16367.1 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4055.1 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 38980.44 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 37944.88 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 38106.99 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18181.43 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18221.55 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12705.47 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23487.45 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 34567.3 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 56903.15 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 120284.05 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 45998.01 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 52055.13 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 38638.57 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 42368.15 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.65 | 755.4 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.28 | 13648.65 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.23 | 15445.94 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.11 | 11464.94 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.7 | 12571.59 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3068.76 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37107.6756 | 44.1485 | 66.9735 | 0 | 0.0003 | 883779.975 | 13963.8425
February | 28250.8845 | 35.0463 | 60.151 | 0 | 0.0003 | 794096.043 | 10784.6747
March | 31444.1635 | 39.4143 | 69.5467 | 0 | 0.0003 | 918218.7666 | 12047.2552
April | 23858.6047 | 31.5887 | 63.5128 | 0 | 0.0003 | 838884.1615 | 9321.2013
May | 21047.092 | 30.1091 | 70.3486 | 0 | 0.0003 | 929538.2034 | 8462.996
June | 19548.9462 | 28.9798 | 71.8147 | 0 | 0.0003 | 949042.5314 | 7969.1843
July | 13391.1715 | 20.0033 | 50.1637 | 0 | 0.0002 | 662939.2932 | 5475.2226
August | 14220.5662 | 21.1938 | 52.9611 | 0 | 0.0002 | 699902.5305 | 5809.1431
September | 19146.6914 | 28.1212 | 68.6623 | 0 | 0.0003 | 907351.2276 | 7777.1113
October | 22285.0758 | 30.7532 | 67.291 | 0 | 0.0003 | 888990.9338 | 8840.0882
November | 30700.4801 | 38.1024 | 65.4772 | 0 | 0.0003 | 864414.7359 | 11721.6545
December | 36575.2874 | 43.4278 | 65.4552 | 0 | 0.0003 | 863723.1131 | 13754.1507
Annual Sum or Average | 297576.6388 | 390.8884 | 772.3579 | 0 | 0.0033 | 10200900 | 115926.5244
Minimum of Months | 13391.1715 | 20.0033 | 50.1637 | 0 | 0.0002 | 662939.2932 | 5475.2226
Maximum of Months | 37107.6756 | 44.1485 | 71.8147 | 0 | 0.0003 | 949042.5314 | 13963.8425
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 311409000000 | 213107.242 | 10-JAN-16:49 | 120876.129 | 73092.045 | 9133.905 | 0 | 0 | 7870 | 143.451 | 0 | 0 | 0 | 0 | 0 | 1991.712 | 0 | 0
February | 279808000000 | 231283.32 | 21-FEB-12:00 | 120876.129 | 79091.122 | 11042.848 | 0 | 17933.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2339.55 | 0 | 0
March | 323544000000 | 254045.658 | 29-MAR-13:00 | 120876.129 | 75091.738 | 18288.822 | 0 | 37330.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2458.396 | 0 | 0
April | 295590000000 | 244832.916 | 18-APR-13:00 | 120876.129 | 75091.738 | 17240.296 | 0 | 29243.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2380.998 | 0 | 0
May | 327533000000 | 310094.598 | 04-MAY-13:00 | 120876.129 | 75091.738 | 28553.306 | 0 | 83022.87 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2550.544 | 0 | 0
June | 334405000000 | 321374.365 | 28-JUN-13:50 | 120876.129 | 75091.738 | 26108.699 | 0 | 96707.155 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2590.638 | 0 | 0
July | 233594000000 | 226815.453 | 24-JUL-14:00 | 67153.405 | 40636.785 | 17126.932 | 0 | 99379.252 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 2519.067 | 0 | 0
August | 246618000000 | 215062.608 | 07-AUG-14:00 | 67153.405 | 40636.785 | 16986.087 | 0 | 87814.563 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2471.763 | 0 | 0
September | 319715000000 | 339551.414 | 13-SEP-14:00 | 120876.129 | 73092.045 | 32062.517 | 0 | 110897.197 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2623.519 | 0 | 0
October | 313246000000 | 268209.375 | 17-OCT-13:39 | 120876.129 | 75091.738 | 20316.631 | 0 | 49428.635 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2496.233 | 0 | 0
November | 304586000000 | 229349.747 | 03-NOV-11:00 | 120876.129 | 79091.122 | 9665.474 | 0 | 17364.722 | 0 | 1.161 | 0 | 0 | 0 | 0 | 0 | 2351.138 | 0 | 0
December | 304342000000 | 213162.463 | 14-DEC-16:19 | 120876.129 | 73092.045 | 9133.905 | 0 | 0 | 7870 | 208.637 | 0 | 0 | 0 | 0 | 0 | 1981.746 | 0 | 0
Annual Sum or Average | 3594390000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 233594000000 | 213107.242 |  | 67153.405 | 40636.785 | 9133.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1981.746 | 0 | 0
Maximum of Months | 334405000000 | 339551.414 |  | 120876.129 | 79091.122 | 32062.517 | 0 | 110897.197 | 7870 | 208.637 | 0 | 0 | 0 | 0 | 0 | 2623.519 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 75206.5 | 20143.94 | 0 | 95350.44
Cost per Total Building Area ($/m2) | 10.95 | 2.93 | 0 | 13.88
Cost per Net Conditioned Building Area ($/m2) | 10.95 | 2.93 | 0 | 13.88

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6809.28 | 991.02 | 991.02
Net Site Energy | 6809.28 | 991.02 | 991.02
Total Source Energy | 16816.37 | 2447.44 | 2447.44
Net Source Energy | 16816.37 | 2447.44 | 2447.44
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2603.22 | 0 | 0 | 0 | 0
Cooling | 382.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 164.36 | 0 | 0 | 0 | 0 | 0
Pumps | 3.09 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 149.14 | 0 | 0 | 0 | 971.75
Refrigeration | 67.47 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3822.59 | 2986.69 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.525 | 0.407 | 0.316 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 324.79 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 554.39 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 588414.39 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17206.71 | 11633.17 | 5573.54 | 0.68 | 3.32
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 164678.67 | 111336.49 | 53342.19 | 0.68 | 3.31
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 161546.26 | 109218.72 | 52327.54 | 0.68 | 3.31
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 123224.25 | 83309.85 | 39914.4 | 0.68 | 3.31
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129028.15 | 87233.77 | 41794.38 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8200.82 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7695.66 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9034.33 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8937.73 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8946.89 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8635.29 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8641.28 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8732.44 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7733.13 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7688.32 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7758.86 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17597.06 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6085.43 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17158.44 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5321.7 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23507.76 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22973.15 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23078.24 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20220.02 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20246.15 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13837.25 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18110.15 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 49681.04 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 76866.16 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 162482.64 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 63623.66 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 62413.45 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 47607.73 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 49850.07 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.69 | 803.72 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.63 | 12440.83 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.51 | 12204.19 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 4.96 | 9309.11 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.2 | 9747.58 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3240.06 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 142210.772 | 226.5257 | 584.7197 | 0 | 0.0018 | 134567.0515 | 58535.7142
February | 122759.0119 | 198.824 | 524.4202 | 0 | 0.0016 | 120695.4349 | 50842.9943
March | 131801.8627 | 220.0158 | 602.2908 | 0 | 0.0019 | 138628.2558 | 55214.1071
April | 109564.2745 | 192.1935 | 556.4159 | 0 | 0.0017 | 128083.7667 | 46787.4516
May | 121735.3388 | 218.3326 | 646.9349 | 0 | 0.002 | 148927.4053 | 52442.7665
June | 142176.6369 | 257.1558 | 768.5241 | 0 | 0.0023 | 176920.7087 | 61455.419
July | 99702.6497 | 180.4856 | 539.8503 | 0 | 0.0016 | 124278.2701 | 43110.7734
August | 99538.1134 | 180.0421 | 538.0868 | 0 | 0.0016 | 123872.1013 | 43025.7115
September | 120461.3845 | 217.3147 | 647.7598 | 0 | 0.002 | 149119.0108 | 52015.0908
October | 116493.2992 | 206.528 | 604.672 | 0 | 0.0018 | 139195.0872 | 49954.7805
November | 121419.014 | 205.4713 | 571.5546 | 0 | 0.0018 | 131558.0921 | 51131.0594
December | 133923.4612 | 216.7971 | 571.4599 | 0 | 0.0018 | 131521.4337 | 55456.5286
Annual Sum or Average | 1461790 | 2519.6862 | 7156.6891 | 0 | 0.0219 | 1647370 | 619972.3969
Minimum of Months | 99538.1134 | 180.0421 | 524.4202 | 0 | 0.0016 | 120695.4349 | 43025.7115
Maximum of Months | 142210.772 | 257.1558 | 768.5241 | 0 | 0.0023 | 176920.7087 | 61455.419
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 312253000000 | 213389.436 | 27-JAN-16:00 | 120876.129 | 73092.045 | 8378.719 | 0 | 0 | 7870 | 1343.256 | 0 | 0 | 0 | 0 | 0 | 1829.287 | 0 | 0
February | 280065000000 | 212423.824 | 28-FEB-11:20 | 120876.129 | 79091.122 | 8925.218 | 0 | 0 | 0 | 8.813 | 0 | 0 | 0 | 0 | 0 | 3522.542 | 0 | 0
March | 321676000000 | 253914.101 | 31-MAR-14:00 | 120876.129 | 73092.045 | 13273.67 | 0 | 44190.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2481.829 | 0 | 0
April | 297209000000 | 264159.161 | 07-APR-13:00 | 120876.129 | 75091.738 | 16416.282 | 0 | 49252.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2522.245 | 0 | 0
May | 345575000000 | 340535.673 | 30-MAY-14:00 | 120876.129 | 73092.045 | 19523.492 | 0 | 124424.917 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2619.087 | 0 | 0
June | 410531000000 | 433438.177 | 08-JUN-12:00 | 120876.129 | 75091.738 | 35292.928 | 0 | 199464.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2712.53 | 0 | 0
July | 288378000000 | 306816.517 | 13-JUL-12:00 | 67153.405 | 41836.601 | 15313.008 | 0 | 179923.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2590.498 | 0 | 0
August | 287436000000 | 315084.645 | 04-AUG-15:50 | 67153.405 | 40636.785 | 20458.639 | 0 | 184286.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2549.312 | 0 | 0
September | 346019000000 | 376068.545 | 06-SEP-11:00 | 120876.129 | 79091.122 | 25339.449 | 0 | 148114.307 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2647.531 | 0 | 0
October | 322992000000 | 306965.687 | 31-OCT-11:00 | 120876.129 | 79091.122 | 14081.342 | 0 | 90360.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.171 | 0 | 0
November | 305271000000 | 299050.517 | 02-NOV-14:39 | 120876.129 | 73092.045 | 14858.724 | 0 | 87671.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2552.547 | 0 | 0
December | 305186000000 | 212425.988 | 13-DEC-16:19 | 120876.129 | 73092.045 | 8378.719 | 0 | 0 | 7870 | 333.792 | 0 | 0 | 0 | 0 | 0 | 1875.303 | 0 | 0
Annual Sum or Average | 3822590000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 280065000000 | 212423.824 |  | 67153.405 | 40636.785 | 8378.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1829.287 | 0 | 0
Maximum of Months | 410531000000 | 433438.177 |  | 120876.129 | 79091.122 | 35292.928 | 0 | 199464.852 | 7870 | 1343.256 | 0 | 0 | 0 | 0 | 0 | 3522.542 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 93961.98 | 25011.57 | 0 | 118973.55
Cost per Total Building Area ($/m2) | 13.68 | 3.64 | 0 | 17.32
Cost per Net Conditioned Building Area ($/m2) | 13.68 | 3.64 | 0 | 17.32

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5966.28 | 868.33 | 868.33
Net Site Energy | 5966.28 | 868.33 | 868.33
Total Source Energy | 14715.83 | 2141.73 | 2141.73
Net Source Energy | 14715.83 | 2141.73 | 2141.73
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1899.93 | 0 | 0 | 0 | 0
Cooling | 236.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 173.3 | 0 | 0 | 0 | 0 | 0
Pumps | 2.7 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 147.98 | 0 | 0 | 0 | 971.75
Refrigeration | 67.09 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3684.03 | 2282.25 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.525 | 0.407 | 0.316 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 324.79 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 554.39 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 458359.68 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15414.15 | 10693.64 | 4720.52 | 0.69 | 3.36
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24154.18 | 16935.08 | 7219.1 | 0.7 | 3.35
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53923.29 | 37032.95 | 16890.34 | 0.69 | 3.12
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 104062.12 | 83109.76 | 20952.36 | 0.8 | 3.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 104788.64 | 82896.21 | 21892.43 | 0.79 | 3.85
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 82389.94 | 63941.59 | 18448.35 | 0.78 | 3.8
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 83905.64 | 66283.4 | 17622.24 | 0.79 | 3.84
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6710.62 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6177.49 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7492.14 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7390.58 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7400.82 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7109.08 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7115.51 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7212.71 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6377.36 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6332.65 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6414.79 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14210.37 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5471.78 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14235.52 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5504.68 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18447.24 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17934.14 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18034.49 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15690.25 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15716.84 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10833.53 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14237.59 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 38739.4 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 62407.86 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 131920.13 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 48701.15 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 48030.72 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 36191.44 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 38340.85 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 771.9 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.29 | 11793.21 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.2 | 11630.86 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.67 | 8910.81 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 4.95 | 9284.41 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2523.92 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 104592.709 | 164.7604 | 378.3519 | 0 | 0.0015 | 393309.2122 | 43048.376
February | 91892.7588 | 145.9208 | 338.7226 | 0 | 0.0014 | 352122.5958 | 37935.6951
March | 100715.3153 | 164.0738 | 393.6685 | 0 | 0.0016 | 409274.6988 | 41984.2818
April | 87238.4142 | 146.934 | 367.0537 | 0 | 0.0014 | 381640.4942 | 36838.6152
May | 93102.0644 | 159.0181 | 403.6756 | 0 | 0.0016 | 419733.0625 | 39531.2704
June | 97041.7438 | 168.0002 | 432.953 | 0 | 0.0017 | 450190.0695 | 41425.0803
July | 68575.5618 | 119.316 | 309.1814 | 0 | 0.0012 | 321494.6121 | 29332.013
August | 70820.2722 | 123.1086 | 318.6901 | 0 | 0.0012 | 331381.27 | 30281.0606
September | 89480.2475 | 154.2919 | 395.8739 | 0 | 0.0015 | 411630.778 | 38136.646
October | 91549.259 | 155.5515 | 392.5349 | 0 | 0.0015 | 408143.6991 | 38792.0611
November | 94626.9329 | 154.0346 | 369.2175 | 0 | 0.0015 | 383853.4968 | 39434.4355
December | 103327.7163 | 161.9624 | 369.4173 | 0 | 0.0015 | 384014.9266 | 42448.7382
Annual Sum or Average | 1092960 | 1816.9722 | 4469.3403 | 0 | 0.0176 | 4646790 | 459188.2732
Minimum of Months | 68575.5618 | 119.316 | 309.1814 | 0 | 0.0012 | 321494.6121 | 29332.013
Maximum of Months | 104592.709 | 168.0002 | 432.953 | 0 | 0.0017 | 450190.0695 | 43048.376
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 311820000000 | 233202.175 | 27-JAN-12:00 | 120876.129 | 79091.122 | 12334.723 | 0 | 18517.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2382.271 | 0 | 0
February | 279167000000 | 227000.492 | 07-FEB-14:00 | 120876.129 | 75091.738 | 15631.909 | 0 | 13105.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2295.211 | 0 | 0
March | 324478000000 | 269197.864 | 30-MAR-14:00 | 120876.129 | 73092.045 | 25135.713 | 0 | 47607.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2486.619 | 0 | 0
April | 302569000000 | 289203.054 | 25-APR-14:00 | 120876.129 | 73092.045 | 28258.165 | 0 | 64417.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2559.349 | 0 | 0
May | 332769000000 | 310226.885 | 23-MAY-15:00 | 120876.129 | 73092.045 | 30058.469 | 0 | 83683.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2517.104 | 0 | 0
June | 356916000000 | 345459.963 | 28-JUN-11:00 | 120876.129 | 79091.122 | 28526.669 | 0 | 114280.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2685.408 | 0 | 0
July | 254885000000 | 251128.781 | 17-JUL-15:30 | 67153.405 | 40636.785 | 29085.119 | 0 | 111790.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2463.147 | 0 | 0
August | 262723000000 | 255830.679 | 30-AUG-13:00 | 67153.405 | 41836.601 | 26991.03 | 0 | 117260.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2588.922 | 0 | 0
September | 326346000000 | 328608.556 | 05-SEP-13:00 | 120876.129 | 75091.738 | 30485.92 | 0 | 99464.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.464 | 0 | 0
October | 323581000000 | 309826.537 | 05-OCT-14:00 | 120876.129 | 73092.045 | 31776.923 | 0 | 81475.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2606.272 | 0 | 0
November | 304324000000 | 252923.784 | 10-NOV-13:00 | 120876.129 | 75091.738 | 18539.312 | 0 | 35945.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2470.994 | 0 | 0
December | 304452000000 | 222006.035 | 21-DEC-14:30 | 120876.129 | 75091.738 | 13616.415 | 0 | 10138.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2282.811 | 0 | 0
Annual Sum or Average | 3684030000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 254885000000 | 222006.035 |  | 67153.405 | 40636.785 | 12334.723 | 0 | 10138.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2282.811 | 0 | 0
Maximum of Months | 356916000000 | 345459.963 |  | 120876.129 | 79091.122 | 31776.923 | 0 | 117260.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.464 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37982.31 | 15862.27 | 0 | 53844.58
Cost per Total Building Area ($/m2) | 5.53 | 2.31 | 0 | 7.84
Cost per Net Conditioned Building Area ($/m2) | 5.53 | 2.31 | 0 | 7.84

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7509.16 | 1092.88 | 1092.88
Net Site Energy | 7509.16 | 1092.88 | 1092.88
Total Source Energy | 16942.16 | 2465.75 | 2465.75
Net Source Energy | 16942.16 | 2465.75 | 2465.75
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3384.84 | 0 | 0 | 0 | 0
Cooling | 293.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 158.59 | 0 | 0 | 0 | 0 | 0
Pumps | 4.85 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 161.97 | 0 | 0 | 0 | 971.75
Refrigeration | 66.67 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3728 | 3781.16 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.525 | 0.407 | 0.316 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 324.79 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 554.39 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 563233.39 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15567.68 | 10525.05 | 5042.63 | 0.68 | 3.32
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 142656.18 | 96447.45 | 46208.73 | 0.68 | 3.31
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 146291.35 | 98905.12 | 47386.22 | 0.68 | 3.31
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 110652.99 | 74810.63 | 35842.36 | 0.68 | 3.33
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116954.02 | 79070.65 | 37883.37 | 0.68 | 3.33
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7052.43 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6755.59 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8337.1 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8239.01 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8248.4 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7767.33 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7773.16 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7864 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6641.26 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6595.55 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6668.37 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15383.25 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6552.29 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14372.32 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5229.09 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21653.33 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21154.19 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21264.73 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17514.51 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17539.63 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12038.63 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15882.49 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 48576.29 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 83069.72 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 175595.96 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 60528.71 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 62071.1 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 46949.82 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 49623.34 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.63 | 727.16 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.74 | 10777.12 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.89 | 11051.74 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.46 | 8499.5 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.71 | 8983.5 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3101.4 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 116826.4677 | 169.0694 | 205.7593 | 0 | 0.0016 | 135092.2243 | 46458.2232
February | 97452.1974 | 144.8842 | 184.1825 | 0 | 0.0014 | 120949.9899 | 39121.9759
March | 93786.7677 | 149.5262 | 210.1144 | 0 | 0.0016 | 138037.9755 | 38615.1072
April | 73270.3364 | 125.8434 | 193.5439 | 0 | 0.0014 | 127196.168 | 31030.6747
May | 79179.7546 | 140.8841 | 225.0798 | 0 | 0.0016 | 147941.8701 | 34000.892
June | 87626.764 | 158.0496 | 256.0464 | 0 | 0.0019 | 168304.0761 | 37832.3172
July | 59481.8519 | 107.4426 | 174.3181 | 0 | 0.0013 | 114583.1573 | 25695.9394
August | 62721.919 | 113.2834 | 183.775 | 0 | 0.0013 | 120799.2982 | 27094.5049
September | 72734.0222 | 130.1273 | 209.0757 | 0 | 0.0015 | 137425.3632 | 31301.0752
October | 76839.4213 | 131.9855 | 203.0111 | 0 | 0.0015 | 133418.0433 | 32543.3747
November | 88176.2358 | 141.1316 | 199.3371 | 0 | 0.0015 | 130960.4239 | 36357.68
December | 106080.3353 | 157.8217 | 200.8472 | 0 | 0.0015 | 131894.093 | 42596.224
Annual Sum or Average | 1014180 | 1670.049 | 2445.0905 | 0 | 0.0182 | 1606600 | 422647.9884
Minimum of Months | 59481.8519 | 107.4426 | 174.3181 | 0 | 0.0013 | 114583.1573 | 25695.9394
Maximum of Months | 116826.4677 | 169.0694 | 256.0464 | 0 | 0.0019 | 168304.0761 | 46458.2232
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 313471000000 | 213870.552 | 04-JAN-16:00 | 120876.129 | 73092.045 | 7957.084 | 0 | 0 | 7870 | 2247.454 | 0 | 0 | 0 | 0 | 0 | 1827.84 | 0 | 0
February | 280655000000 | 212550.725 | 03-FEB-11:09 | 120876.129 | 79091.122 | 7957.084 | 0 | 0 | 0 | 1217.345 | 0 | 0 | 0 | 0 | 0 | 3409.045 | 0 | 0
March | 320307000000 | 228389.951 | 23-MAR-14:00 | 120876.129 | 73092.045 | 11735.107 | 0 | 20366.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2320.094 | 0 | 0
April | 295149000000 | 250211.438 | 14-APR-14:00 | 120876.129 | 73092.045 | 14846.665 | 0 | 38946.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2450.044 | 0 | 0
May | 343288000000 | 353930.269 | 31-MAY-11:00 | 120876.129 | 79091.122 | 21367.656 | 0 | 129948.058 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2647.295 | 0 | 0
June | 390537000000 | 407030.067 | 29-JUN-14:00 | 120876.129 | 73092.045 | 34595.519 | 0 | 175763.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2702.809 | 0 | 0
July | 265882000000 | 285519.12 | 13-JUL-15:00 | 67153.405 | 40636.785 | 13039.811 | 0 | 162132.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.685 | 0 | 0
August | 280306000000 | 284645.067 | 25-AUG-15:00 | 67153.405 | 40636.785 | 15397.789 | 0 | 158911.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2545.38 | 0 | 0
September | 318885000000 | 355068.98 | 14-SEP-14:00 | 120876.129 | 73092.045 | 27714.914 | 0 | 130749.937 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2635.948 | 0 | 0
October | 309587000000 | 266634.896 | 06-OCT-14:00 | 120876.129 | 73092.045 | 17754.132 | 0 | 52409.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2503.401 | 0 | 0
November | 303884000000 | 243338.562 | 02-NOV-14:00 | 120876.129 | 73092.045 | 15298.549 | 0 | 31695.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2375.853 | 0 | 0
December | 306050000000 | 212294.457 | 29-DEC-16:00 | 120876.129 | 73092.045 | 7957.084 | 0 | 0 | 7870 | 661.037 | 0 | 0 | 0 | 0 | 0 | 1838.162 | 0 | 0
Annual Sum or Average | 3728000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 265882000000 | 212294.457 |  | 67153.405 | 40636.785 | 7957.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1827.84 | 0 | 0
Maximum of Months | 390537000000 | 407030.067 |  | 120876.129 | 79091.122 | 34595.519 | 0 | 175763.565 | 7870 | 2247.454 | 0 | 0 | 0 | 0 | 0 | 3409.045 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63473.98 | 29846.32 | 0 | 93320.3
Cost per Total Building Area ($/m2) | 9.24 | 4.34 | 0 | 13.58
Cost per Net Conditioned Building Area ($/m2) | 9.24 | 4.34 | 0 | 13.58

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6582.21 | 957.97 | 957.97
Net Site Energy | 6582.21 | 957.97 | 957.97
Total Source Energy | 15670.56 | 2280.68 | 2280.68
Net Source Energy | 15670.56 | 2280.68 | 2280.68
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2626.13 | 0 | 0 | 0 | 0
Cooling | 132.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.53 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 151.74 | 0 | 0 | 0 | 0 | 0
Pumps | 3.68 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 163.52 | 0 | 0 | 0 | 971.75
Refrigeration | 65.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3558.22 | 3023.99 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.525 | 0.407 | 0.316 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 324.79 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 554.39 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 495106.63 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10977.31 | 8133.6 | 2843.71 | 0.74 | 3.47
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19668.51 | 15001.76 | 4666.75 | 0.76 | 3.5
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46116.8 | 33668.35 | 12448.44 | 0.73 | 3.21
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 100156.51 | 79990.52 | 20165.99 | 0.8 | 3.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 89532.68 | 71505.75 | 18026.94 | 0.8 | 3.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 69178.88 | 55250.08 | 13928.8 | 0.8 | 4.17
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 71668.3 | 57238.26 | 14430.03 | 0.8 | 3.93
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6880.37 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5550.34 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7100.44 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7001.39 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7011.63 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6433.17 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6439.26 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6533.86 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5395.63 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5350.83 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5433.82 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12716.21 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6458.55 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13526.36 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5559.5 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18060.11 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17575.16 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17686.59 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16660.65 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16665.79 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11019.8 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13720.17 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 39473.29 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 75696.65 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 160010.48 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 58246.55 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 52068.21 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 40231.35 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 41679.08 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 648.45 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.05 | 11350.59 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.41 | 10146.61 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.18 | 7971.34 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.33 | 8258.19 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2726.27 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 107315.0846 | 161.2538 | 231.3775 | 0 | 0.0017 | 5484930 | 43313.2427
February | 90933.9545 | 139.9331 | 207.9713 | 0 | 0.0015 | 4930750 | 37020.0884
March | 92993.2601 | 150.3196 | 238.7834 | 0 | 0.0017 | 5662660 | 38556.1297
April | 79192.6596 | 131.5641 | 216.1948 | 0 | 0.0015 | 5127590 | 33177.6386
May | 81090.6585 | 139.0994 | 237.2244 | 0 | 0.0017 | 5627070 | 34396.3967
June | 83890.7023 | 146.0961 | 253.3487 | 0 | 0.0018 | 6009880 | 35796.1363
July | 56141.5184 | 98.5301 | 172.2927 | 0 | 0.0012 | 4087200 | 24028.9678
August | 57322.09 | 100.0592 | 173.9528 | 0 | 0.0012 | 4126500 | 24481.7932
September | 76452.6194 | 132.353 | 228.0303 | 0 | 0.0016 | 5409170 | 32545.9858
October | 81250.0866 | 137.2536 | 230.0264 | 0 | 0.0016 | 5456010 | 34259.1662
November | 88909.6393 | 142.7368 | 224.7472 | 0 | 0.0016 | 5329630 | 36768.1096
December | 102152.9594 | 155.0852 | 225.9913 | 0 | 0.0016 | 5357580 | 41383.2871
Annual Sum or Average | 997645.2328 | 1634.284 | 2639.9409 | 0 | 0.0186 | 62609000 | 415726.9422
Minimum of Months | 56141.5184 | 98.5301 | 172.2927 | 0 | 0.0012 | 4087200 | 24028.9678
Maximum of Months | 107315.0846 | 161.2538 | 253.3487 | 0 | 0.0018 | 6009880 | 43313.2427
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 311722000000 | 216027.349 | 05-JAN-08:09 | 120876.129 | 75091.738 | 7803.214 | 0 | 0 | 7870 | 2498.47 | 0 | 0 | 0 | 0 | 0 | 1887.798 | 0 | 0
February | 280226000000 | 228933.18 | 02-FEB-14:00 | 120876.129 | 75091.738 | 11734.49 | 0 | 18859.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2371.479 | 0 | 0
March | 321823000000 | 245570.502 | 30-MAR-14:00 | 120876.129 | 73092.045 | 18594.209 | 0 | 30581.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2426.505 | 0 | 0
April | 291413000000 | 233710.245 | 06-APR-14:00 | 120876.129 | 73092.045 | 14438.464 | 0 | 22915.638 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2387.965 | 0 | 0
May | 319800000000 | 274651.711 | 16-MAY-14:00 | 120876.129 | 73092.045 | 24511.407 | 0 | 53642.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2529.201 | 0 | 0
June | 341556000000 | 331838.382 | 30-JUN-14:00 | 120876.129 | 73092.045 | 35167.063 | 0 | 99975.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2727.477 | 0 | 0
July | 232285000000 | 232848.285 | 21-JUL-15:00 | 67153.405 | 40636.785 | 30579.095 | 0 | 92030.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2448.241 | 0 | 0
August | 234519000000 | 201648.89 | 09-AUG-15:00 | 67153.405 | 40636.785 | 15101.689 | 0 | 76337.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2419.352 | 0 | 0
September | 307416000000 | 298992.052 | 12-SEP-13:00 | 120876.129 | 75091.738 | 25510.798 | 0 | 74915.461 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2597.919 | 0 | 0
October | 310078000000 | 261551.835 | 06-OCT-14:00 | 120876.129 | 73092.045 | 22154.472 | 0 | 42937.434 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2491.754 | 0 | 0
November | 302896000000 | 217797.91 | 21-NOV-11:50 | 120876.129 | 79091.122 | 8608.355 | 0 | 5888.633 | 0 | 0.625 | 0 | 0 | 0 | 0 | 0 | 3333.046 | 0 | 0
December | 304484000000 | 215597.271 | 18-DEC-08:09 | 120876.129 | 75091.738 | 7803.214 | 0 | 0 | 7870 | 2065.128 | 0 | 0 | 0 | 0 | 0 | 1891.063 | 0 | 0
Annual Sum or Average | 3558220000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 232285000000 | 201648.89 |  | 67153.405 | 40636.785 | 7803.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1887.798 | 0 | 0
Maximum of Months | 341556000000 | 331838.382 |  | 120876.129 | 79091.122 | 35167.063 | 0 | 99975.668 | 7870 | 2498.47 | 0 | 0 | 0 | 0 | 0 | 3333.046 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 74748.98 | 24647.11 | 0 | 99396.1
Cost per Total Building Area ($/m2) | 10.88 | 3.59 | 0 | 14.47
Cost per Net Conditioned Building Area ($/m2) | 10.88 | 3.59 | 0 | 14.47

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7989.38 | 1162.77 | 1162.77
Net Site Energy | 7989.38 | 1162.77 | 1162.77
Total Source Energy | 17018.04 | 2476.79 | 2476.79
Net Source Energy | 17018.04 | 2476.79 | 2476.79
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4036.52 | 0 | 0 | 0 | 0
Cooling | 115.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 123.46 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 146.75 | 0 | 0 | 0 | 0 | 0
Pumps | 6.29 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 181.79 | 0 | 0 | 0 | 971.75
Refrigeration | 64.12 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3536.73 | 4452.65 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.525 | 0.407 | 0.316 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 324.79 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 554.39 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 515995.06 | 0.74
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12901.31 | 8722.36 | 4178.95 | 0.68 | 3.32
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 3.3
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.1
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 130260.27 | 89340.79 | 40919.48 | 0.69 | 3.35
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 125711.06 | 85253.25 | 40457.81 | 0.68 | 3.32
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 100096.81 | 67673.78 | 32423.04 | 0.68 | 3.33
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 99460.85 | 67423.39 | 32037.46 | 0.68 | 3.33
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6347.81 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6000.74 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7107.61 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7009.65 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7020.05 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6458.7 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6464.56 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6557.87 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5395.56 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5350.67 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5434.36 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13713.07 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6931.97 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11371.7 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4544.42 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18110.19 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18105.2 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18028.81 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17991.8 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17996.51 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11895.85 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14764.44 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 41205.42 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 85028.19 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 179735.84 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 59149.53 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 55360.19 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 43708.43 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 43750.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 602.61 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.45 | 10233.37 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.11 | 9577.78 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.03 | 7688.66 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.03 | 7696.09 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2841.29 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 116508.7568 | 168.6921 | 205.4684 | 0 | 0.0016 | 134901.7354 | 46339.7658
February | 100198.1428 | 147.5083 | 184.6235 | 0 | 0.0014 | 121231.0847 | 40084.9269
March | 101406.2264 | 156.5324 | 210.4425 | 0 | 0.0016 | 138228.2122 | 41260.8153
April | 78141.3783 | 129.4526 | 190.9215 | 0 | 0.0014 | 125452.8651 | 32638.9087
May | 76553.4535 | 132.4224 | 205.2776 | 0 | 0.0015 | 134911.4425 | 32510.9735
June | 76398.3677 | 136.636 | 219.4554 | 0 | 0.0016 | 144247.7541 | 32873.5181
July | 53474.6081 | 96.1389 | 155.2389 | 0 | 0.0011 | 102040.2486 | 23057.5519
August | 53705.4988 | 95.4303 | 152.2501 | 0 | 0.0011 | 100071.4052 | 23049.6941
September | 70581.6173 | 123.8884 | 195.1126 | 0 | 0.0014 | 128238.2565 | 30146.5196
October | 78889.5536 | 133.1254 | 200.6726 | 0 | 0.0015 | 131871.2611 | 33184.0039
November | 91873.5883 | 144.4987 | 199.3897 | 0 | 0.0015 | 130982.5264 | 37638.3833
December | 109503.5383 | 160.9778 | 201.022 | 0 | 0.0016 | 131997.6417 | 43785.6704
Annual Sum or Average | 1007230 | 1625.3031 | 2319.8748 | 0 | 0.0174 | 1524170 | 416570.7315
Minimum of Months | 53474.6081 | 95.4303 | 152.2501 | 0 | 0.0011 | 100071.4052 | 23049.6941
Maximum of Months | 116508.7568 | 168.6921 | 219.4554 | 0 | 0.0016 | 144247.7541 | 46339.7658
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 313029000000 | 213444.058 | 09-JAN-11:09 | 120876.129 | 79091.122 | 7518.414 | 0 | 0 | 0 | 2555.43 | 0 | 0 | 0 | 0 | 0 | 3402.962 | 0 | 0
February | 281308000000 | 213264.027 | 01-FEB-11:09 | 120876.129 | 79091.122 | 7518.414 | 0 | 0 | 0 | 2370.489 | 0 | 0 | 0 | 0 | 0 | 3407.873 | 0 | 0
March | 320748000000 | 211627.865 | 07-MAR-11:09 | 120876.129 | 79091.122 | 7518.414 | 0 | 0 | 0 | 721.975 | 0 | 0 | 0 | 0 | 0 | 3420.225 | 0 | 0
April | 291104000000 | 230090.768 | 04-APR-14:00 | 120876.129 | 73092.045 | 12807.606 | 0 | 20987.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2327.61 | 0 | 0
May | 313052000000 | 269489.174 | 31-MAY-14:00 | 120876.129 | 73092.045 | 21609.078 | 0 | 51418.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2493.385 | 0 | 0
June | 334716000000 | 356127.867 | 14-JUN-14:00 | 120876.129 | 73092.045 | 27617.601 | 0 | 131922.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2619.885 | 0 | 0
July | 236777000000 | 245762.169 | 06-JUL-15:00 | 67153.405 | 40636.785 | 15557.745 | 0 | 119974.022 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2440.208 | 0 | 0
August | 232208000000 | 225378.213 | 11-AUG-15:39 | 67153.405 | 40636.785 | 11758.15 | 0 | 103420.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2409.866 | 0 | 0
September | 297567000000 | 321806.786 | 07-SEP-14:00 | 120876.129 | 73092.045 | 23029.766 | 0 | 102237.472 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2571.371 | 0 | 0
October | 305997000000 | 237726.525 | 06-OCT-14:00 | 120876.129 | 73092.045 | 15589.432 | 0 | 25819.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2348.995 | 0 | 0
November | 303935000000 | 212429.477 | 09-NOV-11:50 | 120876.129 | 79091.122 | 7605.984 | 0 | 1576.558 | 0 | 1.313 | 0 | 0 | 0 | 0 | 0 | 3278.37 | 0 | 0
December | 306291000000 | 212137.536 | 20-DEC-16:00 | 120876.129 | 73092.045 | 7518.414 | 0 | 0 | 7870 | 937.121 | 0 | 0 | 0 | 0 | 0 | 1843.826 | 0 | 0
Annual Sum or Average | 3536730000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 232208000000 | 211627.865 |  | 67153.405 | 40636.785 | 7518.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1843.826 | 0 | 0
Maximum of Months | 334716000000 | 356127.867 |  | 120876.129 | 79091.122 | 27617.601 | 0 | 131922.206 | 7870 | 2555.43 | 0 | 0 | 0 | 0 | 0 | 3420.225 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 58521 | 35080.96 | 0 | 93601.96
Cost per Total Building Area ($/m2) | 8.52 | 5.11 | 0 | 13.62
Cost per Net Conditioned Building Area ($/m2) | 8.52 | 5.11 | 0 | 13.62

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11795.58 | 1716.72 | 1716.72
Net Site Energy | 11795.58 | 1716.72 | 1716.72
Total Source Energy | 21593.51 | 3142.7 | 3142.7
Net Source Energy | 21593.51 | 3142.7 | 3142.7
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7842.59 | 0 | 0 | 0 | 0
Cooling | 57.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1850.87 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 122.7 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 174.31 | 0 | 0 | 0 | 0 | 0
Pumps | 15.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 205.45 | 0 | 0 | 0 | 971.75
Refrigeration | 62.03 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3513.2 | 8282.38 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 21.52 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 21.52 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 23.8 | 11.47 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 17.2 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 22.75 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 12.26 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 21.52 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 8.26 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 21.52 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 20.33 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 879.18 | 19.5469 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-NONRES-FIXED | 14 | 14 | 3.525 | 0.407 | 0.316 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 11.2 | 11.2 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 26.6 | 26.6 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 49 | 49 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 29.4 | 29.4 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 879.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 324.79 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 554.39 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 811935.77 | 0.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9844.59 | 7862.43 | 1982.16 | 0.8 | 3.63
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17746.6 | 14173.41 | 3573.18 | 0.8 | 3.61
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37513.44 | 29960.31 | 7553.13 | 0.8 | 3.56
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 121287.98 | 96867.28 | 24420.7 | 0.8 | 3.89
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 109656.67 | 87577.87 | 22078.79 | 0.8 | 3.89
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 86845.89 | 69359.93 | 17485.96 | 0.8 | 3.89
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 86896.2 | 69400.11 | 17496.09 | 0.8 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8814.82 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8090.82 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8328.25 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8317.34 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8317.1 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8304.54 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8305.56 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8314.02 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6670 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6670.01 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6646.12 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18431.26 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9134.66 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17269.16 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6956.07 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24225.21 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24226.14 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24149.01 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24141.51 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24146.27 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15958.43 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19774.29 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 58409.9 | 0.78
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 105294.08 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 222574.67 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 98717.1 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 89250.29 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 70684.45 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 70725.4 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 689.81 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.33 | 13745.39 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.62 | 12427.23 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.25 | 9842.12 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.25 | 9847.82 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4470.86 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 143171.1246 | 151.6833 | 454.7788 | 0 | 0.0017 | 91194.5388 | 52893.7515
February | 124592.0765 | 132.5288 | 406.8326 | 0 | 0.0015 | 81583.7088 | 46111.2511
March | 117467.3571 | 128.6483 | 460.937 | 0 | 0.0017 | 92457.9615 | 44043.4999
April | 83707.4122 | 95.7793 | 414.3315 | 0 | 0.0015 | 83132.1041 | 32017.0636
May | 68982.8515 | 83.5176 | 437.4005 | 0 | 0.0015 | 87780.7324 | 27090.8798
June | 66710.1151 | 82.2016 | 453.0243 | 0 | 0.0015 | 90921.1394 | 26419.2545
July | 44531.4805 | 54.7923 | 300.7297 | 0 | 0.001 | 60355.6418 | 17623.4705
August | 48127.8102 | 58.2841 | 305.4929 | 0 | 0.001 | 61308.6117 | 18903.1225
September | 68125.0754 | 81.2866 | 407.0133 | 0 | 0.0014 | 81678.3553 | 26570.5066
October | 94521.8627 | 106.8284 | 440.1403 | 0 | 0.0016 | 88304.6533 | 35949.5626
November | 124139.6299 | 133.8255 | 442.5537 | 0 | 0.0016 | 88758.7712 | 46217.4174
December | 135319.6716 | 144.1685 | 446.6481 | 0 | 0.0017 | 89569.5976 | 50116.7183
Annual Sum or Average | 1119400 | 1253.5444 | 4969.8828 | 0 | 0.0177 | 997045.816 | 423956.4983
Minimum of Months | 44531.4805 | 54.7923 | 300.7297 | 0 | 0.001 | 60355.6418 | 17623.4705
Maximum of Months | 143171.1246 | 151.6833 | 460.937 | 0 | 0.0017 | 92457.9615 | 52893.7515
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 321334000000 | 223873.001 | 02-JAN-11:09 | 120876.129 | 79091.122 | 8442.558 | 0 | 0 | 7870 | 4216.118 | 0 | 0 | 0 | 0 | 0 | 3377.074 | 0 | 0
February | 287469000000 | 218515.546 | 03-FEB-08:30 | 120876.129 | 75091.738 | 8442.558 | 0 | 0 | 7870 | 4341.22 | 0 | 0 | 0 | 0 | 0 | 1893.901 | 0 | 0
March | 325786000000 | 218052.914 | 14-MAR-07:10 | 120876.129 | 75091.738 | 8442.558 | 0 | 0 | 7870 | 3894.965 | 0 | 0 | 0 | 0 | 0 | 1877.525 | 0 | 0
April | 292925000000 | 212314.685 | 10-APR-10:09 | 120876.129 | 79091.122 | 8442.558 | 0 | 0 | 0 | 492.314 | 0 | 0 | 0 | 0 | 0 | 3412.561 | 0 | 0
May | 309305000000 | 242801.656 | 24-MAY-14:00 | 120876.129 | 73092.045 | 15872.471 | 0 | 30567.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2393.895 | 0 | 0
June | 320370000000 | 281767.167 | 21-JUN-14:00 | 120876.129 | 73092.045 | 18240.61 | 0 | 66990.824 | 0 | 0.015 | 0 | 0 | 0 | 0 | 0 | 2567.545 | 0 | 0
July | 212670000000 | 164525.12 | 21-JUL-15:00 | 67153.405 | 40636.785 | 9436.553 | 0 | 44985.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2312.609 | 0 | 0
August | 216028000000 | 165025.555 | 15-AUG-13:00 | 67153.405 | 41836.601 | 9711.027 | 0 | 43899.574 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2424.947 | 0 | 0
September | 287803000000 | 219345.322 | 07-SEP-14:00 | 120876.129 | 73092.045 | 10435.48 | 0 | 12664.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2277.224 | 0 | 0
October | 311151000000 | 215922.402 | 27-OCT-07:30 | 120876.129 | 75091.738 | 8442.558 | 0 | 0 | 7870 | 1721.852 | 0 | 0 | 0 | 0 | 0 | 1920.125 | 0 | 0
November | 312751000000 | 219583.38 | 30-NOV-10:09 | 120876.129 | 79091.122 | 8442.558 | 0 | 0 | 7870 | 1371.532 | 0 | 0 | 0 | 0 | 0 | 1932.039 | 0 | 0
December | 315608000000 | 223850.306 | 29-DEC-11:09 | 120876.129 | 79091.122 | 8442.558 | 0 | 0 | 7870 | 4190.401 | 0 | 0 | 0 | 0 | 0 | 3380.095 | 0 | 0
Annual Sum or Average | 3513200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 212670000000 | 164525.12 |  | 67153.405 | 40636.785 | 8442.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1877.525 | 0 | 0
Maximum of Months | 325786000000 | 281767.167 |  | 120876.129 | 79091.122 | 18240.61 | 0 | 66990.824 | 7870 | 4341.22 | 0 | 0 | 0 | 0 | 0 | 3412.561 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 92050.33 | 34160.3 | 0 | 126210.63
Cost per Total Building Area ($/m2) | 13.4 | 4.97 | 0 | 18.37
Cost per Net Conditioned Building Area ($/m2) | 13.4 | 4.97 | 0 | 18.37

## Picture
DOE Commercial Building Benchmark - Primary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75 | 1444.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75 | 2395.71
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 2607.14
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720