## BuildingSummary
Building Summary Small Office pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Small Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 511 | 2003 CBECS, ASHRAE Small Office 30% Advanced Energy Design Guide
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.244
| East | 0.198
| North | 0.198
| West | 0.198
| Total | 0.212
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones
| Floor to Ceiling Height (m) | 3.05
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 281.5
| Net Dimensions - Total Area (m2) | 222
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 598.76
| Net Dimensions - Total Area (m2) | 598.76
| Roof to Skin Ratio | 0.64
Window Dimensions (m2)
| South | 16.73
| East | 11.16
| North | 16.73
| West | 11.16
| Total Area (m2) | 55.78
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab w/carpet
| Dimensions - Total Area (m2) | 511
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 0
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.46
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.68 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 17.63

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 19.4827 | 8.0729 |  | 11.3562 | 10 |  | 80.5463 |  | 0
Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 20.64 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 16.73 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 13.1393 | 13.3043 | 12.3848 | 12.6586 | 10.2673 | 10.9939 | 8.1214 | 11.7237 | 11.112 | 8.5654 | 10.5908 | 9.7182 | 8.715 | 8.2954 | 7.7539 | 5.7729
| PSZ-AC:2_COOLC DXCOIL | 14.8178 | 16.0747 | 16.7329 | 16.0058 | 14.4752 | 15.8565 | 16.3677 | 16.0206 | 13.6513 | 16.1492 | 19.1775 | 16.3867 | 21.15 | 19.3721 | 21.1378 | 25.3559
| PSZ-AC:3_COOLC DXCOIL | 11.4665 | 11.2532 | 11.1834 | 10.8682 | 8.8845 | 10.2973 | 6.8764 | 9.8331 | 8.8887 | 7.6841 | 11.1478 | 10.1955 | 12.2531 | 12.0495 | 12.502 | 15.745
| PSZ-AC:4_COOLC DXCOIL | 14.4542 | 14.3172 | 14.1882 | 13.5919 | 9.4996 | 12.4047 | 7.3982 | 14.85 | 13.0094 | 10.1012 | 19.679 | 16.1738 | 21.9318 | 19.0613 | 22.0229 | 25.001
| PSZ-AC:5_COOLC DXCOIL | 14.476 | 14.8262 | 15.3618 | 14.5709 | 12.8436 | 15.2957 | 11.2313 | 13.1995 | 14.3612 | 11.5151 | 10.7939 | 10.9267 | 11.6605 | 12.0341 | 12.1167 | 15.745
Heating (kW)
| PSZ-AC:1_HEATC | 16.9093 | 18.0644 | 16.6199 | 18.0832 | 15.6056 | 15.9858 | 13.008 | 17.0756 | 15.0981 | 14.1761 | 16.1575 | 14.2492 | 16.0237 | 14.0709 | 14.4849 | 13.9773
| PSZ-AC:2_HEATC | 18.1048 | 20.777 | 22.5419 | 21.8268 | 21.0941 | 21.9055 | 24.0442 | 22.2339 | 17.4282 | 23.981 | 24.944 | 21.1038 | 27.8568 | 26.4481 | 29.2898 | 39.3094
| PSZ-AC:3_HEATC | 15.2664 | 15.4839 | 15.6871 | 15.4779 | 12.9253 | 14.1387 | 10.329 | 14.1757 | 11.2426 | 11.6288 | 15.4508 | 13.0611 | 17.2336 | 16.3621 | 18.1076 | 24.2823
| PSZ-AC:4_HEATC | 17.868 | 18.6142 | 18.7258 | 18.1158 | 13.7429 | 17.474 | 11.588 | 20.0139 | 16.6944 | 15.6951 | 24.6393 | 20.8608 | 27.4711 | 26.0734 | 28.8759 | 38.8239
| PSZ-AC:5_HEATC | 19.9931 | 21.0549 | 21.2636 | 20.705 | 18.4049 | 20.5558 | 16.3769 | 19.3548 | 17.4987 | 16.8774 | 15.768 | 13.8956 | 17.2126 | 16.3436 | 18.087 | 24.2823
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.49 | 3.49 | 3.53 | 3.54 | 3.63 | 3.62 | 3.63 | 3.49 | 3.63 | 3.63 | 3.48 | 3.63 | 3.61 | 3.63 | 3.59 | 3.63
| PSZ-AC:2_COOLC DXCOIL | 3.46 | 3.49 | 3.56 | 3.54 | 3.63 | 3.61 | 3.61 | 3.53 | 3.63 | 3.61 | 3.45 | 3.61 | 3.46 | 3.6 | 3.52 | 3.6
| PSZ-AC:3_COOLC DXCOIL | 3.55 | 3.56 | 3.63 | 3.61 | 3.63 | 3.63 | 3.63 | 3.57 | 3.63 | 3.63 | 3.53 | 3.63 | 3.55 | 3.63 | 3.6 | 3.61
| PSZ-AC:4_COOLC DXCOIL | 3.47 | 3.48 | 3.55 | 3.51 | 3.59 | 3.63 | 3.63 | 3.49 | 3.63 | 3.63 | 3.42 | 3.61 | 3.42 | 3.61 | 3.47 | 3.6
| PSZ-AC:5_COOLC DXCOIL | 3.59 | 3.6 | 3.61 | 3.61 | 3.63 | 3.61 | 3.63 | 3.61 | 3.63 | 3.63 | 3.58 | 3.63 | 3.6 | 3.63 | 3.63 | 3.61
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC:1 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC:1_FAN | 0.68 | 0.69 | 0.68 | 0.7 | 0.62 | 0.66 | 0.49 | 0.61 | 0.67 | 0.52 | 0.54 | 0.59 | 0.52 | 0.5 | 0.45 | 0.35
| PSZ-AC:2_FAN | 0.75 | 0.83 | 0.96 | 0.89 | 0.87 | 0.96 | 0.99 | 0.87 | 0.82 | 0.98 | 0.97 | 0.99 | 1.1 | 1.17 | 1.18 | 1.53
| PSZ-AC:3_FAN | 0.64 | 0.63 | 0.68 | 0.64 | 0.54 | 0.62 | 0.42 | 0.56 | 0.54 | 0.46 | 0.61 | 0.62 | 0.68 | 0.73 | 0.73 | 0.95
| PSZ-AC:4_FAN | 0.74 | 0.74 | 0.79 | 0.73 | 0.55 | 0.75 | 0.45 | 0.77 | 0.79 | 0.61 | 0.96 | 0.98 | 1.08 | 1.15 | 1.16 | 1.51
| PSZ-AC:5_FAN | 0.84 | 0.87 | 0.93 | 0.88 | 0.78 | 0.92 | 0.68 | 0.78 | 0.87 | 0.7 | 0.62 | 0.66 | 0.68 | 0.73 | 0.73 | 0.95
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.084628 | 0.12517 | 0.12104 | 0.11485 | 0.14321 | 0.1026 | 0.16044 | 0.073854 | 0.074898 | 0.072925 | 0.060476 | 0.07494 | 0.074527 | 0.077553 | 0.074262 | 0.098978
| Total Cost ($/m2) | 17.49 | 24.32 | 24.79 | 20.73 | 23.21 | 19.73 | 23.95 | 12.69 | 12.99 | 11.16 | 10.14 | 12.42 | 12.7 | 13.01 | 12.51 | 18.21
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011455 | 0.0080868 | 0.0082488 | 0.0096101 | 0.0085796 | 0.0076961 | 0.0086107 | 0.0096788 | 0.0068812 | 0.0084357 | 0.0082974 | 0.0068973 | 0.0078968 | 0.0080281 | 0.0078708 | 0.0041105
| Total Cost ($/m2) | 0.28 | 0.83 | 0.65 | 1.93 | 0.49 | 1.04 | 1.21 | 3.35 | 1.75 | 2.39 | 3.73 | 2.4 | 4.7 | 3.79 | 5.9 | 5.45
Total Utility Costs
| Cost Intensity ($/m2) | 17.77 | 25.16 | 25.44 | 22.66 | 23.7 | 20.77 | 25.16 | 16.04 | 14.75 | 13.55 | 13.86 | 14.82 | 17.4 | 16.8 | 18.41 | 23.66
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 33708.3333 | 25430.5556 | 28961.1111 | 16919.4444 | 12425 | 22327.7778 | 6438.8889 | 12319.4444 | 12919.4444 | 4738.8889 | 8791.6667 | 7252.7778 | 7561.1111 | 4277.7778 | 3627.7778 | 2402.7778
| Interior Lighting | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111
| Exterior Lighting | 5083.3333 | 5080.5556 | 5080.5556 | 5080.5556 | 5075 | 5075 | 5077.7778 | 5075 | 5075 | 5066.6667 | 5075 | 5072.2222 | 5072.2222 | 5069.4444 | 5066.6667 | 5036.1111
| Interior Equipment | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 20091.6667 | 22041.6667 | 23847.2222 | 23477.7778 | 18563.8889 | 24113.8889 | 18005.5556 | 23658.3333 | 23902.7778 | 21666.6667 | 25044.4444 | 25613.8889 | 27683.3333 | 29633.3333 | 30655.5556 | 39800
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 105669.4444 | 99338.8889 | 104675 | 92263.8889 | 82852.7778 | 98302.7778 | 76308.3333 | 87838.8889 | 88686.1111 | 78255.5556 | 85700 | 84727.7778 | 87100 | 85766.6667 | 86136.1111 | 94025
Gas (MJ)
| Heating | 1720 | 41670 | 29410 | 91040 | 17930 | 57760 | 59850 | 165270 | 118370 | 132760 | 217440 | 165960 | 291820 | 229020 | 370230 | 664520
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10690 | 11090 | 10860 | 11470 | 11400 | 11130 | 11730 | 11770 | 11720 | 11930 | 12040 | 12020 | 12270 | 12310 | 12650 | 13100
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 12420 | 52760 | 40270 | 102520 | 29330 | 68900 | 71570 | 177040 | 130090 | 144690 | 229480 | 177990 | 304090 | 241330 | 382880 | 677620
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 392830 | 410380 | 417110 | 434670 | 327590 | 422780 | 346290 | 493260 | 449360 | 426410 | 538000 | 483000 | 617650 | 550090 | 692970 | 1016110
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 237.4012 | 179.1024 | 203.9674 | 119.1603 | 87.5068 | 157.2502 | 45.3478 | 86.7634 | 90.9891 | 33.3751 | 61.918 | 51.0799 | 53.2514 | 30.1276 | 25.5497 | 16.9223
| Interior Lighting (elec) | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982
| Exterior Lighting (elec) | 35.8009 | 35.7814 | 35.7814 | 35.7814 | 35.7422 | 35.7422 | 35.7618 | 35.7422 | 35.7422 | 35.6835 | 35.7422 | 35.7227 | 35.7227 | 35.7031 | 35.6835 | 35.4683
| Interior Equipment (elec) | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 141.5017 | 155.2352 | 167.9513 | 165.3494 | 130.7418 | 169.8294 | 126.8096 | 166.621 | 168.3426 | 152.5941 | 176.3831 | 180.3936 | 194.9683 | 208.7018 | 215.9011 | 280.3036
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 744.2092 | 699.6244 | 737.2056 | 649.7965 | 583.5159 | 692.3273 | 537.4247 | 618.6321 | 624.599 | 551.1386 | 603.5684 | 596.7212 | 613.4283 | 604.0379 | 606.6398 | 662.1997
Gas (MJ/m2)
| Heating (gas) | 3.3649 | 81.5205 | 57.5358 | 178.1047 | 35.0771 | 112.9979 | 117.0866 | 323.3234 | 231.5713 | 259.723 | 425.3854 | 324.6733 | 570.8976 | 448.0398 | 724.2938 | 1300.0235
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.9132 | 21.6958 | 21.2458 | 22.4392 | 22.3022 | 21.774 | 22.9478 | 23.0261 | 22.9282 | 23.3391 | 23.5543 | 23.5151 | 24.0042 | 24.0825 | 24.7476 | 25.628
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 24.2977 | 103.2162 | 78.7816 | 200.5634 | 57.3793 | 134.7915 | 140.0149 | 346.3495 | 254.4996 | 283.0621 | 448.9397 | 348.208 | 594.9018 | 472.1222 | 749.0414 | 1325.6515
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 768.5069 | 802.8406 | 816.0067 | 850.36 | 640.8757 | 827.0991 | 677.4591 | 964.9816 | 879.0985 | 834.2006 | 1052.508 | 944.9096 | 1208.3301 | 1076.1601 | 1355.6812 | 1987.8512
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 27.8707 | 25.833 | 24.4658 | 22.5558 | 23.3685 | 21.9354 | 19.6337 | 18.4948 | 20.6579 | 17.6236 | 18.0973 | 19.1907 | 18.4993 | 18.7509 | 18.7245 | 19.8743
| Feb | 28.6027 | 27.097 | 25.9888 | 22.3163 | 22.8491 | 23.4127 | 21.8787 | 18.3679 | 22.4534 | 18.5635 | 18.0973 | 19.2879 | 17.4138 | 18.5217 | 17.7651 | 19.8743
| Mar | 29.2987 | 25.9867 | 29.1743 | 25.291 | 23.6961 | 24.3801 | 20.7434 | 23.0582 | 22.5809 | 21.0971 | 20.6554 | 21.8196 | 19.6595 | 20.6151 | 17.9923 | 19.8743
| Apr | 30.2734 | 28.7564 | 29.5634 | 26.9598 | 24.8046 | 28.8021 | 22.826 | 24.0123 | 24.8976 | 20.6745 | 21.8167 | 22.9263 | 21.3948 | 19.7212 | 20.0658 | 20.1158
| May | 31.7982 | 32.4352 | 32.6612 | 29.5258 | 24.6421 | 30.7834 | 22.9776 | 26.6778 | 26.6577 | 23.5196 | 25.3408 | 24.3965 | 25.1248 | 22.9622 | 22.6898 | 22.9611
| Jun | 32.6471 | 32.733 | 38.4086 | 31.4567 | 24.7155 | 36.1769 | 23.2419 | 31.4052 | 29.1719 | 24.2153 | 29.502 | 26.3924 | 29.1286 | 27.205 | 25.9509 | 25.2086
| Jul | 31.9675 | 33.7029 | 37.9294 | 33.9982 | 25.92 | 35.4104 | 24.9576 | 32.182 | 30.0614 | 26.0219 | 30.3962 | 27.771 | 28.7972 | 27.1104 | 27.7815 | 25.1866
| Aug | 33.016 | 33.4958 | 38.2027 | 31.8786 | 27.1922 | 34.6362 | 23.9982 | 32.5334 | 30.1442 | 25.4065 | 29.7333 | 27.8655 | 28.9951 | 25.9551 | 26.6815 | 24.7994
| Sep | 31.9811 | 32.1379 | 35.2655 | 30.3911 | 27.0885 | 33.4993 | 27.165 | 29.1919 | 27.0475 | 25.3098 | 26.623 | 25.1882 | 25.9295 | 24.5253 | 24.2812 | 21.1106
| Oct | 31.3188 | 30.0665 | 29.977 | 28.0959 | 25.7003 | 28.8301 | 23.2155 | 26.0506 | 24.7932 | 21.382 | 22.8919 | 23.9994 | 21.6915 | 22.2372 | 20.3912 | 19.8743
| Nov | 29.5593 | 27.3426 | 27.5929 | 23.4638 | 24.0152 | 23.4316 | 20.4955 | 23.8595 | 21.8903 | 17.7442 | 22.4475 | 20.6824 | 20.4802 | 19 | 18.7245 | 19.8743
| Dec | 27.8645 | 26.2991 | 23.8401 | 21.7711 | 23.5962 | 22.4446 | 19.4855 | 18.0276 | 19.9743 | 17.6018 | 18.0973 | 19.125 | 18.4993 | 18.7509 | 18.7245 | 19.8743
Time of Peak Electrical Demand
| Jan | 23-JAN-15:30 | 03-JAN-14:30 | 26-JAN-15:30 | 23-JAN-15:00 | 26-JAN-13:00 | 18-JAN-14:50 | 27-JAN-15:20 | 05-JAN-14:00 | 25-JAN-15:30 | 02-JAN-16:40 | 02-JAN-16:30 | 24-JAN-15:09 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-13:00 | 23-FEB-14:00 | 28-FEB-15:50 | 27-FEB-15:50 | 13-FEB-14:30 | 27-FEB-14:00 | 15-FEB-15:50 | 15-FEB-15:50 | 14-FEB-15:50 | 24-FEB-14:00 | 01-FEB-16:00 | 07-FEB-14:00 | 16-FEB-13:20 | 02-FEB-16:30 | 22-FEB-14:50 | 01-FEB-08:09
| Mar | 27-MAR-15:09 | 27-MAR-15:30 | 17-MAR-15:20 | 28-MAR-15:39 | 31-MAR-14:20 | 31-MAR-14:39 | 20-MAR-15:20 | 09-MAR-15:00 | 02-MAR-15:20 | 29-MAR-15:30 | 31-MAR-15:39 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 22-MAR-14:30 | 01-MAR-08:09
| Apr | 03-APR-14:30 | 17-APR-15:30 | 26-APR-15:30 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:30 | 18-APR-15:30 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:50 | 25-APR-15:00
| May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:30 | 15-MAY-14:00 | 30-MAY-14:09 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 15-MAY-15:20 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:00
| Jun | 27-JUN-15:09 | 13-JUN-15:20 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-14:09 | 27-JUN-15:00 | 15-JUN-13:00 | 30-JUN-15:50 | 29-JUN-15:20 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 21-JUN-15:00
| Jul | 03-JUL-15:20 | 31-JUL-14:30 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-13:09 | 25-JUL-13:30 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-14:50 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-14:50 | 04-AUG-14:00 | 14-AUG-13:50 | 17-AUG-14:00 | 01-AUG-14:30 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 08-AUG-15:00 | 11-AUG-15:39 | 15-AUG-15:00
| Sep | 11-SEP-14:00 | 15-SEP-14:39 | 11-SEP-15:30 | 11-SEP-13:50 | 25-SEP-14:39 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:50 | 01-SEP-15:30 | 05-SEP-14:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
| Oct | 06-OCT-15:20 | 12-OCT-14:00 | 13-OCT-15:20 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-14:50 | 13-OCT-14:50 | 12-OCT-14:00 | 13-OCT-14:39 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-15:09 | 06-OCT-14:00 | 06-OCT-15:00 | 06-OCT-14:00 | 03-OCT-07:10
| Nov | 07-NOV-14:00 | 01-NOV-14:00 | 13-NOV-15:09 | 22-NOV-14:00 | 20-NOV-13:50 | 10-NOV-14:09 | 08-NOV-14:39 | 03-NOV-14:09 | 01-NOV-14:39 | 14-NOV-16:40 | 02-NOV-14:50 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-16:49 | 06-NOV-16:49 | 01-NOV-07:10
| Dec | 19-DEC-14:30 | 19-DEC-15:20 | 13-DEC-14:39 | 01-DEC-15:09 | 19-DEC-13:09 | 05-DEC-14:30 | 07-DEC-14:00 | 12-DEC-16:49 | 05-DEC-14:00 | 01-DEC-16:19 | 01-DEC-16:19 | 21-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 1275.38 | 1356.5 | 1235.9 | 1229.3 | 955.16 | 1341.09 | 928.4 | 1324.13 | 1201.4 | 648.76 | 1344.59 | 1206.41 | 1409.78 | 1336.79 | 1483.89 | 1949.04
| Total Source Energy (MJ/m2) | 2495.08 | 2653.78 | 2417.85 | 2404.93 | 1868.62 | 2623.63 | 1816.26 | 2590.46 | 2350.36 | 1269.2 | 2630.48 | 2360.15 | 2758.01 | 2615.23 | 2903 | 3812.99
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
| Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
Emissions
| Carbon Equivalent (kg) | 29203.6795 | 34087.2623 | 32325.3458 | 30269.2849 | 10211.3486 | 34397.1761 | 10208.6106 | 26896.3878 | 38574.2117 | 8308.879 | 49828.5129 | 37820.3445 | 35297.4966 | 35694.5078 | 36388.3351 | 38676.4943
| CO2 (kg) | 67751.1223 | 85896.1512 | 76409.7928 | 69844.5668 | 27378.5817 | 82117.0199 | 27538.3939 | 62380.5644 | 91193.249 | 21077.9472 | 117375.9668 | 89919.5471 | 84575.9258 | 85472.2767 | 87920.1743 | 101579.6773
| NOX (kg) | 118.9327 | 111.7852 | 127.5036 | 129.4052 | 23.5095 | 132.0383 | 23.7609 | 114.6558 | 154.2635 | 28.5984 | 202.8134 | 149.916 | 139.8083 | 140.8175 | 142.1471 | 115.0821
| SO2 (kg) | 452.3104 | 473.8649 | 420.9343 | 323.8737 | 241.0964 | 540.7578 | 222.0698 | 320.6948 | 387.3115 | 60.5244 | 577.6046 | 370.0329 | 205.6529 | 229.0742 | 203.3992 | 478.8004
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0021 | 0.0013 | 0.0011 | 0.0012 | 0.0001 | 0.001 | 0.0001 | 0.0013 | 0.0015 | 0.0003 | 0.0018 | 0.0015 | 0.0015 | 0.0016 | 0.0015 | 0.0017
| Water for Electricity (m3) | 55.9792 | 161.6375 | 3109.34 | 576.0586 | 1454.69 | 2696.82 | 1339.82 | 19.9427 | 402.708 | 799.5259 | 132.957 | 384.7276 | 135.1314 | 5432.87 | 133.6361 | 96.0622

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 392.83 | 768.5 | 768.5
Net Site Energy | 392.83 | 768.5 | 768.5
Total Source Energy | 1275.38 | 2495.08 | 2495.08
Net Source Energy | 1275.38 | 2495.08 | 2495.08
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1.72 | 0 | 0 | 0 | 0
Cooling | 121.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 72.33 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.69 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 380.41 | 12.42 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13139.29 | 9804.42 | 3334.87 | 0.75 | 3.49
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14817.83 | 10924.9 | 3892.93 | 0.74 | 3.46
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11466.47 | 8832.47 | 2634 | 0.77 | 3.55
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14454.23 | 10705.51 | 3748.73 | 0.74 | 3.47
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14475.99 | 11380.79 | 3095.2 | 0.79 | 3.59
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16909.33 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 18104.82 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 15266.35 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 17868.01 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 19993.09 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 789.29 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 864.96 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.64 | 741.46 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 853.01 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.84 | 979.93 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5019.9074 | 8.775 | 33.2209 | 0 | 0.0002 | 4111.4774 | 2160.0768
February | 4674.5304 | 8.1952 | 31.1235 | 0 | 0.0001 | 3851.9188 | 2013.8569
March | 5548.9461 | 9.7296 | 36.9572 | 0 | 0.0002 | 4573.9116 | 2390.7177
April | 5403.0706 | 9.4887 | 36.1026 | 0 | 0.0002 | 4468.1598 | 2329.3579
May | 6062.6375 | 10.6518 | 40.547 | 0 | 0.0002 | 5018.2183 | 2614.1834
June | 6274.1978 | 11.0265 | 41.9855 | 0 | 0.0002 | 5196.2481 | 2705.707
July | 6229.8622 | 10.9476 | 41.6812 | 0 | 0.0002 | 5158.5828 | 2686.4902
August | 6688.4217 | 11.7556 | 44.7666 | 0 | 0.0002 | 5540.4524 | 2884.4562
September | 5917.0544 | 10.3966 | 39.5781 | 0 | 0.0002 | 4898.3079 | 2551.4696
October | 5758.8921 | 10.1158 | 38.4972 | 0 | 0.0002 | 4764.5208 | 2482.9755
November | 5274.5064 | 9.2618 | 35.2342 | 0 | 0.0002 | 4360.6826 | 2273.8125
December | 4899.0958 | 8.5886 | 32.6165 | 0 | 0.0001 | 4036.701 | 2110.5758
Annual Sum or Average | 67751.1223 | 118.9327 | 452.3104 | 0 | 0.0021 | 55979.1816 | 29203.6795
Minimum of Months | 4674.5304 | 8.1952 | 31.1235 | 0 | 0.0001 | 3851.9188 | 2013.8569
Maximum of Months | 6688.4217 | 11.7556 | 44.7666 | 0 | 0.0002 | 5540.4524 | 2884.4562
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 27939800000 | 27870.719 | 23-JAN-15:30 | 8961.612 | 3712.536 | 4228.646 | 0 | 10967.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 26175900000 | 28602.743 | 22-FEB-13:00 | 8961.612 | 3712.536 | 4228.646 | 0 | 11699.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 31082300000 | 29298.738 | 27-MAR-15:09 | 8961.612 | 3712.536 | 4228.646 | 0 | 12395.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 30363600000 | 30273.379 | 03-APR-14:30 | 8961.612 | 3712.536 | 4228.646 | 0 | 13370.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 34101600000 | 31798.242 | 24-MAY-14:00 | 8961.612 | 3712.536 | 4228.646 | 0 | 14895.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 35311400000 | 32647.053 | 27-JUN-15:09 | 8961.612 | 3712.536 | 4228.646 | 0 | 15744.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 35055400000 | 31967.507 | 03-JUL-15:20 | 8961.612 | 3712.536 | 4228.646 | 0 | 15064.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 37650500000 | 33015.972 | 21-AUG-14:50 | 8961.612 | 3712.536 | 4228.646 | 0 | 16113.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 33286700000 | 31981.106 | 11-SEP-14:00 | 8961.612 | 3712.536 | 4228.646 | 0 | 15078.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 32377600000 | 31318.793 | 06-OCT-15:20 | 8961.612 | 3712.536 | 4228.646 | 0 | 14415.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 29633300000 | 29559.299 | 07-NOV-14:00 | 8961.612 | 3712.536 | 4228.646 | 0 | 12656.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 27431600000 | 27864.536 | 19-DEC-14:30 | 8961.612 | 3712.536 | 4228.646 | 0 | 10961.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 380410000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 26175900000 | 27864.536 |  | 8961.612 | 3712.536 | 4228.646 | 0 | 10961.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 37650500000 | 33015.972 |  | 8961.612 | 3712.536 | 4228.646 | 0 | 16113.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8942.63 | 142.27 | 0 | 9084.9
Cost per Total Building Area ($/m2) | 17.49 | 0.28 | 0 | 17.77
Cost per Net Conditioned Building Area ($/m2) | 17.49 | 0.28 | 0 | 17.77

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 410.38 | 802.85 | 802.85
Net Site Energy | 410.38 | 802.85 | 802.85
Total Source Energy | 1356.5 | 2653.78 | 2653.78
Net Source Energy | 1356.5 | 2653.78 | 2653.78
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 41.67 | 0 | 0 | 0 | 0
Cooling | 91.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 79.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.09 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 357.62 | 52.76 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13304.27 | 9930.63 | 3373.64 | 0.75 | 3.49
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16074.7 | 11988.51 | 4086.19 | 0.75 | 3.49
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11253.24 | 8690.73 | 2562.51 | 0.77 | 3.56
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14317.22 | 10656.68 | 3660.53 | 0.74 | 3.48
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14826.15 | 11710.05 | 3116.1 | 0.79 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 18064.43 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 20777.05 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 15483.85 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 18614.19 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 21054.9 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.69 | 799.79 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.83 | 964.43 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.63 | 731.96 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 854.96 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.87 | 1013.91 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6676.0863 | 8.4811 | 33.9284 | 0 | 0.0001 | 11572.2095 | 2622.6508
February | 5896.8895 | 7.512 | 30.2594 | 0 | 0.0001 | 10320.8878 | 2319.2266
March | 6576.7777 | 8.5513 | 36.1747 | 0 | 0.0001 | 12339.3226 | 2608.9568
April | 6410.8409 | 8.3953 | 36.0983 | 0 | 0.0001 | 12313.518 | 2550.8276
May | 7609.7466 | 9.9803 | 43.059 | 0 | 0.0001 | 14687.9488 | 3029.795
June | 8355.3648 | 10.9634 | 47.3515 | 0 | 0.0001 | 16152.1971 | 3327.3368
July | 8412.8291 | 11.0389 | 47.6776 | 0 | 0.0001 | 16263.4465 | 3350.225
August | 8836.871 | 11.5958 | 50.0879 | 0 | 0.0001 | 17085.6386 | 3519.1564
September | 7501.1281 | 9.8405 | 42.4819 | 0 | 0.0001 | 14491.1335 | 2986.8949
October | 6970.0064 | 9.132 | 39.3089 | 0 | 0.0001 | 13408.7036 | 2773.8864
November | 6240.0053 | 8.1338 | 34.6066 | 0 | 0.0001 | 11804.5394 | 2477.9783
December | 6409.6055 | 8.1609 | 32.8308 | 0 | 0.0001 | 11197.9137 | 2520.3277
Annual Sum or Average | 85896.1512 | 111.7852 | 473.8649 | 0 | 0.0013 | 161637.4592 | 34087.2623
Minimum of Months | 5896.8895 | 7.512 | 30.2594 | 0 | 0.0001 | 10320.8878 | 2319.2266
Maximum of Months | 8836.871 | 11.5958 | 50.0879 | 0 | 0.0001 | 17085.6386 | 3519.1564
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25603500000 | 25832.997 | 03-JAN-14:30 | 8961.612 | 3712.536 | 4365.054 | 0 | 8793.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22835000000 | 27096.97 | 23-FEB-14:00 | 8961.612 | 3712.536 | 4365.054 | 0 | 10057.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 27300800000 | 25986.746 | 27-MAR-15:30 | 8961.612 | 3712.536 | 4365.054 | 0 | 8947.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 27243700000 | 28756.417 | 17-APR-15:30 | 8961.612 | 3712.536 | 4365.054 | 0 | 11717.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 32497100000 | 32435.224 | 26-MAY-14:00 | 8961.612 | 3712.536 | 4365.054 | 0 | 15396.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 35736800000 | 32733.003 | 13-JUN-15:20 | 8961.612 | 3712.536 | 4365.054 | 0 | 15693.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 35982900000 | 33702.885 | 31-JUL-14:30 | 8961.612 | 3712.536 | 4365.054 | 0 | 16663.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 37802000000 | 33495.759 | 31-AUG-13:00 | 8961.612 | 3712.536 | 4365.054 | 0 | 16456.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 32061700000 | 32137.868 | 15-SEP-14:39 | 8961.612 | 3712.536 | 4365.054 | 0 | 15098.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 29666800000 | 30066.497 | 12-OCT-14:00 | 8961.612 | 3712.536 | 4365.054 | 0 | 13027.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 26117600000 | 27342.572 | 01-NOV-14:00 | 8961.612 | 3712.536 | 4365.054 | 0 | 10303.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24775400000 | 26299.054 | 19-DEC-15:20 | 8961.612 | 3712.536 | 4365.054 | 0 | 9259.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 357623000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22835000000 | 25832.997 |  | 8961.612 | 3712.536 | 4365.054 | 0 | 8793.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 37802000000 | 33702.885 |  | 8961.612 | 3712.536 | 4365.054 | 0 | 16663.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12433.83 | 426.66 | 0 | 12860.49
Cost per Total Building Area ($/m2) | 24.32 | 0.83 | 0 | 25.16
Cost per Net Conditioned Building Area ($/m2) | 24.32 | 0.83 | 0 | 25.16

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 417.11 | 816 | 816
Net Site Energy | 417.11 | 816 | 816
Total Source Energy | 1235.9 | 2417.85 | 2417.85
Net Source Energy | 1235.9 | 2417.85 | 2417.85
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 29.41 | 0 | 0 | 0 | 0
Cooling | 104.26 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 85.85 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.86 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 376.83 | 40.27 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12384.84 | 9451.13 | 2933.72 | 0.76 | 3.53
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16732.9 | 13068.02 | 3664.88 | 0.78 | 3.56
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11183.42 | 8931.7 | 2251.72 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14188.22 | 10920.01 | 3268.21 | 0.77 | 3.55
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15361.82 | 12268.8 | 3093.02 | 0.8 | 3.61
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16619.94 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 22541.89 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 15687.13 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 18725.82 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 21263.64 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 783.93 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.96 | 1096.17 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 783.62 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.79 | 915.74 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.93 | 1057.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5480.697 | 8.9174 | 28.5424 | 0 | 0.0001 | 210824.5609 | 2295.5541
February | 5033.9809 | 8.1966 | 26.2597 | 0 | 0.0001 | 193963.6008 | 2109.0602
March | 5888.5655 | 9.8326 | 32.4864 | 0 | 0.0001 | 239969.7406 | 2491.827
April | 5767.8153 | 9.6852 | 32.2124 | 0 | 0.0001 | 237948.4912 | 2446.2119
May | 6695.1491 | 11.2752 | 37.6292 | 0 | 0.0001 | 277962.7808 | 2842.8301
June | 7756.8505 | 13.0749 | 43.6806 | 0 | 0.0001 | 322664.8554 | 3294.8182
July | 7889.3419 | 13.2986 | 44.4299 | 0 | 0.0001 | 328199.4902 | 3351.1397
August | 8129.3588 | 13.7038 | 45.7857 | 0 | 0.0001 | 338214.9604 | 3453.1492
September | 6965.0939 | 11.7367 | 39.1959 | 0 | 0.0001 | 289536.0604 | 2958.1434
October | 6007.615 | 10.101 | 33.6469 | 0 | 0.0001 | 248545.5651 | 2549.2458
November | 5258.096 | 8.7721 | 28.9517 | 0 | 0.0001 | 213859.0784 | 2224.2452
December | 5537.2292 | 8.9094 | 28.1135 | 0 | 0.0001 | 207651.0953 | 2309.1211
Annual Sum or Average | 76409.7928 | 127.5036 | 420.9343 | 0 | 0.0011 | 3109340 | 32325.3458
Minimum of Months | 5033.9809 | 8.1966 | 26.2597 | 0 | 0.0001 | 193963.6008 | 2109.0602
Maximum of Months | 8129.3588 | 13.7038 | 45.7857 | 0 | 0.0001 | 338214.9604 | 3453.1492
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25550700000 | 24465.814 | 26-JAN-15:30 | 8961.612 | 3712.536 | 4636.646 | 0 | 7155.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 23507300000 | 25988.799 | 28-FEB-15:50 | 8961.612 | 3712.536 | 4636.646 | 0 | 8678.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 29082900000 | 29174.286 | 17-MAR-15:20 | 8961.612 | 3712.536 | 4636.646 | 0 | 11863.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 28838000000 | 29563.417 | 26-APR-15:30 | 8961.612 | 3712.536 | 4636.646 | 0 | 12252.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 33687500000 | 32661.181 | 30-MAY-15:30 | 8961.612 | 3712.536 | 4636.646 | 0 | 15350.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 39105100000 | 38408.603 | 28-JUN-15:00 | 8961.612 | 3712.536 | 4636.646 | 0 | 21097.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 39775900000 | 37929.397 | 11-JUL-15:00 | 8961.612 | 3712.536 | 4636.646 | 0 | 20618.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 40989700000 | 38202.734 | 01-AUG-15:00 | 8961.612 | 3712.536 | 4636.646 | 0 | 20891.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 35090100000 | 35265.533 | 11-SEP-15:30 | 8961.612 | 3712.536 | 4636.646 | 0 | 17954.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 30122300000 | 29976.998 | 13-OCT-15:20 | 8961.612 | 3712.536 | 4636.646 | 0 | 12666.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 25918500000 | 27592.909 | 13-NOV-15:09 | 8961.612 | 3712.536 | 4636.646 | 0 | 10282.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 25166100000 | 23840.143 | 13-DEC-14:39 | 8961.612 | 3712.536 | 4636.646 | 0 | 6529.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 376834000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 23507300000 | 23840.143 |  | 8961.612 | 3712.536 | 4636.646 | 0 | 6529.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 40989700000 | 38408.603 |  | 8961.612 | 3712.536 | 4636.646 | 0 | 21097.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12669.42 | 332.18 | 0 | 13001.6
Cost per Total Building Area ($/m2) | 24.79 | 0.65 | 0 | 25.44
Cost per Net Conditioned Building Area ($/m2) | 24.79 | 0.65 | 0 | 25.44

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 434.67 | 850.35 | 850.35
Net Site Energy | 434.67 | 850.35 | 850.35
Total Source Energy | 1229.3 | 2404.93 | 2404.93
Net Source Energy | 1229.3 | 2404.93 | 2404.93
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 91.04 | 0 | 0 | 0 | 0
Cooling | 60.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 84.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.47 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 332.15 | 102.52 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12658.59 | 9694.93 | 2963.66 | 0.77 | 3.54
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16005.84 | 12338.84 | 3667.01 | 0.77 | 3.54
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10868.18 | 8606.05 | 2262.14 | 0.79 | 3.61
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13591.88 | 10279.49 | 3312.39 | 0.76 | 3.51
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14570.92 | 11637.14 | 2933.78 | 0.8 | 3.61
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 18083.18 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 21826.78 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 15477.89 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 18115.83 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 20705.04 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.7 | 807.91 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.89 | 1018.33 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.64 | 747.45 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 842.66 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.88 | 1002.75 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6400.6207 | 10.8399 | 24.6852 | 0 | 0.0001 | 43896.469 | 2679.8034
February | 5447.8124 | 9.4274 | 21.9967 | 0 | 0.0001 | 39117.9707 | 2299.462
March | 5552.526 | 10.2577 | 25.6014 | 0 | 0.0001 | 45535.6542 | 2403.6061
April | 5201.2345 | 9.807 | 24.9536 | 0 | 0.0001 | 44385.4924 | 2269.849
May | 5721.1827 | 10.9854 | 28.4188 | 0 | 0.0001 | 50550.9034 | 2515.0439
June | 6315.7397 | 12.1458 | 31.4642 | 0 | 0.0001 | 55968.1518 | 2778.1465
July | 6336.0687 | 12.1849 | 31.5655 | 0 | 0.0001 | 56148.3869 | 2787.0896
August | 6728.3831 | 12.9418 | 33.5321 | 0 | 0.0001 | 59646.4882 | 2959.8874
September | 5812.0646 | 11.1728 | 28.9337 | 0 | 0.0001 | 51466.8724 | 2556.1909
October | 5175.8808 | 9.8322 | 25.1896 | 0 | 0.0001 | 44805.8567 | 2265.5212
November | 5240.1289 | 9.5683 | 23.6107 | 0 | 0.0001 | 41993.9477 | 2258.0078
December | 5912.9246 | 10.242 | 23.9222 | 0 | 0.0001 | 42542.4251 | 2496.6771
Annual Sum or Average | 69844.5668 | 129.4052 | 323.8737 | 0 | 0.0012 | 576058.6186 | 30269.2849
Minimum of Months | 5175.8808 | 9.4274 | 21.9967 | 0 | 0.0001 | 39117.9707 | 2258.0078
Maximum of Months | 6728.3831 | 12.9418 | 33.5321 | 0 | 0.0001 | 59646.4882 | 2959.8874
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25310300000 | 22555.8 | 23-JAN-15:00 | 8961.612 | 3712.536 | 4419.102 | 0 | 5462.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22555100000 | 22316.281 | 27-FEB-15:50 | 8961.612 | 3712.536 | 4419.102 | 0 | 5223.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26255400000 | 25290.956 | 28-MAR-15:39 | 8961.612 | 3712.536 | 4419.102 | 0 | 8197.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 25592300000 | 26959.802 | 14-APR-15:00 | 8961.612 | 3712.536 | 4419.102 | 0 | 9866.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 29147200000 | 29525.756 | 15-MAY-14:00 | 8961.612 | 3712.536 | 4419.102 | 0 | 12432.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 32270700000 | 31456.688 | 19-JUN-14:00 | 8961.612 | 3712.536 | 4419.102 | 0 | 14363.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 32374600000 | 33998.168 | 03-JUL-15:30 | 8961.612 | 3712.536 | 4419.102 | 0 | 16904.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 34391600000 | 31878.629 | 17-AUG-13:00 | 8961.612 | 3712.536 | 4419.102 | 0 | 14785.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 29675300000 | 30391.109 | 11-SEP-13:50 | 8961.612 | 3712.536 | 4419.102 | 0 | 13297.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 25834600000 | 28095.907 | 12-OCT-15:00 | 8961.612 | 3712.536 | 4419.102 | 0 | 11002.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 24213300000 | 23463.774 | 22-NOV-14:00 | 8961.612 | 3712.536 | 4419.102 | 0 | 6370.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24529600000 | 21771.132 | 01-DEC-15:09 | 8961.612 | 3712.536 | 4419.102 | 0 | 4677.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 332150000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22555100000 | 21771.132 |  | 8961.612 | 3712.536 | 4419.102 | 0 | 4677.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 34391600000 | 33998.168 |  | 8961.612 | 3712.536 | 4419.102 | 0 | 16904.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10596.29 | 985.23 | 0 | 11581.52
Cost per Total Building Area ($/m2) | 20.73 | 1.93 | 0 | 22.66
Cost per Net Conditioned Building Area ($/m2) | 20.73 | 1.93 | 0 | 22.66

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 327.59 | 640.88 | 640.88
Net Site Energy | 327.59 | 640.88 | 640.88
Total Source Energy | 955.16 | 1868.62 | 1868.62
Net Source Energy | 955.16 | 1868.62 | 1868.62
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 17.93 | 0 | 0 | 0 | 0
Cooling | 44.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 66.83 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.4 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 298.27 | 29.33 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10267.3 | 8200.03 | 2067.27 | 0.8 | 3.63
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14475.21 | 11560.7 | 2914.51 | 0.8 | 3.63
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8884.48 | 7095.64 | 1788.84 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9499.56 | 7463.45 | 2036.12 | 0.79 | 3.59
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12843.6 | 10257.61 | 2585.99 | 0.8 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15605.62 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 21094.12 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 12925.26 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 13742.92 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 18404.91 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 719.43 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.87 | 1014.28 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 622.54 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 642.11 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.78 | 899.95 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2313.0997 | 1.9937 | 19.0387 | 0 | 0 | 114867.8224 | 858.6539
February | 2052.7404 | 1.7674 | 17.223 | 0 | 0 | 103914.684 | 763.0037
March | 2346.022 | 2.0174 | 20.1428 | 0 | 0 | 121532.6837 | 873.417
April | 2142.7842 | 1.8402 | 18.8258 | 0 | 0 | 113587.971 | 799.0579
May | 2280.2567 | 1.9558 | 20.477 | 0 | 0 | 123552.3763 | 851.6752
June | 2304.3332 | 1.9753 | 20.9002 | 0 | 0 | 126106.7298 | 861.2994
July | 2338.522 | 2.0039 | 21.3306 | 0 | 0 | 128703.7906 | 874.4452
August | 2608.7691 | 2.2353 | 23.8394 | 0 | 0 | 143841.4885 | 975.6324
September | 2322.3149 | 1.9901 | 21.176 | 0 | 0 | 127771.129 | 868.3643
October | 2269.318 | 1.9457 | 20.4978 | 0 | 0 | 123678.4021 | 847.9528
November | 2153.3692 | 1.8494 | 18.9044 | 0 | 0 | 114062.1299 | 802.9612
December | 2247.0523 | 1.9354 | 18.7407 | 0 | 0 | 113070.8652 | 834.8856
Annual Sum or Average | 27378.5817 | 23.5095 | 241.0964 | 0 | 0.0001 | 1454690 | 10211.3486
Minimum of Months | 2052.7404 | 1.7674 | 17.223 | 0 | 0 | 103914.684 | 763.0037
Maximum of Months | 2608.7691 | 2.2353 | 23.8394 | 0 | 0 | 143841.4885 | 975.6324
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 23552200000 | 23368.513 | 26-JAN-13:00 | 8961.612 | 3712.536 | 3898.303 | 0 | 6796.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 21306400000 | 22849.129 | 13-FEB-14:30 | 8961.612 | 3712.536 | 3898.303 | 0 | 6276.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 24918800000 | 23696.059 | 31-MAR-14:20 | 8961.612 | 3712.536 | 3898.303 | 0 | 7123.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23289800000 | 24804.605 | 11-APR-15:00 | 8961.612 | 3712.536 | 3898.303 | 0 | 8232.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25332900000 | 24642.067 | 30-MAY-14:09 | 8961.612 | 3712.536 | 3898.303 | 0 | 8069.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 25856600000 | 24715.537 | 28-JUN-14:09 | 8961.612 | 3712.536 | 3898.303 | 0 | 8143.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 26389100000 | 25919.971 | 10-JUL-14:00 | 8961.612 | 3712.536 | 3898.303 | 0 | 9347.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 29492900000 | 27192.176 | 08-AUG-14:50 | 8961.612 | 3712.536 | 3898.303 | 0 | 10619.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 26197900000 | 27088.506 | 25-SEP-14:39 | 8961.612 | 3712.536 | 3898.303 | 0 | 10516.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 25358700000 | 25700.252 | 05-OCT-14:09 | 8961.612 | 3712.536 | 3898.303 | 0 | 9127.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 23387000000 | 24015.207 | 20-NOV-13:50 | 8961.612 | 3712.536 | 3898.303 | 0 | 7442.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 23183800000 | 23596.205 | 19-DEC-13:09 | 8961.612 | 3712.536 | 3898.303 | 0 | 7023.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 298266000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 21306400000 | 22849.129 |  | 8961.612 | 3712.536 | 3898.303 | 0 | 6276.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 29492900000 | 27192.176 |  | 8961.612 | 3712.536 | 3898.303 | 0 | 10619.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11865.29 | 251.64 | 0 | 12116.93
Cost per Total Building Area ($/m2) | 23.21 | 0.49 | 0 | 23.7
Cost per Net Conditioned Building Area ($/m2) | 23.21 | 0.49 | 0 | 23.7

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 422.78 | 827.11 | 827.11
Net Site Energy | 422.78 | 827.11 | 827.11
Total Source Energy | 1341.09 | 2623.63 | 2623.63
Net Source Energy | 1341.09 | 2623.63 | 2623.63
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 57.76 | 0 | 0 | 0 | 0
Cooling | 80.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 86.81 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.13 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 353.89 | 68.9 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10993.86 | 8733.26 | 2260.6 | 0.79 | 3.62
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15856.46 | 12663.84 | 3192.61 | 0.8 | 3.61
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10297.27 | 8223.97 | 2073.3 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12404.65 | 9907.04 | 2497.61 | 0.8 | 3.63
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15295.67 | 12215.96 | 3079.7 | 0.8 | 3.61
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15985.84 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 21905.55 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 14138.72 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 17474.03 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 20555.84 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 761.37 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.96 | 1091.22 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 721.53 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 869.19 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.92 | 1052.63 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6803.1398 | 10.3814 | 39.5595 | 0 | 0.0001 | 197266.9885 | 2791.7485
February | 5527.5254 | 8.7598 | 35.1964 | 0 | 0.0001 | 175523.6379 | 2302.0618
March | 6441.3026 | 10.2342 | 41.262 | 0 | 0.0001 | 205773.3692 | 2685.3571
April | 5945.9298 | 9.6775 | 40.2538 | 0 | 0.0001 | 200753.9399 | 2502.7789
May | 6833.1681 | 11.1599 | 46.6203 | 0 | 0.0001 | 232506.6488 | 2880.2187
June | 7984.951 | 13.0605 | 54.6625 | 0 | 0.0001 | 272615.6928 | 3367.7361
July | 8231.659 | 13.4653 | 56.3636 | 0 | 0.0001 | 281099.5085 | 3471.9227
August | 8605.7434 | 14.0783 | 58.9349 | 0 | 0.0001 | 293923.1318 | 3629.8118
September | 7146.1857 | 11.6851 | 48.8876 | 0 | 0.0001 | 243814.9129 | 3013.614
October | 6213.7181 | 10.1216 | 42.1443 | 0 | 0.0001 | 210182.8385 | 2616.3557
November | 5836.5714 | 9.3202 | 37.8284 | 0 | 0.0001 | 188651.7588 | 2438.1146
December | 6547.1256 | 10.0943 | 39.0444 | 0 | 0.0001 | 194702.6795 | 2697.4561
Annual Sum or Average | 82117.0199 | 132.0383 | 540.7578 | 0 | 0.001 | 2696820 | 34397.1761
Minimum of Months | 5527.5254 | 8.7598 | 35.1964 | 0 | 0.0001 | 175523.6379 | 2302.0618
Maximum of Months | 8605.7434 | 14.0783 | 58.9349 | 0 | 0.0001 | 293923.1318 | 3629.8118
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25886200000 | 21935.442 | 18-JAN-14:50 | 8961.612 | 3712.536 | 4495.946 | 0 | 4765.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 23032900000 | 23412.728 | 27-FEB-14:00 | 8961.612 | 3712.536 | 4495.946 | 0 | 6242.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 27002400000 | 24380.073 | 31-MAR-14:39 | 8961.612 | 3712.536 | 4495.946 | 0 | 7209.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 26343700000 | 28802.148 | 21-APR-14:00 | 8961.612 | 3712.536 | 4495.946 | 0 | 11632.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 30510500000 | 30783.399 | 31-MAY-15:00 | 8961.612 | 3712.536 | 4495.946 | 0 | 13613.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 35773700000 | 36176.94 | 27-JUN-15:00 | 8961.612 | 3712.536 | 4495.946 | 0 | 19006.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 36887000000 | 35410.447 | 24-JUL-15:00 | 8961.612 | 3712.536 | 4495.946 | 0 | 18240.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 38569800000 | 34636.165 | 04-AUG-14:00 | 8961.612 | 3712.536 | 4495.946 | 0 | 17466.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 31994400000 | 33499.264 | 01-SEP-14:00 | 8961.612 | 3712.536 | 4495.946 | 0 | 16329.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 27581000000 | 28830.056 | 03-OCT-14:50 | 8961.612 | 3712.536 | 4495.946 | 0 | 11659.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 24755600000 | 23431.624 | 10-NOV-14:09 | 8961.612 | 3712.536 | 4495.946 | 0 | 6261.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 25549700000 | 22444.552 | 05-DEC-14:30 | 8961.612 | 3712.536 | 4495.946 | 0 | 5274.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 353887000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 23032900000 | 21935.442 |  | 8961.612 | 3712.536 | 4495.946 | 0 | 4765.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 38569800000 | 36176.94 |  | 8961.612 | 3712.536 | 4495.946 | 0 | 19006.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10085.65 | 530.26 | 0 | 10615.91
Cost per Total Building Area ($/m2) | 19.73 | 1.04 | 0 | 20.77
Cost per Net Conditioned Building Area ($/m2) | 19.73 | 1.04 | 0 | 20.77

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 346.29 | 677.46 | 677.46
Net Site Energy | 346.29 | 677.46 | 677.46
Total Source Energy | 928.4 | 1816.26 | 1816.26
Net Source Energy | 928.4 | 1816.26 | 1816.26
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 59.85 | 0 | 0 | 0 | 0
Cooling | 23.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 64.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.73 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 274.71 | 71.57 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8121.39 | 6486.19 | 1635.2 | 0.8 | 3.63
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16367.65 | 13072.11 | 3295.54 | 0.8 | 3.61
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6876.42 | 5491.89 | 1384.53 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7398.15 | 5908.57 | 1489.58 | 0.8 | 3.63
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11231.3 | 8969.93 | 2261.36 | 0.8 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13007.99 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 24044.23 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 10329.05 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 11587.99 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 16376.86 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 569.07 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.99 | 1126.4 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 481.83 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 518.39 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 786.98 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2800.0026 | 2.4383 | 18.5733 | 0 | 0 | 112043.5063 | 1025.7521
February | 2129.2686 | 1.84 | 16.6631 | 0 | 0 | 100531.8713 | 787.7819
March | 2495.9325 | 2.1587 | 19.2093 | 0 | 0 | 115892.2145 | 922.4532
April | 2196.8216 | 1.895 | 17.8021 | 0 | 0 | 107406.4188 | 814.6373
May | 2218.0822 | 1.9082 | 18.9003 | 0 | 0 | 114035.2442 | 825.3459
June | 2156.4859 | 1.8525 | 18.8562 | 0 | 0 | 113771.11 | 803.8929
July | 2112.476 | 1.8139 | 18.6139 | 0 | 0 | 112309.9491 | 787.9219
August | 2291.7135 | 1.9681 | 20.1446 | 0 | 0 | 121545.4952 | 854.6264
September | 2147.3846 | 1.844 | 18.9012 | 0 | 0 | 114042.905 | 800.8801
October | 2178.688 | 1.8737 | 18.6738 | 0 | 0 | 112669.0701 | 811.0205
November | 2194.0782 | 1.8934 | 17.6404 | 0 | 0 | 106430.1759 | 813.1944
December | 2617.4601 | 2.2753 | 18.0916 | 0 | 0 | 109140.5259 | 961.1039
Annual Sum or Average | 27538.3939 | 23.7609 | 222.0698 | 0 | 0.0001 | 1339820 | 10208.6106
Minimum of Months | 2112.476 | 1.8139 | 16.6631 | 0 | 0 | 100531.8713 | 787.7819
Maximum of Months | 2800.0026 | 2.4383 | 20.1446 | 0 | 0 | 121545.4952 | 1025.7521
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 22973100000 | 19633.702 | 27-JAN-15:20 | 8961.612 | 3712.536 | 3482.661 | 0 | 3476.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 20612800000 | 21878.716 | 15-FEB-15:50 | 8961.612 | 3712.536 | 3482.661 | 0 | 5721.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 23762300000 | 20743.404 | 20-MAR-15:20 | 8961.612 | 3712.536 | 3482.661 | 0 | 4586.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 22022400000 | 22826.037 | 13-APR-14:00 | 8961.612 | 3712.536 | 3482.661 | 0 | 6669.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 23381500000 | 22977.606 | 17-MAY-13:00 | 8961.612 | 3712.536 | 3482.661 | 0 | 6820.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23327400000 | 23241.86 | 15-JUN-13:00 | 8961.612 | 3712.536 | 3482.661 | 0 | 7085.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 23027800000 | 24957.607 | 03-JUL-13:09 | 8961.612 | 3712.536 | 3482.661 | 0 | 8800.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 24921400000 | 23998.176 | 14-AUG-13:50 | 8961.612 | 3712.536 | 3482.661 | 0 | 7841.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23383100000 | 27165.036 | 28-SEP-14:00 | 8961.612 | 3712.536 | 3482.661 | 0 | 11008.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 23101400000 | 23215.463 | 13-OCT-14:50 | 8961.612 | 3712.536 | 3482.661 | 0 | 7058.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 21822200000 | 20495.534 | 08-NOV-14:39 | 8961.612 | 3712.536 | 3482.661 | 0 | 4338.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 22377900000 | 19485.539 | 07-DEC-14:00 | 8961.612 | 3712.536 | 3482.661 | 0 | 3328.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 274713000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 20612800000 | 19485.539 |  | 8961.612 | 3712.536 | 3482.661 | 0 | 3328.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 24921400000 | 27165.036 |  | 8961.612 | 3712.536 | 3482.661 | 0 | 11008.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12243.18 | 616.27 | 0 | 12859.45
Cost per Total Building Area ($/m2) | 23.95 | 1.21 | 0 | 25.16
Cost per Net Conditioned Building Area ($/m2) | 23.95 | 1.21 | 0 | 25.16

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 493.26 | 964.99 | 964.99
Net Site Energy | 493.26 | 964.99 | 964.99
Total Source Energy | 1324.13 | 2590.46 | 2590.46
Net Source Energy | 1324.13 | 2590.46 | 2590.46
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 165.27 | 0 | 0 | 0 | 0
Cooling | 44.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 85.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.77 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 316.22 | 177.04 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11723.72 | 8772.3 | 2951.42 | 0.75 | 3.49
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16020.58 | 12192.34 | 3828.24 | 0.76 | 3.53
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9833.08 | 7636.84 | 2196.24 | 0.78 | 3.57
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14850.02 | 11097.48 | 3752.53 | 0.75 | 3.49
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13199.45 | 10464.93 | 2734.52 | 0.79 | 3.61
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 17075.56 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 22233.93 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 14175.7 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 20013.9 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 19354.77 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 708.86 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.87 | 1007.72 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 647.76 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.77 | 895.21 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.78 | 910.23 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6701.9684 | 10.6589 | 25.2925 | 0 | 0.0001 | 1572.2697 | 2737.9403
February | 5605.2116 | 9.2406 | 22.9535 | 0 | 0.0001 | 1427.0205 | 2319.6929
March | 5292.264 | 9.5036 | 25.9727 | 0 | 0.0001 | 1615.0659 | 2261.4022
April | 4289.7011 | 8.1458 | 23.4958 | 0 | 0.0001 | 1461.1983 | 1873.4642
May | 4431.3924 | 8.7102 | 25.903 | 0 | 0.0001 | 1611.0009 | 1962.3582
June | 5155.6361 | 10.2494 | 30.7747 | 0 | 0.0001 | 1914.024 | 2293.6451
July | 5247.3088 | 10.4362 | 31.3473 | 0 | 0.0001 | 1949.6388 | 2334.8492
August | 5666.0184 | 11.2713 | 33.8613 | 0 | 0.0001 | 2105.9961 | 2521.3678
September | 4478.8036 | 8.8763 | 26.5823 | 0 | 0.0001 | 1653.2675 | 1990.0123
October | 4540.553 | 8.7044 | 25.3241 | 0 | 0.0001 | 1574.9307 | 1990.5448
November | 4822.681 | 8.7516 | 24.1722 | 0 | 0.0001 | 1503.1326 | 2069.0937
December | 6149.0261 | 10.1073 | 25.0155 | 0 | 0.0001 | 1555.2029 | 2542.0171
Annual Sum or Average | 62380.5644 | 114.6558 | 320.6948 | 0 | 0.0013 | 19942.748 | 26896.3878
Minimum of Months | 4289.7011 | 8.1458 | 22.9535 | 0 | 0.0001 | 1427.0205 | 1873.4642
Maximum of Months | 6701.9684 | 11.2713 | 33.8613 | 0 | 0.0001 | 2105.9961 | 2737.9403
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 24930500000 | 18494.785 | 05-JAN-14:00 | 8961.612 | 3712.536 | 4169.78 | 0 | 1650.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22627400000 | 18367.945 | 15-FEB-15:50 | 8961.612 | 3712.536 | 4169.78 | 0 | 1524.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 25609100000 | 23058.225 | 09-MAR-15:00 | 8961.612 | 3712.536 | 4169.78 | 0 | 6214.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23169400000 | 24012.309 | 04-APR-15:00 | 8961.612 | 3712.536 | 4169.78 | 0 | 7168.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25544700000 | 26677.845 | 31-MAY-15:00 | 8961.612 | 3712.536 | 4169.78 | 0 | 9833.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 30349500000 | 31405.191 | 30-JUN-15:50 | 8961.612 | 3712.536 | 4169.78 | 0 | 14561.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 30914300000 | 32181.962 | 25-JUL-13:30 | 8961.612 | 3712.536 | 4169.78 | 0 | 15338.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 33393500000 | 32533.446 | 17-AUG-14:00 | 8961.612 | 3712.536 | 4169.78 | 0 | 15689.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 26214900000 | 29191.942 | 08-SEP-14:00 | 8961.612 | 3712.536 | 4169.78 | 0 | 12348.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24972700000 | 26050.61 | 12-OCT-14:00 | 8961.612 | 3712.536 | 4169.78 | 0 | 9206.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 23834300000 | 23859.472 | 03-NOV-14:09 | 8961.612 | 3712.536 | 4169.78 | 0 | 7015.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24659900000 | 18027.629 | 12-DEC-16:49 | 8961.612 | 3712.536 | 4169.78 | 0 | 20.701 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 316220000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22627400000 | 18027.629 |  | 8961.612 | 3712.536 | 4169.78 | 0 | 20.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 33393500000 | 32533.446 |  | 8961.612 | 3712.536 | 4169.78 | 0 | 15689.518 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6487.27 | 1713.54 | 0 | 8200.81
Cost per Total Building Area ($/m2) | 12.69 | 3.35 | 0 | 16.04
Cost per Net Conditioned Building Area ($/m2) | 12.69 | 3.35 | 0 | 16.04

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 449.36 | 879.11 | 879.11
Net Site Energy | 449.36 | 879.11 | 879.11
Total Source Energy | 1201.4 | 2350.36 | 2350.36
Net Source Energy | 1201.4 | 2350.36 | 2350.36
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 118.37 | 0 | 0 | 0 | 0
Cooling | 46.51 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 86.05 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.72 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 319.27 | 130.09 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11111.97 | 8874.64 | 2237.34 | 0.8 | 3.63
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13651.29 | 10902.67 | 2748.61 | 0.8 | 3.63
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8888.69 | 7099 | 1789.69 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13009.36 | 10389.99 | 2619.37 | 0.8 | 3.63
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14361.15 | 11469.61 | 2891.54 | 0.8 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15098.07 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 17428.2 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 11242.57 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 16694.35 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 17498.74 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 778.62 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.82 | 956.55 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 622.83 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.79 | 911.57 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.87 | 1006.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8283.8867 | 13.2296 | 30.9421 | 0 | 0.0001 | 32166.7329 | 3427.1797
February | 7098.6669 | 11.5707 | 27.7813 | 0 | 0.0001 | 28882.684 | 2959.7834
March | 7729.3829 | 12.8884 | 31.8171 | 0 | 0.0001 | 33080.583 | 3251.1654
April | 6597.4862 | 11.3205 | 28.8873 | 0 | 0.0001 | 30036.738 | 2806.4067
May | 7379.6587 | 12.862 | 33.3913 | 0 | 0.0001 | 34721.2845 | 3158.6823
June | 7863.8741 | 13.7513 | 35.8274 | 0 | 0.0001 | 37254.7082 | 3370.3814
July | 8090.3888 | 14.1526 | 36.8876 | 0 | 0.0001 | 38357.1981 | 3467.975
August | 8461.2296 | 14.8014 | 38.5792 | 0 | 0.0002 | 40116.1663 | 3626.9509
September | 7184.8262 | 12.5567 | 32.6951 | 0 | 0.0001 | 33997.5912 | 3078.6488
October | 6841.7354 | 11.7593 | 30.063 | 0 | 0.0001 | 31259.3553 | 2912.2298
November | 7409.0515 | 12.2614 | 29.9961 | 0 | 0.0001 | 31186.6843 | 3107.3227
December | 8253.062 | 13.1096 | 30.4439 | 0 | 0.0001 | 31648.3034 | 3407.4856
Annual Sum or Average | 91193.249 | 154.2635 | 387.3115 | 0 | 0.0015 | 402708.0293 | 38574.2117
Minimum of Months | 6597.4862 | 11.3205 | 27.7813 | 0 | 0.0001 | 28882.684 | 2806.4067
Maximum of Months | 8461.2296 | 14.8014 | 38.5792 | 0 | 0.0002 | 40116.1663 | 3626.9509
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25502200000 | 20657.886 | 25-JAN-15:30 | 8961.612 | 3712.536 | 4275.842 | 0 | 3707.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22898500000 | 22453.422 | 14-FEB-15:50 | 8961.612 | 3712.536 | 4275.842 | 0 | 5503.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26226700000 | 22580.924 | 02-MAR-15:20 | 8961.612 | 3712.536 | 4275.842 | 0 | 5630.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23813500000 | 24897.588 | 21-APR-15:30 | 8961.612 | 3712.536 | 4275.842 | 0 | 7947.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 27527500000 | 26657.732 | 31-MAY-15:00 | 8961.612 | 3712.536 | 4275.842 | 0 | 9707.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 29536000000 | 29171.856 | 29-JUN-15:20 | 8961.612 | 3712.536 | 4275.842 | 0 | 12221.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 30410000000 | 30061.421 | 31-JUL-14:00 | 8961.612 | 3712.536 | 4275.842 | 0 | 13111.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 31804600000 | 30144.249 | 01-AUG-14:30 | 8961.612 | 3712.536 | 4275.842 | 0 | 13194.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 26953700000 | 27047.501 | 01-SEP-14:50 | 8961.612 | 3712.536 | 4275.842 | 0 | 10097.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24782800000 | 24793.225 | 13-OCT-14:39 | 8961.612 | 3712.536 | 4275.842 | 0 | 7843.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 24725200000 | 21890.315 | 01-NOV-14:39 | 8961.612 | 3712.536 | 4275.842 | 0 | 4940.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 25091200000 | 19974.262 | 05-DEC-14:00 | 8961.612 | 3712.536 | 4275.842 | 0 | 3024.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 319272000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22898500000 | 19974.262 |  | 8961.612 | 3712.536 | 4275.842 | 0 | 3024.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 31804600000 | 30144.249 |  | 8961.612 | 3712.536 | 4275.842 | 0 | 13194.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6642.38 | 895.18 | 0 | 7537.56
Cost per Total Building Area ($/m2) | 12.99 | 1.75 | 0 | 14.75
Cost per Net Conditioned Building Area ($/m2) | 12.99 | 1.75 | 0 | 14.75

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 426.41 | 834.21 | 834.21
Net Site Energy | 426.41 | 834.21 | 834.21
Total Source Energy | 648.76 | 1269.2 | 1269.2
Net Source Energy | 648.76 | 1269.2 | 1269.2
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 132.76 | 0 | 0 | 0 | 0
Cooling | 17.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 78 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.93 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 281.72 | 144.69 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.54 | 0.384 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 16.73 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8565.36 | 6840.77 | 1724.59 | 0.8 | 3.63
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16149.18 | 12897.63 | 3251.55 | 0.8 | 3.61
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7684.14 | 6136.98 | 1547.16 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10101.23 | 8067.4 | 2033.83 | 0.8 | 3.63
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11515.11 | 9196.6 | 2318.51 | 0.8 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14176.11 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 23980.99 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 11628.75 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 15695.12 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 16877.38 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 600.17 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.98 | 1111.37 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 538.43 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 707.79 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.7 | 806.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2691.2708 | 3.2572 | 5.2102 | 0 | 0 | 68766.2993 | 1018.66
February | 1988.4012 | 2.5296 | 4.6356 | 0 | 0 | 61210.102 | 765.8068
March | 2137.594 | 2.7686 | 5.2975 | 0 | 0 | 69960.0359 | 828.536
April | 1617.0965 | 2.2073 | 4.7278 | 0 | 0 | 62456.0257 | 638.871
May | 1362.2516 | 2.0249 | 5.0392 | 0 | 0 | 66593.8636 | 555.9097
June | 1253.2826 | 1.929 | 5.0581 | 0 | 0 | 66851.601 | 518.5203
July | 1232.9584 | 1.9272 | 5.1641 | 0 | 0 | 68256.7218 | 513.2668
August | 1325.3235 | 2.0767 | 5.5838 | 0 | 0 | 73804.1495 | 552.2676
September | 1262.8404 | 1.9167 | 4.9243 | 0 | 0 | 65080.5343 | 519.5835
October | 1463.2283 | 2.0813 | 4.8145 | 0 | 0 | 63613.4472 | 587.0817
November | 2065.6105 | 2.6502 | 4.9584 | 0 | 0 | 65477.6239 | 797.9395
December | 2678.0892 | 3.2297 | 5.111 | 0 | 0 | 67455.4626 | 1012.4361
Annual Sum or Average | 21077.9472 | 28.5984 | 60.5244 | 0 | 0.0003 | 799525.8667 | 8308.879
Minimum of Months | 1232.9584 | 1.9167 | 4.6356 | 0 | 0 | 61210.102 | 513.2668
Maximum of Months | 2691.2708 | 3.2572 | 5.5838 | 0 | 0 | 73804.1495 | 1018.66
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 24230500000 | 17623.634 | 02-JAN-16:40 | 8961.612 | 3712.536 | 3764.624 | 0 | 21.862 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 21568000000 | 18563.501 | 24-FEB-14:00 | 8961.612 | 3712.536 | 3764.624 | 0 | 2124.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 24651200000 | 21097.087 | 29-MAR-15:30 | 8961.612 | 3712.536 | 3764.624 | 0 | 4658.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 22007100000 | 20674.518 | 18-APR-15:30 | 8961.612 | 3712.536 | 3764.624 | 0 | 4235.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 23465100000 | 23519.643 | 04-MAY-14:00 | 8961.612 | 3712.536 | 3764.624 | 0 | 7080.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23555900000 | 24215.342 | 28-JUN-14:00 | 8961.612 | 3712.536 | 3764.624 | 0 | 7776.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 24051000000 | 26021.921 | 24-JUL-14:00 | 8961.612 | 3712.536 | 3764.624 | 0 | 9583.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26005700000 | 25406.485 | 07-AUG-14:00 | 8961.612 | 3712.536 | 3764.624 | 0 | 8967.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 22931800000 | 25309.807 | 01-SEP-15:30 | 8961.612 | 3712.536 | 3764.624 | 0 | 8871.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 22414900000 | 21382.001 | 17-OCT-14:00 | 8961.612 | 3712.536 | 3764.624 | 0 | 4943.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 23071700000 | 17744.194 | 14-NOV-16:40 | 8961.612 | 3712.536 | 3764.624 | 0 | 142.422 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 23768700000 | 17601.772 | 01-DEC-16:19 | 8961.612 | 3712.536 | 3764.624 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 281722000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 21568000000 | 17601.772 |  | 8961.612 | 3712.536 | 3764.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 26005700000 | 26021.921 |  | 8961.612 | 3712.536 | 3764.624 | 0 | 9583.15 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5706.75 | 1220.56 | 0 | 6927.3
Cost per Total Building Area ($/m2) | 11.16 | 2.39 | 0 | 13.55
Cost per Net Conditioned Building Area ($/m2) | 11.16 | 2.39 | 0 | 13.55

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 538 | 1052.5 | 1052.5
Net Site Energy | 538 | 1052.5 | 1052.5
Total Source Energy | 1344.59 | 2630.48 | 2630.48
Net Source Energy | 1344.59 | 2630.48 | 2630.48
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 217.44 | 0 | 0 | 0 | 0
Cooling | 31.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 90.16 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.04 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 308.52 | 229.48 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 16.73 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 42.95 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10590.81 | 7865.71 | 2725.1 | 0.74 | 3.48
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19177.5 | 14198.68 | 4978.83 | 0.74 | 3.45
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11147.79 | 8500.99 | 2646.8 | 0.76 | 3.53
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19679.01 | 14332.41 | 5346.6 | 0.73 | 3.42
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10793.94 | 8434.28 | 2359.66 | 0.78 | 3.58
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16157.54 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 24944.04 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 15450.75 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 24639.31 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 15768.01 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 629.14 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.97 | 1110.59 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 704.46 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.96 | 1095.16 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 720.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11716.6399 | 18.5618 | 47.5662 | 0 | 0.0001 | 10946.676 | 4813.0098
February | 9953.4997 | 16.1545 | 42.722 | 0 | 0.0001 | 9832.5407 | 4125.6412
March | 10391.768 | 17.5162 | 48.5021 | 0 | 0.0001 | 11163.9058 | 4369.4842
April | 8524.1248 | 14.9891 | 43.5075 | 0 | 0.0001 | 10015.2198 | 3643.5538
May | 8741.3711 | 15.7617 | 46.9576 | 0 | 0.0001 | 10809.9757 | 3773.7558
June | 9797.1732 | 17.7867 | 53.3563 | 0 | 0.0002 | 12283.1665 | 4241.1545
July | 10015.5946 | 18.1892 | 54.5819 | 0 | 0.0002 | 12565.3161 | 4336.283
August | 10398.3418 | 18.8835 | 56.6627 | 0 | 0.0002 | 13044.3403 | 4501.9143
September | 8581.2641 | 15.5516 | 46.5686 | 0 | 0.0001 | 10720.5306 | 3712.149
October | 8647.9008 | 15.3789 | 45.1711 | 0 | 0.0001 | 10398.4218 | 3712.9183
November | 9425.3017 | 16.0949 | 45.2363 | 0 | 0.0001 | 10412.525 | 3982.9664
December | 11182.9872 | 17.9453 | 46.7721 | 0 | 0.0001 | 10764.3341 | 4615.6825
Annual Sum or Average | 117375.9668 | 202.8134 | 577.6046 | 0 | 0.0018 | 132956.9523 | 49828.5129
Minimum of Months | 8524.1248 | 14.9891 | 42.722 | 0 | 0.0001 | 9832.5407 | 3643.5538
Maximum of Months | 11716.6399 | 18.8835 | 56.6627 | 0 | 0.0002 | 13044.3403 | 4813.0098
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25400900000 | 18097.31 | 02-JAN-16:30 | 8961.612 | 3712.536 | 4260.162 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22815700000 | 18097.31 | 01-FEB-16:00 | 8961.612 | 3712.536 | 4260.162 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 25905000000 | 20655.444 | 31-MAR-15:39 | 8961.612 | 3712.536 | 4260.162 | 0 | 3721.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23239600000 | 21816.65 | 07-APR-14:00 | 8961.612 | 3712.536 | 4260.162 | 0 | 4882.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25083700000 | 25340.779 | 30-MAY-15:00 | 8961.612 | 3712.536 | 4260.162 | 0 | 8406.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 28502200000 | 29501.992 | 08-JUN-12:00 | 8961.612 | 3712.536 | 4260.162 | 0 | 12567.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 29156900000 | 30396.207 | 13-JUL-14:00 | 8961.612 | 3712.536 | 4260.162 | 0 | 13461.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 30268400000 | 29733.29 | 04-AUG-15:00 | 8961.612 | 3712.536 | 4260.162 | 0 | 12798.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 24876200000 | 26623.006 | 05-SEP-14:00 | 8961.612 | 3712.536 | 4260.162 | 0 | 9688.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24128800000 | 22891.872 | 31-OCT-13:30 | 8961.612 | 3712.536 | 4260.162 | 0 | 5957.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 24161500000 | 22447.452 | 02-NOV-14:50 | 8961.612 | 3712.536 | 4260.162 | 0 | 5513.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24977800000 | 18097.31 | 01-DEC-16:19 | 8961.612 | 3712.536 | 4260.162 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 308517000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22815700000 | 18097.31 |  | 8961.612 | 3712.536 | 4260.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 30268400000 | 30396.207 |  | 8961.612 | 3712.536 | 4260.162 | 0 | 13461.897 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5182.78 | 1904.09 | 0 | 7086.86
Cost per Total Building Area ($/m2) | 10.14 | 3.73 | 0 | 13.86
Cost per Net Conditioned Building Area ($/m2) | 10.14 | 3.73 | 0 | 13.86

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 483 | 944.92 | 944.92
Net Site Energy | 483 | 944.92 | 944.92
Total Source Energy | 1206.41 | 2360.15 | 2360.15
Net Source Energy | 1206.41 | 2360.15 | 2360.15
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 165.96 | 0 | 0 | 0 | 0
Cooling | 26.11 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 92.21 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.02 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 305.02 | 177.99 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 16.73 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 42.95 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9718.21 | 7761.5 | 1956.71 | 0.8 | 3.63
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16386.72 | 13087.34 | 3299.38 | 0.8 | 3.61
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10195.54 | 8142.72 | 2052.82 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16173.76 | 12917.26 | 3256.5 | 0.8 | 3.61
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10926.66 | 8726.63 | 2200.03 | 0.8 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14249.21 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 21103.83 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 13061.14 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 20860.78 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 13895.62 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 680.95 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.99 | 1127.71 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 714.4 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.98 | 1113.06 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 765.63 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8795.673 | 13.7185 | 31.0761 | 0 | 0.0001 | 32303.5265 | 3606.6993
February | 7534.6777 | 11.9845 | 27.8807 | 0 | 0.0001 | 28983.8128 | 3112.4548
March | 8062.2101 | 13.1845 | 31.7864 | 0 | 0.0001 | 33046.8975 | 3365.7762
April | 6728.8345 | 11.3952 | 28.6469 | 0 | 0.0001 | 29785.7772 | 2847.4997
May | 6799.7889 | 11.7328 | 30.1256 | 0 | 0.0001 | 31324.7284 | 2898.8495
June | 6949.789 | 12.1153 | 31.4594 | 0 | 0.0001 | 32712.4708 | 2974.926
July | 7313.4955 | 12.7869 | 33.3094 | 0 | 0.0001 | 34636.3481 | 3134.3034
August | 7774.4687 | 13.5924 | 35.4063 | 0 | 0.0001 | 36816.7906 | 3331.813
September | 6593.7888 | 11.4575 | 29.6469 | 0 | 0.0001 | 30827.5308 | 2818.8937
October | 6991.5779 | 11.9011 | 30.095 | 0 | 0.0001 | 31291.8839 | 2964.6592
November | 7651.3358 | 12.467 | 29.9195 | 0 | 0.0001 | 31105.5721 | 3189.7694
December | 8723.9071 | 13.5804 | 30.6807 | 0 | 0.0001 | 31892.2617 | 3574.7003
Annual Sum or Average | 89919.5471 | 149.916 | 370.0329 | 0 | 0.0015 | 384727.6005 | 37820.3445
Minimum of Months | 6593.7888 | 11.3952 | 27.8807 | 0 | 0.0001 | 28983.8128 | 2818.8937
Maximum of Months | 8795.673 | 13.7185 | 35.4063 | 0 | 0.0001 | 36816.7906 | 3606.6993
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25610600000 | 19190.735 | 24-JAN-15:09 | 8961.612 | 3712.536 | 4401.757 | 0 | 2114.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22978700000 | 19287.859 | 07-FEB-14:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 2211.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26200000000 | 21819.649 | 30-MAR-15:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 4743.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23614500000 | 22926.304 | 25-APR-14:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 5850.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 24834600000 | 24396.543 | 23-MAY-15:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 7320.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 25934800000 | 26392.381 | 27-JUN-15:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 9316.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 27460100000 | 27770.963 | 17-JUL-15:30 | 8961.612 | 3712.536 | 4401.757 | 0 | 10695.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 29188800000 | 27865.548 | 30-AUG-13:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 10789.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 24440400000 | 25188.207 | 06-SEP-14:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 8112.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24808600000 | 23999.354 | 05-OCT-15:09 | 8961.612 | 3712.536 | 4401.757 | 0 | 6923.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 24660900000 | 20682.432 | 10-NOV-13:00 | 8961.612 | 3712.536 | 4401.757 | 0 | 3606.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 25284600000 | 19125.015 | 21-DEC-16:40 | 8961.612 | 3712.536 | 4401.757 | 0 | 886.11 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 305017000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22978700000 | 19125.015 |  | 8961.612 | 3712.536 | 4401.757 | 0 | 886.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 29188800000 | 27865.548 |  | 8961.612 | 3712.536 | 4401.757 | 0 | 10789.644 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6349.51 | 1227.65 | 0 | 7577.16
Cost per Total Building Area ($/m2) | 12.42 | 2.4 | 0 | 14.82
Cost per Net Conditioned Building Area ($/m2) | 12.42 | 2.4 | 0 | 14.82

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 617.65 | 1208.34 | 1208.34
Net Site Energy | 617.65 | 1208.34 | 1208.34
Total Source Energy | 1409.78 | 2758.01 | 2758.01
Net Source Energy | 1409.78 | 2758.01 | 2758.01
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 291.82 | 0 | 0 | 0 | 0
Cooling | 27.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 99.66 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.27 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 313.56 | 304.09 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 16.73 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 42.95 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8714.98 | 6915.41 | 1799.57 | 0.79 | 3.61
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21149.97 | 15789.06 | 5360.9 | 0.75 | 3.46
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12253.11 | 9432.83 | 2820.29 | 0.77 | 3.55
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21931.8 | 16020.91 | 5910.9 | 0.73 | 3.42
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11660.54 | 9171.71 | 2488.83 | 0.79 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16023.74 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 27856.81 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 17233.57 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 27471.07 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 17212.59 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 602.11 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.1 | 1249.15 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 791.26 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.08 | 1229.47 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 790.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10119.4246 | 14.5105 | 17.3858 | 0 | 0.0001 | 11413.902 | 4011.3524
February | 8242.7443 | 12.2571 | 15.5866 | 0 | 0.0001 | 10235.4964 | 3309.2662
March | 7546.8966 | 12.1797 | 17.3879 | 0 | 0.0001 | 11423.9785 | 3121.4049
April | 5739.8345 | 9.954 | 15.4736 | 0 | 0.0001 | 10169.5713 | 2440.0266
May | 5729.1626 | 10.3238 | 16.7092 | 0 | 0.0001 | 10983.2248 | 2472.6064
June | 6248.9871 | 11.3489 | 18.5129 | 0 | 0.0001 | 12169.1781 | 2705.3977
July | 6291.5262 | 11.4312 | 18.6554 | 0 | 0.0001 | 12262.8828 | 2724.2987
August | 6783.4809 | 12.3286 | 20.1256 | 0 | 0.0001 | 13229.2906 | 2937.6562
September | 5376.4137 | 9.7159 | 15.7707 | 0 | 0.0001 | 10366.4194 | 2323.016
October | 5972.1968 | 10.3872 | 16.1984 | 0 | 0.0001 | 10646.0722 | 2541.6941
November | 7246.7976 | 11.7008 | 16.7141 | 0 | 0.0001 | 10981.2975 | 2997.8003
December | 9278.461 | 13.6706 | 17.1327 | 0 | 0.0001 | 11250.0866 | 3712.9772
Annual Sum or Average | 84575.9258 | 139.8083 | 205.6529 | 0 | 0.0015 | 135131.4003 | 35297.4966
Minimum of Months | 5376.4137 | 9.7159 | 15.4736 | 0 | 0.0001 | 10169.5713 | 2323.016
Maximum of Months | 10119.4246 | 14.5105 | 20.1256 | 0 | 0.0001 | 13229.2906 | 4011.3524
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 26485100000 | 18499.316 | 02-JAN-16:40 | 8961.612 | 3712.536 | 4662.168 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 23750700000 | 17413.789 | 16-FEB-13:20 | 8961.612 | 3712.536 | 4662.168 | 0 | 77.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26508500000 | 19659.544 | 23-MAR-15:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 2323.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23597700000 | 21394.751 | 14-APR-15:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 4058.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25485700000 | 25124.843 | 15-MAY-15:20 | 8961.612 | 3712.536 | 4662.168 | 0 | 7788.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 28237700000 | 29128.595 | 29-JUN-15:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 11792.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 28455100000 | 28797.159 | 13-JUL-15:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 11460.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 30697600000 | 28995.118 | 25-AUG-15:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 11658.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 24054500000 | 25929.473 | 14-SEP-14:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 8593.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24703400000 | 21691.541 | 06-OCT-14:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 4355.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 25481300000 | 20480.196 | 02-NOV-14:00 | 8961.612 | 3712.536 | 4662.168 | 0 | 3143.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 26105000000 | 18499.316 | 01-DEC-16:30 | 8961.612 | 3712.536 | 4662.168 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 313562000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 23597700000 | 17413.789 |  | 8961.612 | 3712.536 | 4662.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 30697600000 | 29128.595 |  | 8961.612 | 3712.536 | 4662.168 | 0 | 11792.279 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6491.26 | 2401.33 | 0 | 8892.59
Cost per Total Building Area ($/m2) | 12.7 | 4.7 | 0 | 17.4
Cost per Net Conditioned Building Area ($/m2) | 12.7 | 4.7 | 0 | 17.4

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 550.09 | 1076.17 | 1076.17
Net Site Energy | 550.09 | 1076.17 | 1076.17
Total Source Energy | 1336.79 | 2615.23 | 2615.23
Net Source Energy | 1336.79 | 2615.23 | 2615.23
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 229.02 | 0 | 0 | 0 | 0
Cooling | 15.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 106.68 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.31 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 308.76 | 241.33 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 16.73 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 42.95 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8295.36 | 6625.13 | 1670.23 | 0.8 | 3.63
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19372.07 | 15471.61 | 3900.46 | 0.8 | 3.6
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12049.45 | 9623.35 | 2426.09 | 0.8 | 3.63
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19061.27 | 15223.38 | 3837.89 | 0.8 | 3.61
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12034.13 | 9611.12 | 2423.01 | 0.8 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14070.93 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 26448.1 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 16362.07 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 26073.44 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 16343.61 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 581.26 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.17 | 1333.16 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 844.3 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.15 | 1311.77 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 843.23 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9519.85 | 14.1935 | 20.1231 | 0 | 0.0001 | 477005.8527 | 3831.537
February | 7989.9445 | 12.2136 | 17.9781 | 0 | 0.0001 | 426224.1163 | 3244.8892
March | 7675.4729 | 12.49 | 20.0085 | 0 | 0.0001 | 474508.2688 | 3190.3566
April | 6348.4649 | 10.7029 | 17.8957 | 0 | 0.0001 | 424467.04 | 2674.7681
May | 6161.1516 | 10.707 | 18.5247 | 0 | 0.0001 | 439436.0898 | 2626.7734
June | 6185.0054 | 10.8808 | 19.0748 | 0 | 0.0001 | 452504.2299 | 2649.7291
July | 6317.5126 | 11.1631 | 19.6616 | 0 | 0.0001 | 466432.0496 | 2711.2586
August | 6600.66 | 11.6546 | 20.5106 | 0 | 0.0001 | 486572.0865 | 2831.915
September | 5775.4938 | 10.112 | 17.6372 | 0 | 0.0001 | 418392.9433 | 2469.6206
October | 6491.2656 | 11.0453 | 18.666 | 0 | 0.0001 | 442752.3395 | 2744.7618
November | 7447.017 | 12.068 | 19.2313 | 0 | 0.0001 | 456069.3352 | 3090.5434
December | 8960.4383 | 13.5867 | 19.7625 | 0 | 0.0001 | 468506.8646 | 3628.3549
Annual Sum or Average | 85472.2767 | 140.8175 | 229.0742 | 0 | 0.0016 | 5432870 | 35694.5078
Minimum of Months | 5775.4938 | 10.112 | 17.6372 | 0 | 0.0001 | 418392.9433 | 2469.6206
Maximum of Months | 9519.85 | 14.1935 | 20.5106 | 0 | 0.0001 | 486572.0865 | 3831.537
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 27109400000 | 18750.872 | 02-JAN-08:09 | 8961.612 | 3712.536 | 4913.724 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 24223300000 | 18521.675 | 02-FEB-16:30 | 8961.612 | 3712.536 | 4913.724 | 0 | 933.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26967400000 | 20615.143 | 30-MAR-15:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 3027.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 24123500000 | 19721.244 | 06-APR-15:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 2133.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 24974200000 | 22962.205 | 16-MAY-15:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 5374.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 25716900000 | 27205.015 | 30-JUN-14:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 9617.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 26508400000 | 27110.393 | 21-JUL-15:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 9522.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 27653100000 | 25955.088 | 08-AUG-15:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 8367.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23778300000 | 24525.278 | 01-SEP-15:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 6937.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 25162700000 | 22237.22 | 06-OCT-15:00 | 8961.612 | 3712.536 | 4913.724 | 0 | 4649.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 25919500000 | 18999.968 | 21-NOV-16:49 | 8961.612 | 3712.536 | 4913.724 | 0 | 249.096 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 26626400000 | 18750.872 | 01-DEC-16:40 | 8961.612 | 3712.536 | 4913.724 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 308763000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 23778300000 | 18521.675 |  | 8961.612 | 3712.536 | 4913.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 27653100000 | 27205.015 |  | 8961.612 | 3712.536 | 4913.724 | 0 | 9617.143 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6651.43 | 1937.42 | 0 | 8588.85
Cost per Total Building Area ($/m2) | 13.01 | 3.79 | 0 | 16.8
Cost per Net Conditioned Building Area ($/m2) | 13.01 | 3.79 | 0 | 16.8

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 692.97 | 1355.69 | 1355.69
Net Site Energy | 692.97 | 1355.69 | 1355.69
Total Source Energy | 1483.89 | 2903 | 2903
Net Source Energy | 1483.89 | 2903 | 2903
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 370.23 | 0 | 0 | 0 | 0
Cooling | 13.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.36 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.65 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 310.09 | 382.88 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 16.73 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 42.95 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7753.88 | 6088.4 | 1665.48 | 0.79 | 3.59
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21137.82 | 16286.16 | 4851.67 | 0.77 | 3.52
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12502.02 | 9848.88 | 2653.14 | 0.79 | 3.6
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22022.93 | 16552.41 | 5470.51 | 0.75 | 3.47
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12116.66 | 9677.03 | 2439.62 | 0.8 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14484.93 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 29289.83 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 18107.64 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 28875.91 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 18086.97 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 523.44 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.18 | 1343.18 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 850.11 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.16 | 1321.61 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 849.01 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10467.4469 | 14.9576 | 17.8146 | 0 | 0.0001 | 11695.0801 | 4144.3442
February | 8959.7903 | 13.0334 | 15.9982 | 0 | 0.0001 | 10504.1384 | 3569.4246
March | 8683.2518 | 13.4515 | 18.1758 | 0 | 0.0001 | 11938.9201 | 3537.6739
April | 6620.4932 | 11.0585 | 16.471 | 0 | 0.0001 | 10823.3811 | 2773.9854
May | 5923.7035 | 10.4237 | 16.4602 | 0 | 0.0001 | 10818.6307 | 2532.6026
June | 5612.0628 | 10.1455 | 16.474 | 0 | 0.0001 | 10828.7729 | 2425.1905
July | 5818.6762 | 10.5526 | 17.1898 | 0 | 0.0001 | 11299.3837 | 2517.6833
August | 6074.0671 | 10.9884 | 17.8552 | 0 | 0.0001 | 11736.697 | 2625.5744
September | 5410.8107 | 9.6499 | 15.4542 | 0 | 0.0001 | 10157.9311 | 2325.6268
October | 6438.6468 | 11.0001 | 16.8176 | 0 | 0.0001 | 11052.2089 | 2721.2466
November | 7964.9017 | 12.4761 | 17.1196 | 0 | 0.0001 | 11245.9111 | 3258.1454
December | 9946.3231 | 14.4098 | 17.5688 | 0 | 0.0001 | 11534.9996 | 3956.8376
Annual Sum or Average | 87920.1743 | 142.1471 | 203.3992 | 0 | 0.0015 | 133636.0549 | 36388.3351
Minimum of Months | 5410.8107 | 9.6499 | 15.4542 | 0 | 0.0001 | 10157.9311 | 2325.6268
Maximum of Months | 10467.4469 | 14.9576 | 18.1758 | 0 | 0.0001 | 11938.9201 | 4144.3442
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 27137600000 | 18724.499 | 02-JAN-16:30 | 8961.612 | 3712.536 | 4887.351 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 24374100000 | 17765.081 | 22-FEB-14:50 | 8961.612 | 3712.536 | 4887.351 | 0 | 203.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 27703400000 | 17992.254 | 22-MAR-14:30 | 8961.612 | 3712.536 | 4887.351 | 0 | 430.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 25114800000 | 20065.798 | 04-APR-15:50 | 8961.612 | 3712.536 | 4887.351 | 0 | 2504.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25103800000 | 22689.838 | 31-MAY-15:00 | 8961.612 | 3712.536 | 4887.351 | 0 | 5128.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 25127400000 | 25950.875 | 14-JUN-15:00 | 8961.612 | 3712.536 | 4887.351 | 0 | 8389.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 26219400000 | 27781.547 | 06-JUL-15:00 | 8961.612 | 3712.536 | 4887.351 | 0 | 10220.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 27234100000 | 26681.546 | 11-AUG-15:39 | 8961.612 | 3712.536 | 4887.351 | 0 | 9120.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23570700000 | 24281.239 | 07-SEP-14:00 | 8961.612 | 3712.536 | 4887.351 | 0 | 6719.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 25645800000 | 20391.238 | 06-OCT-14:00 | 8961.612 | 3712.536 | 4887.351 | 0 | 2829.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 26095300000 | 18724.499 | 06-NOV-16:49 | 8961.612 | 3712.536 | 4887.351 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 26766100000 | 18724.499 | 01-DEC-16:19 | 8961.612 | 3712.536 | 4887.351 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 310092000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 23570700000 | 17765.081 |  | 8961.612 | 3712.536 | 4887.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 27703400000 | 27781.547 |  | 8961.612 | 3712.536 | 4887.351 | 0 | 10220.048 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6396.67 | 3013.59 | 0 | 9410.26
Cost per Total Building Area ($/m2) | 12.51 | 5.9 | 0 | 18.41
Cost per Net Conditioned Building Area ($/m2) | 12.51 | 5.9 | 0 | 18.41

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1016.11 | 1987.86 | 1987.86
Net Site Energy | 1016.11 | 1987.86 | 1987.86
Total Source Energy | 1949.04 | 3812.99 | 3812.99
Net Source Energy | 1949.04 | 3812.99 | 3812.99
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 664.52 | 0 | 0 | 0 | 0
Cooling | 8.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 143.28 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 13.1 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 338.49 | 677.62 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
CORE_ZN_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 149.66 | 270 | 0
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 113.45 | 45 | 0
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 67.3 | 270 | 0
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 113.45 | 180 | 0
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
PERIMETER_ZN_4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 67.3 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.525 | 0.407 | 0.316 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 16.73 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 42.95 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5772.9 | 4610.56 | 1162.34 | 0.8 | 3.63
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25355.87 | 20250.6 | 5105.27 | 0.8 | 3.6
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15745.01 | 12574.83 | 3170.17 | 0.8 | 3.61
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25001.01 | 19967.19 | 5033.82 | 0.8 | 3.6
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15745.01 | 12574.83 | 3170.17 | 0.8 | 3.61
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13977.34 | 0.78
PSZ-AC:2_HEATC | Coil:Heating:Gas | 39309.39 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 24282.25 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 38823.93 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 24282.25 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 404.51 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.53 | 1744.96 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.95 | 1083.55 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.51 | 1720.54 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.95 | 1083.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13328.6371 | 14.1674 | 43.3063 | 0 | 0.0002 | 8684.3089 | 4931.3107
February | 11410.1052 | 12.2024 | 38.627 | 0 | 0.0001 | 7746.4631 | 4232.9276
March | 10396.2333 | 11.5115 | 43.4241 | 0 | 0.0002 | 8710.9919 | 3917.332
April | 7376.8632 | 8.5665 | 39.1446 | 0 | 0.0001 | 7854.5772 | 2840.9118
May | 5635.0623 | 6.9321 | 38.0256 | 0 | 0.0001 | 7631.6334 | 2229.8795
June | 5279.8026 | 6.5737 | 37.2731 | 0 | 0.0001 | 7480.8563 | 2101.3962
July | 5121.5761 | 6.3861 | 36.3527 | 0 | 0.0001 | 7296.1563 | 2039.8671
August | 5467.642 | 6.7942 | 38.3197 | 0 | 0.0001 | 7690.874 | 2174.102
September | 5826.6669 | 7.0879 | 37.6464 | 0 | 0.0001 | 7555.2703 | 2293.4006
October | 8262.3381 | 9.4962 | 41.7822 | 0 | 0.0001 | 8383.4368 | 3166.758
November | 11038.268 | 12.0224 | 41.9215 | 0 | 0.0002 | 8408.5313 | 4128.4746
December | 12436.4826 | 13.3419 | 42.9773 | 0 | 0.0002 | 8619.1453 | 4620.1341
Annual Sum or Average | 101579.6773 | 115.0821 | 478.8004 | 0 | 0.0017 | 96062.2448 | 38676.4943
Minimum of Months | 5121.5761 | 6.3861 | 36.3527 | 0 | 0.0001 | 7296.1563 | 2039.8671
Maximum of Months | 13328.6371 | 14.1674 | 43.4241 | 0 | 0.0002 | 8710.9919 | 4931.3107
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 30600100000 | 19874.253 | 02-JAN-08:09 | 8961.612 | 3712.536 | 6037.105 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 27295500000 | 19874.253 | 01-FEB-08:09 | 8961.612 | 3712.536 | 6037.105 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 30694100000 | 19874.253 | 01-MAR-08:09 | 8961.612 | 3712.536 | 6037.105 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 27676500000 | 20115.801 | 25-APR-15:00 | 8961.612 | 3712.536 | 6037.105 | 0 | 1404.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 26890900000 | 22961.057 | 24-MAY-15:00 | 8961.612 | 3712.536 | 6037.105 | 0 | 4249.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 26359600000 | 25208.58 | 21-JUN-15:00 | 8961.612 | 3712.536 | 6037.105 | 0 | 6497.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 25708800000 | 25186.624 | 21-JUL-15:00 | 8961.612 | 3712.536 | 6037.105 | 0 | 6475.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 27099600000 | 24799.373 | 15-AUG-15:00 | 8961.612 | 3712.536 | 6037.105 | 0 | 6088.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 26621800000 | 21110.633 | 07-SEP-15:00 | 8961.612 | 3712.536 | 6037.105 | 0 | 2399.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 29539900000 | 19874.253 | 03-OCT-07:10 | 8961.612 | 3712.536 | 6037.105 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 29628400000 | 19874.253 | 01-NOV-07:10 | 8961.612 | 3712.536 | 6037.105 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 30370500000 | 19874.253 | 01-DEC-08:09 | 8961.612 | 3712.536 | 6037.105 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 338486000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 25708800000 | 19874.253 |  | 8961.612 | 3712.536 | 6037.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 30694100000 | 25208.58 |  | 8961.612 | 3712.536 | 6037.105 | 0 | 6497.327 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9306.36 | 2785.35 | 0 | 12091.72
Cost per Total Building Area ($/m2) | 18.21 | 5.45 | 0 | 23.66
Cost per Net Conditioned Building Area ($/m2) | 18.21 | 5.45 | 0 | 23.66

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_ZN Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_ZN Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_ZN Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_ZN Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720