## BuildingSummary
Building Summary Small Office post-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Small Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 511 | 2003 CBECS, ASHRAE Small Office 30% Advanced Energy Design Guide
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.244
| East | 0.198
| North | 0.198
| West | 0.198
| Total | 0.212
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones
| Floor to Ceiling Height (m) | 3.05
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 281.5
| Net Dimensions - Total Area (m2) | 222
| Wall to Skin Ratio | 0.32
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 598.76
| Net Dimensions - Total Area (m2) | 598.76
| Roof to Skin Ratio | 0.68
Window Dimensions (m2)
| South | 16.73
| East | 11.16
| North | 16.73
| West | 11.16
| Total Area (m2) | 55.78
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab w/carpet
| Dimensions - Total Area (m2) | 511
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 0
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.46
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.68 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 17.63

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 19.4827 | 8.0729 |  | 11.3562 | 10 |  | 80.5463 |  | 0
Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 20.64 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 16.73 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
Attic | No | 1 | 567.98 | 720.19 | 1.268 | 0 | 0 | [8 empty] | 0 |  | 1
Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value attic floor (m2·K / W) | 2.38 | 2.6685 | 3.8287 | 2.4461 | 1.7612 | 3.6691 | 2.0013 | 3.0365 | 2.9851 | 2.7518 | 3.323 | 3.4533 | 3.9137 | 3.5943 | 4.403 | 5.6812
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 11.1945 | 10.2965 | 10.18 | 10.2974 | 9.0706 | 10.3035 | 6.7187 | 10.9684 | 9.6281 | 7.0837 | 10.6619 | 9.5364 | 11.036 | 8.0571 | 9.0335 | 7.3588
| PSZ-AC:2_COOLC DXCOIL | 11.5376 | 12.6905 | 10.331 | 14.0513 | 8.8985 | 10.0176 | 9.027 | 14.9453 | 12.1838 | 9.1529 | 19.683 | 15.3154 | 21.5204 | 17.7932 | 20.5747 | 22.8464
| PSZ-AC:3_COOLC DXCOIL | 8.1296 | 7.7207 | 7.4301 | 8.5081 | 5.7479 | 6.088 | 4.794 | 8.3823 | 7.5982 | 5.67 | 10.7202 | 9.5571 | 11.5598 | 11.056 | 11.265 | 14.1788
| PSZ-AC:4_COOLC DXCOIL | 11.8215 | 12.0437 | 10.1932 | 13.5248 | 7.8713 | 9.4997 | 7.5408 | 14.8391 | 11.9568 | 8.9687 | 19.5908 | 15.0958 | 19.368 | 17.4991 | 21.3371 | 22.4913
| PSZ-AC:5_COOLC DXCOIL | 9.7836 | 9.5576 | 9.1573 | 8.6735 | 8.9804 | 8.0912 | 6.4727 | 8.182 | 7.9948 | 6.8142 | 10.5841 | 9.5716 | 11.5008 | 11.0465 | 11.142 | 14.1788
Heating (kW)
| PSZ-AC:1_HEATC | 15.4067 | 16.0841 | 15.2753 | 16.0943 | 13.7891 | 15.2642 | 11.0608 | 18.1343 | 13.403 | 12.1477 | 18.4433 | 14.0419 | 19.3158 | 13.784 | 16.5473 | 16.1444
| PSZ-AC:2_HEATC | 13.2102 | 15.0558 | 13.0635 | 17.393 | 12.7574 | 13.7192 | 13.85 | 18.1779 | 15.7506 | 14.3958 | 23.3962 | 19.8812 | 25.764 | 24.5449 | 26.8749 | 35.877
| PSZ-AC:3_HEATC | 9.6987 | 9.5516 | 10.1733 | 10.866 | 8.584 | 8.7348 | 7.4371 | 11.264 | 9.7673 | 8.8693 | 14.4796 | 12.3325 | 15.9141 | 15.1647 | 16.5885 | 22.1401
| PSZ-AC:4_HEATC | 13.8345 | 14.8016 | 13.3937 | 17.1718 | 11.1832 | 13.539 | 11.7862 | 17.9388 | 15.4911 | 14.1435 | 23.0691 | 19.6306 | 25.3962 | 24.1905 | 26.4761 | 35.3912
| PSZ-AC:5_HEATC | 12.4224 | 12.5767 | 12.5493 | 11.8739 | 13.0581 | 11.3065 | 9.7684 | 11.2918 | 10.2207 | 10.437 | 14.4675 | 12.3491 | 15.9012 | 15.1532 | 16.5757 | 22.1401
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.12 | 3.16 | 3.19 | 3.17 | 3.18 | 3.19 | 3.19 | 3.18 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19
| PSZ-AC:2_COOLC DXCOIL | 3.01 | 3.01 | 3.08 | 3.05 | 3.15 | 3.15 | 3.19 | 3.01 | 3.19 | 3.19 | 3.04 | 3.17 | 3.05 | 3.17 | 3.11 | 3.22
| PSZ-AC:3_COOLC DXCOIL | 3.04 | 3.04 | 3.15 | 3.07 | 3.19 | 3.19 | 3.19 | 3.07 | 3.19 | 3.19 | 3.09 | 3.19 | 3.1 | 3.19 | 3.17 | 3.19
| PSZ-AC:4_COOLC DXCOIL | 3.03 | 3.03 | 3.1 | 3.06 | 3.13 | 3.17 | 3.19 | 3.01 | 3.19 | 3.19 | 3.03 | 3.17 | 3.1 | 3.17 | 3.08 | 3.22
| PSZ-AC:5_COOLC DXCOIL | 3.09 | 3.09 | 3.16 | 3.12 | 3.19 | 3.19 | 3.19 | 3.09 | 3.19 | 3.19 | 3.1 | 3.19 | 3.11 | 3.19 | 3.18 | 3.19
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC:1_FAN | 0.62 | 0.6 | 0.61 | 0.61 | 0.54 | 0.62 | 0.41 | 0.66 | 0.58 | 0.43 | 0.64 | 0.58 | 0.67 | 0.49 | 0.55 | 0.44
| PSZ-AC:2_FAN | 0.53 | 0.58 | 0.53 | 0.69 | 0.51 | 0.57 | 0.55 | 0.69 | 0.74 | 0.55 | 0.91 | 0.93 | 1 | 1.07 | 1.07 | 1.38
| PSZ-AC:3_FAN | 0.4 | 0.37 | 0.43 | 0.44 | 0.35 | 0.37 | 0.29 | 0.43 | 0.46 | 0.34 | 0.56 | 0.58 | 0.62 | 0.67 | 0.66 | 0.86
| PSZ-AC:4_FAN | 0.56 | 0.57 | 0.55 | 0.68 | 0.44 | 0.56 | 0.46 | 0.68 | 0.72 | 0.54 | 0.89 | 0.91 | 0.99 | 1.06 | 1.05 | 1.36
| PSZ-AC:5_FAN | 0.52 | 0.5 | 0.53 | 0.48 | 0.54 | 0.49 | 0.39 | 0.43 | 0.48 | 0.41 | 0.56 | 0.58 | 0.62 | 0.67 | 0.66 | 0.86
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.083514 | 0.12622 | 0.12336 | 0.11557 | 0.14514 | 0.1025 | 0.16176 | 0.07434 | 0.075004 | 0.073061 | 0.060749 | 0.074987 | 0.074586 | 0.07741 | 0.074327 | 0.099069
| Total Cost ($/m2) | 15.87 | 21.78 | 21.69 | 18.59 | 20.97 | 16.64 | 21.01 | 11.63 | 11.67 | 9.86 | 9.95 | 11.87 | 12.43 | 12.55 | 12.11 | 17.55
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011464 | 0.0080857 | 0.0082924 | 0.0095908 | 0.0085993 | 0.007704 | 0.0086552 | 0.0096837 | 0.006877 | 0.00844 | 0.0082918 | 0.006887 | 0.0079101 | 0.008011 | 0.0078758 | 0.0041064
| Total Cost ($/m2) | 0.26 | 0.78 | 0.51 | 1.71 | 0.42 | 0.81 | 1.09 | 2.69 | 1.36 | 1.95 | 3.14 | 1.92 | 3.91 | 3.13 | 4.77 | 4.39
Total Utility Costs
| Cost Intensity ($/m2) | 16.14 | 22.55 | 22.2 | 20.3 | 21.38 | 17.45 | 22.1 | 14.32 | 13.04 | 11.81 | 13.08 | 13.8 | 16.33 | 15.68 | 16.88 | 21.94
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 31125 | 21336.1111 | 22702.7778 | 12991.6667 | 9022.2222 | 15672.2222 | 2563.8889 | 9716.6667 | 8958.3333 | 2469.4444 | 8180.5556 | 5897.2222 | 7233.3333 | 4222.2222 | 3433.3333 | 2658.3333
| Interior Lighting | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111
| Exterior Lighting | 5083.3333 | 5080.5556 | 5080.5556 | 5080.5556 | 5075 | 5075 | 5077.7778 | 5075 | 5075 | 5066.6667 | 5075 | 5072.2222 | 5072.2222 | 5069.4444 | 5066.6667 | 5036.1111
| Interior Equipment | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 14144.4444 | 14983.3333 | 15308.3333 | 17350 | 12955.5556 | 15444.4444 | 11977.7778 | 18405.5556 | 18725 | 14672.2222 | 23638.8889 | 23177.7778 | 26066.6667 | 26819.4444 | 28025 | 36058.3333
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 97138.8889 | 88186.1111 | 89875 | 82208.3333 | 73841.6667 | 82975 | 66405.5556 | 79983.3333 | 79547.2222 | 68994.4444 | 83680.5556 | 80933.3333 | 85158.3333 | 82897.2222 | 83313.8889 | 90541.6667
Gas (MJ)
| Heating | 850 | 37760 | 20550 | 79560 | 13200 | 42110 | 52410 | 129790 | 89390 | 105920 | 181200 | 130520 | 239840 | 186920 | 296500 | 533640
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10950 | 11360 | 11120 | 11750 | 11680 | 11410 | 12010 | 12060 | 12000 | 12220 | 12330 | 12320 | 12570 | 12610 | 12950 | 13420
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11800 | 49120 | 31670 | 91310 | 24880 | 53510 | 64420 | 141850 | 101390 | 118140 | 193530 | 142840 | 252410 | 199530 | 309450 | 547060
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 361500 | 366580 | 355230 | 387260 | 290710 | 352230 | 303470 | 429790 | 387760 | 366520 | 494780 | 434200 | 558980 | 497960 | 609380 | 873010
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 219.2073 | 150.2661 | 159.8912 | 91.4978 | 63.5417 | 110.3764 | 18.057 | 68.4326 | 63.0918 | 17.3918 | 57.6141 | 41.533 | 50.943 | 29.7363 | 24.1803 | 18.7221
| Interior Lighting (elec) | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982
| Exterior Lighting (elec) | 35.8009 | 35.7814 | 35.7814 | 35.7814 | 35.7422 | 35.7422 | 35.7618 | 35.7422 | 35.7422 | 35.6835 | 35.7422 | 35.7227 | 35.7227 | 35.7031 | 35.6835 | 35.4683
| Interior Equipment (elec) | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 99.6166 | 105.5247 | 107.8136 | 122.1927 | 91.2434 | 108.7722 | 84.3571 | 129.6267 | 131.8765 | 103.3336 | 166.4841 | 163.2366 | 183.5824 | 188.8841 | 197.3746 | 253.9518
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 684.1302 | 621.0775 | 632.9721 | 578.9772 | 520.0524 | 584.3767 | 467.6814 | 563.307 | 560.2355 | 485.9144 | 589.3458 | 569.9977 | 599.7535 | 583.8289 | 586.7634 | 637.6673
Gas (MJ/m2)
| Heating (gas) | 1.6629 | 73.8712 | 40.2027 | 155.646 | 25.8236 | 82.3813 | 102.5315 | 253.9127 | 174.8768 | 207.215 | 354.4878 | 255.3408 | 469.2073 | 365.6781 | 580.0532 | 1043.9784
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 21.4219 | 22.224 | 21.7544 | 22.9869 | 22.85 | 22.3218 | 23.4956 | 23.5934 | 23.476 | 23.9064 | 24.1216 | 24.102 | 24.5911 | 24.6694 | 25.3345 | 26.254
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 23.0847 | 96.0952 | 61.9571 | 178.6329 | 48.6736 | 104.6835 | 126.0271 | 277.5061 | 198.3528 | 231.1214 | 378.6094 | 279.4428 | 493.7984 | 390.3474 | 605.3877 | 1070.2324
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 707.215 | 717.1531 | 694.9487 | 757.6101 | 568.726 | 689.0797 | 593.6889 | 840.8131 | 758.5883 | 717.0358 | 967.9552 | 849.4405 | 1093.5519 | 974.1764 | 1192.1512 | 1707.8997
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 24.9954 | 22.2254 | 19.2377 | 18.2912 | 20.4242 | 17.5948 | 16.2583 | 17.1937 | 17.4537 | 16.478 | 17.9403 | 18.0436 | 18.3212 | 18.3792 | 18.4223 | 19.4599
| Feb | 25.7266 | 22.4543 | 20.4106 | 17.8609 | 20.2393 | 18.054 | 18.3421 | 16.3076 | 18.8101 | 15.8089 | 17.9403 | 17.6052 | 17.1795 | 18.0836 | 17.3142 | 19.4599
| Mar | 26.1652 | 22.4342 | 23.5544 | 20.4664 | 20.8483 | 19.4776 | 16.6237 | 19.7244 | 19.0258 | 17.8971 | 19.3632 | 19.9306 | 18.6737 | 19.9675 | 17.4213 | 19.4599
| Apr | 27.1746 | 24.7417 | 23.8682 | 23.2922 | 21.975 | 23.2867 | 19.0412 | 20.8246 | 21.4289 | 17.2764 | 19.9896 | 21.0821 | 20.1014 | 19.4303 | 19.0157 | 19.8215
| May | 28.6789 | 28.671 | 27.7909 | 26.2044 | 22.5322 | 25.6749 | 19.2246 | 23.7152 | 23.4394 | 19.6405 | 24.408 | 22.7712 | 24.5233 | 21.3644 | 21.5925 | 22.5662
| Jun | 30.0723 | 29.0299 | 32.8136 | 28.2684 | 22.5609 | 30.6739 | 20.5003 | 28.5737 | 25.7379 | 20.6859 | 28.3875 | 24.584 | 28.3623 | 25.6957 | 25.1227 | 24.9194
| Jul | 29.5506 | 30.29 | 32.3574 | 30.791 | 23.7569 | 29.9672 | 22.0325 | 29.2916 | 26.587 | 22.2928 | 29.4284 | 26.068 | 28.4369 | 25.8322 | 26.8609 | 24.7911
| Aug | 29.8513 | 29.8916 | 32.3655 | 28.0433 | 24.9895 | 29.1178 | 19.9572 | 29.2963 | 26.6173 | 21.8185 | 28.9593 | 26.0511 | 28.1873 | 24.9496 | 25.7659 | 24.6451
| Sep | 28.9083 | 28.4155 | 29.6304 | 26.5406 | 25.0198 | 28.1226 | 23.5306 | 25.4437 | 23.3713 | 21.6704 | 25.3941 | 23.3182 | 25.195 | 22.9838 | 23.5153 | 20.9195
| Oct | 28.3176 | 26.5819 | 24.8118 | 24.0055 | 22.9538 | 23.6206 | 19.879 | 22.9202 | 21.4854 | 18.1379 | 22.3925 | 22.0068 | 20.6966 | 20.9415 | 19.7282 | 19.5448
| Nov | 26.4144 | 23.6219 | 22.2828 | 19.7539 | 21.0615 | 19.4639 | 17.4247 | 20.8624 | 18.6107 | 16.5374 | 21.7145 | 18.6769 | 19.4962 | 18.6545 | 18.4223 | 19.4599
| Dec | 24.7274 | 22.197 | 18.7435 | 17.1959 | 20.5888 | 18.219 | 16.6227 | 17.1937 | 17.7474 | 16.478 | 17.9403 | 18.2139 | 18.3212 | 18.3792 | 18.4223 | 19.4599
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 03-JAN-13:00 | 27-JAN-14:00 | 23-JAN-16:00 | 25-JAN-15:30 | 18-JAN-16:49 | 02-JAN-16:00 | 02-JAN-16:49 | 26-JAN-15:00 | 02-JAN-16:30 | 02-JAN-16:30 | 24-JAN-15:30 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-15:00 | 23-FEB-15:30 | 28-FEB-16:49 | 27-FEB-16:00 | 13-FEB-14:00 | 27-FEB-15:00 | 15-FEB-15:00 | 15-FEB-15:00 | 14-FEB-15:00 | 21-FEB-15:50 | 01-FEB-16:00 | 07-FEB-15:20 | 16-FEB-13:30 | 02-FEB-15:00 | 17-FEB-13:20 | 01-FEB-08:09
| Mar | 13-MAR-15:00 | 28-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-15:00 | 01-MAR-14:00 | 09-MAR-15:00 | 02-MAR-15:00 | 29-MAR-15:50 | 31-MAR-15:30 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 22-MAR-14:09 | 01-MAR-08:09
| Apr | 03-APR-15:00 | 21-APR-15:30 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:50 | 13-APR-15:20 | 04-APR-15:00 | 21-APR-15:00 | 18-APR-15:00 | 07-APR-14:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:39 | 25-APR-15:00
| May | 24-MAY-14:00 | 18-MAY-15:39 | 30-MAY-15:00 | 15-MAY-15:20 | 30-MAY-15:50 | 31-MAY-15:00 | 25-MAY-15:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-15:00 | 28-JUN-15:00 | 19-JUN-15:50 | 30-JUN-15:39 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:30 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 21-JUN-15:00
| Jul | 03-JUL-15:20 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:50 | 24-JUL-15:00 | 03-JUL-14:00 | 25-JUL-12:00 | 03-JUL-15:30 | 24-JUL-14:00 | 03-JUL-14:00 | 17-JUL-15:39 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-15:30 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-15:39 | 08-AUG-15:30 | 04-AUG-15:00 | 15-AUG-12:00 | 17-AUG-15:00 | 01-AUG-15:30 | 07-AUG-15:20 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-14:30
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:00 | 11-SEP-13:00 | 25-SEP-15:09 | 01-SEP-14:00 | 28-SEP-15:30 | 08-SEP-15:00 | 29-SEP-14:50 | 01-SEP-15:00 | 27-SEP-15:30 | 01-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
| Oct | 06-OCT-15:00 | 06-OCT-15:00 | 13-OCT-15:00 | 12-OCT-15:00 | 05-OCT-14:39 | 03-OCT-15:30 | 13-OCT-15:00 | 03-OCT-14:00 | 11-OCT-15:00 | 17-OCT-15:39 | 31-OCT-13:30 | 05-OCT-15:20 | 06-OCT-14:00 | 06-OCT-15:00 | 06-OCT-14:00 | 03-OCT-14:00
| Nov | 07-NOV-15:09 | 03-NOV-14:39 | 13-NOV-16:30 | 22-NOV-15:30 | 10-NOV-14:00 | 10-NOV-16:40 | 14-NOV-16:00 | 03-NOV-13:00 | 08-NOV-15:39 | 14-NOV-16:00 | 02-NOV-14:39 | 10-NOV-16:49 | 02-NOV-14:00 | 21-NOV-16:49 | 06-NOV-16:49 | 01-NOV-07:10
| Dec | 15-DEC-15:39 | 19-DEC-15:30 | 11-DEC-15:00 | 05-DEC-15:09 | 19-DEC-13:09 | 05-DEC-16:30 | 07-DEC-16:49 | 01-DEC-16:40 | 08-DEC-16:49 | 01-DEC-16:19 | 01-DEC-16:19 | 21-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 1172.84 | 1206.68 | 1057.99 | 1095.27 | 849.9 | 1126.94 | 810.23 | 1184.56 | 1060.88 | 561.69 | 1279.56 | 1122.72 | 1329.31 | 1255.24 | 1368.77 | 1761.67
| Total Source Energy (MJ/m2) | 2294.48 | 2360.67 | 2069.8 | 2142.73 | 1662.7 | 2204.68 | 1585.08 | 2317.41 | 2075.45 | 1098.85 | 2503.25 | 2196.42 | 2600.58 | 2455.68 | 2677.78 | 3446.43
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
| Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
Emissions
| Carbon Equivalent (kg) | 26853.1598 | 30300.8665 | 27702.6234 | 26969.426 | 9078.0822 | 28950.7789 | 8922.0703 | 24141.5966 | 34322.7882 | 7155.5174 | 48103.6818 | 35637.0242 | 33700.5983 | 33892.1312 | 34097.6272 | 35341.9117
| CO2 (kg) | 62301.9921 | 76370.0437 | 65455.2216 | 62229.9954 | 24335.3676 | 69072.706 | 24075.2357 | 55792.5214 | 80997.6797 | 18092.1953 | 113019.0577 | 84477.857 | 80350.3968 | 80855.564 | 81866.195 | 92321.9844
| NOX (kg) | 109.3501 | 99.3411 | 109.339 | 115.2988 | 20.8931 | 111.2333 | 20.7778 | 103.4847 | 137.6409 | 24.7679 | 196.59 | 141.9187 | 134.5664 | 134.5111 | 134.6075 | 105.8304
| SO2 (kg) | 415.7976 | 420.6569 | 361.4189 | 288.5723 | 214.8735 | 456.4503 | 193.2476 | 292.0042 | 347.3887 | 53.3588 | 563.9871 | 353.459 | 201.0539 | 221.4013 | 196.7145 | 461.0336
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0019 | 0.0012 | 0.001 | 0.0011 | 0.0001 | 0.0009 | 0.0001 | 0.0012 | 0.0014 | 0.0002 | 0.0017 | 0.0014 | 0.0015 | 0.0016 | 0.0015 | 0.0016
| Water for Electricity (m3) | 51.4602 | 143.4878 | 2669.72 | 513.2698 | 1296.47 | 2276.37 | 1165.92 | 18.1589 | 361.2025 | 704.9012 | 129.8243 | 367.5031 | 132.1174 | 5251.11 | 129.2548 | 92.5034

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 361.5 | 707.22 | 707.22
Net Site Energy | 361.5 | 707.22 | 707.22
Total Source Energy | 1172.84 | 2294.48 | 2294.48
Net Source Energy | 1172.84 | 2294.48 | 2294.48
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 0.85 | 0 | 0 | 0 | 0
Cooling | 112.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 50.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.95 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 349.7 | 11.8 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.42 | 0.468 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.42 | 0.468 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.42 | 0.468 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.42 | 0.468 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 16.73 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11194.47 | 8568.39 | 2626.08 | 0.77 | 3.12
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11537.57 | 8215.43 | 3322.14 | 0.71 | 3.01
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8129.65 | 5920.47 | 2209.17 | 0.73 | 3.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11821.47 | 8503.04 | 3318.42 | 0.72 | 3.03
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9783.59 | 7354.3 | 2429.29 | 0.75 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15406.69 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 13210.18 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 9698.73 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 13834.45 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 12422.36 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 713.47 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 618.02 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 460.57 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 649.52 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 597.98 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4513.886 | 7.8948 | 29.9061 | 0 | 0.0001 | 3701.2358 | 1942.7671
February | 4223.0872 | 7.4053 | 28.1302 | 0 | 0.0001 | 3481.4592 | 1819.5268
March | 5000.5764 | 8.7708 | 33.3257 | 0 | 0.0002 | 4124.4759 | 2154.722
April | 4918.6878 | 8.6343 | 32.8361 | 0 | 0.0001 | 4063.8852 | 2120.1511
May | 5602.8712 | 9.8401 | 37.4413 | 0 | 0.0002 | 4633.844 | 2415.5423
June | 5874.9847 | 10.3215 | 39.2872 | 0 | 0.0002 | 4862.2942 | 2533.2068
July | 5793.8018 | 10.1777 | 38.7353 | 0 | 0.0002 | 4793.9953 | 2498.0879
August | 6256.2763 | 10.9927 | 41.8474 | 0 | 0.0002 | 5179.1541 | 2697.747
September | 5453.5448 | 9.5783 | 36.4474 | 0 | 0.0002 | 4510.8349 | 2351.2143
October | 5344.0759 | 9.3834 | 35.6945 | 0 | 0.0002 | 4417.6503 | 2303.7472
November | 4889.4844 | 8.5823 | 32.6359 | 0 | 0.0001 | 4039.1026 | 2107.496
December | 4430.7157 | 7.7691 | 29.5106 | 0 | 0.0001 | 3652.3075 | 1908.9513
Annual Sum or Average | 62301.9921 | 109.3501 | 415.7976 | 0 | 0.0019 | 51460.2391 | 26853.1598
Minimum of Months | 4223.0872 | 7.4053 | 28.1302 | 0 | 0.0001 | 3481.4592 | 1819.5268
Maximum of Months | 6256.2763 | 10.9927 | 41.8474 | 0 | 0.0002 | 5179.1541 | 2697.747
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25152000000 | 24995.419 | 23-JAN-15:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 9281.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 23658500000 | 25726.558 | 22-FEB-15:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 10012.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 28028100000 | 26165.165 | 13-MAR-15:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 10451.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 27616400000 | 27174.553 | 03-APR-15:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 11460.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 31489500000 | 28678.874 | 24-MAY-14:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 12965.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 33042000000 | 30072.306 | 28-JUN-14:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 14358.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 32577900000 | 29550.644 | 03-JUL-15:20 | 8961.612 | 3712.536 | 3039.555 | 0 | 13836.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 35195200000 | 29851.298 | 21-AUG-15:30 | 8961.612 | 3712.536 | 3039.555 | 0 | 14137.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 30653600000 | 28908.337 | 11-SEP-14:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 13194.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 30020400000 | 28317.558 | 06-OCT-15:00 | 8961.612 | 3712.536 | 3039.555 | 0 | 12603.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 27447900000 | 26414.435 | 07-NOV-15:09 | 8961.612 | 3712.536 | 3039.555 | 0 | 10700.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24819500000 | 24727.43 | 15-DEC-15:39 | 8961.612 | 3712.536 | 3039.555 | 0 | 9013.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 349701000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 23658500000 | 24727.43 |  | 8961.612 | 3712.536 | 3039.555 | 0 | 9013.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 35195200000 | 30072.306 |  | 8961.612 | 3712.536 | 3039.555 | 0 | 14358.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8112.43 | 135.28 | 0 | 8247.71
Cost per Total Building Area ($/m2) | 15.87 | 0.26 | 0 | 16.14
Cost per Net Conditioned Building Area ($/m2) | 15.87 | 0.26 | 0 | 16.14

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 366.58 | 717.16 | 717.16
Net Site Energy | 366.58 | 717.16 | 717.16
Total Source Energy | 1206.68 | 2360.67 | 2360.67
Net Source Energy | 1206.68 | 2360.67 | 2360.67
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 37.76 | 0 | 0 | 0 | 0
Cooling | 76.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 53.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.36 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 317.47 | 49.12 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.375 | 0.412 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.375 | 0.412 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.375 | 0.412 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.375 | 0.412 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 16.73 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10296.49 | 8108.04 | 2188.45 | 0.79 | 3.16
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12690.47 | 9010.6 | 3679.87 | 0.71 | 3.01
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7720.65 | 5592.87 | 2127.78 | 0.72 | 3.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12043.71 | 8664.35 | 3379.36 | 0.72 | 3.03
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9557.6 | 7187.89 | 2369.71 | 0.75 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16084.07 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 15055.81 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 9551.63 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 14801.63 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 12576.65 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 699.5 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 674.87 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 431.73 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 662 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 584.83 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5826.5827 | 7.3806 | 29.3136 | 0 | 0.0001 | 9998.1108 | 2286.1914
February | 5205.3094 | 6.5956 | 26.2144 | 0 | 0.0001 | 8941.0632 | 2042.664
March | 5650.3647 | 7.3505 | 31.1318 | 0 | 0.0001 | 10619.1853 | 2241.941
April | 5578.2405 | 7.3073 | 31.4426 | 0 | 0.0001 | 10725.4166 | 2219.8411
May | 6809.799 | 8.9301 | 38.5178 | 0 | 0.0001 | 13138.9022 | 2711.163
June | 7596.1641 | 9.9652 | 43.0197 | 0 | 0.0001 | 14674.5607 | 3024.733
July | 7656.3143 | 10.0441 | 43.3606 | 0 | 0.0001 | 14790.8456 | 3048.6866
August | 8040.007 | 10.548 | 45.542 | 0 | 0.0001 | 15534.9538 | 3201.5476
September | 6804.6369 | 8.9248 | 38.5096 | 0 | 0.0001 | 13136.1184 | 2709.3013
October | 6199.467 | 8.1247 | 34.9958 | 0 | 0.0001 | 11937.4734 | 2467.5307
November | 5418.6075 | 7.0751 | 30.2201 | 0 | 0.0001 | 10308.3051 | 2153.3457
December | 5584.5504 | 7.095 | 28.389 | 0 | 0.0001 | 9682.8335 | 2193.9211
Annual Sum or Average | 76370.0437 | 99.3411 | 420.6569 | 0 | 0.0012 | 143487.7685 | 30300.8665
Minimum of Months | 5205.3094 | 6.5956 | 26.2144 | 0 | 0.0001 | 8941.0632 | 2042.664
Maximum of Months | 8040.007 | 10.548 | 45.542 | 0 | 0.0001 | 15534.9538 | 3201.5476
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 22120800000 | 22225.351 | 03-JAN-13:00 | 8961.612 | 3712.536 | 3052.923 | 0 | 6498.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 19782100000 | 22454.331 | 23-FEB-15:30 | 8961.612 | 3712.536 | 3052.923 | 0 | 6727.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 23495000000 | 22434.218 | 28-MAR-14:00 | 8961.612 | 3712.536 | 3052.923 | 0 | 6707.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23730000000 | 24741.687 | 21-APR-15:30 | 8961.612 | 3712.536 | 3052.923 | 0 | 9014.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 29069800000 | 28670.975 | 18-MAY-15:39 | 8961.612 | 3712.536 | 3052.923 | 0 | 12943.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 32467500000 | 29029.912 | 13-JUN-15:00 | 8961.612 | 3712.536 | 3052.923 | 0 | 13302.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 32724800000 | 30290.005 | 05-JUL-15:00 | 8961.612 | 3712.536 | 3052.923 | 0 | 14562.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 34371100000 | 29891.637 | 31-AUG-15:00 | 8961.612 | 3712.536 | 3052.923 | 0 | 14164.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 29063700000 | 28415.483 | 15-SEP-14:00 | 8961.612 | 3712.536 | 3052.923 | 0 | 12688.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 26411700000 | 26581.92 | 06-OCT-15:00 | 8961.612 | 3712.536 | 3052.923 | 0 | 10854.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 22807100000 | 23621.907 | 03-NOV-14:39 | 8961.612 | 3712.536 | 3052.923 | 0 | 7894.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 21423300000 | 22197.001 | 19-DEC-15:30 | 8961.612 | 3712.536 | 3052.923 | 0 | 6469.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 317467000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19782100000 | 22197.001 |  | 8961.612 | 3712.536 | 3052.923 | 0 | 6469.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 34371100000 | 30290.005 |  | 8961.612 | 3712.536 | 3052.923 | 0 | 14562.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11130.9 | 397.17 | 0 | 11528.07
Cost per Total Building Area ($/m2) | 21.78 | 0.78 | 0 | 22.55
Cost per Net Conditioned Building Area ($/m2) | 21.78 | 0.78 | 0 | 22.55

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 355.23 | 694.95 | 694.95
Net Site Energy | 355.23 | 694.95 | 694.95
Total Source Energy | 1057.99 | 2069.8 | 2069.8
Net Source Energy | 1057.99 | 2069.8 | 2069.8
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 20.55 | 0 | 0 | 0 | 0
Cooling | 81.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 55.11 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.12 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 323.55 | 31.67 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.261 | 0.279 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.261 | 0.279 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.261 | 0.279 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.261 | 0.279 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 16.73 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10179.95 | 8130.27 | 2049.68 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10330.99 | 7697.67 | 2633.32 | 0.75 | 3.08
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7430.12 | 5795.06 | 1635.06 | 0.78 | 3.15
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10193.22 | 7729.26 | 2463.96 | 0.76 | 3.1
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9157.34 | 7194.03 | 1963.31 | 0.79 | 3.16
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15275.34 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 13063.49 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 10173.27 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 13393.7 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 12549.25 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 713.31 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 618.45 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 494.13 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 635.79 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 618.87 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4498.7513 | 7.3361 | 23.5473 | 0 | 0.0001 | 173930.0528 | 1885.9321
February | 4023.6896 | 6.5926 | 21.286 | 0 | 0.0001 | 157228.6365 | 1689.9289
March | 4910.4264 | 8.2116 | 27.1787 | 0 | 0.0001 | 200763.7194 | 2079.1523
April | 4780.945 | 8.0396 | 26.784 | 0 | 0.0001 | 197850.3149 | 2028.8284
May | 5696.1409 | 9.5893 | 31.9889 | 0 | 0.0001 | 236298.6434 | 2418.2849
June | 6891.1589 | 11.6112 | 38.773 | 0 | 0.0001 | 286412.4043 | 2926.6476
July | 7051.4322 | 11.8818 | 39.6787 | 0 | 0.0001 | 293102.9641 | 2994.7703
August | 7254.3199 | 12.2242 | 40.8247 | 0 | 0.0001 | 301568.0786 | 3080.9976
September | 6120.9184 | 10.3093 | 34.4096 | 0 | 0.0001 | 254180.2635 | 2599.1151
October | 5142.8 | 8.6522 | 28.841 | 0 | 0.0001 | 213044.8546 | 2182.7998
November | 4424.7399 | 7.4117 | 24.5795 | 0 | 0.0001 | 181564.5389 | 1874.7494
December | 4659.8992 | 7.4796 | 23.5273 | 0 | 0.0001 | 173776.0648 | 1941.417
Annual Sum or Average | 65455.2216 | 109.339 | 361.4189 | 0 | 0.001 | 2669720 | 27702.6234
Minimum of Months | 4023.6896 | 6.5926 | 21.286 | 0 | 0.0001 | 157228.6365 | 1689.9289
Maximum of Months | 7254.3199 | 12.2242 | 40.8247 | 0 | 0.0001 | 301568.0786 | 3080.9976
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 21079300000 | 19237.724 | 27-JAN-14:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 3483.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 19055200000 | 20410.551 | 28-FEB-16:49 | 8961.612 | 3712.536 | 3080.558 | 0 | 4655.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 24331400000 | 23554.39 | 17-MAR-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 7799.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23978300000 | 23868.237 | 26-APR-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 8113.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 28638000000 | 27790.883 | 30-MAY-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 12036.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 34711500000 | 32813.575 | 28-JUN-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 17058.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 35522400000 | 32357.391 | 11-JUL-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 16602.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 36548300000 | 32365.508 | 01-AUG-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 16610.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 30805200000 | 29630.414 | 11-SEP-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 13875.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 25819800000 | 24811.814 | 13-OCT-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 9057.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 22004600000 | 22282.801 | 13-NOV-16:30 | 8961.612 | 3712.536 | 3080.558 | 0 | 6528.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 21060600000 | 18743.531 | 11-DEC-15:00 | 8961.612 | 3712.536 | 3080.558 | 0 | 2988.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 323555000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19055200000 | 18743.531 |  | 8961.612 | 3712.536 | 3080.558 | 0 | 2988.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 36548300000 | 32813.575 |  | 8961.612 | 3712.536 | 3080.558 | 0 | 17058.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11086.75 | 262.62 | 0 | 11349.36
Cost per Total Building Area ($/m2) | 21.69 | 0.51 | 0 | 22.2
Cost per Net Conditioned Building Area ($/m2) | 21.69 | 0.51 | 0 | 22.2

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 387.26 | 757.6 | 757.6
Net Site Energy | 387.26 | 757.6 | 757.6
Total Source Energy | 1095.27 | 2142.73 | 2142.73
Net Source Energy | 1095.27 | 2142.73 | 2142.73
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 79.56 | 0 | 0 | 0 | 0
Cooling | 46.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 62.46 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.75 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 295.95 | 91.31 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.409 | 0.454 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.409 | 0.454 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.409 | 0.454 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.409 | 0.454 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 16.73 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 42.95 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10297.38 | 8130.71 | 2166.68 | 0.79 | 3.17
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14051.32 | 10279.05 | 3772.27 | 0.73 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8508.14 | 6322.58 | 2185.56 | 0.74 | 3.07
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13524.81 | 9991.39 | 3533.42 | 0.74 | 3.06
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8673.47 | 6670.57 | 2002.9 | 0.77 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16094.3 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 17393.04 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 10865.99 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 17171.84 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 11873.88 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 703.75 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.69 | 804.83 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 506.11 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 793.26 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 558.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5784.4167 | 9.7326 | 21.9963 | 0 | 0.0001 | 39114.2347 | 2415.9271
February | 4835.0835 | 8.3313 | 19.3471 | 0 | 0.0001 | 34405.61 | 2037.5277
March | 4808.5104 | 8.9077 | 22.2911 | 0 | 0.0001 | 39648.154 | 2083.7979
April | 4479.4482 | 8.4744 | 21.6296 | 0 | 0.0001 | 38473.2908 | 1957.4734
May | 5060.1461 | 9.7142 | 25.1261 | 0 | 0.0001 | 44693.8324 | 2224.2782
June | 5746.1275 | 11.0452 | 28.6011 | 0 | 0.0001 | 50875.1892 | 2527.1088
July | 5747.0564 | 11.0468 | 28.6049 | 0 | 0.0001 | 50881.975 | 2527.5021
August | 6164.1575 | 11.8515 | 30.6954 | 0 | 0.0001 | 54600.6434 | 2711.2126
September | 5282.1755 | 10.1498 | 26.2743 | 0 | 0.0001 | 46736.4242 | 2322.7376
October | 4494.0079 | 8.574 | 22.0534 | 0 | 0.0001 | 39227.6573 | 1970.4942
November | 4540.7453 | 8.3381 | 20.6892 | 0 | 0.0001 | 36798.1856 | 1960.9663
December | 5288.1204 | 9.1331 | 21.2639 | 0 | 0.0001 | 37814.6401 | 2230.4002
Annual Sum or Average | 62229.9954 | 115.2988 | 288.5723 | 0 | 0.0011 | 513269.8369 | 26969.426
Minimum of Months | 4479.4482 | 8.3313 | 19.3471 | 0 | 0.0001 | 34405.61 | 1957.4734
Maximum of Months | 6164.1575 | 11.8515 | 30.6954 | 0 | 0.0001 | 54600.6434 | 2711.2126
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 22552900000 | 18291.192 | 23-JAN-16:00 | 8961.612 | 3712.536 | 3366.805 | 0 | 2250.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 19837900000 | 17860.871 | 27-FEB-16:00 | 8961.612 | 3712.536 | 3366.805 | 0 | 1819.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 22860800000 | 20466.397 | 28-MAR-15:00 | 8961.612 | 3712.536 | 3366.805 | 0 | 4425.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 22183300000 | 23292.179 | 14-APR-15:00 | 8961.612 | 3712.536 | 3366.805 | 0 | 7251.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25770000000 | 26204.432 | 15-MAY-15:20 | 8961.612 | 3712.536 | 3366.805 | 0 | 10163.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 29334200000 | 28268.419 | 19-JUN-15:50 | 8961.612 | 3712.536 | 3366.805 | 0 | 12227.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 29338100000 | 30790.988 | 03-JUL-15:00 | 8961.612 | 3712.536 | 3366.805 | 0 | 14750.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 31482200000 | 28043.313 | 17-AUG-15:39 | 8961.612 | 3712.536 | 3366.805 | 0 | 12002.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 26947800000 | 26540.585 | 11-SEP-13:00 | 8961.612 | 3712.536 | 3366.805 | 0 | 10499.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 22618300000 | 24005.497 | 12-OCT-15:00 | 8961.612 | 3712.536 | 3366.805 | 0 | 7964.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 21217500000 | 19753.889 | 22-NOV-15:30 | 8961.612 | 3712.536 | 3366.805 | 0 | 3712.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 21803600000 | 17195.86 | 05-DEC-15:09 | 8961.612 | 3712.536 | 3366.805 | 0 | 1154.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 295947000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19837900000 | 17195.86 |  | 8961.612 | 3712.536 | 3366.805 | 0 | 1154.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 31482200000 | 30790.988 |  | 8961.612 | 3712.536 | 3366.805 | 0 | 14750.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9500.46 | 875.74 | 0 | 10376.2
Cost per Total Building Area ($/m2) | 18.59 | 1.71 | 0 | 20.3
Cost per Net Conditioned Building Area ($/m2) | 18.59 | 1.71 | 0 | 20.3

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 290.71 | 568.72 | 568.72
Net Site Energy | 290.71 | 568.72 | 568.72
Total Source Energy | 849.9 | 1662.7 | 1662.7
Net Source Energy | 849.9 | 1662.7 | 1662.7
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13.2 | 0 | 0 | 0 | 0
Cooling | 32.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 46.64 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.68 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 265.83 | 24.88 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.568 | 0.659 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.568 | 0.659 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.568 | 0.659 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.568 | 0.659 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 16.73 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9070.6 | 7201.63 | 1868.97 | 0.79 | 3.18
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8898.51 | 6942.61 | 1955.9 | 0.78 | 3.15
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5747.86 | 4590.56 | 1157.3 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7871.34 | 6081.73 | 1789.61 | 0.77 | 3.13
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8980.42 | 7172.26 | 1808.16 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13789.13 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 12757.44 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8584.01 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 11183.24 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 13058.07 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 627.45 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 592.22 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 402.75 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 512.52 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 629.26 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2042.3541 | 1.7606 | 16.7647 | 0 | 0 | 101147.7698 | 758.0105
February | 1787.385 | 1.5384 | 15.087 | 0 | 0 | 91027.2309 | 664.6467
March | 2047.3995 | 1.7601 | 17.6697 | 0 | 0 | 106611.3911 | 762.5179
April | 1864.4825 | 1.6006 | 16.488 | 0 | 0 | 99482.7489 | 695.6046
May | 2000.8018 | 1.7159 | 18.0123 | 0 | 0 | 108680.9639 | 747.4355
June | 2040.1864 | 1.7488 | 18.5112 | 0 | 0 | 111691.7157 | 762.5888
July | 2119.4846 | 1.8165 | 19.2901 | 0 | 0 | 116391.7905 | 792.4105
August | 2379.8703 | 2.0393 | 21.7101 | 0 | 0 | 130993.5322 | 889.9137
September | 2112.0635 | 1.8101 | 19.2253 | 0 | 0 | 116000.6931 | 789.6443
October | 2044.6356 | 1.7528 | 18.514 | 0 | 0 | 111708.5185 | 764.1372
November | 1920.414 | 1.6487 | 16.978 | 0 | 0 | 102439.773 | 716.4579
December | 1976.2904 | 1.7014 | 16.6233 | 0 | 0 | 100296.572 | 734.7146
Annual Sum or Average | 24335.3676 | 20.8931 | 214.8735 | 0 | 0.0001 | 1296470 | 9078.0822
Minimum of Months | 1787.385 | 1.5384 | 15.087 | 0 | 0 | 91027.2309 | 664.6467
Maximum of Months | 2379.8703 | 2.0393 | 21.7101 | 0 | 0 | 130993.5322 | 889.9137
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 20739100000 | 20424.153 | 25-JAN-15:30 | 8961.612 | 3712.536 | 2764.194 | 0 | 4985.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 18664000000 | 20239.316 | 13-FEB-14:00 | 8961.612 | 3712.536 | 2764.194 | 0 | 4800.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 21859300000 | 20848.338 | 31-MAR-14:00 | 8961.612 | 3712.536 | 2764.194 | 0 | 5409.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 20397700000 | 21974.992 | 11-APR-15:00 | 8961.612 | 3712.536 | 2764.194 | 0 | 6536.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 22283700000 | 22532.205 | 30-MAY-15:50 | 8961.612 | 3712.536 | 2764.194 | 0 | 7093.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 22901000000 | 22560.882 | 30-JUN-15:39 | 8961.612 | 3712.536 | 2764.194 | 0 | 7122.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 23864700000 | 23756.949 | 10-JUL-15:50 | 8961.612 | 3712.536 | 2764.194 | 0 | 8318.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26858600000 | 24989.506 | 08-AUG-15:30 | 8961.612 | 3712.536 | 2764.194 | 0 | 9551.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23784500000 | 25019.796 | 25-SEP-15:09 | 8961.612 | 3712.536 | 2764.194 | 0 | 9581.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 22904400000 | 22953.804 | 05-OCT-14:39 | 8961.612 | 3712.536 | 2764.194 | 0 | 7515.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 21004000000 | 21061.456 | 10-NOV-14:00 | 8961.612 | 3712.536 | 2764.194 | 0 | 5623.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 20564600000 | 20588.841 | 19-DEC-13:09 | 8961.612 | 3712.536 | 2764.194 | 0 | 5150.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 265826000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 18664000000 | 20239.316 |  | 8961.612 | 3712.536 | 2764.194 | 0 | 4800.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 26858600000 | 25019.796 |  | 8961.612 | 3712.536 | 2764.194 | 0 | 9581.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10717.07 | 213.95 | 0 | 10931.02
Cost per Total Building Area ($/m2) | 20.97 | 0.42 | 0 | 21.38
Cost per Net Conditioned Building Area ($/m2) | 20.97 | 0.42 | 0 | 21.38

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 352.23 | 689.08 | 689.08
Net Site Energy | 352.23 | 689.08 | 689.08
Total Source Energy | 1126.94 | 2204.68 | 2204.68
Net Source Energy | 1126.94 | 2204.68 | 2204.68
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 42.11 | 0 | 0 | 0 | 0
Cooling | 56.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 55.6 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.41 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 298.71 | 53.51 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.273 | 0.292 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.273 | 0.292 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.273 | 0.292 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.273 | 0.292 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 16.73 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10303.47 | 8228.92 | 2074.55 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10017.63 | 7802.93 | 2214.7 | 0.78 | 3.15
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6088.03 | 4862.23 | 1225.79 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9499.72 | 7528.1 | 1971.62 | 0.79 | 3.17
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8091.19 | 6462.07 | 1629.12 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15264.18 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 13719.18 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8734.75 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 13538.96 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 11306.48 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 721.96 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 664.26 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 426.59 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 654.42 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 566.95 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5725.7188 | 8.7342 | 33.2652 | 0 | 0.0001 | 165879.9097 | 2349.2934
February | 4498.0744 | 7.1662 | 28.9971 | 0 | 0.0001 | 144608.9259 | 1877.2564
March | 5235.8836 | 8.3565 | 33.893 | 0 | 0.0001 | 169025.7082 | 2186.7227
April | 4921.5053 | 8.0233 | 33.4416 | 0 | 0.0001 | 166780.5881 | 2072.9367
May | 5738.4588 | 9.3712 | 39.1438 | 0 | 0.0001 | 195219.3881 | 2418.7073
June | 6848.6598 | 11.1968 | 46.8354 | 0 | 0.0001 | 233580.0143 | 2887.9588
July | 7059.1375 | 11.5419 | 48.2839 | 0 | 0.0001 | 240803.7162 | 2976.8135
August | 7442.1114 | 12.1694 | 50.9163 | 0 | 0.0001 | 253932.3227 | 3138.4551
September | 6117.5702 | 9.9981 | 41.8033 | 0 | 0.0001 | 208483.3705 | 2579.312
October | 5289.5314 | 8.6283 | 35.9897 | 0 | 0.0001 | 179488.8667 | 2228.4733
November | 4763.9903 | 7.6527 | 31.3023 | 0 | 0.0001 | 156107.4415 | 1994.7706
December | 5432.0646 | 8.3947 | 32.5787 | 0 | 0.0001 | 162460.8098 | 2240.0792
Annual Sum or Average | 69072.706 | 111.2333 | 456.4503 | 0 | 0.0009 | 2276370 | 28950.7789
Minimum of Months | 4498.0744 | 7.1662 | 28.9971 | 0 | 0.0001 | 144608.9259 | 1877.2564
Maximum of Months | 7442.1114 | 12.1694 | 50.9163 | 0 | 0.0001 | 253932.3227 | 3138.4551
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 21767400000 | 17594.843 | 18-JAN-16:49 | 8961.612 | 3712.536 | 3034.177 | 0 | 723.518 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 18976200000 | 18054.027 | 27-FEB-15:00 | 8961.612 | 3712.536 | 3034.177 | 0 | 2345.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 22180200000 | 19477.639 | 31-MAR-15:00 | 8961.612 | 3712.536 | 3034.177 | 0 | 3769.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 21885600000 | 23286.695 | 21-APR-15:50 | 8961.612 | 3712.536 | 3034.177 | 0 | 7578.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25617500000 | 25674.867 | 31-MAY-15:00 | 8961.612 | 3712.536 | 3034.177 | 0 | 9966.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 30651300000 | 30673.927 | 27-JUN-15:00 | 8961.612 | 3712.536 | 3034.177 | 0 | 14965.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 31599200000 | 29967.173 | 24-JUL-15:00 | 8961.612 | 3712.536 | 3034.177 | 0 | 14258.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 33322000000 | 29117.841 | 04-AUG-15:00 | 8961.612 | 3712.536 | 3034.177 | 0 | 13409.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 27358000000 | 28122.588 | 01-SEP-14:00 | 8961.612 | 3712.536 | 3034.177 | 0 | 12414.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 23553300000 | 23620.63 | 03-OCT-15:30 | 8961.612 | 3712.536 | 3034.177 | 0 | 7912.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 20485000000 | 19463.88 | 10-NOV-16:40 | 8961.612 | 3712.536 | 3034.177 | 0 | 2592.555 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 21318800000 | 18219.047 | 05-DEC-16:30 | 8961.612 | 3712.536 | 3034.177 | 0 | 1347.722 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 298715000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 18976200000 | 17594.843 |  | 8961.612 | 3712.536 | 3034.177 | 0 | 723.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 33322000000 | 30673.927 |  | 8961.612 | 3712.536 | 3034.177 | 0 | 14965.603 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8505.15 | 412.24 | 0 | 8917.38
Cost per Total Building Area ($/m2) | 16.64 | 0.81 | 0 | 17.45
Cost per Net Conditioned Building Area ($/m2) | 16.64 | 0.81 | 0 | 17.45

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 303.47 | 593.7 | 593.7
Net Site Energy | 303.47 | 593.7 | 593.7
Total Source Energy | 810.23 | 1585.08 | 1585.08
Net Source Energy | 810.23 | 1585.08 | 1585.08
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 52.41 | 0 | 0 | 0 | 0
Cooling | 9.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 43.12 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.01 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 239.06 | 64.42 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.5 | 0.569 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.5 | 0.569 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.5 | 0.569 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.5 | 0.569 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 16.73 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 42.95 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6718.7 | 5365.92 | 1352.77 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9026.97 | 7209.44 | 1817.53 | 0.8 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4794.03 | 3828.77 | 965.25 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7540.84 | 6022.53 | 1518.31 | 0.8 | 3.19
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6472.68 | 5169.44 | 1303.24 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11060.79 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 13850 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 7437.14 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 11786.16 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 9768.37 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 470.78 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 632.52 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 335.92 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 528.39 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 453.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2561.9467 | 2.2344 | 16.392 | 0 | 0 | 98881.8682 | 936.7054
February | 1861.4172 | 1.6091 | 14.4714 | 0 | 0 | 87308.8075 | 688.3914
March | 2195.3713 | 1.9 | 16.6629 | 0 | 0 | 100528.6106 | 810.6596
April | 1885.7238 | 1.6267 | 15.269 | 0 | 0 | 92123.3108 | 699.2374
May | 1897.4923 | 1.6317 | 16.2836 | 0 | 0 | 98247.898 | 706.4058
June | 1859.0155 | 1.5965 | 16.3359 | 0 | 0 | 98564.9663 | 693.2486
July | 1801.2497 | 1.5458 | 16.014 | 0 | 0 | 96623.518 | 672.2737
August | 1954.469 | 1.6773 | 17.3839 | 0 | 0 | 104888.6537 | 729.4825
September | 1842.6659 | 1.5811 | 16.4296 | 0 | 0 | 99131.2237 | 687.8759
October | 1878.2179 | 1.6137 | 16.3805 | 0 | 0 | 98833.5398 | 700.0306
November | 1924.5349 | 1.6602 | 15.5865 | 0 | 0 | 94038.4925 | 713.6385
December | 2413.1315 | 2.1012 | 16.0382 | 0 | 0 | 96750.481 | 884.1208
Annual Sum or Average | 24075.2357 | 20.7778 | 193.2476 | 0 | 0.0001 | 1165920 | 8922.0703
Minimum of Months | 1801.2497 | 1.5458 | 14.4714 | 0 | 0 | 87308.8075 | 672.2737
Maximum of Months | 2561.9467 | 2.2344 | 17.3839 | 0 | 0 | 104888.6537 | 936.7054
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 20274500000 | 16258.29 | 02-JAN-16:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 17901600000 | 18342.137 | 15-FEB-15:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 3246.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 20612100000 | 16623.691 | 01-MAR-14:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 1528.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 18888700000 | 19041.195 | 13-APR-15:20 | 8961.612 | 3712.536 | 2421.142 | 0 | 3945.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 20144500000 | 19224.617 | 25-MAY-15:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 4129.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 20209500000 | 20500.34 | 16-JUN-15:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 5405.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 19811500000 | 22032.541 | 03-JUL-14:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 6937.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 21506100000 | 19957.244 | 15-AUG-12:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 4861.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 20325600000 | 23530.557 | 28-SEP-15:30 | 8961.612 | 3712.536 | 2421.142 | 0 | 8435.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20264600000 | 19878.996 | 13-OCT-15:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 4783.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 19281400000 | 17424.735 | 14-NOV-16:00 | 8961.612 | 3712.536 | 2421.142 | 0 | 1166.445 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 19837500000 | 16622.673 | 07-DEC-16:49 | 8961.612 | 3712.536 | 2421.142 | 0 | 364.383 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 239058000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 17901600000 | 16258.29 |  | 8961.612 | 3712.536 | 2421.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 21506100000 | 23530.557 |  | 8961.612 | 3712.536 | 2421.142 | 0 | 8435.267 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10741.48 | 557.57 | 0 | 11299.05
Cost per Total Building Area ($/m2) | 21.01 | 1.09 | 0 | 22.1
Cost per Net Conditioned Building Area ($/m2) | 21.01 | 1.09 | 0 | 22.1

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 429.79 | 840.82 | 840.82
Net Site Energy | 429.79 | 840.82 | 840.82
Total Source Energy | 1184.56 | 2317.41 | 2317.41
Net Source Energy | 1184.56 | 2317.41 | 2317.41
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 129.79 | 0 | 0 | 0 | 0
Cooling | 34.98 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 66.26 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.06 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 287.94 | 141.85 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.329 | 0.358 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.329 | 0.358 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.329 | 0.358 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.329 | 0.358 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 16.73 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 42.95 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10968.38 | 8728.54 | 2239.83 | 0.8 | 3.18
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14945.28 | 10650.3 | 4294.98 | 0.71 | 3.01
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8382.26 | 6237.26 | 2145 | 0.74 | 3.07
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14839.06 | 10540.93 | 4298.13 | 0.71 | 3.01
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8181.96 | 6158.32 | 2023.64 | 0.75 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 18134.27 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 18177.87 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 11263.96 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 17938.76 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 11291.77 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 762.57 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.69 | 802.15 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 500.19 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 790.04 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 501.6 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5907.0251 | 9.5618 | 23.2156 | 0 | 0.0001 | 1443.2438 | 2428.4717
February | 5011.029 | 8.3493 | 21.0076 | 0 | 0.0001 | 1306.0829 | 2081.8629
March | 4655.7053 | 8.4702 | 23.4543 | 0 | 0.0001 | 1458.4991 | 1999.4266
April | 3740.3564 | 7.1648 | 20.8302 | 0 | 0.0001 | 1295.4465 | 1639.2314
May | 3935.8062 | 7.7658 | 23.1702 | 0 | 0.0001 | 1441.0459 | 1745.6139
June | 4704.7983 | 9.3501 | 28.0671 | 0 | 0.0001 | 1745.6261 | 2092.8032
July | 4807.6917 | 9.5571 | 28.6945 | 0 | 0.0001 | 1784.647 | 2138.7972
August | 5249.8665 | 10.4398 | 31.3542 | 0 | 0.0001 | 1950.0685 | 2335.8488
September | 4106.4115 | 8.1483 | 24.4274 | 0 | 0.0001 | 1519.2488 | 1825.4677
October | 4010.2321 | 7.7679 | 22.8087 | 0 | 0.0001 | 1418.5169 | 1765.3806
November | 4249.5633 | 7.8422 | 22.0205 | 0 | 0.0001 | 1369.3794 | 1835.1452
December | 5414.0359 | 9.0673 | 22.9539 | 0 | 0.0001 | 1427.1099 | 2253.5475
Annual Sum or Average | 55792.5214 | 103.4847 | 292.0042 | 0 | 0.0012 | 18158.9147 | 24141.5966
Minimum of Months | 3740.3564 | 7.1648 | 20.8302 | 0 | 0.0001 | 1295.4465 | 1639.2314
Maximum of Months | 5907.0251 | 10.4398 | 31.3542 | 0 | 0.0001 | 1950.0685 | 2428.4717
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 22884700000 | 17193.703 | 02-JAN-16:49 | 8961.612 | 3712.536 | 3356.555 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 20709800000 | 16307.592 | 15-FEB-15:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 276.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 23126600000 | 19724.372 | 09-MAR-15:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 3693.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 20541100000 | 20824.614 | 04-APR-15:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 4793.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 22849800000 | 23715.2 | 31-MAY-15:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 7684.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 27679400000 | 28573.657 | 30-JUN-15:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 12542.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 28298100000 | 29291.649 | 25-JUL-12:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 13260.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 30921100000 | 29296.284 | 17-AUG-15:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 13265.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 24089800000 | 25443.656 | 08-SEP-15:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 9412.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 22492600000 | 22920.197 | 03-OCT-14:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 6889.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 21713400000 | 20862.4 | 03-NOV-13:00 | 8961.612 | 3712.536 | 3356.555 | 0 | 4831.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 22628800000 | 17193.703 | 01-DEC-16:40 | 8961.612 | 3712.536 | 3356.555 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 287935000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 20541100000 | 16307.592 |  | 8961.612 | 3712.536 | 3356.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 30921100000 | 29296.284 |  | 8961.612 | 3712.536 | 3356.555 | 0 | 13265.582 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5946 | 1373.63 | 0 | 7319.63
Cost per Total Building Area ($/m2) | 11.63 | 2.69 | 0 | 14.32
Cost per Net Conditioned Building Area ($/m2) | 11.63 | 2.69 | 0 | 14.32

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 387.76 | 758.59 | 758.59
Net Site Energy | 387.76 | 758.59 | 758.59
Total Source Energy | 1060.88 | 2075.45 | 2075.45
Net Source Energy | 1060.88 | 2075.45 | 2075.45
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 89.39 | 0 | 0 | 0 | 0
Cooling | 32.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 67.41 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 286.37 | 101.39 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.335 | 0.365 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.335 | 0.365 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.335 | 0.365 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.335 | 0.365 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 16.73 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 42.95 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9628.09 | 7689.53 | 1938.57 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12183.84 | 9730.69 | 2453.15 | 0.8 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7598.22 | 6068.36 | 1529.86 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11956.83 | 9549.38 | 2407.44 | 0.8 | 3.19
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7994.78 | 6385.07 | 1609.71 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13403.04 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 15750.64 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 9767.31 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 15491.11 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 10220.67 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 674.64 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 853.72 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 532.41 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.72 | 837.81 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 560.19 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7403.2722 | 11.9085 | 28.1142 | 0 | 0.0001 | 29227.6087 | 3071.2173
February | 6247.986 | 10.2758 | 24.9481 | 0 | 0.0001 | 25937.8502 | 2614.0821
March | 6733.6952 | 11.3153 | 28.1907 | 0 | 0.0001 | 29310.8033 | 2840.9134
April | 5689.0965 | 9.8235 | 25.2437 | 0 | 0.0001 | 26248.5364 | 2426.0494
May | 6538.8164 | 11.4137 | 29.6798 | 0 | 0.0001 | 30862.0754 | 2800.4682
June | 7081.4983 | 12.3811 | 32.252 | 0 | 0.0001 | 33536.8323 | 3034.8639
July | 7283.9204 | 12.7371 | 33.1853 | 0 | 0.0001 | 34507.2742 | 3121.82
August | 7671.431 | 13.4161 | 34.9581 | 0 | 0.0001 | 36350.7111 | 3288.036
September | 6495.968 | 11.3537 | 29.5651 | 0 | 0.0001 | 30742.8336 | 2783.5617
October | 6021.4791 | 10.4176 | 26.8276 | 0 | 0.0001 | 27895.5909 | 2569.7659
November | 6485.919 | 10.825 | 26.7531 | 0 | 0.0001 | 27815.6392 | 2729.1248
December | 7344.5976 | 11.7734 | 27.6712 | 0 | 0.0001 | 28766.7219 | 3042.8855
Annual Sum or Average | 80997.6797 | 137.6409 | 347.3887 | 0 | 0.0014 | 361202.4771 | 34322.7882
Minimum of Months | 5689.0965 | 9.8235 | 24.9481 | 0 | 0.0001 | 25937.8502 | 2426.0494
Maximum of Months | 7671.431 | 13.4161 | 34.9581 | 0 | 0.0001 | 36350.7111 | 3288.036
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 23172000000 | 17453.718 | 26-JAN-15:00 | 8961.612 | 3712.536 | 3458.777 | 0 | 1320.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 20563800000 | 18810.141 | 14-FEB-15:00 | 8961.612 | 3712.536 | 3458.777 | 0 | 2677.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 23238000000 | 19025.799 | 02-MAR-15:00 | 8961.612 | 3712.536 | 3458.777 | 0 | 2892.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 20810200000 | 21428.856 | 21-APR-15:00 | 8961.612 | 3712.536 | 3458.777 | 0 | 5295.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 24467800000 | 23439.396 | 31-MAY-15:00 | 8961.612 | 3712.536 | 3458.777 | 0 | 7306.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 26588400000 | 25737.908 | 29-JUN-15:30 | 8961.612 | 3712.536 | 3458.777 | 0 | 9604.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 27357800000 | 26586.982 | 03-JUL-15:30 | 8961.612 | 3712.536 | 3458.777 | 0 | 10454.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 28819300000 | 26617.268 | 01-AUG-15:30 | 8961.612 | 3712.536 | 3458.777 | 0 | 10484.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 24373300000 | 23371.335 | 29-SEP-14:50 | 8961.612 | 3712.536 | 3458.777 | 0 | 7238.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 22116000000 | 21485.415 | 11-OCT-15:00 | 8961.612 | 3712.536 | 3458.777 | 0 | 5352.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 22052600000 | 18610.733 | 08-NOV-15:39 | 8961.612 | 3712.536 | 3458.777 | 0 | 2477.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 22806600000 | 17747.411 | 08-DEC-16:49 | 8961.612 | 3712.536 | 3458.777 | 0 | 451.486 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 286366000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 20563800000 | 17453.718 |  | 8961.612 | 3712.536 | 3458.777 | 0 | 451.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 28819300000 | 26617.268 |  | 8961.612 | 3712.536 | 3458.777 | 0 | 10484.343 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5966.34 | 697.26 | 0 | 6663.6
Cost per Total Building Area ($/m2) | 11.67 | 1.36 | 0 | 13.04
Cost per Net Conditioned Building Area ($/m2) | 11.67 | 1.36 | 0 | 13.04

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 366.52 | 717.04 | 717.04
Net Site Energy | 366.52 | 717.04 | 717.04
Total Source Energy | 561.69 | 1098.85 | 1098.85
Net Source Energy | 561.69 | 1098.85 | 1098.85
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 105.92 | 0 | 0 | 0 | 0
Cooling | 8.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 52.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.22 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 248.38 | 118.14 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.363 | 0.399 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.363 | 0.399 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.363 | 0.399 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.363 | 0.399 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 16.73 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 42.95 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7083.73 | 5657.46 | 1426.27 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9152.86 | 7309.98 | 1842.88 | 0.8 | 3.19
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5669.99 | 4528.37 | 1141.62 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8968.66 | 7162.87 | 1805.79 | 0.8 | 3.19
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6814.24 | 5442.23 | 1372.01 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 12147.72 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 14395.81 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8869.26 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 14143.45 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 10436.95 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 496.36 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 641.34 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.3 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 628.43 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 477.47 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 2314.1129 | 2.8266 | 4.6455 | 0 | 0 | 61320.1725 | 878.6808
February | 1705.9402 | 2.1923 | 4.1174 | 0 | 0 | 54372.2475 | 659.3748
March | 1831.4517 | 2.3945 | 4.6818 | 0 | 0 | 61832.8652 | 712.2732
April | 1383.6732 | 1.9054 | 4.1525 | 0 | 0 | 54858.4082 | 548.4489
May | 1153.33 | 1.7301 | 4.3668 | 0 | 0 | 57710.2186 | 472.3379
June | 1081.1244 | 1.6699 | 4.4007 | 0 | 0 | 58164.2834 | 447.9218
July | 1069.3798 | 1.6722 | 4.4836 | 0 | 0 | 59261.2686 | 445.2473
August | 1160.6528 | 1.8216 | 4.9089 | 0 | 0 | 64883.8983 | 483.9654
September | 1080.9387 | 1.6561 | 4.3139 | 0 | 0 | 57014.8178 | 446.4005
October | 1266.5521 | 1.8232 | 4.3054 | 0 | 0 | 56889.5394 | 510.4858
November | 1782.3828 | 2.3111 | 4.4332 | 0 | 0 | 58546.775 | 691.1243
December | 2262.6565 | 2.7649 | 4.5491 | 0 | 0 | 60046.7377 | 859.2567
Annual Sum or Average | 18092.1953 | 24.7679 | 53.3588 | 0 | 0.0002 | 704901.2321 | 7155.5174
Minimum of Months | 1069.3798 | 1.6561 | 4.1174 | 0 | 0 | 54372.2475 | 445.2473
Maximum of Months | 2314.1129 | 2.8266 | 4.9089 | 0 | 0 | 64883.8983 | 878.6808
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 21606800000 | 16478.049 | 02-JAN-16:30 | 8961.612 | 3712.536 | 2640.901 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 19158600000 | 15808.915 | 21-FEB-15:50 | 8961.612 | 3712.536 | 2640.901 | 0 | 493.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 21787500000 | 17897.105 | 29-MAR-15:50 | 8961.612 | 3712.536 | 2640.901 | 0 | 2582.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19330000000 | 17276.38 | 18-APR-15:00 | 8961.612 | 3712.536 | 2640.901 | 0 | 1961.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 20334800000 | 19640.532 | 04-MAY-15:00 | 8961.612 | 3712.536 | 2640.901 | 0 | 4325.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 20494800000 | 20685.928 | 28-JUN-15:30 | 8961.612 | 3712.536 | 2640.901 | 0 | 5370.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 20881300000 | 22292.803 | 24-JUL-14:00 | 8961.612 | 3712.536 | 2640.901 | 0 | 6977.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 22862500000 | 21818.478 | 07-AUG-15:20 | 8961.612 | 3712.536 | 2640.901 | 0 | 6503.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 20089800000 | 21670.421 | 01-SEP-15:00 | 8961.612 | 3712.536 | 2640.901 | 0 | 6355.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20045600000 | 18137.857 | 17-OCT-15:39 | 8961.612 | 3712.536 | 2640.901 | 0 | 2822.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 20629600000 | 16537.423 | 14-NOV-16:00 | 8961.612 | 3712.536 | 2640.901 | 0 | 59.374 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 21158100000 | 16478.049 | 01-DEC-16:19 | 8961.612 | 3712.536 | 2640.901 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 248380000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 19158600000 | 15808.915 |  | 8961.612 | 3712.536 | 2640.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 22862500000 | 22292.803 |  | 8961.612 | 3712.536 | 2640.901 | 0 | 6977.754 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5040.77 | 997.1 | 0 | 6037.87
Cost per Total Building Area ($/m2) | 9.86 | 1.95 | 0 | 11.81
Cost per Net Conditioned Building Area ($/m2) | 9.86 | 1.95 | 0 | 11.81

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 494.78 | 967.95 | 967.95
Net Site Energy | 494.78 | 967.95 | 967.95
Total Source Energy | 1279.56 | 2503.25 | 2503.25
Net Source Energy | 1279.56 | 2503.25 | 2503.25
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 181.2 | 0 | 0 | 0 | 0
Cooling | 29.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 85.1 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.33 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 301.25 | 193.53 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.296 | 0.319 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.296 | 0.319 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.296 | 0.319 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.296 | 0.319 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10661.92 | 8515.2 | 2146.72 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19682.97 | 13997.89 | 5685.08 | 0.71 | 3.04
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10720.15 | 8054.01 | 2666.13 | 0.75 | 3.09
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19590.79 | 13869.71 | 5721.08 | 0.71 | 3.03
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10584.14 | 7992.13 | 2592.01 | 0.76 | 3.1
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 18443.32 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 23396.16 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 14479.62 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 23069.13 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 14467.54 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.64 | 747.08 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.91 | 1032.22 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 654.4 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.89 | 1015.67 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 653.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11137.8662 | 17.8721 | 46.5784 | 0 | 0.0001 | 10719.7432 | 4596.9789
February | 9489.3608 | 15.5922 | 41.8749 | 0 | 0.0001 | 9637.8814 | 3951.5212
March | 9959.9436 | 16.9549 | 47.4849 | 0 | 0.0001 | 10930.0287 | 4203.8344
April | 8065.106 | 14.2803 | 41.7541 | 0 | 0.0001 | 9611.7412 | 3456.7526
May | 8311.4097 | 15.0252 | 44.8803 | 0 | 0.0001 | 10331.8049 | 3591.842
June | 9621.5954 | 17.4698 | 52.4111 | 0 | 0.0002 | 12065.5714 | 4165.3231
July | 9822.6553 | 17.838 | 53.5254 | 0 | 0.0002 | 12322.0822 | 4252.6679
August | 10290.718 | 18.6891 | 56.0825 | 0 | 0.0002 | 12910.7531 | 4455.4176
September | 8411.0011 | 15.2571 | 45.7293 | 0 | 0.0001 | 10527.329 | 3639.8455
October | 8263.996 | 14.7924 | 43.7427 | 0 | 0.0001 | 10069.7289 | 3557.2916
November | 9027.2288 | 15.5511 | 44.1409 | 0 | 0.0001 | 10160.5906 | 3827.7488
December | 10618.1769 | 17.268 | 45.7827 | 0 | 0.0001 | 10537.0186 | 4404.4581
Annual Sum or Average | 113019.0577 | 196.59 | 563.9871 | 0 | 0.0017 | 129824.2732 | 48103.6818
Minimum of Months | 8065.106 | 14.2803 | 41.7541 | 0 | 0.0001 | 9611.7412 | 3456.7526
Maximum of Months | 11137.8662 | 18.6891 | 56.0825 | 0 | 0.0002 | 12910.7531 | 4596.9789
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 24874400000 | 17940.304 | 02-JAN-16:30 | 8961.612 | 3712.536 | 4103.156 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22364000000 | 17940.304 | 01-FEB-16:00 | 8961.612 | 3712.536 | 4103.156 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 25362300000 | 19363.172 | 31-MAR-15:30 | 8961.612 | 3712.536 | 4103.156 | 0 | 2585.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 22303300000 | 19989.608 | 07-APR-14:00 | 8961.612 | 3712.536 | 4103.156 | 0 | 3212.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 23974200000 | 24408.014 | 30-MAY-15:00 | 8961.612 | 3712.536 | 4103.156 | 0 | 7630.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 27997200000 | 28387.496 | 08-JUN-12:00 | 8961.612 | 3712.536 | 4103.156 | 0 | 11610.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 28592500000 | 29428.446 | 03-JUL-14:00 | 8961.612 | 3712.536 | 4103.156 | 0 | 12651.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 29958400000 | 28959.257 | 04-AUG-15:00 | 8961.612 | 3712.536 | 4103.156 | 0 | 12181.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 24427900000 | 25394.132 | 27-SEP-15:30 | 8961.612 | 3712.536 | 4103.156 | 0 | 8616.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 23366000000 | 22392.506 | 31-OCT-13:30 | 8961.612 | 3712.536 | 4103.156 | 0 | 5615.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 23576900000 | 21714.502 | 02-NOV-14:39 | 8961.612 | 3712.536 | 4103.156 | 0 | 4937.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24450400000 | 17940.304 | 01-DEC-16:19 | 8961.612 | 3712.536 | 4103.156 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 301247000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22303300000 | 17940.304 |  | 8961.612 | 3712.536 | 4103.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 29958400000 | 29428.446 |  | 8961.612 | 3712.536 | 4103.156 | 0 | 12651.142 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5083.48 | 1604.72 | 0 | 6688.2
Cost per Total Building Area ($/m2) | 9.95 | 3.14 | 0 | 13.08
Cost per Net Conditioned Building Area ($/m2) | 9.95 | 3.14 | 0 | 13.08

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 434.2 | 849.45 | 849.45
Net Site Energy | 434.2 | 849.45 | 849.45
Total Source Energy | 1122.72 | 2196.42 | 2196.42
Net Source Energy | 1122.72 | 2196.42 | 2196.42
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 130.52 | 0 | 0 | 0 | 0
Cooling | 21.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 83.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.32 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 291.36 | 142.84 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.285 | 0.306 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.285 | 0.306 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.285 | 0.306 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.285 | 0.306 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9536.39 | 7616.29 | 1920.1 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15315.39 | 12231.72 | 3083.67 | 0.8 | 3.17
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9557.1 | 7632.83 | 1924.27 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15095.83 | 12056.37 | 3039.47 | 0.8 | 3.17
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9571.62 | 7644.42 | 1927.19 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14041.9 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 19881.2 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 12332.55 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 19630.63 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 12349.12 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 668.21 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.93 | 1053.99 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 669.67 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.91 | 1038.88 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 670.68 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8226.3091 | 12.9775 | 29.8602 | 0 | 0.0001 | 31040.8446 | 3387.6509
February | 7033.6044 | 11.3326 | 26.8119 | 0 | 0.0001 | 27873.8582 | 2919.7017
March | 7506.6929 | 12.4172 | 30.3602 | 0 | 0.0001 | 31565.1806 | 3147.7072
April | 6207.8609 | 10.5996 | 26.8976 | 0 | 0.0001 | 27967.5208 | 2635.5281
May | 6315.3968 | 10.9492 | 28.2622 | 0 | 0.0001 | 29387.5029 | 2697.4683
June | 6641.6408 | 11.5929 | 30.145 | 0 | 0.0001 | 31345.7292 | 2844.4773
July | 7047.9832 | 12.3214 | 32.0929 | 0 | 0.0001 | 33371.4112 | 3020.384
August | 7536.6764 | 13.1773 | 34.3268 | 0 | 0.0001 | 35694.3213 | 3229.9682
September | 6239.6759 | 10.8781 | 28.2493 | 0 | 0.0001 | 29374.4567 | 2671.0328
October | 6463.9543 | 11.0943 | 28.3183 | 0 | 0.0001 | 29445.0961 | 2749.8892
November | 7096.0584 | 11.7042 | 28.5167 | 0 | 0.0001 | 29648.2274 | 2972.2077
December | 8162.0039 | 12.8744 | 29.6179 | 0 | 0.0001 | 30788.9609 | 3361.0087
Annual Sum or Average | 84477.857 | 141.9187 | 353.459 | 0 | 0.0014 | 367503.1099 | 35637.0242
Minimum of Months | 6207.8609 | 10.5996 | 26.8119 | 0 | 0.0001 | 27873.8582 | 2635.5281
Maximum of Months | 8226.3091 | 13.1773 | 34.3268 | 0 | 0.0001 | 35694.3213 | 3387.6509
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 24609600000 | 18043.621 | 24-JAN-15:30 | 8961.612 | 3712.536 | 4101.424 | 0 | 1268.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 22098700000 | 17605.198 | 07-FEB-15:20 | 8961.612 | 3712.536 | 4101.424 | 0 | 829.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 25025300000 | 19930.606 | 30-MAR-15:00 | 8961.612 | 3712.536 | 4101.424 | 0 | 3155.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 22173000000 | 21082.093 | 26-APR-15:00 | 8961.612 | 3712.536 | 4101.424 | 0 | 4306.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 23298800000 | 22771.234 | 23-MAY-15:00 | 8961.612 | 3712.536 | 4101.424 | 0 | 5995.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 24851300000 | 24583.973 | 27-JUN-15:00 | 8961.612 | 3712.536 | 4101.424 | 0 | 7808.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 26457300000 | 26067.954 | 17-JUL-15:39 | 8961.612 | 3712.536 | 4101.424 | 0 | 9292.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 28298900000 | 26051.102 | 30-AUG-13:00 | 8961.612 | 3712.536 | 4101.424 | 0 | 9275.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23288400000 | 23318.18 | 01-SEP-15:00 | 8961.612 | 3712.536 | 4101.424 | 0 | 6542.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 23344400000 | 22006.825 | 05-OCT-15:20 | 8961.612 | 3712.536 | 4101.424 | 0 | 5231.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 23505500000 | 18676.862 | 10-NOV-16:49 | 8961.612 | 3712.536 | 4101.424 | 0 | 738.29 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 24409900000 | 18213.943 | 21-DEC-16:40 | 8961.612 | 3712.536 | 4101.424 | 0 | 275.371 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 291361000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22098700000 | 17605.198 |  | 8961.612 | 3712.536 | 4101.424 | 0 | 275.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 28298900000 | 26067.954 |  | 8961.612 | 3712.536 | 4101.424 | 0 | 9292.382 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6068.96 | 983.74 | 0 | 7052.71
Cost per Total Building Area ($/m2) | 11.87 | 1.92 | 0 | 13.8
Cost per Net Conditioned Building Area ($/m2) | 11.87 | 1.92 | 0 | 13.8

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 558.98 | 1093.56 | 1093.56
Net Site Energy | 558.98 | 1093.56 | 1093.56
Total Source Energy | 1329.31 | 2600.58 | 2600.58
Net Source Energy | 1329.31 | 2600.58 | 2600.58
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 239.84 | 0 | 0 | 0 | 0
Cooling | 26.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 93.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.57 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 306.57 | 252.41 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.252 | 0.268 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.252 | 0.268 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.252 | 0.268 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.252 | 0.268 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11036.04 | 8813.99 | 2222.05 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21520.39 | 15378.31 | 6142.09 | 0.71 | 3.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11559.81 | 8774.37 | 2785.44 | 0.76 | 3.1
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19367.95 | 14350.34 | 5017.6 | 0.74 | 3.1
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11500.82 | 8745.42 | 2755.4 | 0.76 | 3.11
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 19315.81 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 25764.02 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 15914.11 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 25396.17 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 15901.17 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 773.29 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1 | 1142.38 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 722.72 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.99 | 1123.61 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 722.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9372.0625 | 13.7071 | 16.9754 | 0 | 0.0001 | 11146.1961 | 3740.7428
February | 7677.9035 | 11.6429 | 15.2536 | 0 | 0.0001 | 10018.1189 | 3104.074
March | 7074.7746 | 11.622 | 16.9653 | 0 | 0.0001 | 11147.313 | 2945.6613
April | 5408.0954 | 9.4896 | 14.9403 | 0 | 0.0001 | 9819.5558 | 2309.6018
May | 5528.2187 | 9.9902 | 16.2159 | 0 | 0.0001 | 10659.065 | 2388.6048
June | 6151.1598 | 11.1726 | 18.2277 | 0 | 0.0001 | 11981.7091 | 2663.1804
July | 6234.9293 | 11.3283 | 18.4873 | 0 | 0.0001 | 12152.3669 | 2699.7826
August | 6738.8934 | 12.2474 | 19.993 | 0 | 0.0001 | 13142.0936 | 2918.3364
September | 5240.3804 | 9.4921 | 15.4432 | 0 | 0.0001 | 10151.2467 | 2266.3399
October | 5599.9401 | 9.8551 | 15.5642 | 0 | 0.0001 | 10229.6981 | 2394.2872
November | 6753.227 | 11.115 | 16.2634 | 0 | 0.0001 | 10686.1846 | 2813.8105
December | 8570.8121 | 12.904 | 16.7247 | 0 | 0.0001 | 10983.8087 | 3456.1767
Annual Sum or Average | 80350.3968 | 134.5664 | 201.0539 | 0 | 0.0015 | 132117.3565 | 33700.5983
Minimum of Months | 5240.3804 | 9.4896 | 14.9403 | 0 | 0.0001 | 9819.5558 | 2266.3399
Maximum of Months | 9372.0625 | 13.7071 | 19.993 | 0 | 0.0001 | 13142.0936 | 3740.7428
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 25863900000 | 18321.201 | 02-JAN-16:40 | 8961.612 | 3712.536 | 4484.054 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 23246300000 | 17179.465 | 16-FEB-13:30 | 8961.612 | 3712.536 | 4484.054 | 0 | 21.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 25866500000 | 18673.706 | 23-MAR-15:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 1515.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 22785500000 | 20101.435 | 14-APR-15:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 2943.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 24733600000 | 24523.345 | 31-MAY-12:09 | 8961.612 | 3712.536 | 4484.054 | 0 | 7365.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 27802700000 | 28362.349 | 29-JUN-15:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 11204.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 28198700000 | 28436.909 | 13-JUL-15:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 11278.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 30495200000 | 28187.299 | 25-AUG-15:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 11029.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23555200000 | 25195.002 | 14-SEP-14:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 8036.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 23737200000 | 20696.61 | 06-OCT-14:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 3538.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 24796500000 | 19496.233 | 02-NOV-14:00 | 8961.612 | 3712.536 | 4484.054 | 0 | 2338.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 25487100000 | 18321.201 | 01-DEC-16:30 | 8961.612 | 3712.536 | 4484.054 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 306568000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22785500000 | 17179.465 |  | 8961.612 | 3712.536 | 4484.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 30495200000 | 28436.909 |  | 8961.612 | 3712.536 | 4484.054 | 0 | 11278.708 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6351.65 | 1996.58 | 0 | 8348.22
Cost per Total Building Area ($/m2) | 12.43 | 3.91 | 0 | 16.33
Cost per Net Conditioned Building Area ($/m2) | 12.43 | 3.91 | 0 | 16.33

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 497.96 | 974.19 | 974.19
Net Site Energy | 497.96 | 974.19 | 974.19
Total Source Energy | 1255.24 | 2455.68 | 2455.68
Net Source Energy | 1255.24 | 2455.68 | 2455.68
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 186.92 | 0 | 0 | 0 | 0
Cooling | 15.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 96.55 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.61 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 298.43 | 199.53 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.274 | 0.294 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.274 | 0.294 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.274 | 0.294 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.274 | 0.294 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8057.1 | 6434.84 | 1622.25 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17793.18 | 14210.62 | 3582.56 | 0.8 | 3.17
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11056.03 | 8829.95 | 2226.07 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17499.12 | 13975.77 | 3523.36 | 0.8 | 3.17
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11046.51 | 8822.35 | 2224.16 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13784.01 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 24544.92 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 15164.66 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 24190.46 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 15153.18 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 564.56 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1224.5 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 774.7 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.06 | 1204.27 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 774.03 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8836.145 | 13.3724 | 19.3951 | 0 | 0.0001 | 459790.8917 | 3575.5309
February | 7458.8633 | 11.5558 | 17.34 | 0 | 0.0001 | 411125.8744 | 3044.0897
March | 7211.2979 | 11.8799 | 19.3238 | 0 | 0.0001 | 458295.1533 | 3011.4606
April | 5952.0733 | 10.1408 | 17.1623 | 0 | 0.0001 | 407088.2658 | 2518.0219
May | 5816.0969 | 10.1575 | 17.6683 | 0 | 0.0001 | 419127.8503 | 2484.5006
June | 5956.7052 | 10.4976 | 18.4375 | 0 | 0.0001 | 437389.2882 | 2553.7086
July | 6180.0644 | 10.9216 | 19.2385 | 0 | 0.0001 | 456395.6144 | 2652.3961
August | 6481.2925 | 11.4516 | 20.168 | 0 | 0.0001 | 478445.3629 | 2781.4586
September | 5544.7005 | 9.7476 | 17.0756 | 0 | 0.0001 | 405076.3126 | 2374.76
October | 6105.8661 | 10.4886 | 17.9158 | 0 | 0.0001 | 424974.4671 | 2591.3713
November | 6978.1612 | 11.4617 | 18.5757 | 0 | 0.0001 | 440546.5545 | 2910.8037
December | 8334.2977 | 12.8361 | 19.1006 | 0 | 0.0001 | 452853.2812 | 3394.0291
Annual Sum or Average | 80855.564 | 134.5111 | 221.4013 | 0 | 0.0016 | 5251110 | 33892.1312
Minimum of Months | 5544.7005 | 9.7476 | 17.0756 | 0 | 0.0001 | 405076.3126 | 2374.76
Maximum of Months | 8836.145 | 13.3724 | 20.168 | 0 | 0.0001 | 478445.3629 | 3575.5309
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 26131000000 | 18379.204 | 02-JAN-08:09 | 8961.612 | 3712.536 | 4542.056 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 23365300000 | 18083.587 | 02-FEB-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 867.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26046000000 | 19967.533 | 30-MAR-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 2751.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 23135800000 | 19430.26 | 06-APR-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 2214.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 23820000000 | 21364.401 | 16-MAY-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 4148.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 24857900000 | 25695.694 | 30-JUN-14:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 8479.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 25938100000 | 25832.15 | 21-JUL-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 8615.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 27191200000 | 24949.585 | 09-AUG-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 7733.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 23021500000 | 22983.755 | 01-SEP-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 5767.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24152300000 | 20941.523 | 06-OCT-15:00 | 8961.612 | 3712.536 | 4542.056 | 0 | 3725.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 25037300000 | 18654.497 | 21-NOV-16:49 | 8961.612 | 3712.536 | 4542.056 | 0 | 275.294 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 25736700000 | 18379.204 | 01-DEC-16:40 | 8961.612 | 3712.536 | 4542.056 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 298433000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 23021500000 | 18083.587 |  | 8961.612 | 3712.536 | 4542.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 27191200000 | 25832.15 |  | 8961.612 | 3712.536 | 4542.056 | 0 | 8615.947 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6417.04 | 1598.44 | 0 | 8015.47
Cost per Total Building Area ($/m2) | 12.55 | 3.13 | 0 | 15.68
Cost per Net Conditioned Building Area ($/m2) | 12.55 | 3.13 | 0 | 15.68

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 609.38 | 1192.15 | 1192.15
Net Site Energy | 609.38 | 1192.15 | 1192.15
Total Source Energy | 1368.77 | 2677.78 | 2677.78
Net Source Energy | 1368.77 | 2677.78 | 2677.78
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 296.5 | 0 | 0 | 0 | 0
Cooling | 12.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 100.89 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.95 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 299.93 | 309.45 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.227 | 0.24 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.227 | 0.24 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.227 | 0.24 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.227 | 0.24 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 16.73 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 42.95 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9033.47 | 7214.63 | 1818.84 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20574.7 | 15371.15 | 5203.55 | 0.75 | 3.11
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11264.97 | 8892.78 | 2372.19 | 0.79 | 3.17
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21337.07 | 15588.71 | 5748.35 | 0.73 | 3.08
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11142.03 | 8836.23 | 2305.8 | 0.79 | 3.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16547.32 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 26874.89 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 16588.5 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 26476.08 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 16575.69 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 632.98 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1217.33 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 769.51 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.05 | 1196.55 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 768.83 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9494.0508 | 13.8953 | 17.2282 | 0 | 0.0001 | 11312.2611 | 3790.3684
February | 8188.823 | 12.1774 | 15.486 | 0 | 0.0001 | 10169.4737 | 3287.6597
March | 7993.0893 | 12.648 | 17.5962 | 0 | 0.0001 | 11559.63 | 3281.8875
April | 6134.2518 | 10.4109 | 15.7974 | 0 | 0.0001 | 10381.4628 | 2585.9876
May | 5513.905 | 9.8031 | 15.6487 | 0 | 0.0001 | 10285.6296 | 2367.0024
June | 5436.2319 | 9.8505 | 16.0323 | 0 | 0.0001 | 10538.5336 | 2351.3932
July | 5731.0248 | 10.401 | 16.9551 | 0 | 0.0001 | 11145.117 | 2480.4682
August | 5917.9751 | 10.7272 | 17.4654 | 0 | 0.0001 | 11480.5062 | 2560.127
September | 5146.9074 | 9.2456 | 14.9166 | 0 | 0.0001 | 9804.8452 | 2218.5443
October | 5973.8689 | 10.3545 | 16.0869 | 0 | 0.0001 | 10572.6134 | 2538.998
November | 7303.2158 | 11.687 | 16.5026 | 0 | 0.0001 | 10841.8916 | 3011.1128
December | 9032.8512 | 13.4069 | 16.999 | 0 | 0.0001 | 11162.8466 | 3624.0781
Annual Sum or Average | 81866.195 | 134.6075 | 196.7145 | 0 | 0.0015 | 129254.8107 | 34097.6272
Minimum of Months | 5146.9074 | 9.2456 | 14.9166 | 0 | 0.0001 | 9804.8452 | 2218.5443
Maximum of Months | 9494.0508 | 13.8953 | 17.5962 | 0 | 0.0001 | 11559.63 | 3790.3684
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 26249200000 | 18422.344 | 02-JAN-16:30 | 8961.612 | 3712.536 | 4585.196 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 23597500000 | 17314.224 | 17-FEB-13:20 | 8961.612 | 3712.536 | 4585.196 | 0 | 54.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 26823300000 | 17421.261 | 22-MAR-14:09 | 8961.612 | 3712.536 | 4585.196 | 0 | 161.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 24089400000 | 19015.693 | 04-APR-15:39 | 8961.612 | 3712.536 | 4585.196 | 0 | 1756.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 23867000000 | 21592.541 | 31-MAY-15:00 | 8961.612 | 3712.536 | 4585.196 | 0 | 4333.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 24453900000 | 25122.66 | 14-JUN-15:00 | 8961.612 | 3712.536 | 4585.196 | 0 | 7863.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 25861400000 | 26860.923 | 06-JUL-15:00 | 8961.612 | 3712.536 | 4585.196 | 0 | 9601.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26639600000 | 25765.945 | 11-AUG-15:39 | 8961.612 | 3712.536 | 4585.196 | 0 | 8506.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 22751400000 | 23515.287 | 07-SEP-14:00 | 8961.612 | 3712.536 | 4585.196 | 0 | 6255.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 24533000000 | 19728.182 | 06-OCT-14:00 | 8961.612 | 3712.536 | 4585.196 | 0 | 2468.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 25157800000 | 18422.344 | 06-NOV-16:49 | 8961.612 | 3712.536 | 4585.196 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 25902500000 | 18422.344 | 01-DEC-16:19 | 8961.612 | 3712.536 | 4585.196 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 299926000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 22751400000 | 17314.224 |  | 8961.612 | 3712.536 | 4585.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 26823300000 | 26860.923 |  | 8961.612 | 3712.536 | 4585.196 | 0 | 9601.579 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6192.48 | 2437.16 | 0 | 8629.64
Cost per Total Building Area ($/m2) | 12.11 | 4.77 | 0 | 16.88
Cost per Net Conditioned Building Area ($/m2) | 12.11 | 4.77 | 0 | 16.88

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 873.01 | 1707.9 | 1707.9
Net Site Energy | 873.01 | 1707.9 | 1707.9
Total Source Energy | 1761.67 | 3446.43 | 3446.43
Net Source Energy | 1761.67 | 3446.43 | 3446.43
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 533.64 | 0 | 0 | 0 | 0
Cooling | 9.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 102.64 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 18.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 129.81 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 13.42 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 325.95 | 547.06 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 19.48 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 19.48 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 9.2272 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 19.48 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.174 | 0.182 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.174 | 0.182 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.174 | 0.182 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.174 | 0.182 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-NONRES-FIXED | 3.91 | 3.91 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 16.73 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 42.95 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7358.82 | 5877.16 | 1481.66 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22846.39 | 18246.39 | 4600 | 0.8 | 3.22
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14178.77 | 11323.95 | 2854.82 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22491.26 | 17962.76 | 4528.5 | 0.8 | 3.22
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14178.77 | 11323.95 | 2854.82 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16144.37 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 35876.97 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 22140.1 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 35391.21 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 22140.1 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 515.63 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.38 | 1572.26 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.86 | 993.51 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.36 | 1547.82 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.86 | 993.51 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.78 | 4.4 | 0.56
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11861.4505 | 12.7553 | 41.6235 | 0 | 0.0002 | 8347.8284 | 4411.1693
February | 10149.4194 | 10.9863 | 37.1229 | 0 | 0.0001 | 7445.6492 | 3785.5659
March | 9318.1533 | 10.4552 | 41.7962 | 0 | 0.0001 | 8385.1558 | 3532.257
April | 6667.0937 | 7.8442 | 37.5113 | 0 | 0.0001 | 7527.2603 | 2583.2612
May | 5241.9052 | 6.4883 | 36.2073 | 0 | 0.0001 | 7266.8392 | 2080.4415
June | 5146.4691 | 6.4168 | 36.5226 | 0 | 0.0001 | 7330.2551 | 2049.7318
July | 5039.8926 | 6.2881 | 35.8538 | 0 | 0.0001 | 7196.0469 | 2007.9289
August | 5294.2011 | 6.5937 | 37.4195 | 0 | 0.0001 | 7510.2377 | 2107.4558
September | 5310.3336 | 6.5162 | 35.4909 | 0 | 0.0001 | 7122.8709 | 2098.8533
October | 7429.6946 | 8.6556 | 40.0056 | 0 | 0.0001 | 8027.4576 | 2865.5289
November | 9826.1835 | 10.8426 | 40.2553 | 0 | 0.0001 | 8075.1414 | 3696.7417
December | 11037.1878 | 11.9881 | 41.2248 | 0 | 0.0002 | 8268.6089 | 4122.9765
Annual Sum or Average | 92321.9844 | 105.8304 | 461.0336 | 0 | 0.0016 | 92503.3515 | 35341.9117
Minimum of Months | 5039.8926 | 6.2881 | 35.4909 | 0 | 0.0001 | 7122.8709 | 2007.9289
Maximum of Months | 11861.4505 | 12.7553 | 41.7962 | 0 | 0.0002 | 8385.1558 | 4411.1693
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 29414500000 | 19459.871 | 02-JAN-08:09 | 8961.612 | 3712.536 | 5622.723 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 26235600000 | 19459.871 | 01-FEB-08:09 | 8961.612 | 3712.536 | 5622.723 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 29546000000 | 19459.871 | 01-MAR-08:09 | 8961.612 | 3712.536 | 5622.723 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 26523100000 | 19821.455 | 25-APR-15:00 | 8961.612 | 3712.536 | 5622.723 | 0 | 1524.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 25605500000 | 22566.168 | 24-MAY-14:00 | 8961.612 | 3712.536 | 5622.723 | 0 | 4269.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 25828900000 | 24919.442 | 21-JUN-15:00 | 8961.612 | 3712.536 | 5622.723 | 0 | 6622.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 25356000000 | 24791.093 | 21-JUL-15:00 | 8961.612 | 3712.536 | 5622.723 | 0 | 6494.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 26463100000 | 24645.105 | 15-AUG-14:30 | 8961.612 | 3712.536 | 5622.723 | 0 | 6348.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 25098200000 | 20919.526 | 07-SEP-15:00 | 8961.612 | 3712.536 | 5622.723 | 0 | 2622.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 28285600000 | 19544.809 | 03-OCT-14:00 | 8961.612 | 3712.536 | 5622.723 | 0 | 1247.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 28453600000 | 19459.871 | 01-NOV-07:10 | 8961.612 | 3712.536 | 5622.723 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 29135300000 | 19459.871 | 01-DEC-08:09 | 8961.612 | 3712.536 | 5622.723 | 0 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 325946000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 25098200000 | 19459.871 |  | 8961.612 | 3712.536 | 5622.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 29546000000 | 24919.442 |  | 8961.612 | 3712.536 | 5622.723 | 0 | 6622.571 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8969.86 | 2246.47 | 0 | 11216.34
Cost per Total Building Area ($/m2) | 17.55 | 4.39 | 0 | 21.94
Cost per Net Conditioned Building Area ($/m2) | 17.55 | 4.39 | 0 | 21.94

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_ZN Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_ZN Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_ZN Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_ZN Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720