## BuildingSummary
Building Summary Warehouse post-1980 construction
|  | Value | Data Source
Program
| Building Name | Warehouse
| Available Fuel Types | gas, electricity
| Principal Building Activity | Nonrefrigerated warehouse
Form
| Total Floor Area (m2) | 4835.13 | Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory
| Building Shape | Rectangle
| Aspect Ratio | 0.45
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.0286
| East | 0
| North | 0
| West | 0.0076
| Total | 0.0058
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Bulk storage, fine storage, office
| Floor to Ceiling Height (m) | 8.53
| Floor to Floor Height (m) | 8.53
| Roof type | Metal building roof | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Metal building wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.35192
Roof
| Construction Type | Metal building roof | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4598.25
| Net Dimensions - Total Area (m2) | 4598.25
| Roof to Skin Ratio | 0.64808
Window Dimensions (m2)
| South | 11.15
| East | 0
| North | 0
| West | 6.51
| Total Area (m2) | 17.66
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 8in slab-on-grade
| Dimensions - Total Area (m2) | 4598.25
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 539.71
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9670.26
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.74 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC office, semi-conditioned storage | 2003 CBECS
| Heating Type | Gas furnace office, gas unit heaters storage | 2003 CBECS
| Cooling Type | PACU office | 2003 CBECS
| Fan Control | SZ CAV | 2003 CBECS
Service Water Heating
| SWH Type | n/a
| Fuel | n/a
| Thermal Efficiency (%) | n/a
| Temperature Setpoint (ºC ) | n/a
| Water Consumption (m3 ) | n/a

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.5601 | 17.66 | 47.376 | 5 | 21.6974 | 8.0729 |  |  | 10 |  | 50 |  | 0.60391
FineStorage | Yes | 1 | 1393.41 | 10880.57 | 7.8086 | 760.8007 | 0 |  | 0 | 11.6478 | 0 |  |  |  | 0.25 | 348.3525 |  | 0.80806
BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.6315 | 0 |  | 0 | 3.3409 | 2.691 |  |  |  | 0.25 | 801.21 |  | 0.71502
Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
| R-value (m2·K / W) | 0.2291 | 0.98232 | 0.5423 | 1.1628 | 0.60901 | 0.90909 | 1.1628 | 1.7889 | 1.5699 | 1.7241 | 1.9569 | 1.9569 | 2.5189 | 2.2523 | 2.849 | 3.7175
Roof
| Construction Type | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
| R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
HVAC
HVAC Sizing
Air Conditioning (kW)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 29.4318 | 26.9042 | 28.2511 | 25.072 | 15.928 | 21.6578 | 12.3804 | 26.9189 | 20.8375 | 16.1336 | 34.8208 | 25.9621 | 37.4397 | 30.4251 | 38.3517 | 37.8
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 85.0996 | 87.1116 | 96.9637 | 117.6013 | 44.3917 | 81.4513 | 47.2632 | 132.2649 | 116.5201 | 84.8148 | 188.3548 | 176.1554 | 217.2209 | 191.0397 | 234.9479 | 209.9295
Heating (kW)
| BULKSTORAGE UNIT HEATER COIL | 39.3476 | 39.2032 | 37.8007 | 46.1858 | 39.2079 | 36.3558 | 39.3336 | 88.4697 | 44.8326 | 38.791 | 202.7478 | 139.3554 | 262.7257 | 251.1025 | 290.1463 | 485.6104
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 19.749 | 23.913 | 22.0153 | 27.3591 | 17.4676 | 23.7441 | 18.2669 | 29.1796 | 25.3076 | 23.6184 | 37.2148 | 31.5885 | 40.6493 | 39.2001 | 42.2795 | 55.4787
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 44.6608 | 110.7635 | 78.9442 | 144.0415 | 56.3686 | 103.6843 | 75.349 | 167.6189 | 135.2568 | 121.5626 | 234.017 | 191.5237 | 267.7531 | 256.609 | 283.3926 | 392.7649
HVAC Efficiency
Air Conditioning (COP)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.02 | 3.01 | 3.11 | 3.04 | 3.09 | 3.19 | 3.19 | 3.02 | 3.22 | 3.17 | 3.02 | 3.22 | 3.03 | 3.19 | 3.03 | 3.19
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 2.62 | 2.62 | 2.9 | 2.9 | 2.62 | 2.96 | 2.71 | 2.89 | 2.97 | 3.01 | 2.89 | 2.92 | 2.89 | 3.06 | 2.75 | 3.18
Heating Efficiency (%)
| BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.78 | 0.78 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BULKSTORAGE UNIT HEATERFAN | 0.8 | 0.8 | 0.8 | 0.84 | 0.8 | 0.8 | 0.8 | 1.76 | 0.96 | 0.8 | 4.47 | 3.58 | 5.91 | 6.35 | 6.7 | 11.04
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.31 | 1.17 | 1.48 | 1.16 | 0.84 | 1.27 | 0.75 | 1.19 | 1.26 | 0.97 | 1.54 | 1.57 | 1.7 | 1.84 | 1.8 | 2.28
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 3.43 | 3.51 | 3.9 | 4.74 | 1.79 | 3.55 | 2.38 | 5.33 | 5.22 | 3.89 | 7.59 | 7.41 | 8.75 | 9.41 | 9.46 | 12.68
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.094104 | 0.12664 | 0.11307 | 0.10464 | 0.13742 | 0.1027 | 0.15228 | 0.08235 | 0.037889 | 0.072477 | 0.0536 | 0.037824 | 0.065564 | 0.079757 | 0.062721 | 0.10151
| Total Cost ($/m2) | 4.11 | 5.17 | 5.44 | 4.34 | 4.58 | 4.48 | 5.12 | 3.47 | 1.57 | 2.75 | 2.43 | 1.68 | 3.1 | 3.78 | 2.96 | 5.41
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011427 | 0.0080529 | 0.0080486 | 0.0094155 | 0.0088659 | 0.0075684 | 0.0087208 | 0.0096376 | 0.0068388 | 0.0084607 | 0.0082493 | 0.0068601 | 0.0079267 | 0.0079658 | 0.0078908 | 0.004106
| Total Cost ($/m2) | 0.02 | 0.35 | 0.25 | 0.88 | 0.14 | 0.45 | 0.49 | 1.66 | 0.84 | 1.09 | 2.2 | 1.36 | 3.35 | 2.54 | 4.34 | 4.72
Total Utility Costs
| Cost Intensity ($/m2) | 4.13 | 5.52 | 5.69 | 5.22 | 4.72 | 4.94 | 5.61 | 5.13 | 2.41 | 3.83 | 4.62 | 3.04 | 6.45 | 6.31 | 7.3 | 10.13
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 43333.3333 | 28811.1111 | 47252.7778 | 12550 | 1616.6667 | 29097.2222 | 347.2222 | 9644.4444 | 7105.5556 | 363.8889 | 6236.1111 | 3797.2222 | 4433.3333 | 1680.5556 | 966.6667 | 175
| Interior Lighting | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111
| Exterior Lighting | 32122.2222 | 32111.1111 | 32102.7778 | 32100 | 32075 | 32066.6667 | 32083.3333 | 32063.8889 | 32077.7778 | 32013.8889 | 32069.4444 | 32052.7778 | 32050 | 32041.6667 | 32022.2222 | 31827.7778
| Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 18305.5556 | 18830.5556 | 35605.5556 | 38255.5556 | 10027.7778 | 32341.6667 | 12727.7778 | 44422.2222 | 43558.3333 | 33197.2222 | 63008.3333 | 61452.7778 | 74663.8889 | 77608.3333 | 77458.3333 | 108055.5556
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 211330.5556 | 197319.4444 | 232530.5556 | 200472.2222 | 161286.1111 | 211072.2222 | 162727.7778 | 203697.2222 | 200305.5556 | 183141.6667 | 218880.5556 | 214869.4444 | 228711.1111 | 228897.2222 | 228016.6667 | 257625
Gas (MJ)
| Heating | 9140 | 211340 | 148830 | 450390 | 76140 | 290160 | 269660 | 834240 | 597040 | 621820 | 1286610 | 957690 | 2041250 | 1539250 | 2660170 | 5562430
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 9140 | 211340 | 148830 | 450390 | 76140 | 290160 | 269660 | 834240 | 597040 | 621820 | 1286610 | 957690 | 2041250 | 1539250 | 2660170 | 5562430
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 769930 | 921690 | 985940 | 1172090 | 656770 | 1050030 | 855480 | 1567550 | 1318150 | 1281130 | 2074580 | 1731220 | 2864610 | 2363280 | 3481030 | 6489880
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 32.2639 | 21.4513 | 35.1821 | 9.3441 | 1.2037 | 21.6644 | 0.25852 | 7.1808 | 5.2904 | 0.27093 | 4.6431 | 2.8272 | 3.3008 | 1.2513 | 0.71973 | 0.1303
| Interior Lighting (elec) | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382
| Exterior Lighting (elec) | 23.9166 | 23.9084 | 23.9021 | 23.9001 | 23.8815 | 23.8753 | 23.8877 | 23.8732 | 23.8835 | 23.836 | 23.8773 | 23.8649 | 23.8629 | 23.8566 | 23.8422 | 23.6974
| Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 13.6294 | 14.0203 | 26.5101 | 28.4832 | 7.4662 | 24.08 | 9.4765 | 33.0746 | 32.4314 | 24.717 | 46.9129 | 45.7547 | 55.5911 | 57.7833 | 57.6717 | 80.4529
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 157.3463 | 146.9144 | 173.1308 | 149.2618 | 120.0857 | 157.154 | 121.1591 | 151.6629 | 149.1377 | 136.3583 | 162.9677 | 159.9812 | 170.287 | 170.4256 | 169.77 | 191.8149
Gas (MJ/m2)
| Heating (gas) | 1.8903 | 43.7093 | 30.781 | 93.1495 | 15.7472 | 60.0108 | 55.771 | 172.5372 | 123.4796 | 128.6046 | 266.0963 | 198.0691 | 422.1707 | 318.3472 | 550.1755 | 1150.4199
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1.8903 | 43.7093 | 30.781 | 93.1495 | 15.7472 | 60.0108 | 55.771 | 172.5372 | 123.4796 | 128.6046 | 266.0963 | 198.0691 | 422.1707 | 318.3472 | 550.1755 | 1150.4199
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 159.2367 | 190.6236 | 203.9118 | 242.4113 | 135.833 | 217.1669 | 176.9301 | 324.2002 | 272.6194 | 264.9629 | 429.064 | 358.0504 | 592.4577 | 488.7728 | 719.9455 | 1342.2349
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 55.8267 | 46.7397 | 48.8303 | 48.389 | 48.3083 | 53.6063 | 48.8489 | 56.7322 | 49.2547 | 53.911 | 61.7129 | 61.3281 | 64.2012 | 65.5529 | 64.1792 | 70.3176
| Feb | 62.8109 | 48.3172 | 49.7679 | 48.3922 | 42.9063 | 46.2573 | 42.1037 | 49.4726 | 49.2547 | 46.562 | 61.3724 | 53.9791 | 56.8522 | 58.2039 | 56.8302 | 70.3176
| Mar | 68.8795 | 46.3635 | 64.9136 | 50.0096 | 42.6338 | 47.7278 | 41.4999 | 50.7355 | 49.2547 | 46.6983 | 54.3613 | 54.3696 | 56.8522 | 58.2039 | 56.8302 | 62.9686
| Apr | 73.5445 | 59.9372 | 67.8665 | 58.7669 | 43.4599 | 63.6653 | 42.3508 | 51.1577 | 51.1839 | 46.562 | 54.7768 | 55.2721 | 56.8285 | 57.6889 | 56.8302 | 62.9686
| May | 83.5203 | 80.3669 | 83.185 | 71.7084 | 42.8328 | 74.5726 | 42.748 | 57.5682 | 64.678 | 47.8056 | 65.9169 | 63.4803 | 67.9993 | 59.0947 | 57.6542 | 62.7199
| Jun | 84.5327 | 82.1705 | 94.2781 | 82.7716 | 43.1018 | 83.0752 | 42.9731 | 86.9312 | 76.387 | 48.5455 | 91.4708 | 75.661 | 90.7 | 82.7155 | 63.6821 | 64.423
| Jul | 83.0708 | 84.6402 | 94.4091 | 93.4631 | 51.2561 | 82.9775 | 52.6243 | 93.3006 | 78.3507 | 59.4443 | 94.3706 | 82.5837 | 89.1656 | 82.2004 | 80.613 | 64.6178
| Aug | 84.4811 | 84.8517 | 94.1502 | 83.2004 | 56.8707 | 82.7923 | 43.4151 | 90.1646 | 78.9639 | 54.2609 | 89.4078 | 83.3138 | 86.1244 | 77.0452 | 70.5663 | 64.2889
| Sep | 82.9307 | 80.7534 | 90.6578 | 74.1522 | 57.9807 | 81.6035 | 59.1146 | 72.7785 | 61.6503 | 52.5152 | 72.6491 | 68.4668 | 68.5664 | 60.2469 | 58.6686 | 62.0181
| Oct | 79.0986 | 67.7502 | 69.2216 | 60.4357 | 47.2571 | 63.0371 | 42.7655 | 54.9434 | 51.2154 | 47.1706 | 56.256 | 56.1275 | 57.26 | 58.6665 | 56.2826 | 70.3176
| Nov | 67.0414 | 49.5163 | 57.7099 | 49.4463 | 48.7604 | 53.8107 | 48.8489 | 56.7322 | 56.6037 | 53.911 | 61.3724 | 61.0697 | 64.2012 | 65.0379 | 64.1792 | 70.3176
| Dec | 57.4578 | 46.6716 | 48.6851 | 48.389 | 48.5708 | 53.6063 | 48.8489 | 56.7322 | 56.6037 | 53.911 | 61.3724 | 61.3281 | 64.2012 | 65.5529 | 64.1792 | 70.3176
Time of Peak Electrical Demand
| Jan | 24-JAN-13:00 | 03-JAN-13:00 | 26-JAN-15:00 | 02-JAN-09:30 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 02-JAN-16:49 | 02-JAN-09:09 | 02-JAN-16:30 | 06-JAN-16:30 | 05-JAN-16:49 | 02-JAN-16:40 | 04-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 22-FEB-13:00 | 23-FEB-15:50 | 28-FEB-15:00 | 09-FEB-09:09 | 13-FEB-11:00 | 01-FEB-09:09 | 15-FEB-15:00 | 08-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-16:00 | 14-FEB-09:09 | 01-FEB-09:09 | 06-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
| Mar | 13-MAR-15:00 | 24-MAR-13:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:09 | 31-MAR-14:00 | 01-MAR-09:09 | 09-MAR-15:00 | 01-MAR-09:09 | 29-MAR-15:50 | 31-MAR-15:50 | 30-MAR-15:00 | 06-MAR-09:09 | 03-MAR-09:09 | 02-MAR-09:09 | 01-MAR-09:09
| Apr | 03-APR-14:50 | 21-APR-14:00 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 03-APR-08:09 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09
| May | 24-MAY-14:00 | 18-MAY-15:39 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-13:50 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-15:39 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 10-JUL-13:50 | 31-JUL-13:00 | 11-JUL-15:00 | 03-JUL-15:50 | 10-JUL-15:00 | 25-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 03-JUL-14:00 | 17-JUL-15:50 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-14:30 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-15:00 | 15-AUG-12:09 | 17-AUG-15:39 | 01-AUG-13:00 | 07-AUG-15:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:50 | 15-AUG-15:00
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 14-SEP-15:00 | 01-SEP-15:00 | 27-SEP-15:00 | 06-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 01-SEP-08:09
| Oct | 06-OCT-14:20 | 06-OCT-15:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 06-OCT-13:00 | 30-OCT-13:50 | 03-OCT-14:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:00 | 02-OCT-08:09 | 23-OCT-08:09
| Nov | 07-NOV-14:50 | 03-NOV-14:00 | 13-NOV-15:00 | 22-NOV-15:09 | 20-NOV-16:49 | 10-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 06-NOV-16:49 | 27-NOV-16:40 | 08-NOV-16:00 | 24-NOV-16:30 | 01-NOV-08:09
| Dec | 13-DEC-15:39 | 19-DEC-14:00 | 11-DEC-15:50 | 01-DEC-09:09 | 18-DEC-16:49 | 01-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 13-DEC-16:30 | 08-DEC-16:40 | 05-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 2533.53 | 2810.79 | 2810.3 | 2919.62 | 1880.19 | 3034.89 | 2107.57 | 3533.31 | 3044.6 | 1827.54 | 4199.12 | 3612.37 | 5058.94 | 4545.19 | 5726.21 | 9387.02
| Total Source Energy (MJ/m2) | 523.98 | 581.33 | 581.23 | 603.83 | 388.86 | 627.68 | 435.89 | 730.76 | 629.68 | 377.97 | 868.46 | 747.11 | 1046.29 | 940.03 | 1184.29 | 1941.42
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 58122.3469 | 69629.428 | 72879.0765 | 69874.3974 | 20221.764 | 76422.1908 | 23879.9007 | 70012.559 | 92591.2112 | 24552.0096 | 139897.1805 | 105043.4141 | 115095.5532 | 111404.4266 | 126018.9372 | 172797.9993
| CO2 (kg) | 134679.9839 | 176168.0023 | 172832.1043 | 163619.1116 | 54289.8713 | 183731.3358 | 64821.9947 | 166733.6638 | 221765.9173 | 64083.1525 | 336282.0006 | 254416.8238 | 286829.8415 | 274748.2454 | 318528.1791 | 471396.9804
| NOX (kg) | 237.1148 | 227.0805 | 286.0485 | 291.9403 | 46.6665 | 290.2392 | 56.2049 | 285.9256 | 362.7604 | 80.3238 | 551.1319 | 404.139 | 425.8953 | 418.1574 | 454.1715 | 490.6061
| SO2 (kg) | 904.5841 | 941.2761 | 935.0925 | 703.7766 | 469.3434 | 1161.1494 | 473.5883 | 743.8012 | 874.8594 | 141.7196 | 1475.4252 | 938.5474 | 540.3418 | 611.5957 | 538.871 | 1312.9041
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0041 | 0.0027 | 0.0026 | 0.0026 | 0.0002 | 0.0022 | 0.0002 | 0.0031 | 0.0035 | 0.0006 | 0.0046 | 0.0038 | 0.0042 | 0.0044 | 0.0042 | 0.005
| Water for Electricity (m3) | 111.9543 | 321.0638 | 6907.19 | 1251.67 | 2831.82 | 5790.58 | 2857.12 | 46.247 | 909.5526 | 1871.11 | 339.5802 | 975.6777 | 354.8315 | 14499.3 | 353.7557 | 263.2101

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 769.93 | 159.24 | 159.24
Net Site Energy | 769.93 | 159.24 | 159.24
Total Source Energy | 2533.53 | 523.98 | 523.98
Net Source Energy | 2533.53 | 523.98 | 523.98
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9.14 | 0 | 0 | 0 | 0
Cooling | 156 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 65.9 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 760.79 | 9.14 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.421 | 0.457 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.421 | 0.457 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 4.365 | 12.593 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29431.79 | 20655.68 | 8776.11 | 0.7 | 3.02
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 85099.56 | 57534.39 | 27565.18 | 0.68 | 2.62
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39347.64 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19749.01 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44660.82 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.31 | 1491.95 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.43 | 3747.81 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9784.6025 | 17.0149 | 64.053 | 0 | 0.0003 | 7927.2544 | 4201.4264
February | 8762.3914 | 15.4013 | 58.6513 | 0 | 0.0003 | 7258.857 | 3778.9199
March | 10141.861 | 17.8101 | 67.7605 | 0 | 0.0003 | 8386.2264 | 4372.2554
April | 10101.8133 | 17.8104 | 68.0489 | 0 | 0.0003 | 8421.9724 | 4362.0684
May | 11987.8192 | 21.1418 | 80.8023 | 0 | 0.0004 | 10000.3829 | 5177.0852
June | 13156.5322 | 23.2029 | 88.6798 | 0 | 0.0004 | 10975.3373 | 5681.8081
July | 13822.1641 | 24.3768 | 93.1664 | 0 | 0.0004 | 11530.6154 | 5969.2693
August | 14442.7009 | 25.4712 | 97.349 | 0 | 0.0004 | 12048.2747 | 6237.2557
September | 12175.859 | 21.4734 | 82.0697 | 0 | 0.0004 | 10157.2479 | 5258.2925
October | 11149.5746 | 19.6629 | 75.1478 | 0 | 0.0003 | 9300.572 | 4815.0239
November | 9840.3543 | 17.3508 | 66.2982 | 0 | 0.0003 | 8205.3066 | 4249.3028
December | 9314.3114 | 16.3982 | 62.5573 | 0 | 0.0003 | 7742.294 | 4019.6393
Annual Sum or Average | 134679.9839 | 237.1148 | 904.5841 | 0 | 0.0041 | 111954.3411 | 58122.3469
Minimum of Months | 8762.3914 | 15.4013 | 58.6513 | 0 | 0.0003 | 7258.857 | 3778.9199
Maximum of Months | 14442.7009 | 25.4712 | 97.349 | 0 | 0.0004 | 12048.2747 | 6237.2557
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 53870100000 | 55826.748 | 24-JAN-13:00 | 28855.207 | 9104.397 | 5314.174 | 0 | 12552.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 49328000000 | 62810.948 | 22-FEB-13:00 | 28855.207 | 9104.397 | 5314.174 | 0 | 19537.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 56989100000 | 68879.476 | 13-MAR-15:00 | 28855.207 | 9104.397 | 5314.174 | 0 | 25605.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 57232000000 | 73544.473 | 03-APR-14:50 | 28855.207 | 9104.397 | 5314.174 | 0 | 30270.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 67958200000 | 83520.254 | 24-MAY-14:00 | 28855.207 | 9104.397 | 5314.174 | 0 | 40246.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 74583500000 | 84532.717 | 28-JUN-14:00 | 28855.207 | 9104.397 | 5314.174 | 0 | 41258.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 78356900000 | 83070.756 | 10-JUL-13:50 | 28855.207 | 9104.397 | 5314.174 | 0 | 39796.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 81874700000 | 84481.124 | 21-AUG-14:30 | 28855.207 | 9104.397 | 5314.174 | 0 | 41207.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 69024100000 | 82930.679 | 11-SEP-14:00 | 28855.207 | 9104.397 | 5314.174 | 0 | 39656.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63202600000 | 79098.62 | 06-OCT-14:20 | 28855.207 | 9104.397 | 5314.174 | 0 | 35824.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 55759600000 | 67041.386 | 07-NOV-14:50 | 28855.207 | 9104.397 | 5314.174 | 0 | 23767.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 52613200000 | 57457.757 | 13-DEC-15:39 | 28855.207 | 9104.397 | 5314.174 | 0 | 14183.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 760792000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 49328000000 | 55826.748 |  | 28855.207 | 9104.397 | 5314.174 | 0 | 12552.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 81874700000 | 84532.717 |  | 28855.207 | 9104.397 | 5314.174 | 0 | 41258.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 19886.97 | 104.44 | 0 | 19991.41
Cost per Total Building Area ($/m2) | 4.11 | 0.02 | 0 | 4.13
Cost per Net Conditioned Building Area ($/m2) | 4.11 | 0.02 | 0 | 4.13

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 921.69 | 190.62 | 190.62
Net Site Energy | 921.69 | 190.62 | 190.62
Total Source Energy | 2810.79 | 581.33 | 581.33
Net Source Energy | 2810.79 | 581.33 | 581.33
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 211.34 | 0 | 0 | 0 | 0
Cooling | 103.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.6 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 67.79 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 710.35 | 211.34 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.375 | 0.404 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.375 | 0.404 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.018 | 1.201 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26904.23 | 18694.01 | 8210.21 | 0.69 | 3.01
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 87111.62 | 58894.71 | 28216.92 | 0.68 | 2.62
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39203.23 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23913.05 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 110763.49 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.17 | 1328.68 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.51 | 3836.43 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15960.596 | 19.5233 | 70.5734 | 0 | 0.0002 | 24067.332 | 6173.0005
February | 14028.3024 | 17.232 | 63.0428 | 0 | 0.0002 | 21499.6342 | 5434.985
March | 13313.6201 | 17.1767 | 71.3515 | 0 | 0.0002 | 24337.6457 | 5264.1227
April | 11729.6172 | 15.3924 | 66.4951 | 0 | 0.0002 | 22682.3402 | 4671.2512
May | 14040.2986 | 18.4523 | 79.9805 | 0 | 0.0002 | 27282.4997 | 5595.0205
June | 16690.7523 | 21.9385 | 95.1193 | 0 | 0.0003 | 32446.6072 | 6651.5927
July | 17971.2088 | 23.6215 | 102.4166 | 0 | 0.0003 | 34935.798 | 7161.8797
August | 17984.54 | 23.639 | 102.4925 | 0 | 0.0003 | 34961.7137 | 7167.1925
September | 14045.3406 | 18.4613 | 80.0427 | 0 | 0.0002 | 27303.7378 | 5597.3381
October | 12704.778 | 16.6812 | 72.151 | 0 | 0.0002 | 24611.6793 | 5060.7788
November | 12528.269 | 16.2538 | 68.408 | 0 | 0.0002 | 23334.0478 | 4965.246
December | 15170.6793 | 18.7085 | 69.2028 | 0 | 0.0002 | 23600.7874 | 5887.0204
Annual Sum or Average | 176168.0023 | 227.0805 | 941.2761 | 0 | 0.0027 | 321063.823 | 69629.428
Minimum of Months | 11729.6172 | 15.3924 | 63.0428 | 0 | 0.0002 | 21499.6342 | 4671.2512
Maximum of Months | 17984.54 | 23.639 | 102.4925 | 0 | 0.0003 | 34961.7137 | 7167.1925
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 53249000000 | 46739.705 | 03-JAN-13:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 3540.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 47568000000 | 48317.165 | 23-FEB-15:50 | 28855.207 | 9104.397 | 5239.508 | 0 | 5118.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 53847100000 | 46363.537 | 24-MAR-13:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 3164.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 50184700000 | 59937.184 | 21-APR-14:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 16738.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 60362600000 | 80366.892 | 18-MAY-15:39 | 28855.207 | 9104.397 | 5239.508 | 0 | 37167.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 71788200000 | 82170.535 | 13-JUN-14:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 38971.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 77295500000 | 84640.152 | 31-JUL-13:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 41441.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77352900000 | 84851.747 | 31-AUG-13:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 41652.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60409600000 | 80753.365 | 15-SEP-14:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 37554.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 54453400000 | 67750.231 | 06-OCT-15:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 24551.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 51626600000 | 49516.299 | 03-NOV-14:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 6317.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 52216800000 | 46671.554 | 19-DEC-14:00 | 28855.207 | 9104.397 | 5239.508 | 0 | 3472.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 710354000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 47568000000 | 46363.537 |  | 28855.207 | 9104.397 | 5239.508 | 0 | 3164.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 77352900000 | 84851.747 |  | 28855.207 | 9104.397 | 5239.508 | 0 | 41652.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24989.09 | 1701.91 | 0 | 26690.99
Cost per Total Building Area ($/m2) | 5.17 | 0.35 | 0 | 5.52
Cost per Net Conditioned Building Area ($/m2) | 5.17 | 0.35 | 0 | 5.52

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 985.94 | 203.91 | 203.91
Net Site Energy | 985.94 | 203.91 | 203.91
Total Source Energy | 2810.3 | 581.23 | 581.23
Net Source Energy | 2810.3 | 581.23 | 581.23
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 148.83 | 0 | 0 | 0 | 0
Cooling | 170.11 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 128.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 837.11 | 148.83 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.261 | 0.275 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.261 | 0.275 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.844 | 2.547 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28251.09 | 21174.92 | 7076.17 | 0.75 | 3.11
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 96963.67 | 65555.51 | 31408.16 | 0.68 | 2.9
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 37800.65 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22015.29 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 78944.21 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.48 | 1684.4 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.9 | 7448 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13526.327 | 21.1644 | 64.3391 | 0 | 0.0002 | 475186.9913 | 5580.0961
February | 12169.8866 | 19.0256 | 57.7679 | 0 | 0.0002 | 426653.9187 | 5018.8508
March | 11973.3642 | 19.9245 | 65.5605 | 0 | 0.0002 | 484276.6027 | 5059.7737
April | 11016.7247 | 18.5795 | 62.109 | 0 | 0.0002 | 458794.3199 | 4680.4867
May | 13566.2758 | 22.9239 | 76.805 | 0 | 0.0002 | 567354.4423 | 5768.1769
June | 18478.5871 | 31.2318 | 104.668 | 0 | 0.0003 | 773176.8041 | 7857.5456
July | 19992.5995 | 33.7907 | 113.2441 | 0 | 0.0003 | 836528.2793 | 8501.3453
August | 19553.0798 | 33.0479 | 110.7545 | 0 | 0.0003 | 818137.9426 | 8314.4507
September | 15426.7574 | 26.0737 | 87.3818 | 0 | 0.0002 | 645484.7872 | 6559.8369
October | 11770.5758 | 19.8706 | 66.5017 | 0 | 0.0002 | 491243.3609 | 5002.7566
November | 11180.0071 | 18.683 | 61.7858 | 0 | 0.0002 | 456398.5452 | 4732.4721
December | 14177.9192 | 21.7329 | 64.1752 | 0 | 0.0002 | 473950.2351 | 5803.2852
Annual Sum or Average | 172832.1043 | 286.0485 | 935.0925 | 0 | 0.0026 | 6907190 | 72879.0765
Minimum of Months | 11016.7247 | 18.5795 | 57.7679 | 0 | 0.0002 | 426653.9187 | 4680.4867
Maximum of Months | 19992.5995 | 33.7907 | 113.2441 | 0 | 0.0003 | 836528.2793 | 8501.3453
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 57589900000 | 48830.343 | 26-JAN-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 1663.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 51708000000 | 49767.92 | 28-FEB-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 2601.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 58691500000 | 64913.598 | 17-MAR-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 17747.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 55603200000 | 67866.518 | 26-APR-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 20700.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 68760100000 | 83185 | 30-MAY-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 36018.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 93704500000 | 94278.076 | 28-JUN-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 47111.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 101382000000 | 94409.14 | 11-JUL-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 47242.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 99153500000 | 94150.178 | 01-AUG-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 46983.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 78229000000 | 90657.805 | 08-SEP-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 43491.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59535800000 | 69221.587 | 02-OCT-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 22055.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 55312800000 | 57709.864 | 13-NOV-15:00 | 28855.207 | 9104.397 | 9206.806 | 0 | 10543.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 57440000000 | 48685.149 | 11-DEC-15:50 | 28855.207 | 9104.397 | 9206.806 | 0 | 1518.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 837111000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 51708000000 | 48685.149 |  | 28855.207 | 9104.397 | 9206.806 | 0 | 1518.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 101382000000 | 94409.14 |  | 28855.207 | 9104.397 | 9206.806 | 0 | 47242.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26292.43 | 1197.87 | 0 | 27490.3
Cost per Total Building Area ($/m2) | 5.44 | 0.25 | 0 | 5.69
Cost per Net Conditioned Building Area ($/m2) | 5.44 | 0.25 | 0 | 5.69

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1172.09 | 242.41 | 242.41
Net Site Energy | 1172.09 | 242.41 | 242.41
Total Source Energy | 2919.62 | 603.83 | 603.83
Net Source Energy | 2919.62 | 603.83 | 603.83
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 450.39 | 0 | 0 | 0 | 0
Cooling | 45.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 137.72 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 721.7 | 450.39 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.409 | 0.444 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.409 | 0.444 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.255 | 0.129 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.255 | 0.129 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.255 | 0.129 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.255 | 0.129 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25072 | 17867.32 | 7204.68 | 0.71 | 3.04
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 117601.33 | 79508.29 | 38093.05 | 0.68 | 2.9
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 46185.81 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27359.1 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 144041.49 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.84 | 77.66 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.16 | 1321.75 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.74 | 9033.22 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18936.0962 | 29.4072 | 59.9797 | 0 | 0.0002 | 106628.0405 | 7682.2675
February | 16090.1711 | 25.3638 | 52.8098 | 0 | 0.0002 | 93887.161 | 6562.4412
March | 13489.4238 | 24.1041 | 58.1954 | 0 | 0.0002 | 103500.8224 | 5763.9926
April | 11182.9963 | 20.8413 | 52.4538 | 0 | 0.0002 | 93298.1998 | 4857.7513
May | 11386.2528 | 21.9716 | 57.091 | 0 | 0.0002 | 101553.4957 | 5015.4453
June | 12605.839 | 24.3417 | 63.2878 | 0 | 0.0002 | 112576.6186 | 5554.1931
July | 13242.4826 | 25.571 | 66.4842 | 0 | 0.0002 | 118262.3678 | 5834.7034
August | 13485.3899 | 26.0403 | 67.7047 | 0 | 0.0002 | 120433.3506 | 5941.7474
September | 11381.5022 | 21.9768 | 57.1378 | 0 | 0.0002 | 101636.9247 | 5014.6837
October | 11295.7476 | 21.4607 | 54.9889 | 0 | 0.0002 | 97811.2847 | 4944.5262
November | 13459.3559 | 23.5519 | 55.6221 | 0 | 0.0002 | 98918.8832 | 5705.1074
December | 17063.854 | 27.3099 | 58.0213 | 0 | 0.0002 | 103158.0502 | 6997.5384
Annual Sum or Average | 163619.1116 | 291.9403 | 703.7766 | 0 | 0.0026 | 1251670 | 69874.3974
Minimum of Months | 11182.9963 | 20.8413 | 52.4538 | 0 | 0.0002 | 93298.1998 | 4857.7513
Maximum of Months | 18936.0962 | 29.4072 | 67.7047 | 0 | 0.0002 | 120433.3506 | 7682.2675
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 61480700000 | 48388.985 | 02-JAN-09:30 | 28855.207 | 9104.397 | 10429.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54134400000 | 48392.236 | 09-FEB-09:09 | 28855.207 | 9104.397 | 10432.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 59677600000 | 50009.643 | 28-MAR-15:00 | 28855.207 | 9104.397 | 10429.381 | 0 | 1620.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 53794900000 | 58766.862 | 14-APR-15:00 | 28855.207 | 9104.397 | 10429.381 | 0 | 10377.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 58554800000 | 71708.392 | 15-MAY-14:00 | 28855.207 | 9104.397 | 10429.381 | 0 | 23319.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64910600000 | 82771.604 | 19-JUN-14:00 | 28855.207 | 9104.397 | 10429.381 | 0 | 34382.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 68189000000 | 93463.056 | 03-JUL-15:50 | 28855.207 | 9104.397 | 10429.381 | 0 | 45074.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 69440700000 | 83200.449 | 17-AUG-13:00 | 28855.207 | 9104.397 | 10429.381 | 0 | 34811.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 58602900000 | 74152.18 | 11-SEP-13:00 | 28855.207 | 9104.397 | 10429.381 | 0 | 25763.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 56397100000 | 60435.714 | 12-OCT-15:00 | 28855.207 | 9104.397 | 10429.381 | 0 | 12046.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 57035700000 | 49446.269 | 22-NOV-15:09 | 28855.207 | 9104.397 | 10429.381 | 0 | 1057.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 59480000000 | 48388.985 | 01-DEC-09:09 | 28855.207 | 9104.397 | 10429.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 721698000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 53794900000 | 48388.985 |  | 28855.207 | 9104.397 | 10429.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 69440700000 | 93463.056 |  | 28855.207 | 9104.397 | 10432.632 | 0 | 45074.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20976.78 | 4240.65 | 0 | 25217.43
Cost per Total Building Area ($/m2) | 4.34 | 0.88 | 0 | 5.22
Cost per Net Conditioned Building Area ($/m2) | 4.34 | 0.88 | 0 | 5.22

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 656.77 | 135.83 | 135.83
Net Site Energy | 656.77 | 135.83 | 135.83
Total Source Energy | 1880.19 | 388.86 | 388.86
Net Source Energy | 1880.19 | 388.86 | 388.86
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 76.14 | 0 | 0 | 0 | 0
Cooling | 5.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 36.1 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 580.63 | 76.14 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.642 | 2.177 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.44 | 0.272 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.44 | 0.272 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.44 | 0.272 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.44 | 0.272 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15927.95 | 11955.79 | 3972.16 | 0.75 | 3.09
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 44391.71 | 30012.49 | 14379.22 | 0.68 | 2.62
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39207.88 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17467.59 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 56368.56 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.84 | 970.24 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.79 | 1955.03 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5531.885 | 4.795 | 40.691 | 0 | 0 | 245487.0174 | 2038.7415
February | 4781.0191 | 4.1379 | 36.2746 | 0 | 0 | 218847.3352 | 1765.391
March | 4921.6558 | 4.2378 | 41.2506 | 0 | 0 | 248884.3087 | 1829.2474
April | 4191.8963 | 3.5986 | 37.0792 | 0 | 0 | 223723.3988 | 1563.9496
May | 4247.2674 | 3.6385 | 38.926 | 0 | 0 | 234871.1092 | 1588.7481
June | 4134.0217 | 3.5398 | 38.194 | 0 | 0 | 230455.3643 | 1547.3202
July | 4019.3559 | 3.4399 | 37.4465 | 0 | 0 | 225946.0176 | 1505.3536
August | 4457.0171 | 3.8144 | 41.524 | 0 | 0 | 250549.0575 | 1669.2691
September | 4150.9648 | 3.5527 | 38.6473 | 0 | 0 | 233191.2121 | 1554.5671
October | 4317.413 | 3.6968 | 39.9033 | 0 | 0 | 240768.8433 | 1616.0072
November | 4429.6988 | 3.8008 | 39.5351 | 0 | 0 | 238542.7018 | 1653.7462
December | 5107.6765 | 4.4144 | 39.8719 | 0 | 0 | 240554.9832 | 1889.4231
Annual Sum or Average | 54289.8713 | 46.6665 | 469.3434 | 0 | 0.0002 | 2831820 | 20221.764
Minimum of Months | 4019.3559 | 3.4399 | 36.2746 | 0 | 0 | 218847.3352 | 1505.3536
Maximum of Months | 5531.885 | 4.795 | 41.524 | 0 | 0 | 250549.0575 | 2038.7415
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 50334100000 | 48308.28 | 02-JAN-16:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 44871900000 | 42906.264 | 13-FEB-11:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 1946.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 51030600000 | 42633.806 | 31-MAR-14:09 | 28855.207 | 9104.397 | 2999.676 | 0 | 1674.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 45871700000 | 43459.931 | 11-APR-15:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 2500.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 48157400000 | 42832.78 | 30-MAY-13:50 | 28855.207 | 9104.397 | 2999.676 | 0 | 1873.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 47252000000 | 43101.773 | 30-JUN-14:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 2142.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 46327400000 | 51256.146 | 10-JUL-15:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 10296.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 51372000000 | 56870.726 | 08-AUG-12:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 15911.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 47813000000 | 57980.736 | 25-SEP-12:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 17021.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 49366700000 | 47257.092 | 19-OCT-10:00 | 28855.207 | 9104.397 | 2999.676 | 0 | 6297.812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 48910200000 | 48760.381 | 20-NOV-16:49 | 28855.207 | 9104.397 | 2999.676 | 0 | 452.101 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 49322800000 | 48570.817 | 18-DEC-16:49 | 28855.207 | 9104.397 | 2999.676 | 0 | 262.537 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 580630000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 44871900000 | 42633.806 |  | 28855.207 | 9104.397 | 2999.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 51372000000 | 57980.736 |  | 28855.207 | 9104.397 | 2999.676 | 0 | 17021.455 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22163.89 | 675.05 | 0 | 22838.95
Cost per Total Building Area ($/m2) | 4.58 | 0.14 | 0 | 4.72
Cost per Net Conditioned Building Area ($/m2) | 4.58 | 0.14 | 0 | 4.72

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1050.03 | 217.17 | 217.17
Net Site Energy | 1050.03 | 217.17 | 217.17
Total Source Energy | 3034.89 | 627.68 | 627.68
Net Source Energy | 3034.89 | 627.68 | 627.68
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 290.16 | 0 | 0 | 0 | 0
Cooling | 104.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.44 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 116.43 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 759.86 | 290.16 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.273 | 0.288 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.273 | 0.288 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.1 | 1.317 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.251 | 0.11 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21657.82 | 17055.67 | 4602.15 | 0.79 | 3.19
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 81451.3 | 56731.9 | 24719.4 | 0.7 | 2.96
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 36355.77 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23744.13 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 103684.34 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1445.27 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.55 | 6777.99 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18437.5095 | 26.3347 | 90.2888 | 0 | 0.0002 | 450158.4408 | 7378.911
February | 13131.2693 | 20.1518 | 77.4266 | 0 | 0.0001 | 386099.3205 | 5400.4
March | 14858.7474 | 22.8866 | 88.3998 | 0 | 0.0002 | 440822.3874 | 6119.5543
April | 11597.4493 | 18.9553 | 79.2617 | 0 | 0.0001 | 395297.6291 | 4889.898
May | 13085.2341 | 21.4289 | 89.8237 | 0 | 0.0002 | 447974.593 | 5521.5569
June | 17270.4389 | 28.3218 | 118.9197 | 0 | 0.0002 | 593085.0703 | 7291.635
July | 18838.7006 | 30.8941 | 129.723 | 0 | 0.0002 | 646964.1919 | 7953.8119
August | 19110.2777 | 31.3395 | 131.5931 | 0 | 0.0002 | 656290.7722 | 8068.4734
September | 14400.4332 | 23.6156 | 99.1601 | 0 | 0.0002 | 494538.5877 | 6079.9371
October | 12417.9731 | 20.3192 | 85.0834 | 0 | 0.0002 | 424332.8607 | 5238.2258
November | 13591.1224 | 21.2383 | 83.7174 | 0 | 0.0002 | 417484.675 | 5629.1004
December | 16992.1803 | 24.7534 | 87.752 | 0 | 0.0002 | 437534.1112 | 6850.687
Annual Sum or Average | 183731.3358 | 290.2392 | 1161.1494 | 0 | 0.0022 | 5790580 | 76422.1908
Minimum of Months | 11597.4493 | 18.9553 | 77.4266 | 0 | 0.0001 | 386099.3205 | 4889.898
Maximum of Months | 19110.2777 | 31.3395 | 131.5931 | 0 | 0.0002 | 656290.7722 | 8068.4734
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 59071600000 | 53606.267 | 02-JAN-16:40 | 28855.207 | 9104.397 | 8297.662 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 50665500000 | 46257.267 | 01-FEB-09:09 | 28855.207 | 9104.397 | 8297.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 57846500000 | 47727.778 | 31-MAR-14:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 1470.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 51872600000 | 63665.316 | 21-APR-15:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 17408.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 58785000000 | 74572.633 | 31-MAY-15:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 28315.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 77827000000 | 83075.164 | 27-JUN-15:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 36817.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 84897300000 | 82977.528 | 25-JUL-15:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 36720.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 86121100000 | 82792.335 | 04-AUG-15:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 36535.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 64895400000 | 81603.521 | 01-SEP-14:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 35346.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 55682700000 | 63037.068 | 06-OCT-13:00 | 28855.207 | 9104.397 | 8297.662 | 0 | 16779.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 54784000000 | 53810.73 | 10-NOV-16:40 | 28855.207 | 9104.397 | 8297.662 | 0 | 204.464 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 57415000000 | 53606.267 | 01-DEC-16:30 | 28855.207 | 9104.397 | 8297.662 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 759864000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 50665500000 | 46257.267 |  | 28855.207 | 9104.397 | 8297.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 86121100000 | 83075.164 |  | 28855.207 | 9104.397 | 8297.662 | 0 | 36817.898 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21676.39 | 2196.05 | 0 | 23872.44
Cost per Total Building Area ($/m2) | 4.48 | 0.45 | 0 | 4.94
Cost per Net Conditioned Building Area ($/m2) | 4.48 | 0.45 | 0 | 4.94

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 855.48 | 176.93 | 176.93
Net Site Energy | 855.48 | 176.93 | 176.93
Total Source Energy | 2107.57 | 435.89 | 435.89
Net Source Energy | 2107.57 | 435.89 | 435.89
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 269.66 | 0 | 0 | 0 | 0
Cooling | 1.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.5 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 45.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 585.82 | 269.66 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.501 | 0.553 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.501 | 0.553 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.86 | 0.987 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12380.39 | 9887.66 | 2492.73 | 0.8 | 3.19
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 47263.22 | 34830.58 | 12432.64 | 0.74 | 2.71
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39333.64 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18266.9 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 75348.98 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.75 | 867.49 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.38 | 2598.42 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8403.6403 | 7.395 | 41.9906 | 0 | 0 | 253243.3888 | 3036.6256
February | 5453.0513 | 4.7447 | 36.8839 | 0 | 0 | 222505.2207 | 1999.8416
March | 6450.1976 | 5.6209 | 42.0899 | 0 | 0 | 253903.4437 | 2360.8388
April | 5137.6021 | 4.4542 | 37.6059 | 0 | 0 | 226873.5428 | 1892.8667
May | 4684.4311 | 4.034 | 39.186 | 0 | 0 | 236427.4331 | 1740.8445
June | 4316.1163 | 3.7045 | 38.3092 | 0 | 0 | 231145.0586 | 1610.6949
July | 4104.0178 | 3.5174 | 37.3322 | 0 | 0 | 225253.6859 | 1534.3066
August | 4461.0928 | 3.8237 | 40.5344 | 0 | 0 | 244574.8434 | 1667.6607
September | 4188.0642 | 3.5889 | 38.1978 | 0 | 0 | 230476.8811 | 1566.0362
October | 4555.7103 | 3.9123 | 40.0555 | 0 | 0 | 241680.5725 | 1698.9468
November | 5410.9495 | 4.6878 | 40.2277 | 0 | 0 | 242693.2706 | 1995.4717
December | 7657.1213 | 6.7218 | 41.1752 | 0 | 0 | 248344.15 | 2775.7666
Annual Sum or Average | 64821.9947 | 56.2049 | 473.5883 | 0 | 0.0002 | 2857120 | 23879.9007
Minimum of Months | 4104.0178 | 3.5174 | 36.8839 | 0 | 0 | 222505.2207 | 1534.3066
Maximum of Months | 8403.6403 | 7.395 | 42.0899 | 0 | 0 | 253903.4437 | 3036.6256
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 51924400000 | 48848.923 | 02-JAN-16:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 45621900000 | 42103.727 | 15-FEB-15:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 603.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 52059700000 | 41499.923 | 01-MAR-09:09 | 28855.207 | 9104.397 | 3540.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 46517600000 | 42350.842 | 13-APR-14:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 850.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 48476500000 | 42748.017 | 17-MAY-13:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 1248.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 47393400000 | 42973.079 | 16-JUN-14:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 1473.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 46185500000 | 52624.267 | 03-JUL-12:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 11124.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 50147000000 | 43415.086 | 15-AUG-12:09 | 28855.207 | 9104.397 | 3540.318 | 0 | 1915.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 47256400000 | 59114.64 | 28-SEP-14:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 17614.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 49553600000 | 42765.49 | 30-OCT-13:50 | 28855.207 | 9104.397 | 3540.318 | 0 | 1265.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 49761200000 | 48848.923 | 10-NOV-16:00 | 28855.207 | 9104.397 | 3540.318 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 50919900000 | 48848.923 | 01-DEC-16:49 | 28855.207 | 9104.397 | 3540.318 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 585817000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 45621900000 | 41499.923 |  | 28855.207 | 9104.397 | 3540.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 52059700000 | 59114.64 |  | 28855.207 | 9104.397 | 3540.318 | 0 | 17614.717 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24779.97 | 2351.65 | 0 | 27131.63
Cost per Total Building Area ($/m2) | 5.12 | 0.49 | 0 | 5.61
Cost per Net Conditioned Building Area ($/m2) | 5.12 | 0.49 | 0 | 5.61

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1567.55 | 324.2 | 324.2
Net Site Energy | 1567.55 | 324.2 | 324.2
Total Source Energy | 3533.31 | 730.76 | 730.76
Net Source Energy | 3533.31 | 730.76 | 730.76
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 834.24 | 0 | 0 | 0 | 0
Cooling | 34.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.43 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 159.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 733.31 | 834.24 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.33 | 0.352 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.33 | 0.352 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.559 | 0.611 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.354 | 0.355 | 0.274 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.354 | 0.355 | 0.274 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.354 | 0.355 | 0.274 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.354 | 0.355 | 0.274 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26918.93 | 18851.91 | 8067.03 | 0.7 | 3.02
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 132264.86 | 89422.05 | 42842.81 | 0.68 | 2.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 88469.74 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29179.63 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 167618.86 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 1.76 | 163.81 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.19 | 1357.05 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.33 | 9992.1 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23974.7977 | 33.7859 | 66.4918 | 0 | 0.0003 | 4131.3282 | 9397.1558
February | 18788.3953 | 27.6214 | 58.4266 | 0 | 0.0003 | 3630.9411 | 7468.9333
March | 15454.0339 | 25.5031 | 63.4277 | 0 | 0.0003 | 3943.3197 | 6397.9552
April | 10838.1514 | 19.8739 | 55.4608 | 0 | 0.0002 | 3448.87 | 4668.7791
May | 9757.7217 | 19.2396 | 57.3688 | 0 | 0.0002 | 3567.9912 | 4326.5135
June | 10673.5154 | 21.3352 | 64.3537 | 0 | 0.0003 | 4002.4912 | 4759.0761
July | 10944.5736 | 21.8819 | 66.0151 | 0 | 0.0003 | 4105.8248 | 4880.384
August | 11881.4312 | 23.7536 | 71.6584 | 0 | 0.0003 | 4456.8096 | 5298.0196
September | 9539.9562 | 19.0429 | 57.3734 | 0 | 0.0002 | 3568.3424 | 4251.2345
October | 11059.4758 | 20.7024 | 58.9267 | 0 | 0.0002 | 3664.5491 | 4802.7607
November | 13767.9898 | 23.4051 | 60.2864 | 0 | 0.0003 | 3748.3215 | 5762.5105
December | 20053.6219 | 29.7805 | 64.012 | 0 | 0.0003 | 3978.2182 | 7999.2367
Annual Sum or Average | 166733.6638 | 285.9256 | 743.8012 | 0 | 0.0031 | 46247.007 | 70012.559
Minimum of Months | 9539.9562 | 19.0429 | 55.4608 | 0 | 0.0002 | 3448.87 | 4251.2345
Maximum of Months | 23974.7977 | 33.7859 | 71.6584 | 0 | 0.0003 | 4456.8096 | 9397.1558
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 65508000000 | 56732.153 | 02-JAN-16:49 | 28855.207 | 9104.397 | 11423.548 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 57573700000 | 49472.561 | 08-FEB-09:09 | 28855.207 | 9104.397 | 11512.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 62526900000 | 50735.465 | 09-MAR-15:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 1352.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 54686700000 | 51157.722 | 04-APR-15:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 1774.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 56575500000 | 57568.233 | 15-MAY-15:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 8185.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63465100000 | 86931.159 | 30-JUN-15:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 37548.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 65103600000 | 93300.585 | 25-JUL-12:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 43917.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 70669000000 | 90164.611 | 17-AUG-15:39 | 28855.207 | 9104.397 | 11423.548 | 0 | 40781.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 56581100000 | 72778.52 | 08-SEP-14:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 23395.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 58106600000 | 54943.436 | 03-OCT-14:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 5560.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 59434900000 | 56732.153 | 06-NOV-16:00 | 28855.207 | 9104.397 | 11423.548 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 63080200000 | 56732.153 | 01-DEC-16:40 | 28855.207 | 9104.397 | 11423.548 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 733311000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54686700000 | 49472.561 |  | 28855.207 | 9104.397 | 11423.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 70669000000 | 93300.585 |  | 28855.207 | 9104.397 | 11512.957 | 0 | 43917.432 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16774.55 | 8040.09 | 0 | 24814.63
Cost per Total Building Area ($/m2) | 3.47 | 1.66 | 0 | 5.13
Cost per Net Conditioned Building Area ($/m2) | 3.47 | 1.66 | 0 | 5.13

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1318.15 | 272.62 | 272.62
Net Site Energy | 1318.15 | 272.62 | 272.62
Total Source Energy | 3044.6 | 629.68 | 629.68
Net Source Energy | 3044.6 | 629.68 | 629.68
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 597.04 | 0 | 0 | 0 | 0
Cooling | 25.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.48 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 156.81 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 721.1 | 597.04 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.335 | 0.358 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.335 | 0.358 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.637 | 0.704 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.362 | 0.225 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.362 | 0.225 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.362 | 0.225 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.362 | 0.225 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20837.51 | 16641.98 | 4195.52 | 0.8 | 3.22
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 116520.09 | 81969.63 | 34550.46 | 0.7 | 2.97
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 44832.58 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25307.63 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 135256.81 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.96 | 88.94 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.26 | 1434.01 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.22 | 9786.67 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24422.4072 | 36.4607 | 77.4612 | 0 | 0.0003 | 80507.2922 | 9854.5509
February | 19975.4891 | 30.6625 | 67.9069 | 0 | 0.0003 | 70585.0195 | 8142.6609
March | 20449.5383 | 32.5134 | 75.5984 | 0 | 0.0003 | 78589.4481 | 8446.0847
April | 15532.4494 | 26.2898 | 66.0494 | 0 | 0.0003 | 68675.1562 | 6571.5993
May | 15349.4894 | 26.8181 | 69.807 | 0 | 0.0003 | 72587.8022 | 6576.3879
June | 16175.6666 | 28.3761 | 74.1841 | 0 | 0.0003 | 77140.0155 | 6941.5906
July | 17061.3881 | 29.9348 | 78.273 | 0 | 0.0003 | 81391.8761 | 7322.1738
August | 17143.3252 | 30.0775 | 78.643 | 0 | 0.0003 | 81776.5563 | 7357.2304
September | 14777.1504 | 25.9171 | 67.7395 | 0 | 0.0003 | 70438.6166 | 6340.8768
October | 16296.8879 | 27.7059 | 69.9619 | 0 | 0.0003 | 72744.0188 | 6907.0186
November | 20071.1216 | 31.6341 | 72.6966 | 0 | 0.0003 | 75570.6815 | 8262.5551
December | 24511.004 | 36.3705 | 76.5383 | 0 | 0.0003 | 79546.0858 | 9868.4824
Annual Sum or Average | 221765.9173 | 362.7604 | 874.8594 | 0 | 0.0035 | 909552.5687 | 92591.2112
Minimum of Months | 14777.1504 | 25.9171 | 66.0494 | 0 | 0.0003 | 68675.1562 | 6340.8768
Maximum of Months | 24511.004 | 36.4607 | 78.643 | 0 | 0.0003 | 81776.5563 | 9868.4824
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 63827200000 | 49254.694 | 02-JAN-09:09 | 28855.207 | 9104.397 | 11295.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 55960700000 | 49254.694 | 01-FEB-09:09 | 28855.207 | 9104.397 | 11295.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 62306700000 | 49254.694 | 01-MAR-09:09 | 28855.207 | 9104.397 | 11295.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 54446500000 | 51183.856 | 21-APR-15:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 1929.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 57548500000 | 64677.986 | 31-MAY-15:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 15423.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 61157500000 | 76387.036 | 29-JUN-15:39 | 28855.207 | 9104.397 | 11295.089 | 0 | 27132.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 64528500000 | 78350.721 | 31-JUL-14:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 29096.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 64833400000 | 78963.869 | 01-AUG-13:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 29709.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 55844600000 | 61650.301 | 14-SEP-15:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 12395.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 57672300000 | 51215.399 | 13-OCT-14:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 1960.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 59913300000 | 56603.694 | 13-NOV-16:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 63065100000 | 56603.694 | 01-DEC-16:00 | 28855.207 | 9104.397 | 11295.089 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 721104000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54446500000 | 49254.694 |  | 28855.207 | 9104.397 | 11295.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 64833400000 | 78963.869 |  | 28855.207 | 9104.397 | 11295.089 | 0 | 29709.175 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7589.47 | 4083.05 | 0 | 11672.52
Cost per Total Building Area ($/m2) | 1.57 | 0.84 | 0 | 2.41
Cost per Net Conditioned Building Area ($/m2) | 1.57 | 0.84 | 0 | 2.41

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1281.13 | 264.96 | 264.96
Net Site Energy | 1281.13 | 264.96 | 264.96
Total Source Energy | 1827.54 | 377.97 | 377.97
Net Source Energy | 1827.54 | 377.97 | 377.97
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 621.82 | 0 | 0 | 0 | 0
Cooling | 1.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 119.51 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 659.31 | 621.82 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.364 | 0.391 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.364 | 0.391 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.58 | 0.636 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 4.092 | 0.392 | 0.253 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16133.65 | 12885.22 | 3248.43 | 0.8 | 3.17
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 84814.83 | 60222.52 | 24592.32 | 0.71 | 3.01
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 38791.02 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23618.39 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 121562.61 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1110.3 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.89 | 7417.65 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9759.4557 | 10.8927 | 13.0267 | 0 | 0.0001 | 171726.4748 | 3595.5883
February | 7003.5928 | 8.1299 | 11.3471 | 0 | 0.0001 | 149687.2179 | 2613.8005
March | 7357.89 | 8.6757 | 12.78 | 0 | 0.0001 | 168625.7111 | 2760.4343
April | 5030.2128 | 6.3181 | 11.208 | 0 | 0 | 147980.8258 | 1928.6165
May | 3342.5826 | 4.8206 | 11.4203 | 0 | 0 | 150904.4712 | 1348.2041
June | 2701.6053 | 4.1849 | 11.0734 | 0 | 0 | 146358.2536 | 1120.5883
July | 2458.0066 | 3.9148 | 10.7598 | 0 | 0 | 142225.0867 | 1031.0355
August | 2689.8585 | 4.2944 | 11.8409 | 0 | 0 | 156515.0333 | 1129.3966
September | 2787.2879 | 4.278 | 11.1716 | 0 | 0 | 147651.5406 | 1151.8838
October | 4061.6849 | 5.5498 | 11.9113 | 0 | 0 | 157353.5877 | 1605.2725
November | 7203.834 | 8.4714 | 12.3677 | 0 | 0.0001 | 163180.3965 | 2700.2107
December | 9687.1414 | 10.7936 | 12.8128 | 0 | 0.0001 | 168901.6244 | 3566.9785
Annual Sum or Average | 64083.1525 | 80.3238 | 141.7196 | 0 | 0.0006 | 1871110 | 24552.0096
Minimum of Months | 2458.0066 | 3.9148 | 10.7598 | 0 | 0 | 142225.0867 | 1031.0355
Maximum of Months | 9759.4557 | 10.8927 | 13.0267 | 0 | 0.0001 | 171726.4748 | 3595.5883
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 60509700000 | 53910.953 | 02-JAN-16:30 | 28855.207 | 9104.397 | 8602.349 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 52743900000 | 46561.953 | 01-FEB-09:09 | 28855.207 | 9104.397 | 8602.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 59417100000 | 46698.269 | 29-MAR-15:50 | 28855.207 | 9104.397 | 8602.349 | 0 | 136.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 52142600000 | 46561.953 | 03-APR-08:09 | 28855.207 | 9104.397 | 8602.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 53172800000 | 47805.633 | 04-MAY-14:00 | 28855.207 | 9104.397 | 8602.349 | 0 | 1243.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 51570900000 | 48545.5 | 28-JUN-14:00 | 28855.207 | 9104.397 | 8602.349 | 0 | 1983.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 50114500000 | 59444.28 | 24-JUL-14:00 | 28855.207 | 9104.397 | 8602.349 | 0 | 12882.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 55149800000 | 54260.886 | 07-AUG-15:00 | 28855.207 | 9104.397 | 8602.349 | 0 | 7698.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 52026600000 | 52515.155 | 01-SEP-15:00 | 28855.207 | 9104.397 | 8602.349 | 0 | 5953.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 55445200000 | 47170.625 | 17-OCT-14:00 | 28855.207 | 9104.397 | 8602.349 | 0 | 608.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 57498400000 | 53910.953 | 06-NOV-16:49 | 28855.207 | 9104.397 | 8602.349 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 59514300000 | 53910.953 | 01-DEC-16:19 | 28855.207 | 9104.397 | 8602.349 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 659306000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 50114500000 | 46561.953 |  | 28855.207 | 9104.397 | 8602.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 60509700000 | 59444.28 |  | 28855.207 | 9104.397 | 8602.349 | 0 | 12882.327 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13273.5 | 5261.05 | 0 | 18534.56
Cost per Total Building Area ($/m2) | 2.75 | 1.09 | 0 | 3.83
Cost per Net Conditioned Building Area ($/m2) | 2.75 | 1.09 | 0 | 3.83

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2074.58 | 429.06 | 429.06
Net Site Energy | 2074.58 | 429.06 | 429.06
Total Source Energy | 4199.12 | 868.46 | 868.46
Net Source Energy | 4199.12 | 868.46 | 868.46
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1286.61 | 0 | 0 | 0 | 0
Cooling | 22.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.45 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 226.83 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 787.97 | 1286.61 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.296 | 0.314 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.296 | 0.314 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34820.79 | 24409.81 | 10410.98 | 0.7 | 3.02
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 188354.83 | 127343.54 | 61011.29 | 0.68 | 2.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 202747.77 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37214.8 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 234016.98 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 4.47 | 414.97 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.54 | 1759.9 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.59 | 14229.48 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44086.438 | 62.8028 | 136.775 | 0 | 0.0005 | 31464.488 | 17436.9054
February | 34282.1124 | 50.9436 | 118.9915 | 0 | 0.0004 | 27378.3014 | 13760.6314
March | 32515.8569 | 51.2828 | 130.6285 | 0 | 0.0004 | 30061.8918 | 13335.0451
April | 23593.4619 | 40.1895 | 112.6408 | 0 | 0.0003 | 25927.5958 | 9960.6927
May | 21466.9147 | 38.645 | 114.9445 | 0 | 0.0003 | 26460.9599 | 9261.5747
June | 22305.6697 | 40.6048 | 122.1324 | 0 | 0.0004 | 28116.2392 | 9666.453
July | 23048.8614 | 41.9682 | 126.2646 | 0 | 0.0004 | 29067.5501 | 9989.5297
August | 23285.1906 | 42.3962 | 127.5457 | 0 | 0.0004 | 29362.4689 | 10091.7403
September | 20532.0777 | 37.3349 | 112.1738 | 0 | 0.0003 | 25823.6121 | 8893.8971
October | 23370.2506 | 40.8713 | 117.9416 | 0 | 0.0004 | 27149.3091 | 9967.9966
November | 28499.9947 | 46.2446 | 122.2615 | 0 | 0.0004 | 28138.6585 | 11811.9682
December | 39295.172 | 57.8482 | 133.1252 | 0 | 0.0004 | 30629.1453 | 15720.7464
Annual Sum or Average | 336282.0006 | 551.1319 | 1475.4252 | 0 | 0.0046 | 339580.2202 | 139897.1805
Minimum of Months | 20532.0777 | 37.3349 | 112.1738 | 0 | 0.0003 | 25823.6121 | 8893.8971
Maximum of Months | 44086.438 | 62.8028 | 136.775 | 0 | 0.0005 | 31464.488 | 17436.9054
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73011000000 | 61712.947 | 06-JAN-16:30 | 28855.207 | 9104.397 | 16404.342 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 63529300000 | 61372.387 | 01-FEB-16:00 | 28855.207 | 9104.397 | 16063.782 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 69756400000 | 54361.32 | 31-MAR-15:50 | 28855.207 | 9104.397 | 16063.782 | 0 | 337.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60163000000 | 54776.805 | 07-APR-14:00 | 28855.207 | 9104.397 | 16063.782 | 0 | 753.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 61400700000 | 65916.863 | 30-MAY-15:00 | 28855.207 | 9104.397 | 16063.782 | 0 | 11893.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 65241600000 | 91470.816 | 08-JUN-12:00 | 28855.207 | 9104.397 | 16063.782 | 0 | 37447.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 67449100000 | 94370.619 | 03-JUL-14:00 | 28855.207 | 9104.397 | 16063.782 | 0 | 40347.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 68133400000 | 89407.82 | 04-AUG-15:00 | 28855.207 | 9104.397 | 16063.782 | 0 | 35384.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 59921700000 | 72649.075 | 27-SEP-15:00 | 28855.207 | 9104.397 | 16063.782 | 0 | 18625.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 62997900000 | 56255.991 | 31-OCT-13:30 | 28855.207 | 9104.397 | 16063.782 | 0 | 2232.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 65293600000 | 61372.387 | 06-NOV-16:40 | 28855.207 | 9104.397 | 16063.782 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 71072600000 | 61372.387 | 01-DEC-16:19 | 28855.207 | 9104.397 | 16063.782 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 787970000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59921700000 | 54361.32 |  | 28855.207 | 9104.397 | 16063.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73011000000 | 94370.619 |  | 28855.207 | 9104.397 | 16404.342 | 0 | 40347.233 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11732.02 | 10613.59 | 0 | 22345.61
Cost per Total Building Area ($/m2) | 2.43 | 2.2 | 0 | 4.62
Cost per Net Conditioned Building Area ($/m2) | 2.43 | 2.2 | 0 | 4.62

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1731.22 | 358.05 | 358.05
Net Site Energy | 1731.22 | 358.05 | 358.05
Total Source Energy | 3612.37 | 747.11 | 747.11
Net Source Energy | 3612.37 | 747.11 | 747.11
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 957.69 | 0 | 0 | 0 | 0
Cooling | 13.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 221.23 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 773.53 | 957.69 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.285 | 0.302 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.285 | 0.302 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.511 | 0.554 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.354 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25962.13 | 20734.79 | 5227.34 | 0.8 | 3.22
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 176155.42 | 121016.74 | 55138.68 | 0.69 | 2.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 139355.41 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31588.53 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 191523.68 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 3.58 | 332.82 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.57 | 1786.68 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.41 | 13900 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 30349.3685 | 43.405 | 85.9538 | 0 | 0.0004 | 89316.4917 | 12059.3324
February | 24563.3161 | 36.1844 | 75.2742 | 0 | 0.0003 | 78229.935 | 9863.676
March | 24466.4306 | 37.68 | 83.8448 | 0 | 0.0003 | 87152.5484 | 9985.4738
April | 18373.1084 | 30.0702 | 72.5667 | 0 | 0.0003 | 75444.5285 | 7672.647
May | 17154.635 | 29.3023 | 74.392 | 0 | 0.0003 | 77351.1883 | 7284.1048
June | 16248.9855 | 28.3935 | 73.9183 | 0 | 0.0003 | 76862.8717 | 6962.1428
July | 16773.0387 | 29.4279 | 76.9446 | 0 | 0.0003 | 80010.5574 | 7198.324
August | 17831.6759 | 31.2804 | 81.775 | 0 | 0.0003 | 85033.3678 | 7652.1775
September | 16091.734 | 27.9703 | 72.3999 | 0 | 0.0003 | 75283.0443 | 6880.2125
October | 18600.668 | 30.9835 | 76.3934 | 0 | 0.0003 | 79426.9198 | 7820.7378
November | 23441.9846 | 36.0616 | 80.1138 | 0 | 0.0003 | 83273.956 | 9563.3738
December | 30521.8784 | 43.3799 | 84.9709 | 0 | 0.0004 | 88292.3371 | 12101.2118
Annual Sum or Average | 254416.8238 | 404.139 | 938.5474 | 0 | 0.0038 | 975677.746 | 105043.4141
Minimum of Months | 16091.734 | 27.9703 | 72.3999 | 0 | 0.0003 | 75283.0443 | 6880.2125
Maximum of Months | 30521.8784 | 43.405 | 85.9538 | 0 | 0.0004 | 89316.4917 | 12101.2118
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 70811200000 | 61328.112 | 05-JAN-16:49 | 28855.207 | 9104.397 | 16019.507 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62021600000 | 53979.112 | 14-FEB-09:09 | 28855.207 | 9104.397 | 16019.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 69095600000 | 54369.59 | 30-MAR-15:00 | 28855.207 | 9104.397 | 15761.092 | 0 | 648.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 59813300000 | 55272.097 | 25-APR-14:00 | 28855.207 | 9104.397 | 15761.092 | 0 | 1551.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 61325000000 | 63480.288 | 23-MAY-15:00 | 28855.207 | 9104.397 | 15761.092 | 0 | 9759.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 60937800000 | 75660.981 | 28-JUN-13:00 | 28855.207 | 9104.397 | 15761.092 | 0 | 21940.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 63433300000 | 82583.672 | 17-JUL-15:50 | 28855.207 | 9104.397 | 15761.092 | 0 | 28862.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67415500000 | 83313.776 | 30-AUG-13:00 | 28855.207 | 9104.397 | 15761.092 | 0 | 29593.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 59685300000 | 68466.789 | 06-SEP-15:00 | 28855.207 | 9104.397 | 15761.092 | 0 | 14746.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 62970600000 | 56127.476 | 05-OCT-14:00 | 28855.207 | 9104.397 | 15761.092 | 0 | 2406.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66020600000 | 61069.696 | 06-NOV-16:49 | 28855.207 | 9104.397 | 15761.092 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 69999200000 | 61328.112 | 01-DEC-16:40 | 28855.207 | 9104.397 | 16019.507 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 773529000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 59685300000 | 53979.112 |  | 28855.207 | 9104.397 | 15761.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 70811200000 | 83313.776 |  | 28855.207 | 9104.397 | 16019.507 | 0 | 29593.079 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8127.23 | 6569.84 | 0 | 14697.08
Cost per Total Building Area ($/m2) | 1.68 | 1.36 | 0 | 3.04
Cost per Net Conditioned Building Area ($/m2) | 1.68 | 1.36 | 0 | 3.04

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2864.61 | 592.46 | 592.46
Net Site Energy | 2864.61 | 592.46 | 592.46
Total Source Energy | 5058.94 | 1046.29 | 1046.29
Net Source Energy | 5058.94 | 1046.29 | 1046.29
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2041.25 | 0 | 0 | 0 | 0
Cooling | 15.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 268.79 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 823.36 | 2041.25 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.252 | 0.265 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.252 | 0.265 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.397 | 0.422 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37439.69 | 26466.19 | 10973.5 | 0.71 | 3.03
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 217220.86 | 146859.38 | 70361.48 | 0.68 | 2.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 262725.69 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40649.25 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 267753.12 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 5.91 | 548.91 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.7 | 1933.54 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.75 | 16410.19 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 51431.2362 | 62.7972 | 52.7029 | 0 | 0.0005 | 34529.4693 | 19340.6046
February | 36755.7562 | 47.2433 | 45.3648 | 0 | 0.0004 | 29747.2089 | 14047.9677
March | 26512.1617 | 38.7713 | 48.0077 | 0 | 0.0004 | 31522.1802 | 10581.6116
April | 16711.2425 | 27.6779 | 40.8083 | 0 | 0.0003 | 26814.7826 | 6979.4824
May | 14522.9896 | 26.0726 | 42.0388 | 0 | 0.0003 | 27632.4061 | 6258.5406
June | 14497.6913 | 26.4433 | 43.3206 | 0 | 0.0003 | 28476.534 | 6287.4165
July | 14238.9984 | 25.9809 | 42.5783 | 0 | 0.0003 | 27988.6697 | 6176.1289
August | 15316.6901 | 27.9489 | 45.8063 | 0 | 0.0003 | 30110.5326 | 6643.7316
September | 13578.5298 | 24.632 | 40.1352 | 0 | 0.0003 | 26382.1155 | 5875.9074
October | 17417.5794 | 29.0753 | 43.2741 | 0 | 0.0003 | 28436.0279 | 7296.2347
November | 24756.3955 | 36.4771 | 45.7187 | 0 | 0.0004 | 30020.9153 | 9906.9825
December | 41090.5707 | 52.7755 | 50.5862 | 0 | 0.0004 | 33170.6927 | 15700.9448
Annual Sum or Average | 286829.8415 | 425.8953 | 540.3418 | 0 | 0.0042 | 354831.535 | 115095.5532
Minimum of Months | 13578.5298 | 24.632 | 40.1352 | 0 | 0.0003 | 26382.1155 | 5875.9074
Maximum of Months | 51431.2362 | 62.7972 | 52.7029 | 0 | 0.0005 | 34529.4693 | 19340.6046
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 80123000000 | 64201.246 | 02-JAN-16:40 | 28855.207 | 9104.397 | 18892.641 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 69026200000 | 56852.246 | 01-FEB-09:09 | 28855.207 | 9104.397 | 18892.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 73144800000 | 56852.246 | 06-MAR-09:09 | 28855.207 | 9104.397 | 18892.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62221700000 | 56828.544 | 14-APR-15:00 | 28855.207 | 9104.397 | 18418.137 | 0 | 450.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 64118900000 | 67999.26 | 31-MAY-12:09 | 28855.207 | 9104.397 | 18418.137 | 0 | 11621.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 66077700000 | 90699.981 | 29-JUN-14:00 | 28855.207 | 9104.397 | 18418.137 | 0 | 34322.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 64945600000 | 89165.579 | 13-JUL-14:00 | 28855.207 | 9104.397 | 18418.137 | 0 | 32787.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 69869200000 | 86124.431 | 25-AUG-15:00 | 28855.207 | 9104.397 | 18418.137 | 0 | 29746.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 61217700000 | 68566.444 | 14-SEP-14:00 | 28855.207 | 9104.397 | 18418.137 | 0 | 12188.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65983700000 | 57259.986 | 06-OCT-14:00 | 28855.207 | 9104.397 | 18418.137 | 0 | 882.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 69661300000 | 64201.246 | 27-NOV-16:40 | 28855.207 | 9104.397 | 18892.641 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 76970100000 | 64201.246 | 13-DEC-16:30 | 28855.207 | 9104.397 | 18892.641 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 823360000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61217700000 | 56828.544 |  | 28855.207 | 9104.397 | 18418.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 80123000000 | 90699.981 |  | 28855.207 | 9104.397 | 18892.641 | 0 | 34322.24 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14995.12 | 16180.47 | 0 | 31175.59
Cost per Total Building Area ($/m2) | 3.1 | 3.35 | 0 | 6.45
Cost per Net Conditioned Building Area ($/m2) | 3.1 | 3.35 | 0 | 6.45

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2363.28 | 488.77 | 488.77
Net Site Energy | 2363.28 | 488.77 | 488.77
Total Source Energy | 4545.19 | 940.03 | 940.03
Net Source Energy | 4545.19 | 940.03 | 940.03
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1539.25 | 0 | 0 | 0 | 0
Cooling | 6.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 279.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 824.03 | 1539.25 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.274 | 0.289 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.274 | 0.289 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.444 | 0.475 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.385 | 0.305 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30425.09 | 24299.16 | 6125.93 | 0.8 | 3.19
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 191039.74 | 139580.78 | 51458.96 | 0.73 | 3.06
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 251102.53 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39200.05 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 256609.05 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 6.35 | 589.35 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.84 | 2010.06 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 9.41 | 17644.86 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 40332.4588 | 52.8184 | 58.8014 | 0 | 0.0005 | 1392320 | 15525.8948
February | 31874.3183 | 43.0609 | 51.2403 | 0 | 0.0004 | 1213690 | 12397.4512
March | 25445.9651 | 38.2011 | 54.7383 | 0 | 0.0004 | 1297600 | 10266.8679
April | 19147.9567 | 30.5331 | 47.6529 | 0 | 0.0003 | 1130000 | 7898.4989
May | 16754.9674 | 28.5182 | 48.2105 | 0 | 0.0003 | 1143540 | 7085.4788
June | 15632.3586 | 27.4639 | 48.0778 | 0 | 0.0003 | 1140530 | 6693.5318
July | 14974.341 | 26.5716 | 47.0077 | 0 | 0.0003 | 1115180 | 6437.2685
August | 16024.143 | 28.4124 | 50.2235 | 0 | 0.0003 | 1191460 | 6886.4306
September | 15326.222 | 26.7208 | 46.3937 | 0 | 0.0003 | 1100550 | 6542.6004
October | 19072.4819 | 31.1737 | 50.2167 | 0 | 0.0004 | 1190930 | 7940.9151
November | 24189.3511 | 36.4193 | 52.4136 | 0 | 0.0004 | 1242510 | 9769.9668
December | 35973.6815 | 48.2641 | 56.6193 | 0 | 0.0004 | 1341000 | 13959.5217
Annual Sum or Average | 274748.2454 | 418.1574 | 611.5957 | 0 | 0.0044 | 14499300 | 111404.4266
Minimum of Months | 14974.341 | 26.5716 | 46.3937 | 0 | 0.0003 | 1100550 | 6437.2685
Maximum of Months | 40332.4588 | 52.8184 | 58.8014 | 0 | 0.0005 | 1392320 | 15525.8948
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 79129100000 | 65552.878 | 04-JAN-16:49 | 28855.207 | 9104.397 | 20244.273 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 68976800000 | 58203.878 | 06-FEB-09:09 | 28855.207 | 9104.397 | 20244.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 73745500000 | 58203.878 | 03-MAR-09:09 | 28855.207 | 9104.397 | 20244.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 64220500000 | 57688.936 | 03-APR-08:09 | 28855.207 | 9104.397 | 19729.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 64990300000 | 59094.715 | 16-MAY-15:00 | 28855.207 | 9104.397 | 19729.332 | 0 | 1405.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64818900000 | 82715.518 | 30-JUN-14:00 | 28855.207 | 9104.397 | 19729.332 | 0 | 25026.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 63378300000 | 82200.42 | 21-JUL-15:00 | 28855.207 | 9104.397 | 19729.332 | 0 | 24511.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67713700000 | 77045.239 | 09-AUG-15:00 | 28855.207 | 9104.397 | 19729.332 | 0 | 19356.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 62546600000 | 60246.906 | 01-SEP-15:00 | 28855.207 | 9104.397 | 19729.332 | 0 | 2557.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67683500000 | 58666.481 | 06-OCT-15:00 | 28855.207 | 9104.397 | 19729.332 | 0 | 977.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 70614700000 | 65037.936 | 08-NOV-16:00 | 28855.207 | 9104.397 | 19729.332 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 76212500000 | 65552.878 | 08-DEC-16:40 | 28855.207 | 9104.397 | 20244.273 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 824030000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62546600000 | 57688.936 |  | 28855.207 | 9104.397 | 19729.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 79129100000 | 82715.518 |  | 28855.207 | 9104.397 | 20244.273 | 0 | 25026.581 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18256.1 | 12261.3 | 0 | 30517.4
Cost per Total Building Area ($/m2) | 3.78 | 2.54 | 0 | 6.31
Cost per Net Conditioned Building Area ($/m2) | 3.78 | 2.54 | 0 | 6.31

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3481.03 | 719.95 | 719.95
Net Site Energy | 3481.03 | 719.95 | 719.95
Total Source Energy | 5726.21 | 1184.29 | 1184.29
Net Source Energy | 5726.21 | 1184.29 | 1184.29
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2660.17 | 0 | 0 | 0 | 0
Cooling | 3.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 278.85 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 820.86 | 2660.17 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.227 | 0.237 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.227 | 0.237 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.351 | 0.371 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.487 | 0.409 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.487 | 0.409 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.487 | 0.409 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.487 | 0.409 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38351.68 | 27501.81 | 10849.88 | 0.72 | 3.03
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 234947.89 | 158844.32 | 76103.56 | 0.68 | 2.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 290146.32 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42279.46 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 283392.64 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 6.7 | 621.97 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.8 | 1971.66 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1017.59 | 9.46 | 16276.92 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 52257.5402 | 63.5342 | 52.6644 | 0 | 0.0005 | 34501.3461 | 19625.3489
February | 43360.8695 | 53.5223 | 46.3182 | 0 | 0.0004 | 30352.6253 | 16361.1023
March | 34585.0254 | 46.6199 | 49.7407 | 0 | 0.0004 | 32636.0061 | 13425.4256
April | 20656.6277 | 31.6312 | 42.0381 | 0 | 0.0003 | 27611.2062 | 8380.5542
May | 16329.3006 | 27.6781 | 41.9362 | 0 | 0.0003 | 27558.7784 | 6880.4538
June | 13699.3408 | 24.8307 | 40.4258 | 0 | 0.0003 | 26573.1024 | 5926.2365
July | 13454.4579 | 24.519 | 40.1334 | 0 | 0.0003 | 26381.3997 | 5832.932
August | 14643.9015 | 26.5567 | 43.2584 | 0 | 0.0003 | 28435.0684 | 6336.1738
September | 14670.7813 | 25.6832 | 40.3348 | 0 | 0.0003 | 26509.8937 | 6259.6511
October | 19140.2438 | 30.8067 | 43.8283 | 0 | 0.0003 | 28795.1436 | 7908.4886
November | 29608.8057 | 41.2378 | 46.9005 | 0 | 0.0004 | 30782.625 | 11620.4438
December | 46121.2848 | 57.5516 | 51.2921 | 0 | 0.0004 | 33618.5078 | 17462.1264
Annual Sum or Average | 318528.1791 | 454.1715 | 538.871 | 0 | 0.0042 | 353755.7025 | 126018.9372
Minimum of Months | 13454.4579 | 24.519 | 40.1334 | 0 | 0.0003 | 26381.3997 | 5832.932
Maximum of Months | 52257.5402 | 63.5342 | 52.6644 | 0 | 0.0005 | 34501.3461 | 19625.3489
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 80057800000 | 64179.151 | 02-JAN-16:30 | 28855.207 | 9104.397 | 18870.547 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 70431000000 | 56830.151 | 01-FEB-09:09 | 28855.207 | 9104.397 | 18870.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 75729400000 | 56830.151 | 02-MAR-09:09 | 28855.207 | 9104.397 | 18870.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 64069700000 | 56830.151 | 03-APR-08:09 | 28855.207 | 9104.397 | 18870.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63948100000 | 57654.24 | 31-MAY-15:00 | 28855.207 | 9104.397 | 18322.981 | 0 | 1371.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 61660900000 | 63682.096 | 14-JUN-15:00 | 28855.207 | 9104.397 | 18322.981 | 0 | 7399.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61216100000 | 80612.989 | 06-JUL-15:00 | 28855.207 | 9104.397 | 18322.981 | 0 | 24330.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 65981400000 | 70566.313 | 11-AUG-15:50 | 28855.207 | 9104.397 | 18322.981 | 0 | 14283.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 61514200000 | 58668.645 | 07-SEP-14:00 | 28855.207 | 9104.397 | 18322.981 | 0 | 2386.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 66817000000 | 56282.586 | 02-OCT-08:09 | 28855.207 | 9104.397 | 18322.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71428800000 | 64179.151 | 24-NOV-16:30 | 28855.207 | 9104.397 | 18870.547 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 78009200000 | 64179.151 | 05-DEC-16:19 | 28855.207 | 9104.397 | 18870.547 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 820863000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61216100000 | 56282.586 |  | 28855.207 | 9104.397 | 18322.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 80057800000 | 80612.989 |  | 28855.207 | 9104.397 | 18870.547 | 0 | 24330.403 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14301.4 | 20990.91 | 0 | 35292.31
Cost per Total Building Area ($/m2) | 2.96 | 4.34 | 0 | 7.3
Cost per Net Conditioned Building Area ($/m2) | 2.96 | 4.34 | 0 | 7.3

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6489.88 | 1342.23 | 1342.23
Net Site Energy | 6489.88 | 1342.23 | 1342.23
Total Source Energy | 9387.02 | 1941.42 | 1941.42
Net Source Energy | 9387.02 | 1941.42 | 1941.42
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5562.43 | 0 | 0 | 0 | 0
Cooling | 0.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 114.58 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 389 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 927.45 | 5562.43 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.174 | 0.18 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-METAL-SEMI | 0.3 | 0.174 | 0.18 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.269 | 0.28 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.702 | 0.633 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 2.956 | 0.702 | 0.633 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.702 | 0.633 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 2.956 | 0.702 | 0.633 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 2.96 | 0.702 | 0.633
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 2.96 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37799.96 | 30189.13 | 7610.82 | 0.8 | 3.19
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 209929.52 | 167661.32 | 42268.2 | 0.8 | 3.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 485610.43 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55478.72 | 0.8
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 392764.87 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 11.04 | 1024.91 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.28 | 2497.29 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.6 | 1017.59 | 12.68 | 21486.75 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 85054.8156 | 83.6598 | 135.1921 | 0 | 0.0006 | 27065.4868 | 30430.1454
February | 70802.1747 | 69.9137 | 118.246 | 0 | 0.0005 | 23676.5823 | 25372.9498
March | 53050.1339 | 54.0862 | 124.2001 | 0 | 0.0005 | 24890.8232 | 19273.128
April | 27724.9637 | 30.0011 | 101.2007 | 0 | 0.0004 | 20297.5453 | 10339.4308
May | 15300.8426 | 18.4062 | 94.538 | 0 | 0.0003 | 18972.166 | 5990.6884
June | 12809.7894 | 15.9113 | 89.6433 | 0 | 0.0003 | 17991.6531 | 5092.5831
July | 12104.7573 | 15.1351 | 86.7924 | 0 | 0.0003 | 17419.7709 | 4827.6157
August | 14163.6167 | 17.552 | 98.262 | 0 | 0.0003 | 19721.3089 | 5624.5099
September | 16993.6602 | 20.0154 | 96.0593 | 0 | 0.0003 | 19275.9756 | 6587.7281
October | 31300.0022 | 33.7332 | 111.3961 | 0 | 0.0004 | 22341.6076 | 11651.6717
November | 58844.4412 | 59.3789 | 124.9055 | 0 | 0.0005 | 25026.5141 | 21283.6077
December | 73247.7827 | 72.8132 | 132.4686 | 0 | 0.0006 | 26530.6871 | 26323.9406
Annual Sum or Average | 471396.9804 | 490.6061 | 1312.9041 | 0 | 0.005 | 263210.1208 | 172797.9993
Minimum of Months | 12104.7573 | 15.1351 | 86.7924 | 0 | 0.0003 | 17419.7709 | 4827.6157
Maximum of Months | 85054.8156 | 83.6598 | 135.1921 | 0 | 0.0006 | 27065.4868 | 30430.1454
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 95368200000 | 70317.559 | 02-JAN-09:09 | 28855.207 | 9104.397 | 25008.954 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 83427000000 | 70317.559 | 01-FEB-09:09 | 28855.207 | 9104.397 | 25008.954 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 87705500000 | 62968.559 | 01-MAR-09:09 | 28855.207 | 9104.397 | 25008.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 71520600000 | 62968.559 | 03-APR-08:09 | 28855.207 | 9104.397 | 25008.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 66850500000 | 62719.856 | 24-MAY-14:00 | 28855.207 | 9104.397 | 24058.446 | 0 | 701.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63395500000 | 64423.04 | 20-JUN-15:00 | 28855.207 | 9104.397 | 24058.446 | 0 | 2404.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 61380400000 | 64617.815 | 21-JUL-15:00 | 28855.207 | 9104.397 | 24058.446 | 0 | 2599.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 69490200000 | 64288.942 | 15-AUG-15:00 | 28855.207 | 9104.397 | 24058.446 | 0 | 2270.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 67921000000 | 62018.05 | 01-SEP-08:09 | 28855.207 | 9104.397 | 24058.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 78723100000 | 70317.559 | 23-OCT-08:09 | 28855.207 | 9104.397 | 25008.954 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 88183600000 | 70317.559 | 01-NOV-08:09 | 28855.207 | 9104.397 | 25008.954 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 93483700000 | 70317.559 | 01-DEC-09:09 | 28855.207 | 9104.397 | 25008.954 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 927449000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61380400000 | 62018.05 |  | 28855.207 | 9104.397 | 24058.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 95368200000 | 70317.559 |  | 28855.207 | 9104.397 | 25008.954 | 0 | 2599.765 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26150.5 | 22839.5 | 0 | 48990
Cost per Total Building Area ($/m2) | 5.41 | 4.72 | 0 | 10.13
Cost per Net Conditioned Building Area ($/m2) | 5.41 | 4.72 | 0 | 10.13

## Picture
DOE Commercial Building Benchmark - Warehouse

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 3.5 | 182.5
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.38 | 0.4 | 0.3 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 4.29 | 22.88 | 1193.03
|  |  | Sat, WinterDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.12 | 0.12 | 0.17 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.91
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.52
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2956 | 154134.29
|  |  | SummerDesign | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
|  |  | Sun, Hol, Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
HTGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372 | 2604 | 135780
HTGSETP_BulkStorage_SCH | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 4692 | 244654.29
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
CLGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8 | 4485.6 | 233892
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58 | 3024.29
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Through 9/30 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -240 | -1680 | -87600
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600