## Instructions
DRAFT PEI CALCULATOR |  |  |  | APPLICABILITY OF TEST METHODS BASED ON PUMP CONFIGURATION
INTRODUCTION: This Excel spreadsheet is designed to perform the calculations necessary to determine PEI -- a pump’s energy index -- as proposed in DOE's Notices of Proposed Rulemaking (Dockets EERE-2011-BT-STD-0031 and EERE-2013-BT-TP-0055). Under the proposals, the PEI calculations must be performed using measured values – that is, using results from testing actual pumps in accordance with the proposed test method and sampling plan. The PEI calculator is not considered an Alternative Efficiency Determination Method (AEDM) by the Department and could not to be used to simulate or estimate the efficiency of a pump. DOE is providing this "calculator" as a convenience at the request of interested parties. Interested parties should consult the Federal Register for the proposed formulas for calculating PEI and should not rely on this spreadsheet. Dockets EERE-2011-BT-STD-0031 and EERE-2013-BT-TP-0055 (available at www.regulations.gov) contains DOE's proposed rules for the standards and test procedure, respectively. While this calculator is an excel-based version of the calculations in the test procedure proposal, DOE did not rely on this document to develop the proposal itself. |  |  |  | Metric | Pump Configuration | Pump Sub-Configuration | Calculation-Based Test Method | Testing-Based Test Method
|  |  |  | PEICL | Bare Pump | Bare Pump | PEICL_Calc_BarePump: Tested Pump Efficiency of Bare Pump + Default Motor Efficiency + Default Motor Part Load Loss Curve | Not Applicable
[5 empty] | Pump + Motor | Pump + Motor Covered by DOE’s Electric Motor Energy Conservation Standards OR Pump + Submersible Motor | PEICL_Calc_Pump+Motor: Tested Pump Efficiency of Bare Pump + Motor Nameplate Efficiency for Actual Motor Paired with Pump + Default Motor Part Load Loss Curve | PEICL_Test_Pump+Motor: Tested Wire-to-Water Performance
INSTRUCTIONS: The calculator contains 5 separate tabs for data input -- 3 for pumps rated using the calculation-based approach and 2 for pumps rated using the physical testing-based approach. The table at right clarifies the applicability of the different test methods to specific configurations of pumps with certain characteristics, paired motors, and/or integral controls. The tabs are labeled using nomenclature that indicate the metric, test method, and pump configuration as follows: | [5 empty] | Pump + Motor Not Covered by DOE’s Electric Motor Energy Conservation Standards (Except Submersible Motors) | Not Applicable
| Metric | Test Method | Pump Configuration | PEIVL | Pump + Motor + Speed Controls | Pump + Motor Covered by DOE’s Electric Motor Energy Conservation Standards + Continuous Control OR Pump + Submersible Motor + Continuous Control | PEIVL_Calc_Pump+Motor+Control: Tested Pump Efficiency of Bare Pump + Motor Nameplate Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed System Curve | PEIVL_Test_Pump+Motor+Control: Tested Wire-to-Water Performance
| PEICL or PEIVL | Calculation-Based ("Calc") or Testing-based ("Test") | Bare pump, pump + motor, or pump + motor + controls
TO USE: 1. Determine which tab is appropriate for the pump configuration (bare pump, pump + motor, or pump + motor + control) and test method (calculation-based or testing-based) being evaluated. 2. Enter relevant pump performance data at tested speed at the specified load points on the appropriate tab/worksheet as described below. Note, if data normalized to nominal speed (i.e., 1800 or 3600 rpm) is entered, the PEI will still calculate correctly. Each row represents one pump model and all the data in that row should correspond to that model.
[6 empty] | Pump + Motor Covered by DOE’s Electric Motor Energy Conservation Standards + Non-Continuous Control OR Pump + Submersible Motor + Non-Continuous Control | Not Applicable
For Pumps Rated Using The Calculation-Based Approach The green-shaded "Calc" tabs accept tested pump shaft input power data (as determined in accordance with HI 40.6) and the full load motor efficiency information, if applicable. Fill out the "Calc" tab for each equipment class as follows: FOR BARE PUMPS, PUMPS SOLD WITH DRIVERS OTHER THAN ELECTRIC MOTORS, AND PUMPS SOLD WITH ONLY SINGLE-PHASE INDUCTION MOTORS: Use the PEICL_Calc_BarePump tab and enter: -Pump make and model information, including tested speed (i.e., the speed at which the pump was tested). -Select the appropriate pump equipment class. This will ensure the correct C-Value is selected. Please refer to the Pump equipment class table to the right. -Pump shaft input power, efficiency, and flow rate at pump BEP. -Pump shaft input power and efficiency at 50%, 75%, and 110% of BEP flow. -Motor information in the green cells is NOT REQUIRED to calculate PER or PEI. FOR PUMPS SOLD WITH MOTORS SUBJECT TO DOE's ENERGY CONSERVATION STANDARDS FOR ELECTRIC MOTORS AT 431.25 AND VERTICAL TURBINE SUBMERSIBLE PUMPS SOLD WITH SUBMERSIBLE MOTORS (WITH OR WITHOUT CONTINUOUS CONTROLS): Use the PEICL_Calc_Pump+Motor or PEIVL_Calc_Pump+Motor+Controls tabs, as appropriate. Enter the same pump information as for a bare pump and, in addition: - Motor size, full load efficiency, and type (enclosed or open) for the motor sold with that pump. | [5 empty] | Pump + Motor Not Covered by DOE’s Electric Motor Energy Conservation Standards (Except Submersible Motors) + Continuous or Non-Continuous Controls | Not Applicable
PUMP EQUIPMENT CLASSES
|  |  |  | Abbr. | ANSI/HI Term | Equipment Category | Definitions
|  |  |  | ESCC | OH7 | End Suction Close-Coupled Pump | an end suction pump in which: (1) the motor shaft also serves as the impeller shaft for the bare pump; (2) the pump requires attachment to a rigid foundation to function as designed and cannot function as designed when supported only by the supply and discharge piping to which it is connected; and (3) the pump does not include a basket strainer. Examples include, but are not limited to, pumps complying with ANSI/HI nomenclature OH7, as described in ANSI/HI 1.1–1.2–2014.
|  |  |  | ESFM | OH0 | End Suction Frame Mounted Pump | an end suction pump where: (1) the bare pump has its own impeller shaft and bearings and does not rely on the motor shaft to serve as the impeller shaft; (2) the pump requires attachment to a rigid foundation to function as designed and cannot function as designed when supported only by the supply and discharge piping to which it is connected; and (3) the pump does not include a basket strainer. Examples include, but are not limited to, pumps complying with ANSI/HI nomenclature OH0 and OH1, as described in ANSI/HI 1.1–1.2–2014.
For Pumps Rated Using The Testing-Based Approach The testing-based approach is applicable to all pumps sold with electric motors, other than single-phase induction motors, including pumps sold with continuous controls and pumps sold with non-continuous controls. The blue-shaded, "Test" tabs accept the input power to the motor as determined by a wire-to-water test of the combined bare pump and motor and should be filled out as follows: FOR PUMPS SOLD WITH ELECTRIC MOTORS AND NO CONTROLS: Use the PEICL_Test_Pump+Motor tab and enter: -Pump make and model information, including tested speed (i.e., the speed at which the pump was tested). -Select the appropriate pump equipment class. This will ensure the correct C-Value is selected. Please refer to the Pump equipment class table to the right. -Pump flow rate, head, and input power to the motor at the specified load points (i.e., 75%, 100%, and 110% of BEP flow). FOR PUMPS SOLD WITH ELECTIC MOTORS AND CONTINUOUS OR NON-CONTINUOUS CONTROLS: Use the PEICL_Test_Pump+Motor+Controls tab and enter: -Pump make and model information, including rated speed (i.e. the speed at which the pump was tested). -Select the appropriate pump equipment class. This will ensure the correct C-Value is selected. Please refer to the Pump equipment class table to the right. -Pump flow rate, head, and input power to the controls at the specified variable load points (i.e., 25%, 50%, 75%, and 100% of BEP flow). -Pump hydraulic power at full speed at 75% and 110% of BEP flow. |  |  |  |  | OH1
|  |  |  | IL | OH3 | In-Line Pump | a single-stage, single axis flow, rotodynamic pump in which: (1) liquid is discharged through a volute in a plane perpendicular to the impeller shaft; and (2) the pump requires attachment to a rigid foundation to function as designed and cannot function as designed when supported only by the supply and discharge piping to which it is connected. Examples include, but are not limited to, pumps complying with ANSI/HI nomenclature OH3, OH4, or OH5, as described in ANSI/HI 1.1–1.2–2014.
OH4 (single suction)
OH5
|  |  |  | RSV | VS8 | Radially Split, Multistage, Vertical, In-line Casing Diffuser Pump | a vertically suspended, multi-stage, single axis flow, rotodynamic pump in which: (1) liquid is discharged in a plane perpendicular to the impeller shaft, (2) each stage (or bowl) consists of an impeller and diffuser, and (3) no external part of such a pump is designed to be submerged in the pumped liquid. Examples include, but are not limited to, pumps complying with ANSI/HI nomenclature VS8, as described in ANSI/HI 2.1–2.2–2008.
|  |  |  | VTS | VS0 | Vertical Turbine Submersible Pump | a single-stage or multistage rotodynamic pump that is designed to be operated with the motor and stage(s) (or bowl(s)) fully submerged in the pumped liquid, and in which: (1) each stage of this pump consists of an impeller and diffuser, and (2) liquid enters and exits each stage of the bare pump in a direction parallel to the impeller shaft. Examples include, but are not limited to, pumps complying with ANSI/HI nomenclature VS0, as described in ANSI/HI 2.1–2.2–2008.
NOTES The Constant Load Pump Energy Index (PEICL) or Variable Load Pump Energy Index (PEIVL) calculated in this tool is based on the standard level (C-Value) proposed in the Pumps Energy Conservation Standard Notice of Proposed Rulemaking. 80 FR 17826 (April 2, 2015). In addition to the PEICL or PEIVL, the calculator will determine whether or not the given pump passes or fails under the proposed standard; above these columns, the total number and percentage of pump models of a given pump configuration is presented. The data entry format has generally been kept consistent with the original PEI Calculator developed during the Pumps Working Group negotiated rulemaking (Docket No. EERE-2013-BT-NOC-0039), although some minor changes have been made, especially on the tabs corresponding to the testing-based approach. Future versions of the calculator may remove some unnecessary cells and be more consistent with the HI 40.6 data outputs. It may be helpful to create separate tabs for each equipment class, depending on the number of pumps in each equipment class that must be certified. DOE invites comments on the format and accuracy of this Draft PEI Calculator. However, the equations within these cells cannot be edited.

## PEICL_Calc_BarePump
CALCULATION-BASED APPROACH TO CALCULATE PEICL FOR BARE PUMPS
| This tab calculates the PEICL for pumps rated as bare pumps and pumps sold with motors rated using the calculation-based approach. This procedure is applicable to pumps sold as bare pumps, pumps sold with drivers other than electric motors, and pumps sold with only single-phase induction motors. | [10 empty] | Key
[12 empty] | Primary Data Collection Fields | [29 empty] | TOTAL PUMPS FAILING |  | 0
[12 empty] | Calculation - DO NOT ENTER DATA | [29 empty] | % PUMPS FAILING |  | 0%
PRIMARY DATA COLLECTION FIELDS | [14 empty] | CALCULATIONS | [26 empty] | RATINGS
PUMP INFORMATION |  |  |  |  | 100% of BEP Q |  |  |  | 75% of BEP Q |  |  | 110% of BEP Q |  |  | PUMP INFORMATION |  |  | BEP Data Corrected to Nominal Speed |  |  |  |  | 75% of BEP Q Corrected to Nominal Speed |  |  |  |  | 110% of BEP Q Corrected to Nominal Speed |  |  |  |  | MOTOR |  |  | ESTABLISHING THE PER_STD FOR THE MINIMALLY COMPLIANT PUMP | [5 empty] | PERCL | PEICL
Brand | Model Name / Number | DOE Pump Type | # of Stages | Tested Speed (rpm) | Q (GPM) | H (ft) | Bare Pump Efficiency (%) | Pump Input Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Motor Pole Config. | Nominal Speed of Rotation (rpm) | Specific Speed, Ns | Q (GPM) | H (ft) | Pump Input Power (hp) | Part Load Loss (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Part Load Loss (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Part Load Loss (hp) | Hydraulic Output Power (hp) | Shaft HP @ 120% of BEP flow for Motor Sizing | Nominal Motor Horsepower (hp) | Motor Efficiency for Use in Calculations (%) | Default Motor Full Load Loss (hp) | Default Motor Part Load Loss @ BEP Q (hp) | Default Motor Part Load Loss @ 75% BEP Q (hp) | Default Motor Part Load Loss @ 110% BEP Q (hp) | PER_STD Pump Efficiency | PER_STD | PER Numerator (hp) | Constant Load PEI | PASS?
EXAMPLE | BARE PUMP | ESCC | 1 | 1750 | 940 | 162.58 | 77.86 | 47.66 | 705 | 178.4 | 40.1585 | 1034 | 157.91 | 50.6536 | 4 | 1800 | 1178.4242 | 966.8571 | 172.003 | 51.863 | 2.8563 | 42.038 | 725.1429 | 188.7399 | 43.6999 | 2.562 | 34.5964 | 1063.5429 | 167.0623 | 55.1206 | 2.9772 | 44.9135 | 58.3836 | 60 | 95 | 3.1579 | 2.9565 | 2.6936 | 3.1279 | 77.0436 | 56.648 | 53.0263 | 0.93607 | PASS
EXAMPLE | BARE PUMP | VTS | 9 | 3450 | 398.8251 | 382.4467 | 75.9997 | 50.6811 | 299.1188 | 407.4395 | 45.7855 | 438.7076 | 350.6985 | 52.3554 | 2 | 3600 | 4139.6539 | 416.1653 | 416.4259 | 57.5833 | 13.3262 | 43.8074 | 312.124 | 443.6392 | 52.0209 | 12.5485 | 35.0026 | 457.7819 | 381.8569 | 59.4856 | 13.6012 | 44.1879 | 61.6183 | 75 | 82.5 | 15.9091 | 14.2195 | 12.7832 | 14.4476 | 68.7865 | 74.6959 | 69.5219 | 0.93073 | PASS
Note on E9: PNNL SW: Note, if enetered data is normalized to nominal speed, enter the noiminal speed here.
Note on AH9: PNNL SW: Based on linear interpolation of 75% and 110% of BEP flow points

## PEICL_Calc_Pump+Motor
CALCULATION-BASED APPROACH TO CALCULATE PEICL FOR PUMPS + MOTORS
| This tab calculates the PEICL for pumps rated as pumps sold with motors rated using the calculation-based approach. This procedure is applicable to pumps sold with motors subject to DOE’s energy conservation standards for electric motors at §431.25 (except for single-phase induction motors) and VTS pumps sold with submersible motors. Pumps sold with any other motors cannot use this calculation-based approach and must apply the testing-based method. | [11 empty] | Key
[13 empty] | Primary Data Collection Fields | [30 empty] | TOTAL PUMPS FAILING |  | 0
[13 empty] | Calculation - DO NOT ENTER DATA | [30 empty] | % PUMPS FAILING |  | 0%
PRIMARY DATA COLLECTION FIELDS | [16 empty] | CALCULATIONS | [26 empty] | RATINGS
PUMP INFORMATION |  |  |  |  | 100% of BEP Q |  |  |  | 75% of BEP Q |  |  | 110% of BEP Q |  |  | MOTOR |  | PUMP INFORMATION |  |  | BEP Data Corrected to Nominal Speed |  |  |  |  | 75% of BEP Q Corrected to Nominal Speed |  |  |  |  | 110% of BEP Q Corrected to Nominal Speed |  |  |  |  | MOTOR | ESTABLISHING THE PER_STD FOR THE MINIMALLY COMPLIANT PUMP | [7 empty] | PERCL | PEICL
Brand | Model Name / Number | DOE Pump Type | # of Stages | Tested Speed (rpm) | Q (GPM) | H (ft) | Bare Pump Efficiency (%) | Pump Input Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Motor Horsepower (hp) | Full Load Efficiency (%) | Motor Pole Config. | Nominal Speed of Rotation (rpm) | Specific Speed, Ns | Q (GPM) | H (ft) | Pump Input Power (hp) | Part Load Loss (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Part Load Loss (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Part Load Loss (hp) | Hydraulic Output Power (hp) | Full Load Losses (hp) | Motor HP for Default Motor Efficiency (hp) | Default Motor Efficiency (%) | Default Motor Full Load Losses (hp) | Default Motor Part Load Loss @ BEP Q (hp) | Default Motor Part Load Loss @ 75% BEP Q (hp) | Default Motor Part Load Loss @ 110% BEP Q (hp) | PER_STD Pump Efficiency | PER_STD | PER Numerator (hp) | Constant Load PEI | PASS?
EXAMPLE | BARE PUMP + 95% EFF. MOTOR | ESCC | 1 | 1750 | 940 | 162.58 | 77.86 | 47.66 | 705 | 178.4 | 40.1585 | 1034 | 157.91 | 50.6536 | 60 | 96.2 | 4 | 1800 | 1178.4242 | 966.8571 | 172.003 | 51.863 | 2.1437 | 42.038 | 725.1429 | 188.7399 | 43.6999 | 1.9228 | 34.5964 | 1063.5429 | 167.0623 | 55.1206 | 2.2345 | 44.9135 | 2.3701 | 60 | 95 | 3.1579 | 2.9565 | 2.6936 | 3.1279 | 77.0436 | 56.648 | 52.3282 | 0.92374 | PASS
EXAMPLE | BARE PUMP + 95% EFF. MOTOR | VTS | 9 | 3450 | 398.8251 | 382.4467 | 75.9997 | 50.6811 | 299.1188 | 407.4395 | 45.7855 | 438.7076 | 350.6985 | 52.3554 | 75 | 87 | 2 | 3600 | 4139.6539 | 416.1653 | 416.4259 | 57.5833 | 9.3875 | 43.8074 | 312.124 | 443.6392 | 52.0209 | 8.8396 | 35.0026 | 457.7819 | 381.8569 | 59.4856 | 9.5812 | 44.1879 | 11.2069 | 75 | 82.5 | 15.9091 | 14.2195 | 12.7832 | 14.4476 | 68.7865 | 74.6959 | 65.6327 | 0.87867 | PASS
Note on E9: PNNL SW: Note, if enetered data is normalized to nominal speed, enter the noiminal speed here.

## PEICL_Test_Pump+Motor
TESTING-BASED APPROACH TO CALCULATE PEICL FOR PUMPS + MOTORS
| This tab calculates the PEICL for pumps rated as pumps sold with motors rated using the testing-based approach. This procedure is applicable to all pumps sold with electric motors, other than single-phase induction motors. | [9 empty] | Key
[11 empty] | Primary Data Collection Fields | [26 empty] | TOTAL PUMPS FAILING |  | 0
[11 empty] | Calculation - DO NOT ENTER DATA | [26 empty] | % PUMPS FAILING |  | 0%
PRIMARY DATA COLLECTION FIELDS | [14 empty] | CALCULATIONS | [22 empty] | RATINGS
PUMP INFORMATION |  |  |  |  | BEP |  |  | 75% of BEP Q |  |  | 110% of BEP Q |  |  | MOTOR | PUMP INFORMATION |  |  | BEP Data Corrected to Nominal Speed |  |  |  | 75% of BEP Q Corrected to Nominal Speed |  |  |  | 110% of BEP Q Corrected to Nominal Speed |  |  |  | ESTABLISHING THE PER_STD FOR THE MINIMALLY COMPLIANT PUMP | [7 empty] | PERCL | PEICL
Brand | Model Name / Number | DOE Pump Type | # of Stages | Tested Speed (rpm) | Q (GPM) | H (ft) | Input Power to the Motor (hp) | Q (GPM) | H (ft) | Input Power to the Motor (hp) | Q (GPM) | H (ft) | Input Power to the Motor (hp) | Motor Horsepower (hp) | Motor Pole Config. | Nominal Speed of Rotation (rpm) | Specific Speed, Ns | Q (GPM) | H (ft) | Input Power to the Motor (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Input Power to the Motor (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Input Power to the Motor (hp) | Hydraulic Output Power (hp) | Motor HP for Default Motor Efficiency (hp) | Default Motor Efficiency (%) | Default Motor Full Load Losses (hp) | Default Motor Part Load Loss @ BEP Q (hp) | Default Motor Part Load Loss @ 75% BEP Q (hp) | Default Motor Part Load Loss @ 110% BEP Q (hp) | PER_STD Pump Efficiency | PER_STD | PER Numerator (hp) | Constant Load PEI | PASS?
EXAMPLE | BARE PUMP + 96% EFF. MOTOR | ESCC | 1 | 1750 | 940 | 162.58 | 50.43 | 705 | 162.58 | 43.85 | 1034 | 162.58 | 52.49 | 60 | 4 | 1800 | 1178.4242 | 966.8571 | 172.003 | 54.8772 | 42.038 | 725.1429 | 172.003 | 47.717 | 31.5285 | 1063.5429 | 172.003 | 57.1189 | 46.2418 | 60 | 95 | 3.1579 | 2.9565 | 2.5452 | 3.1921 | 77.0436 | 55.8017 | 53.2377 | 0.95405 | PASS
EXAMPLE | BARE PUMP + 87% EFF. MOTOR | VTS | 9 | 3450 | 398.8251 | 382.4467 | 57.25 | 299.1188 | 382.4467 | 51.97 | 438.7076 | 382.4467 | 58.4 | 75 | 2 | 3600 | 4139.6539 | 416.1653 | 416.4259 | 65.0468 | 43.8074 | 312.124 | 416.4259 | 59.0477 | 32.8555 | 457.7819 | 416.4259 | 66.3534 | 48.1881 | 75 | 82.5 | 15.9091 | 14.2195 | 12.336 | 15.3316 | 68.7865 | 75.7108 | 63.4826 | 0.83849 | PASS
Note on E9: PNNL SW: Note, if enetered data is normalized to nominal speed, enter the noiminal speed here.

## PEIVL_Calc_Pump+Motor+Control
CALCULATION-BASED APPROACH TO CALCULATE PEIVL FOR PUMPS + MOTORS + CONTROLS
| This tab calculates the PEIVL for pumps sold with motors and controls rated using the calculation-based approach. This procedure is applicable to pumps sold with motors subject to DOE’s energy conservation standards for electric motors at §431.25 (except for single-phase induction motors) and continuous controls and pumps sold with submersible motors and continuous controls. Pumps sold with any other motors and/or non-continuous controls cannot use this calculation-based approach and must apply the testing-based method. | [11 empty] | Key
[13 empty] | Primary Data Collection Fields | [31 empty] | TOTAL PUMPS FAILING |  | 0
[13 empty] | Calculation - DO NOT ENTER DATA | [31 empty] | % PUMPS FAILING |  | 0%
PRIMARY DATA COLLECTION FIELDS | [16 empty] | CALCULATIONS | [27 empty] | RATINGS
PUMP INFORMATION |  |  |  |  | 100% of BEP Q |  |  |  | 75% of BEP Q |  |  | 110% of BEP Q |  |  | MOTOR |  | PUMP INFORMATION |  |  | BEP Data Corrected to Nominal Speed |  |  |  | 75% of BEP Q Corrected to Nominal Speed |  |  | 110% of BEP Q Corrected to Nominal Speed |  |  | CONTROLS | [6 empty] | ESTABLISHING THE PER_STD FOR THE MINIMALLY COMPLIANT PUMP | [7 empty] | PERVL | PEIVL
Brand | Model Name / Number | DOE Pump Type | # of Stages | Tested Speed (rpm) | Q (GPM) | H (ft) | Bare Pump Efficiency (%) | Pump Input Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Q (GPM) | H (ft) | Pump Input Power (hp) | Motor Horsepower (hp) | Full Load Efficiency (%) | Motor Pole Config. | Nominal Speed of Rotation (rpm) | Specific Speed, Ns | Q (GPM) | H (ft) | Pump Input Power (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Hydraulic Output Power (hp) | Motor+ Control Losses @ BEP (hp) | Pump Input Power @ 25% BEP (hp) | Motor+ Control Losses @ 25% BEP (hp) | Pump Input Power @ 50% BEP (hp) | Motor+ Control Losses @ 50% BEP (hp) | Pump Input Power @ 75% BEP (hp) | Motor+ Control Losses @ 75% BEP (hp) | Motor HP for Default Motor Efficiency (hp) | Default Motor Efficiency (%) | Default Motor Full Load Losses (hp) | Default Motor Part Load Loss @ BEP Q (hp) | Default Motor Part Load Loss @ 75% BEP Q (hp) | Default Motor Part Load Loss @ 110% BEP Q (hp) | PER_STD Pump Efficiency | PER_STD | PER Numerator (hp) | Variable Load PEI | PASS?
EXAMPLE | BARE PUMP + 95% EFF. MOTOR + CONT. CONTROL | ESCC | 1 | 1750 | 940 | 162.58 | 77.86 | 47.66 | 705 | 178.4 | 40.1585 | 1034 | 157.91 | 50.6536 | 60 | 96.2 | 4 | 1800 | 1178.4242 | 966.8571 | 172.003 | 51.863 | 42.038 | 725.1429 | 188.7399 | 34.5964 | 1063.5429 | 167.0623 | 44.9135 | 3.3455 | 3.2414 | 3.1985 | 10.3726 | 3.2933 | 25.2832 | 3.4102 | 60 | 95 | 3.1579 | 2.9565 | 2.6936 | 3.1279 | 77.0436 | 56.648 | 26.0019 | 0.45901 | PASS
EXAMPLE | BARE PUMP + 95% EFF. MOTOR + CONT. CONTROL | VTS | 9 | 3450 | 398.8251 | 382.4467 | 75.9997 | 50.6811 | 299.1188 | 407.4395 | 45.7855 | 438.7076 | 350.6985 | 52.3554 | 75 | 87 | 2 | 3600 | 4139.6539 | 416.1653 | 416.4259 | 57.5833 | 43.8074 | 312.124 | 443.6392 | 35.0026 | 457.7819 | 381.8569 | 44.1879 | 3.3894 | 3.599 | 3.193 | 11.5167 | 3.2796 | 28.0719 | 3.3965 | 75 | 82.5 | 15.9091 | 14.2195 | 12.7832 | 14.4476 | 68.7865 | 74.6959 | 28.5073 | 0.38165 | PASS
Note on E9: PNNL SW: Note, if enetered data is normalized to nominal speed, enter the noiminal speed here.

## PEIVL_Test_Pump+Motor+Control
TESTING-BASED APPROACH TO CALCULATE PEIVL FOR PUMPS + MOTORS + CONTROLS
| This tab calculates the PEIVL for pumps rated as pumps sold with motors and controls rated using the testing-based approach. This procedure is applicable to all pumps sold with electric motors, other than single-phase induction motors, with continuous or non-continuous controls. | [12 empty] | Key
[14 empty] | Primary Data Collection Fields | [31 empty] | TOTAL PUMPS FAILING |  | 0
[14 empty] | Calculation - DO NOT ENTER DATA | [31 empty] | % PUMPS FAILING |  | 0%
PRIMARY DATA COLLECTION FIELDS | [19 empty] | CALCULATIONS | [25 empty] | RATINGS
PUMP INFORMATION |  |  |  |  | 100% of BEP Q at Full Speed |  |  | 75% of BEP Q at Reduced Speed |  |  | 50% of BEP Q at Reduced Speed |  |  | 25% of BEP Q at Reduced Speed |  |  | 75% of BEP Q at Full Speed | 110% of BEP Q at Full Speed | MOTOR | PUMP INFORMATION |  |  | BEP Data Corrected to Nominal Full Speed |  |  |  | 75% of BEP Q Corrected to Reference System Curve |  |  | 50% of BEP Q Corrected to Reference System Curve |  |  | 25% of BEP Q Corrected to Reference System Curve |  |  | 75 % of BEP Q Corrected to Nominal Full Speed | 110% of BEP Q Corrected to Nominal Full Speed | ESTABLISHING THE PER_STD FOR THE MINIMALLY COMPLIANT PUMP | [7 empty] | PERVL | PEIVL
Brand | Model Name / Number | DOE Pump Type | # of Stages | Tested Full Speed (rpm) | Q (GPM) | H (ft) | Input Power to the Control (hp) | Q (GPM) | H (ft) | Input Power to the Control (hp) | Q (GPM) | H (ft) | Input Power to the Control (hp) | Q (GPM) | H (ft) | Input Power to the Control (hp) | Hydraulic Output Power (hp) @ Full Speed | Hydraulic Output Power (hp) @ Full Speed | Motor Horsepower (hp) | Motor Pole Config. | Nominal Full Speed of Rotation (rpm) | Specific Speed, Ns | Q (GPM) | H (ft) | Input Power to the Control (hp) | Hydraulic Output Power (hp) | Q (GPM) | H (ft) | Input Power to the Control (hp) | Q (GPM) | H (ft) | Input Power to the Control (hp) | Q (GPM) | H (ft) | Input Power to the Control (hp) | Hydraulic Output Power (hp) @ Nominal Speed | Hydraulic Output Power (hp) @ Nominal Speed | Motor HP for Default Motor Efficiency (hp) | Default Motor Efficiency (%) | Default Motor Full Load Losses (hp) | Default Motor Part Load Loss @ BEP Q (hp) | Default Motor Part Load Loss @ 75% BEP Q (hp) | Default Motor Part Load Loss @ 110% BEP Q (hp) | PER_STD Pump Efficiency | PER_STD | PER Numerator (hp) | Variable Load PEI | PASS?
EXAMPLE | BARE PUMP + 96% EFF. MOTOR | ESCC | 1 | 1750 | 940 | 162.58 | 52.34 | 705 | 110.82 | 27.83 | 500 | 65.2 | 11.5 | 238 | 40.25 | 3.45 | 33.1945 | 42.757 | 60 | 4 | 1800 | 1178.4242 | 966.8571 | 172.003 | 56.9557 | 42.038 | 725.1429 | 111.802 | 28.8788 | 483.4286 | 68.8012 | 11.733 | 241.7143 | 43.0008 | 3.7433 | 36.1218 | 46.5276 | 60 | 95 | 3.1579 | 2.9565 | 2.7696 | 3.2058 | 77.0436 | 58.1052 | 25.3277 | 0.43589 | PASS
EXAMPLE | BARE PUMP + 87% EFF. MOTOR | VTS | 9 | 3450 | 398.8251 | 382.4467 | 57.25 | 299.1188 | 248.59 | 27.77 | 212 | 153.02 | 11.65 | 98 | 95.22 | 3.55 | 34.9673 | 44.1432 | 75 | 2 | 3600 | 4139.6539 | 416.1653 | 416.4259 | 65.0468 | 43.8074 | 312.124 | 270.6768 | 31.552 | 208.0827 | 166.5704 | 12.4473 | 104.0413 | 104.1065 | 4.1206 | 39.7294 | 50.155 | 75 | 82.5 | 15.9091 | 14.2195 | 13.8211 | 15.7645 | 68.7865 | 80.8353 | 28.2917 | 0.34999 | PASS
Note on E9: PNNL SW: Note, if enetered data is normalized to nominal speed, enter the noiminal full speed here.

## Assumptions
ASSUMPTIONS
LOAD POINTS & WEIGHTS |  |  |  |  | DEFAULT MOTOR EFFICIENCY | [6 empty] | MOTOR LOSSES |  |  | CONTROLS |  |  |  | CALCULATION OF PER_STD
§431.25 Electric Motors Energy Conservation Standards and Effective Dates.
| Bare Pump & Bare Pump+Motor |  | Bare Pump+Motor+ Controls |  | (h) Starting on June 1, 2016, each NEMA Design A motor, NEMA Design B motor, and IEC Design N motor that is an electric motor meeting the criteria in paragraph (g) of this section and with a power rating from 1 horsepower through 500 horsepower, but excluding fire pump electric motors, manufactured (alone or as a component of another piece of equipment) shall have a nominal full-load efficiency of not less than the following: | [6 empty] | Motor Loss Equation Coefficients |  |  | Motor and Continuous Control Part Load Loss Factor Equation Coefficients |  |  |  | % BEP Flow | MEI Weighting Factors |  | Pump Efficiency Coefficients
% BEP flow | Load Points | Equal Weights | Load Points | Equal Weights | [7 empty] | a | -0.4508 |  | Motor horsepower (hp) | a | b | c | 25 | 0 |  | a | b | c | d | e | f
25 | 0 | 0 | 1 | 0.25 | Nominal Full-Load Efficiencies of NEMA Design A, NEMA Design B and IEC Design N Motors (Excluding Fire Pump Electric Motors) at 60 Hz | [6 empty] | b | 1.2399 | ODP | ≤5 | -0.4658 | 1.4965 | 0.5303 | 75 | 0.947 |  | -0.85 | -0.38 | -11.48 | 17.8 | 179.8 | 555.6
50 | 0 | 0 | 1 | 0.25 |  |  |  | Nominal Full-Load Efficiency (%) |  |  |  | c | -0.4301 | TEFC | >5 and ≤20 | -1.3198 | 2.9551 | 0.1052 | 100 | 1
75 | 1 | 0.33333 | 1 | 0.25 |  | Minimum Efficiency (%) |  | Enclosed Motors |  | Open Motors |  | d | 0.641 |  | >20 and ≤50 | -1.5122 | 3.0777 | 0.1847 | 110 | 0.985
100 | 1 | 0.33333 | 1 | 0.25 | Motor horsepower | Number of Poles |  | Number of Poles |  | Number of Poles |  |  |  |  | >50 | -0.8914 | 2.8846 | 0.2625
110 | 1 | 0.33333 | 0 | 0 |  | 4 | 2 | 4 | 2 | 4 | 2 | Motor Loss Equations | [6 empty] | Category | Nominal Speed | C-value
[5 empty] | 250 | 95.8 | 95 | 96.2 | 95.8 | 95.8 | 95 |  |  |  | Motor and Continuous Control Part Load Loss Factor Equation |  |  |  | ESCC | 1800 | 128.47
[5 empty] | 200 | 95.8 | 95 | 96.2 | 95.4 | 95.8 | 95 | [7 empty] | ESFM | 1800 | 128.85
1 | Specific gravity (SG) |  |  |  | 150 | 95.8 | 94.1 | 95.8 | 95 | 95.8 | 94.1 | [7 empty] | IL | 1800 | 129.3
[5 empty] | 125 | 95.4 | 94.1 | 95.4 | 95 | 95.4 | 94.1 | [7 empty] | RSV | 1800 | 129.63
[5 empty] | 100 | 95.4 | 93.6 | 95.4 | 94.1 | 95.4 | 93.6 | [7 empty] | VTS | 1800 | 134.13
[5 empty] | 75 | 95 | 93.6 | 95.4 | 93.6 | 95 | 93.6 | [7 empty] | ESCC | 3600 | 130.42
[5 empty] | 60 | 95 | 93.6 | 95 | 93.6 | 95 | 93.6 |  |  |  | Reference System Curve Equation |  |  |  | ESFM | 3600 | 130.99
[5 empty] | 50 | 94.5 | 93 | 94.5 | 93 | 94.5 | 93 | [7 empty] | IL | 3600 | 133.84
[5 empty] | 40 | 94.1 | 92.4 | 94.1 | 92.4 | 94.1 | 92.4 | [7 empty] | RSV | 3600 | 133.2
[5 empty] | 30 | 93.6 | 91.7 | 93.6 | 91.7 | 94.1 | 91.7 | [7 empty] | VTS | 3600 | 134.13
[5 empty] | 25 | 93.6 | 91.7 | 93.6 | 91.7 | 93.6 | 91.7
[5 empty] | 20 | 93 | 91 | 93 | 91 | 93 | 91
[5 empty] | 15 | 92.4 | 90.2 | 92.4 | 91 | 93 | 90.2
[5 empty] | 10 | 91.7 | 89.5 | 91.7 | 90.2 | 91.7 | 89.5
[5 empty] | 7.5 | 91 | 88.5 | 91.7 | 89.5 | 91 | 88.5
[5 empty] | 5 | 89.5 | 86.5 | 89.5 | 88.5 | 89.5 | 86.5
[5 empty] | 3 | 89.5 | 85.5 | 89.5 | 86.5 | 89.5 | 85.5
[5 empty] | 2 | 86.5 | 85.5 | 86.5 | 85.5 | 86.5 | 85.5
[5 empty] | 1.5 | 86.5 | 84 | 86.5 | 84 | 86.5 | 84
[5 empty] | 1 | 85.5 | 77 | 85.5 | 77 | 85.5 | 77
Default Submersible Motor Full Load Nominal Efficiency
[5 empty] | Motor horsepower | Number of Poles
[6 empty] | 4 | 2
[5 empty] | 250 | 87.5 | 86.5
[5 empty] | 200 | 87.5 | 85.5
[5 empty] | 150 | 86.5 | 84
[5 empty] | 125 | 85.5 | 84
[5 empty] | 100 | 85.5 | 81.5
[5 empty] | 75 | 87.5 | 82.5
[5 empty] | 60 | 86.5 | 82.5
[5 empty] | 50 | 85.5 | 81.5
[5 empty] | 40 | 84 | 80
[5 empty] | 30 | 82.5 | 78.5
[5 empty] | 25 | 78.5 | 74
[5 empty] | 20 | 77 | 72
[5 empty] | 15 | 75.5 | 72
[5 empty] | 10 | 74 | 70
[5 empty] | 7.5 | 74 | 68
[5 empty] | 5 | 75.5 | 74
[5 empty] | 3 | 75.5 | 70
[5 empty] | 2 | 70 | 68
[5 empty] | 1.5 | 70 | 66
[5 empty] | 1 | 68 | 55
𝑃𝑎𝑟𝑡 𝑙𝑜𝑎𝑑 𝑙𝑜𝑠𝑠 𝑓𝑎𝑐𝑡𝑜𝑟 (𝑦_𝑖 )=𝑎∗〖𝑥_𝑖〗^3+𝑏∗〖𝑥_𝑖〗^2+𝑐∗𝑥_𝑖+𝑑
𝑚𝑜𝑡𝑜𝑟 𝑙𝑜𝑎𝑑 𝑓𝑎𝑐𝑡𝑖𝑜𝑛 (𝑥𝑖)= 𝑃_𝑖/𝑀𝑜𝑡𝑜𝑟𝐻𝑃
𝑃𝑎𝑟𝑡 𝑙𝑜𝑎𝑑 𝑙𝑜𝑠𝑠 (𝐿_𝑖)=𝐿_(𝑓𝑢𝑙𝑙, 𝑑𝑒𝑓𝑎𝑢𝑙𝑡)∗𝑦𝑖
Note, these C-values are based on preliminary data that DOE had available at the time of the calculator construction. These numbers can be manually updated and changed to evaluate pass/fail rates with different C-values and associated standard levels.
To change the C-values just enter a new value in the tan-shaded cells and all the equipment type-specific sheets will update the minimally compliant pump and associated pass fail rates for the new C-values.
𝜂_(𝑝𝑢𝑚𝑝,𝑆𝑇𝐷)=𝑎∗〖ln⁡(𝑄_(100%) )〗^2+𝑏∗ln⁡(𝑁𝑠)∗ln⁡(𝑄_(100%) )+𝑐∗〖ln⁡(𝑁𝑠)〗^2+𝑑∗ln⁡(𝑄_(100%) )+𝑒∗ln⁡(𝑁𝑠)−(𝐶+𝑓)
𝑃_𝑖=(0.8∗〖𝑄_𝑖〗^3/〖𝑄_(100%)〗^3 +0.2∗𝑄_𝑖/𝑄_(100%) ) ∗𝑃_(100%)
𝑧_𝑖=(𝑎∗(𝑃_𝑖/𝑀𝑜𝑡𝑜𝑟𝐻𝑃)^2+𝑏∗(𝑃_𝑖/𝑀𝑜𝑡𝑜𝑟𝐻𝑃)+𝑐) ∗𝑃_(100%)
Note on I11: Jason Tuenge (PNNL): HP values are listed in descending order, as required by the MATCH function when the 3rd argument has a value of -1 (see BarePump sheet).
Note on I36: Jason Tuenge (PNNL): HP values are listed in descending order, as required by the MATCH function when the 3rd argument has a value of -1 (see BarePump sheet).