## Metadata (System Properties)
Metadata | Unit | Value | Additional Requests for Awardee
System Specifications
Rated power | kVA |  | Provide energy at which Rated Power is measured.
Rated energy | kWh |  | Provide power at which Rated Energy is measured.
Rated charge power | kVA |  | If different from rated power
Maximum or peak discharge power | kVA |  | Provide duration at maximum discharge power
Maximum or peak charge power | kVA |  | Provide duration at maximum charge power
Minimum operating temperature | C
Maximum operating temperature | C
Operating temperature window (lower to upper bound) | C |  | Temperature range for which the system specifications (power, energy, etc.) are met
Maximum state of charge (SOC) (operating limit) | percent
Minimum SOC (operating limit) | percent
Power Conversion System (PCS) Specifications
Power conversion system rated power | kVA
# of AC/DC bidirectional inverters
AC/DC bidirectional inverter rated power | kVA |  | For each bi-directional inverter
AC/DC bidirectional inverter rated voltage (in/out) | V_ac / V_dc |  | For each bi-directional inverter
AC/DC bidirectional inverter rated current | A_ac / A_dc |  | For each bi-directional inverter
DC/DC bidirectional converter rated power | kW |  | For each converter
DC/DC bidirectional converter rated voltage | V_high / V_low |  | For each converter
DC/DC bidirectional converter rated current | A_high / A_low |  | For each converter
# of DC/DC converters per AC/DC inverter | --
Bank Specifications
Rated power | kW
Rated energy | kWh
Rated charge power | kW
Maximum or peak discharge power | kW
Maximum or peak charge power | kW
Total # of strings per bank |  |  | One bank connected to each AC/DC bidirectional inverter
How are Strings connected? “x” Parallel “y” Series |  |  | Most probably in parallel directly to each other or to dc-dc converter.
String Specifications
Total # stacks per string with xPyS configuration | x, y |  | How are stacks connected within each string, directly to each other or via a dc-dc converter?
Total # of stacks per set of electrolyte tanks
Stack Specifications
Total # cells in stack
Rated charge power | kW
Rated discharge power | kW
Max voltage | V
Min voltage | V
Max current charge | A
Max current discharge | A
Cell Specifications
Flow pattern |  |  | e.g., flow through, interdigitated, etc. (provide associated dimensions if possible)
Negative electrode material
Negative electrode size (l x w x thickness) | cm
Negative electrode pre-treatments
Negative electrode compression ratio
Negative electrode conductivity | S/cm
Negative electrode area density | g/cm2
Negative electrode volumetric density | g/cm3
Positive electrode material
Positive electrode size (l x w x thickness)
Positive electrode pre-treatments
Positive electrode compression ratio
Positive electrode conductivity | S/cm
Positive electrode area density | g/cm2
Positive electrode volumetric density | g/cm3
Membrane material
Membrane size (l x w x thickness) | cm
Membrane pre-treatments
Membrane water uptake | percent
Membrane swelling ratio | percent
Membrane area resistance | Ohm cm2
Membrane proton conductivity | mS/cm
Membrane permeability | cm2
Membrane porosity | percent
Membrane ion selectivity | S min/cm3
Electrolyte Specifications
Negative electrolyte active species
Negative electrolyte active species initial concentration | M
Negative electrolyte supporting species
Negative electrolyte supporting species initial concentration | M
Negative electrolyte initial volume in tank | L
Negative electrolyte viscosity | Pa s |  | Varies with SOC and temperature. Provide values at multiple SOCs and temperatures.
Negative electrolyte density | g/cc |  | Varies with SOC and temperature. Provide values at multiple SOCs and temperatures.
Negative electrolyte specific heat capacity | J/(kg-C)
Negative electrolyte conductivity | S/cm |  | Varies with SOC and temperature. Provide values at multiple SOCs and temperatures.
Negative electrolyte precipitation temperature | C |  | Specify if precipitation occurs at less than or greater than this value.
Negative electrolyte pH
Positive electrolyte active species
Positive electrolyte active species initial concentration | M
Positive electrolyte supporting species
Positive electrolyte supporting species initial concentration | M
Positive electrolyte initial volume in tank | L
Positive electrolyte viscosity | Pa s |  | Varies with SOC and temperature. Provide values at multiple SOCs and temperatures.
Positive electrolyte density | g/cc |  | Varies with SOC and temperature. Provide values at multiple SOCs and temperatures.
Positive electrolyte specific heat capacity | J/(kg-C)
Positive electrolyte conductivity | S/cm |  | Varies with SOC and temperature. Provide values at multiple SOCs and temperatures.
Positive electrolyte precipitation temperature | C |  | Specify if precipitation occurs at less than or greater than this value.
Positive electrolyte pH
Other Specifications
Positive tank internal volume | L
Negative tank internal volume | L
List of wetted materials external to stack and their composition |  |  | e.g., tubing material composition
Component Manufacturers + Product IDs
Electrodes
Membrane
Electrolyte
Stack
Battery management system
Thermal management system
Power conversion system or inverter
Transformer
HVAC
Pumps
Tanks

## Streaming Data
Data Point | Units | Sample Rate Minimum (sample/s) | Values | Additional Requests for Awardee
System Level
Time |  | 1 | value | ISO 8601 format
Power at Point of Common Coupling | kW | 1 | value | see meter layout diagram
Reactive Power at Point of Common Coupling | kVAR | 1 | value | see meter layout diagram
Power Factor at Point of Common Coupling |  | 1 | value | see meter layout diagram
AC RMS Voltage (A/B/C) | VRMS | 1 | value | distinct output for A/B/C
AC RMS Current (A/B/C) | IRMS | 1 | value | distinct output for A/B/C
Power at Transformer | kW | 1 | value | see meter layout diagram
Reactive Power at Transformer | kVAR | 1 | value | see meter layout diagram
Power Factor at Transformer |  | 1 | value | see meter layout diagram
AC RMS Voltage (A/B/C) at Transformer | VRMS | 1 | value | distinct output for A/B/C
AC RMS Current (A/B/C) at Transformer | IRMS | 1 | value | distinct output for A/B/C
Power Requested (command) | kW | 1 | value | At what meter does BESS attempt to provide the requested power
Reactive Power Requested (command) | kVAR | 1 | value
System State | Binary | 1 | on/off
SOC |  | 1 | value | 0.1% precision
State of Health (SOH) |  | 1 per day | value | 1% precision (Specify what this is this based on. The electrolyte?)
Total AC Discharge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation? If at meter, get at each meter.
Total AC Charge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation? If at meter, get at each meter.
Contactor Status | Binary | 1 | 1 = closed, 0 = open | For every contactor
Breaker Status | Binary | 1 | 1 = closed, 0 = open | For every breaker
System Frequency | Hz | 1 | value
Power Conversion System
Power at PCS | kW | 1 | value | see meter layout diagram
Reactive Power at PCS | kVAR | 1 | value | see meter layout diagram
Power Factor at PCS |  | 1 | value | see meter layout diagram
AC RMS Voltage (A/B/C) at PCS | VRMS | 1 | value | distinct output for A/B/C
AC RMS Current (A/B/C) at PCS | IRMS | 1 | value | distinct output for A/B/C
THD | dBm | 1 | value | Usually measured at converter level
Contactor Status | Binary | 1 | 1 = closed, 0 = open | For every contactor
Breaker Status | Binary | 1 | 1 = closed, 0 = open | For every breaker
Total DC Discharge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation?
Total DC Charge Energy | kWh | 1 per 10 min | value | Recorded at meter or calculation?
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | I | 1 | value
Device Temperature | C | 1 | value | 0.1C precision
Tank and Pumps
Negative Electrolyte Pump Power | kW | 1 | value
Negative Electrolyte Pump Flow Rate | m^3/s | 1 | value
Negative Electrolyte Tank Headspace Pressure | psi | 1 per 10 s | value | If monitored.
Negative Electrolyte Tank Level | m | 1 per 10 s | value | If monitored.
Negative Electrolyte Stack Inlet or Pump Outlet Pressure | psi | 1 | value | Per hydraulic parallel connection
Negative Electrolyte Tank Temperature | C | 1 | value | 0.1C precision; At all locations where measured
Negative Electrolyte Return Manifold Temperature
Negative Electrolyte Tank SOC
Positive Electrolyte Pump Power | kW | 1 | value
Positive Electrolyte Pump Flow Rate | m^3/s | 1 | value
Positive Electrolyte Tank Headspace Pressure | psi | 1 per 10 s | value | If monitored.
Positive Electrolyte Tank Level | m | 1 per 10 s | value | If monitored.
Positive Electrolyte Stack Inlet or Pump Outlet Pressure | psi | 1 | value | Per hydraulic parallel connection
Positive Electrolyte Return Manifold Temperature | C | 1 | value | 0.1C precision; At all locations where measured
Positive Electrolyte Tank SOC |  | 1 | value | 0.1% precision; Based on positive/negative electrolyte tanks
Bank Level
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | A | 1 | value
SOC |  | 1 | value
SOH |  | 1 per day | value | 1% precision
String Level
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | A | 1 | value | Add data points if charge/discharge current limits are dynamic
SOC |  | 1 | value | If multiple tanks in a string
SOH |  | 1 per day | value | 1% precision
Stack Level
DC Power | kW | 1 | value
DC Voltage | V | 1 | value
DC Current | A | 1 | value
Cell Level
DC Voltage | V | 1 | value | if measured
Other Auxiliary Systems
Auxiliary System Power | kW | 1 | value | For every auxiliary meter
Auxiliary System Reactive Power | kVAR | 1 | value | For every auxiliary meter
HVAC/Thermal Control Power | kW | 1 | value
External Conditions
Outside Temperature | C | 1 per min | value | 0.1C precision
Outside Dew Point Or Humidity % |  | 1 per min | value
Precipitation | mm | 1 per min | value

## O&M - Written Log
| Event Information |  |  | Component Information |  | Event Description |  | Resolution
Event # | Planned vs Unplanned | % System Rated Power Unavailable | Event Category (see options) | Component (see options) | Additional Component Details? (e.g., associated streaming label in system diagram) | Event Start Time (ISO 8601 format) | Short Event Description | Root Cause | Solution | Event Resolution Time (ISO 8601 format) | Event Duration (x days, y hours, z minutes) | Related to Previous Event # | Enter outage duration if less than event duration | Additional Details (provide version ID# if standard firmware update)
1 | Unplanned |  | Hardware | Tank | Tank 2 | 2020-02-02 | Loss of containment |  |  | 2020-03-13 11:01 | 40 days, 11 hours, 1 minutes | none | 3 days
2 | Unplanned |  | Firmware / Software | Database issue |  | 2020-07-17 | Database software crash | firmware issue / update firmware with vendors help. |  | 2020-07-20 00:01 | 3 days, 0 hours, 1 minutes | 1
3 | Planned |  | Firmware / Software | Update | [9 empty] | BMS upgraded to Version 11.2

## O&M Event Category Options
Event Category Options: Hardware, Firmware/Software, Network, External
Hardware | Notes
Stack
Inverter | Bi or mono-directional AC-DC converter
Converter | Bi or mono-directional DC-DC converter
Tank
Pump
Plumbing
Sensors
Thermal management | Anything related to HVAC
Electrical conductor | Only conductors used for moving energy in/out of storage system (excludes comms or auxiliary conductors)
Energy management system | High level system controller typically used to orchestrate the operation of many storage devices and inverters
Transformer | Generic transformer. Details about the transformer can be provided in the blue table
Meter | Any device in the system that is measuring and externally reporting data
Battery management system | Controller that manages the operation of a single battery / storage system
Data acquisition (DAQ) | A device which collects and communicates data from many different metering devices, but does not necessarily measure data directly
Database | A repository for historical system data
Network equipment
Uninterruptible power supply
Fire detection or suppression systems
Firmware/Software | Notes
Update
Error | Bug in firmware requiring update
Database issue
Network | Notes
Data transfer error
Device failure
Internet service provider error
Local area network error
VPN error
Firewall error
Physical disconnection
Cloud service outages
External | Notes
Loss of grid power
Loss of auxiliary power
Weather/natural causes | Earthquake, thunderstorm, pandemic, rodents, corrosion, erosion
Operator error
External tampering | Vandalism
Site access issues