Pressurized Systems and Cryogens

Performance Objective:

Assure personnel health and safety through regularly scheduled inspections and maintenance on pressure vessels and equipment, compressed gases and gas cylinders, vacuum equipment and systems, hydraulics, and cryogenic materials and systems.

Performance Criteria:

- BN inspects, operates and safely stores unmodified compressed-gas or liquid cylinders approved by the Department of Transportation (DOT) and the appropriate regulators.

- BN inspects, operates and maintains refrigeration systems that comply with the American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Codes, and applicable Air Conditioning and Refrigeration Institute (ARI) standards.

- BN inspects, operates and maintains pressure systems that operate at an MAWP that is less than one atmospheric pressure. (Design guidance for these systems is given in the ASME Unified Pressure Vessel Code and the Mechanical Engineering Design Safety Standards M-012, Section 3.3, "Vacuum Systems.") However, the requirements do apply to vacuum systems that may be pressurized (i.e., for purging, or back-filling).

- BN inspects, operates and maintains ASME coded air-pressure tanks, liquefied petroleum gas tanks, anhydrous-ammonia tanks, and fired steam boilers that periodically in accordance with Unfired Pressure Vessel Safety Orders or Boiler and Fired Pressure Vessel Safety Orders.

- BN ensures the safety of personnel through a definitive training program on pressurized systems.

## REFERENCES:

29 CFR 1910.101, Compressed Gases General Requirements.

29 CFR 1910.132, Subpart I, Personal Protective Equipment.

29 CFR 1910.146, Permit Required Confined Spaces.

29 CFR 1910, Subpart J, General Environmental Controls.

29 CFR 1910, Subpart M, Compressed Gas and Compressed Air Equipment.

AGA Z 21.13, Gas Fired Low Pressure Steam and Hot Water Boilers (American Gas Association, 1991).

ANSI/B 31.1, Power Piping, ASME Code for Pressure Piping, 1995.

ASME Boiler & Pressure Vessel Codes, Section I, "Boilers," 1998.

ASME Boiler & Pressure Vessel Codes, Section VIII, "Div. 1 & 2 Rules for Construction of Pressure Vessels," 1998.

Compressed Gas Association (CGA) Pamphlet P-1, Safe Handling of Compressed Gases in Containers, 1995.

Compressed Gas Association (CGA), Pamphlet P-12, Safe Handling of Cryogenic Liquids, 1993.

Compressed Gas Association (CGA) Pamphlet S-1.1, Pressure Relief Device Standards, Part 1 Cylinders for Compressed Gases, 1991.

DOE M 440.1-1, DOE Explosives Safety Manual.

DOE Order 440.1A, Attachment 2, Section 20, Pressure Safety

BN Procedure, CD-2110.002, Standard Pressure Systems, 12/7/00

BN Procedure, CD-2110.003, Nonstandard Pressure Systems, 10/30/01

BN Procedure, OP-2110.116, Standard Pressure Safety Inspection, 1/21/03

BN Procedure,  OP-2110.131, Pressure testing of Piping, Tubing, and Components, 2/24/03

APPROACH:

Document Review:

- Selected maintenance work packages

- Selected test documents and/or experiment plans,

- Selected occurrence report

- Selected training plans that has been approved and released to the field for work.

- Selected Hot Work Permits

Observations:

- Selected work, testing, or training being performed including crew briefings, testing setup and/or conduct of testing, maintenance activities, trouble-shooting activities, research and development activities, or training activities (classroom or on-the-job).

Interviews:

- Selected Management personnel

- Selected maintenance, support and/or operations staff

- Selected Trainers/Training Coordinators

Pressurized Systems and Cryogens Assessment Plan

NNSA/NV Facility Representative

Guide for planning the review approach

| No. | Description | YES | NO | N/A | COMMENTS |
| --- | --- | --- | --- | --- | --- |
| High Pressure Boiler Operations |  |  |  |  |  |
| 1. | Are operations being performed on a boiler/air tank which is not constructed the American Society of Mechanical Engineers (A.S.M.E) Code? |  |  |  |  |
| 2. | Are all boilers equipped with a safety valve, having sufficient relief capacity, and set at or below the maximum allowable working pressure? |  |  |  |  |
| 3. | Do personnel bypass the pressure controls, low water cutout, or any other limit switch or control? |  |  |  |  |
| 4. | Do personnel restrict the design function of safety valves; i.e., such as reducing or plugging the outlet, painting, or removing it? |  |  |  |  |
| 5. | Are unqualified personnel permitted to operate a boiler?. |  |  |  |  |
| 6. | Are operating boilers left unattended for long periods of time? |  |  |  |  |
| 7. | Are boilers allowed to operate without an adequate source of combustion air? |  |  |  |  |
| 8. | Are boilers operating without a valid certificate of inspection? |  |  |  |  |
| 9. | Have all boilers been internally inspected annually, and do they have an inspection card as required by State law? |  |  |  |  |
| 10. | Have all newly installed boilers been reported to the State Office of Boiler and Pressure Vessel Safety? |  |  |  |  |
| 11. | Are safety controls and devices tested on a periodic basis (as recommended by CSD1)? |  |  |  |  |
| 12. | Are boiler operators adequately trained to assure safe and efficient operation? |  |  |  |  |
| 13. | Are boilers inspected daily for adverse conditions prior to proper operations? |  |  |  |  |
| 14. | Is a log of incidents maintained that record boiler operations, and when safety controls and devices were tested (i.e., low water cutout, safety valve(s), combustion controller)? |  |  |  |  |
| 15. | Are only authorized (“R” stamp or proper ASME symbol holder) repair firms allowed to make welded repairs? |  |  |  |  |
| 16. | Have burners been immediately serviced, if the burner starts with a puff or operates in an unusual manner? |  |  |  |  |
| Compressed Air Storage Tank Operations |  |  |  |  |  |
| 17. | Are vessels rigidly mounted without vibration buffer supports under tank legs? |  |  |  |  |
| 18. | Are vessels operated without a properly equipped and calibrated pressure gauge? |  |  |  |  |
| 19. | Are pressure control switches, or similar devices controlling pressure, ever bypassed? |  |  |  |  |
| 20. | Do personnel restrict the design function of any safety relief valve: i.e., tie down, paint, block, cap, or remove such valve? |  |  |  |  |
| 21. | Are welded repairs performed on air tanks? |  |  |  |  |
| 22. | Is plastic pipe used on any air discharge line? |  |  |  |  |
| 23. | Has stock been piled up against the tank? |  |  |  |  |
| 24. | Is the safety relief valve tested monthly? |  |  |  |  |
| 25. | Is the condensate drained from the tank regularly, or daily, if necessary? |  |  |  |  |
| 26. | Are the vessels mounted in level positions at all times, with vibration protection in place? |  |  |  |  |
| 27. | Have the vessel been inspected biannually, as required by State law? |  |  |  |  |
| 28. | Are the tanks protected from damage caused by vehicle traffic or plant operations? |  |  |  |  |
| 29. | Are the vessels inspected for air leaks at least weekly? On finding an air leak, determine its source (i.e. line, fitting or crack). |  |  |  |  |
| 30. | Report new installations to the State Office of Boiler and Pressure Vessel Safety. |  |  |  |  |
| 31. | Have all welded repairs made only by companies holding the “R” stamp authorization or the A.S.M.E. “U” symbol. |  |  |  |  |
| 32. | When opening a valve to a pressure source, do not stand directly in front of any pressure gauges, especially non-safety types of pressure gauges. |  |  |  |  |
| Hot Water Heater Safety |  |  |  |  |  |
| 33. | Is the hot water heater flushed through the drain valve at least once a year to remove sediment build-up? |  |  |  |  |
| 34. | Is the safety relief valve tested once a year to ensure proper operation (this device protects the heater from over-pressurizing and from exceeding 210° F.) ? |  |  |  |  |
| 35. | Is the area around the hot water heater kept clean and free of combustible and flammable material? |  |  |  |  |
| 36. | Upon leaving for an extended time period involving days or weeks, is the hot water heater temperature set at its lowest setting. This will save money and reduce the risk of any problems. |  |  |  |  |
| 37. | Are the manufacturer’s guidelines followed for recommended maintenance schedules? |  |  |  |  |
| 38. | Is the hot water heater temperature above 120° F? |  |  |  |  |
| 39. | Is combustible material or flammable material kept at least 18” from a hot water heater? |  |  |  |  |
| 40. | Never leave children unattended around a hot water heater. |  |  |  |  |
| ### Compressed-Gas Cylinders |  |  |  |  |  |
| 41. | Is the protective valve cover in place when a cylinder is not connected to a regulator or manifold? |  |  |  |  |
| 42. | Are personnel allowed to handle oxygen cylinders with greasy, oily hands or gloves? The reaction between oxygen and hydrocarbons can be violent, even when small quantities are involved. |  |  |  |  |
| 43. | Before raising cylinders with cranes, fork trucks, or hoists, are they secured within suitable cradles or skid boxes? Do not use ropes or chain slings alone for this purpose. |  |  |  |  |
| 44. | Never use a gas cylinder as a roller for moving materials or for supporting other items. |  |  |  |  |
| 45. | Are cylinders adequately secured in an upright position upright on solid, dry, level footings? Store preferably outside of occupied buildings and away from traffic lanes. |  |  |  |  |
| 46. | Are cylinders stored in the sun shaded during the summer? Whenever possible store cylinders away from sources of intense heat (furnaces, steam lines, radiators). |  |  |  |  |
| 47. | Is gas, especially flammables, poisons, or corrosives, stockpiled beyond the amount required for immediate use? |  |  |  |  |
| 48. | Are containers that are stored for use in public areas, protected against tampering and damage? Containers stored inside or outside shall not obstruct exit routes or other areas that are normally used or intended for the safe exit of people. |  |  |  |  |
| 49. | Do stored cylinders have protective caps in place? |  |  |  |  |
| 50. | Are storage baskets for smaller cylinders (<5 L) being used? These baskets are available commercially. |  |  |  |  |
| 51. | Secure both ends of the hose with a hose restraint to prevent whipping in the event the hose or fitting fails. For systems in manned areas, support and secure the hose and tubing at least every 7 ft. |  |  |  |  |
| 52. | Do not use an open flame to leak-check a gas cylinder; use soapsuds or a leak-detection solution. |  |  |  |  |
| 53. | Remove the talc and dust from a new hose before connecting it. |  |  |  |  |
| 54. | Never interchange regulators and hose lines (with one type of gas for another). Explosions can occur if flammable gases or organic materials come in contact with oxidizers (e.g., oxygen) under pressure. |  |  |  |  |
| 55. | Never use oxygen to purge lines, operate pneumatic tools, or dust clothing. Remember, oxygen is not a substitute for compressed air. |  |  |  |  |
| 56. | After installing the regulator and before opening the cylinder valve, fully release (turning counterclockwise) the regulator pressure-adjusting screw. |  |  |  |  |
| 57. | Keep removable keys or handles from valve spindles or stems in place while the cylinders are in service. |  |  |  |  |
| 58. | Never leave pressure on a hose or line that is not being used. To shut down a system, close the cylinder valve and vent the pressure from the entire system. |  |  |  |  |
| 59. | Close the valves on empty cylinders to prevent internal contamination; remove the regulators and replace the protective cap. |  |  |  |  |
| 60. | Are empty cylinders stored separately from full cylinders? |  |  |  |  |