## BuildingSummary
Building Summary Hospital post-1980 construction
|  | Value | Data Source
Program
| Building Name | Hospital post-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, inpatient
Form
| Total Floor Area (m2) | 22422.1768 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3142
| Number of Floors | 5 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.1334
| East | 0.121
| North | 0.117
| West | 0.2315
| Total | 0.1461
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures and zone summary
| Floor to Ceiling Height (m) | 4.27
| Floor to Floor Height (m) | 4.27
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 5184.32
| Net Dimensions - Total Area (m2) | 4338.78
| Wall to Skin Ratio | 0.41902
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3739.134
| Net Dimensions - Total Area (m2) | 3739.134
| Roof to Skin Ratio | 0.58098
Window Dimensions (m2)
| South | 220.72
| East | 144.86
| North | 186.18
| West | 293.66
| Total Area (m2) | 845.42
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab
| Dimensions - Total Area (m2) | 3739.134
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15534.17
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 44872.35
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.26534 | See Reference Buildings Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Boiler | 2003 CBECS
| Cooling Type | Chiller, water cooled | 2003 CBECS
| Fan Control | CAV, VAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 4037.61

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 19.375 | 8.0729 |  |  | 10 |  | 1006.2497 |  | 0
ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
ER_Trauma1_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.66938
ER_Trauma2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
ER_Triage_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1.0503 | 25.7922 | 11.8403 |  |  | 10 |  | 10.5034 |  | 0.89241
Lobby_Records_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.7804 | 62.6301 | 13.0064 | 113.3908 | 15.7328 | 1.0764 |  |  | 10 |  | 1133.9077 |  | 0.26568
Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  |  | 0.25 | 1349.325 |  | 0.15304
ER_NurseStn_Lobby_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.5801 | 30.42 | 14.8645 | 83.1249 | 17.8959 | 14.6389 |  |  |  |  | 2929.9675 |  | 0.085575
OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.0501 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 1.1159
OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.44637
OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.66955
OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 84.9091 | 53.8195 |  | 7.5708 |  |  | 793.0838 |  | 0
IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 41.3698 | 32.2917 |  |  |  |  | 66.0874 |  | 1.5621
IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.6802 | 25.03 | 4.6452 | 133.0332 | 41.3698 | 32.2917 |  |  |  |  | 1465.3513 |  | 0.33219
ICU_NurseStn_Lobby_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 18.4588 | 21.5278 |  |  | 10 |  | 1585.8356 |  | 0
Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  | 10 | 0.25 | 1349.325 |  | 0.15304
OR_NurseStn_Lobby_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.1402 | 35.76 | 13.0064 | 77.8568 | 15.6644 | 11.1945 |  |  | 10 |  | 2401.245 |  | 0.17199
PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 26.9378 | 16.1458 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
NurseStn_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 23.8269 | 107.639 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
NurseStn_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.6702 | 35.76 | 9.2903 | 74.9999 | 27.7331 | 10.7639 |  |  | 10 |  | 749.9993 |  | 0.31244
NurseStn_Lobby_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.0801 | 0 | 13.0064 | 79.9999 | 15.6443 | 11.1945 |  |  | 10 |  | 2467.3419 |  | 0.095647
Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2002 | 0 | 18.5806 | 49.9999 | 15.2932 | 80.7294 | 304.9413 | 567.81 | 15 |  | 2202.9829 | 2501.3191 | 0.26781
Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.5601 | 17.98 | 13.2719 | 5.2517 | 25.7922 | 10.7639 |  |  | 10 |  | 52.5171 |  | 0.98173
Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.44627
Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.5501 | 17.98 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.98187
Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1 | 25.7922 | 10.7639 |  |  | 10 |  | 10 |  | 0.89241
Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.0601 | 0 | 92.9031 | 5.4 | 14.6034 | 0 |  |  |  | 0.25 | 125.42 |  | 0.14878
Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 1291.1824 |  |  |  | 1037.1996
Data Source | [7 empty] | 1 |  | 2 | 5, 6 | 5, 6 | 5, 6 | 3, 4 | 3, 4 | 3, 4 | 5 | 5
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] DOE Commercial Reference Buildings Report
[6] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 2.377 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Underground walls
| Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
| R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 1.5385 | 0.30675 | 0.30675 | 1.5385 | 1.8904 | 1.7123 | 1.8904 | 2.0661 | 2.0661 | 2.4155 | 2.2422 | 2.5974 | 3.125
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 3317.7354 | 3272.1969 | 2992.1053 | 3052.2014 | 2637.6716 | 2600.8729 | 2214.0284 | 3052.2193 | 2185.9303 | 2281.7485 | 3019.3167 | 2147.4495 | 2905.9548 | 2050.9651 | 2569.7719 | 2078.5723
Heating (kW)
| HEATSYS1 BOILER | 3292.1556 | 3444.169 | 3450.4642 | 3463.4962 | 3283.1835 | 3332.8226 | 3191.185 | 3572.7157 | 3158.2495 | 3404.7626 | 3749.1716 | 3265.9071 | 3832.2463 | 3556.5715 | 3840.169 | 4321.1484
HVAC Efficiency
| Air Conditioning (COP) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
| Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
HVAC Control - Economizer
| CAV_1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| CAV_2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CAV_1_FAN | 17.09 | 17.09 | 18.94 | 16.8 | 17.38 | 18.06 | 16.6 | 16.58 | 17.51 | 16.83 | 16.81 | 17.14 | 16.71 | 16.88 | 17.11 | 18.22
| CAV_2_FAN | 15.97 | 15.91 | 17.17 | 16.28 | 15.37 | 17.22 | 14.96 | 15.57 | 18.09 | 15.5 | 15.8 | 17.9 | 15.84 | 17.1 | 15.94 | 15.56
| VAV_1_FAN | 29.68 | 29.45 | 29.83 | 29.36 | 28.83 | 29.01 | 25.74 | 27.92 | 30.35 | 26.27 | 28.05 | 29.75 | 27.81 | 28.34 | 26.69 | 25.39
| VAV_2_FAN | 46.62 | 46.48 | 47.58 | 47.09 | 46.75 | 47.12 | 44.41 | 44.53 | 48.45 | 44.17 | 44.38 | 46.91 | 43.47 | 45.39 | 43.23 | 42.35
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.072201 | 0.090768 | 0.06245 | 0.09426 | 0.038797 | 0.083277 | 0.12172 | 0.049975 | 0.036945 | 0.063341 | 0.10044 | 0.036945 | 0.048928 | 0.0669 | 0.049505 | 0.086788
| Total Cost ($/m2) | 42.57 | 53.76 | 36.35 | 54.31 | 20.96 | 45.86 | 61.23 | 28.33 | 18.54 | 32.08 | 53.09 | 18.08 | 24.75 | 31.6 | 23.72 | 37.51
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011443 | 0.0081705 | 0.0085474 | 0.010664 | 0.0084165 | 0.0080861 | 0.0084171 | 0.010079 | 0.0071605 | 0.0082897 | 0.0088991 | 0.0071692 | 0.007977 | 0.0086961 | 0.0079732 | 0.0041782
| Total Cost ($/m2) | 5.43 | 4.6 | 4.81 | 6.5 | 5.08 | 4.45 | 5.48 | 6.54 | 3.6 | 5.53 | 6.16 | 3.86 | 5.82 | 5.34 | 6.22 | 4.57
Total Utility Costs
| Cost Intensity ($/m2) | 48 | 58.36 | 41.16 | 60.82 | 26.04 | 50.32 | 66.7 | 34.87 | 22.14 | 37.61 | 59.25 | 21.95 | 30.57 | 36.94 | 29.95 | 42.08
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 6291316.6667 | 6327405.5556 | 5806275 | 5917802.7778 | 5333411.1111 | 4916425 | 4704761.1111 | 5643586.1111 | 3966250 | 4629002.7778 | 4759355.5556 | 3723822.2222 | 4221366.6667 | 3422533.3333 | 3579569.4444 | 2426752.7778
| Interior Lighting | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667
| Exterior Lighting | 91075 | 90913.8889 | 90886.1111 | 91038.8889 | 91022.2222 | 90933.3333 | 90836.1111 | 90927.7778 | 90913.8889 | 90777.7778 | 90802.7778 | 90819.4444 | 90877.7778 | 90766.6667 | 90741.6667 | 90200
| Interior Equipment | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444
| Exterior Equipment | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667
| Fans | 1050097.2222 | 1028925 | 1133869.4444 | 1023011.1111 | 1017877.7778 | 1100808.3333 | 967747.2222 | 986611.1111 | 1102127.7778 | 987019.4444 | 998491.6667 | 1076816.6667 | 998786.1111 | 1041483.3333 | 1011933.3333 | 1041294.4444
| Pumps | 522341.6667 | 496483.3333 | 442780.5556 | 448083.3333 | 401408.3333 | 382502.7778 | 322527.7778 | 434172.2222 | 319716.6667 | 324766.6667 | 412483.3333 | 304838.8889 | 382250 | 279822.2222 | 323005.5556 | 222172.2222
| Heat Rejection | 363850 | 355044.4444 | 327152.7778 | 321372.2222 | 289269.4444 | 280572.2222 | 242791.6667 | 302705.5556 | 221719.4444 | 247530.5556 | 263952.7778 | 201636.1111 | 227830.5556 | 181480.5556 | 185627.7778 | 122941.6667
| Humidification | 7213.8889 | 87619.4444 | 357386.1111 | 227838.8889 | 90444.4444 | 686469.4444 | 60405.5556 | 362627.7778 | 660875 | 188041.6667 | 439116.6667 | 688458.3333 | 531252.7778 | 687075 | 668430.5556 | 902380.5556
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 57044.4444 | 54875 | 55077.7778 | 52772.2222 | 53069.4444 | 53394.4444 | 51586.1111 | 51430.5556 | 51455.5556 | 50519.4444 | 50444.4444 | 50205.5556 | 49969.4444 | 49244.4444 | 48597.2222 | 47677.7778
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 13220791.6667 | 13279116.6667 | 13051286.1111 | 12919775 | 12114355.5556 | 12348961.1111 | 11278505.5556 | 12709916.6667 | 11250911.1111 | 11355511.1111 | 11852505.5556 | 10974452.7778 | 11340188.8889 | 10590258.3333 | 10745761.1111 | 9691275
Gas (MJ)
| Heating | 8811250 | 10710350 | 10744110 | 11670030 | 11548980 | 10424190 | 12522680 | 12467270 | 9216260 | 12851960 | 13371500 | 9947810 | 14179610 | 11578470 | 15224430 | 22116480
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 464640 | 557300 | 504030 | 646620 | 629310 | 568200 | 705730 | 716820 | 703520 | 753400 | 778460 | 775260 | 831690 | 841380 | 919530 | 1025850
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10634310 | 12626070 | 12606550 | 13675070 | 13536710 | 12350810 | 14586820 | 14542510 | 11278200 | 14963770 | 15508380 | 12081480 | 16369720 | 13778270 | 17502370 | 24500740
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 58229160 | 60430890 | 59591170 | 60186260 | 57148390 | 56807070 | 55189440 | 60298210 | 51781480 | 55843620 | 58177390 | 51589510 | 57194400 | 51903190 | 56187110 | 59389330
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 1010.1016 | 1015.8958 | 932.2258 | 950.1321 | 856.3052 | 789.356 | 755.3723 | 906.1053 | 636.8008 | 743.209 | 764.1377 | 597.8778 | 677.761 | 549.5044 | 574.7173 | 389.627
| Interior Lighting (elec) | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135
| Exterior Lighting (elec) | 14.6225 | 14.5967 | 14.5922 | 14.6167 | 14.6141 | 14.5998 | 14.5842 | 14.5989 | 14.5967 | 14.5748 | 14.5788 | 14.5815 | 14.5909 | 14.573 | 14.569 | 14.482
| Interior Equipment (elec) | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554
| Exterior Equipment (elec) | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719
| Fans (elec) | 168.5982 | 165.1989 | 182.0483 | 164.2494 | 163.4252 | 176.7401 | 155.3765 | 158.4052 | 176.952 | 158.4708 | 160.3127 | 172.8882 | 160.36 | 167.2152 | 162.4708 | 167.1849
| Pumps (elec) | 83.8645 | 79.7128 | 71.0906 | 71.942 | 64.4481 | 61.4127 | 51.7834 | 69.7085 | 51.3321 | 52.1429 | 66.2262 | 48.9434 | 61.3721 | 44.9268 | 51.8601 | 35.6708
| Heat Rejection (elec) | 58.4179 | 57.0041 | 52.526 | 51.5979 | 46.4436 | 45.0472 | 38.9814 | 48.6009 | 35.5981 | 39.7422 | 42.3789 | 32.3737 | 36.5793 | 29.1376 | 29.8034 | 19.7389
| Humidification (elec) | 1.1582 | 14.0677 | 57.3801 | 36.5806 | 14.5213 | 110.216 | 9.6984 | 58.2217 | 106.1067 | 30.191 | 70.5023 | 110.5353 | 85.2952 | 110.3132 | 107.3198 | 144.8816
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 9.1588 | 8.8104 | 8.843 | 8.4728 | 8.5206 | 8.5727 | 8.2824 | 8.2574 | 8.2614 | 8.1111 | 8.0991 | 8.0607 | 8.0228 | 7.9064 | 7.8025 | 7.6549
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2122.6626 | 2132.027 | 2095.4476 | 2074.3329 | 1945.0189 | 1982.6859 | 1810.8191 | 2040.6391 | 1806.3887 | 1823.1827 | 1902.9776 | 1762.0019 | 1820.7226 | 1700.3176 | 1725.2844 | 1555.9815
Gas (MJ/m2)
| Heating (gas) | 392.9692 | 477.6664 | 479.172 | 520.4667 | 515.0681 | 464.904 | 558.4937 | 556.0225 | 411.0321 | 573.1791 | 596.3499 | 443.6582 | 632.3904 | 516.3833 | 678.9879 | 986.3635
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.7223 | 24.8548 | 22.479 | 28.8383 | 28.0663 | 25.3409 | 31.4746 | 31.9692 | 31.376 | 33.6006 | 34.7182 | 34.5755 | 37.0922 | 37.5244 | 41.0097 | 45.7515
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 474.2751 | 563.1048 | 562.2342 | 609.8887 | 603.718 | 550.8286 | 650.5514 | 648.5753 | 502.9917 | 667.3629 | 691.6517 | 538.8168 | 730.0662 | 614.4912 | 780.5808 | 1092.6981
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2596.9377 | 2695.1317 | 2657.6814 | 2684.2216 | 2548.7369 | 2533.5145 | 2461.3705 | 2689.2144 | 2309.3803 | 2490.546 | 2594.6288 | 2300.8187 | 2550.7889 | 2314.8084 | 2505.8652 | 2648.6796
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 2010.1245 | 2058.4051 | 1999.8704 | 1967.0553 | 1875.5368 | 1935.3438 | 1732.8398 | 1977.512 | 1800.4223 | 1746.7142 | 1882.1986 | 1784.9747 | 1618.401 | 1676.3881 | 1641.8027 | 1685.9593
| Feb | 1971.7821 | 2018.7011 | 2027.3283 | 1948.748 | 1847.569 | 1923.7388 | 1712.4349 | 1960.9116 | 1816.7859 | 1765.056 | 1898.2977 | 1780.13 | 1671.7623 | 1752.6229 | 1818.4025 | 1693.7376
| Mar | 2022.3181 | 2012.7668 | 1945.2487 | 1933.6721 | 1857.2372 | 1924.3491 | 1734.3917 | 1982.8572 | 1825.6945 | 1740.2699 | 1914.4109 | 1793.7366 | 1920.7909 | 1711.3285 | 1748.8258 | 1689.4795
| Apr | 1983.6301 | 1986.0323 | 1970.9911 | 1910.0022 | 1816.2613 | 1858.5959 | 1695.842 | 1941.4039 | 1762.3918 | 1732.1818 | 1980.876 | 1757.2545 | 1931.6464 | 1722.0587 | 1840.6778 | 1719.9464
| May | 1921.8372 | 1927.7697 | 1889.0521 | 1905.9877 | 1802.8828 | 1875.6705 | 1700.1365 | 1934.7613 | 1742.6596 | 1705.9926 | 1949.9977 | 1740.0894 | 1908.7265 | 1693.6431 | 1839.2453 | 1722.6534
| Jun | 1866.0624 | 1829.2616 | 1899.83 | 1851.6549 | 1764.2952 | 1795.7252 | 1687.2601 | 1877.672 | 1718.4418 | 1707.171 | 1927.9152 | 1709.8163 | 1892.2963 | 1708.5132 | 1836.6112 | 1701.6076
| Jul | 1847.1424 | 1827.3973 | 1823.7084 | 1827.7983 | 1684.2121 | 1798.921 | 1675.3495 | 1841.1249 | 1679.0091 | 1687.306 | 1830.9659 | 1637.3176 | 1841.7542 | 1618.492 | 1796.7792 | 1642.2151
| Aug | 1844.0847 | 1885.944 | 1797.2077 | 1816.8622 | 1692.6857 | 1770.9698 | 1672.2089 | 1853.2951 | 1618.6902 | 1670.1521 | 1890.0591 | 1631.9552 | 1821.5699 | 1661.4511 | 1803.978 | 1657.9198
| Sep | 1887.2244 | 1893.6647 | 1833.1728 | 1831.6476 | 1735.5403 | 1779.4834 | 1656.1923 | 1880.5467 | 1665.9925 | 1700.2211 | 1936.6042 | 1716.4652 | 1894.2007 | 1673.0102 | 1848.2867 | 1679.5272
| Oct | 1903.1175 | 1943.5753 | 1940.9799 | 1930.8021 | 1811.7668 | 1845.4433 | 1669.0434 | 1952.9994 | 1790.7144 | 1717.3888 | 1999.5378 | 1759.7609 | 1914.6512 | 1706.4017 | 1831.4882 | 1704.5741
| Nov | 1937.6124 | 2024.3711 | 1937.9352 | 1972.5901 | 1860.3763 | 1914.6884 | 1723.3562 | 1977.4263 | 1818.8732 | 1745.9969 | 1919.6786 | 1797.6514 | 1940.5754 | 1728.4119 | 1871.8899 | 1591.7935
| Dec | 1970.8419 | 2025.9564 | 2010.2425 | 1983.7951 | 1917.7096 | 1929.448 | 1756.7926 | 1948.9741 | 1789.5315 | 1723.7183 | 1878.9867 | 1775.2489 | 1687.6905 | 1709.363 | 1601.8421 | 1664.0365
Time of Peak Electrical Demand
| Jan | 12-JAN-17:00 | 09-JAN-17:45 | 23-JAN-17:00 | 20-JAN-17:00 | 18-JAN-14:00 | 30-JAN-17:30 | 17-JAN-17:00 | 05-JAN-16:00 | 20-JAN-17:30 | 03-JAN-17:00 | 17-JAN-14:45 | 25-JAN-17:45 | 30-JAN-17:00 | 25-JAN-17:15 | 13-JAN-16:45 | 19-JAN-16:30
| Feb | 10-FEB-17:00 | 08-FEB-15:30 | 21-FEB-13:30 | 22-FEB-17:00 | 14-FEB-17:00 | 06-FEB-17:00 | 23-FEB-17:00 | 28-FEB-17:00 | 15-FEB-17:00 | 21-FEB-17:00 | 28-FEB-11:45 | 07-FEB-17:00 | 17-FEB-16:15 | 03-FEB-17:45 | 28-FEB-17:00 | 28-FEB-17:00
| Mar | 15-MAR-08:15 | 29-MAR-15:00 | 03-MAR-10:15 | 14-MAR-10:45 | 22-MAR-16:00 | 06-MAR-17:00 | 03-MAR-17:00 | 10-MAR-17:45 | 03-MAR-17:00 | 23-MAR-15:00 | 30-MAR-15:45 | 31-MAR-15:45 | 31-MAR-16:45 | 31-MAR-16:00 | 21-MAR-15:00 | 30-MAR-16:00
| Apr | 06-APR-08:15 | 07-APR-09:00 | 20-APR-08:15 | 26-APR-09:00 | 04-APR-16:00 | 13-APR-08:15 | 21-APR-16:15 | 21-APR-16:00 | 11-APR-16:45 | 13-APR-15:00 | 27-APR-16:00 | 07-APR-16:00 | 13-APR-16:00 | 04-APR-16:00 | 27-APR-16:00 | 25-APR-16:00
| May | 02-MAY-08:15 | 10-MAY-08:15 | 16-MAY-15:45 | 09-MAY-09:15 | 19-MAY-09:00 | 05-MAY-09:30 | 19-MAY-16:00 | 18-MAY-15:00 | 05-MAY-16:00 | 11-MAY-15:15 | 12-MAY-15:00 | 09-MAY-15:00 | 17-MAY-16:00 | 18-MAY-10:15 | 03-MAY-16:00 | 09-MAY-15:15
| Jun | 02-JUN-16:00 | 05-JUN-10:45 | 19-JUN-10:45 | 12-JUN-09:15 | 01-JUN-08:45 | 19-JUN-09:00 | 02-JUN-16:45 | 20-JUN-10:00 | 26-JUN-16:00 | 08-JUN-10:45 | 23-JUN-15:00 | 15-JUN-16:00 | 14-JUN-10:45 | 01-JUN-16:00 | 23-JUN-16:00 | 02-JUN-10:45
| Jul | 25-JUL-15:00 | 28-JUL-16:00 | 06-JUL-10:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-16:00 | 06-JUL-10:45 | 20-JUL-09:15 | 31-JUL-16:00 | 03-JUL-15:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-10:45 | 13-JUL-08:15 | 21-JUL-09:30 | 27-JUL-08:15
| Aug | 01-AUG-12:15 | 09-AUG-10:45 | 16-AUG-10:00 | 30-AUG-08:15 | 09-AUG-16:00 | 15-AUG-10:00 | 03-AUG-08:15 | 23-AUG-09:15 | 29-AUG-16:00 | 10-AUG-09:15 | 07-AUG-08:15 | 25-AUG-16:00 | 11-AUG-08:00 | 31-AUG-09:15 | 31-AUG-16:00 | 28-AUG-16:00
| Sep | 21-SEP-09:00 | 18-SEP-10:45 | 22-SEP-06:15 | 26-SEP-08:15 | 21-SEP-07:15 | 29-SEP-16:00 | 12-SEP-08:15 | 22-SEP-14:00 | 20-SEP-16:00 | 19-SEP-16:00 | 20-SEP-15:00 | 26-SEP-10:45 | 28-SEP-16:00 | 14-SEP-10:15 | 27-SEP-15:45 | 28-SEP-16:00
| Oct | 24-OCT-08:15 | 16-OCT-09:15 | 16-OCT-08:15 | 23-OCT-09:45 | 30-OCT-07:15 | 30-OCT-16:00 | 02-OCT-09:15 | 24-OCT-16:45 | 31-OCT-16:00 | 16-OCT-16:00 | 26-OCT-16:00 | 17-OCT-15:15 | 19-OCT-15:15 | 17-OCT-15:15 | 19-OCT-15:15 | 03-OCT-16:00
| Nov | 22-NOV-09:15 | 29-NOV-17:00 | 16-NOV-09:15 | 16-NOV-17:00 | 24-NOV-17:00 | 24-NOV-17:45 | 20-NOV-16:00 | 07-NOV-16:00 | 13-NOV-17:00 | 21-NOV-16:00 | 01-NOV-16:00 | 10-NOV-17:45 | 01-NOV-16:00 | 21-NOV-16:45 | 03-NOV-16:00 | 14-NOV-09:15
| Dec | 26-DEC-17:00 | 12-DEC-17:30 | 27-DEC-17:45 | 27-DEC-17:45 | 08-DEC-16:00 | 14-DEC-16:00 | 29-DEC-16:00 | 08-DEC-16:00 | 05-DEC-16:00 | 07-DEC-17:00 | 12-DEC-17:00 | 29-DEC-16:00 | 01-DEC-13:00 | 01-DEC-16:45 | 01-DEC-16:30 | 18-DEC-10:00
Source Energy
| Total Source Energy (GJ) | 169484.78 | 187414.78 | 162378.72 | 171396.83 | 149760.24 | 172507.11 | 141593.93 | 179502.82 | 146705.67 | 87553.12 | 168239.49 | 144280.61 | 158190.16 | 147568.11 | 152072.03 | 151376.84
| Total Source Energy (MJ/m2) | 7558.78 | 8358.43 | 7241.86 | 7644.05 | 6679.09 | 7693.57 | 6314.89 | 8005.57 | 6542.86 | 3904.74 | 7503.24 | 6434.71 | 7055.06 | 6581.33 | 6782.2 | 6751.19
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 40269.52 | 34223.06 | 42996.58 | 28840.48 | 25275.24 | 36622.36 | 17491.89 | 25316.04 | 23972.31 | 16832.45 | 21198.75 | 19900.51 | 18792.58 | 15928.49 | 13573 | 9396.54
| Humidification | 9.66 | 117.34 | 478.61 | 305.12 | 121.12 | 919.32 | 80.89 | 485.63 | 885.04 | 251.83 | 588.07 | 921.98 | 711.45 | 920.13 | 895.16 | 1208.47
| Water Systems | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67
| Total Building | 44284.86 | 38346.07 | 47480.86 | 33151.27 | 29402.04 | 41547.35 | 21578.45 | 29807.35 | 28863.03 | 21089.95 | 25792.49 | 24828.16 | 23509.7 | 20854.29 | 18473.83 | 14610.68
Emissions
| Carbon Equivalent (kg) | 3817560 | 4657080 | 4167190 | 4226360 | 1659860 | 4387710 | 1581110 | 3692080 | 4799350 | 1096910 | 6598810 | 4700900 | 4176860 | 4118540 | 3993810 | 3168820
| CO2 (kg) | 8949780 | 11772400 | 9922170 | 9744940 | 4485090 | 10508300 | 4279000 | 8449200 | 11296700 | 2744300 | 15388000 | 11075400 | 9801630 | 9719140 | 9391570 | 8107670
| NOX (kg) | 15309.7605 | 15206.3665 | 16256.2654 | 18088.5281 | 3874.9646 | 16761.8251 | 3701.4532 | 16066.3528 | 19322.9301 | 3864.5278 | 27282.21 | 18899.2271 | 17104.16 | 16629.8686 | 16301.7572 | 9717.0552
| SO2 (kg) | 56593.1267 | 63344.7726 | 52485.2049 | 45352.078 | 35254.9508 | 67932.4702 | 32823.0093 | 46400.1817 | 49133.5006 | 8780.912 | 79880.5605 | 47926.4724 | 26769.0477 | 28280.9504 | 25366.4046 | 49339.0262
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.259 | 0.1793 | 0.1437 | 0.1669 | 0.0173 | 0.1286 | 0.0163 | 0.1884 | 0.1925 | 0.0357 | 0.2423 | 0.1879 | 0.1969 | 0.1975 | 0.1868 | 0.1694
| Water for Electricity (m3) | 7003.82 | 21606.7 | 387681 | 80665.9 | 212701 | 338781 | 198025 | 2885.63 | 51088.1 | 116017 | 18388.5 | 49832.8 | 17593.6 | 670831 | 16671.4 | 9901.38

## Picture
DOE Commercial Building Benchmark - Hospital
Second Floor
Third Floor
Forth Floor
Fifth Floor

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 73 | 3806.43
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 13
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
|  |  | Sats | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ADMIN_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 93.6 | 4880.57
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
ADMIN_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 73.1 | 3811.64
|  |  | SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5
|  |  | WinterDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
ADMIN_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 76.56 | 3992.06
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 58.5 | 3050.36
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
CRITICAL_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6 | 130.2 | 6789
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
CRITICAL_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18 | 108 | 5631.43
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
CRITICAL_OCC_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1 | 102.6 | 5349.86
|  |  | SummerDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | WinterDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 36 | 1877.14
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 17.7 | 922.93
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 18.25 | 951.61
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ADMIN_CLGSETP_SCH | Temperature | Through 12/31 | WD | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3395.6 | 177056.29
|  |  | SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6
|  |  | WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sats | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
ADMIN_HTGSETP_SCH | Temperature | Through 12/31 | WD | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 2839.6 | 148064.86
|  |  | SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6
|  |  | WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sats | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | WD | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668 | 4028 | 210031.43
|  |  | SummerDesign | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Sats | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6 | 2494.6 | 130075.57
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6
|  |  | WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Sats | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CRITICAL_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 532.8 | 3729.6 | 194472
CRITICAL_HTGSETP_SCH | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CAV_OAminFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
VAV_OAminFracSchedule | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 57.4 | 2993
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600