## BuildingSummary
Building Summary Large Hotel post-1980 construction
|  | Value | Data Source
Program
| Building Name | Large Hotel post-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.59998 | See Reference Buildings Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZVAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | 2 air cooled chillers | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 44332.9

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 7.5347 | 5.3819 |  |  |  | 0.25 | 494.7075 |  | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.8401 | 23.3 | 6.1939 | 10.8285 | 38.099 | 10.7639 |  |  |  | 1.5 | 100.605 |  | 1.0572
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 38.099 | 10.7639 |  |  |  | 1.5 | 116.505 |  | 0.35236
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8001 | 0 | 0 | 0 | 8.6039 | 5.3819 |  |  |  | 0.25 | 41.06 |  | 0.39384
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 3.9573 | 2.691 |  |  |  | 0.75 | 71.07 |  | 0.39382
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.7501 | 0 | 23.2258 | 3.3601 | 12.2365 | 61.6991 | 536.0463 | 592.7936 | 8 |  | 26.8805 | 235.9735 | 1.1318
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.1701 | 65.6201 | 1.3935 | 135.5247 | 15.7419 | 5.3819 |  |  | 10 |  | 1355.2468 |  | 0.82991
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.7904 | 85.2401 | 3.0965 | 422.479 | 20.2858 | 8.0729 |  |  | 10 |  | 4224.7904 |  | 0.34234
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60879
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 89.9032 |  |  | 14.1584 |  | 0.60863
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 13.1176 |  |  |  |  | 0.25 | 97.35 |  | 0.16612
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.3709
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 19.0986 | 14.3052 |  | 4.7317 |  |  | 14.1584 |  | 1.371
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.1801 | 6.75 | 16.3533 | 1.5 | 19.0986 | 14.3052 |  | 42.5858 |  |  | 14.1584 |  | 3.4487
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.5501 | 32.21 | 1.3935 | 237.997 | 27.558 | 67.8406 |  |  | 10 |  | 2379.97 |  | 0.39385
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.3301 | 26.38 | 18.5806 | 5.5596 | 16.8341 | 508.2285 | 1613.4237 | 503.4582 | 8 |  | 44.4764 | 1887.788 | 1.132
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5001 | 28.22 | 92.9031 | 4.436 | 13.081 |  |  |  |  | 0.25 | 103.03 |  | 0.44675
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.8441 | 1214.3111 |  | 1411.2773 |  |  |  | 15229.9891
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls - commercial space
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Exterior walls - residential space
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Underground walls
| Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
| R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 1.5385 | 0.30675 | 0.30675 | 1.5385 | 1.8904 | 1.7123 | 1.8904 | 2.0661 | 2.0661 | 2.4155 | 2.2422 | 2.5974 | 3.125
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Windows - fixed, commercial
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Windows - operable, residential
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER 1 | 737.5845 | 702.6069 | 607.815 | 631.102 | 450.5009 | 459.9849 | 305.371 | 640.3378 | 306.8086 | 344.9758 | 635.4637 | 304.4547 | 602.0284 | 286.8262 | 494.1713 | 266.2151
| COOLSYS1 CHILLER 2 | 737.5845 | 702.6069 | 607.815 | 631.102 | 450.5009 | 459.9849 | 305.371 | 640.3378 | 306.8086 | 344.9758 | 635.4637 | 304.4547 | 602.0284 | 286.8262 | 494.1713 | 266.2151
Heating (kW)
| HEATSYS1 BOILER | 2157.8931 | 2877.1676 | 2435.8301 | 3140.6752 | 2234.3423 | 2645.3089 | 2456.6815 | 3466.0462 | 2814.8411 | 2982.6092 | 4078.8929 | 3365.5417 | 4417.2371 | 4068.1662 | 4527.3688 | 5629.8293
| CORRIDOR_FLR_6 UNIT HEATER COIL | 5.5576 | 11.8899 | 7.7688 | 14.1897 | 7.6304 | 9.8006 | 9.2563 | 13.1945 | 12.6222 | 10.4816 | 16.9624 | 15.3253 | 17.4642 | 17.9083 | 17.7842 | 21.4869
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER 1 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| COOLSYS1 CHILLER 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| CORRIDOR_FLR_6 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Control - Economizer
| FLR_3_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| FLR_6_DOAS_FAN | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA | NoEcono:100%OA
| VAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CORRIDOR_FLR_6 UNIT HEATERFAN | 0.15 | 0.33 | 0.22 | 0.4 | 0.22 | 0.28 | 0.26 | 0.33 | 0.41 | 0.27 | 0.43 | 0.48 | 0.43 | 0.51 | 0.44 | 0.49
| DINING_FLR_6 EXHAUST FAN | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84 | 1.84
| KITCHEN_FLR_6 EXHAUST FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 1.34 | 1.36 | 1.58 | 1.3 | 1.55 | 1.51 | 1.37 | 1.3 | 1.53 | 1.39 | 1.36 | 1.48 | 1.35 | 1.42 | 1.5 | 1.68
| ROOM_1_FLR_6 FAN COILFAN | 0.37 | 0.37 | 0.41 | 0.36 | 0.43 | 0.39 | 0.37 | 0.35 | 0.41 | 0.38 | 0.36 | 0.39 | 0.35 | 0.37 | 0.39 | 0.44
| ROOM_2_FLR_3 FAN COILFAN | 1.36 | 1.37 | 1.57 | 1.29 | 1.46 | 1.49 | 1.19 | 1.29 | 1.52 | 1.31 | 1.35 | 1.46 | 1.33 | 1.4 | 1.46 | 1.56
| ROOM_2_FLR_6 FAN COILFAN | 0.37 | 0.37 | 0.41 | 0.36 | 0.41 | 0.39 | 0.32 | 0.35 | 0.41 | 0.36 | 0.36 | 0.39 | 0.35 | 0.37 | 0.38 | 0.41
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.36 | 1.39 | 1.57 | 1.43 | 1.82 | 1.52 | 2.03 | 1.3 | 1.39 | 1.93 | 1.31 | 1.33 | 1.34 | 1.44 | 1.59 | 2.65
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45 | 20.45
| ROOM_5_FLR_3 FAN COILFAN | 1.12 | 1.13 | 1.31 | 1.12 | 1.25 | 1.22 | 1.07 | 1.12 | 1.24 | 1.21 | 1.17 | 1.2 | 1.18 | 1.21 | 1.29 | 1.55
| ROOM_6_FLR_3 FAN COILFAN | 1.17 | 1.17 | 1.34 | 1.15 | 1.22 | 1.24 | 0.95 | 1.15 | 1.28 | 1.15 | 1.19 | 1.23 | 1.2 | 1.23 | 1.3 | 1.47
| FLR_3_DOAS_FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| FLR_6_DOAS_FAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
| VAV WITH REHEAT_FAN | 36.67 | 36.49 | 37.86 | 38.34 | 35.53 | 38.03 | 34.02 | 37.44 | 41.99 | 37.12 | 38.07 | 42.15 | 38.45 | 40.79 | 38.55 | 39
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.072333 | 0.098509 | 0.066648 | 0.099304 | 0.041362 | 0.086312 | 0.12326 | 0.056194 | 0.036979 | 0.06615 | 0.096232 | 0.036981 | 0.052968 | 0.069078 | 0.053534 | 0.089836
| Total Cost ($/m2) | 47.67 | 53.92 | 35.13 | 45.34 | 17.08 | 36.09 | 39.62 | 24.13 | 12.24 | 20.87 | 37.77 | 11.79 | 20.19 | 21.09 | 17.68 | 24.4
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.0081735 | 0.0085404 | 0.010616 | 0.0084064 | 0.0080689 | 0.00842 | 0.010014 | 0.0071612 | 0.0083047 | 0.0088124 | 0.0071606 | 0.0079621 | 0.0086554 | 0.0079592 | 0.0041817
| Total Cost ($/m2) | 5.35 | 5.08 | 4.61 | 8.25 | 5.43 | 5.13 | 6.54 | 9.34 | 6.01 | 7.8 | 9.59 | 7.06 | 9.81 | 10.06 | 11.23 | 7.71
Total Utility Costs
| Cost Intensity ($/m2) | 53.01 | 59 | 39.75 | 53.59 | 22.51 | 41.22 | 46.16 | 33.47 | 18.25 | 28.67 | 47.36 | 18.85 | 30 | 31.16 | 28.92 | 32.11
Energy - End Uses
Electricity (kWh)
| Heating | 400 | 341.6667 | 1311.1111 | 119.4444 | 27.7778 | 858.3333 | 0 | 58.3333 | 152.7778 | 0 | 86.1111 | 72.2222 | 175 | 205.5556 | 175 | 1169.4444
| Cooling | 5548369.4444 | 4289858.3333 | 4053141.6667 | 3266430.5556 | 2772277.7778 | 2825097.2222 | 1745588.8889 | 2962100 | 1834988.8889 | 1672211.1111 | 2544022.2222 | 1702650 | 2414741.6667 | 1552463.8889 | 1836216.6667 | 1157341.6667
| Interior Lighting | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111 | 628386.1111
| Exterior Lighting | 121627.7778 | 121580.5556 | 121558.3333 | 121538.8889 | 121447.2222 | 121419.4444 | 121483.3333 | 121408.3333 | 121455.5556 | 121213.8889 | 121427.7778 | 121358.3333 | 121350 | 121322.2222 | 121252.7778 | 120511.1111
| Interior Equipment | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222 | 542272.2222
| Exterior Equipment | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556 | 263205.5556
| Fans | 318902.7778 | 316733.3333 | 325644.4444 | 316088.8889 | 317691.6667 | 322130.5556 | 310130.5556 | 313741.6667 | 324927.7778 | 316783.3333 | 315313.8889 | 322411.1111 | 315944.4444 | 320441.6667 | 319813.8889 | 330916.6667
| Pumps | 31280.5556 | 26244.4444 | 23616.6667 | 21677.7778 | 18827.7778 | 19872.2222 | 15619.4444 | 20041.6667 | 18483.3333 | 15697.2222 | 18516.6667 | 16691.6667 | 19061.1111 | 16572.2222 | 17341.6667 | 18672.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21830.5556 | 21077.7778 | 21208.3333 | 20419.4444 | 20608.3333 | 20686.1111 | 20005.5556 | 19969.4444 | 19969.4444 | 19611.1111 | 19633.3333 | 19594.4444 | 19488.8889 | 19283.3333 | 19027.7778 | 18630.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 7476277.7778 | 6209700 | 5980344.4444 | 5180141.6667 | 4684747.2222 | 4743925 | 3646694.4444 | 4871186.1111 | 3753841.6667 | 3579380.5556 | 4452863.8889 | 3616641.6667 | 4324625 | 3464152.7778 | 3747691.6667 | 3081102.7778
Gas (MJ)
| Heating | 180310 | 909270 | 573960 | 1687040 | 393770 | 950500 | 1030990 | 2676960 | 1767110 | 2349060 | 3752730 | 2634960 | 4798200 | 3904590 | 5862750 | 9597950
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650 | 1238650
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3880220 | 4905880 | 4316720 | 5893750 | 5701720 | 5026760 | 6547090 | 6670230 | 6523020 | 7074150 | 7351750 | 7316160 | 7940640 | 8047570 | 8911920 | 10087700
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5299180 | 7053810 | 6129320 | 8819430 | 7334130 | 7215910 | 8816730 | 10585840 | 9528780 | 10661860 | 12343130 | 11189770 | 13977490 | 13190810 | 16013330 | 20924300
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 32213770 | 29408720 | 27658560 | 27467940 | 24199220 | 24294040 | 21944830 | 28122110 | 23042610 | 23547620 | 28373440 | 24209680 | 29546140 | 25661760 | 29505020 | 32016270
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.12692 | 0.10842 | 0.41603 | 0.037901 | 0.0088142 | 0.27236 | 0 | 0.01851 | 0.048478 | 0 | 0.027324 | 0.022917 | 0.05553 | 0.065225 | 0.05553 | 0.37108
| Cooling (elec) | 1760.5658 | 1361.2248 | 1286.1117 | 1036.4786 | 879.6778 | 896.4381 | 553.8968 | 939.9107 | 582.2645 | 530.6131 | 807.2495 | 540.2718 | 766.2272 | 492.6159 | 582.6541 | 367.2387
| Interior Lighting (elec) | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946 | 199.3946
| Exterior Lighting (elec) | 38.594 | 38.579 | 38.572 | 38.5658 | 38.5367 | 38.5279 | 38.5482 | 38.5244 | 38.5393 | 38.4627 | 38.5305 | 38.5085 | 38.5058 | 38.497 | 38.475 | 38.2397
| Interior Equipment (elec) | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696 | 172.0696
| Exterior Equipment (elec) | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184 | 83.5184
| Fans (elec) | 101.1918 | 100.5034 | 103.331 | 100.2989 | 100.8075 | 102.216 | 98.4082 | 99.5541 | 103.1036 | 100.5192 | 100.053 | 102.305 | 100.2531 | 101.6801 | 101.4809 | 105.0039
| Pumps (elec) | 9.9257 | 8.3277 | 7.4939 | 6.8786 | 5.9743 | 6.3057 | 4.9562 | 6.3595 | 5.865 | 4.9809 | 5.8756 | 5.2965 | 6.0483 | 5.2586 | 5.5027 | 5.9249
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 6.9271 | 6.6882 | 6.7297 | 6.4793 | 6.5393 | 6.564 | 6.348 | 6.3366 | 6.3366 | 6.2228 | 6.2299 | 6.2176 | 6.1841 | 6.1188 | 6.0377 | 5.9117
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2372.3149 | 1970.4142 | 1897.6368 | 1643.7226 | 1486.5279 | 1505.3057 | 1157.141 | 1545.6872 | 1191.1401 | 1135.7815 | 1412.9485 | 1147.6049 | 1372.2567 | 1099.2183 | 1189.1886 | 977.6718
Gas (MJ/m2)
| Heating (gas) | 15.8929 | 80.1452 | 50.5902 | 148.6996 | 34.7078 | 83.7793 | 90.8738 | 235.9534 | 155.7571 | 207.0516 | 330.7743 | 232.2514 | 422.9244 | 344.1596 | 516.7563 | 845.9854
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775 | 109.1775
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 342.0115 | 432.4156 | 380.4856 | 519.4887 | 502.5627 | 443.0702 | 577.0756 | 587.9294 | 574.954 | 623.5319 | 648.0002 | 644.8632 | 699.9063 | 709.3314 | 785.5172 | 889.1531
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 467.0819 | 621.7391 | 540.2524 | 777.3649 | 646.4471 | 636.0269 | 777.1269 | 933.0603 | 839.8886 | 939.7609 | 1087.9519 | 986.2921 | 1232.0082 | 1162.6684 | 1411.4518 | 1844.316
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2839.3959 | 2592.1523 | 2437.8892 | 2421.0875 | 2132.975 | 2141.3327 | 1934.2679 | 2478.7476 | 2031.0287 | 2075.5415 | 2500.9004 | 2133.897 | 2604.2649 | 2261.8867 | 2600.6404 | 2821.9878
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1100.4761 | 1057.789 | 965.3219 | 969.8062 | 801.982 | 637.7233 | 658.0453 | 841.979 | 652.2122 | 595.5682 | 614.3543 | 659.3479 | 586.7091 | 598.6618 | 573.5975 | 571.517
| Feb | 1095.314 | 1066.1164 | 969.91 | 928.8236 | 801.1514 | 807.681 | 662.2872 | 757.4908 | 661.0856 | 700.211 | 603.9428 | 658.8534 | 606.2435 | 642.062 | 615.5919 | 576.599
| Mar | 1109.0482 | 1070.1959 | 995.9766 | 1001.6984 | 798.4397 | 817.163 | 662.2786 | 1013.9565 | 664.5038 | 697.0703 | 965.7849 | 663.2302 | 807.0064 | 642.9856 | 636.9027 | 633.087
| Apr | 1119.3192 | 1069.4441 | 998.9036 | 998.1161 | 804.7235 | 827.5502 | 660.7534 | 1005.5886 | 664.2845 | 698.1017 | 918.0862 | 660.7977 | 949.7109 | 646.4875 | 781.9034 | 636.0293
| May | 1121.745 | 1078.2581 | 1009.2206 | 1004.805 | 800.6928 | 827.6109 | 662.0386 | 1013.8309 | 659.7062 | 698.5882 | 1012.1848 | 660.2761 | 972.0955 | 644.2153 | 839.1184 | 596.7389
| Jun | 1106.9889 | 1047.5771 | 1013.1747 | 1011.5166 | 802.1693 | 830.6617 | 660.8381 | 1010.5048 | 657.8428 | 696.9861 | 1022.0161 | 659.791 | 967.8857 | 612.2114 | 843.1469 | 594.0578
| Jul | 1077.3315 | 1066.2891 | 1012.6168 | 995.1505 | 792.8552 | 829.0899 | 661.8324 | 1006.2129 | 653.1453 | 695.3974 | 1005.3357 | 650.223 | 963.8509 | 626.762 | 840.3981 | 590.8024
| Aug | 1080.0185 | 1056.9242 | 1013.7459 | 988.1757 | 791.0654 | 830.9943 | 662.0408 | 1029.9134 | 655.0145 | 695.6691 | 995.2419 | 654.1288 | 963.0554 | 639.5381 | 846.5654 | 596.2419
| Sep | 1078.7189 | 1084.0718 | 1008.6938 | 982.1084 | 798.3723 | 824.79 | 658.6121 | 1009.9006 | 658.5039 | 700.0881 | 1010.6319 | 660.7425 | 958.782 | 643.5672 | 840.6421 | 634.6215
| Oct | 1104.8019 | 1045.9319 | 994.2802 | 992.1522 | 804.9594 | 821.1303 | 659.6905 | 992.0426 | 666.1321 | 698.8061 | 1001.071 | 660.1065 | 959.8222 | 645.8619 | 819.2665 | 630.4927
| Nov | 1105.3662 | 1052.9852 | 969.9086 | 981.2645 | 803.5364 | 813.6091 | 664.417 | 980.765 | 661.7805 | 683.8685 | 1004.9164 | 660.0639 | 765.6553 | 645.4132 | 673.3382 | 573.8902
| Dec | 1104.3867 | 1061.7814 | 964.6402 | 957.2248 | 813.9423 | 784.7742 | 648.4282 | 777.0209 | 627.2495 | 588.8892 | 618.0566 | 623.6751 | 588.2346 | 605.0895 | 576.2186 | 534.3859
Time of Peak Electrical Demand
| Jan | 04-JAN-20:10 | 18-JAN-20:10 | 27-JAN-20:10 | 24-JAN-20:10 | 12-JAN-20:10 | 18-JAN-20:00 | 17-JAN-20:49 | 09-JAN-06:10 | 26-JAN-20:30 | 27-JAN-21:00 | 17-JAN-21:00 | 24-JAN-20:19 | 30-JAN-21:00 | 30-JAN-21:00 | 15-JAN-20:00 | 20-JAN-21:00
| Feb | 17-FEB-20:10 | 22-FEB-20:00 | 27-FEB-20:10 | 22-FEB-07:10 | 23-FEB-20:10 | 27-FEB-20:10 | 13-FEB-20:00 | 14-FEB-06:30 | 13-FEB-20:10 | 21-FEB-20:10 | 27-FEB-21:00 | 10-FEB-20:00 | 19-FEB-20:00 | 03-FEB-20:10 | 22-FEB-21:00 | 28-FEB-20:10
| Mar | 14-MAR-19:10 | 21-MAR-19:10 | 17-MAR-19:10 | 28-MAR-19:10 | 28-MAR-19:10 | 22-MAR-19:10 | 30-MAR-19:10 | 09-MAR-20:10 | 31-MAR-19:30 | 28-MAR-19:10 | 31-MAR-18:10 | 31-MAR-19:00 | 23-MAR-17:19 | 15-MAR-19:10 | 22-MAR-19:19 | 28-MAR-19:00
| Apr | 19-APR-19:10 | 04-APR-19:10 | 26-APR-19:10 | 13-APR-19:10 | 11-APR-19:10 | 28-APR-19:10 | 20-APR-19:10 | 05-APR-19:10 | 28-APR-19:10 | 26-APR-19:10 | 28-APR-17:10 | 28-APR-19:19 | 27-APR-19:10 | 04-APR-19:49 | 04-APR-18:10 | 05-APR-19:49
| May | 05-MAY-19:10 | 11-MAY-19:10 | 19-MAY-19:19 | 26-MAY-19:40 | 08-MAY-19:10 | 31-MAY-19:10 | 15-MAY-19:10 | 05-MAY-19:10 | 05-MAY-19:10 | 01-MAY-19:19 | 04-MAY-19:10 | 12-MAY-19:49 | 15-MAY-19:30 | 10-MAY-19:00 | 31-MAY-19:49 | 12-MAY-19:00
| Jun | 02-JUN-19:10 | 23-JUN-19:30 | 20-JUN-19:40 | 12-JUN-19:49 | 08-JUN-19:10 | 21-JUN-19:10 | 12-JUN-19:00 | 05-JUN-19:30 | 12-JUN-19:00 | 08-JUN-19:00 | 15-JUN-19:30 | 01-JUN-19:00 | 22-JUN-19:00 | 12-JUN-19:10 | 15-JUN-19:00 | 07-JUN-19:10
| Jul | 24-JUL-19:00 | 28-JUL-19:19 | 06-JUL-19:40 | 11-JUL-19:49 | 28-JUL-19:10 | 06-JUL-19:10 | 06-JUL-19:30 | 20-JUL-19:30 | 06-JUL-19:19 | 12-JUL-19:00 | 21-JUL-19:19 | 27-JUL-19:30 | 03-JUL-19:00 | 31-JUL-19:00 | 28-JUL-19:49 | 05-JUL-19:10
| Aug | 04-AUG-19:10 | 11-AUG-19:10 | 23-AUG-19:10 | 29-AUG-19:10 | 01-AUG-19:00 | 09-AUG-19:10 | 03-AUG-19:19 | 18-AUG-19:10 | 24-AUG-19:19 | 30-AUG-19:00 | 01-AUG-19:10 | 04-AUG-19:00 | 29-AUG-19:10 | 22-AUG-19:40 | 23-AUG-19:10 | 31-AUG-19:10
| Sep | 08-SEP-19:00 | 26-SEP-19:10 | 07-SEP-19:10 | 13-SEP-19:10 | 20-SEP-19:10 | 11-SEP-19:10 | 18-SEP-19:00 | 08-SEP-19:10 | 08-SEP-19:10 | 19-SEP-19:10 | 26-SEP-19:10 | 15-SEP-19:40 | 15-SEP-19:10 | 20-SEP-19:10 | 06-SEP-19:10 | 28-SEP-19:00
| Oct | 24-OCT-19:10 | 26-OCT-19:10 | 02-OCT-19:10 | 12-OCT-19:10 | 20-OCT-19:30 | 06-OCT-19:10 | 06-OCT-19:10 | 20-OCT-19:10 | 04-OCT-19:10 | 05-OCT-19:10 | 11-OCT-19:10 | 02-OCT-19:10 | 02-OCT-19:10 | 20-OCT-19:00 | 07-OCT-19:10 | 04-OCT-19:00
| Nov | 16-NOV-20:10 | 24-NOV-20:10 | 06-NOV-20:10 | 22-NOV-20:00 | 24-NOV-20:10 | 21-NOV-20:10 | 06-NOV-20:10 | 03-NOV-19:10 | 13-NOV-20:40 | 03-NOV-19:00 | 02-NOV-19:10 | 03-NOV-19:10 | 02-NOV-15:09 | 21-NOV-20:10 | 02-NOV-20:00 | 14-NOV-21:00
| Dec | 28-DEC-20:10 | 20-DEC-20:49 | 13-DEC-20:00 | 04-DEC-20:00 | 29-DEC-20:10 | 05-DEC-19:19 | 17-DEC-20:10 | 08-DEC-06:30 | 05-DEC-20:30 | 31-DEC-20:00 | 11-DEC-21:00 | 22-DEC-21:00 | 01-DEC-21:00 | 31-DEC-20:00 | 01-DEC-21:00 | 18-DEC-07:00
Source Energy
| Total Source Energy (GJ) | 95062.42 | 88895.81 | 74790.2 | 72364.4 | 60206.32 | 68968.24 | 50259.35 | 74269.43 | 55244.31 | 34089.75 | 70322.17 | 55419.29 | 68772.86 | 57753.38 | 63857.49 | 62469.85
| Total Source Energy (MJ/m2) | 8379.02 | 7835.48 | 6592.18 | 6378.37 | 5306.73 | 6079.02 | 4429.98 | 6546.28 | 4869.36 | 3004.75 | 6198.36 | 4884.79 | 6061.8 | 5090.52 | 5628.55 | 5506.24
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
| Total Building | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9 | 44332.9
Emissions
| Carbon Equivalent (kg) | 2145930 | 2198510 | 1915850 | 1754710 | 679741.0293 | 1730130 | 585163.6146 | 1505410 | 1705270 | 452963.1235 | 2596620 | 1679170 | 1732340 | 1503800 | 1571570 | 1244310
| CO2 (kg) | 5023820 | 5565020 | 4564900 | 4081030 | 1843810 | 4165590 | 1597160 | 3499370 | 4069510 | 1174770 | 6120630 | 4025450 | 4140870 | 3631630 | 3791670 | 3261960
| NOX (kg) | 8623.7824 | 7165.3073 | 7465.6124 | 7410.349 | 1597.7881 | 6556.0442 | 1390.7428 | 6394.6497 | 6719.7755 | 1499.3447 | 10557.8874 | 6569.2121 | 6888.5942 | 5850.4999 | 6154.1066 | 3710.5793
| SO2 (kg) | 32002.877 | 29622.1535 | 24049.8032 | 18184.6572 | 13634.0154 | 26097.3176 | 10613.8098 | 17784.6117 | 16394.8252 | 2769.4314 | 30012.0432 | 15796.1488 | 10210.5512 | 9253.2374 | 8849.4437 | 15689.6517
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1464 | 0.084 | 0.0659 | 0.0673 | 0.0069 | 0.0497 | 0.0057 | 0.0728 | 0.0649 | 0.0119 | 0.0918 | 0.0627 | 0.0759 | 0.0656 | 0.0662 | 0.0553
| Water for Electricity (m3) | 3960.62 | 10103.9 | 177643 | 32342.7 | 82253.6 | 130145 | 64027.8 | 1105.94 | 17045.4 | 36569.8 | 6908.35 | 16422.4 | 6709.4 | 219434 | 5814.32 | 3147.9

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 618 | 4326 | 225570
HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 469 | 3283 | 171185
Corr_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
Corr_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Guest_CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Guest_HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652 | 4564 | 237980
Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 435 | 3045 | 158775
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HVACOperationSchd | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
MinOA_Sched | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 119 | 6205
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
Kitchen_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Guest Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Guest Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Laundry Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600