## BuildingSummary
Building Summary Medium Office post-1980 construction
|  | Value | Data Source
Program
| Building Name | Medium Office Reference Building post-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.75222 | See Reference Buildings Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace and electric reheat | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.59

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 10.76 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 10.76 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 10.76 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 10.76 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 10.76 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 10.76 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 10.76 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 10.76 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 10.76 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 3.7565
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.7218 | 652.8006 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_1_COOLC DXCOIL | 171.9399 | 154.7795 | 152.4872 | 143.632 | 140.4 | 132.4676 | 109.1508 | 141.145 | 125.1774 | 116.4154 | 142.4152 | 119.5848 | 138.6839 | 115.9516 | 126.1089 | 126.6364
| VAV_2_COOLC DXCOIL | 172.1953 | 152.7247 | 163.8381 | 146.4557 | 142.5388 | 143.4752 | 124.8882 | 143.8637 | 136.99 | 131.2215 | 146.1537 | 131.8772 | 143.8392 | 130.2098 | 134.9113 | 153.7953
| VAV_3_COOLC DXCOIL | 188.6261 | 168.717 | 168.9337 | 159.0738 | 155.3602 | 145.2318 | 127.1501 | 152.7481 | 136.9864 | 130.1207 | 145.2154 | 125.4055 | 142.5781 | 122.3591 | 128.5054 | 144.336
Heating (kW)
| VAV_1_HEATC | 4.6586 | 20.2279 | 11.9985 | 26.3316 | 6.784 | 17.7838 | 13.7705 | 32.585 | 23.6636 | 23.174 | 44.4857 | 34.7112 | 51.2548 | 47.1572 | 53.8754 | 72.7482
| VAV_2_HEATC | 4.2973 | 19.7654 | 10.4463 | 25.693 | 6.3988 | 16.2394 | 12.2892 | 31.7506 | 22.7501 | 21.8014 | 43.5081 | 33.7632 | 50.23 | 45.9967 | 52.3105 | 70.2427
| VAV_3_HEATC | 3.1103 | 19.0183 | 9.9324 | 24.8787 | 5.4074 | 16.0932 | 12.0771 | 31.5503 | 22.7484 | 21.9031 | 43.6039 | 34.2588 | 50.3748 | 46.6305 | 52.96 | 71.104
HVAC Efficiency
Air Conditioning (COP)
| VAV_1_COOLC DXCOIL | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| VAV_2_COOLC DXCOIL | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| VAV_3_COOLC DXCOIL | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Heating Efficiency (%)
| VAV_1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| VAV_2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| VAV_3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 8.28 | 7.27 | 7.68 | 7.01 | 8.11 | 7.34 | 6.59 | 6.74 | 7.56 | 7.03 | 6.9 | 7.22 | 6.88 | 7 | 6.99 | 7.65
| VAV_2_FAN | 8.51 | 7.56 | 8.72 | 7.43 | 8.36 | 8.41 | 7.54 | 7.28 | 8.28 | 7.93 | 7.54 | 7.97 | 7.56 | 7.87 | 8.05 | 9.29
| VAV_3_FAN | 9.27 | 8.05 | 9.06 | 7.98 | 9 | 8.51 | 7.68 | 7.4 | 8.28 | 7.86 | 7.47 | 7.58 | 7.46 | 7.39 | 7.6 | 8.72
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.086781 | 0.11552 | 0.094813 | 0.09785 | 0.12904 | 0.10159 | 0.14681 | 0.078593 | 0.037146 | 0.078836 | 0.088041 | 0.037147 | 0.061716 | 0.0798 | 0.061359 | 0.10086
| Total Cost ($/m2) | 17.93 | 22.59 | 19.16 | 18.21 | 22.02 | 19.59 | 23.31 | 14.85 | 6.57 | 13.85 | 17.01 | 6.54 | 12.28 | 14.72 | 12.5 | 25.08
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011454 | 0.0081465 | 0.0085512 | 0.0099677 | 0.0083942 | 0.0080263 | 0.0084611 | 0.0097494 | 0.0069708 | 0.0083698 | 0.0083025 | 0.0069016 | 0.0079565 | 0.007995 | 0.0079132 | 0.004095
| Total Cost ($/m2) | 0.05 | 0.07 | 0.05 | 0.16 | 0.05 | 0.06 | 0.06 | 0.31 | 0.12 | 0.11 | 0.44 | 0.23 | 0.73 | 0.47 | 0.86 | 0.87
Total Utility Costs
| Cost Intensity ($/m2) | 17.98 | 22.66 | 19.2 | 18.37 | 22.07 | 19.65 | 23.38 | 15.15 | 6.69 | 13.96 | 17.45 | 6.77 | 13.01 | 15.19 | 13.36 | 25.95
Energy - End Uses
Electricity (kWh)
| Heating | 15858.3333 | 68258.3333 | 62336.1111 | 108008.3333 | 64258.3333 | 85680.5556 | 89841.6667 | 156075 | 112050 | 177663.8889 | 215697.2222 | 146411.1111 | 255519.4444 | 213811.1111 | 316416.6667 | 549708.3333
| Cooling | 345730.5556 | 244022.2222 | 275666.6667 | 158980.5556 | 125150 | 207800 | 45094.4444 | 126166.6667 | 105050 | 39541.6667 | 86750 | 69297.2222 | 75663.8889 | 45050 | 37911.1111 | 24447.2222
| Interior Lighting | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889
| Exterior Lighting | 77844.4444 | 77813.8889 | 77800 | 77786.1111 | 77727.7778 | 77708.3333 | 77750 | 77702.7778 | 77733.3333 | 77577.7778 | 77716.6667 | 77672.2222 | 77663.8889 | 77647.2222 | 77602.7778 | 77127.7778
| Interior Equipment | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 29280.5556 | 23561.1111 | 30277.7778 | 21702.7778 | 22305.5556 | 28933.3333 | 17780.5556 | 20722.2222 | 25661.1111 | 19622.2222 | 21491.6667 | 22869.4444 | 22041.6667 | 21927.7778 | 22716.6667 | 27138.8889
| Pumps | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1029380.5556 | 974325 | 1006747.2222 | 927147.2222 | 850108.3333 | 960791.6667 | 791136.1111 | 941336.1111 | 881163.8889 | 875075 | 962325 | 876916.6667 | 991555.5556 | 919102.7778 | 1015316.6667 | 1239091.6667
Gas (MJ)
| Heating | 30 | 16090 | 1880 | 49880 | 100 | 6430 | 3390 | 121630 | 48700 | 28740 | 227890 | 129820 | 416260 | 253610 | 498180 | 1007350
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 23290 | 27320 | 24990 | 31210 | 30470 | 27790 | 33800 | 34280 | 33700 | 35880 | 36970 | 36830 | 39290 | 39710 | 43120 | 47760
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 23320 | 43410 | 26870 | 81090 | 30570 | 34220 | 37190 | 155910 | 82400 | 64610 | 264860 | 166650 | 455550 | 293320 | 541300 | 1055110
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3729090 | 3550980 | 3651160 | 3418820 | 3090960 | 3493070 | 2885290 | 3544710 | 3254580 | 3214890 | 3729220 | 3323550 | 4025150 | 3602090 | 4196440 | 5515840
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 11.4588 | 49.3217 | 45.0424 | 78.044 | 46.4314 | 61.9105 | 64.9172 | 112.7757 | 80.9644 | 128.3753 | 155.8572 | 105.7928 | 184.6317 | 154.4943 | 228.6344 | 397.2048
| Cooling (elec) | 249.8158 | 176.3241 | 199.1895 | 114.8752 | 90.4301 | 150.1508 | 32.5841 | 91.1647 | 75.9064 | 28.5718 | 62.6833 | 50.0724 | 54.6727 | 32.552 | 27.3936 | 17.6649
| Interior Lighting (elec) | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044
| Exterior Lighting (elec) | 56.2484 | 56.2263 | 56.2162 | 56.2062 | 56.1641 | 56.15 | 56.1801 | 56.146 | 56.1681 | 56.0557 | 56.156 | 56.1239 | 56.1179 | 56.1058 | 56.0737 | 55.7305
| Interior Equipment (elec) | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 21.1574 | 17.0246 | 21.8779 | 15.6819 | 16.1174 | 20.9065 | 12.8478 | 14.9733 | 18.542 | 14.1785 | 15.5293 | 16.5249 | 15.9267 | 15.8444 | 16.4145 | 19.6099
| Pumps (elec) | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 743.8034 | 704.0217 | 727.4492 | 669.9323 | 614.266 | 694.2429 | 571.6542 | 680.1848 | 636.7059 | 632.3063 | 695.3508 | 633.637 | 716.4721 | 664.1196 | 733.6412 | 895.3352
Gas (MJ/m2)
| Heating (gas) | 0.0060214 | 3.2295 | 0.37734 | 10.0117 | 0.020071 | 1.2906 | 0.68042 | 24.413 | 9.7748 | 5.7685 | 45.7409 | 26.0568 | 83.5496 | 50.9033 | 99.9922 | 202.1902
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 4.6747 | 5.4835 | 5.0159 | 6.2643 | 6.1158 | 5.5779 | 6.7842 | 6.8805 | 6.7641 | 7.2017 | 7.4204 | 7.3923 | 7.8861 | 7.9704 | 8.6548 | 9.5861
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4.6807 | 8.713 | 5.3932 | 16.276 | 6.1359 | 6.8685 | 7.4646 | 31.2935 | 16.5389 | 12.9682 | 53.1614 | 33.4491 | 91.4357 | 58.8737 | 108.647 | 211.7763
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 748.4841 | 712.7348 | 732.8424 | 686.2083 | 620.4019 | 701.1114 | 579.1208 | 711.4763 | 653.2429 | 645.2765 | 748.5102 | 667.0862 | 807.9078 | 722.9933 | 842.2882 | 1107.1115
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 258.5237 | 315.099 | 320.162 | 367.6289 | 266.4917 | 336.8868 | 322.6871 | 343.9655 | 318.7033 | 347.7834 | 361.1802 | 340.6874 | 383.2134 | 370.24 | 380.032 | 489.1572
| Feb | 242.3013 | 291.3525 | 270.574 | 297.8492 | 264.231 | 281.4819 | 213.2715 | 320.0053 | 288.2896 | 295.5466 | 310.476 | 288.9248 | 326.9419 | 326.5807 | 344.7195 | 420.6106
| Mar | 244.9096 | 264.74 | 244.4388 | 293.2503 | 214.127 | 277.1377 | 238.9975 | 295.5347 | 267.0188 | 304.7979 | 291.3385 | 274.9581 | 319.2087 | 311.0257 | 321.7798 | 398.7194
| Apr | 257.0806 | 225.0189 | 245.8936 | 259.1443 | 223.9313 | 238.9151 | 232.4812 | 282.448 | 217.2158 | 288.2511 | 281.8583 | 241.2522 | 285.5934 | 250.2997 | 301.1563 | 362.9167
| May | 274.6429 | 271.2641 | 286.1603 | 231.9989 | 208.3334 | 276.4678 | 187.5229 | 212.5533 | 238.3628 | 210.6914 | 216.1214 | 218.1894 | 212.0155 | 197.8812 | 274.3847 | 287.1118
| Jun | 295.5239 | 273.8668 | 381.4493 | 252.7004 | 209.3416 | 376.936 | 192.1408 | 268.7607 | 266.3466 | 197.8805 | 257.6405 | 241.0546 | 250.9874 | 232.2165 | 218.4408 | 209.0419
| Jul | 284.3123 | 283.2431 | 354.1623 | 285.5399 | 217.8696 | 340.67 | 207.6823 | 276.7385 | 294.7124 | 212.5868 | 263.7121 | 259.3004 | 251.8897 | 244.634 | 239.7407 | 211.5779
| Aug | 298.2175 | 285.0822 | 361.2415 | 256.1864 | 258.0908 | 322.122 | 196.0097 | 278.2492 | 263.1254 | 208.47 | 260.9485 | 253.1983 | 248.0697 | 232.1131 | 226.638 | 243.5177
| Sep | 285.5345 | 271.134 | 306.1583 | 237.3934 | 244.3826 | 316.6381 | 243.2414 | 230.8895 | 231.8042 | 220.7299 | 218.9209 | 228.7899 | 215.853 | 208.2983 | 218.1967 | 313.0917
| Oct | 278.3263 | 242.137 | 250.9421 | 213.7769 | 225.8245 | 245.8989 | 196.0885 | 276.5907 | 242.7248 | 287.499 | 264.29 | 244.5907 | 282.985 | 265.646 | 289.2727 | 375.5899
| Nov | 249.9948 | 242.947 | 220.6911 | 270.6593 | 214.6757 | 280.9302 | 229.4969 | 292.2784 | 278.7461 | 292.087 | 293.5211 | 260.507 | 318.8366 | 285.314 | 333.5753 | 406.5419
| Dec | 228.189 | 313.5022 | 330.1784 | 309.0623 | 267.7721 | 301.2975 | 289.7766 | 307.6365 | 300.5178 | 309.8576 | 332.5695 | 315.9495 | 327.308 | 347.2127 | 339.5393 | 406.2672
Time of Peak Electrical Demand
| Jan | 02-JAN-06:10 | 17-JAN-06:10 | 02-JAN-06:10 | 02-JAN-08:09 | 02-JAN-06:10 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09
| Feb | 22-FEB-16:10 | 06-FEB-06:10 | 23-FEB-06:10 | 13-FEB-06:10 | 21-FEB-06:10 | 06-FEB-06:10 | 27-FEB-06:10 | 21-FEB-08:09 | 06-FEB-08:09 | 13-FEB-06:10 | 06-FEB-08:09 | 21-FEB-08:09 | 06-FEB-08:09 | 27-FEB-08:09 | 06-FEB-08:09 | 06-FEB-08:09
| Mar | 27-MAR-15:09 | 20-MAR-05:10 | 17-MAR-15:30 | 13-MAR-05:10 | 22-MAR-05:10 | 06-MAR-06:10 | 06-MAR-06:10 | 13-MAR-05:10 | 13-MAR-07:10 | 20-MAR-05:10 | 20-MAR-05:10 | 06-MAR-08:09 | 06-MAR-08:09 | 06-MAR-08:09 | 27-MAR-07:10 | 13-MAR-07:10
| Apr | 03-APR-15:09 | 21-APR-15:30 | 26-APR-15:00 | 03-APR-05:10 | 24-APR-05:10 | 21-APR-15:20 | 24-APR-05:10 | 17-APR-05:10 | 21-APR-15:00 | 03-APR-05:10 | 03-APR-05:10 | 03-APR-05:10 | 24-APR-05:10 | 03-APR-05:10 | 03-APR-05:10 | 10-APR-05:10
| May | 24-MAY-14:00 | 18-MAY-15:30 | 30-MAY-15:00 | 31-MAY-15:00 | 30-MAY-07:00 | 31-MAY-15:00 | 01-MAY-07:10 | 31-MAY-15:00 | 31-MAY-15:00 | 18-MAY-07:10 | 01-MAY-05:10 | 23-MAY-15:00 | 31-MAY-12:09 | 08-MAY-07:10 | 01-MAY-05:10 | 01-MAY-05:10
| Jun | 28-JUN-15:09 | 13-JUN-15:30 | 08-JUN-15:00 | 19-JUN-15:39 | 28-JUN-12:00 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 20-JUN-15:00 | 28-JUN-15:09 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 13-JUL-15:20 | 05-JUL-15:00 | 11-JUL-15:50 | 03-JUL-15:00 | 20-JUL-15:09 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:00 | 24-JUL-15:09 | 13-JUL-15:09 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 11-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 01-AUG-15:00 | 18-AUG-15:00 | 08-AUG-15:39 | 04-AUG-15:20 | 15-AUG-12:20 | 17-AUG-15:00 | 01-AUG-15:20 | 18-AUG-15:00 | 04-AUG-15:50 | 29-AUG-15:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 28-AUG-05:10
| Sep | 11-SEP-15:09 | 15-SEP-15:09 | 12-SEP-15:30 | 11-SEP-12:00 | 25-SEP-15:09 | 01-SEP-15:09 | 28-SEP-15:09 | 08-SEP-15:00 | 20-SEP-15:30 | 25-SEP-07:10 | 06-SEP-15:09 | 06-SEP-15:09 | 14-SEP-15:09 | 01-SEP-15:00 | 18-SEP-05:10 | 25-SEP-05:10
| Oct | 06-OCT-15:20 | 06-OCT-15:00 | 02-OCT-15:09 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:09 | 10-OCT-07:10 | 30-OCT-05:10 | 30-OCT-05:10 | 30-OCT-05:10 | 02-OCT-05:10 | 10-OCT-05:10 | 16-OCT-05:10 | 16-OCT-05:10 | 30-OCT-05:10 | 30-OCT-07:10
| Nov | 07-NOV-14:00 | 06-NOV-06:10 | 13-NOV-13:00 | 15-NOV-06:10 | 15-NOV-08:09 | 27-NOV-06:10 | 27-NOV-06:10 | 20-NOV-06:10 | 20-NOV-06:10 | 27-NOV-06:10 | 20-NOV-06:10 | 24-NOV-06:10 | 27-NOV-08:09 | 27-NOV-08:09 | 27-NOV-08:09 | 06-NOV-08:09
| Dec | 19-DEC-13:00 | 11-DEC-06:10 | 26-DEC-06:10 | 18-DEC-06:10 | 11-DEC-06:10 | 26-DEC-06:10 | 26-DEC-06:10 | 26-DEC-08:09 | 26-DEC-08:09 | 11-DEC-06:10 | 26-DEC-08:09 | 11-DEC-08:09 | 11-DEC-08:09 | 18-DEC-08:09 | 11-DEC-08:09 | 26-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 12317.52 | 12786.89 | 11492.98 | 11316.66 | 9505.3 | 12409.68 | 8855.47 | 12288.63 | 10615.3 | 5558.34 | 12573.86 | 10656.58 | 12766.18 | 11821.6 | 13153.82 | 17085.9
| Total Source Energy (MJ/m2) | 2472.31 | 2566.52 | 2306.82 | 2271.42 | 1907.86 | 2490.81 | 1777.43 | 2466.51 | 2130.65 | 1115.64 | 2523.76 | 2138.94 | 2562.37 | 2372.77 | 2640.17 | 3429.4
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
| Total Building | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
Emissions
| Carbon Equivalent (kg) | 282728.1445 | 325779.468 | 304397.1559 | 287057.2658 | 99899.9627 | 324668.2593 | 93127.6122 | 256835.9646 | 361439.2828 | 64900.5601 | 517838.333 | 361223.8334 | 347617.3937 | 341164.077 | 357296.949 | 367690.9119
| CO2 (kg) | 654913.4307 | 817771.4402 | 716110.7093 | 652411.2021 | 266836.971 | 769302.0322 | 248782.1524 | 577781.4041 | 843019.3563 | 154768.5966 | 1197570 | 843366.7807 | 806190.7166 | 796482.89 | 829408.641 | 928381.5382
| NOX (kg) | 1153.9693 | 1073.9664 | 1209.2482 | 1255.4828 | 228.4353 | 1260.2947 | 213.0024 | 1146.3528 | 1475.4753 | 246.3204 | 2168.0562 | 1472.3684 | 1449.3879 | 1400.58 | 1487.6598 | 1144.123
| SO2 (kg) | 4406.1717 | 4647.5407 | 4048.3439 | 3254.3042 | 2473.7255 | 5285.1346 | 2302.1246 | 3436.2933 | 3847.886 | 676.3812 | 6485.3642 | 3829.3641 | 2340.3523 | 2454.1941 | 2396.4552 | 6307.7512
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0201 | 0.0131 | 0.011 | 0.0119 | 0.0011 | 0.0099 | 0.001 | 0.0139 | 0.015 | 0.0026 | 0.0196 | 0.0149 | 0.0171 | 0.017 | 0.0175 | 0.0214
| Water for Electricity (m3) | 545.3232 | 1585.34 | 29904.9 | 5788.73 | 14926 | 26358.4 | 13890.6 | 213.7186 | 4001.19 | 8940.48 | 1492.99 | 3981.9 | 1538.34 | 58219.8 | 1575.2 | 1265.95

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 54.5 | 2841.79
|  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | 10.2
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 11.3 | 60.8 | 3170.29
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 15 | 83.75 | 4366.96
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.75
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
|  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
|  |  | WinterDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
|  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600