## BuildingSummary
Building Summary Quick Service Restaurant post-1980 construction
|  | Value | Data Source
Program
| Building Name | Reference Building Quick Service Post-1980 Construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Service
Form |  |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991 for all Form parameters
| Total Floor Area (m2) | 232.2
| Building Shape | Rectangle
| Aspect Ratio | 1
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.28
| East | 0.14
| North | 0
| West | 0.14
| Total | 0.14
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 2 zones plus attic
| Floor to Ceiling Height (m) | 3.048
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Wood-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 185.9
| Net Dimensions - Total Area (m2) | 159.9
| Wall to Skin Ratio | 0.418
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 258.86
| Net Dimensions - Total Area (m2) | 258.86
| Roof to Skin Ratio | 0.582
| Window Dimensions (m2) |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991
| South | 13.01
| East | 6.51
| North | 0
| West | 6.51
| Total Area (m2) | 26.03
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4-in slab-on-grade
| Dimensions - Total Area (m2) | 232.2
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 2.41 | See Reference Buildings Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 414.19

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Dining | Yes | 1 | 116.1289 | 354.1871 | 3.0499 | 92.9401 | 26.02 | 1.3935 | 83.3333 | 15.4586 | 129.1668 |  |  | 10 |  | 833.3333 |  | 2.4091
Kitchen | Yes | 1 | 116.1289 | 354.1871 | 3.0499 | 92.9401 | 0 | 18.5806 | 6.25 | 16.6478 | 301.3892 | 1292.1384 | 151.416 | 8 |  | 50 | 1557.4251 | 2.4091
Attic | No | 1 | 232.2578 | 262.3272 | 1.1295 | 0 | 0 | [10 empty] | 1
Total Conditioned Zones |  |  | 232.2578 | 708.3742 |  | 185.8802 | 26.02 |  | 89.5833
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed | Wood-Framed
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value attic floor (m2·K / W) | 2.38 | 2.6685 | 3.8287 | 2.4461 | 1.7612 | 3.6691 | 2.0013 | 3.0365 | 2.9851 | 2.7518 | 3.323 | 3.4533 | 3.9137 | 3.5943 | 4.403 | 5.6812
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_COOLC DXCOIL | 36.4615 | 32.3677 | 33.7705 | 32.2752 | 32.5868 | 32.9466 | 22.6519 | 29.7931 | 27.1262 | 25.0986 | 29.7933 | 26.0155 | 28.9351 | 21.7576 | 27.6935 | 18.2568
| PSZ-AC_2:2_COOLC DXCOIL | 20.3222 | 17.9406 | 17.9406 | 17.9406 | 17.9406 | 17.9406 | 13.6134 | 17.9406 | 13.702 | 13.8185 | 17.9406 | 13.3887 | 17.9406 | 11.9594 | 11.9594 | 11.9594
Heating (kW)
| PSZ-AC_1:1_HEATC | 46.9004 | 53.4352 | 47.62 | 56.3638 | 45.9408 | 49.3944 | 45.3331 | 59.6263 | 50.8222 | 52.5228 | 68.1156 | 57.3047 | 72.1173 | 66.7557 | 72.3969 | 88.0372
| PSZ-AC_2:2_HEATC | 31.6842 | 36.9256 | 31.1539 | 39.8332 | 29.091 | 33.6782 | 32.1552 | 44.3415 | 35.2317 | 38.3469 | 51.8 | 42.0566 | 55.9806 | 51.0119 | 57.3004 | 70.9575
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67
| PSZ-AC_2:2_COOLC DXCOIL | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
Heating Efficiency (%)
| PSZ-AC_1:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_2:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| DINING EXHAUST FAN | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| KITCHEN EXHAUST FAN | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
| PSZ-AC_1:1_FAN | 1.47 | 1.3 | 1.36 | 1.3 | 1.37 | 1.33 | 1.19 | 1.2 | 1.37 | 1.2 | 1.2 | 1.29 | 1.17 | 1.22 | 1.12 | 1.1
| PSZ-AC_2:2_FAN | 0.82 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.075956 | 0.10538 | 0.098328 | 0.11055 | 0.12545 | 0.094067 | 0.14589 | 0.071083 | 0.037924 | 0.072409 | 0.054282 | 0.037946 | 0.051683 | 0.067869 | 0.050718 | 0.088404
| Total Cost ($/m2) | 73.87 | 95.5 | 91.53 | 94.06 | 102.12 | 83.87 | 115.6 | 59.04 | 31.56 | 57.41 | 44.31 | 30.89 | 41.92 | 54.32 | 40.12 | 69.45
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01147 | 0.0081965 | 0.0085982 | 0.010678 | 0.0084064 | 0.0081468 | 0.0084221 | 0.010015 | 0.0071688 | 0.0083102 | 0.008763 | 0.0071474 | 0.0079487 | 0.008581 | 0.0079342 | 0.0041615
| Total Cost ($/m2) | 30.9 | 25.38 | 25.35 | 37.52 | 24.6 | 25.85 | 28.2 | 41.7 | 26.37 | 32.86 | 42.16 | 30 | 43.72 | 42.61 | 49.39 | 35.69
Total Utility Costs
| Cost Intensity ($/m2) | 104.76 | 120.89 | 116.88 | 131.57 | 126.72 | 109.73 | 143.8 | 100.74 | 57.93 | 90.27 | 86.48 | 60.88 | 85.64 | 96.93 | 89.51 | 105.13
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 37533.3333 | 24711.1111 | 30075 | 12683.3333 | 3541.6667 | 21841.6667 | 850 | 9344.4444 | 8452.7778 | 1252.7778 | 6363.8889 | 5213.8889 | 5463.8889 | 2930.5556 | 1722.2222 | 658.3333
| Interior Lighting | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333 | 24083.3333
| Exterior Lighting | 12955.5556 | 12933.3333 | 12927.7778 | 12950 | 12947.2222 | 12936.1111 | 12922.2222 | 12936.1111 | 12933.3333 | 12913.8889 | 12916.6667 | 12919.4444 | 12927.7778 | 12911.1111 | 12908.3333 | 12830.5556
| Interior Equipment | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 18527.7778 | 16858.3333 | 17319.4444 | 16850 | 17419.4444 | 17047.2222 | 15900 | 16050 | 17408.3333 | 15950 | 16125 | 16863.8889 | 15952.7778 | 16361.1111 | 15630.5556 | 15866.6667
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 19133.3333 | 18272.2222 | 18158.3333 | 17405.5556 | 17430.5556 | 17541.6667 | 16633.3333 | 16852.7778 | 16752.7778 | 16297.2222 | 16472.2222 | 16322.2222 | 16313.8889 | 15952.7778 | 15722.2222 | 15366.6667
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 225947.2222 | 210569.4444 | 216277.7778 | 197686.1111 | 189136.1111 | 207163.8889 | 184102.7778 | 192977.7778 | 193344.4444 | 184211.1111 | 189675 | 189113.8889 | 188455.5556 | 185952.7778 | 183777.7778 | 182522.2222
Gas (MJ)
| Heating | 5600 | 89610 | 60700 | 177310 | 42540 | 106350 | 132890 | 321140 | 209710 | 268510 | 465210 | 322710 | 619720 | 494520 | 779110 | 1314110
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 56340 | 65930 | 60420 | 75170 | 73380 | 67060 | 81280 | 82430 | 81050 | 86210 | 88800 | 88470 | 94310 | 95310 | 103390 | 114380
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 625850 | 719460 | 685030 | 816380 | 679830 | 737320 | 778080 | 967480 | 854670 | 918630 | 1117920 | 975090 | 1277930 | 1153740 | 1446410 | 1992410
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1439260 | 1477510 | 1463630 | 1528050 | 1360720 | 1483110 | 1440850 | 1662200 | 1550720 | 1581790 | 1800760 | 1655910 | 1956370 | 1823170 | 2108010 | 2649480
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 581.5615 | 382.8871 | 465.9981 | 196.5223 | 54.8765 | 338.4264 | 13.1704 | 144.7878 | 130.9719 | 19.4112 | 98.6055 | 80.7868 | 84.6604 | 45.4076 | 26.685 | 10.2006
| Interior Lighting (elec) | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16 | 373.16
| Exterior Lighting (elec) | 200.7403 | 200.396 | 200.3099 | 200.6542 | 200.6112 | 200.439 | 200.2238 | 200.439 | 200.396 | 200.0947 | 200.1377 | 200.1808 | 200.3099 | 200.0516 | 200.0086 | 198.8035
| Interior Equipment (elec) | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 287.0793 | 261.212 | 268.3567 | 261.0829 | 269.9062 | 264.1388 | 246.3631 | 248.6873 | 269.734 | 247.1378 | 249.8494 | 261.2981 | 247.1809 | 253.5078 | 242.1882 | 245.8466
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 296.4621 | 283.1196 | 281.3549 | 269.691 | 270.0783 | 271.7999 | 257.7257 | 261.1259 | 259.5765 | 252.5179 | 255.2294 | 252.9052 | 252.7761 | 247.1809 | 243.6085 | 238.0993
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3500.9469 | 3262.6754 | 3351.1234 | 3063.0541 | 2930.5759 | 3209.9079 | 2852.5867 | 2990.1007 | 2995.782 | 2854.2653 | 2938.9257 | 2930.2316 | 2920.031 | 2881.2516 | 2847.551 | 2828.0968
Gas (MJ/m2)
| Heating (gas) | 24.1026 | 385.6848 | 261.2551 | 763.1488 | 183.0937 | 457.7344 | 571.9635 | 1382.1985 | 902.5996 | 1155.677 | 2002.2811 | 1388.9558 | 2667.2979 | 2128.4325 | 3353.3184 | 5655.9783
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 242.4895 | 283.7652 | 260.0499 | 323.5345 | 315.8302 | 288.6287 | 349.8321 | 354.7818 | 348.8422 | 371.051 | 382.1985 | 380.7782 | 405.9137 | 410.2178 | 444.9944 | 492.2958
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2693.6817 | 3096.5826 | 2948.3946 | 3513.7299 | 2926.0136 | 3173.4527 | 3348.8853 | 4164.0699 | 3678.5315 | 3953.8177 | 4811.5693 | 4196.8236 | 5500.2582 | 4965.7399 | 6225.4024 | 8575.4067
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 6194.6286 | 6359.258 | 6299.5179 | 6576.784 | 5856.5895 | 6383.3606 | 6201.472 | 7154.1706 | 6674.3565 | 6808.083 | 7750.538 | 7127.0982 | 8420.2892 | 7846.9915 | 9072.9534 | 11403.4604
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 36.5378 | 32.9518 | 30.6629 | 28.769 | 31.9538 | 28.6938 | 28.6193 | 28.5196 | 28.6921 | 28.5563 | 28.5197 | 28.7232 | 28.4501 | 28.5605 | 28.3792 | 30.839
| Feb | 37.9527 | 31.6767 | 31.8777 | 29.0575 | 32.6478 | 28.8106 | 28.7646 | 28.5552 | 28.7105 | 28.5499 | 28.5447 | 28.6316 | 28.4662 | 28.5538 | 28.4144 | 28.3486
| Mar | 37.7985 | 33.7867 | 35.8271 | 30.6474 | 31.7283 | 29.4988 | 28.6308 | 30.1897 | 29.1422 | 28.637 | 29.0719 | 30.3596 | 28.5581 | 28.6169 | 28.4052 | 28.3635
| Apr | 38.4686 | 36.8536 | 36.3423 | 31.5641 | 32.933 | 36.2748 | 28.7933 | 30.5863 | 32.154 | 28.5639 | 28.8713 | 30.0348 | 29.8047 | 28.6383 | 28.4376 | 28.3983
| May | 41.4115 | 39.2078 | 42.7104 | 35.498 | 32.9807 | 38.6195 | 29.1463 | 32.982 | 33.9591 | 28.6323 | 32.4977 | 31.9253 | 36.1061 | 29.4518 | 28.7732 | 28.1108
| Jun | 43.3247 | 39.525 | 45.2119 | 37.4188 | 31.406 | 45.3435 | 31.0451 | 39.445 | 36.7265 | 30.6023 | 39.0706 | 36.0939 | 37.2028 | 35.2532 | 31.2999 | 30.19
| Jul | 42.9283 | 41.7859 | 44.3741 | 40.4437 | 34.1187 | 45.1152 | 35.3799 | 41.3394 | 38.0148 | 31.2864 | 40.0379 | 36.1733 | 37.9248 | 35.6069 | 35.4531 | 30.8836
| Aug | 42.1825 | 41.9677 | 44.8724 | 39.0792 | 36.5833 | 42.4828 | 31.2445 | 41.3716 | 35.6475 | 30.9318 | 38.2672 | 36.8229 | 38.7262 | 34.4266 | 33.8701 | 29.4308
| Sep | 42.6806 | 41.461 | 41.9455 | 36.1615 | 39.2037 | 41.2497 | 34.1787 | 34.3273 | 34.6182 | 36.5409 | 34.4784 | 33.9039 | 32.0272 | 32.477 | 30.3128 | 28.4797
| Oct | 42.4574 | 37.5248 | 37.0266 | 33.2478 | 34.8433 | 35.938 | 30.0534 | 33.3615 | 32.3904 | 29.2749 | 30.4824 | 31.4549 | 30.2295 | 29.4544 | 29.4894 | 28.4261
| Nov | 39.2526 | 35.137 | 35.2334 | 29.373 | 32.3109 | 29.172 | 28.7347 | 30.2476 | 28.8084 | 28.6893 | 30.3506 | 28.6275 | 28.6035 | 28.642 | 28.4745 | 28.3689
| Dec | 36.1177 | 34.4765 | 30.3578 | 28.9085 | 32.5099 | 28.7403 | 28.6173 | 28.5557 | 28.6838 | 28.5835 | 28.5892 | 28.5875 | 28.4419 | 28.5537 | 28.3892 | 30.8586
Time of Peak Electrical Demand
| Jan | 23-JAN-11:15 | 03-JAN-12:15 | 28-JAN-17:00 | 24-JAN-06:00 | 26-JAN-12:00 | 03-JAN-06:45 | 06-JAN-06:30 | 06-JAN-06:45 | 20-JAN-06:30 | 10-JAN-06:45 | 17-JAN-06:00 | 24-JAN-06:45 | 31-JAN-06:45 | 10-JAN-06:45 | 17-JAN-06:00 | 01-JAN-11:15
| Feb | 23-FEB-11:15 | 22-FEB-18:15 | 28-FEB-18:30 | 20-FEB-18:30 | 12-FEB-13:00 | 17-FEB-06:30 | 15-FEB-17:45 | 14-FEB-06:00 | 21-FEB-06:45 | 17-FEB-06:45 | 28-FEB-06:30 | 10-FEB-06:45 | 21-FEB-06:00 | 14-FEB-06:00 | 21-FEB-06:00 | 21-FEB-06:45
| Mar | 14-MAR-10:15 | 25-MAR-18:45 | 17-MAR-18:45 | 28-MAR-18:00 | 31-MAR-10:15 | 30-MAR-17:00 | 31-MAR-05:45 | 09-MAR-19:15 | 25-MAR-18:30 | 29-MAR-18:30 | 31-MAR-18:15 | 26-MAR-18:15 | 19-MAR-18:30 | 30-MAR-18:00 | 31-MAR-05:45 | 10-MAR-06:45
| Apr | 17-APR-12:00 | 30-APR-18:00 | 01-APR-16:00 | 15-APR-16:15 | 11-APR-18:30 | 21-APR-18:15 | 29-APR-10:15 | 05-APR-18:30 | 22-APR-18:45 | 21-APR-05:15 | 29-APR-10:15 | 26-APR-18:45 | 02-APR-18:45 | 06-APR-18:00 | 21-APR-05:15 | 14-APR-05:30
| May | 24-MAY-10:15 | 18-MAY-11:15 | 28-MAY-17:15 | 31-MAY-17:30 | 28-MAY-10:15 | 31-MAY-16:15 | 09-MAY-10:15 | 15-MAY-12:00 | 31-MAY-16:45 | 06-MAY-10:15 | 30-MAY-16:30 | 23-MAY-16:00 | 27-MAY-16:15 | 16-MAY-16:00 | 31-MAY-10:15 | 30-MAY-10:15
| Jun | 26-JUN-10:15 | 30-JUN-10:15 | 28-JUN-16:15 | 19-JUN-11:15 | 28-JUN-10:15 | 27-JUN-18:00 | 16-JUN-10:15 | 30-JUN-16:00 | 20-JUN-16:45 | 18-JUN-12:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-11:15 | 30-JUN-16:15 | 14-JUN-16:30 | 20-JUN-17:00
| Jul | 13-JUL-10:15 | 30-JUL-10:15 | 19-JUL-16:00 | 03-JUL-16:15 | 29-JUL-10:15 | 24-JUL-18:00 | 02-JUL-12:00 | 25-JUL-10:15 | 31-JUL-16:15 | 24-JUL-18:15 | 14-JUL-10:15 | 17-JUL-11:15 | 15-JUL-12:00 | 21-JUL-16:00 | 08-JUL-10:15 | 29-JUL-17:45
| Aug | 21-AUG-12:00 | 31-AUG-10:15 | 01-AUG-16:00 | 17-AUG-11:00 | 08-AUG-10:15 | 04-AUG-16:15 | 15-AUG-11:15 | 17-AUG-18:00 | 01-AUG-12:00 | 07-AUG-16:00 | 04-AUG-11:15 | 30-AUG-12:00 | 25-AUG-18:00 | 09-AUG-16:00 | 12-AUG-12:00 | 15-AUG-16:00
| Sep | 10-SEP-10:15 | 16-SEP-10:15 | 09-SEP-18:45 | 11-SEP-12:00 | 24-SEP-10:00 | 01-SEP-11:15 | 28-SEP-16:15 | 05-SEP-10:15 | 02-SEP-18:30 | 02-SEP-16:15 | 06-SEP-11:15 | 02-SEP-12:00 | 13-SEP-18:30 | 01-SEP-16:00 | 08-SEP-18:45 | 19-SEP-05:00
| Oct | 07-OCT-10:15 | 29-OCT-10:15 | 24-OCT-17:45 | 21-OCT-18:15 | 19-OCT-10:00 | 03-OCT-17:30 | 16-OCT-17:30 | 20-OCT-17:30 | 01-OCT-17:00 | 17-OCT-17:30 | 31-OCT-16:45 | 05-OCT-12:00 | 08-OCT-17:45 | 05-OCT-17:00 | 07-OCT-17:45 | 06-OCT-05:45
| Nov | 01-NOV-10:15 | 26-NOV-11:00 | 12-NOV-13:00 | 19-NOV-17:30 | 20-NOV-11:15 | 10-NOV-17:15 | 03-NOV-05:00 | 04-NOV-17:15 | 10-NOV-06:30 | 03-NOV-05:00 | 02-NOV-18:15 | 10-NOV-06:30 | 03-NOV-05:00 | 21-NOV-06:00 | 03-NOV-05:00 | 14-NOV-06:00
| Dec | 16-DEC-11:15 | 02-DEC-11:15 | 11-DEC-17:30 | 26-DEC-06:00 | 19-DEC-12:00 | 05-DEC-11:15 | 15-DEC-06:30 | 08-DEC-06:00 | 08-DEC-06:00 | 05-DEC-06:45 | 12-DEC-06:00 | 26-DEC-06:45 | 26-DEC-06:00 | 29-DEC-06:45 | 26-DEC-06:00 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 3381.51 | 3538.89 | 3210.77 | 3285.54 | 2849.73 | 3472.84 | 2900.94 | 3540.81 | 3242.77 | 2158.37 | 3642.1 | 3323.74 | 3727.29 | 3586.82 | 3853.41 | 4522.79
| Total Source Energy (MJ/m2) | 14553.97 | 15231.33 | 13819.09 | 14140.9 | 12265.17 | 14947.04 | 12485.61 | 15239.57 | 13956.84 | 9289.57 | 15675.53 | 14305.32 | 16042.19 | 15437.6 | 16584.99 | 19465.99
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19
| Total Building | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19
Emissions
| Carbon Equivalent (kg) | 73251.7622 | 83211.6865 | 77641.9806 | 75615.9163 | 34362.7068 | 83166.9485 | 35546.2794 | 69522.3729 | 94393.1746 | 29982.1977 | 121284.7939 | 94836.6268 | 87551.323 | 88759.0309 | 88988.7744 | 87287.6524
| CO2 (kg) | 176092.4112 | 213730.7834 | 189230.1994 | 180739.3034 | 94431.8404 | 203904.8731 | 97980.4088 | 167188.1114 | 228562.1066 | 79731.9759 | 291567.9945 | 230809.445 | 215293.6942 | 218161.9147 | 220381.1864 | 232459.9452
| NOX (kg) | 282.6545 | 265.691 | 291.9095 | 305.49 | 82.6575 | 306.2676 | 85.961 | 279.257 | 363.3201 | 94.6603 | 477.7368 | 361.9514 | 331.821 | 335.1295 | 333.0563 | 255.4217
| SO2 (kg) | 967.3112 | 1004.6119 | 869.8799 | 694.0938 | 550.544 | 1139.7616 | 535.9279 | 704.7046 | 844.5284 | 142.6263 | 1278.5641 | 826.0885 | 445.1257 | 496.8247 | 434.1346 | 929.6395
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0045 | 0.0029 | 0.0024 | 0.0026 | 0.0003 | 0.0022 | 0.0003 | 0.0029 | 0.0034 | 0.0007 | 0.004 | 0.0033 | 0.0034 | 0.0036 | 0.0033 | 0.0034
| Water for Electricity (m3) | 119.6972 | 342.6221 | 6424.4 | 1234.27 | 3320.8 | 5683.32 | 3232.45 | 43.8132 | 877.9411 | 1882.04 | 294.271 | 858.7329 | 292.3761 | 11779 | 285.1215 | 186.4782

## Picture
DOE Commercial Building Benchmark - Quick Service Restaurant

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 24 | 1251.43
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 6
BLDG_LIGHT_SCH | Fraction | Through 12/31 | SummerDesign | [24 empty] | 24 | 35.4 | 1845.86 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 17.7
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.3 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | 7.55 | 44.5 | 2320.36
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.2 | 0.45 | 0.6 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | 6.75
GAS_EQUIP_SCH | Fraction | Through 12/31 | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 0 | 0
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.09 | 0.14 | 0.1 | 0.1 | 0.22 | 0.27 | 0.24 | 0.21 | 0.14 | 0.13 | 0.15 | 0.17 | 0.17 | 0.17 | 0.15 | 0.14 | 0.12 | 0.02 | 2.86
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5 | 101.5 | 5292.5
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
Kitchen_Exhaust_SCH | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456
|  |  | Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
CLGSETP_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 600
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482.4
HVACOperationSchd | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
MinOA_Sched | Fraction | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 7.75 | 52.65 | 2745.32
|  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 7.45
|  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 6.45
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600