## BuildingSummary
Building Summary Small Hotel pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Small Hotel Reference Building pre-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 4013.63 | PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings
| Building Shape | Rectangle
| Aspect Ratio | 3
| Number of Floors | 4
Window Fraction (Window to Wall Ratio)
| South | 0.1524
| East | 0.0313
| North | 0.1139
| West | 0.0395
| Total | 0.1087
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor plus attic
| Floor to Ceiling Height (m) | 3.35 1st floor, 2.74 upper floors
| Floor to Floor Height (m) | 3.35 1st floor, 2.74 upper floors
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1694.66
| Net Dimensions - Total Area (m2) | 1510.43
| Wall to Skin Ratio | 0.6
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1003.3894
| Net Dimensions - Total Area (m2) | 1003.3894
| Roof to Skin Ratio | 0.4
Window Dimensions (m2)
| South | 96.83
| East | 6.62
| North | 72.38
| West | 8.38
| Total Area (m2) | 184.21
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
Dimensions - Total Area (m2)
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.95 | See Reference Building Technical Report
HVAC
| System Type | PTAC | 2003 CBECS
| Heating Type | Unit heater, PTAC electric heat | 2003 CBECS
| Cooling Type | DX | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 3470.09

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 9.9549 | 0 |  |  |  |  | 0 |  | 2.1693
CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 9.5035 | 0 |  |  |  | 0.25 | 37.6275 |  | 0.26448
REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 4.9774 | 0 |  |  |  |  | 0 |  | 2.1693
FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.0201 | 14.83 | 3.0937 | 52.7076 | 14.1516 | 15.4389 |  |  | 8 |  | 421.6604 |  | 0.7019
RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 11.8232 | 10.767 |  |  |  |  | 0 | 188.7788 | 0.49608
MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.8581 | 43.2009 | 22.9155 | 12.9047 |  |  | 10 |  | 432.0091 |  | 0.49588
MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 10.3453 | 0 |  |  |  | 0.25 | 8.1525 |  | 0.49608
GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613
GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613
EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 3.0937 | 10.5409 | 17.7339 | 77.1847 |  |  | 8 |  | 84.3269 |  | 0.49613
LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 9.2903 | 10.5303 | 11.1826 | 21.8747 | 184.3145 | 255.5145 | 13 |  | 136.8942 |  | 0.496
ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.4161 |  |  |  | 5 | 75.25 |  | 0.49582
EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 3.0937 | 10.5409 | 14.7782 | 11.5041 |  |  | 10 |  | 105.4086 |  | 0.49613
FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.0064 | 10.0289 | 21.6803 | 12.9047 |  |  | 10 |  | 100.2888 |  | 0.49593
FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 9.9528 | 0 |  |  |  |  | 0 |  | 2.1699
FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 5.7543 | 0 |  |  |  |  | 0 |  | 0.49598
REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697
CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816
REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261
GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594
GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591
GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693
REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697
CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816
REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261
GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594
GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591
GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693
REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 4.3874 | 0 |  |  |  |  | 0 |  | 3.6574
CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 1.706
REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 3.6567
GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 3.0138
GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 1.9838
GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9837
GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 1.9838
GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 1.9832
FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 3.6573
ATTIC | No | 1 | 1092.62 | 1582.44 | 1.4483 | 0 | 0 | [8 empty] | 0 |  | 1
Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541
Data Source | [7 empty] | 1 |  | 2 | 4 |  | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value attic floor (m2·K / W) | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 2.0492 | 1.9802 | 2.0704 | 2.5 | 2.3697 | 2.994 | 2.994 | 2.9326 | 2.994
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| CORRIDORFLR1 PTAC DXCOIL | 10.3264 | 10.383 | 10.4105 | 10.6061 | 9.2966 | 10.0868 | 8.0209 | 9.9477 | 10.5683 | 8.7762 | 9.3829 | 9.8597 | 9.3947 | 9.3987 | 8.4228 | 7.2015
| CORRIDORFLR2 PTAC DXCOIL | 5.8807 | 5.9477 | 6.5338 | 6.0652 | 5.3265 | 6.5374 | 5.125 | 5.7194 | 6.2551 | 5.4277 | 5.3395 | 5.6749 | 5.2892 | 5.4429 | 4.9639 | 4.6262
| CORRIDORFLR3 PTAC DXCOIL | 5.5806 | 5.6507 | 6.2322 | 5.6803 | 4.8921 | 6.2009 | 4.74 | 5.3261 | 5.7731 | 5.0382 | 4.9665 | 5.2032 | 4.9074 | 5.0126 | 4.602 | 4.321
| CORRIDORFLR4 PTAC DXCOIL | 7.0569 | 7.3907 | 8.4179 | 7.491 | 6.0509 | 8.1218 | 5.6692 | 6.6831 | 7.1457 | 6.004 | 5.9323 | 6.0903 | 5.4985 | 5.4784 | 5.0686 | 4.6142
| EMPLOYEELOUNGEFLR1 PTAC DXCOIL | 7.8002 | 7.69 | 7.1093 | 7.1783 | 5.6732 | 6.3282 | 5.0843 | 7.0771 | 6.5475 | 5.3312 | 7.5533 | 6.344 | 7.2631 | 6.0088 | 6.1271 | 5.0248
| EXERCISECENTERFLR1 PTAC DXCOIL | 3.9425 | 3.9194 | 3.9871 | 4.0368 | 3.1734 | 3.9795 | 1.9905 | 3.7086 | 3.0094 | 2.4811 | 3.5879 | 2.8931 | 3.6249 | 2.455 | 3.1098 | 1.9652
| FRONTLOUNGEFLR1 PTAC DXCOIL | 22.5281 | 24.1166 | 26.1654 | 25.36 | 19.8554 | 23.8905 | 17.8153 | 25.0463 | 18.3019 | 18.7079 | 22.2867 | 16.9851 | 22.4304 | 15.6762 | 19.6683 | 14.5728
| FRONTOFFICEFLR1 PTAC DXCOIL | 11.0552 | 10.815 | 9.9582 | 10.0079 | 7.2674 | 8.6744 | 5.8929 | 9.6788 | 8.4907 | 6.6426 | 9.8239 | 7.7248 | 9.3865 | 7.3354 | 7.3712 | 5.4021
| GUESTROOM101 PTAC DXCOIL | 2.3981 | 2.5563 | 2.5429 | 2.4996 | 2.3039 | 2.3662 | 2.4287 | 2.5163 | 2.3273 | 2.4271 | 2.3096 | 2.1294 | 2.2554 | 2.1352 | 1.8795 | 1.9222
| GUESTROOM102 PTAC DXCOIL | 2.4567 | 2.6173 | 2.6131 | 2.5619 | 2.3781 | 2.4513 | 2.5076 | 2.5793 | 2.4074 | 2.5108 | 2.364 | 2.1971 | 2.3104 | 2.2053 | 1.945 | 1.9946
| GUESTROOM103 PTAC DXCOIL | 2.6286 | 2.795 | 2.8474 | 2.7335 | 2.4834 | 2.6732 | 2.5245 | 2.7027 | 2.4607 | 2.577 | 2.4742 | 2.2104 | 2.4119 | 2.2308 | 1.9745 | 1.9851
| GUESTROOM104 PTAC DXCOIL | 2.5901 | 2.5508 | 2.4434 | 2.3783 | 1.8075 | 2.3631 | 1.4507 | 2.252 | 2.1417 | 1.6902 | 2.237 | 1.8953 | 2.1406 | 1.8118 | 1.6426 | 1.5116
| GUESTROOM105 PTAC DXCOIL | 2.5362 | 2.4933 | 2.3268 | 2.3294 | 1.8712 | 2.2705 | 1.5862 | 2.2398 | 2.2627 | 1.7685 | 2.2326 | 2.0561 | 2.1464 | 1.9501 | 1.7336 | 1.4574
| GUESTROOM201 PTAC DXCOIL | 4.1068 | 4.2297 | 4.5362 | 4.096 | 3.6986 | 4.5594 | 3.8653 | 3.7935 | 3.9964 | 3.7104 | 3.5847 | 3.6449 | 3.372 | 3.4488 | 3.0703 | 2.8915
| GUESTROOM202_205 PTAC DXCOIL | 10.0189 | 10.7961 | 11.3711 | 10.6608 | 10.1176 | 11.1935 | 11.4346 | 10.8062 | 11.0294 | 11.3451 | 10.0687 | 10.2737 | 9.8947 | 10.2922 | 9.3053 | 10.0356
| GUESTROOM206_208 PTAC DXCOIL | 8.0175 | 8.6689 | 9.1863 | 8.6002 | 8.3449 | 9.1717 | 9.5569 | 8.766 | 9.0511 | 9.4815 | 8.0571 | 8.317 | 7.9486 | 8.3905 | 7.587 | 8.319
| GUESTROOM209_212 PTAC DXCOIL | 9.8536 | 10.6209 | 11.1714 | 10.4821 | 9.9012 | 10.9432 | 11.1906 | 10.6251 | 10.7917 | 11.0929 | 9.9072 | 10.0581 | 9.7339 | 10.0784 | 9.107 | 9.8104
| GUESTROOM213 PTAC DXCOIL | 2.7352 | 2.9464 | 3.1773 | 2.9101 | 2.719 | 3.1471 | 2.9764 | 2.9081 | 2.9132 | 3.0099 | 2.7046 | 2.6745 | 2.649 | 2.6963 | 2.4539 | 2.6102
| GUESTROOM214 PTAC DXCOIL | 2.7927 | 2.7742 | 2.9874 | 2.7056 | 2.1459 | 2.9544 | 1.9746 | 2.5304 | 2.7026 | 2.1855 | 2.4051 | 2.4361 | 2.4387 | 2.3492 | 2.1473 | 1.9522
| GUESTROOM215_218 PTAC DXCOIL | 10.4472 | 10.3361 | 10.502 | 9.884 | 8.3526 | 10.6249 | 7.995 | 9.5996 | 10.5919 | 8.54 | 9.6904 | 9.8857 | 9.3687 | 9.4529 | 8.5716 | 7.9791
| GUESTROOM219 PTAC DXCOIL | 3.0051 | 2.9782 | 3.1677 | 2.9982 | 2.5756 | 3.2028 | 2.4699 | 2.8332 | 3.2309 | 2.6311 | 2.837 | 3.0572 | 2.7504 | 2.9207 | 2.6528 | 2.51
| GUESTROOM220_223 PTAC DXCOIL | 9.9821 | 9.8711 | 9.8783 | 9.3704 | 7.7568 | 9.9709 | 7.3813 | 9.1375 | 9.8541 | 7.9218 | 9.1733 | 9.1348 | 8.8784 | 8.7399 | 7.9223 | 7.349
| GUESTROOM224 PTAC DXCOIL | 2.7415 | 2.7118 | 2.8568 | 2.633 | 2.1138 | 2.843 | 1.9649 | 2.4806 | 2.6823 | 2.1474 | 2.3636 | 2.4393 | 2.2967 | 2.3327 | 2.1331 | 1.967
| GUESTROOM301 PTAC DXCOIL | 4.0948 | 4.2084 | 4.5272 | 4.0646 | 3.6326 | 4.5266 | 3.7946 | 3.744 | 3.9432 | 3.6623 | 3.5468 | 3.5993 | 3.3423 | 3.4106 | 3.041 | 2.8822
| GUESTROOM302_305 PTAC DXCOIL | 10.0034 | 10.5676 | 11.4142 | 10.6543 | 10.0432 | 11.2295 | 11.4273 | 10.7832 | 11.0258 | 11.3483 | 10.0943 | 10.3265 | 9.9199 | 10.3607 | 9.3802 | 10.1603
| GUESTROOM306_308 PTAC DXCOIL | 8.0903 | 8.5473 | 9.3266 | 8.689 | 8.4029 | 9.3308 | 9.7084 | 8.8442 | 9.1629 | 9.6417 | 8.1614 | 8.4607 | 8.0543 | 8.5541 | 7.7492 | 8.5557
| GUESTROOM309_312 PTAC DXCOIL | 9.9872 | 10.5507 | 11.3938 | 10.6378 | 10.0262 | 11.203 | 11.4079 | 10.7681 | 11.0034 | 11.3292 | 10.0805 | 10.3038 | 9.9073 | 10.3421 | 9.3644 | 10.1432
| GUESTROOM313 PTAC DXCOIL | 2.7448 | 2.9029 | 3.2205 | 2.9314 | 2.7242 | 3.1949 | 3.0088 | 2.9277 | 2.9404 | 3.0497 | 2.7338 | 2.71 | 2.6774 | 2.7418 | 2.5021 | 2.6821
| GUESTROOM314 PTAC DXCOIL | 2.8228 | 2.8079 | 3.0653 | 2.7539 | 2.173 | 3.033 | 2.0183 | 2.5671 | 2.7509 | 2.2326 | 2.4454 | 2.4805 | 2.4754 | 2.3983 | 2.2029 | 2.0261
| GUESTROOM315_318 PTAC DXCOIL | 10.194 | 10.0968 | 10.2652 | 9.5942 | 8.0075 | 10.3776 | 7.6932 | 9.3596 | 10.1993 | 8.2348 | 9.417 | 9.4777 | 9.1208 | 9.0883 | 8.2679 | 7.7328
| GUESTROOM319 PTAC DXCOIL | 2.6666 | 2.6426 | 2.7399 | 2.5455 | 2.1185 | 2.7622 | 2.0284 | 2.4339 | 2.6951 | 2.1776 | 2.4597 | 2.4989 | 2.3826 | 2.3982 | 2.1837 | 2.0376
| GUESTROOM320_323 PTAC DXCOIL | 10.0908 | 9.9938 | 10.1249 | 9.4935 | 7.888 | 10.2342 | 7.5767 | 9.2606 | 10.046 | 8.1124 | 9.3143 | 9.3281 | 9.0188 | 8.9455 | 8.1378 | 7.607
| GUESTROOM324 PTAC DXCOIL | 2.7516 | 2.731 | 2.9196 | 2.6615 | 2.1203 | 2.9019 | 1.9869 | 2.5013 | 2.7004 | 2.1738 | 2.3874 | 2.4558 | 2.3262 | 2.3527 | 2.1663 | 2.014
| GUESTROOM401 PTAC DXCOIL | 4.3471 | 4.4827 | 4.946 | 4.3943 | 3.7375 | 4.8704 | 3.8156 | 3.8823 | 4.1782 | 3.6772 | 3.6396 | 3.7305 | 3.3329 | 3.4021 | 3.0633 | 3.3365
| GUESTROOM402_405 PTAC DXCOIL | 11.1926 | 11.5678 | 12.0985 | 11.0628 | 9.8632 | 11.9787 | 11.5373 | 10.7683 | 11.2838 | 11.4322 | 10.2316 | 10.4514 | 9.7762 | 9.9655 | 9.1126 | 10.0349
| GUESTROOM406_408 PTAC DXCOIL | 9.0634 | 9.3507 | 9.9388 | 9.0618 | 8.1456 | 9.8405 | 9.7684 | 8.761 | 9.2677 | 9.6715 | 8.2852 | 8.5526 | 7.9323 | 8.1873 | 7.4869 | 8.4746
| GUESTROOM409_412 PTAC DXCOIL | 11.192 | 11.5417 | 12.0699 | 11.0722 | 9.8525 | 11.9413 | 11.5323 | 10.7828 | 11.2518 | 11.4293 | 10.2468 | 10.4246 | 9.7703 | 9.9565 | 9.1054 | 10.0349
| GUESTROOM413 PTAC DXCOIL | 3.0484 | 3.1578 | 3.4821 | 3.0949 | 2.664 | 3.3941 | 3.0425 | 2.9205 | 3.0144 | 3.0728 | 2.7682 | 2.7528 | 2.639 | 2.6533 | 2.4363 | 2.6545
| GUESTROOM414 PTAC DXCOIL | 3.0985 | 3.1488 | 3.58 | 3.1659 | 2.5066 | 3.5015 | 2.2855 | 2.9121 | 3.1034 | 2.5097 | 2.713 | 2.7407 | 2.5949 | 2.5476 | 2.3702 | 2.1486
| GUESTROOM415_418 PTAC DXCOIL | 11.1869 | 11.2922 | 12.0615 | 11.0119 | 9.1779 | 11.9828 | 8.5847 | 10.2824 | 11.3666 | 9.1658 | 9.6578 | 10.26 | 9.1548 | 9.4447 | 8.7259 | 8.1294
| GUESTROOM419 PTAC DXCOIL | 2.904 | 2.9256 | 3.1954 | 2.9 | 2.3891 | 3.1618 | 2.2208 | 2.6741 | 2.9568 | 2.3777 | 2.4805 | 2.6481 | 2.3737 | 2.432 | 2.2485 | 2.0806
| GUESTROOM420_423 PTAC DXCOIL | 11.1166 | 11.2216 | 11.9629 | 10.9196 | 9.0964 | 11.8823 | 8.5096 | 10.2147 | 11.2649 | 9.0848 | 9.5918 | 10.1618 | 9.0683 | 9.352 | 8.6409 | 8.0491
| GUESTROOM424 PTAC DXCOIL | 3.0405 | 3.0684 | 3.4494 | 3.0882 | 2.4547 | 3.3823 | 2.2491 | 2.8353 | 3.0517 | 2.4501 | 2.6399 | 2.7112 | 2.5285 | 2.5124 | 2.3364 | 2.144
| LAUNDRYROOMFLR1 PTAC DXCOIL | 27.9282 | 27.6523 | 27.2934 | 27.0372 | 25.4091 | 27.4894 | 24.1873 | 26.2794 | 30.24 | 25.1107 | 26.0891 | 29.9808 | 26.1958 | 28.3656 | 25.9211 | 24.3898
| MECHANICALROOMFLR1 PTAC DXCOIL | 1.3242 | 1.4373 | 1.381 | 1.3829 | 1.2039 | 1.2375 | 1.2006 | 1.355 | 1.1052 | 1.1764 | 1.2835 | 1.048 | 1.232 | 1.0626 | 0.96483 | 1.1817
| MEETINGROOMFLR1 PTAC DXCOIL | 12.3347 | 12.9707 | 13.7126 | 13.6256 | 12.7625 | 13.9755 | 9.7912 | 13.3718 | 11.8331 | 11.1302 | 12.4611 | 11.4006 | 12.6029 | 9.8861 | 12.0254 | 8.1116
| RESTROOMFLR1 PTAC DXCOIL | 1.6239 | 1.7462 | 1.8267 | 1.8182 | 1.7485 | 1.826 | 1.7345 | 1.7342 | 1.7607 | 1.727 | 1.6599 | 1.696 | 1.6545 | 1.6767 | 1.4648 | 1.3918
Heating (kW)
| CORRIDORFLR1 PTAC HEAT COIL | 1.8478 | 1.9515 | 1.6465 | 2.5962 | 1.8413 | 1.9228 | 1.6994 | 3.0398 | 2.4439 | 2.0267 | 3.9178 | 3.2114 | 4.5912 | 4.3754 | 4.891 | 6.9593
| CORRIDORFLR2 PTAC HEAT COIL | 1.5398 | 1.6346 | 1.3721 | 2.1558 | 1.2812 | 1.529 | 1.4162 | 2.3876 | 1.9055 | 1.6944 | 3.0048 | 2.4746 | 3.4108 | 3.2134 | 3.5745 | 4.7914
| CORRIDORFLR3 PTAC HEAT COIL | 1.2319 | 2.0773 | 1.4499 | 2.5922 | 1.2812 | 1.9183 | 1.4398 | 2.8124 | 2.3225 | 2.1003 | 3.4368 | 2.9001 | 3.8315 | 3.6337 | 4.0032 | 5.2453
| CORRIDORFLR4 PTAC HEAT COIL | 1.9219 | 3.8189 | 2.8833 | 4.5699 | 2.2473 | 3.5907 | 2.8344 | 4.7791 | 4.2527 | 3.6783 | 5.5089 | 5.0226 | 5.8198 | 5.7355 | 6.1401 | 8.0024
| EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | 3.4574 | 4.5642 | 3.8508 | 4.9236 | 3.5958 | 4.1628 | 3.9746 | 5.4808 | 4.3548 | 4.7399 | 6.4028 | 5.1984 | 6.9195 | 6.3053 | 7.0826 | 8.7707
| EXERCISECENTERFLR1 PTAC HEAT COIL | 4.3217 | 5.7052 | 4.8135 | 6.1545 | 4.4948 | 5.2035 | 4.9682 | 6.851 | 5.4435 | 5.9249 | 8.0034 | 6.498 | 8.6494 | 7.8817 | 8.8533 | 10.9634
| FRONTLOUNGEFLR1 PTAC HEAT COIL | 16.6395 | 21.9664 | 18.533 | 23.6961 | 17.3058 | 20.0346 | 19.1286 | 26.378 | 20.9588 | 22.812 | 30.815 | 25.0188 | 33.3019 | 30.7566 | 34.3081 | 44.9394
| FRONTOFFICEFLR1 PTAC HEAT COIL | 3.9288 | 5.9224 | 4.7587 | 7.2113 | 4.0861 | 5.9287 | 4.6389 | 8.0221 | 6.7731 | 6.3216 | 9.8122 | 8.3616 | 10.9368 | 10.3752 | 11.3998 | 14.8785
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 0.1392 | 1.3463 | 0.81589 | 1.8542 | 0.42135 | 1.2745 | 0.77823 | 2.1164 | 1.6722 | 1.4229 | 2.9754 | 2.4394 | 3.4524 | 3.2744 | 3.6473 | 5.1584
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 0.35115 | 1.2993 | 0.79855 | 1.7072 | 0.49073 | 1.1764 | 0.78229 | 1.9043 | 1.524 | 1.3173 | 2.6109 | 2.1596 | 2.9996 | 2.8474 | 3.1542 | 4.3795
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 0.39517 | 1.3402 | 0.83218 | 1.7428 | 0.52367 | 1.2095 | 0.81877 | 1.9393 | 1.5574 | 1.3541 | 2.647 | 2.1941 | 3.0348 | 2.8815 | 3.1905 | 4.416
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.49359 | 1.5348 | 0.99272 | 1.9725 | 0.64645 | 1.3968 | 0.97446 | 2.1787 | 1.7889 | 1.5411 | 2.9137 | 2.4642 | 3.2958 | 3.1576 | 3.4745 | 4.7927
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05597 | 0 | 0.10501 | 0.10129 | 0.1252 | 0.28239
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0.03112 | 0 | 0 | 0 | 0.03816 | 0 | 0 | 0.10932 | 0.07358 | 0.14614 | 0.13792 | 0.15937 | 0.27127
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0.05343 | 0 | 0 | 0 | 0.05945 | 0.02627 | 0 | 0.12844 | 0.09224 | 0.16426 | 0.15584 | 0.17799 | 0.29012
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.12342 | 0.02802 | 0.1992 | 0 | 0.10475 | 0 | 0.20828 | 0.17116 | 0.10127 | 0.292 | 0.25912 | 0.32339 | 0.3253 | 0.35058 | 0.52128
| GUESTROOM101 PTAC HEAT COIL | 0.55632 | 1.1637 | 0.95054 | 1.4295 | 0.73062 | 1.1911 | 0.91477 | 1.5655 | 1.3561 | 1.2371 | 1.8937 | 1.6374 | 2.1135 | 2.0236 | 2.2038 | 2.8757
| GUESTROOM102 PTAC HEAT COIL | 0.55632 | 1.1855 | 0.97048 | 1.4526 | 0.74959 | 1.2123 | 0.93476 | 1.5893 | 1.3794 | 1.2593 | 1.9173 | 1.6605 | 2.138 | 2.0482 | 2.2288 | 2.9025
| GUESTROOM103 PTAC HEAT COIL | 0.72626 | 1.4302 | 1.2019 | 1.7114 | 0.96531 | 1.4585 | 1.1628 | 1.844 | 1.6321 | 1.4976 | 2.1875 | 1.9286 | 2.4136 | 2.3261 | 2.5053 | 3.1959
| GUESTROOM104 PTAC HEAT COIL | 0.71733 | 1.4105 | 1.1879 | 1.6914 | 0.95226 | 1.4458 | 1.1488 | 1.8272 | 1.6113 | 1.4778 | 2.178 | 1.9224 | 2.3999 | 2.3122 | 2.4914 | 3.1825
| GUESTROOM105 PTAC HEAT COIL | 0.55632 | 1.1788 | 0.9697 | 1.4469 | 0.74459 | 1.2138 | 0.93311 | 1.5876 | 1.3731 | 1.2537 | 1.9243 | 1.6702 | 2.1419 | 2.052 | 2.2331 | 2.9113
| GUESTROOM201 PTAC HEAT COIL | 1.2081 | 2.2033 | 1.6761 | 2.6328 | 1.3575 | 2.0691 | 1.6627 | 2.785 | 2.3826 | 2.1861 | 3.3898 | 2.9292 | 3.7484 | 3.5844 | 3.8832 | 4.9909
| GUESTROOM202_205 PTAC HEAT COIL | 2.4048 | 4.4566 | 3.3839 | 5.3422 | 2.7364 | 4.1795 | 3.3721 | 5.8049 | 4.8985 | 4.5759 | 6.9484 | 5.9194 | 7.7165 | 7.3247 | 8.0252 | 10.3172
| GUESTROOM206_208 PTAC HEAT COIL | 1.7942 | 3.4478 | 2.5951 | 4.1665 | 2.0725 | 3.2365 | 2.5833 | 4.5453 | 3.8286 | 3.5646 | 5.408 | 4.5972 | 6.0194 | 5.7124 | 6.2709 | 8.0797
| GUESTROOM209_212 PTAC HEAT COIL | 2.3446 | 4.3573 | 3.3039 | 5.225 | 2.6695 | 4.0822 | 3.2943 | 5.6901 | 4.787 | 4.4807 | 6.8266 | 5.8011 | 7.5868 | 7.1933 | 7.8925 | 10.1662
| GUESTROOM213 PTAC HEAT COIL | 0.81934 | 1.3625 | 1.0815 | 1.5935 | 0.90891 | 1.2913 | 1.0768 | 1.7048 | 1.4759 | 1.3848 | 2.004 | 1.7446 | 2.1998 | 2.1032 | 2.2769 | 2.8609
| GUESTROOM214 PTAC HEAT COIL | 0.78385 | 1.3275 | 1.0492 | 1.5628 | 0.87336 | 1.263 | 1.0437 | 1.6745 | 1.4419 | 1.3503 | 1.9751 | 1.7186 | 2.1686 | 2.0705 | 2.2463 | 2.8308
| GUESTROOM215_218 PTAC HEAT COIL | 2.2253 | 4.0968 | 3.054 | 4.9989 | 2.3918 | 3.859 | 3.0378 | 5.4725 | 4.5447 | 4.2296 | 6.6298 | 5.6042 | 7.3926 | 6.991 | 7.7061 | 10.0183
| GUESTROOM219 PTAC HEAT COIL | 0.55632 | 0.84847 | 0.61963 | 1.0898 | 0.5786 | 0.78888 | 0.63954 | 1.2083 | 0.96446 | 0.87662 | 1.5171 | 1.2479 | 1.7166 | 1.6124 | 1.7985 | 2.418
| GUESTROOM220_223 PTAC HEAT COIL | 2.2253 | 4.2213 | 3.1869 | 5.1136 | 2.5341 | 3.9807 | 3.1728 | 5.5863 | 4.6649 | 4.3562 | 6.7313 | 5.7141 | 7.4874 | 7.087 | 7.7977 | 10.0751
| GUESTROOM224 PTAC HEAT COIL | 0.70663 | 1.274 | 0.98856 | 1.5096 | 0.80448 | 1.2102 | 0.98207 | 1.6255 | 1.3946 | 1.3009 | 1.9162 | 1.6619 | 2.1058 | 2.0065 | 2.1831 | 2.7572
| GUESTROOM301 PTAC HEAT COIL | 1.2709 | 2.2653 | 1.7225 | 2.6991 | 1.403 | 2.1197 | 1.7116 | 2.8477 | 2.4392 | 2.2378 | 3.458 | 2.9933 | 3.8132 | 3.6475 | 3.9495 | 5.0596
| GUESTROOM302_305 PTAC HEAT COIL | 2.5831 | 4.5987 | 3.4852 | 5.4801 | 2.8467 | 4.2797 | 3.4859 | 5.94 | 5.0167 | 4.6914 | 7.0837 | 6.0477 | 7.8315 | 7.4374 | 8.1471 | 10.4457
| GUESTROOM306_308 PTAC HEAT COIL | 2.055 | 3.6714 | 2.7773 | 4.3907 | 2.2644 | 3.4202 | 2.7776 | 4.7673 | 4.0359 | 3.765 | 5.6284 | 4.8098 | 6.2268 | 5.9181 | 6.4863 | 8.3076
| GUESTROOM309_312 PTAC HEAT COIL | 2.5661 | 4.5649 | 3.4596 | 5.4393 | 2.8271 | 4.2468 | 3.4614 | 5.9026 | 4.9806 | 4.6623 | 7.0407 | 6.0061 | 7.7861 | 7.3915 | 8.1014 | 10.3936
| GUESTROOM313 PTAC HEAT COIL | 0.87194 | 1.4075 | 1.1148 | 1.6394 | 0.94352 | 1.3258 | 1.1131 | 1.7501 | 1.5166 | 1.4237 | 2.0497 | 1.7879 | 2.2417 | 2.1446 | 2.3208 | 2.9074
| GUESTROOM314 PTAC HEAT COIL | 0.84321 | 1.3804 | 1.0903 | 1.6173 | 0.9151 | 1.3039 | 1.0877 | 1.7269 | 1.4903 | 1.3976 | 2.0272 | 1.7683 | 2.2174 | 2.1178 | 2.2974 | 2.8831
| GUESTROOM315_318 PTAC HEAT COIL | 2.5131 | 4.5136 | 3.4268 | 5.4079 | 2.78 | 4.219 | 3.4264 | 5.8679 | 4.9325 | 4.619 | 7.0106 | 5.9849 | 7.7511 | 7.3457 | 8.0703 | 10.3643
| GUESTROOM319 PTAC HEAT COIL | 0.60096 | 1.1528 | 0.857 | 1.3971 | 0.67851 | 1.0752 | 0.85471 | 1.5131 | 1.2663 | 1.1727 | 1.8264 | 1.554 | 2.0253 | 1.9203 | 2.111 | 2.7342
| GUESTROOM320_323 PTAC HEAT COIL | 2.4995 | 4.4882 | 3.4058 | 5.3777 | 2.7632 | 4.1937 | 3.4062 | 5.8381 | 4.9044 | 4.5949 | 6.9759 | 5.9532 | 7.7133 | 7.3081 | 8.0311 | 10.3148
| GUESTROOM324 PTAC HEAT COIL | 0.78197 | 1.3365 | 1.0394 | 1.5665 | 0.85757 | 1.2582 | 1.0371 | 1.6799 | 1.4449 | 1.3565 | 1.9697 | 1.7134 | 2.1558 | 2.0549 | 2.2352 | 2.8101
| GUESTROOM401 PTAC HEAT COIL | 1.4935 | 2.6572 | 2.0405 | 3.1501 | 1.6619 | 2.4962 | 2.0212 | 3.3022 | 2.8834 | 2.5984 | 3.9448 | 3.4895 | 4.2801 | 4.14 | 4.4542 | 5.7147
| GUESTROOM402_405 PTAC HEAT COIL | 3.4961 | 6.1828 | 4.7791 | 7.2858 | 3.9058 | 5.8014 | 4.7438 | 7.7461 | 6.7853 | 6.1295 | 8.999 | 8.0052 | 9.6655 | 9.3782 | 10.1235 | 13.0122
| GUESTROOM406_408 PTAC HEAT COIL | 2.8103 | 4.9679 | 3.8382 | 5.8666 | 3.1362 | 4.6657 | 3.8099 | 6.244 | 5.4815 | 4.9431 | 7.1942 | 6.409 | 7.7266 | 7.5039 | 8.1016 | 10.4007
| GUESTROOM409_412 PTAC HEAT COIL | 3.4851 | 6.1576 | 4.7609 | 7.2547 | 3.8927 | 5.7771 | 4.7265 | 7.7181 | 6.7585 | 6.1086 | 8.9656 | 7.973 | 9.6301 | 9.3425 | 10.088 | 12.9715
| GUESTROOM413 PTAC HEAT COIL | 1.0984 | 1.8008 | 1.4358 | 2.0885 | 1.2064 | 1.7038 | 1.4252 | 2.1995 | 1.9565 | 1.7813 | 2.5271 | 2.2756 | 2.6994 | 2.6288 | 2.8141 | 3.5461
| GUESTROOM414 PTAC HEAT COIL | 1.0827 | 1.7939 | 1.4297 | 2.0897 | 1.1935 | 1.7009 | 1.4181 | 2.1995 | 1.9535 | 1.7755 | 2.5298 | 2.2815 | 2.7003 | 2.6278 | 2.8179 | 3.5552
| GUESTROOM415_418 PTAC HEAT COIL | 3.4758 | 6.1407 | 4.7646 | 7.2585 | 3.8852 | 5.7803 | 4.7286 | 7.7144 | 6.7448 | 6.102 | 8.9656 | 7.9831 | 9.6263 | 9.3253 | 10.0886 | 12.9672
| GUESTROOM419 PTAC HEAT COIL | 0.9316 | 1.6688 | 1.291 | 1.9761 | 1.0468 | 1.5719 | 1.2789 | 2.0927 | 1.8362 | 1.649 | 2.4367 | 2.1788 | 2.6133 | 2.5391 | 2.7399 | 3.5286
| GUESTROOM420_423 PTAC HEAT COIL | 3.4395 | 6.0952 | 4.7241 | 7.2083 | 3.8475 | 5.7353 | 4.6886 | 7.6641 | 6.696 | 6.0573 | 8.9116 | 7.9307 | 9.57 | 9.2689 | 10.0312 | 12.9031
| GUESTROOM424 PTAC HEAT COIL | 1.043 | 1.7559 | 1.4015 | 2.0416 | 1.1596 | 1.664 | 1.3912 | 2.1548 | 1.9111 | 1.7424 | 2.4734 | 2.2279 | 2.6393 | 2.5655 | 2.7559 | 3.483
| LAUNDRYROOMFLR1 PTAC HEAT COIL | 7.0228 | 7.4168 | 6.2575 | 8.0008 | 6.9978 | 6.7646 | 6.4586 | 8.9064 | 7.0766 | 7.7023 | 10.4045 | 8.4474 | 11.2442 | 10.2462 | 11.5093 | 15.0169
| MECHANICALROOMFLR1 PTAC HEAT COIL | 0.37283 | 0.91995 | 0.77158 | 1.1346 | 0.58449 | 0.96985 | 0.73217 | 1.2187 | 1.0753 | 0.96177 | 1.5018 | 1.3186 | 1.6692 | 1.6103 | 1.735 | 2.2643
| MEETINGROOMFLR1 PTAC HEAT COIL | 16.8654 | 22.2646 | 18.7845 | 24.0178 | 17.5407 | 20.3066 | 19.3883 | 26.7361 | 21.2433 | 23.1216 | 31.2333 | 25.3584 | 33.754 | 30.7581 | 34.5498 | 42.7845
| REARSTAIRSFLR1 UNIT HEATER COIL | 0.07041 | 1.2364 | 0.7216 | 1.7236 | 0.34002 | 1.1601 | 0.68481 | 1.9796 | 1.5417 | 1.3053 | 2.8233 | 2.2857 | 3.2989 | 3.1227 | 3.4918 | 4.9976
| REARSTAIRSFLR2 UNIT HEATER COIL | 0.24294 | 1.1489 | 0.67212 | 1.5441 | 0.3782 | 1.0282 | 0.65901 | 1.7408 | 1.362 | 1.1701 | 2.4391 | 1.9862 | 2.8269 | 2.6755 | 2.9808 | 4.1996
| REARSTAIRSFLR3 UNIT HEATER COIL | 0.27468 | 1.179 | 0.69294 | 1.5752 | 0.40113 | 1.0522 | 0.68193 | 1.7717 | 1.3908 | 1.1971 | 2.4718 | 2.018 | 2.8587 | 2.7068 | 3.0138 | 4.2333
| REARSTAIRSFLR4 UNIT HEATER COIL | 0.36446 | 1.3681 | 0.83545 | 1.799 | 0.50767 | 1.2325 | 0.81812 | 2.005 | 1.6165 | 1.3753 | 2.7287 | 2.2792 | 3.1092 | 2.9723 | 3.2863 | 4.5966
| REARSTORAGEFLR1 UNIT HEATER COIL | 0 | 0.80169 | 0.47094 | 1.148 | 0.19816 | 0.78855 | 0.4291 | 1.2493 | 1.022 | 0.80336 | 1.7554 | 1.4759 | 2.0321 | 1.9604 | 2.1372 | 2.996
| REARSTORAGEFLR2 UNIT HEATER COIL | 0.19133 | 0.83053 | 0.50253 | 1.1079 | 0.29073 | 0.7606 | 0.48364 | 1.1789 | 0.97281 | 0.79849 | 1.6015 | 1.3596 | 1.8268 | 1.7615 | 1.9088 | 2.6018
| REARSTORAGEFLR3 UNIT HEATER COIL | 0.21791 | 0.84948 | 0.51681 | 1.1262 | 0.30706 | 0.77432 | 0.49963 | 1.1967 | 0.98885 | 0.81516 | 1.6199 | 1.3769 | 1.8442 | 1.7779 | 1.9263 | 2.616
| REARSTORAGEFLR4 UNIT HEATER COIL | 0.22768 | 0.8612 | 0.52532 | 1.1412 | 0.31519 | 0.78579 | 0.50909 | 1.2139 | 1.0051 | 0.83038 | 1.6383 | 1.3946 | 1.8601 | 1.7929 | 1.9445 | 2.6384
| RESTROOMFLR1 PTAC HEAT COIL | 0.17815 | 0.64586 | 0.5519 | 0.82784 | 0.38493 | 0.72157 | 0.50645 | 0.86809 | 0.79421 | 0.67175 | 1.0635 | 0.96056 | 1.1832 | 1.1616 | 1.2311 | 1.6138
HVAC Efficiency
Air Conditioning (COP)
| CORRIDORFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| CORRIDORFLR2 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| CORRIDORFLR3 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| CORRIDORFLR4 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| EMPLOYEELOUNGEFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| EXERCISECENTERFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4
| FRONTLOUNGEFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| FRONTOFFICEFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM101 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM102 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM103 PTAC DXCOIL | 3.4 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM104 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM105 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM201 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM202_205 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM206_208 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM209_212 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM213 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.4
| GUESTROOM214 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM215_218 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM219 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4
| GUESTROOM220_223 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM224 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM301 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM302_305 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM306_308 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM309_312 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM313 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21
| GUESTROOM314 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM315_318 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM319 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM320_323 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM324 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM401 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM402_405 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM406_408 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM409_412 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM413 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21
| GUESTROOM414 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM415_418 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM419 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4
| GUESTROOM420_423 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| GUESTROOM424 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4
| LAUNDRYROOMFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| MECHANICALROOMFLR1 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
| MEETINGROOMFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
| RESTROOMFLR1 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
Heating Efficiency (%)
| CORRIDORFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| CORRIDORFLR2 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| CORRIDORFLR3 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| CORRIDORFLR4 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| EXERCISECENTERFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTLOUNGEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTOFFICEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| LAUNDRYROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| MECHANICALROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| MEETINGROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| RESTROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Control - Economizer
| All Systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| CORRIDORFLR1 PTACFAN | 0.62 | 0.63 | 0.63 | 0.64 | 0.56 | 0.61 | 0.48 | 0.6 | 0.64 | 0.53 | 0.57 | 0.6 | 0.57 | 0.57 | 0.51 | 0.44
| CORRIDORFLR2 PTACFAN | 0.35 | 0.36 | 0.39 | 0.37 | 0.32 | 0.39 | 0.31 | 0.35 | 0.38 | 0.33 | 0.32 | 0.34 | 0.32 | 0.33 | 0.3 | 0.28
| CORRIDORFLR3 PTACFAN | 0.33 | 0.34 | 0.38 | 0.34 | 0.3 | 0.37 | 0.29 | 0.32 | 0.35 | 0.3 | 0.3 | 0.31 | 0.3 | 0.3 | 0.28 | 0.26
| CORRIDORFLR4 PTACFAN | 0.43 | 0.45 | 0.51 | 0.45 | 0.37 | 0.49 | 0.34 | 0.4 | 0.43 | 0.36 | 0.36 | 0.37 | 0.33 | 0.33 | 0.31 | 0.28
| EMPLOYEELOUNGEFLR1 PTACFAN | 0.35 | 0.35 | 0.36 | 0.36 | 0.33 | 0.37 | 0.31 | 0.34 | 0.4 | 0.32 | 0.34 | 0.38 | 0.34 | 0.36 | 0.33 | 0.3
| EXERCISECENTERFLR1 PTACFAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.14 | 0.16 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.16 | 0.15 | 0.15 | 0.13 | 0.12
| FRONTLOUNGEFLR1 PTACFAN | 0.91 | 0.97 | 1.05 | 1.02 | 1 | 1.07 | 1.08 | 1.01 | 1.05 | 1.08 | 0.9 | 0.96 | 0.9 | 0.95 | 0.84 | 0.88
| FRONTOFFICEFLR1 PTACFAN | 0.53 | 0.53 | 0.53 | 0.52 | 0.43 | 0.52 | 0.36 | 0.48 | 0.51 | 0.4 | 0.45 | 0.47 | 0.45 | 0.44 | 0.39 | 0.33
| FRONTSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.05 | 0.03 | 0.06 | 0.01 | 0.05 | 0.03 | 0.07 | 0.07 | 0.05 | 0.1 | 0.1 | 0.12 | 0.13 | 0.13 | 0.17
| FRONTSTAIRSFLR2 UNIT HEATERFAN | 0.01 | 0.04 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.06 | 0.06 | 0.04 | 0.09 | 0.09 | 0.1 | 0.11 | 0.11 | 0.15
| FRONTSTAIRSFLR3 UNIT HEATERFAN | 0.01 | 0.04 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.07 | 0.06 | 0.05 | 0.09 | 0.09 | 0.1 | 0.11 | 0.11 | 0.15
| FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.02 | 0.05 | 0.03 | 0.07 | 0.02 | 0.05 | 0.03 | 0.07 | 0.07 | 0.05 | 0.1 | 0.1 | 0.11 | 0.12 | 0.12 | 0.16
| FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01
| FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01
| FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01
| FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02
| GUESTROOM101 PTACFAN | 0.12 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15 | 0.14 | 0.14 | 0.15 | 0.12 | 0.13 | 0.12 | 0.13 | 0.11 | 0.12
| GUESTROOM102 PTACFAN | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12
| GUESTROOM103 PTACFAN | 0.14 | 0.15 | 0.16 | 0.16 | 0.15 | 0.16 | 0.15 | 0.15 | 0.15 | 0.16 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12 | 0.12
| GUESTROOM104 PTACFAN | 0.14 | 0.14 | 0.15 | 0.14 | 0.11 | 0.14 | 0.09 | 0.13 | 0.13 | 0.1 | 0.12 | 0.11 | 0.12 | 0.11 | 0.1 | 0.09
| GUESTROOM105 PTACFAN | 0.14 | 0.14 | 0.14 | 0.14 | 0.11 | 0.14 | 0.1 | 0.13 | 0.14 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.1 | 0.09
| GUESTROOM201 PTACFAN | 0.23 | 0.24 | 0.27 | 0.25 | 0.22 | 0.28 | 0.23 | 0.22 | 0.24 | 0.22 | 0.21 | 0.22 | 0.2 | 0.21 | 0.19 | 0.17
| GUESTROOM202_205 PTACFAN | 0.53 | 0.58 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.62 | 0.67 | 0.69 | 0.57 | 0.62 | 0.57 | 0.62 | 0.56 | 0.61
| GUESTROOM206_208 PTACFAN | 0.43 | 0.47 | 0.54 | 0.51 | 0.5 | 0.55 | 0.58 | 0.51 | 0.55 | 0.57 | 0.46 | 0.5 | 0.47 | 0.51 | 0.46 | 0.5
| GUESTROOM209_212 PTACFAN | 0.52 | 0.57 | 0.64 | 0.61 | 0.6 | 0.66 | 0.68 | 0.6 | 0.65 | 0.67 | 0.55 | 0.61 | 0.56 | 0.61 | 0.55 | 0.59
| GUESTROOM213 PTACFAN | 0.15 | 0.16 | 0.19 | 0.17 | 0.16 | 0.19 | 0.18 | 0.17 | 0.18 | 0.18 | 0.16 | 0.16 | 0.16 | 0.16 | 0.15 | 0.16
| GUESTROOM214 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.18 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| GUESTROOM215_218 PTACFAN | 0.59 | 0.59 | 0.63 | 0.6 | 0.5 | 0.64 | 0.48 | 0.56 | 0.64 | 0.52 | 0.54 | 0.6 | 0.54 | 0.57 | 0.52 | 0.48
| GUESTROOM219 PTACFAN | 0.18 | 0.18 | 0.19 | 0.18 | 0.16 | 0.19 | 0.15 | 0.17 | 0.2 | 0.16 | 0.17 | 0.18 | 0.17 | 0.18 | 0.16 | 0.15
| GUESTROOM220_223 PTACFAN | 0.55 | 0.55 | 0.6 | 0.56 | 0.47 | 0.6 | 0.45 | 0.53 | 0.6 | 0.48 | 0.5 | 0.55 | 0.5 | 0.53 | 0.48 | 0.44
| GUESTROOM224 PTACFAN | 0.16 | 0.16 | 0.17 | 0.16 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| GUESTROOM301 PTACFAN | 0.23 | 0.24 | 0.27 | 0.25 | 0.22 | 0.27 | 0.23 | 0.22 | 0.24 | 0.22 | 0.21 | 0.22 | 0.2 | 0.21 | 0.18 | 0.17
| GUESTROOM302_305 PTACFAN | 0.54 | 0.57 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.61 | 0.67 | 0.69 | 0.57 | 0.62 | 0.58 | 0.63 | 0.57 | 0.61
| GUESTROOM306_308 PTACFAN | 0.44 | 0.47 | 0.55 | 0.51 | 0.51 | 0.56 | 0.59 | 0.51 | 0.55 | 0.58 | 0.47 | 0.51 | 0.48 | 0.52 | 0.47 | 0.52
| GUESTROOM309_312 PTACFAN | 0.53 | 0.56 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.61 | 0.66 | 0.68 | 0.57 | 0.62 | 0.58 | 0.62 | 0.57 | 0.61
| GUESTROOM313 PTACFAN | 0.15 | 0.16 | 0.19 | 0.18 | 0.16 | 0.19 | 0.18 | 0.17 | 0.18 | 0.18 | 0.16 | 0.16 | 0.16 | 0.17 | 0.15 | 0.16
| GUESTROOM314 PTACFAN | 0.16 | 0.16 | 0.19 | 0.17 | 0.13 | 0.18 | 0.12 | 0.16 | 0.17 | 0.13 | 0.15 | 0.15 | 0.15 | 0.14 | 0.13 | 0.12
| GUESTROOM315_318 PTACFAN | 0.57 | 0.57 | 0.62 | 0.58 | 0.48 | 0.63 | 0.46 | 0.54 | 0.62 | 0.5 | 0.52 | 0.57 | 0.52 | 0.55 | 0.5 | 0.47
| GUESTROOM319 PTACFAN | 0.15 | 0.15 | 0.17 | 0.15 | 0.13 | 0.17 | 0.12 | 0.14 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| GUESTROOM320_323 PTACFAN | 0.56 | 0.56 | 0.61 | 0.57 | 0.48 | 0.62 | 0.46 | 0.54 | 0.61 | 0.49 | 0.51 | 0.56 | 0.51 | 0.54 | 0.49 | 0.46
| GUESTROOM324 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.18 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| GUESTROOM401 PTACFAN | 0.25 | 0.26 | 0.3 | 0.27 | 0.23 | 0.29 | 0.23 | 0.23 | 0.25 | 0.22 | 0.21 | 0.23 | 0.2 | 0.21 | 0.19 | 0.2
| GUESTROOM402_405 PTACFAN | 0.63 | 0.65 | 0.73 | 0.67 | 0.6 | 0.72 | 0.7 | 0.62 | 0.68 | 0.69 | 0.59 | 0.63 | 0.57 | 0.6 | 0.55 | 0.61
| GUESTROOM406_408 PTACFAN | 0.52 | 0.54 | 0.6 | 0.55 | 0.49 | 0.59 | 0.59 | 0.51 | 0.56 | 0.58 | 0.48 | 0.52 | 0.47 | 0.49 | 0.45 | 0.51
| GUESTROOM409_412 PTACFAN | 0.63 | 0.65 | 0.73 | 0.66 | 0.6 | 0.72 | 0.7 | 0.62 | 0.68 | 0.69 | 0.59 | 0.63 | 0.57 | 0.6 | 0.55 | 0.61
| GUESTROOM413 PTACFAN | 0.18 | 0.18 | 0.21 | 0.19 | 0.16 | 0.21 | 0.18 | 0.17 | 0.18 | 0.19 | 0.16 | 0.17 | 0.16 | 0.16 | 0.15 | 0.16
| GUESTROOM414 PTACFAN | 0.19 | 0.19 | 0.22 | 0.19 | 0.15 | 0.21 | 0.14 | 0.18 | 0.19 | 0.15 | 0.16 | 0.17 | 0.16 | 0.15 | 0.14 | 0.13
| GUESTROOM415_418 PTACFAN | 0.64 | 0.66 | 0.73 | 0.67 | 0.55 | 0.72 | 0.52 | 0.62 | 0.69 | 0.55 | 0.57 | 0.62 | 0.55 | 0.57 | 0.53 | 0.49
| GUESTROOM419 PTACFAN | 0.17 | 0.17 | 0.19 | 0.18 | 0.14 | 0.19 | 0.13 | 0.16 | 0.18 | 0.14 | 0.15 | 0.16 | 0.14 | 0.15 | 0.14 | 0.13
| GUESTROOM420_423 PTACFAN | 0.64 | 0.65 | 0.72 | 0.66 | 0.55 | 0.72 | 0.51 | 0.61 | 0.68 | 0.55 | 0.57 | 0.61 | 0.55 | 0.56 | 0.52 | 0.49
| GUESTROOM424 PTACFAN | 0.18 | 0.19 | 0.21 | 0.19 | 0.15 | 0.2 | 0.14 | 0.17 | 0.18 | 0.15 | 0.16 | 0.16 | 0.15 | 0.15 | 0.14 | 0.13
| LAUNDRYROOMFLR1 PTACFAN | 1.59 | 1.58 | 1.62 | 1.62 | 1.53 | 1.66 | 1.46 | 1.56 | 1.83 | 1.52 | 1.58 | 1.81 | 1.58 | 1.71 | 1.57 | 1.47
| MECHANICALROOMFLR1 PTACFAN | 0.06 | 0.07 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.06 | 0.07 | 0.06 | 0.06 | 0.07
| MEETINGROOMFLR1 PTACFAN | 0.5 | 0.52 | 0.55 | 0.55 | 0.54 | 0.56 | 0.56 | 0.54 | 0.58 | 0.57 | 0.5 | 0.55 | 0.51 | 0.54 | 0.48 | 0.49
| REARSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.04 | 0.03 | 0.06 | 0.01 | 0.04 | 0.02 | 0.07 | 0.06 | 0.04 | 0.1 | 0.09 | 0.11 | 0.12 | 0.12 | 0.17
| REARSTAIRSFLR2 UNIT HEATERFAN | 0.01 | 0.04 | 0.02 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.1 | 0.1 | 0.1 | 0.14
| REARSTAIRSFLR3 UNIT HEATERFAN | 0.01 | 0.04 | 0.02 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.1 | 0.1 | 0.11 | 0.14
| REARSTAIRSFLR4 UNIT HEATERFAN | 0.01 | 0.05 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.07 | 0.07 | 0.05 | 0.09 | 0.09 | 0.11 | 0.11 | 0.12 | 0.16
| REARSTORAGEFLR1 UNIT HEATERFAN | 0 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.01 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.07 | 0.08 | 0.08 | 0.1
| REARSTORAGEFLR2 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.05 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
| REARSTORAGEFLR3 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
| REARSTORAGEFLR4 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
| RESTROOMFLR1 PTACFAN | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 0.08
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.079051 | 0.10802 | 0.087357 | 0.10015 | 0.12324 | 0.094839 | 0.14501 | 0.069942 | 0.037194 | 0.071815 | 0.0963 | 0.0372 | 0.056427 | 0.073085 | 0.056906 | 0.093034
| Total Cost ($/m2) | 17.18 | 21.81 | 17.8 | 18.89 | 21.88 | 18.29 | 23.97 | 12.99 | 6.7 | 12 | 17.74 | 6.56 | 10.97 | 13.13 | 11.09 | 22.3
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01146 | 0.0082004 | 0.0086055 | 0.010915 | 0.0083923 | 0.0081734 | 0.0083919 | 0.01015 | 0.0072406 | 0.0082682 | 0.0090446 | 0.0072473 | 0.0080119 | 0.0089154 | 0.0080171 | 0.0042313
| Total Cost ($/m2) | 1.25 | 0.99 | 0.98 | 1.45 | 1.1 | 1 | 1.18 | 1.45 | 1.02 | 1.22 | 1.36 | 1.09 | 1.27 | 1.42 | 1.36 | 0.78
Total Utility Costs
| Cost Intensity ($/m2) | 18.43 | 22.8 | 18.78 | 20.35 | 22.97 | 19.29 | 25.16 | 14.44 | 7.72 | 13.22 | 19.1 | 7.65 | 12.24 | 14.55 | 12.45 | 23.08
Energy - End Uses
Electricity (kWh)
| Heating | 19.4444 | 8558.3333 | 2319.4444 | 24283.3333 | 180.5556 | 7261.1111 | 3363.8889 | 46694.4444 | 22663.8889 | 24905.5556 | 66366.6667 | 41027.7778 | 111552.7778 | 73811.1111 | 146513.8889 | 338402.7778
| Cooling | 267991.6667 | 204441.6667 | 215361.1111 | 141091.6667 | 122811.1111 | 170752.7778 | 77002.7778 | 110986.1111 | 111102.7778 | 63838.8889 | 87950 | 81388.8889 | 82875 | 63908.3333 | 52597.2222 | 39375
| Interior Lighting | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667
| Exterior Lighting | 73086.1111 | 72955.5556 | 72936.1111 | 73058.3333 | 73044.4444 | 72972.2222 | 72894.4444 | 72969.4444 | 72955.5556 | 72847.2222 | 72869.4444 | 72880.5556 | 72927.7778 | 72838.8889 | 72819.4444 | 72383.3333
| Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 32991.6667 | 25863.8889 | 28916.6667 | 20247.2222 | 18027.7778 | 24561.1111 | 11850 | 16497.2222 | 17986.1111 | 10658.3333 | 13805.5556 | 14033.3333 | 14525 | 12219.4444 | 11530.5556 | 13441.6667
| Pumps | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 872497.2222 | 810230.5556 | 817941.6667 | 757086.1111 | 712472.2222 | 773955.5556 | 663516.6667 | 745555.5556 | 723116.6667 | 670661.1111 | 739397.2222 | 707738.8889 | 780288.8889 | 721186.1111 | 781866.6667 | 962013.8889
Gas (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 247280 | 297060 | 268460 | 344970 | 335670 | 302920 | 376670 | 382630 | 375520 | 402240 | 415710 | 413990 | 444290 | 449480 | 491410 | 548430
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 436750 | 486540 | 457940 | 534450 | 525150 | 492400 | 566150 | 572110 | 565000 | 591710 | 605190 | 603470 | 633770 | 638960 | 680890 | 737910
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3577740 | 3403370 | 3402530 | 3259950 | 3090040 | 3278640 | 2954810 | 3256110 | 3168220 | 3006090 | 3267030 | 3151330 | 3442810 | 3235230 | 3495610 | 4201160
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.017441 | 7.6764 | 2.0804 | 21.781 | 0.16195 | 6.5129 | 3.0172 | 41.8827 | 20.3284 | 22.3391 | 59.5278 | 36.8 | 100.0576 | 66.2051 | 131.416 | 303.5313
| Cooling (elec) | 240.3758 | 183.3745 | 193.1687 | 126.5525 | 110.1557 | 153.1571 | 69.0678 | 99.5493 | 99.6539 | 57.2605 | 78.887 | 73.002 | 74.3349 | 57.3227 | 47.1772 | 35.3175
| Interior Lighting (elec) | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551
| Exterior Lighting (elec) | 65.5548 | 65.4377 | 65.4202 | 65.5299 | 65.5174 | 65.4526 | 65.3829 | 65.4501 | 65.4377 | 65.3405 | 65.3604 | 65.3704 | 65.4128 | 65.333 | 65.3156 | 64.9244
| Interior Equipment (elec) | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 29.592 | 23.1987 | 25.9369 | 18.1608 | 16.1701 | 22.0302 | 10.6289 | 14.7972 | 16.1327 | 9.56 | 12.3829 | 12.5872 | 13.0282 | 10.9603 | 10.3424 | 12.0565
| Pumps (elec) | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 782.5887 | 726.7384 | 733.6549 | 679.0704 | 639.0538 | 694.2015 | 595.143 | 668.728 | 648.6014 | 601.5512 | 663.2043 | 634.8082 | 699.8822 | 646.8698 | 701.2973 | 862.8809
Gas (MJ/m2)
| Heating (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 61.6107 | 74.0135 | 66.8877 | 85.9505 | 83.6334 | 75.4736 | 93.8486 | 95.3336 | 93.5621 | 100.2195 | 103.5756 | 103.1471 | 110.6964 | 111.9895 | 122.4365 | 136.6433
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 108.8178 | 121.2231 | 114.0974 | 133.1601 | 130.843 | 122.6832 | 141.0583 | 142.5432 | 140.7717 | 147.4266 | 150.7852 | 150.3567 | 157.906 | 159.1991 | 169.6461 | 183.8529
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 891.4064 | 847.9616 | 847.7523 | 812.228 | 769.8943 | 816.8846 | 736.2013 | 811.2712 | 789.3731 | 748.9778 | 813.992 | 785.1649 | 857.7882 | 806.0689 | 870.9435 | 1046.7337
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 150.8302 | 164.0306 | 134.1068 | 173.8353 | 132.1964 | 124.0024 | 124.2109 | 196.3023 | 147.9993 | 126.8311 | 218.1102 | 192.9975 | 246.3319 | 221.4929 | 257.5189 | 360.6813
| Feb | 152.9571 | 140.0124 | 134.2299 | 174.3046 | 133.0169 | 128.1243 | 130.555 | 156.9855 | 125.0876 | 124.8087 | 164.692 | 169.5689 | 222.0618 | 207.5689 | 256.6967 | 340.5898
| Mar | 156.5244 | 151.3064 | 152.4158 | 139.7791 | 131.4861 | 132.6128 | 126.6074 | 133.596 | 129.006 | 131.2386 | 129.3215 | 132.6347 | 151.8749 | 154.3007 | 210.7534 | 260.537
| Apr | 161.321 | 160.2624 | 153.031 | 149.6304 | 138.2609 | 150.1791 | 132.9431 | 137.4228 | 139.3855 | 132.1311 | 129.0872 | 135.7752 | 137.0718 | 128.7854 | 124.4293 | 155.1984
| May | 165.0349 | 171.9455 | 175.9861 | 162.1033 | 141.8902 | 159.1021 | 134.5803 | 148.477 | 146.6649 | 137.8168 | 144.254 | 143.6562 | 159.2256 | 135.5349 | 133.2678 | 117.767
| Jun | 177.222 | 169.3291 | 197.7642 | 164.8682 | 140.6205 | 190.2383 | 135.8525 | 166.2448 | 154.702 | 139.7398 | 154.4134 | 146.8197 | 158.742 | 148.5208 | 148.8115 | 126.8929
| Jul | 171.4215 | 176.8698 | 193.066 | 174.7696 | 143.9488 | 185.8496 | 153.0663 | 173.7972 | 163.6086 | 147.4036 | 163.2821 | 153.9738 | 164.252 | 144.0632 | 154.6821 | 132.6549
| Aug | 172.1127 | 183.3364 | 197.5227 | 166.1151 | 145.6293 | 178.7916 | 135.9211 | 174.8876 | 160.3833 | 147.782 | 167.9751 | 150.7923 | 163.5322 | 148.0767 | 155.9559 | 131.4888
| Sep | 167.6368 | 168.3272 | 180.8181 | 158.2767 | 144.8721 | 164.8545 | 145.2255 | 151.8909 | 149.0932 | 152.7096 | 147.9577 | 144.2771 | 144.4449 | 145.1105 | 140.3944 | 126.775
| Oct | 165.678 | 160.4614 | 156.3209 | 147.8485 | 140.0783 | 146.4975 | 135.0609 | 145.6648 | 140.2385 | 132.9291 | 137.9022 | 137.8396 | 139.3929 | 131.6396 | 134.2956 | 176.145
| Nov | 157.5998 | 150.3117 | 138.3384 | 132.9722 | 134.7592 | 130.1613 | 128.1646 | 139.9735 | 128.0794 | 133.3772 | 137.5621 | 129.7379 | 148.6508 | 134.9201 | 193.9415 | 233.8997
| Dec | 150.9443 | 149.0058 | 133.4113 | 160.5456 | 132.3041 | 125.5043 | 123.4719 | 167.0195 | 145.7635 | 130.6114 | 199.1447 | 180.7088 | 250.7613 | 232.674 | 246.6438 | 301.9919
Time of Peak Electrical Demand
| Jan | 06-JAN-20:00 | 14-JAN-07:15 | 29-JAN-20:15 | 14-JAN-07:15 | 26-JAN-20:15 | 10-JAN-20:45 | 15-JAN-20:15 | 31-JAN-07:15 | 04-JAN-07:15 | 02-JAN-07:00 | 07-JAN-07:15 | 06-JAN-06:15 | 06-JAN-06:15 | 07-JAN-07:15 | 09-JAN-07:15 | 13-JAN-06:15
| Feb | 20-FEB-20:15 | 20-FEB-20:15 | 28-FEB-20:15 | 10-FEB-07:15 | 12-FEB-20:15 | 27-FEB-20:15 | 15-FEB-20:15 | 01-FEB-07:15 | 14-FEB-20:15 | 01-FEB-07:15 | 09-FEB-06:15 | 16-FEB-06:45 | 04-FEB-06:15 | 26-FEB-07:15 | 02-FEB-07:15 | 04-FEB-07:15
| Mar | 13-MAR-19:15 | 26-MAR-19:15 | 17-MAR-19:15 | 28-MAR-19:15 | 04-MAR-20:00 | 31-MAR-19:00 | 30-MAR-19:30 | 09-MAR-20:00 | 20-MAR-19:15 | 29-MAR-19:00 | 03-MAR-20:00 | 07-MAR-06:15 | 05-MAR-21:00 | 04-MAR-06:15 | 09-MAR-06:15 | 14-MAR-06:00
| Apr | 01-APR-19:15 | 30-APR-19:15 | 02-APR-19:15 | 15-APR-19:15 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-19:15 | 05-APR-19:15 | 22-APR-19:15 | 29-APR-19:15 | 28-APR-19:30 | 25-APR-19:30 | 02-APR-19:30 | 30-APR-19:30 | 15-APR-19:15 | 02-APR-06:15
| May | 15-MAY-19:15 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 29-MAY-19:15 | 31-MAY-19:15 | 25-MAY-19:15 | 15-MAY-19:15 | 30-MAY-19:15 | 04-MAY-19:30 | 30-MAY-19:15 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 31-MAY-19:00 | 29-MAY-19:00
| Jun | 27-JUN-19:15 | 13-JUN-19:30 | 27-JUN-19:45 | 19-JUN-19:00 | 28-JUN-19:15 | 27-JUN-19:15 | 16-JUN-19:30 | 30-JUN-19:45 | 28-JUN-19:30 | 18-JUN-20:15 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:00 | 25-JUN-20:30 | 14-JUN-19:00 | 23-JUN-19:00
| Jul | 04-JUL-19:15 | 30-JUL-19:15 | 11-JUL-19:45 | 02-JUL-19:00 | 10-JUL-19:15 | 24-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:00 | 13-JUL-19:30 | 17-JUL-19:30 | 15-JUL-19:00 | 30-JUL-19:00 | 06-JUL-19:00 | 29-JUL-19:15
| Aug | 21-AUG-19:15 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 16-AUG-19:15 | 04-AUG-19:15 | 27-AUG-19:15 | 03-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 27-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 19-AUG-20:00
| Sep | 10-SEP-19:15 | 16-SEP-19:15 | 09-SEP-19:15 | 10-SEP-19:15 | 25-SEP-19:15 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:15 | 02-SEP-19:15 | 02-SEP-19:15 | 06-SEP-19:15 | 01-SEP-19:15 | 14-SEP-19:15 | 02-SEP-19:15 | 08-SEP-19:15 | 09-SEP-19:45
| Oct | 06-OCT-19:15 | 29-OCT-19:15 | 02-OCT-19:15 | 01-OCT-19:15 | 05-OCT-19:15 | 03-OCT-19:15 | 16-OCT-19:15 | 20-OCT-19:15 | 01-OCT-19:15 | 09-OCT-19:15 | 31-OCT-19:15 | 01-OCT-19:15 | 08-OCT-19:15 | 06-OCT-19:15 | 07-OCT-19:15 | 22-OCT-07:15
| Nov | 01-NOV-19:15 | 26-NOV-20:00 | 05-NOV-19:15 | 22-NOV-20:00 | 09-NOV-20:30 | 09-NOV-20:30 | 12-NOV-20:30 | 04-NOV-19:15 | 09-NOV-20:00 | 29-NOV-07:15 | 02-NOV-19:00 | 18-NOV-20:00 | 30-NOV-07:15 | 30-NOV-07:15 | 25-NOV-07:15 | 23-NOV-06:15
| Dec | 17-DEC-20:15 | 02-DEC-20:15 | 13-DEC-20:15 | 22-DEC-07:15 | 18-DEC-20:15 | 05-DEC-20:15 | 17-DEC-20:15 | 21-DEC-07:15 | 29-DEC-07:15 | 11-DEC-07:15 | 31-DEC-07:15 | 12-DEC-07:15 | 31-DEC-06:15 | 11-DEC-07:15 | 31-DEC-07:15 | 29-DEC-06:15
Source Energy
| Total Source Energy (GJ) | 10895.59 | 11125.22 | 9813.82 | 9752.22 | 8511.81 | 10504.07 | 8011.15 | 10222.73 | 9254.47 | 4852 | 10099.73 | 9112.78 | 10346.76 | 9722.37 | 10417.71 | 13176.52
| Total Source Energy (MJ/m2) | 2714.68 | 2771.89 | 2445.15 | 2429.8 | 2120.75 | 2617.13 | 1996.01 | 2547.03 | 2305.78 | 1208.89 | 2516.39 | 2270.48 | 2577.93 | 2422.37 | 2595.61 | 3282.98
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
| Total Building | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
Emissions
| Carbon Equivalent (kg) | 247157.725 | 279034.6777 | 255174.5904 | 242847.4891 | 92733.3226 | 269914.9529 | 87751.7219 | 211508.8781 | 305580.3579 | 59517.1683 | 405122.9008 | 299991.8913 | 278516.2125 | 275070.5034 | 279905.4116 | 284004.8068
| CO2 (kg) | 576824.9099 | 703511.121 | 604532.2318 | 557138.0192 | 249659.6499 | 643920.1292 | 236521.8071 | 480987.2199 | 717728.213 | 146863.3053 | 941079.1197 | 705094.4113 | 648761.4981 | 646268.9039 | 652460.194 | 716548.9385
| NOX (kg) | 997.8194 | 914.3959 | 1003.0931 | 1047.3442 | 215.0777 | 1037.2024 | 203.946 | 929.153 | 1234.359 | 214.4263 | 1684.8186 | 1210.4955 | 1153.5942 | 1118.3192 | 1158.0927 | 884.4377
| SO2 (kg) | 3734.75 | 3864.9277 | 3289.2322 | 2657.5116 | 2073.3464 | 4257.5036 | 1930.9089 | 2721.7289 | 3157.8598 | 518.5256 | 4983.1152 | 3090.7139 | 1841.7779 | 1925.8241 | 1845.5106 | 4897.23
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0171 | 0.0109 | 0.009 | 0.0098 | 0.001 | 0.008 | 0.0009 | 0.011 | 0.0124 | 0.0021 | 0.0151 | 0.0121 | 0.0135 | 0.0134 | 0.0135 | 0.0166
| Water for Electricity (m3) | 462.2119 | 1318.34 | 24296.5 | 4726.94 | 12509.4 | 21232.7 | 11649.9 | 169.2691 | 3283.53 | 6852.01 | 1147.13 | 3213.7 | 1210.57 | 45682.9 | 1213.02 | 982.8697

## Picture
DOE Commercial Building Benchmark - Small Hotel
First Floor
Upper Floors

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
UnitHeater_ClgSP_Sch | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
UnitHeater_HtgSP_Sch | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Laundry Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600