## BuildingSummary
Building Summary Small Office pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Small Office Reference Building pre-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 511 | 2003 CBECS, ASHRAE Small Office 30% Advanced Energy Design Guide
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.244
| East | 0.198
| North | 0.198
| West | 0.198
| Total | 0.212
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones
| Floor to Ceiling Height (m) | 3.05
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 281.5
| Net Dimensions - Total Area (m2) | 222
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 598.76
| Net Dimensions - Total Area (m2) | 598.76
| Roof to Skin Ratio | 0.64
Window Dimensions (m2)
| South | 16.73
| East | 11.16
| North | 16.73
| West | 11.16
| Total Area (m2) | 55.78
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab w/carpet
| Dimensions - Total Area (m2) | 511
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 0
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.46
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.68 | See Reference Building Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 17.63

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 19.4827 | 8.0729 |  | 11.3562 | 10 |  | 80.5463 |  | 0
Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 20.64 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 16.73 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 14.0702 | 14.3172 | 13.3971 | 13.6299 | 10.8899 | 12.0158 | 8.7265 | 12.6538 | 11.8599 | 9.1845 | 11.4936 | 10.4201 | 10.1186 | 8.8957 | 8.4604 | 7.4131
| PSZ-AC:2_COOLC DXCOIL | 15.3291 | 16.6759 | 17.3917 | 16.6398 | 14.9485 | 16.3623 | 16.8634 | 16.6356 | 14.2362 | 16.6376 | 19.157 | 16.3695 | 21.132 | 19.3499 | 21.0724 | 25.3241
| PSZ-AC:3_COOLC DXCOIL | 11.784 | 11.6241 | 11.4591 | 11.2512 | 9.186 | 10.6232 | 7.1947 | 10.181 | 9.2621 | 7.9935 | 11.1126 | 10.185 | 12.225 | 12.0359 | 12.4006 | 15.7255
| PSZ-AC:4_COOLC DXCOIL | 14.9502 | 14.8467 | 14.8018 | 14.1739 | 9.9629 | 12.8992 | 7.5833 | 14.8015 | 12.9973 | 10.091 | 19.5653 | 16.1566 | 21.7694 | 19.0392 | 21.779 | 24.9693
| PSZ-AC:5_COOLC DXCOIL | 14.8775 | 15.2634 | 15.6351 | 14.8579 | 13.1264 | 15.5989 | 11.5214 | 13.6123 | 14.7104 | 11.8026 | 11.1763 | 11.2802 | 11.7208 | 12.0206 | 12.1019 | 15.7255
Heating (kW)
| PSZ-AC:1_HEATC | 17.6629 | 18.9166 | 17.5832 | 18.9164 | 16.3392 | 16.9726 | 13.8495 | 17.9166 | 15.9559 | 15.0266 | 16.9817 | 15.0533 | 16.2834 | 14.7976 | 15.226 | 16.2227
| PSZ-AC:2_HEATC | 18.6807 | 21.4194 | 23.1395 | 22.4704 | 21.752 | 22.5619 | 24.7384 | 22.8906 | 18.1037 | 24.6601 | 24.9315 | 21.0944 | 27.8436 | 26.4366 | 29.2766 | 39.2936
| PSZ-AC:3_HEATC | 15.5936 | 15.8904 | 16.0384 | 15.883 | 13.3443 | 14.5616 | 10.7735 | 14.5899 | 11.674 | 12.0572 | 15.4432 | 13.0554 | 17.2255 | 16.3551 | 18.0996 | 24.2727
| PSZ-AC:4_HEATC | 18.4589 | 19.2443 | 19.3211 | 18.7489 | 14.378 | 18.1143 | 11.8474 | 20.0032 | 16.6868 | 15.6869 | 24.6268 | 20.8513 | 27.4578 | 26.0619 | 28.8627 | 38.8082
| PSZ-AC:5_HEATC | 20.3553 | 21.4499 | 21.6333 | 21.0989 | 18.7988 | 20.952 | 16.7837 | 19.755 | 17.9052 | 17.2784 | 16.1687 | 14.3062 | 17.2046 | 16.3367 | 18.079 | 24.2727
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
| PSZ-AC:2_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ-AC:3_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
| PSZ-AC:4_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
| PSZ-AC:5_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC:1 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC:1_FAN | 0.71 | 0.73 | 0.72 | 0.73 | 0.65 | 0.7 | 0.53 | 0.65 | 0.72 | 0.55 | 0.58 | 0.63 | 0.53 | 0.54 | 0.49 | 0.45
| PSZ-AC:2_FAN | 0.77 | 0.86 | 0.99 | 0.92 | 0.9 | 0.99 | 1.02 | 0.9 | 0.86 | 1.01 | 0.97 | 0.99 | 1.1 | 1.17 | 1.18 | 1.53
| PSZ-AC:3_FAN | 0.65 | 0.65 | 0.69 | 0.66 | 0.55 | 0.64 | 0.43 | 0.58 | 0.56 | 0.48 | 0.61 | 0.62 | 0.68 | 0.73 | 0.73 | 0.95
| PSZ-AC:4_FAN | 0.76 | 0.76 | 0.82 | 0.75 | 0.58 | 0.78 | 0.46 | 0.77 | 0.79 | 0.61 | 0.96 | 0.98 | 1.08 | 1.15 | 1.16 | 1.51
| PSZ-AC:5_FAN | 0.86 | 0.89 | 0.94 | 0.9 | 0.79 | 0.94 | 0.7 | 0.8 | 0.89 | 0.71 | 0.64 | 0.68 | 0.68 | 0.73 | 0.73 | 0.95
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.082867 | 0.12251 | 0.1157 | 0.11481 | 0.13891 | 0.10093 | 0.15704 | 0.073127 | 0.074768 | 0.072814 | 0.058994 | 0.074805 | 0.074303 | 0.075839 | 0.074066 | 0.10004
| Total Cost ($/m2) | 19.52 | 27.27 | 28.06 | 23.86 | 25.94 | 22.91 | 27.4 | 14.48 | 15.05 | 13.02 | 11.38 | 14.38 | 14.53 | 14.66 | 14.33 | 20.84
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011462 | 0.0080872 | 0.0082432 | 0.0096104 | 0.0085825 | 0.0076955 | 0.0085986 | 0.0096747 | 0.0068771 | 0.0084378 | 0.0082912 | 0.0068935 | 0.0078898 | 0.0080174 | 0.0078672 | 0.0041076
| Total Cost ($/m2) | 0.26 | 0.79 | 0.59 | 1.79 | 0.44 | 0.94 | 1.08 | 3.2 | 1.66 | 2.22 | 3.57 | 2.27 | 4.52 | 3.66 | 5.74 | 5.31
Total Utility Costs
| Cost Intensity ($/m2) | 19.78 | 28.06 | 28.65 | 25.65 | 26.38 | 23.86 | 28.48 | 17.68 | 16.7 | 15.24 | 14.96 | 16.65 | 19.05 | 18.31 | 20.07 | 26.16
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 33680.5556 | 25519.4444 | 32494.4444 | 16638.8889 | 11297.2222 | 24986.1111 | 5625 | 11900 | 13191.6667 | 4300 | 8147.2222 | 7205.5556 | 7005.5556 | 4152.7778 | 3183.3333 | 2033.3333
| Interior Lighting | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111
| Exterior Lighting | 12088.8889 | 12086.1111 | 12083.3333 | 12080.5556 | 12072.2222 | 12069.4444 | 12075 | 12069.4444 | 12072.2222 | 12050 | 12069.4444 | 12063.8889 | 12063.8889 | 12061.1111 | 12052.7778 | 11977.7778
| Interior Equipment | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 21769.4444 | 23300 | 26530.5556 | 24641.6667 | 19222.2222 | 26113.8889 | 18600 | 24336.1111 | 24725 | 22161.1111 | 25541.6667 | 26147.2222 | 28000 | 29694.4444 | 30802.7778 | 39602.7778
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 120416.6667 | 113783.3333 | 123986.1111 | 106241.6667 | 95466.6667 | 116047.2222 | 89180.5556 | 101183.3333 | 102866.6667 | 91388.8889 | 98638.8889 | 98294.4444 | 99944.4444 | 98786.1111 | 98919.4444 | 106494.4444
Gas (MJ)
| Heating | 1380 | 39420 | 26170 | 83990 | 15170 | 52130 | 52880 | 157920 | 111960 | 123280 | 208820 | 156680 | 281120 | 221230 | 360610 | 648800
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10180 | 10580 | 10350 | 10970 | 10890 | 10630 | 11220 | 11270 | 11210 | 11420 | 11530 | 11520 | 11760 | 11800 | 12140 | 12590
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11560 | 50000 | 36520 | 94950 | 26060 | 62760 | 64100 | 169190 | 123180 | 134710 | 220360 | 168200 | 292890 | 233030 | 372750 | 661390
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 445060 | 459620 | 482870 | 477420 | 369750 | 480530 | 385150 | 533440 | 493500 | 463700 | 575460 | 522060 | 652690 | 588660 | 728850 | 1044770
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 237.2056 | 179.7285 | 228.852 | 117.1844 | 79.5641 | 175.9723 | 39.6158 | 83.8094 | 92.9063 | 30.2841 | 57.3793 | 50.7473 | 49.3388 | 29.2472 | 22.4196 | 14.3204
| Interior Lighting (elec) | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982
| Exterior Lighting (elec) | 85.1397 | 85.1201 | 85.1006 | 85.081 | 85.0223 | 85.0027 | 85.0419 | 85.0027 | 85.0223 | 84.8658 | 85.0027 | 84.9636 | 84.9636 | 84.944 | 84.8854 | 84.3571
| Interior Equipment (elec) | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 153.3179 | 164.0973 | 186.8495 | 173.5464 | 135.3784 | 183.915 | 130.9962 | 171.3945 | 174.1333 | 156.0764 | 179.885 | 184.1498 | 197.1985 | 209.1322 | 216.9379 | 278.9146
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 848.0711 | 801.3538 | 873.21 | 748.2393 | 672.3531 | 817.2979 | 628.0812 | 712.6144 | 724.4698 | 643.6341 | 694.6944 | 692.2686 | 703.8892 | 695.7313 | 696.6703 | 750.0196
Gas (MJ/m2)
| Heating (gas) | 2.6997 | 77.1187 | 51.1973 | 164.3125 | 29.6776 | 101.9837 | 103.451 | 308.9444 | 219.0312 | 241.1769 | 408.5218 | 306.5185 | 549.9648 | 432.7999 | 705.4738 | 1269.2699
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 19.9155 | 20.698 | 20.2481 | 21.461 | 21.3045 | 20.7958 | 21.9501 | 22.0479 | 21.9305 | 22.3413 | 22.5565 | 22.537 | 23.0065 | 23.0847 | 23.7499 | 24.6303
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 22.6152 | 97.8167 | 71.4453 | 185.754 | 50.9821 | 122.7796 | 125.401 | 330.9923 | 240.9813 | 263.5378 | 431.0979 | 329.0555 | 572.9908 | 455.8847 | 729.2237 | 1293.9001
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 870.6863 | 899.1705 | 944.6553 | 933.9933 | 723.3547 | 940.0775 | 753.4823 | 1043.5871 | 965.4511 | 907.1524 | 1125.7923 | 1021.324 | 1276.88 | 1151.6159 | 1425.8745 | 2043.9197
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 28.6762 | 26.7046 | 25.8075 | 23.1631 | 25.063 | 23.5025 | 20.4259 | 21.1113 | 21.4371 | 20.5456 | 20.9967 | 21.447 | 21.348 | 21.5984 | 21.5685 | 22.6842
| Feb | 29.6752 | 28.301 | 27.611 | 22.9225 | 24.2548 | 24.4696 | 22.8393 | 19.4759 | 23.626 | 19.6286 | 20.9967 | 20.3226 | 18.6302 | 19.7023 | 19.0125 | 22.6842
| Mar | 30.3459 | 26.8307 | 31.605 | 26.3122 | 25.0004 | 25.8873 | 21.4816 | 23.9637 | 23.7985 | 22.0773 | 21.6324 | 23.1159 | 20.5973 | 21.7582 | 19.0773 | 22.6842
| Apr | 31.5715 | 29.9317 | 32.0943 | 28.2874 | 26.5038 | 31.4788 | 24.0146 | 24.8344 | 26.7692 | 21.4025 | 22.5835 | 24.3204 | 22.3393 | 20.8544 | 20.945 | 20.9969
| May | 33.7367 | 34.5277 | 35.7161 | 31.0812 | 25.42 | 34.1698 | 24.2849 | 27.6417 | 29.0745 | 24.6076 | 26.3403 | 26.2732 | 26.1294 | 24.2736 | 23.7187 | 23.7269
| Jun | 34.629 | 34.9265 | 42.6415 | 33.6178 | 25.7042 | 40.6441 | 24.5461 | 33.5499 | 32.1672 | 25.5508 | 30.9039 | 28.7592 | 30.5353 | 29.0766 | 26.8905 | 26.2649
| Jul | 33.7035 | 35.9481 | 41.6533 | 36.7158 | 27.2727 | 39.6101 | 26.6985 | 34.4766 | 33.3794 | 27.8574 | 31.9956 | 30.3833 | 30.1035 | 29.2567 | 29.0319 | 26.4039
| Aug | 35.0524 | 35.8691 | 42.0369 | 34.0956 | 28.679 | 38.4254 | 25.4493 | 34.8846 | 33.0426 | 26.9649 | 31.0204 | 30.4068 | 30.2979 | 27.8518 | 27.7511 | 25.8292
| Sep | 33.7155 | 34.0519 | 38.4711 | 32.0445 | 29.1573 | 37.377 | 29.8471 | 31.0816 | 29.0706 | 26.9709 | 27.8195 | 27.3815 | 26.9588 | 26.137 | 25.0234 | 21.9792
| Oct | 32.9065 | 31.5147 | 32.4288 | 29.9283 | 27.0171 | 31.5794 | 24.3135 | 27.0256 | 26.5856 | 22.449 | 23.5639 | 25.8522 | 22.6241 | 23.3578 | 21.2609 | 22.6842
| Nov | 30.7727 | 28.2988 | 29.7029 | 24.1569 | 25.5531 | 25.1025 | 21.8446 | 24.6058 | 22.9113 | 20.6754 | 23.162 | 22.6964 | 21.4754 | 21.9238 | 21.5685 | 22.6842
| Dec | 28.847 | 27.2198 | 24.8315 | 22.621 | 25.3887 | 24.3896 | 21.2126 | 20.9108 | 22.2375 | 20.5456 | 20.9967 | 21.8707 | 21.348 | 21.5984 | 21.5685 | 22.6842
Time of Peak Electrical Demand
| Jan | 24-JAN-13:00 | 03-JAN-13:00 | 26-JAN-15:39 | 23-JAN-15:00 | 26-JAN-13:00 | 30-JAN-16:00 | 27-JAN-15:09 | 05-JAN-16:00 | 25-JAN-15:20 | 02-JAN-16:30 | 02-JAN-16:30 | 12-JAN-16:00 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-13:00 | 21-FEB-14:00 | 28-FEB-15:00 | 27-FEB-15:00 | 13-FEB-11:00 | 27-FEB-14:00 | 15-FEB-15:00 | 15-FEB-15:50 | 14-FEB-15:50 | 21-FEB-13:00 | 01-FEB-16:00 | 07-FEB-14:00 | 16-FEB-14:30 | 02-FEB-15:00 | 28-FEB-13:39 | 01-FEB-08:09
| Mar | 27-MAR-14:00 | 27-MAR-15:20 | 17-MAR-15:20 | 28-MAR-15:50 | 31-MAR-14:09 | 31-MAR-14:39 | 20-MAR-14:00 | 09-MAR-15:00 | 02-MAR-15:09 | 29-MAR-15:30 | 31-MAR-15:30 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 22-MAR-14:39 | 01-MAR-08:09
| Apr | 03-APR-14:30 | 17-APR-15:30 | 26-APR-15:30 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:39 | 18-APR-15:30 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:39 | 25-APR-15:00
| May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:39 | 15-MAY-14:00 | 30-MAY-13:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 15-MAY-15:20 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:39
| Jun | 28-JUN-14:00 | 13-JUN-15:20 | 08-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 15-JUN-13:39 | 30-JUN-15:00 | 29-JUN-15:20 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 13-JUL-14:00 | 31-JUL-14:30 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-13:30 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-14:50 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-14:50 | 04-AUG-14:00 | 15-AUG-12:20 | 17-AUG-14:00 | 01-AUG-14:30 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-15:00
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:30 | 11-SEP-13:50 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-14:00 | 01-SEP-15:30 | 05-SEP-14:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
| Oct | 06-OCT-15:09 | 12-OCT-14:00 | 02-OCT-14:50 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-14:50 | 13-OCT-14:50 | 12-OCT-14:00 | 13-OCT-14:39 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:00 | 06-OCT-14:00 | 03-OCT-07:10
| Nov | 07-NOV-14:00 | 01-NOV-14:00 | 13-NOV-14:00 | 22-NOV-14:00 | 20-NOV-13:39 | 10-NOV-16:40 | 14-NOV-16:00 | 03-NOV-13:00 | 08-NOV-14:00 | 14-NOV-16:40 | 02-NOV-14:50 | 10-NOV-16:49 | 06-NOV-16:00 | 21-NOV-16:49 | 06-NOV-16:49 | 01-NOV-07:10
| Dec | 19-DEC-14:30 | 19-DEC-14:00 | 11-DEC-15:30 | 01-DEC-15:09 | 19-DEC-13:09 | 05-DEC-16:30 | 07-DEC-16:49 | 01-DEC-16:40 | 05-DEC-16:49 | 01-DEC-16:19 | 01-DEC-16:19 | 21-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 1450.55 | 1542.34 | 1451.68 | 1390.3 | 1092.16 | 1562.9 | 1063.64 | 1487.34 | 1363.23 | 720.21 | 1499.82 | 1357.78 | 1556.47 | 1490.64 | 1630.98 | 2091.67
| Total Source Energy (MJ/m2) | 2837.78 | 3017.35 | 2839.98 | 2719.91 | 2136.65 | 3057.58 | 2080.85 | 2909.75 | 2666.95 | 1408.98 | 2934.16 | 2656.28 | 3045 | 2916.2 | 3190.75 | 4092.03
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
| Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
Emissions
| Carbon Equivalent (kg) | 33232.9151 | 38855.2942 | 38086.6322 | 34438.1588 | 11626.9015 | 40271.7225 | 11577.9744 | 30355.6715 | 44241.9922 | 9085.2885 | 56562.969 | 43186.0206 | 39492.0903 | 40302.2344 | 40580.6826 | 41892.786
| CO2 (kg) | 77072.1876 | 97841.5962 | 89922.2666 | 79221.7443 | 31144.9617 | 95973.3462 | 31164.7832 | 70046.5058 | 104329.9975 | 22829.8119 | 132818.445 | 102323.3871 | 94128.1569 | 96104.9221 | 97478.5236 | 109524.1091
| NOX (kg) | 135.4095 | 127.5448 | 150.4946 | 147.9157 | 26.7238 | 154.9957 | 26.844 | 130.4299 | 177.6175 | 31.7767 | 231.3665 | 172.1109 | 157.7747 | 160.0666 | 160.0733 | 125.3267
| SO2 (kg) | 515.4379 | 542.76 | 498.5782 | 372.9289 | 277.8069 | 638.3718 | 259.5217 | 369.4038 | 449.2309 | 70.6715 | 664.8077 | 429.2761 | 235.9654 | 263.8328 | 233.5631 | 542.2743
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0023 | 0.0015 | 0.0014 | 0.0014 | 0.0001 | 0.0012 | 0.0001 | 0.0015 | 0.0018 | 0.0003 | 0.002 | 0.0017 | 0.0018 | 0.0019 | 0.0017 | 0.0019
| Water for Electricity (m3) | 63.7921 | 185.1389 | 3682.9 | 663.3218 | 1676.2 | 3183.65 | 1565.81 | 22.9723 | 467.0965 | 933.6897 | 153.0327 | 446.3341 | 155.0592 | 6257.51 | 153.4659 | 108.8028

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 47.4 | 2471.57
|  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 55.3 | 2883.5
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 78.95 | 4116.68
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
|  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
|  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 29.42 | 1534.04
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600