## BuildingSummary
Building Summary Warehouse new construction
|  | Value | Data Source
Program
| Building Name | Warehouse Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Nonrefrigerated warehouse
Form
| Total Floor Area (m2) | 4835.13 | Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory
| Building Shape | Rectangle
| Aspect Ratio | 0.45
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.0286
| East | 0
| North | 0
| West | 0.0076
| Total | 0.0058
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Bulk storage, fine storage, office
| Floor to Ceiling Height (m) | 8.53
| Floor to Floor Height (m) | 8.53
| Roof type | Metal building roof | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Metal building wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.35192
Roof
| Construction Type | Metal building roof | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4598.25
| Net Dimensions - Total Area (m2) | 4598.25
| Roof to Skin Ratio | 0.64808
Window Dimensions (m2)
| South | 11.15
| East | 0
| North | 0
| West | 6.51
| Total Area (m2) | 17.66
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 8in slab-on-grade
| Dimensions - Total Area (m2) | 4598.25
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 539.71
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9670.26
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.2 | See Reference Building Technical Report
HVAC
| System Type | PSZ-AC office, semi-conditioned storage | 2003 CBECS
| Heating Type | Gas furnace office, gas unit heaters storage | 2003 CBECS
| Cooling Type | PACU office | 2003 CBECS
| Fan Control | SZ CAV | 2003 CBECS
Service Water Heating
| SWH Type | n/a
| Fuel | n/a
| Thermal Efficiency (%) | n/a
| Temperature Setpoint (ºC ) | n/a
| Water Consumption (m3 ) | n/a

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.5601 | 17.66 | 47.376 | 5 | 11.8403 | 8.0729 |  |  | 10 |  | 50 |  | 0.16104
FineStorage | Yes | 1 | 1393.41 | 10880.57 | 7.8086 | 760.8007 | 0 |  | 0 | 15.0695 | 0 |  |  |  | 0.25 | 348.3525 |  | 0.21548
BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.6315 | 0 |  | 0 | 9.6875 | 2.691 |  |  |  | 0.25 | 801.21 |  | 0.19067
Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 88.7974 | 658.6289 | 147.5727 | 754.1966 |  | 584.3224 | 39.0954 | 621.8326 | 17.2482 | 110.7246 | 910.1259 | 175.0078 | 118.4487 | 12.4546 | 10.9617 | 0.56144
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
| R-value (m2·K / W) | 0.2291 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 1.1223 | 1.1223 | 1.1223 | 1.2407 | 1.2407 | 1.3661 | 1.3661 | 1.3661 | 1.3661
Roof
| Construction Type | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof
| R-value (m2·K / W) | 0.18847 | 1.0515 | 1.0515 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8657 | 1.8657 | 1.8657 | 1.8657 | 1.8116 | 2.5
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835
| SHGC | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| Visible transmittance | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
| R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
HVAC
HVAC Sizing
Air Conditioning (kW)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 22.0861 | 19.2571 | 18.8806 | 21.0199 | 13.7603 | 17.0576 | 13.8889 | 20.6442 | 20.0677 | 16.0568 | 24.1654 | 22.6181 | 25.1705 | 24.8526 | 25.0987 | 27.8349
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 335.1554 | 102.217 | 111.7733 | 89.7577 | 43.2529 | 70.0671 | 43.2277 | 95.5099 | 77.8327 | 55.1649 | 125.0283 | 104.5818 | 141.3315 | 110.6517 | 153.2237 | 122.3102
Heating (kW)
| BULKSTORAGE UNIT HEATER COIL | 31.4781 | 65.0562 | 35.0601 | 76.7305 | 39.2079 | 41.9101 | 36.1869 | 96.9069 | 75.8177 | 44.1586 | 154.4995 | 120.0761 | 188.0875 | 186.0076 | 207.2885 | 285.0474
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 23.8184 | 23.9123 | 19.9695 | 26.7943 | 18.2755 | 23.1599 | 20.3598 | 26.5845 | 24.4226 | 22.2641 | 31.0449 | 27.765 | 33.1375 | 32.4732 | 34.5377 | 41.8321
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 116.7284 | 105.2984 | 78.4584 | 113.243 | 57.2177 | 89.7951 | 71.229 | 124.1214 | 109.3203 | 94.0345 | 160.3218 | 139.8467 | 180.111 | 177.0725 | 192.0849 | 238.8159
HVAC Efficiency
Air Conditioning (COP)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.23 | 3.23 | 3.23 | 3.3 | 3.3 | 3.3 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
Heating Efficiency (%)
| BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BULKSTORAGE UNIT HEATERFAN | 0.8 | 1.39 | 0.8 | 1.62 | 0.8 | 0.91 | 0.8 | 1.97 | 1.89 | 0.83 | 3.24 | 3 | 4 | 4.48 | 4.53 | 5.98
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.2 | 0.98 | 1.08 | 1.14 | 0.83 | 1.03 | 0.84 | 1.08 | 1.21 | 0.97 | 1.27 | 1.37 | 1.36 | 1.5 | 1.45 | 1.68
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 17.57 | 4.23 | 5.2 | 3.65 | 1.97 | 3.43 | 2.24 | 3.85 | 4.15 | 2.94 | 5.03 | 5.28 | 5.69 | 6.3 | 6.21 | 7.39
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.097442 | 0.12068 | 0.10992 | 0.10307 | 0.13389 | 0.10192 | 0.1506 | 0.079436 | 0.037661 | 0.078372 | 0.052785 | 0.037641 | 0.063908 | 0.079676 | 0.062985 | 0.10379
| Total Cost ($/m2) | 8.66 | 6.79 | 6.77 | 5.52 | 6.42 | 5.44 | 7.26 | 4.29 | 2.05 | 3.85 | 2.93 | 2.1 | 3.62 | 4.55 | 3.62 | 6.21
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01137 | 0.0080412 | 0.0080776 | 0.009471 | 0.0088194 | 0.0075965 | 0.0087051 | 0.0096359 | 0.0068419 | 0.0084743 | 0.0082569 | 0.0068526 | 0.007924 | 0.0079517 | 0.0079006 | 0.0041052
| Total Cost ($/m2) | 0.13 | 0.5 | 0.41 | 1.01 | 0.37 | 0.62 | 0.74 | 1.61 | 0.89 | 1.2 | 1.87 | 1.26 | 2.52 | 2.07 | 3.13 | 2.74
Total Utility Costs
| Cost Intensity ($/m2) | 8.79 | 7.29 | 7.18 | 6.54 | 6.79 | 6.06 | 8 | 5.9 | 2.94 | 5.05 | 4.8 | 3.37 | 6.14 | 6.62 | 6.75 | 8.96
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 102244.4444 | 19052.7778 | 35319.4444 | 7794.4444 | 1044.4444 | 19277.7778 | 450 | 6647.2222 | 6019.4444 | 575 | 4344.4444 | 3827.7778 | 3363.8889 | 1941.6667 | 1305.5556 | 263.8889
| Interior Lighting | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778
| Exterior Lighting | 39002.7778 | 38988.8889 | 38980.5556 | 38975 | 38944.4444 | 38936.1111 | 38955.5556 | 38933.3333 | 38947.2222 | 38869.4444 | 38938.8889 | 38916.6667 | 38913.8889 | 38905.5556 | 38883.3333 | 38644.4444
| Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 108011.1111 | 33586.1111 | 42977.7778 | 31975 | 11394.4444 | 19655.5556 | 13430.5556 | 35127.7778 | 37397.2222 | 17786.1111 | 44647.2222 | 46883.3333 | 50986.1111 | 55033.3333 | 57036.1111 | 70169.4444
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 429669.4444 | 272033.3333 | 297688.8889 | 259152.7778 | 231794.4444 | 258280.5556 | 233247.2222 | 261119.4444 | 262772.2222 | 237638.8889 | 268338.8889 | 270036.1111 | 273672.2222 | 276288.8889 | 277633.3333 | 289486.1111
Gas (MJ)
| Heating | 56480 | 301980 | 244620 | 517240 | 205400 | 392460 | 408410 | 805640 | 629390 | 682230 | 1097100 | 891740 | 1537720 | 1257720 | 1918020 | 3232070
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 56480 | 301980 | 244620 | 517240 | 205400 | 392460 | 408410 | 805640 | 629390 | 682230 | 1097100 | 891740 | 1537720 | 1257720 | 1918020 | 3232070
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1603280 | 1281310 | 1316300 | 1450190 | 1039860 | 1322270 | 1248100 | 1745670 | 1575370 | 1537740 | 2063120 | 1863870 | 2522940 | 2252360 | 2917490 | 4274220
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 76.1262 | 14.1858 | 26.2971 | 5.8034 | 0.77764 | 14.3533 | 0.33505 | 4.9492 | 4.4818 | 0.42812 | 3.2347 | 2.85 | 2.5046 | 1.4457 | 0.97205 | 0.19648
| Interior Lighting (elec) | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271
| Exterior Lighting (elec) | 29.0396 | 29.0292 | 29.023 | 29.0189 | 28.9961 | 28.9899 | 29.0044 | 28.9878 | 28.9982 | 28.9403 | 28.992 | 28.9754 | 28.9734 | 28.9672 | 28.9506 | 28.7728
| Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 80.4198 | 25.0066 | 31.9991 | 23.807 | 8.4837 | 14.6346 | 9.9997 | 26.1544 | 27.8441 | 13.2427 | 33.2421 | 34.907 | 37.9618 | 40.9751 | 42.4663 | 52.2447
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 319.9107 | 202.5426 | 221.6445 | 192.9524 | 172.5827 | 192.303 | 173.6644 | 194.4167 | 195.6473 | 176.9342 | 199.7919 | 201.0556 | 203.7629 | 205.7111 | 206.7121 | 215.5371
Gas (MJ/m2)
| Heating (gas) | 11.6812 | 62.4554 | 50.5922 | 106.9754 | 42.4808 | 81.1684 | 84.4672 | 166.6222 | 130.1702 | 141.0986 | 226.9019 | 184.4294 | 318.0307 | 260.1212 | 396.6843 | 668.4557
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11.6812 | 62.4554 | 50.5922 | 106.9754 | 42.4808 | 81.1684 | 84.4672 | 166.6222 | 130.1702 | 141.0986 | 226.9019 | 184.4294 | 318.0307 | 260.1212 | 396.6843 | 668.4557
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 331.5898 | 265.0001 | 272.2367 | 299.9278 | 215.0635 | 273.4714 | 258.1316 | 361.0389 | 325.8175 | 318.0349 | 426.6938 | 385.485 | 521.7936 | 465.8324 | 603.3943 | 883.9928
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 127.2383 | 67.6128 | 69.4926 | 66.8485 | 70.5303 | 72.3603 | 70.8344 | 75.9973 | 67.7769 | 71.7569 | 78.553 | 79.0982 | 79.9579 | 81.2397 | 81.0135 | 83.6138
| Feb | 135.299 | 67.7457 | 69.5169 | 66.8485 | 61.6073 | 63.4373 | 61.9114 | 67.1833 | 67.6755 | 62.8339 | 78.3262 | 70.1752 | 71.0349 | 72.3167 | 72.0905 | 83.6138
| Mar | 141.7339 | 67.5584 | 75.087 | 66.7721 | 61.6073 | 63.4373 | 61.9114 | 67.0743 | 67.6755 | 62.8339 | 69.4032 | 70.1752 | 71.0349 | 72.3167 | 72.0905 | 74.6908
| Apr | 153.9767 | 71.1271 | 80.095 | 67.4648 | 61.6073 | 66.1814 | 61.9114 | 67.0743 | 67.9068 | 62.8339 | 69.4032 | 69.9709 | 70.7377 | 71.9747 | 72.0905 | 74.6908
| May | 173.3455 | 88.4376 | 95.9885 | 75.2994 | 62.0277 | 78.3211 | 62.1702 | 68.1548 | 74.3341 | 63.335 | 73.3444 | 74.3972 | 72.6639 | 72.5573 | 72.1976 | 74.3523
| Jun | 177.4184 | 94.6565 | 118.2406 | 85.2637 | 62.567 | 94.1524 | 62.8272 | 86.3867 | 85.9631 | 66.2054 | 87.359 | 84.3753 | 88.7366 | 88.2498 | 79.7732 | 78.0327
| Jul | 188.6094 | 101.5503 | 117.5225 | 96.6857 | 68.5909 | 93.7033 | 70.664 | 93.8074 | 90.8411 | 73.1376 | 93.4574 | 91.8588 | 88.8789 | 90.4173 | 89.125 | 81.4513
| Aug | 191.3136 | 102.3148 | 118.2138 | 91.7564 | 73.3298 | 93.3477 | 68.6033 | 95.7047 | 92.1517 | 72.2846 | 92.6229 | 94.7958 | 91.3961 | 88.5916 | 87.9027 | 82.485
| Sep | 178.715 | 93.8807 | 108.4182 | 83.0667 | 70.4346 | 92.0866 | 74.0355 | 81.8402 | 78.3105 | 69.2129 | 82.1045 | 82.2492 | 80.7948 | 80.7495 | 73.4867 | 74.4954
| Oct | 159.2686 | 79.2639 | 84.1919 | 68.5293 | 62.6317 | 70.335 | 62.5392 | 68.4819 | 68.7809 | 63.0327 | 70.1334 | 71.4269 | 71.0866 | 72.5264 | 71.744 | 83.133
| Nov | 134.2066 | 68.6891 | 71.8598 | 66.7721 | 70.5303 | 72.3603 | 70.8344 | 75.9973 | 76.5985 | 71.7569 | 78.3262 | 78.8939 | 79.6607 | 80.8977 | 81.0135 | 83.6138
| Dec | 123.8079 | 67.5584 | 69.4926 | 66.8485 | 70.5303 | 72.3603 | 70.8344 | 75.9973 | 76.5985 | 71.7569 | 78.3262 | 79.0982 | 79.9579 | 81.2397 | 81.0135 | 83.6138
Time of Peak Electrical Demand
| Jan | 25-JAN-13:30 | 11-JAN-09:09 | 02-JAN-09:09 | 02-JAN-09:09 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 02-JAN-16:49 | 04-JAN-09:09 | 02-JAN-16:30 | 06-JAN-16:30 | 05-JAN-16:49 | 02-JAN-16:40 | 03-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 24-FEB-13:09 | 21-FEB-15:39 | 28-FEB-15:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:39 | 01-FEB-09:09 | 01-FEB-16:00 | 02-FEB-09:09 | 01-FEB-09:09 | 06-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
| Mar | 27-MAR-13:30 | 01-MAR-09:09 | 17-MAR-14:00 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 02-MAR-09:09 | 01-MAR-09:09 | 02-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09
| Apr | 04-APR-13:30 | 17-APR-15:39 | 26-APR-14:00 | 14-APR-15:00 | 03-APR-08:09 | 21-APR-15:39 | 03-APR-08:09 | 03-APR-08:09 | 21-APR-15:00 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09
| May | 24-MAY-12:39 | 26-MAY-14:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-14:00 | 31-MAY-15:00 | 17-MAY-14:30 | 15-MAY-14:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 31-MAY-13:20 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:00
| Jun | 20-JUN-13:09 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:30 | 29-JUN-15:39 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 30-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 10-JUL-13:30 | 31-JUL-14:39 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-13:09 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:39 | 13-JUL-15:39 | 21-JUL-15:00 | 06-JUL-15:30 | 21-JUL-15:00
| Aug | 18-AUG-12:00 | 28-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-13:20 | 04-AUG-15:09 | 15-AUG-12:39 | 04-AUG-14:00 | 01-AUG-14:50 | 07-AUG-15:30 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:20 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-15:00
| Sep | 06-SEP-12:30 | 15-SEP-13:00 | 08-SEP-14:09 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:00 | 01-SEP-15:50 | 05-SEP-13:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
| Oct | 06-OCT-13:30 | 13-OCT-13:00 | 02-OCT-14:00 | 12-OCT-15:00 | 05-OCT-13:50 | 03-OCT-15:20 | 13-OCT-14:00 | 03-OCT-14:50 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:00 | 02-OCT-08:09 | 23-OCT-08:09
| Nov | 07-NOV-13:00 | 01-NOV-14:00 | 13-NOV-15:09 | 01-NOV-08:09 | 06-NOV-16:00 | 06-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 06-NOV-16:49 | 06-NOV-16:00 | 08-NOV-16:00 | 24-NOV-16:30 | 01-NOV-08:09
| Dec | 14-DEC-13:09 | 01-DEC-09:09 | 01-DEC-09:09 | 22-DEC-09:09 | 01-DEC-16:49 | 01-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 13-DEC-16:30 | 08-DEC-16:40 | 05-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 5192.43 | 3886.67 | 3656.84 | 3703.27 | 2806.94 | 3754.49 | 3044.83 | 4241.3 | 3826.06 | 2235.28 | 4623.55 | 4199.32 | 5065.39 | 4830.79 | 5529.67 | 7251.98
| Total Source Energy (MJ/m2) | 1073.9 | 803.84 | 756.31 | 765.91 | 580.53 | 776.5 | 629.73 | 877.18 | 791.3 | 462.3 | 956.24 | 868.5 | 1047.62 | 999.1 | 1143.65 | 1499.85
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 118854.8288 | 96185.593 | 94275.858 | 89155.7906 | 30792.6881 | 94188.5279 | 34623.3568 | 84992.2456 | 118691.5983 | 29610.777 | 162848.884 | 126390.2137 | 121405.4286 | 123646.1797 | 129618.5793 | 139740.7041
| CO2 (kg) | 275798.9753 | 243426.0182 | 224079.3837 | 208127.0432 | 83023.7778 | 226771.5865 | 94054.0498 | 199992.6242 | 282908.4989 | 76659.7595 | 387249.1216 | 303491.997 | 296075.643 | 300361.1448 | 319013.7512 | 372443.795
| NOX (kg) | 483.8826 | 313.5651 | 368.7603 | 374.3218 | 71.6071 | 356.9206 | 81.5976 | 354.0501 | 468.6105 | 98.3316 | 652.9526 | 493.1525 | 466.8225 | 476.3428 | 490.5125 | 408.5163
| SO2 (kg) | 1839.1666 | 1297.685 | 1197.1278 | 909.7654 | 674.5479 | 1420.8525 | 678.8328 | 953.4036 | 1147.6426 | 183.8597 | 1808.6901 | 1179.4384 | 646.3228 | 738.06 | 655.7702 | 1474.466
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0084 | 0.0037 | 0.0033 | 0.0034 | 0.0003 | 0.0027 | 0.0003 | 0.0039 | 0.0045 | 0.0008 | 0.0056 | 0.0047 | 0.0049 | 0.0053 | 0.005 | 0.0053
| Water for Electricity (m3) | 227.6201 | 442.6318 | 8842.64 | 1618.05 | 4069.78 | 7085.66 | 4095.31 | 59.2838 | 1193.2 | 2427.92 | 416.3133 | 1226.19 | 424.5864 | 17501.3 | 430.7296 | 295.7621

## Picture
DOE Commercial Building Benchmark - Warehouse

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8 | 4485.6 | 233892
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 3972 | 207111.43
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
|  |  | Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HTGSETP_BulkStorage_SCH | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
HTGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2584 | 134737.14
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
|  |  | Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0