## BuildingSummary
Building Summary Warehouse pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Warehouse Reference Building pre-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Nonrefrigerated warehouse
Form
| Total Floor Area (m2) | 4835.13 | Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory
| Building Shape | Rectangle
| Aspect Ratio | 0.45
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.0286
| East | 0
| North | 0
| West | 0.0076
| Total | 0.0058
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Bulk storage, fine storage, office
| Floor to Ceiling Height (m) | 8.53
| Floor to Floor Height (m) | 8.53
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Metal building wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.35192
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4598.25
| Net Dimensions - Total Area (m2) | 4598.25
| Roof to Skin Ratio | 0.64808
Window Dimensions (m2)
| South | 11.15
| East | 0
| North | 0
| West | 6.51
| Total Area (m2) | 17.66
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 8in slab-on-grade
| Dimensions - Total Area (m2) | 4598.25
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 539.71
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9670.26
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.74 | See Reference Building Technical Report
HVAC
| System Type | PSZ-AC office, semi-conditioned storage | 2003 CBECS
| Heating Type | Gas furnace office, gas unit heaters storage | 2003 CBECS
| Cooling Type | PACU office | 2003 CBECS
| Fan Control | SZ CAV | 2003 CBECS
Service Water Heating
| SWH Type | n/a
| Fuel | n/a
| Thermal Efficiency (%) | n/a
| Temperature Setpoint (ºC ) | n/a
| Water Consumption (m3 ) | n/a

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.5601 | 17.66 | 47.376 | 5 | 21.6974 | 8.0729 |  |  | 10 |  | 50 |  | 0.60391
FineStorage | Yes | 1 | 1393.41 | 10880.57 | 7.8086 | 760.8007 | 0 |  | 0 | 11.6478 | 0 |  |  |  | 0.25 | 348.3525 |  | 0.80806
BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.6315 | 0 |  | 0 | 3.3409 | 2.691 |  |  |  | 0.25 | 801.21 |  | 0.71502
Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Weighting Factor
Fabric
Exterior walls
| Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
| R-value (m2·K / W) | 0.57405 | 0.57405 | 0.57405 | 0.59137 | 0.57405 | 0.57405 | 0.59453 | 0.79808 | 0.7657 | 0.815 | 0.93721 | 0.90253 | 1.0235 | 1.0235 | 1.1038 | 1.218
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
| R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
HVAC
HVAC Sizing
Air Conditioning (kW)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 27.248 | 32.9452 | 30.3039 | 36.2581 | 19.4417 | 25.595 | 19.6895 | 37.9489 | 30.93 | 23.6698 | 46.662 | 36.0606 | 50.0172 | 41.1476 | 50.0633 | 48.9196
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 78.6252 | 125.9396 | 131.5553 | 159.2472 | 70.6886 | 111.3702 | 71.9944 | 173.5643 | 150.0761 | 106.0719 | 230.6689 | 213.8104 | 261.8887 | 222.7025 | 282.8402 | 246.5494
Heating (kW)
| BULKSTORAGE UNIT HEATER COIL | 39.3476 | 111.5083 | 35.0601 | 172.4346 | 39.2079 | 97.4243 | 37.1186 | 217.6959 | 166.0511 | 117.8466 | 334.185 | 260.6949 | 398.2948 | 380.4253 | 430.388 | 644.5138
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 23.2358 | 34.7697 | 27.9385 | 39.8129 | 24.8557 | 33.2005 | 28.4218 | 41.8491 | 36.8547 | 33.9521 | 49.6677 | 43.1285 | 54.2757 | 52.1468 | 56.0797 | 70.7263
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 75.2655 | 156.8091 | 111.5441 | 191.8255 | 87.5293 | 145.9623 | 113.4103 | 216.5627 | 181.1002 | 160.9056 | 283.3746 | 238.0026 | 319.479 | 305.3987 | 337.699 | 457.3434
HVAC Efficiency
Air Conditioning (COP)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.3
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.13 | 3.23 | 3.13 | 3.13 | 3.13 | 3.13
Heating Efficiency (%)
| BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BULKSTORAGE UNIT HEATERFAN | 0.8 | 2.54 | 0.8 | 4.09 | 0.8 | 2.4 | 0.82 | 4.99 | 4.62 | 2.68 | 7.8 | 7.25 | 9.38 | 10.04 | 10.36 | 15.04
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.17 | 1.46 | 1.61 | 1.72 | 1.05 | 1.53 | 1.19 | 1.74 | 1.87 | 1.43 | 2.1 | 2.18 | 2.31 | 2.49 | 2.43 | 2.96
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 3.17 | 5.07 | 5.3 | 6.41 | 2.85 | 5.1 | 3.66 | 6.99 | 7.1 | 5.24 | 9.29 | 9.32 | 10.55 | 11.3 | 11.39 | 14.89
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.087054 | 0.12197 | 0.11096 | 0.10419 | 0.13311 | 0.10154 | 0.14959 | 0.078736 | 0.037738 | 0.072453 | 0.053014 | 0.037692 | 0.06261 | 0.077933 | 0.060786 | 0.10003
| Total Cost ($/m2) | 3.63 | 5.79 | 5.97 | 4.97 | 5.01 | 5.2 | 6.18 | 3.87 | 1.85 | 3.2 | 2.77 | 1.96 | 3.31 | 4.17 | 3.32 | 6.11
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011403 | 0.0080456 | 0.0080763 | 0.0094639 | 0.0087791 | 0.0075985 | 0.0086542 | 0.0096475 | 0.0068385 | 0.0084571 | 0.0082569 | 0.0068581 | 0.0079169 | 0.0079687 | 0.0078875 | 0.0041044
| Total Cost ($/m2) | 0.12 | 0.91 | 0.64 | 2.1 | 0.6 | 1.08 | 1.29 | 3.66 | 1.93 | 2.28 | 4.41 | 2.84 | 6.03 | 4.72 | 7.45 | 6.83
Total Utility Costs
| Cost Intensity ($/m2) | 3.75 | 6.7 | 6.61 | 7.07 | 5.61 | 6.27 | 7.46 | 7.52 | 3.78 | 5.49 | 7.18 | 4.8 | 9.34 | 8.89 | 10.77 | 12.94
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 19680.5556 | 22222.2222 | 47672.2222 | 10891.6667 | 783.3333 | 35166.6667 | 433.3333 | 9358.3333 | 8297.2222 | 486.1111 | 5497.2222 | 4838.8889 | 3663.8889 | 2077.7778 | 1147.2222 | 113.8889
| Interior Lighting | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111
| Exterior Lighting | 47897.2222 | 47877.7778 | 47869.4444 | 47863.8889 | 47825 | 47813.8889 | 47841.6667 | 47811.1111 | 47830.5556 | 47736.1111 | 47819.4444 | 47791.6667 | 47788.8889 | 47777.7778 | 47750 | 47458.3333
| Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 16633.3333 | 41936.1111 | 47183.3333 | 54197.2222 | 15986.1111 | 46900 | 33902.7778 | 62700 | 63863.8889 | 48077.7778 | 81436.1111 | 81752.7778 | 86791.6667 | 91361.1111 | 97372.2222 | 130083.3333
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 201777.7778 | 229605.5556 | 260291.6667 | 230516.6667 | 182161.1111 | 247450 | 199741.6667 | 237433.3333 | 237558.3333 | 213866.6667 | 252319.4444 | 251950 | 255811.1111 | 258783.3333 | 263833.3333 | 295222.2222
Gas (MJ)
| Heating | 49380 | 544500 | 381420 | 1072030 | 329020 | 685660 | 717970 | 1832410 | 1362090 | 1305340 | 2581860 | 2000690 | 3683010 | 2861730 | 4569090 | 8044240
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 49380 | 544500 | 381420 | 1072030 | 329020 | 685660 | 717970 | 1832410 | 1362090 | 1305340 | 2581860 | 2000690 | 3683010 | 2861730 | 4569090 | 8044240
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 775780 | 1371080 | 1318470 | 1901890 | 984810 | 1576480 | 1437040 | 2687170 | 2217300 | 2075250 | 3490220 | 2907710 | 4603920 | 3793350 | 5518890 | 9107040
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 14.6532 | 16.5456 | 35.4944 | 8.1094 | 0.58323 | 26.1834 | 0.32264 | 6.9678 | 6.1777 | 0.36193 | 4.093 | 3.6028 | 2.728 | 1.547 | 0.85417 | 0.084796
| Interior Lighting (elec) | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382
| Exterior Lighting (elec) | 35.6619 | 35.6474 | 35.6412 | 35.6371 | 35.6081 | 35.5999 | 35.6206 | 35.5978 | 35.6123 | 35.542 | 35.604 | 35.5833 | 35.5813 | 35.573 | 35.5523 | 35.3351
| Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 12.3844 | 31.2236 | 35.1304 | 40.3526 | 11.9025 | 34.9194 | 25.2423 | 46.6833 | 47.5499 | 35.7963 | 60.6333 | 60.8691 | 64.6208 | 68.023 | 72.4986 | 96.8537
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 150.2338 | 170.953 | 193.8004 | 171.6314 | 135.6282 | 184.2391 | 148.7178 | 176.7812 | 176.8743 | 159.2346 | 187.8646 | 187.5896 | 190.4644 | 192.6773 | 196.4373 | 219.8079
Gas (MJ/m2)
| Heating (gas) | 10.2128 | 112.6133 | 78.8852 | 221.7169 | 68.0478 | 141.808 | 148.4903 | 378.9784 | 281.707 | 269.97 | 533.9794 | 413.782 | 761.7189 | 591.8621 | 944.9777 | 1663.7071
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10.2128 | 112.6133 | 78.8852 | 221.7169 | 68.0478 | 141.808 | 148.4903 | 378.9784 | 281.707 | 269.97 | 533.9794 | 413.782 | 761.7189 | 591.8621 | 944.9777 | 1663.7071
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 160.4466 | 283.5663 | 272.6855 | 393.3483 | 203.6781 | 326.0471 | 297.2081 | 555.7596 | 458.5813 | 429.2025 | 721.8462 | 601.3716 | 952.1812 | 784.5394 | 1141.415 | 1883.515
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 44.0366 | 49.7582 | 49.7915 | 52.2526 | 53.2978 | 60.2407 | 57.3376 | 64.4005 | 53.7538 | 60.558 | 69.098 | 69.1956 | 70.1791 | 71.7216 | 71.8382 | 78.6181
| Feb | 44.4626 | 50.452 | 50.6311 | 52.2526 | 42.3398 | 49.2827 | 46.3796 | 53.4425 | 53.7538 | 49.6 | 69.098 | 58.2376 | 59.2211 | 60.7636 | 60.8802 | 78.6181
| Mar | 45.0924 | 49.859 | 57.1316 | 52.3119 | 42.3679 | 49.6108 | 46.3796 | 53.4425 | 53.7538 | 49.6 | 58.14 | 58.2376 | 59.2211 | 60.7636 | 60.8802 | 71.1942
| Apr | 48.9801 | 51.3729 | 61.7029 | 53.7895 | 43.1801 | 61.3622 | 46.3796 | 53.4789 | 54.5582 | 49.4253 | 57.4898 | 58.2376 | 59.2211 | 60.7636 | 60.8802 | 67.6601
| May | 65.511 | 75.3642 | 82.7734 | 66.23 | 42.9807 | 77.9361 | 47.1939 | 55.8539 | 65.4079 | 50.3031 | 64.7055 | 65.1386 | 61.1183 | 60.9206 | 60.7379 | 66.338
| Jun | 72.96 | 82.3739 | 110.0547 | 81.2429 | 43.7687 | 99.049 | 47.7798 | 84.9365 | 80.6403 | 53.0922 | 87.3049 | 79.0519 | 84.9147 | 83.4411 | 68.7304 | 71.8282
| Jul | 72.0442 | 90.778 | 109.3314 | 97.6262 | 49.0935 | 98.1096 | 58.7102 | 95.5898 | 87.9215 | 63.8821 | 93.6473 | 88.2857 | 85.4182 | 84.7276 | 82.2027 | 75.6348
| Aug | 74.1855 | 93.5159 | 110.0632 | 88.1803 | 55.6992 | 97.4618 | 54.0328 | 95.5455 | 88.0346 | 60.6601 | 91.3503 | 91.4062 | 86.1794 | 82.2658 | 79.249 | 76.3452
| Sep | 70.491 | 82.6747 | 99.1625 | 74.8371 | 54.8912 | 95.4767 | 66.6313 | 75.6055 | 66.7372 | 58.7185 | 74.9776 | 75.1434 | 71.0862 | 69.3882 | 62.4136 | 66.338
| Oct | 59.7616 | 64.5602 | 67.9732 | 58.5282 | 44.4113 | 64.8793 | 47.412 | 55.5632 | 55.2402 | 49.4253 | 58.7513 | 60.6439 | 58.8108 | 63.4393 | 59.9927 | 78.6181
| Nov | 45.811 | 51.2246 | 53.924 | 51.9473 | 53.2978 | 60.2407 | 57.3376 | 64.0116 | 64.3575 | 60.3833 | 68.4478 | 69.1956 | 70.1791 | 71.7216 | 71.8382 | 78.6181
| Dec | 44.3469 | 50.2479 | 49.7427 | 52.2526 | 53.2978 | 60.2407 | 57.3376 | 64.4005 | 64.7118 | 60.558 | 69.098 | 69.1956 | 70.1791 | 71.7216 | 71.8382 | 78.6181
Time of Peak Electrical Demand
| Jan | 23-JAN-15:30 | 03-JAN-14:30 | 26-JAN-15:00 | 02-JAN-09:09 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 10-JAN-16:00 | 02-JAN-09:09 | 02-JAN-16:40 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 22-FEB-15:00 | 21-FEB-14:00 | 28-FEB-15:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-16:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
| Mar | 13-MAR-15:00 | 27-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:39 | 31-MAR-14:00 | 01-MAR-09:09 | 01-MAR-09:09 | 13-MAR-08:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-08:09
| Apr | 03-APR-14:00 | 21-APR-14:00 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:30 | 03-APR-08:09 | 05-APR-15:00 | 21-APR-15:00 | 03-APR-08:09 | 03-APR-08:09 | 04-APR-08:09 | 04-APR-08:09 | 04-APR-08:09 | 03-APR-08:09 | 03-APR-08:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-10:00 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 15-MAY-15:00 | 16-MAY-15:00 | 31-MAY-15:00 | 01-MAY-08:09
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-15:20 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 30-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 10-JUL-13:50 | 31-JUL-13:00 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:50 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-14:50 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-15:20 | 15-AUG-12:09 | 17-AUG-14:00 | 01-AUG-14:09 | 07-AUG-15:30 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-15:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:00 | 01-SEP-15:00 | 05-SEP-13:00 | 06-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 01-SEP-08:09
| Oct | 06-OCT-14:30 | 06-OCT-15:00 | 02-OCT-15:50 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:20 | 30-OCT-13:50 | 03-OCT-14:09 | 13-OCT-14:00 | 02-OCT-08:09 | 31-OCT-13:39 | 05-OCT-15:00 | 06-OCT-14:00 | 30-OCT-07:10 | 02-OCT-08:09 | 23-OCT-08:09
| Nov | 07-NOV-14:00 | 03-NOV-14:30 | 13-NOV-15:00 | 01-NOV-08:09 | 06-NOV-16:00 | 06-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 17-NOV-16:40 | 13-NOV-16:49 | 29-NOV-16:40 | 10-NOV-16:40 | 01-NOV-08:09
| Dec | 19-DEC-14:30 | 19-DEC-15:30 | 01-DEC-09:09 | 07-DEC-09:09 | 01-DEC-16:49 | 01-DEC-16:30 | 01-DEC-16:49 | 14-DEC-16:40 | 21-DEC-16:00 | 11-DEC-16:40 | 05-DEC-16:19 | 01-DEC-16:40 | 04-DEC-16:30 | 04-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 2463.39 | 3596.73 | 3380.41 | 3962.31 | 2388.95 | 3935.19 | 3009.55 | 5057.62 | 4324.98 | 2766.62 | 6040.42 | 5194.26 | 7187.03 | 6363.33 | 8253.91 | 12580.62
| Total Source Energy (MJ/m2) | 509.48 | 743.87 | 699.14 | 819.48 | 494.08 | 813.88 | 622.44 | 1046.02 | 894.49 | 572.19 | 1249.28 | 1074.28 | 1486.42 | 1316.06 | 1707.07 | 2601.92
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 56228.0116 | 86406.0734 | 85454.0759 | 90339.4145 | 27221.7229 | 95822.7307 | 36290.0332 | 97116.2498 | 121604.1271 | 39115.4473 | 181082.5028 | 138999.4077 | 153976.5455 | 146174.229 | 172701.5099 | 228130.9782
| CO2 (kg) | 130709.7638 | 220547.8352 | 204659.1223 | 217012.0853 | 73978.9249 | 233395.1587 | 99728.3437 | 239154.233 | 297082.0281 | 105010.1372 | 444899.575 | 344053.1152 | 393749.362 | 369052.3876 | 446245.9936 | 627200.4144
| NOX (kg) | 228.319 | 278.3571 | 330.3614 | 361.9054 | 64.2023 | 356.6 | 87.2937 | 373.959 | 461.1582 | 121.1953 | 687.3 | 515.4011 | 542.5725 | 525.8032 | 596.0385 | 641.1964
| SO2 (kg) | 863.7043 | 1095.3618 | 1046.7919 | 809.403 | 530.1585 | 1361.3524 | 581.4187 | 867.2216 | 1037.7334 | 165.6508 | 1701.1308 | 1100.7564 | 604.7394 | 691.7522 | 623.9144 | 1504.9489
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0039 | 0.0031 | 0.0029 | 0.0031 | 0.0003 | 0.0026 | 0.0003 | 0.0037 | 0.0042 | 0.0008 | 0.0054 | 0.0045 | 0.0048 | 0.0051 | 0.005 | 0.006
| Water for Electricity (m3) | 106.8936 | 373.5942 | 7731.84 | 1439.26 | 3198.36 | 6788.52 | 3507.03 | 53.9065 | 1078.7 | 2185.02 | 391.4603 | 1144.06 | 396.8738 | 16392.5 | 409.3223 | 301.6214

## Picture
DOE Commercial Building Benchmark - Warehouse

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8 | 4485.6 | 233892
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 3972 | 207111.43
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
|  |  | Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HTGSETP_BulkStorage_SCH | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
HTGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2584 | 134737.14
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
|  |  | Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0