## BuildingSummary
Building Summary Full Service Restaurant new construction
|  | Value | Data Source
Program
| Building Name | Full Service Restaurant
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Service
Form |  |  | Time Saver Standards; Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991 for all Form parameters
| Total Floor Area (m2) | 511.15
| Building Shape | Rectangle
| Aspect Ratio | 1
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.28
| East | 0.224
| North | 0
| West | 0.224
| Total | 0.182
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 2 zones plus attic
| Floor to Ceiling Height (m) | 3.048
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 275.72
| Net Dimensions - Total Area (m2) | 225.54
| Wall to Skin Ratio | 0.326
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 569.52
| Net Dimensions - Total Area (m2) | 569.52
| Roof to Skin Ratio | 0.674
| Window Dimensions (m2) |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991
| South | 19.3
| East | 15.44
| North | 0
| West | 15.44
| Total Area (m2) | 50.18
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab-on-grade
| Dimensions - Total Area (m2) | 511.15
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 68.93
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.31
| Thermal diffusivity (m2/s) | 1.84e-07
| Air Barrier System |  | See Benchmark Technical Report
| Infiltration (ACH) | 0.55
HVAC |  |  | 2003 CBECS
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas | Standard 90.1-2004
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 140
| Water Consumption (m3 ) | 1375.88

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Dining | Yes | 1 | 371.75 | 1133.39 | 3.0488 | 169.19 | 47.17 | 1.3935 | 266.7653 | 22.596 | 60.256 | 0 | 0 | 10 | 0 | 2667.6532 | 0 | 0.51945
Kitchen | Yes | 1 | 139.41 | 425.02 | 3.0487 | 106.53 | 0 | 18.5806 | 7.503 | 12.912 | 376.6 | 1197.9108 | 503.4582 | 8 | 0 | 60.0238 | 1887.788 | 0.62979
Attic | No | 1 | 511.15 | 856.26 | 1.6752 | 0 | 0 | [10 empty] | 1
Total Conditioned Zones |  |  | 511.16 | 1558.41 |  | 275.72 | 47.17 |  | 274.2683
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 21.72 | 253.9818 | 59.0764 | 267.6909 |  | 114.1855 | 13.8582 | 305.8982 | 13.9891 | 24.5709 | 344.1964 | 74.7018 | 74.6182 | 9.6255 | 8.8145 | 0.33091
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 6.5229 | 6.5229 | 6.5229 | 6.5229
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor
| Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_COOLC DXCOIL | 74.9277 | 75.7114 | 75.9793 | 74.48 | 69.2363 | 73.9357 | 54.673 | 73.1414 | 68.734 | 58.1859 | 72.4041 | 67.927 | 72.255 | 55.5828 | 69.0085 | 45.1727
| PSZ-AC_2:2_COOLC DXCOIL | 18.3269 | 18.3088 | 18.1524 | 18.7909 | 14.5712 | 18.2861 | 8.4446 | 17.5739 | 15.5744 | 11.2631 | 16.9095 | 13.9263 | 16.9311 | 12.2896 | 10.5047 | 8.7949
Heating (kW)
| PSZ-AC_1:1_HEATC | 111.4264 | 145.2702 | 123.8351 | 154.6524 | 110.2945 | 131.1066 | 121.6818 | 170.3419 | 141.7602 | 143.5714 | 197.1803 | 165.5657 | 212.4803 | 196.2191 | 214.3996 | 263.9041
| PSZ-AC_2:2_HEATC | 28.5733 | 37.6835 | 31.5217 | 41.721 | 25.79 | 34.3268 | 22.7049 | 43.4351 | 41.1958 | 32.4957 | 48.8231 | 47.2765 | 52.8305 | 52.4203 | 50.3304 | 52.182
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_COOLC DXCOIL | 3.11 | 3.11 | 3.11 | 3.11 | 3.19 | 3.11 | 3.32 | 3.11 | 3.28 | 3.27 | 3.11 | 3.27 | 3.11 | 3.37 | 3.19 | 3.45
| PSZ-AC_2:2_COOLC DXCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.72 | 3.65 | 4.04 | 3.65 | 3.91 | 3.91 | 3.65 | 3.99 | 3.65 | 4.04 | 4.04 | 4.04
Heating Efficiency (%)
| PSZ-AC_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_1:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| DINING EXHAUST FAN | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83
| KITCHEN EXHAUST FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| PSZ-AC_1:1_FAN | 3.02 | 3.05 | 3.06 | 3 | 2.79 | 2.98 | 2.79 | 2.95 | 3.27 | 2.75 | 2.92 | 3.2 | 2.91 | 3.04 | 2.78 | 2.73
| PSZ-AC_2:2_FAN | 0.74 | 0.74 | 0.73 | 0.76 | 0.64 | 0.74 | 0.51 | 0.71 | 0.84 | 0.61 | 0.68 | 0.81 | 0.68 | 0.74 | 0.63 | 0.53
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.077041 | 0.10752 | 0.095919 | 0.10393 | 0.12511 | 0.094332 | 0.14532 | 0.067088 | 0.037548 | 0.072245 | 0.052365 | 0.037568 | 0.052917 | 0.06845 | 0.051942 | 0.087706
| Total Cost ($/m2) | 59.02 | 75.47 | 66.75 | 66.03 | 72.23 | 61.67 | 80.41 | 41.13 | 22.81 | 40.26 | 31.1 | 22.1 | 31.15 | 39.06 | 29.06 | 48.17
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011467 | 0.0081839 | 0.0085659 | 0.010565 | 0.0084206 | 0.0080961 | 0.0084347 | 0.0099723 | 0.0071388 | 0.0083199 | 0.0087285 | 0.0071287 | 0.0079303 | 0.0085605 | 0.007925 | 0.004169
| Total Cost ($/m2) | 21.02 | 18.65 | 18.31 | 28.59 | 18.26 | 19.33 | 22.93 | 33.24 | 20.58 | 27.46 | 33.55 | 23.82 | 34.56 | 34.11 | 39.54 | 27.89
Total Utility Costs
| Cost Intensity ($/m2) | 80.04 | 94.12 | 85.07 | 94.62 | 90.49 | 81.01 | 103.34 | 74.38 | 43.4 | 67.72 | 64.65 | 45.92 | 65.71 | 73.17 | 68.6 | 76.06
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 106277.7778 | 73922.2222 | 70902.7778 | 40825 | 13777.7778 | 50472.2222 | 3283.3333 | 30805.5556 | 24255.5556 | 5086.1111 | 21780.5556 | 15572.2222 | 19202.7778 | 8688.8889 | 6208.3333 | 2216.6667
| Interior Lighting | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222
| Exterior Lighting | 3908.3333 | 3902.7778 | 3900 | 3908.3333 | 3905.5556 | 3902.7778 | 3900 | 3902.7778 | 3902.7778 | 3897.2222 | 3897.2222 | 3897.2222 | 3900 | 3894.4444 | 3894.4444 | 3872.2222
| Interior Equipment | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 30338.8889 | 30583.3333 | 30616.6667 | 30352.7778 | 27683.3333 | 30005.5556 | 26591.6667 | 29505.5556 | 33288.8889 | 27105.5556 | 29050 | 32408.3333 | 29063.8889 | 30633.3333 | 27647.2222 | 26775
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 18780.5556 | 18077.7778 | 18011.1111 | 17369.4444 | 17419.4444 | 17508.3333 | 16772.2222 | 16891.6667 | 16836.1111 | 16472.2222 | 16575 | 16488.8889 | 16422.2222 | 16172.2222 | 15947.2222 | 15569.4444
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 391605.5556 | 358786.1111 | 355733.3333 | 324755.5556 | 295086.1111 | 334188.8889 | 282847.2222 | 313405.5556 | 310586.1111 | 284858.3333 | 303605.5556 | 300666.6667 | 300888.8889 | 291688.8889 | 285997.2222 | 280730.5556
Gas (MJ)
| Heating | 14670 | 211280 | 157340 | 399840 | 131180 | 263480 | 386450 | 697040 | 471400 | 667720 | 937050 | 681760 | 1182440 | 988000 | 1475580 | 2308940
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 121380 | 152460 | 134590 | 182410 | 176600 | 156110 | 202220 | 205940 | 201480 | 218200 | 226610 | 225530 | 244460 | 247700 | 273910 | 309550
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 936980 | 1164660 | 1092850 | 1383170 | 1108690 | 1220510 | 1389590 | 1703910 | 1473800 | 1686840 | 1964580 | 1708210 | 2227820 | 2036630 | 2550410 | 3419400
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2346750 | 2456290 | 2373490 | 2552290 | 2171000 | 2423590 | 2407830 | 2832160 | 2591920 | 2712330 | 3057560 | 2790610 | 3311020 | 3086710 | 3580000 | 4430030
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 748.5083 | 520.63 | 499.3642 | 287.5281 | 97.0361 | 355.473 | 23.1243 | 216.9618 | 170.8305 | 35.8212 | 153.3992 | 109.6743 | 135.2441 | 61.1953 | 43.7249 | 15.6119
| Interior Lighting (elec) | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103
| Exterior Lighting (elec) | 27.5262 | 27.487 | 27.4675 | 27.5262 | 27.5066 | 27.487 | 27.4675 | 27.487 | 27.487 | 27.4479 | 27.4479 | 27.4479 | 27.4675 | 27.4283 | 27.4283 | 27.2718
| Interior Equipment (elec) | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 213.675 | 215.3967 | 215.6314 | 213.7729 | 194.9721 | 211.3274 | 187.2836 | 207.8059 | 234.4517 | 190.9029 | 204.5975 | 228.25 | 204.6953 | 215.7488 | 194.7178 | 188.5748
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 132.2704 | 127.3207 | 126.8512 | 122.332 | 122.6841 | 123.3102 | 118.1258 | 118.967 | 118.5758 | 116.0129 | 116.7368 | 116.1303 | 115.6608 | 113.9 | 112.3154 | 109.6547
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2758.0554 | 2526.9099 | 2505.4094 | 2287.2347 | 2078.2745 | 2353.6731 | 1992.0767 | 2207.2973 | 2187.4401 | 2006.2408 | 2138.2764 | 2117.578 | 2119.1431 | 2054.348 | 2014.262 | 1977.1691
Gas (MJ/m2)
| Heating (gas) | 28.7 | 413.3425 | 307.8157 | 782.2361 | 256.637 | 515.4651 | 756.0403 | 1363.6702 | 922.2342 | 1306.3093 | 1833.2192 | 1333.7768 | 2313.2936 | 1932.8964 | 2886.7847 | 4517.1476
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 237.4645 | 298.2686 | 263.3082 | 356.862 | 345.4955 | 305.4094 | 395.6177 | 402.8954 | 394.17 | 426.8806 | 443.3337 | 441.2208 | 478.2549 | 484.5936 | 535.8701 | 605.5952
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1833.0823 | 2278.5092 | 2138.0221 | 2705.9963 | 2169.0111 | 2387.7727 | 2718.5562 | 3333.4833 | 2883.3024 | 3300.088 | 3843.451 | 3341.8957 | 4358.4466 | 3984.4077 | 4989.553 | 6689.6214
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 4591.1181 | 4805.4192 | 4643.4315 | 4993.2309 | 4247.2855 | 4741.4458 | 4710.6133 | 5540.761 | 5070.762 | 5306.3289 | 5981.7275 | 5459.4737 | 6477.5897 | 6038.7557 | 7003.8149 | 8666.7906
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 66.0594 | 62.5272 | 50.6986 | 44.4299 | 54.4377 | 44.8776 | 43.1194 | 43.5522 | 44.0149 | 43.1841 | 43.4274 | 44.2386 | 43.4066 | 43.6319 | 43.2076 | 43.8516
| Feb | 67.0248 | 58.3394 | 53.8471 | 46.3213 | 55.0156 | 47.1193 | 47.348 | 43.5041 | 45.7332 | 43.1728 | 43.43 | 43.8941 | 43.4089 | 43.6485 | 43.214 | 43.0094
| Mar | 67.3242 | 63.7858 | 62.2882 | 52.769 | 52.4129 | 50.8741 | 43.1274 | 52.5401 | 46.9775 | 44.8518 | 46.7537 | 51.0311 | 43.4376 | 47.0999 | 43.2221 | 43.0288
| Apr | 68.7582 | 67.5374 | 64.7426 | 60.5712 | 55.5144 | 62.7687 | 48.3474 | 53.727 | 54.671 | 46.8774 | 47.0275 | 50.9866 | 52.2269 | 46.0993 | 43.2417 | 43.0382
| May | 70.3627 | 71.2712 | 73.7696 | 68.3664 | 57.1821 | 67.5465 | 50.2628 | 63.3885 | 59.9029 | 51.6228 | 62.5702 | 56.6014 | 68.3617 | 52.0158 | 49.8353 | 45.8453
| Jun | 71.3552 | 71.6003 | 78.4101 | 69.0803 | 54.9565 | 76.0249 | 52.5593 | 70.6061 | 63.2708 | 54.7655 | 69.0665 | 62.4902 | 69.0489 | 60.5108 | 60.2294 | 53.618
| Jul | 71.2235 | 72.4318 | 77.809 | 72.2694 | 58.7438 | 74.8778 | 58.129 | 71.495 | 65.4643 | 57.2168 | 70.791 | 63.3512 | 69.1178 | 61.0935 | 64.7056 | 55.0917
| Aug | 71.0056 | 72.3287 | 78.1605 | 70.3339 | 62.7923 | 74.4796 | 55.7416 | 70.9798 | 65.2294 | 56.6982 | 69.1132 | 64.3583 | 68.8213 | 60.0631 | 62.3728 | 52.4432
| Sep | 71.0244 | 71.4303 | 74.6639 | 67.2762 | 63.9282 | 71.3889 | 58.7823 | 65.2492 | 59.6003 | 62.7928 | 64.0153 | 58.9278 | 59.6698 | 57.1984 | 53.4839 | 43.0651
| Oct | 70.7495 | 69.3255 | 64.4463 | 61.4684 | 58.3613 | 62.1775 | 50.058 | 60.9454 | 54.5544 | 47.1813 | 55.6186 | 53.9812 | 55.3383 | 49.5042 | 50.1773 | 43.0476
| Nov | 68.701 | 65.3254 | 59.3889 | 50.6779 | 55.278 | 49.1606 | 43.1393 | 55.7489 | 45.0447 | 43.202 | 55.5303 | 47.2024 | 43.4377 | 43.6513 | 43.2595 | 43.0205
| Dec | 63.9757 | 64.7328 | 50.6339 | 46.3446 | 55.1379 | 48.3336 | 43.1285 | 43.5432 | 44.0108 | 43.1799 | 43.4348 | 43.8947 | 43.4146 | 43.6345 | 43.2084 | 43.915
Time of Peak Electrical Demand
| Jan | 06-JAN-12:15 | 03-JAN-12:15 | 27-JAN-12:00 | 23-JAN-18:30 | 26-JAN-12:00 | 18-JAN-12:00 | 05-JAN-11:15 | 09-JAN-11:15 | 21-JAN-11:15 | 14-JAN-11:15 | 17-JAN-11:15 | 27-JAN-11:15 | 16-JAN-11:15 | 23-JAN-11:15 | 16-JAN-11:15 | 01-JAN-11:15
| Feb | 23-FEB-12:15 | 24-FEB-12:00 | 28-FEB-17:15 | 18-FEB-16:15 | 12-FEB-12:00 | 08-FEB-12:00 | 14-FEB-12:00 | 13-FEB-11:15 | 14-FEB-16:15 | 20-FEB-11:15 | 28-FEB-11:15 | 11-FEB-11:15 | 18-FEB-11:15 | 02-FEB-11:15 | 21-FEB-11:15 | 27-FEB-11:15
| Mar | 13-MAR-11:00 | 25-MAR-17:30 | 17-MAR-17:15 | 28-MAR-17:30 | 04-MAR-11:00 | 31-MAR-16:15 | 01-MAR-11:15 | 09-MAR-18:00 | 25-MAR-15:00 | 29-MAR-17:15 | 31-MAR-17:15 | 26-MAR-17:15 | 29-MAR-10:15 | 30-MAR-17:15 | 30-MAR-10:15 | 31-MAR-10:15
| Apr | 04-APR-17:30 | 29-APR-11:00 | 01-APR-17:15 | 14-APR-17:15 | 11-APR-17:15 | 21-APR-17:15 | 29-APR-11:00 | 04-APR-17:15 | 21-APR-17:15 | 29-APR-17:15 | 07-APR-11:00 | 24-APR-11:00 | 01-APR-17:15 | 06-APR-17:15 | 14-APR-10:15 | 14-APR-10:15
| May | 24-MAY-10:00 | 26-MAY-17:45 | 28-MAY-16:00 | 31-MAY-17:00 | 29-MAY-11:00 | 31-MAY-17:15 | 09-MAY-11:00 | 15-MAY-17:15 | 31-MAY-17:15 | 05-MAY-17:00 | 30-MAY-17:15 | 23-MAY-17:15 | 27-MAY-15:15 | 16-MAY-17:15 | 31-MAY-17:15 | 30-MAY-17:15
| Jun | 28-JUN-10:15 | 13-JUN-16:30 | 28-JUN-16:00 | 08-JUN-17:30 | 28-JUN-11:00 | 27-JUN-16:15 | 16-JUN-11:15 | 30-JUN-16:00 | 20-JUN-17:15 | 18-JUN-15:30 | 08-JUN-10:00 | 28-JUN-11:00 | 29-JUN-17:15 | 30-JUN-16:15 | 14-JUN-17:15 | 20-JUN-17:00
| Jul | 13-JUL-10:15 | 30-JUL-10:00 | 19-JUL-16:00 | 03-JUL-16:30 | 29-JUL-10:15 | 25-JUL-16:30 | 02-JUL-15:30 | 25-JUL-10:00 | 31-JUL-17:15 | 24-JUL-17:00 | 14-JUL-10:00 | 17-JUL-11:00 | 15-JUL-15:15 | 21-JUL-17:15 | 08-JUL-10:00 | 29-JUL-17:45
| Aug | 21-AUG-15:45 | 31-AUG-10:15 | 01-AUG-16:00 | 17-AUG-11:00 | 08-AUG-10:15 | 04-AUG-16:30 | 15-AUG-11:00 | 04-AUG-16:30 | 01-AUG-17:15 | 18-AUG-17:30 | 03-AUG-10:00 | 30-AUG-11:00 | 27-AUG-15:15 | 09-AUG-17:15 | 12-AUG-11:00 | 15-AUG-17:15
| Sep | 10-SEP-10:15 | 16-SEP-10:15 | 12-SEP-17:30 | 11-SEP-11:00 | 24-SEP-10:00 | 01-SEP-11:00 | 28-SEP-15:15 | 05-SEP-11:00 | 02-SEP-17:15 | 02-SEP-15:00 | 06-SEP-11:15 | 01-SEP-17:15 | 14-SEP-11:00 | 01-SEP-17:15 | 08-SEP-17:00 | 01-SEP-10:15
| Oct | 07-OCT-10:15 | 29-OCT-11:00 | 13-OCT-17:15 | 12-OCT-15:00 | 19-OCT-10:00 | 06-OCT-11:15 | 16-OCT-17:30 | 03-OCT-11:00 | 11-OCT-17:15 | 17-OCT-17:30 | 31-OCT-11:00 | 05-OCT-11:00 | 08-OCT-15:15 | 06-OCT-17:15 | 07-OCT-15:15 | 02-OCT-10:15
| Nov | 01-NOV-11:15 | 26-NOV-11:00 | 13-NOV-12:00 | 22-NOV-12:00 | 20-NOV-12:00 | 10-NOV-12:00 | 06-NOV-11:15 | 04-NOV-11:00 | 01-NOV-17:30 | 03-NOV-10:15 | 02-NOV-11:00 | 10-NOV-12:00 | 03-NOV-10:15 | 21-NOV-11:15 | 09-NOV-11:15 | 14-NOV-11:15
| Dec | 15-DEC-12:00 | 02-DEC-12:00 | 13-DEC-12:00 | 13-DEC-12:00 | 19-DEC-12:00 | 05-DEC-12:00 | 03-DEC-11:15 | 23-DEC-11:15 | 08-DEC-11:15 | 31-DEC-11:15 | 12-DEC-11:15 | 30-DEC-11:15 | 02-DEC-11:15 | 01-DEC-11:15 | 02-DEC-11:15 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 5699.4 | 5963.01 | 5244.05 | 5443.34 | 4498.53 | 5636.21 | 4668.9 | 5895.32 | 5319.28 | 3628.44 | 6021.03 | 5456.77 | 6155.74 | 5874.09 | 6323.75 | 7343.95
| Total Source Energy (MJ/m2) | 11150.09 | 11665.8 | 10259.26 | 10649.13 | 8800.75 | 11026.46 | 9134.05 | 11533.37 | 10406.44 | 7098.53 | 11779.3 | 10675.41 | 12042.85 | 11491.84 | 12371.54 | 14367.42
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
| Total Building | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
Emissions
| Carbon Equivalent (kg) | 124293.6176 | 140679.1333 | 127094.1058 | 124978.7872 | 54478.1475 | 134722.5917 | 58113.0712 | 115300.1425 | 153450.5349 | 51165.7066 | 197293.8475 | 153625.5051 | 143165.9444 | 143320.4154 | 143885.7792 | 140655.0179
| CO2 (kg) | 297500.9053 | 360983.0368 | 309479.4809 | 299105.9436 | 149833.122 | 330551.8479 | 160648.8831 | 278433.775 | 372413.5797 | 137169.3698 | 475826.0231 | 375184.5846 | 353507.1593 | 354033.2156 | 358562.7483 | 376031.9693
| NOX (kg) | 482.9002 | 449.811 | 478.5286 | 503.8433 | 131.2326 | 495.5306 | 141.2508 | 459.8025 | 588.4023 | 158.976 | 772.977 | 582.9241 | 538.6566 | 536.4228 | 532.471 | 409.6449
| SO2 (kg) | 1676.4742 | 1711.7243 | 1430.7652 | 1140.261 | 858.9596 | 1838.6314 | 823.4201 | 1144.5108 | 1356.6627 | 220.6257 | 2046.5858 | 1313.4096 | 710.7446 | 779.3933 | 675.6839 | 1429.9445
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0077 | 0.0049 | 0.004 | 0.0043 | 0.0005 | 0.0036 | 0.0005 | 0.0048 | 0.0054 | 0.001 | 0.0064 | 0.0053 | 0.0054 | 0.0056 | 0.0052 | 0.0052
| Water for Electricity (m3) | 207.4555 | 583.7879 | 10566.8 | 2027.64 | 5181.03 | 9168.13 | 4966.14 | 71.1548 | 1410.31 | 2910.35 | 471.026 | 1365.27 | 466.8122 | 18476.9 | 443.7083 | 286.8163

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2346.75 | 4591.09 | 4591.09
Net Site Energy | 2346.75 | 4591.09 | 4591.09
Total Source Energy | 5699.4 | 11150.09 | 11150.09
Net Source Energy | 5699.4 | 11150.09 | 11150.09
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14.67 | 0 | 0 | 0 | 0
Cooling | 382.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.07 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 109.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 121.38 | 0 | 0 | 0 | 1377.36
Refrigeration | 67.61 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1409.78 | 936.98 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74927.72 | 50657.37 | 24270.35 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18326.92 | 12390.52 | 5936.4 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 111426.39 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 28573.33 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.02 | 3299.84 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 856.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22705.6586 | 36.1953 | 122.754 | 0 | 0.0006 | 15189.6164 | 9420.0928
February | 20595.9728 | 32.9758 | 112.4785 | 0 | 0.0005 | 13918.2594 | 8559.217
March | 23247.1725 | 37.3391 | 127.8898 | 0 | 0.0006 | 15825.3917 | 9672.8686
April | 23854.3748 | 38.674 | 134.0609 | 0 | 0.0006 | 16589.3442 | 9961.5549
May | 26357.9861 | 43.0248 | 150.4276 | 0 | 0.0007 | 18614.8966 | 11036.2954
June | 26431.893 | 43.2946 | 152.0233 | 0 | 0.0007 | 18812.4954 | 11082.1861
July | 28239.2857 | 46.3884 | 163.4684 | 0 | 0.0008 | 20228.9132 | 11853.3431
August | 28008.361 | 45.9686 | 161.8132 | 0 | 0.0007 | 20024.046 | 11752.3587
September | 26581.4809 | 43.5394 | 152.8823 | 0 | 0.0007 | 18918.7937 | 11144.887
October | 25849.7919 | 42.1008 | 146.7837 | 0 | 0.0007 | 18163.8938 | 10814.0441
November | 23253.92 | 37.5819 | 129.7529 | 0 | 0.0006 | 16056.1475 | 9698.9223
December | 22375.0078 | 35.8173 | 122.1395 | 0 | 0.0006 | 15113.7201 | 9297.8478
Annual Sum or Average | 297500.9053 | 482.9002 | 1676.4742 | 0 | 0.0077 | 207455.518 | 124293.6176
Minimum of Months | 20595.9728 | 32.9758 | 112.4785 | 0 | 0.0005 | 13918.2594 | 8559.217
Maximum of Months | 28239.2857 | 46.3884 | 163.4684 | 0 | 0.0008 | 20228.9132 | 11853.3431
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 103222000000 | 66059.425 | 06-JAN-12:15 | 9179.851 | 26914.7 | 4155.882 | 0 | 23354.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2454.775 | 0 | 0
February | 94582300000 | 67024.761 | 23-FEB-12:15 | 9179.851 | 26914.7 | 4155.882 | 0 | 24302.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2471.926 | 0 | 0
March | 107542000000 | 67324.161 | 13-MAR-11:00 | 9179.851 | 26914.7 | 4155.882 | 0 | 24911.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2161.796 | 0 | 0
April | 112734000000 | 68758.16 | 04-APR-17:30 | 9179.851 | 26914.7 | 4155.882 | 0 | 26335.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2172.558 | 0 | 0
May | 126499000000 | 70362.738 | 24-MAY-10:00 | 9179.851 | 26914.7 | 4155.882 | 0 | 27076.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3035.537 | 0 | 0
June | 127841000000 | 71355.201 | 28-JUN-10:15 | 9179.851 | 26914.7 | 4155.882 | 0 | 27663.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
July | 137467000000 | 71223.488 | 13-JUL-10:15 | 9179.851 | 26914.7 | 4155.882 | 0 | 27531.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
August | 136075000000 | 71005.597 | 21-AUG-15:45 | 9179.851 | 26914.7 | 4155.882 | 0 | 28517.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2237.318 | 0 | 0
September | 128564000000 | 71024.424 | 10-SEP-10:15 | 9179.851 | 26914.7 | 4155.882 | 0 | 27332.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
October | 123434000000 | 70749.549 | 07-OCT-10:15 | 9179.851 | 26914.7 | 4155.882 | 0 | 27057.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
November | 109110000000 | 68701.039 | 01-NOV-11:15 | 9179.851 | 26914.7 | 4155.882 | 0 | 25967.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2482.645 | 0 | 0
December | 102706000000 | 63975.745 | 15-DEC-12:00 | 9179.851 | 26914.7 | 4155.882 | 0 | 21579.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2146.015 | 0 | 0
Annual Sum or Average | 1409780000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 94582300000 | 63975.745 |  | 9179.851 | 26914.7 | 4155.882 | 0 | 21579.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2146.015 | 0 | 0
Maximum of Months | 137467000000 | 71355.201 |  | 9179.851 | 26914.7 | 4155.882 | 0 | 28517.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 30169.66 | 10744.56 | 0 | 40914.22
Cost per Total Building Area ($/m2) | 59.02 | 21.02 | 0 | 80.04
Cost per Net Conditioned Building Area ($/m2) | 59.02 | 21.02 | 0 | 80.04

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2456.29 | 4805.39 | 4805.39
Net Site Energy | 2456.29 | 4805.39 | 4805.39
Total Source Energy | 5963.01 | 11665.8 | 11665.8
Net Source Energy | 5963.01 | 11665.8 | 11665.8
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 211.28 | 0 | 0 | 0 | 0
Cooling | 266.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.1 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 152.46 | 0 | 0 | 0 | 1377.36
Refrigeration | 65.08 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1291.63 | 1164.66 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75711.37 | 51187.19 | 24524.18 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18308.82 | 12378.28 | 5930.53 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 145270.18 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 37683.45 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.05 | 3334.35 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 855.19 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 28614.1313 | 34.6361 | 121.4102 | 0 | 0.0004 | 41401.9578 | 11019.8825
February | 25561.8305 | 30.8607 | 107.3276 | 0 | 0.0003 | 36599.218 | 9833.9651
March | 27207.397 | 33.5424 | 123.972 | 0 | 0.0004 | 42279.0879 | 10556.6313
April | 27702.0508 | 34.6515 | 133.2172 | 0 | 0.0004 | 45434.7419 | 10812.9036
May | 31486.3006 | 39.6733 | 155.4526 | 0 | 0.0004 | 53019.7648 | 12327.1607
June | 33107.9375 | 41.9066 | 166.1196 | 0 | 0.0005 | 56658.8739 | 12986.5335
July | 35814.0309 | 45.4283 | 181.0489 | 0 | 0.0005 | 61751.3523 | 14060.4327
August | 35110.7464 | 44.4988 | 176.9693 | 0 | 0.0005 | 60359.7175 | 13779.5007
September | 31741.4456 | 40.1048 | 158.253 | 0 | 0.0005 | 53975.4434 | 12441.2321
October | 29565.6569 | 37.0809 | 143.5565 | 0 | 0.0004 | 48961.5359 | 11552.9986
November | 26866.1821 | 33.2831 | 124.6766 | 0 | 0.0004 | 42520.2488 | 10445.0316
December | 28205.3272 | 34.1445 | 119.721 | 0 | 0.0004 | 40825.9423 | 10862.8612
Annual Sum or Average | 360983.0368 | 449.811 | 1711.7243 | 0 | 0.0049 | 583787.8845 | 140679.1333
Minimum of Months | 25561.8305 | 30.8607 | 107.3276 | 0 | 0.0003 | 36599.218 | 9833.9651
Maximum of Months | 35814.0309 | 45.4283 | 181.0489 | 0 | 0.0005 | 61751.3523 | 14060.4327
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 91601900000 | 62527.211 | 03-JAN-12:15 | 9179.851 | 26914.7 | 4189.549 | 0 | 19807.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2435.949 | 0 | 0
February | 80975800000 | 58339.361 | 24-FEB-12:00 | 9179.851 | 26914.7 | 4189.549 | 0 | 15929.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.215 | 0 | 0
March | 93542600000 | 63785.82 | 25-MAR-17:30 | 9179.851 | 26914.7 | 4189.549 | 0 | 21344.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2157.171 | 0 | 0
April | 100524000000 | 67537.396 | 29-APR-11:00 | 9179.851 | 26914.7 | 4189.549 | 0 | 25047.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2205.889 | 0 | 0
May | 117306000000 | 71271.195 | 26-MAY-17:45 | 9179.851 | 26914.7 | 4189.549 | 0 | 28751.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2235.66 | 0 | 0
June | 125358000000 | 71600.317 | 13-JUN-16:30 | 9179.851 | 26914.7 | 4189.549 | 0 | 29070.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2245.708 | 0 | 0
July | 136625000000 | 72431.767 | 30-JUL-10:00 | 9179.851 | 26914.7 | 4189.549 | 0 | 29018.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3129.206 | 0 | 0
August | 133546000000 | 72328.744 | 31-AUG-10:15 | 9179.851 | 26914.7 | 4189.549 | 0 | 28603.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
September | 119421000000 | 71430.255 | 16-SEP-10:15 | 9179.851 | 26914.7 | 4189.549 | 0 | 27704.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
October | 108327000000 | 69325.45 | 29-OCT-11:00 | 9179.851 | 26914.7 | 4189.549 | 0 | 26849.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2192.057 | 0 | 0
November | 94076100000 | 65325.358 | 26-NOV-11:00 | 9179.851 | 26914.7 | 4189.549 | 0 | 22077.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2963.571 | 0 | 0
December | 90327500000 | 64732.844 | 02-DEC-12:00 | 9179.851 | 26914.7 | 4189.549 | 0 | 22286.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2162.37 | 0 | 0
Annual Sum or Average | 1291630000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 80975800000 | 58339.361 |  | 9179.851 | 26914.7 | 4189.549 | 0 | 15929.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.215 | 0 | 0
Maximum of Months | 136625000000 | 72431.767 |  | 9179.851 | 26914.7 | 4189.549 | 0 | 29070.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 38578.22 | 9531.45 | 0 | 48109.67
Cost per Total Building Area ($/m2) | 75.47 | 18.65 | 0 | 94.12
Cost per Net Conditioned Building Area ($/m2) | 75.47 | 18.65 | 0 | 94.12

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2373.49 | 4643.41 | 4643.41
Net Site Energy | 2373.49 | 4643.41 | 4643.41
Total Source Energy | 5244.05 | 10259.26 | 10259.26
Net Source Energy | 5244.05 | 10259.26 | 10259.26
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 157.34 | 0 | 0 | 0 | 0
Cooling | 255.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 134.59 | 0 | 0 | 0 | 1377.36
Refrigeration | 64.84 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1280.64 | 1092.85 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.251 | 0.11 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75979.32 | 51368.34 | 24610.98 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18152.36 | 12272.5 | 5879.85 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 123835.15 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 31521.66 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.06 | 3346.15 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 847.89 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23737.7087 | 35.077 | 97.9719 | 0 | 0.0003 | 723468.3754 | 9583.8391
February | 21448.2522 | 31.7599 | 89.0004 | 0 | 0.0003 | 657223.4591 | 8666.1743
March | 23787.1555 | 36.3422 | 106.7999 | 0 | 0.0003 | 788737.5364 | 9724.3529
April | 23982.5006 | 37.1852 | 111.6163 | 0 | 0.0003 | 824340.9114 | 9859.2777
May | 26355.6677 | 41.3354 | 126.0652 | 0 | 0.0004 | 931081.219 | 10882.4777
June | 28798.5541 | 45.6795 | 141.4596 | 0 | 0.0004 | 1044810 | 11943.0205
July | 31059.246 | 49.4404 | 153.8305 | 0 | 0.0004 | 1136190 | 12898.25
August | 30435.7686 | 48.3693 | 150.174 | 0 | 0.0004 | 1109180 | 12631.3859
September | 27866.9448 | 44.0707 | 135.9352 | 0 | 0.0004 | 1004000 | 11543.4179
October | 25130.3221 | 39.1461 | 118.2689 | 0 | 0.0003 | 873484.5981 | 10349.4708
November | 22739.5825 | 34.6576 | 101.488 | 0 | 0.0003 | 749503.4189 | 9287.5927
December | 24137.7781 | 35.4653 | 98.1554 | 0 | 0.0003 | 724809.8306 | 9724.8463
Annual Sum or Average | 309479.4809 | 478.5286 | 1430.7652 | 0 | 0.004 | 10566800 | 127094.1058
Minimum of Months | 21448.2522 | 31.7599 | 89.0004 | 0 | 0.0003 | 657223.4591 | 8666.1743
Maximum of Months | 31059.246 | 49.4404 | 153.8305 | 0 | 0.0004 | 1136190 | 12898.25
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 87680100000 | 50698.604 | 27-JAN-12:00 | 9179.851 | 26914.7 | 4194.041 | 0 | 8362.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2047.452 | 0 | 0
February | 79651700000 | 53847.134 | 28-FEB-17:15 | 9179.851 | 26914.7 | 4194.041 | 0 | 11517.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2040.712 | 0 | 0
March | 95590400000 | 62288.241 | 17-MAR-17:15 | 9179.851 | 26914.7 | 4194.041 | 0 | 19886.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2112.952 | 0 | 0
April | 99905300000 | 64742.645 | 01-APR-17:15 | 9179.851 | 26914.7 | 4194.041 | 0 | 22315.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2138.263 | 0 | 0
May | 112842000000 | 73769.573 | 28-MAY-16:00 | 9179.851 | 26914.7 | 4194.041 | 0 | 31331.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2149.391 | 0 | 0
June | 126625000000 | 78410.101 | 28-JUN-16:00 | 9179.851 | 26914.7 | 4194.041 | 0 | 35924.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2197.303 | 0 | 0
July | 137700000000 | 77809.045 | 19-JUL-16:00 | 9179.851 | 26914.7 | 4194.041 | 0 | 35308.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2211.978 | 0 | 0
August | 134426000000 | 78160.527 | 01-AUG-16:00 | 9179.851 | 26914.7 | 4194.041 | 0 | 35670.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2201.637 | 0 | 0
September | 121679000000 | 74663.929 | 12-SEP-17:30 | 9179.851 | 26914.7 | 4194.041 | 0 | 32197.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2177.904 | 0 | 0
October | 105861000000 | 64446.308 | 13-OCT-17:15 | 9179.851 | 26914.7 | 4194.041 | 0 | 22012.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2145.535 | 0 | 0
November | 90835400000 | 59388.909 | 13-NOV-12:00 | 9179.851 | 26914.7 | 4194.041 | 0 | 16960.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2140.166 | 0 | 0
December | 87842700000 | 50633.898 | 13-DEC-12:00 | 9179.851 | 26914.7 | 4194.041 | 0 | 8287.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2058.116 | 0 | 0
Annual Sum or Average | 1280640000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 79651700000 | 50633.898 |  | 9179.851 | 26914.7 | 4194.041 | 0 | 8287.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2040.712 | 0 | 0
Maximum of Months | 137700000000 | 78410.101 |  | 9179.851 | 26914.7 | 4194.041 | 0 | 35924.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2211.978 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34121.75 | 9361.21 | 0 | 43482.96
Cost per Total Building Area ($/m2) | 66.75 | 18.31 | 0 | 85.07
Cost per Net Conditioned Building Area ($/m2) | 66.75 | 18.31 | 0 | 85.07

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2552.29 | 4993.2 | 4993.2
Net Site Energy | 2552.29 | 4993.2 | 4993.2
Total Source Energy | 5443.34 | 10649.13 | 10649.13
Net Source Energy | 5443.34 | 10649.13 | 10649.13
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 399.84 | 0 | 0 | 0 | 0
Cooling | 146.97 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.07 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 109.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 182.41 | 0 | 0 | 0 | 1377.36
Refrigeration | 62.53 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1169.12 | 1383.17 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74479.99 | 50354.67 | 24125.32 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18790.87 | 12704.19 | 6086.68 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 154652.36 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 41721.04 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3 | 3280.12 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.76 | 877.71 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26780.0755 | 41.5055 | 84.4176 | 0 | 0.0003 | 150070.9223 | 10856.8432
February | 23427.2112 | 36.8322 | 76.4133 | 0 | 0.0003 | 135849.0678 | 9545.8873
March | 23819.139 | 39.0469 | 85.5275 | 0 | 0.0003 | 152074.422 | 9853.2093
April | 22806.0534 | 38.6281 | 87.9779 | 0 | 0.0003 | 156446.998 | 9548.8259
May | 24396.5663 | 42.5908 | 100.3332 | 0 | 0.0004 | 178432.6646 | 10331.9447
June | 25527.945 | 45.0971 | 107.5897 | 0 | 0.0004 | 191343.3591 | 10860.1334
July | 27867.9732 | 49.5368 | 118.9515 | 0 | 0.0004 | 211552.9683 | 11883.8813
August | 27341.3633 | 48.5201 | 116.3084 | 0 | 0.0004 | 206851.495 | 11651.8696
September | 24962.4872 | 44.0193 | 104.8198 | 0 | 0.0004 | 186416.4392 | 10612.2904
October | 23183.8399 | 39.5985 | 91.0554 | 0 | 0.0003 | 161923.4297 | 9737.5266
November | 23181.7875 | 37.8117 | 82.3055 | 0 | 0.0003 | 146343.1625 | 9571.9725
December | 25811.5021 | 40.6565 | 84.5612 | 0 | 0.0003 | 150335.5469 | 10524.403
Annual Sum or Average | 299105.9436 | 503.8433 | 1140.261 | 0 | 0.0043 | 2027640 | 124978.7872
Minimum of Months | 22806.0534 | 36.8322 | 76.4133 | 0 | 0.0003 | 135849.0678 | 9545.8873
Maximum of Months | 27867.9732 | 49.5368 | 118.9515 | 0 | 0.0004 | 211552.9683 | 11883.8813
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 86529500000 | 44429.911 | 23-JAN-18:30 | 9179.851 | 26914.7 | 4157.835 | 0 | 1360.337 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 1923.189 | 0 | 0
February | 78329300000 | 46321.338 | 18-FEB-16:15 | 9179.851 | 26914.7 | 4157.835 | 0 | 4083.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1985.664 | 0 | 0
March | 87684700000 | 52769.002 | 28-MAR-17:30 | 9179.851 | 26914.7 | 4157.835 | 0 | 10496.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020.162 | 0 | 0
April | 90205900000 | 60571.237 | 14-APR-17:15 | 9179.851 | 26914.7 | 4157.835 | 0 | 18231.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2087.066 | 0 | 0
May | 102883000000 | 68366.445 | 31-MAY-17:00 | 9179.851 | 26914.7 | 4157.835 | 0 | 25980.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2133.861 | 0 | 0
June | 110327000000 | 69080.313 | 08-JUN-17:30 | 9179.851 | 26914.7 | 4157.835 | 0 | 26651.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2175.954 | 0 | 0
July | 121979000000 | 72269.391 | 03-JUL-16:30 | 9179.851 | 26914.7 | 4157.835 | 0 | 29760.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2256.341 | 0 | 0
August | 119269000000 | 70333.872 | 17-AUG-11:00 | 9179.851 | 26914.7 | 4157.835 | 0 | 27866.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2215.053 | 0 | 0
September | 107486000000 | 67276.238 | 11-SEP-11:00 | 9179.851 | 26914.7 | 4157.835 | 0 | 24855.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2168.241 | 0 | 0
October | 93363500000 | 61468.403 | 12-OCT-15:00 | 9179.851 | 26914.7 | 4157.835 | 0 | 19076.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2139.431 | 0 | 0
November | 84380100000 | 50677.877 | 22-NOV-12:00 | 9179.851 | 26914.7 | 4157.835 | 0 | 8363.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2061.653 | 0 | 0
December | 86682100000 | 46344.633 | 13-DEC-12:00 | 9179.851 | 26914.7 | 4157.835 | 0 | 4059.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2033.115 | 0 | 0
Annual Sum or Average | 1169120000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 78329300000 | 44429.911 |  | 9179.851 | 26914.7 | 4157.835 | 0 | 1360.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1923.189 | 0 | 0
Maximum of Months | 121979000000 | 72269.391 |  | 9179.851 | 26914.7 | 4157.835 | 0 | 29760.665 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 2256.341 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33753.19 | 14613.09 | 0 | 48366.29
Cost per Total Building Area ($/m2) | 66.03 | 28.59 | 0 | 94.62
Cost per Net Conditioned Building Area ($/m2) | 66.03 | 28.59 | 0 | 94.62

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2171 | 4247.26 | 4247.26
Net Site Energy | 2171 | 4247.26 | 4247.26
Total Source Energy | 4498.53 | 8800.75 | 8800.75
Net Source Energy | 4498.53 | 8800.75 | 8800.75
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 131.18 | 0 | 0 | 0 | 0
Cooling | 49.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 99.66 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 176.6 | 0 | 0 | 0 | 1377.36
Refrigeration | 62.71 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1062.31 | 1108.69 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 69236.34 | 46809.53 | 22426.81 | 0.68 | 3.19
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14571.23 | 10178.2 | 4393.03 | 0.7 | 3.72
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 110294.53 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 25789.97 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.79 | 3049.19 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.64 | 742.9 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13373.3415 | 11.7495 | 70.1555 | 0 | 0 | 423125.4302 | 4842.5776
February | 12038.5541 | 10.5762 | 63.273 | 0 | 0 | 381616.1559 | 4359.6073
March | 12848.1764 | 11.273 | 70.107 | 0 | 0 | 422849.1011 | 4660.6692
April | 12189.3426 | 10.685 | 68.2853 | 0 | 0 | 411871.3143 | 4427.0876
May | 12347.3175 | 10.8091 | 71.7513 | 0 | 0 | 432791.6704 | 4492.3378
June | 11837.1798 | 10.3551 | 70.1094 | 0 | 0 | 422894.8905 | 4310.7688
July | 12581.4081 | 10.9898 | 77.4386 | 0 | 0 | 467119.6733 | 4590.7087
August | 12828.2736 | 11.2014 | 79.6858 | 0 | 0 | 480678.8062 | 4683.0054
September | 12246.5336 | 10.6971 | 75.4205 | 0 | 0 | 454946.3091 | 4468.6509
October | 12315.5506 | 10.7712 | 73.3667 | 0 | 0 | 442544.732 | 4486.2716
November | 12146.8217 | 10.6439 | 68.7399 | 0 | 0 | 414617.5445 | 4413.7582
December | 13080.6226 | 11.4811 | 70.6265 | 0 | 0 | 425978.4145 | 4742.7043
Annual Sum or Average | 149833.122 | 131.2326 | 858.9596 | 0 | 0.0005 | 5181030 | 54478.1475
Minimum of Months | 11837.1798 | 10.3551 | 63.273 | 0 | 0 | 381616.1559 | 4310.7688
Maximum of Months | 13373.3415 | 11.7495 | 79.6858 | 0 | 0 | 480678.8062 | 4842.5776
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 86756600000 | 54437.682 | 26-JAN-12:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 12442.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2108.243 | 0 | 0
February | 78245600000 | 55015.567 | 12-FEB-12:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 12995.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2132.973 | 0 | 0
March | 86700000000 | 52412.88 | 04-MAR-11:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 9615.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2910.528 | 0 | 0
April | 84449100000 | 55514.412 | 11-APR-17:15 | 9179.851 | 26914.7 | 3792.096 | 0 | 13575.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2052.557 | 0 | 0
May | 88738600000 | 57182.134 | 29-MAY-11:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 15128.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2166.956 | 0 | 0
June | 86709300000 | 54956.501 | 28-JUN-11:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 12956.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2113.554 | 0 | 0
July | 95777100000 | 58743.752 | 29-JUL-10:15 | 9179.851 | 26914.7 | 3792.096 | 0 | 15415.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
August | 98557200000 | 62792.282 | 08-AUG-10:15 | 9179.851 | 26914.7 | 3792.096 | 0 | 19464.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
September | 93281100000 | 63928.21 | 24-SEP-10:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 20938.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.691 | 0 | 0
October | 90738300000 | 58361.277 | 19-OCT-10:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 15472.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3002.027 | 0 | 0
November | 85012200000 | 55277.982 | 20-NOV-12:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 13267.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2123.596 | 0 | 0
December | 87341600000 | 55137.867 | 19-DEC-12:00 | 9179.851 | 26914.7 | 3792.096 | 0 | 13140.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2110.843 | 0 | 0
Annual Sum or Average | 1062310000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 78245600000 | 52412.88 |  | 9179.851 | 26914.7 | 3792.096 | 0 | 9615.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2052.557 | 0 | 0
Maximum of Months | 98557200000 | 63928.21 |  | 9179.851 | 26914.7 | 3792.096 | 0 | 20938.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.386 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 36919.69 | 9335.84 | 0 | 46255.53
Cost per Total Building Area ($/m2) | 72.23 | 18.26 | 0 | 90.49
Cost per Net Conditioned Building Area ($/m2) | 72.23 | 18.26 | 0 | 90.49

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2423.59 | 4741.42 | 4741.42
Net Site Energy | 2423.59 | 4741.42 | 4741.42
Total Source Energy | 5636.21 | 11026.46 | 11026.46
Net Source Energy | 5636.21 | 11026.46 | 11026.46
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 263.48 | 0 | 0 | 0 | 0
Cooling | 181.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 108.02 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 156.11 | 0 | 0 | 0 | 1377.36
Refrigeration | 63.03 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1203.08 | 1220.51 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.252 | 0.162 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73935.69 | 49986.68 | 23949.01 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18286.07 | 12362.91 | 5923.17 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 131106.57 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 34326.75 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.98 | 3256.15 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 854.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 27667.6206 | 39.1636 | 132.1561 | 0 | 0.0003 | 658881.3101 | 11036.0581
February | 23294.3177 | 33.8782 | 119.7728 | 0 | 0.0002 | 597188.5233 | 9385.6958
March | 25779.7024 | 37.5829 | 133.3987 | 0 | 0.0003 | 665131.5362 | 10396.4647
April | 25085.0667 | 37.84 | 141.7389 | 0 | 0.0003 | 706775.364 | 10248.3051
May | 27237.8759 | 41.4987 | 157.769 | 0 | 0.0003 | 786726.1827 | 11170.5683
June | 30132.834 | 46.5433 | 180.4957 | 0 | 0.0003 | 900081.0184 | 12423.712
July | 32772.7263 | 50.8274 | 198.2501 | 0 | 0.0004 | 988625.3041 | 13533.6028
August | 32378.4062 | 50.1718 | 195.4505 | 0 | 0.0004 | 974662.8645 | 13366.1867
September | 28693.1709 | 44.1724 | 170.4892 | 0 | 0.0003 | 850175.4686 | 11814.8491
October | 25980.2536 | 39.3014 | 147.8408 | 0 | 0.0003 | 737206.9098 | 10625.5688
November | 24476.0947 | 35.9193 | 128.8792 | 0 | 0.0003 | 642607.8056 | 9895.36
December | 27053.7789 | 38.6316 | 132.3902 | 0 | 0.0003 | 660065.4681 | 10826.2204
Annual Sum or Average | 330551.8479 | 495.5306 | 1838.6314 | 0 | 0.0036 | 9168130 | 134722.5917
Minimum of Months | 23294.3177 | 33.8782 | 119.7728 | 0 | 0.0002 | 597188.5233 | 9385.6958
Maximum of Months | 32772.7263 | 50.8274 | 198.2501 | 0 | 0.0004 | 988625.3041 | 13533.6028
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 86461100000 | 44877.563 | 18-JAN-12:00 | 9179.851 | 26914.7 | 4110.285 | 0 | 2676.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1996.101 | 0 | 0
February | 78365500000 | 47119.348 | 08-FEB-12:00 | 9179.851 | 26914.7 | 4110.285 | 0 | 4899.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014.875 | 0 | 0
March | 87281200000 | 50874.083 | 31-MAR-16:15 | 9179.851 | 26914.7 | 4110.285 | 0 | 8649.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019.326 | 0 | 0
April | 92745900000 | 62768.727 | 21-APR-17:15 | 9179.851 | 26914.7 | 4110.285 | 0 | 20433.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2130.13 | 0 | 0
May | 103237000000 | 67546.49 | 31-MAY-17:15 | 9179.851 | 26914.7 | 4110.285 | 0 | 25192.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2149.429 | 0 | 0
June | 118112000000 | 76024.879 | 27-JUN-16:15 | 9179.851 | 26914.7 | 4110.285 | 0 | 33674.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2145.778 | 0 | 0
July | 129731000000 | 74877.831 | 25-JUL-16:30 | 9179.851 | 26914.7 | 4110.285 | 0 | 32507.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2165.274 | 0 | 0
August | 127899000000 | 74479.635 | 04-AUG-16:30 | 9179.851 | 26914.7 | 4110.285 | 0 | 32105.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2168.938 | 0 | 0
September | 111563000000 | 71388.894 | 01-SEP-11:00 | 9179.851 | 26914.7 | 4110.285 | 0 | 28971.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2212.236 | 0 | 0
October | 96739300000 | 62177.48 | 06-OCT-11:15 | 9179.851 | 26914.7 | 4110.285 | 0 | 19440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2532.644 | 0 | 0
November | 84325600000 | 49160.627 | 10-NOV-12:00 | 9179.851 | 26914.7 | 4110.285 | 0 | 6922.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2033.289 | 0 | 0
December | 86616500000 | 48333.586 | 05-DEC-12:00 | 9179.851 | 26914.7 | 4110.285 | 0 | 6102.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026.079 | 0 | 0
Annual Sum or Average | 1203080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 78365500000 | 44877.563 |  | 9179.851 | 26914.7 | 4110.285 | 0 | 2676.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1996.101 | 0 | 0
Maximum of Months | 129731000000 | 76024.879 |  | 9179.851 | 26914.7 | 4110.285 | 0 | 33674.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2532.644 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 31524.77 | 9881.36 | 0 | 41406.13
Cost per Total Building Area ($/m2) | 61.67 | 19.33 | 0 | 81.01
Cost per Net Conditioned Building Area ($/m2) | 61.67 | 19.33 | 0 | 81.01

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2407.83 | 4710.59 | 4710.59
Net Site Energy | 2407.83 | 4710.59 | 4710.59
Total Source Energy | 4668.9 | 9134.05 | 9134.05
Net Source Energy | 4668.9 | 9134.05 | 9134.05
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 386.45 | 0 | 0 | 0 | 0
Cooling | 11.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 95.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 202.22 | 0 | 0 | 0 | 1377.36
Refrigeration | 60.38 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1018.25 | 1389.59 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.39 | 0.223 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 5.835 | 0.39 | 0.223 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 5.835 | 0.39 | 0.223 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54672.96 | 40542.17 | 14130.79 | 0.74 | 3.32
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8444.56 | 6744.29 | 1700.27 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 121681.82 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 22704.88 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.79 | 3050.89 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 591.71 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15544.2096 | 13.7261 | 69.146 | 0 | 0 | 416963.6879 | 5590.8389
February | 12853.6674 | 11.3201 | 62.5739 | 0 | 0 | 377370.5435 | 4639.5866
March | 14383.9759 | 12.6733 | 69.0498 | 0 | 0 | 416418.777 | 5188.9864
April | 13347.9637 | 11.7435 | 67.117 | 0 | 0 | 404782.2177 | 4824.524
May | 13172.9333 | 11.5702 | 69.6811 | 0 | 0 | 420267.4974 | 4771.7686
June | 12445.2718 | 10.9207 | 67.6915 | 0 | 0 | 408278.9498 | 4513.8537
July | 12642.6408 | 11.0812 | 71.0475 | 0 | 0 | 428533.4147 | 4592.4024
August | 12644.5481 | 11.0834 | 70.9524 | 0 | 0 | 427959.2419 | 4592.7724
September | 12254.5954 | 10.7368 | 69.6202 | 0 | 0 | 419928.6903 | 4453.7446
October | 12873.2858 | 11.2945 | 70.3344 | 0 | 0 | 424220.9836 | 4670.0533
November | 13162.8974 | 11.576 | 67.0228 | 0 | 0 | 404219.546 | 4760.1849
December | 15322.8938 | 13.525 | 69.1835 | 0 | 0 | 417196.7289 | 5514.3554
Annual Sum or Average | 160648.8831 | 141.2508 | 823.4201 | 0 | 0.0005 | 4966140 | 58113.0712
Minimum of Months | 12254.5954 | 10.7368 | 62.5739 | 0 | 0 | 377370.5435 | 4453.7446
Maximum of Months | 15544.2096 | 13.7261 | 71.0475 | 0 | 0 | 428533.4147 | 5590.8389
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85493200000 | 43119.404 | 05-JAN-11:15 | 9179.851 | 26914.7 | 3642.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3382.252 | 0 | 0
February | 77375100000 | 47347.952 | 14-FEB-12:00 | 9179.851 | 26914.7 | 3642.601 | 0 | 5564.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2046.275 | 0 | 0
March | 85381500000 | 43127.354 | 01-MAR-11:15 | 9179.851 | 26914.7 | 3642.601 | 0 | 4.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3385.261 | 0 | 0
April | 82995600000 | 48347.365 | 29-APR-11:00 | 9179.851 | 26914.7 | 3642.601 | 0 | 6536.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2073.89 | 0 | 0
May | 86170600000 | 50262.8 | 09-MAY-11:00 | 9179.851 | 26914.7 | 3642.601 | 0 | 8444.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2081.226 | 0 | 0
June | 83712500000 | 52559.262 | 16-JUN-11:15 | 9179.851 | 26914.7 | 3642.601 | 0 | 10398.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2423.54 | 0 | 0
July | 87865400000 | 58128.98 | 02-JUL-15:30 | 9179.851 | 26914.7 | 3642.601 | 0 | 16160.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2231.036 | 0 | 0
August | 87747700000 | 55741.575 | 15-AUG-11:00 | 9179.851 | 26914.7 | 3642.601 | 0 | 13843.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2160.917 | 0 | 0
September | 86101200000 | 58782.315 | 28-SEP-15:15 | 9179.851 | 26914.7 | 3642.601 | 0 | 16901.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2143.985 | 0 | 0
October | 86981200000 | 50058.049 | 16-OCT-17:30 | 9179.851 | 26914.7 | 3642.601 | 0 | 7411.26 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 2015.638 | 0 | 0
November | 82880200000 | 43139.314 | 06-NOV-11:15 | 9179.851 | 26914.7 | 3642.601 | 0 | 17.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3384.289 | 0 | 0
December | 85541000000 | 43128.541 | 03-DEC-11:15 | 9179.851 | 26914.7 | 3642.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3391.389 | 0 | 0
Annual Sum or Average | 1018250000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 77375100000 | 43119.404 |  | 9179.851 | 26914.7 | 3642.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015.638 | 0 | 0
Maximum of Months | 87865400000 | 58782.315 |  | 9179.851 | 26914.7 | 3642.601 | 0 | 16901.178 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 3391.389 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 41103.09 | 11720.76 | 0 | 52823.85
Cost per Total Building Area ($/m2) | 80.41 | 22.93 | 0 | 103.34
Cost per Net Conditioned Building Area ($/m2) | 80.41 | 22.93 | 0 | 103.34

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2832.16 | 5540.73 | 5540.73
Net Site Energy | 2832.16 | 5540.73 | 5540.73
Total Source Energy | 5895.32 | 11533.37 | 11533.37
Net Source Energy | 5895.32 | 11533.37 | 11533.37
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 697.04 | 0 | 0 | 0 | 0
Cooling | 110.9 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 106.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 205.94 | 0 | 0 | 0 | 1377.36
Refrigeration | 60.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1128.26 | 1703.91 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73141.39 | 49449.67 | 23691.72 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17573.87 | 11881.4 | 5692.47 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 170341.9 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 43435.09 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.95 | 3221.17 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.71 | 820.87 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 27682.1379 | 40.9389 | 87.4224 | 0 | 0.0004 | 5433.0346 | 11026.625
February | 24195.9606 | 36.2307 | 78.8835 | 0 | 0.0003 | 4902.618 | 9678.8911
March | 23896.929 | 37.6145 | 88.0219 | 0 | 0.0004 | 5471.5666 | 9726.7491
April | 20867.762 | 34.3629 | 85.237 | 0 | 0.0004 | 5299.1826 | 8632.4423
May | 20838.0671 | 36.0232 | 94.5532 | 0 | 0.0004 | 5879.1112 | 8776.4433
June | 22082.993 | 39.4842 | 107.4289 | 0 | 0.0004 | 6680.2032 | 9420.4492
July | 24146.3055 | 43.5976 | 119.8091 | 0 | 0.0005 | 7450.1858 | 10339.4368
August | 24151.9898 | 43.6049 | 119.8206 | 0 | 0.0005 | 7450.9032 | 10341.595
September | 20591.7105 | 36.403 | 97.8839 | 0 | 0.0004 | 6086.5168 | 8746.3514
October | 21315.1323 | 36.0146 | 92.1169 | 0 | 0.0004 | 5727.3003 | 8901.1775
November | 22271.0879 | 35.7482 | 85.8587 | 0 | 0.0004 | 5337.434 | 9128.3338
December | 26393.6994 | 39.7798 | 87.4746 | 0 | 0.0004 | 5436.6952 | 10581.6479
Annual Sum or Average | 278433.775 | 459.8025 | 1144.5108 | 0 | 0.0048 | 71154.7516 | 115300.1425
Minimum of Months | 20591.7105 | 34.3629 | 78.8835 | 0 | 0.0003 | 4902.618 | 8632.4423
Maximum of Months | 27682.1379 | 43.6049 | 119.8206 | 0 | 0.0005 | 7450.9032 | 11026.625
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 86148400000 | 43552.215 | 09-JAN-11:15 | 9179.851 | 26914.7 | 4042.037 | 0 | 33.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3382.532 | 0 | 0
February | 77737900000 | 43504.054 | 13-FEB-11:15 | 9179.851 | 26914.7 | 4042.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3367.465 | 0 | 0
March | 86759400000 | 52540.134 | 09-MAR-18:00 | 9179.851 | 26914.7 | 4042.037 | 0 | 9489.111 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 2020.436 | 0 | 0
April | 84026000000 | 53727.011 | 04-APR-17:15 | 9179.851 | 26914.7 | 4042.037 | 0 | 11562.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2028.203 | 0 | 0
May | 93221600000 | 63388.467 | 15-MAY-17:15 | 9179.851 | 26914.7 | 4042.037 | 0 | 21110.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2141.013 | 0 | 0
June | 105924000000 | 70606.069 | 30-JUN-16:00 | 9179.851 | 26914.7 | 4042.037 | 0 | 28217.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2251.612 | 0 | 0
July | 118133000000 | 71494.965 | 25-JUL-10:00 | 9179.851 | 26914.7 | 4042.037 | 0 | 28217.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3140.508 | 0 | 0
August | 118145000000 | 70979.848 | 04-AUG-16:30 | 9179.851 | 26914.7 | 4042.037 | 0 | 28587.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2255.972 | 0 | 0
September | 96510300000 | 65249.194 | 05-SEP-11:00 | 9179.851 | 26914.7 | 4042.037 | 0 | 22944.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2168.224 | 0 | 0
October | 90814400000 | 60945.382 | 03-OCT-11:00 | 9179.851 | 26914.7 | 4042.037 | 0 | 18662.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2146.051 | 0 | 0
November | 84632500000 | 55748.945 | 04-NOV-11:00 | 9179.851 | 26914.7 | 4042.037 | 0 | 13489.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2122.99 | 0 | 0
December | 86206400000 | 43543.207 | 23-DEC-11:15 | 9179.851 | 26914.7 | 4042.037 | 0 | 22.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3384.243 | 0 | 0
Annual Sum or Average | 1128260000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 77737900000 | 43504.054 |  | 9179.851 | 26914.7 | 4042.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020.436 | 0 | 0
Maximum of Months | 118145000000 | 71494.965 |  | 9179.851 | 26914.7 | 4042.037 | 0 | 28587.288 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 3384.243 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21025.89 | 16991.92 | 0 | 38017.81
Cost per Total Building Area ($/m2) | 41.13 | 33.24 | 0 | 74.38
Cost per Net Conditioned Building Area ($/m2) | 41.13 | 33.24 | 0 | 74.38

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2591.92 | 5070.72 | 5070.72
Net Site Energy | 2591.92 | 5070.72 | 5070.72
Total Source Energy | 5319.28 | 10406.44 | 10406.44
Net Source Energy | 5319.28 | 10406.44 | 10406.44
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 471.4 | 0 | 0 | 0 | 0
Cooling | 87.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 119.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 201.48 | 0 | 0 | 0 | 1377.36
Refrigeration | 60.61 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1118.11 | 1473.8 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 68734.03 | 49549.37 | 19184.66 | 0.72 | 3.28
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15574.36 | 11853.8 | 3720.56 | 0.76 | 3.91
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 141760.22 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 41195.75 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.27 | 3580.43 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.84 | 979.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32992.9683 | 49.5028 | 105.9812 | 0 | 0.0004 | 110151.1676 | 13337.0338
February | 28904.2897 | 43.9129 | 95.796 | 0 | 0.0004 | 99570.1234 | 11737.6684
March | 31000.447 | 47.758 | 106.3185 | 0 | 0.0004 | 110512.9321 | 12653.6855
April | 28718.0941 | 45.5086 | 105.3467 | 0 | 0.0004 | 109513.5365 | 11846.3252
May | 30426.3281 | 49.3066 | 117.5185 | 0 | 0.0005 | 122175.3582 | 12658.0012
June | 31025.8846 | 50.8391 | 122.8698 | 0 | 0.0005 | 127742.8797 | 12962.4417
July | 33809.5475 | 55.7168 | 135.6062 | 0 | 0.0005 | 140986.7612 | 14156.4752
August | 32791.0567 | 53.9247 | 130.9059 | 0 | 0.0005 | 136099.1693 | 13718.871
September | 29889.1055 | 48.8612 | 117.7445 | 0 | 0.0005 | 122413.481 | 12476.2045
October | 29601.9122 | 47.1305 | 109.7873 | 0 | 0.0004 | 114131.5285 | 12232.6235
November | 30098.8761 | 46.2886 | 102.7908 | 0 | 0.0004 | 106845.3938 | 12277.7888
December | 33155.0701 | 49.6527 | 105.9973 | 0 | 0.0004 | 110167.017 | 13393.416
Annual Sum or Average | 372413.5797 | 588.4023 | 1356.6627 | 0 | 0.0054 | 1410310 | 153450.5349
Minimum of Months | 28718.0941 | 43.9129 | 95.796 | 0 | 0.0004 | 99570.1234 | 11737.6684
Maximum of Months | 33809.5475 | 55.7168 | 135.6062 | 0 | 0.0005 | 140986.7612 | 14156.4752
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 87329200000 | 44014.854 | 21-JAN-11:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3360.021 | 0 | 0
February | 78940400000 | 45733.192 | 14-FEB-16:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 3124.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1954.057 | 0 | 0
March | 87616000000 | 46977.539 | 25-MAR-15:00 | 9179.851 | 26914.7 | 4560.282 | 0 | 4354.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1967.781 | 0 | 0
April | 86823700000 | 54671.043 | 21-APR-17:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 11979.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2036.85 | 0 | 0
May | 96862100000 | 59902.878 | 31-MAY-17:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 17138.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2109.053 | 0 | 0
June | 101276000000 | 63270.819 | 20-JUN-17:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 20480.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2135.578 | 0 | 0
July | 111776000000 | 65464.264 | 31-JUL-17:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 22668.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2141.331 | 0 | 0
August | 107901000000 | 65229.436 | 01-AUG-17:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 22413.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2160.674 | 0 | 0
September | 97050900000 | 59600.299 | 02-SEP-17:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 16836.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2109.324 | 0 | 0
October | 90484900000 | 54554.366 | 11-OCT-17:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 11857.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2041.817 | 0 | 0
November | 84708300000 | 45044.718 | 01-NOV-17:30 | 9179.851 | 26914.7 | 4560.282 | 0 | 1584.231 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 1911.654 | 0 | 0
December | 87341700000 | 44010.797 | 08-DEC-11:15 | 9179.851 | 26914.7 | 4560.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3355.964 | 0 | 0
Annual Sum or Average | 1118110000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 78940400000 | 44010.797 |  | 9179.851 | 26914.7 | 4560.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1911.654 | 0 | 0
Maximum of Months | 111776000000 | 65464.264 |  | 9179.851 | 26914.7 | 4560.282 | 0 | 22668.101 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 3360.021 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11661.85 | 10521.23 | 0 | 22183.08
Cost per Total Building Area ($/m2) | 22.81 | 20.58 | 0 | 43.4
Cost per Net Conditioned Building Area ($/m2) | 22.81 | 20.58 | 0 | 43.4

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2712.33 | 5306.29 | 5306.29
Net Site Energy | 2712.33 | 5306.29 | 5306.29
Total Source Energy | 3628.44 | 7098.53 | 7098.53
Net Source Energy | 3628.44 | 7098.53 | 7098.53
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 667.72 | 0 | 0 | 0 | 0
Cooling | 18.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 97.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 218.2 | 0 | 0 | 0 | 1377.36
Refrigeration | 59.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1025.49 | 1686.84 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58185.89 | 41789.16 | 16396.74 | 0.72 | 3.27
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11263.12 | 8580.43 | 2682.69 | 0.76 | 3.91
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 143571.4 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 32495.69 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.75 | 3002.9 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 710.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14666.5597 | 16.1905 | 18.4333 | 0 | 0.0001 | 242941.9361 | 5384.2911
February | 12191.368 | 13.6632 | 16.6317 | 0 | 0.0001 | 219269.1933 | 4497.578
March | 13191.6448 | 14.8461 | 18.3912 | 0 | 0.0001 | 242485.6726 | 4873.2191
April | 11469.9159 | 13.1902 | 17.7899 | 0 | 0.0001 | 234645.6941 | 4267.3613
May | 10355.8664 | 12.3082 | 18.6101 | 0 | 0.0001 | 245574.8828 | 3895.6226
June | 9291.8085 | 11.2821 | 18.2211 | 0 | 0.0001 | 240499.3165 | 3520.9002
July | 9176.121 | 11.3859 | 19.5542 | 0 | 0.0001 | 258149.4048 | 3503.231
August | 9103.36 | 11.3315 | 19.6282 | 0 | 0.0001 | 259134.0544 | 3479.2952
September | 9479.118 | 11.5119 | 18.6041 | 0 | 0.0001 | 245554.8332 | 3592.1393
October | 10921.7726 | 12.7998 | 18.4718 | 0 | 0.0001 | 243706.5127 | 4089.1243
November | 12788.2614 | 14.3944 | 17.843 | 0 | 0.0001 | 235257.67 | 4724.4393
December | 14533.5735 | 16.0721 | 18.4471 | 0 | 0.0001 | 243133.6585 | 5338.5053
Annual Sum or Average | 137169.3698 | 158.976 | 220.6257 | 0 | 0.001 | 2910350 | 51165.7066
Minimum of Months | 9103.36 | 11.2821 | 16.6317 | 0 | 0.0001 | 219269.1933 | 3479.2952
Maximum of Months | 14666.5597 | 16.1905 | 19.6282 | 0 | 0.0001 | 259134.0544 | 5384.2911
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85603200000 | 43184.061 | 14-JAN-11:15 | 9179.851 | 26914.7 | 3713.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3376.485 | 0 | 0
February | 77261900000 | 43172.827 | 20-FEB-11:15 | 9179.851 | 26914.7 | 3713.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3365.252 | 0 | 0
March | 85442400000 | 44851.85 | 29-MAR-17:15 | 9179.851 | 26914.7 | 3713.025 | 0 | 3091.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1952.768 | 0 | 0
April | 82679900000 | 46877.42 | 29-APR-17:15 | 9179.851 | 26914.7 | 3713.025 | 0 | 5079.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1990.687 | 0 | 0
May | 86531000000 | 51622.794 | 05-MAY-17:00 | 9179.851 | 26914.7 | 3713.025 | 0 | 9783.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2031.455 | 0 | 0
June | 84742500000 | 54765.528 | 18-JUN-15:30 | 9179.851 | 26914.7 | 3713.025 | 0 | 12787.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2170.405 | 0 | 0
July | 90961700000 | 57216.794 | 24-JUL-17:00 | 9179.851 | 26914.7 | 3713.025 | 0 | 15306.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2103.008 | 0 | 0
August | 91308700000 | 56698.211 | 18-AUG-17:30 | 9179.851 | 26914.7 | 3713.025 | 0 | 14808.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2081.671 | 0 | 0
September | 86523900000 | 62792.826 | 02-SEP-15:00 | 9179.851 | 26914.7 | 3713.025 | 0 | 20812.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2172.74 | 0 | 0
October | 85872600000 | 47181.313 | 17-OCT-17:30 | 9179.851 | 26914.7 | 3713.025 | 0 | 4511.042 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 1968.696 | 0 | 0
November | 82895600000 | 43202.013 | 03-NOV-10:15 | 9179.851 | 26914.7 | 3713.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3394.438 | 0 | 0
December | 85670800000 | 43179.919 | 31-DEC-11:15 | 9179.851 | 26914.7 | 3713.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3372.344 | 0 | 0
Annual Sum or Average | 1025490000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 77261900000 | 43172.827 |  | 9179.851 | 26914.7 | 3713.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1952.768 | 0 | 0
Maximum of Months | 91308700000 | 62792.826 |  | 9179.851 | 26914.7 | 3713.025 | 0 | 20812.511 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 3394.438 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20579.56 | 14034.38 | 0 | 34613.94
Cost per Total Building Area ($/m2) | 40.26 | 27.46 | 0 | 67.72
Cost per Net Conditioned Building Area ($/m2) | 40.26 | 27.46 | 0 | 67.72

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3057.56 | 5981.69 | 5981.69
Net Site Energy | 3057.56 | 5981.69 | 5981.69
Total Source Energy | 6021.03 | 11779.3 | 11779.3
Net Source Energy | 6021.03 | 11779.3 | 11779.3
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 937.05 | 0 | 0 | 0 | 0
Cooling | 78.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 104.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 226.61 | 0 | 0 | 0 | 1377.36
Refrigeration | 59.67 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1092.98 | 1964.58 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 72404.12 | 48951.21 | 23452.91 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16909.55 | 11432.27 | 5477.29 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 197180.25 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 48823.06 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.92 | 3188.7 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 789.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44595.347 | 67.3179 | 161.075 | 0 | 0.0005 | 37063.2823 | 18000.5697
February | 39059.1177 | 59.6656 | 145.3038 | 0 | 0.0005 | 33435.719 | 15833.3017
March | 41235.2613 | 64.2362 | 160.8708 | 0 | 0.0005 | 37020.216 | 16834.6047
April | 36478.1103 | 59.0982 | 155.9356 | 0 | 0.0005 | 35888.636 | 15109.7495
May | 36909.1409 | 61.9674 | 170.7923 | 0 | 0.0005 | 39311.5288 | 15495.8531
June | 38703.7028 | 66.3796 | 187.4845 | 0 | 0.0006 | 43155.7414 | 16383.0603
July | 42576.2384 | 73.5083 | 209.1629 | 0 | 0.0006 | 48146.4577 | 18068.846
August | 41093.584 | 70.7945 | 200.9562 | 0 | 0.0006 | 46257.1671 | 17424.9058
September | 36194.702 | 61.6576 | 172.8195 | 0 | 0.0005 | 39779.4845 | 15280.963
October | 36803.9103 | 60.8027 | 164.3822 | 0 | 0.0005 | 37834.5964 | 15357.2047
November | 38696.8063 | 61.2348 | 156.6802 | 0 | 0.0005 | 36057.5854 | 15889.3726
December | 43480.1021 | 66.3143 | 161.1227 | 0 | 0.0005 | 37075.5981 | 17615.4164
Annual Sum or Average | 475826.0231 | 772.977 | 2046.5858 | 0 | 0.0064 | 471026.0124 | 197293.8475
Minimum of Months | 36194.702 | 59.0982 | 145.3038 | 0 | 0.0005 | 33435.719 | 15109.7495
Maximum of Months | 44595.347 | 73.5083 | 209.1629 | 0 | 0.0006 | 48146.4577 | 18068.846
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 86002600000 | 43427.368 | 17-JAN-11:15 | 9179.851 | 26914.7 | 3978.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3354.28 | 0 | 0
February | 77585100000 | 43430.018 | 28-FEB-11:15 | 9179.851 | 26914.7 | 3978.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3356.93 | 0 | 0
March | 85902600000 | 46753.698 | 31-MAR-17:15 | 9179.851 | 26914.7 | 3978.537 | 0 | 4715.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1965.239 | 0 | 0
April | 83276900000 | 47027.523 | 07-APR-11:00 | 9179.851 | 26914.7 | 3978.537 | 0 | 4918.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2035.865 | 0 | 0
May | 91219400000 | 62570.245 | 30-MAY-17:15 | 9179.851 | 26914.7 | 3978.537 | 0 | 20334.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2162.708 | 0 | 0
June | 100140000000 | 69066.493 | 08-JUN-10:00 | 9179.851 | 26914.7 | 3978.537 | 0 | 25942.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3050.511 | 0 | 0
July | 111720000000 | 70790.977 | 14-JUL-10:00 | 9179.851 | 26914.7 | 3978.537 | 0 | 27588.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3129.206 | 0 | 0
August | 107336000000 | 69113.232 | 03-AUG-10:00 | 9179.851 | 26914.7 | 3978.537 | 0 | 25989.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3050.511 | 0 | 0
September | 92305300000 | 64015.343 | 06-SEP-11:15 | 9179.851 | 26914.7 | 3978.537 | 0 | 21429.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2513.038 | 0 | 0
October | 87792300000 | 55618.626 | 31-OCT-11:00 | 9179.851 | 26914.7 | 3978.537 | 0 | 13438.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2107.504 | 0 | 0
November | 83668900000 | 55530.279 | 02-NOV-11:00 | 9179.851 | 26914.7 | 3978.537 | 0 | 13342.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2114.41 | 0 | 0
December | 86031100000 | 43434.816 | 12-DEC-11:15 | 9179.851 | 26914.7 | 3978.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3361.728 | 0 | 0
Annual Sum or Average | 1092980000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 77585100000 | 43427.368 |  | 9179.851 | 26914.7 | 3978.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1965.239 | 0 | 0
Maximum of Months | 111720000000 | 70790.977 |  | 9179.851 | 26914.7 | 3978.537 | 0 | 27588.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3361.728 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15898.39 | 17147.8 | 0 | 33046.19
Cost per Total Building Area ($/m2) | 31.1 | 33.55 | 0 | 64.65
Cost per Net Conditioned Building Area ($/m2) | 31.1 | 33.55 | 0 | 64.65

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2790.61 | 5459.44 | 5459.44
Net Site Energy | 2790.61 | 5459.44 | 5459.44
Total Source Energy | 5456.77 | 10675.41 | 10675.41
Net Source Energy | 5456.77 | 10675.41 | 10675.41
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 681.76 | 0 | 0 | 0 | 0
Cooling | 56.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 116.67 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 225.53 | 0 | 0 | 0 | 1377.36
Refrigeration | 59.36 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1082.4 | 1708.21 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 67927 | 48737.77 | 19189.23 | 0.72 | 3.27
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13926.29 | 10944.91 | 2981.39 | 0.79 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 165565.73 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 47276.5 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.2 | 3497.09 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.81 | 942 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 34364.8393 | 50.6989 | 105.7212 | 0 | 0.0004 | 109873.1804 | 13807.0228
February | 30402.8005 | 45.1923 | 95.3652 | 0 | 0.0004 | 99113.5694 | 12248.381
March | 32473.7513 | 49.0366 | 106.0067 | 0 | 0.0004 | 110180.4417 | 13157.8335
April | 29529.3311 | 45.903 | 103.4996 | 0 | 0.0004 | 107586.2949 | 12093.5576
May | 29875.3714 | 47.4177 | 109.999 | 0 | 0.0004 | 114350.4545 | 12331.0837
June | 29419.8094 | 47.5854 | 113.1429 | 0 | 0.0005 | 117625.7199 | 12230.4241
July | 32301.3445 | 52.9453 | 128.009 | 0 | 0.0005 | 133086.0578 | 13496.9186
August | 31402.3748 | 51.3226 | 123.6388 | 0 | 0.0005 | 128541.493 | 13106.6544
September | 29229.025 | 47.0662 | 111.2695 | 0 | 0.0004 | 115676.4894 | 12130.4566
October | 30312.1911 | 47.5634 | 108.6437 | 0 | 0.0004 | 112937.1646 | 12457.671
November | 31276.6164 | 47.2917 | 102.4391 | 0 | 0.0004 | 106472.9423 | 12678.9413
December | 34597.1297 | 50.901 | 105.6749 | 0 | 0.0004 | 109823.6619 | 13886.5606
Annual Sum or Average | 375184.5846 | 582.9241 | 1313.4096 | 0 | 0.0053 | 1365270 | 153625.5051
Minimum of Months | 29229.025 | 45.1923 | 95.3652 | 0 | 0.0004 | 99113.5694 | 12093.5576
Maximum of Months | 34597.1297 | 52.9453 | 128.009 | 0 | 0.0005 | 133086.0578 | 13886.5606
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 87108800000 | 44238.601 | 27-JAN-11:15 | 9179.851 | 26914.7 | 4439.099 | 0 | 325.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3379.883 | 0 | 0
February | 78578400000 | 43894.112 | 11-FEB-11:15 | 9179.851 | 26914.7 | 4439.099 | 0 | 3.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3357.15 | 0 | 0
March | 87352400000 | 51031.121 | 26-MAR-17:15 | 9179.851 | 26914.7 | 4439.099 | 0 | 8482.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2014.884 | 0 | 0
April | 85295700000 | 50986.598 | 24-APR-11:00 | 9179.851 | 26914.7 | 4439.099 | 0 | 8382.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2070.081 | 0 | 0
May | 90658400000 | 56601.38 | 23-MAY-17:15 | 9179.851 | 26914.7 | 4439.099 | 0 | 13989.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2078.465 | 0 | 0
June | 93255100000 | 62490.235 | 28-JUN-11:00 | 9179.851 | 26914.7 | 4439.099 | 0 | 19759.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2196.97 | 0 | 0
July | 105512000000 | 63351.202 | 17-JUL-11:00 | 9179.851 | 26914.7 | 4439.099 | 0 | 20606.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2210.705 | 0 | 0
August | 101909000000 | 64358.286 | 30-AUG-11:00 | 9179.851 | 26914.7 | 4439.099 | 0 | 21606.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2218.315 | 0 | 0
September | 91709700000 | 58927.754 | 01-SEP-17:15 | 9179.851 | 26914.7 | 4439.099 | 0 | 16283.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2110.798 | 0 | 0
October | 89537900000 | 53981.232 | 05-OCT-11:00 | 9179.851 | 26914.7 | 4439.099 | 0 | 11347.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2100.194 | 0 | 0
November | 84413000000 | 47202.379 | 10-NOV-12:00 | 9179.851 | 26914.7 | 4439.099 | 0 | 4657.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2010.752 | 0 | 0
December | 87069500000 | 43894.656 | 30-DEC-11:15 | 9179.851 | 26914.7 | 4439.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3361.006 | 0 | 0
Annual Sum or Average | 1082400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 78578400000 | 43894.112 |  | 9179.851 | 26914.7 | 4439.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2010.752 | 0 | 0
Maximum of Months | 105512000000 | 64358.286 |  | 9179.851 | 26914.7 | 4439.099 | 0 | 21606.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3379.883 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11295.55 | 12177.39 | 0 | 23472.94
Cost per Total Building Area ($/m2) | 22.1 | 23.82 | 0 | 45.92
Cost per Net Conditioned Building Area ($/m2) | 22.1 | 23.82 | 0 | 45.92

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3311.02 | 6477.54 | 6477.54
Net Site Energy | 3311.02 | 6477.54 | 6477.54
Total Source Energy | 6155.74 | 12042.85 | 12042.85
Net Source Energy | 6155.74 | 12042.85 | 12042.85
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1182.44 | 0 | 0 | 0 | 0
Cooling | 69.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 104.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 244.46 | 0 | 0 | 0 | 1377.36
Refrigeration | 59.12 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1083.2 | 2227.82 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 72255.02 | 48850.41 | 23404.61 | 0.68 | 3.11
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16931.06 | 11446.81 | 5484.26 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 212480.25 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 52830.49 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.91 | 3182.14 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 790.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37908.1821 | 51.717 | 56.531 | 0 | 0.0005 | 37095.9775 | 14774.4581
February | 32288.5738 | 44.9051 | 50.9338 | 0 | 0.0004 | 33429.4176 | 12665.9549
March | 31313.7302 | 45.6807 | 56.3362 | 0 | 0.0004 | 36990.0931 | 12487.2832
April | 26474.6671 | 40.8776 | 54.9766 | 0 | 0.0004 | 36111.1833 | 10773.2166
May | 26144.8341 | 42.4255 | 60.9902 | 0 | 0.0005 | 40072.1682 | 10835.6405
June | 26231.9015 | 43.6804 | 64.8194 | 0 | 0.0005 | 42593.2853 | 10978.1701
July | 28146.5857 | 47.2314 | 70.7317 | 0 | 0.0005 | 46479.9184 | 11814.1457
August | 27768.5271 | 46.5681 | 69.6876 | 0 | 0.0005 | 45793.6508 | 11652.6986
September | 24238.4045 | 39.6457 | 57.5646 | 0 | 0.0004 | 37822.8932 | 10075.5171
October | 27104.4883 | 42.0779 | 57.0263 | 0 | 0.0004 | 37458.7215 | 11051.2833
November | 30030.8168 | 44.0018 | 54.6552 | 0 | 0.0004 | 35887.5263 | 11994.091
December | 35856.4481 | 49.8456 | 56.4921 | 0 | 0.0004 | 37077.3151 | 14063.4853
Annual Sum or Average | 353507.1593 | 538.6566 | 710.7446 | 0 | 0.0054 | 466812.1505 | 143165.9444
Minimum of Months | 24238.4045 | 39.6457 | 50.9338 | 0 | 0.0004 | 33429.4176 | 10075.5171
Maximum of Months | 37908.1821 | 51.717 | 70.7317 | 0 | 0.0005 | 46479.9184 | 14774.4581
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 86078400000 | 43406.638 | 16-JAN-11:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3339.112 | 0 | 0
February | 77570400000 | 43408.94 | 18-FEB-11:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3341.414 | 0 | 0
March | 85832700000 | 43437.557 | 29-MAR-10:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.03 | 0 | 0
April | 83793300000 | 52226.891 | 01-APR-17:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 10125.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2034.231 | 0 | 0
May | 92984400000 | 68361.698 | 27-MAY-15:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 26039.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2254.397 | 0 | 0
June | 98834500000 | 69048.942 | 29-JUN-17:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 26763.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2217.986 | 0 | 0
July | 107853000000 | 69117.761 | 15-JUL-15:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 26829.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2220.362 | 0 | 0
August | 106261000000 | 68821.337 | 27-AUG-15:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 26543.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2210.01 | 0 | 0
September | 87765200000 | 59669.758 | 14-SEP-11:00 | 9179.851 | 26914.7 | 3972.976 | 0 | 17464.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.513 | 0 | 0
October | 86920100000 | 55338.297 | 08-OCT-15:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 13112.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2158.639 | 0 | 0
November | 83274300000 | 43437.735 | 03-NOV-10:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.209 | 0 | 0
December | 86035100000 | 43414.624 | 02-DEC-11:15 | 9179.851 | 26914.7 | 3972.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3347.097 | 0 | 0
Annual Sum or Average | 1083200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 77570400000 | 43406.638 |  | 9179.851 | 26914.7 | 3972.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2034.231 | 0 | 0
Maximum of Months | 107853000000 | 69117.761 |  | 9179.851 | 26914.7 | 3972.976 | 0 | 26829.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.209 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15922.17 | 17667.17 | 0 | 33589.34
Cost per Total Building Area ($/m2) | 31.15 | 34.56 | 0 | 65.71
Cost per Net Conditioned Building Area ($/m2) | 31.15 | 34.56 | 0 | 65.71

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3086.71 | 6038.72 | 6038.72
Net Site Energy | 3086.71 | 6038.72 | 6038.72
Total Source Energy | 5874.09 | 11491.84 | 11491.84
Net Source Energy | 5874.09 | 11491.84 | 11491.84
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 988 | 0 | 0 | 0 | 0
Cooling | 31.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.28 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 247.7 | 0 | 0 | 0 | 1377.36
Refrigeration | 58.22 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1050.08 | 2036.63 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.385 | 0.305 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55582.81 | 42485.8 | 13097.01 | 0.76 | 3.37
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12289.6 | 9815.15 | 2474.45 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 196219.1 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 52420.28 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.04 | 3329.69 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 861.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 35571.1105 | 50.0178 | 64.2812 | 0 | 0.0005 | 1523120 | 14025.0326
February | 30922.6825 | 44.0602 | 57.9739 | 0 | 0.0004 | 1373810 | 12248.1838
March | 30901.2576 | 45.7623 | 64.1998 | 0 | 0.0005 | 1521760 | 12407.181
April | 28307.8591 | 42.806 | 62.0099 | 0 | 0.0004 | 1470030 | 11451.3835
May | 27393.8828 | 42.7538 | 64.8173 | 0 | 0.0005 | 1536860 | 11210.204
June | 26542.0404 | 42.5781 | 66.9746 | 0 | 0.0005 | 1588220 | 10973.1459
July | 27831.5114 | 45.3493 | 72.7694 | 0 | 0.0005 | 1725760 | 11574.1633
August | 27271.7613 | 44.2288 | 70.5522 | 0 | 0.0005 | 1673150 | 11321.2381
September | 26124.2462 | 41.5982 | 64.8004 | 0 | 0.0005 | 1536610 | 10770.4824
October | 28323.6285 | 43.5176 | 64.5317 | 0 | 0.0005 | 1529960 | 11524.243
November | 30200.6954 | 44.5689 | 62.1804 | 0 | 0.0005 | 1473860 | 12110.8256
December | 34642.54 | 49.1819 | 64.3024 | 0 | 0.0005 | 1523740 | 13704.332
Annual Sum or Average | 354033.2156 | 536.4228 | 779.3933 | 0 | 0.0056 | 18476900 | 143320.4154
Minimum of Months | 26124.2462 | 41.5982 | 57.9739 | 0 | 0.0004 | 1373810 | 10770.4824
Maximum of Months | 35571.1105 | 50.0178 | 72.7694 | 0 | 0.0005 | 1725760 | 14025.0326
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 86562500000 | 43631.891 | 23-JAN-11:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3346.523 | 0 | 0
February | 78076900000 | 43648.475 | 02-FEB-11:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3363.107 | 0 | 0
March | 86485000000 | 47099.948 | 30-MAR-17:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 4854.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1960.504 | 0 | 0
April | 83545600000 | 46099.267 | 06-APR-17:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 3867.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1945.992 | 0 | 0
May | 87343200000 | 52015.791 | 16-MAY-17:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 9695.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2034.462 | 0 | 0
June | 90262500000 | 60510.804 | 30-JUN-16:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 18071.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2153.958 | 0 | 0
July | 98079200000 | 61093.477 | 21-JUL-17:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 18660.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2147.397 | 0 | 0
August | 95088900000 | 60063.079 | 09-AUG-17:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 17644.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2133.409 | 0 | 0
September | 87329200000 | 57198.423 | 01-SEP-17:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 14804.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2108.797 | 0 | 0
October | 86951000000 | 49504.211 | 06-OCT-17:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 7220.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1998.568 | 0 | 0
November | 83762700000 | 43651.297 | 21-NOV-11:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 13.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3352.576 | 0 | 0
December | 86597500000 | 43634.549 | 01-DEC-11:15 | 9179.851 | 26914.7 | 4190.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3349.181 | 0 | 0
Annual Sum or Average | 1050080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 78076900000 | 43631.891 |  | 9179.851 | 26914.7 | 4190.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1945.992 | 0 | 0
Maximum of Months | 98079200000 | 61093.477 |  | 9179.851 | 26914.7 | 4190.817 | 0 | 18660.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3363.107 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 19966.2 | 17434.53 | 0 | 37400.73
Cost per Total Building Area ($/m2) | 39.06 | 34.11 | 0 | 73.17
Cost per Net Conditioned Building Area ($/m2) | 39.06 | 34.11 | 0 | 73.17

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3580 | 7003.77 | 7003.77
Net Site Energy | 3580 | 7003.77 | 7003.77
Total Source Energy | 6323.75 | 12371.54 | 12371.54
Net Source Energy | 6323.75 | 12371.54 | 12371.54
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1475.58 | 0 | 0 | 0 | 0
Cooling | 22.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 14.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 99.53 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 273.91 | 0 | 0 | 0 | 1377.36
Refrigeration | 57.41 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1029.59 | 2550.41 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.487 | 0.409 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 3.241 | 0.487 | 0.409 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 3.241 | 0.487 | 0.409 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 69008.55 | 46655.52 | 22353.03 | 0.68 | 3.19
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10504.67 | 8389.61 | 2115.06 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 214399.61 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 50330.4 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.78 | 3039.16 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.63 | 736.06 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 38224.1356 | 51.9145 | 56.2415 | 0 | 0.0005 | 36904.3014 | 14875.2699
February | 33471.0894 | 45.9116 | 50.7215 | 0 | 0.0004 | 33285.5946 | 13068.8323
March | 33947.4226 | 47.9664 | 56.0066 | 0 | 0.0004 | 36764.1373 | 13388.7766
April | 28843.7677 | 42.768 | 54.1409 | 0 | 0.0004 | 35552.87 | 11568.3133
May | 26629.9744 | 41.4053 | 56.2366 | 0 | 0.0004 | 36940.3617 | 10863.9368
June | 24304.7992 | 39.4086 | 56.5966 | 0 | 0.0004 | 37185.2548 | 10070.0709
July | 26026.8755 | 42.9475 | 63.0381 | 0 | 0.0005 | 41421.0301 | 10854.9467
August | 25667.4685 | 41.9127 | 60.7291 | 0 | 0.0005 | 39901.7993 | 10662.8208
September | 25012.7571 | 39.587 | 55.0884 | 0 | 0.0004 | 36189.7417 | 10270.7264
October | 28249.1106 | 42.8889 | 56.2894 | 0 | 0.0004 | 36969.6179 | 11425.6523
November | 31287.3004 | 45.053 | 54.3704 | 0 | 0.0004 | 35695.7261 | 12420.4312
December | 36898.0474 | 50.7076 | 56.2249 | 0 | 0.0004 | 36897.8942 | 14416.0021
Annual Sum or Average | 358562.7483 | 532.471 | 675.6839 | 0 | 0.0052 | 443708.3292 | 143885.7792
Minimum of Months | 24304.7992 | 39.4086 | 50.7215 | 0 | 0.0004 | 33285.5946 | 10070.0709
Maximum of Months | 38224.1356 | 51.9145 | 63.0381 | 0 | 0.0005 | 41421.0301 | 14875.2699
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85633700000 | 43207.602 | 16-JAN-11:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3337.83 | 0 | 0
February | 77236700000 | 43213.955 | 21-FEB-11:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3344.182 | 0 | 0
March | 85308400000 | 43222.076 | 30-MAR-10:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3352.303 | 0 | 0
April | 82497800000 | 43241.654 | 14-APR-10:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3371.882 | 0 | 0
May | 85717300000 | 49835.305 | 31-MAY-17:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 7966.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1999.447 | 0 | 0
June | 86285600000 | 60229.354 | 14-JUN-17:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 18198.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2160.885 | 0 | 0
July | 96114400000 | 64705.575 | 08-JUL-10:00 | 9179.851 | 26914.7 | 3775.222 | 0 | 21828.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3007.645 | 0 | 0
August | 92589100000 | 62372.812 | 12-AUG-11:00 | 9179.851 | 26914.7 | 3775.222 | 0 | 20319.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2183.266 | 0 | 0
September | 83975600000 | 53483.885 | 08-SEP-17:00 | 9179.851 | 26914.7 | 3775.222 | 0 | 11578.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2035.602 | 0 | 0
October | 85785200000 | 50177.295 | 07-OCT-15:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 8259.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.012 | 0 | 0
November | 82829200000 | 43259.486 | 09-NOV-11:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3389.713 | 0 | 0
December | 85618800000 | 43208.364 | 02-DEC-11:15 | 9179.851 | 26914.7 | 3775.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3338.591 | 0 | 0
Annual Sum or Average | 1029590000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 77236700000 | 43207.602 |  | 9179.851 | 26914.7 | 3775.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1999.447 | 0 | 0
Maximum of Months | 96114400000 | 64705.575 |  | 9179.851 | 26914.7 | 3775.222 | 0 | 21828.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3389.713 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14855.21 | 20212.06 | 0 | 35067.27
Cost per Total Building Area ($/m2) | 29.06 | 39.54 | 0 | 68.6
Cost per Net Conditioned Building Area ($/m2) | 29.06 | 39.54 | 0 | 68.6

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4430.03 | 8666.74 | 8666.74
Net Site Energy | 4430.03 | 8666.74 | 8666.74
Total Source Energy | 7343.95 | 14367.42 | 14367.42
Net Source Energy | 7343.95 | 14367.42 | 14367.42
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2308.94 | 0 | 0 | 0 | 0
Cooling | 7.98 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 237.23 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 13.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 599.05 | 800.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 96.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 309.55 | 0 | 0 | 0 | 1377.36
Refrigeration | 56.05 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1010.63 | 3419.4 | 0 | 0 | 0 | 1377.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.2612
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.9 | 18.59 | 1579.5173
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9773 | 3.72 | 237.3016
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9545 | 1.86 | 474.6032
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 371.75 | 0 | 180
KITCHEN_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.8 | 90 | 90 | E
KITCHEN_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68.93 | 0 | 90 | N
KITCHEN_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 139.41 | 0 | 180
EAST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 90 | 18.44
NORTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 0 | 45
SOUTH-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 60.26 | 180 | 45
WEST-ROOF | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 224.5 | 270 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 2.615 | 0.702 | 0.633 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 19.3 | 19.3 | 2.615 | 0.702 | 0.633 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 13.94 | 13.94 | 2.615 | 0.702 | 0.633 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45172.74 | 36077.45 | 9095.29 | 0.8 | 3.45
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8794.92 | 7024.11 | 1770.81 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 263904.06 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 52181.98 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.83 | 0 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.06 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.73 | 2984.38 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 616.26 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.43 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43484.5271 | 45.2858 | 121.724 | 0 | 0.0005 | 24403.3806 | 15944.454
February | 38247.9037 | 39.9496 | 109.5197 | 0 | 0.0004 | 21957.548 | 14042.3961
March | 36463.9606 | 38.848 | 120.3472 | 0 | 0.0004 | 24134.0973 | 13504.6522
April | 29553.4351 | 32.3608 | 115.8476 | 0 | 0.0004 | 23237.4812 | 11079.9632
May | 24666.0884 | 28.1146 | 119.8162 | 0 | 0.0004 | 24039.6326 | 9417.7441
June | 22388.6223 | 26.015 | 119.1356 | 0 | 0.0004 | 23905.2898 | 8624.5535
July | 22996.1172 | 26.8844 | 125.79 | 0 | 0.0004 | 25241.2054 | 8883.7421
August | 23335.5636 | 27.0115 | 122.0035 | 0 | 0.0004 | 24480.3271 | 8973.3655
September | 25078.6696 | 28.3261 | 116.4082 | 0 | 0.0004 | 23354.7155 | 9535.4625
October | 31274.4235 | 34.1438 | 120.4714 | 0 | 0.0004 | 24164.4032 | 11709.5731
November | 37241.7501 | 39.4038 | 117.2059 | 0 | 0.0004 | 23502.3521 | 13750.7228
December | 41300.9082 | 43.3016 | 121.6752 | 0 | 0.0005 | 24395.8237 | 15188.3888
Annual Sum or Average | 376031.9693 | 409.6449 | 1429.9445 | 0 | 0.0052 | 286816.2565 | 140655.0179
Minimum of Months | 22388.6223 | 26.015 | 109.5197 | 0 | 0.0004 | 21957.548 | 8624.5535
Maximum of Months | 43484.5271 | 45.2858 | 125.79 | 0 | 0.0005 | 25241.2054 | 15944.454
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85988000000 | 43851.64 | 01-JAN-11:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 3262.449 | 0 | 0
February | 77369800000 | 43009.4 | 27-FEB-11:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3314.209 | 0 | 0
March | 85039100000 | 43028.777 | 31-MAR-10:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3333.586 | 0 | 0
April | 81879800000 | 43038.207 | 14-APR-10:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3343.016 | 0 | 0
May | 84706200000 | 45845.3 | 30-MAY-17:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 4177.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1972.335 | 0 | 0
June | 84232900000 | 53617.982 | 20-JUN-17:00 | 9179.851 | 26914.7 | 3600.64 | 0 | 11847.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2074.893 | 0 | 0
July | 88940100000 | 55091.736 | 29-JUL-17:45 | 9179.851 | 26914.7 | 3600.64 | 0 | 13276.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2120.204 | 0 | 0
August | 86259100000 | 52443.16 | 15-AUG-17:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 10675.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2072.116 | 0 | 0
September | 82292900000 | 43065.072 | 01-SEP-10:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3369.881 | 0 | 0
October | 85145900000 | 43047.638 | 02-OCT-10:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3352.447 | 0 | 0
November | 82813100000 | 43020.486 | 14-NOV-11:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3325.294 | 0 | 0
December | 85961300000 | 43914.96 | 18-DEC-11:15 | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 3325.768 | 0 | 0
Annual Sum or Average | 1010630000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 77369800000 | 43009.4 |  | 9179.851 | 26914.7 | 3600.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1972.335 | 0 | 0
Maximum of Months | 88940100000 | 55091.736 |  | 9179.851 | 26914.7 | 3600.64 | 0 | 13276.341 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 3369.881 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24621.82 | 14255.39 | 0 | 38877.21
Cost per Total Building Area ($/m2) | 48.17 | 27.89 | 0 | 76.06
Cost per Net Conditioned Building Area ($/m2) | 48.17 | 27.89 | 0 | 76.06

## Picture
DOE Commercial Building Benchmark - Full Service Restaurant

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | SummerDesign | [24 empty] | 24 | 35.4 | 1845.86 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 17.7
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | 8.4 | 56.8 | 2961.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | 8.25
|  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | 6.55
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35 | 1825
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5 | 101.5 | 5292.5
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 7.75 | 52.65 | 2745.32
|  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 7.45
|  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 6.45
Hours_of_operation | On/Off | Through 12/31 | Weekday, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 80 | 4171.43
|  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | Weekday, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 80 | 4171.43
|  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Exhaust_SCH | On/Off | Through 12/31 | Weekday, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 72 | 3754.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482.4 | 3376.8 | 176076
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482.4
|  |  | Sun, Hol, Other | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 600 | 4200 | 219000
|  |  | Sat | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 600
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 600
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4 | 3096.8 | 161476
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
|  |  | Sun, Hol, Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640 | 4480 | 233600
|  |  | Sat | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 133 | 6935
|  |  | Sat | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_SDKitch_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720