## BuildingSummary
Building Summary Medium Office new construction
|  | Value | Data Source
Program
| Building Name | Benchmark Medium Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.29 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.77

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6435 | 0 | 0.2759
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6381 | 0 | 0.27592
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 10 | 0 | 529.3363 | 0 | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6435 | 0 | 0.2759
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.262
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6381 | 0 | 0.27592
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 10 | 0 | 529.3363 | 0 | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0702 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.65876
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.28 | 43.52 | 18.5806 | 7.0643 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6435 | 0 | 0.67264
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.92 | 65.28 | 18.5806 | 11.1589 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 111.5894 | 0 | 0.65876
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.28 | 43.52 | 18.5806 | 7.0638 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 70.6381 | 0 | 0.67267
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.76 | 8.07 | 0 | 37.4755 | 10 | 0 | 529.3363 | 0 | 0
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 0.10903
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 0.10903
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.84 | 0 | [10 empty] | 1.0017
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.72 | 652.8 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 31.9373 | 200.4848 | 72.0444 | 188.9275 |  | 176.4374 | 33.513 | 293.5454 | 8.9823 | 48.3147 | 261.4197 | 84.3871 | 73.6319 | 8.5933 | 8.1354 | 1.6864
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_1_COOLC DXCOIL | 133.4931 | 132.3059 | 122.9933 | 119.5586 | 99.4168 | 100.8089 | 102.261 | 125.3047 | 109.8797 | 99.2808 | 122.3339 | 105.7159 | 120.4456 | 103.2178 | 109.1357 | 127.9325
| VAV_2_COOLC DXCOIL | 142.3006 | 139.4602 | 143.1998 | 129.9956 | 113.3956 | 120.8399 | 132.0029 | 135.458 | 129.692 | 129.7489 | 133.5124 | 126.719 | 133.1015 | 124.3624 | 127.8076 | 173.6377
| VAV_3_COOLC DXCOIL | 146.7544 | 144.1025 | 149.8404 | 134.604 | 113.6707 | 128.8512 | 125.5494 | 141.1767 | 129.7859 | 129.4558 | 138.1065 | 122.0008 | 136.8606 | 121.5446 | 127.4188 | 172.0037
Heating (kW)
| HEATSYS1 BOILER | 255.4137 | 257.2234 | 267.8515 | 238.1921 | 222.3738 | 235.4241 | 266.5073 | 256.6723 | 225.1196 | 261.8609 | 251.4752 | 215.6264 | 252.0787 | 224.3184 | 252.452 | 345.2713
HVAC Efficiency
Air Conditioning (COP)
| VAV_1_COOLC DXCOIL | 3.72 | 3.74 | 3.85 | 3.79 | 3.99 | 3.99 | 4.14 | 3.78 | 4.14 | 4.14 | 3.79 | 4.14 | 3.84 | 4.14 | 4.02 | 4.14
| VAV_2_COOLC DXCOIL | 3.74 | 3.81 | 3.93 | 3.87 | 3.96 | 4.14 | 4.14 | 3.87 | 4.14 | 4.14 | 3.92 | 4.14 | 3.95 | 4.14 | 4.14 | 3.95
| VAV_3_COOLC DXCOIL | 3.78 | 3.82 | 3.99 | 3.89 | 3.94 | 4.14 | 4.14 | 3.89 | 4.14 | 4.14 | 3.92 | 4.14 | 3.95 | 4.14 | 4.14 | 3.95
| Heating Efficiency (%) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 6.45 | 6.49 | 6.44 | 6.06 | 5.62 | 5.69 | 6.18 | 6.31 | 6.64 | 6 | 6.19 | 6.39 | 6.26 | 6.24 | 6.25 | 7.73
| VAV_2_FAN | 6.99 | 7.14 | 7.85 | 6.9 | 6.31 | 7.3 | 7.97 | 7.17 | 7.83 | 7.84 | 7.27 | 7.66 | 7.36 | 7.51 | 7.72 | 10.49
| VAV_3_FAN | 7.38 | 7.42 | 8.44 | 7.2 | 6.27 | 7.78 | 7.58 | 7.55 | 7.84 | 7.82 | 7.5 | 7.37 | 7.55 | 7.34 | 7.7 | 10.39
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.089539 | 0.12266 | 0.10456 | 0.099577 | 0.13298 | 0.10199 | 0.15177 | 0.079617 | 0.037341 | 0.078277 | 0.086799 | 0.03736 | 0.064446 | 0.080279 | 0.064393 | 0.10435
| Total Cost ($/m2) | 10.84 | 13.87 | 11.64 | 10.11 | 12.44 | 10.27 | 13.36 | 7.9 | 3.5 | 6.77 | 8.07 | 3.34 | 5.91 | 6.98 | 5.58 | 9.08
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01141 | 0.0080553 | 0.0082089 | 0.0096119 | 0.0086218 | 0.0076774 | 0.0085321 | 0.0096942 | 0.0068962 | 0.0084048 | 0.008334 | 0.006909 | 0.0078849 | 0.0080818 | 0.0078752 | 0.004117
| Total Cost ($/m2) | 0.13 | 0.54 | 0.48 | 0.92 | 0.3 | 0.48 | 0.98 | 1.51 | 0.68 | 1.39 | 1.72 | 0.99 | 2.23 | 1.83 | 2.6 | 2.3
Total Utility Costs
| Cost Intensity ($/m2) | 10.98 | 14.42 | 12.12 | 11.03 | 12.74 | 10.75 | 14.35 | 9.41 | 4.18 | 8.16 | 9.79 | 4.33 | 8.14 | 8.81 | 8.18 | 11.38
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 197813.8889 | 158913.8889 | 145736.1111 | 103005.5556 | 66119.4444 | 95780.5556 | 35697.2222 | 90669.4444 | 60047.2222 | 28147.2222 | 59113.8889 | 40819.4444 | 51722.2222 | 28425 | 26102.7778 | 20711.1111
| Interior Lighting | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667 | 153491.6667
| Exterior Lighting | 7775 | 7772.2222 | 7772.2222 | 7769.4444 | 7763.8889 | 7763.8889 | 7766.6667 | 7761.1111 | 7763.8889 | 7750 | 7763.8889 | 7758.3333 | 7758.3333 | 7755.5556 | 7752.7778 | 7705.5556
| Interior Equipment | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900 | 223900
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 20294.4444 | 19311.1111 | 23547.2222 | 17452.7778 | 14666.6667 | 20725 | 17591.6667 | 18536.1111 | 20966.6667 | 17583.3333 | 18588.8889 | 19311.1111 | 19583.3333 | 19002.7778 | 20283.3333 | 26736.1111
| Pumps | 80.5556 | 158.3333 | 138.8889 | 200 | 105.5556 | 147.2222 | 208.3333 | 280.5556 | 216.6667 | 275 | 352.7778 | 294.4444 | 488.8889 | 433.3333 | 552.7778 | 800
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 603355.5556 | 563547.2222 | 554586.1111 | 505819.4444 | 466047.2222 | 501808.3333 | 438655.5556 | 494641.6667 | 466386.1111 | 431147.2222 | 463208.3333 | 445575 | 456941.6667 | 433005.5556 | 432080.5556 | 433338.8889
Gas (MJ)
| Heating | 30220 | 303140 | 259780 | 440700 | 139990 | 276750 | 535550 | 736210 | 453080 | 782470 | 985500 | 673760 | 1364240 | 1086030 | 1596960 | 2731090
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 27740 | 31670 | 29400 | 35470 | 34740 | 32130 | 37990 | 38460 | 37890 | 40020 | 41080 | 40940 | 43340 | 43750 | 47080 | 51600
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 57960 | 334810 | 289170 | 476170 | 174730 | 308870 | 573540 | 774670 | 490970 | 822490 | 1026570 | 714700 | 1407580 | 1129780 | 1644040 | 2782690
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2230040 | 2363580 | 2285680 | 2297110 | 1852500 | 2115380 | 2152710 | 2555380 | 2169960 | 2374610 | 2694130 | 2318770 | 3052570 | 2688610 | 3199540 | 4342710
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 142.9351 | 114.827 | 105.3051 | 74.4291 | 47.7762 | 69.2085 | 25.7939 | 65.5154 | 43.3886 | 20.3384 | 42.7141 | 29.4951 | 37.3731 | 20.5392 | 18.8612 | 14.9653
| Interior Lighting (elec) | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091 | 110.9091
| Exterior Lighting (elec) | 5.618 | 5.616 | 5.616 | 5.614 | 5.61 | 5.61 | 5.612 | 5.608 | 5.61 | 5.5999 | 5.61 | 5.606 | 5.606 | 5.604 | 5.602 | 5.5678
| Interior Equipment (elec) | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843 | 161.7843
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 14.6642 | 13.9537 | 17.0146 | 12.6109 | 10.5977 | 14.9753 | 12.7113 | 13.3937 | 15.15 | 12.7053 | 13.4318 | 13.9537 | 14.1504 | 13.7309 | 14.6562 | 19.3188
| Pumps (elec) | 0.058207 | 0.11441 | 0.10036 | 0.14451 | 0.076272 | 0.10638 | 0.15054 | 0.20272 | 0.15656 | 0.19871 | 0.25491 | 0.21276 | 0.35326 | 0.31312 | 0.39942 | 0.57806
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 435.9689 | 407.2045 | 400.7294 | 365.4919 | 336.7535 | 362.5936 | 316.961 | 357.4151 | 336.9984 | 311.5357 | 334.7022 | 321.9608 | 330.1741 | 312.8785 | 312.2101 | 313.1193
Gas (MJ/m2)
| Heating (gas) | 6.0656 | 60.8447 | 52.1417 | 88.4551 | 28.0981 | 55.5479 | 107.4929 | 147.7684 | 90.9399 | 157.0534 | 197.8046 | 135.2337 | 273.8234 | 217.9825 | 320.5337 | 548.1706
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 5.5678 | 6.3566 | 5.901 | 7.1194 | 6.9728 | 6.449 | 7.6252 | 7.7195 | 7.6051 | 8.0326 | 8.2454 | 8.2173 | 8.699 | 8.7813 | 9.4497 | 10.3569
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11.6334 | 67.2014 | 58.0407 | 95.5744 | 35.0709 | 61.9948 | 115.1181 | 155.4878 | 98.545 | 165.086 | 206.0479 | 143.451 | 282.5223 | 226.7637 | 329.9834 | 558.5275
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 447.6024 | 474.4058 | 458.7701 | 461.0643 | 371.8244 | 424.5884 | 432.0811 | 512.903 | 435.5434 | 476.6197 | 540.7522 | 465.4118 | 612.6964 | 539.6442 | 642.1955 | 871.6468
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 155.8806 | 142.1545 | 129.7135 | 124.5422 | 127.7279 | 118.3978 | 112.6704 | 124.4928 | 112.2509 | 110.377 | 110.4837 | 114.8371 | 110.9872 | 112.4896 | 110.9212 | 114.124
| Feb | 160.4845 | 142.5087 | 133.8391 | 127.5386 | 126.0659 | 121.1773 | 128.0039 | 118.2332 | 120.7016 | 115.2465 | 110.3154 | 110.5784 | 110.4739 | 112.4605 | 110.6935 | 113.1898
| Mar | 163.4885 | 142.1439 | 150.7663 | 128.6332 | 125.2922 | 124.8238 | 122.3006 | 132.3725 | 122.8629 | 119.7464 | 123.3282 | 121.0282 | 115.6908 | 119.1232 | 110.4329 | 113.1017
| Apr | 170.1593 | 153.0296 | 152.0278 | 140.1982 | 129.4392 | 144.7262 | 124.4412 | 132.1647 | 134.7347 | 115.9964 | 128.9381 | 126.4145 | 122.687 | 115.9513 | 114.8017 | 111.1787
| May | 179.5781 | 182.0474 | 182.5554 | 159.2257 | 141.2599 | 163.7412 | 129.6301 | 148.3044 | 149.9002 | 131.2043 | 148.1155 | 139.6088 | 147.4087 | 124.5936 | 126.3364 | 127.1098
| Jun | 189.5667 | 183.7411 | 234.7862 | 171.4607 | 136.9451 | 209.1426 | 133.7183 | 180.3882 | 165.1726 | 133.5793 | 170.8543 | 151.2815 | 169.9099 | 155.5829 | 148.5125 | 151.6757
| Jul | 185.5309 | 194.7674 | 224.7549 | 190.6168 | 144.0254 | 205.45 | 144.1732 | 187.2335 | 174.8318 | 145.0973 | 178.1763 | 164.3967 | 169.2534 | 155.7826 | 165.5416 | 150.1052
| Aug | 194.1769 | 191.8954 | 232.0905 | 172.9281 | 159.1762 | 197.865 | 138.8436 | 186.7672 | 171.3841 | 142.6356 | 176.4694 | 157.8578 | 166.7046 | 148.8304 | 153.5837 | 148.0726
| Sep | 186.2562 | 180.1538 | 200.453 | 165.3335 | 154.1237 | 179.2291 | 156.3446 | 157.5133 | 152.9637 | 140.2049 | 151.6318 | 143.8617 | 146.4769 | 138.6777 | 146.437 | 117.7298
| Oct | 178.2652 | 162.3023 | 160.5556 | 144.595 | 137.6815 | 149.6351 | 139.3052 | 143.4367 | 136.7395 | 125.4233 | 140.3971 | 133.5889 | 126.8632 | 125.1055 | 120.2561 | 113.0221
| Nov | 162.6565 | 149.1742 | 143.867 | 128.8226 | 130.4436 | 123.674 | 120.6706 | 134.6736 | 119.2263 | 115.8324 | 136.1052 | 122.1803 | 120.2945 | 111.8944 | 110.5014 | 113.1167
| Dec | 151.9776 | 140.8959 | 132.7287 | 129.1573 | 129.8314 | 122.7179 | 111.9742 | 116.1329 | 111.6754 | 110.3351 | 110.4169 | 110.6456 | 110.4116 | 112.4488 | 110.5873 | 113.1581
Time of Peak Electrical Demand
| Jan | 23-JAN-16:10 | 03-JAN-08:00 | 27-JAN-13:30 | 24-JAN-08:00 | 26-JAN-13:09 | 18-JAN-13:00 | 06-JAN-13:00 | 09-JAN-08:00 | 26-JAN-16:10 | 02-JAN-08:09 | 30-JAN-08:09 | 24-JAN-13:00 | 02-JAN-08:09 | 17-JAN-08:09 | 09-JAN-08:09 | 02-JAN-08:09
| Feb | 22-FEB-16:10 | 23-FEB-13:00 | 28-FEB-16:19 | 22-FEB-08:09 | 13-FEB-12:30 | 08-FEB-13:00 | 15-FEB-16:10 | 15-FEB-13:00 | 14-FEB-16:10 | 21-FEB-13:00 | 06-FEB-08:09 | 07-FEB-13:00 | 06-FEB-08:09 | 02-FEB-14:00 | 02-FEB-08:09 | 03-FEB-08:09
| Mar | 27-MAR-15:20 | 29-MAR-07:00 | 17-MAR-15:00 | 30-MAR-07:00 | 03-MAR-13:00 | 31-MAR-12:00 | 01-MAR-13:09 | 09-MAR-13:00 | 02-MAR-13:00 | 29-MAR-12:00 | 31-MAR-15:09 | 30-MAR-12:00 | 23-MAR-15:00 | 30-MAR-15:20 | 27-MAR-07:10 | 13-MAR-07:10
| Apr | 03-APR-15:09 | 17-APR-15:00 | 17-APR-15:00 | 20-APR-15:00 | 11-APR-15:00 | 21-APR-15:30 | 28-APR-12:09 | 04-APR-07:00 | 21-APR-15:00 | 18-APR-15:00 | 10-APR-07:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:09 | 03-APR-07:10
| May | 15-MAY-15:00 | 18-MAY-15:30 | 30-MAY-15:00 | 15-MAY-15:09 | 30-MAY-07:00 | 31-MAY-15:00 | 26-MAY-12:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 24-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 30-MAY-12:39
| Jun | 27-JUN-15:20 | 13-JUN-15:00 | 28-JUN-15:00 | 19-JUN-15:00 | 29-JUN-07:00 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:30 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 26-JUN-15:20 | 14-JUN-15:00 | 21-JUN-15:20
| Jul | 03-JUL-15:20 | 05-JUL-15:00 | 11-JUL-15:50 | 03-JUL-15:00 | 11-JUL-07:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-15:30 | 03-JUL-15:30 | 24-JUL-15:20 | 03-JUL-15:30 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 07-JUL-07:00 | 11-JUL-15:00
| Aug | 21-AUG-15:09 | 28-AUG-15:30 | 01-AUG-15:50 | 14-AUG-15:00 | 08-AUG-15:00 | 04-AUG-15:50 | 15-AUG-12:09 | 17-AUG-15:00 | 01-AUG-15:20 | 07-AUG-15:39 | 04-AUG-15:50 | 30-AUG-15:30 | 25-AUG-15:00 | 09-AUG-15:00 | 14-AUG-07:00 | 15-AUG-12:00
| Sep | 11-SEP-15:09 | 15-SEP-15:20 | 11-SEP-15:30 | 11-SEP-12:00 | 25-SEP-15:20 | 01-SEP-15:09 | 28-SEP-15:09 | 08-SEP-15:00 | 05-SEP-12:00 | 01-SEP-15:00 | 06-SEP-12:30 | 01-SEP-15:00 | 14-SEP-15:09 | 12-SEP-12:00 | 07-SEP-15:09 | 07-SEP-15:00
| Oct | 06-OCT-15:20 | 13-OCT-15:09 | 02-OCT-15:09 | 12-OCT-15:00 | 19-OCT-12:00 | 03-OCT-15:09 | 31-OCT-12:50 | 12-OCT-12:00 | 11-OCT-15:00 | 17-OCT-12:00 | 30-OCT-12:09 | 05-OCT-15:20 | 06-OCT-15:09 | 06-OCT-15:09 | 27-OCT-12:30 | 30-OCT-07:10
| Nov | 07-NOV-16:10 | 27-NOV-08:30 | 13-NOV-13:00 | 22-NOV-13:30 | 20-NOV-13:09 | 10-NOV-13:09 | 14-NOV-13:09 | 03-NOV-12:00 | 08-NOV-13:00 | 03-NOV-12:00 | 02-NOV-07:00 | 10-NOV-13:00 | 02-NOV-15:09 | 03-NOV-07:10 | 27-NOV-08:09 | 06-NOV-08:09
| Dec | 19-DEC-13:00 | 19-DEC-13:00 | 13-DEC-13:09 | 26-DEC-08:00 | 19-DEC-13:09 | 05-DEC-13:00 | 01-DEC-13:00 | 08-DEC-08:00 | 05-DEC-13:00 | 11-DEC-08:09 | 26-DEC-08:09 | 11-DEC-08:09 | 18-DEC-08:09 | 18-DEC-08:09 | 11-DEC-08:09 | 29-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 7268.07 | 7734.1 | 6630.72 | 6645.64 | 5383.5 | 6799.17 | 5513.81 | 7213.75 | 6107.03 | 3601.96 | 7034.16 | 6102.76 | 7190.91 | 6652.2 | 7141.53 | 8611.09
| Total Source Energy (MJ/m2) | 1458.81 | 1552.35 | 1330.89 | 1333.88 | 1080.55 | 1364.7 | 1106.71 | 1447.91 | 1225.77 | 722.97 | 1411.86 | 1224.92 | 1443.32 | 1335.2 | 1433.41 | 1728.38
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
| Total Building | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
Emissions
| Carbon Equivalent (kg) | 166515.0444 | 194014.7608 | 172630.1348 | 164397.2116 | 57615.8031 | 174817.1934 | 61606.4423 | 147450.884 | 199371.4593 | 46233.7755 | 265471.605 | 194904.4855 | 181790.3941 | 178609.9265 | 177545.0972 | 172115.5958
| CO2 (kg) | 386174.0709 | 489132.3325 | 408776.8236 | 378436.1141 | 154515.6754 | 416956.7479 | 166747.5785 | 339697.0629 | 469504.8346 | 117446.6471 | 623287.4969 | 461351.9659 | 433916.7192 | 426900.0602 | 426618.9482 | 450430.2281
| NOX (kg) | 678.4747 | 635.8283 | 679.1131 | 705.3776 | 132.7049 | 671.9985 | 144.255 | 635.1373 | 802.1069 | 158.7587 | 1086.1088 | 777.9335 | 724.5744 | 706.7419 | 699.961 | 514.2944
| SO2 (kg) | 2582.6157 | 2688.2086 | 2230.1737 | 1775.5501 | 1356.1854 | 2760.4297 | 1276.5898 | 1805.8439 | 2036.7479 | 333.4617 | 3121.9356 | 1945.9292 | 1078.8323 | 1156.4827 | 1020.2229 | 2206.6171
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0118 | 0.0076 | 0.0061 | 0.0065 | 0.0006 | 0.0052 | 0.0006 | 0.0074 | 0.008 | 0.0014 | 0.0095 | 0.0077 | 0.008 | 0.0081 | 0.0076 | 0.0078
| Water for Electricity (m3) | 319.6321 | 916.9569 | 16473.6 | 3158.13 | 8182.73 | 13766.6 | 7701.81 | 112.302 | 2117.77 | 4404.93 | 718.6416 | 2023.27 | 708.9174 | 27428.4 | 670.3492 | 442.7343

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2230.04 | 447.6 | 447.6
Net Site Energy | 2230.04 | 447.6 | 447.6
Total Source Energy | 7268.07 | 1458.81 | 1458.81
Net Source Energy | 7268.07 | 1458.81 | 1458.81
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 30.22 | 0 | 0 | 0 | 0
Cooling | 712.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 73.06 | 0 | 0 | 0 | 0 | 0
Pumps | 0.29 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.74 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2172.08 | 57.96 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 195.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 255413.66 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 133493.12 | 96814.75 | 36678.37 | 0.73 | 3.72
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 142300.57 | 103878.52 | 38422.05 | 0.73 | 3.74
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 146754.4 | 108160.48 | 38593.91 | 0.74 | 3.78
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 40504.42 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 40784.29 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 41994.53 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7674.23 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10454.17 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8023.22 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12538.78 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9621.99 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11806.78 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9861.43 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13708.79 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10643.95 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11696.46 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11525.85 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14685.51 | -
VAV_1_HEATC | Coil:Heating:Gas | 18825.47 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 3147.78 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 2542.15 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.45 | 12107.69 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.99 | 13114.97 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.38 | 13843.16 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1489.15 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29619.0395 | 51.5917 | 194.5698 | 0 | 0.0009 | 24080.1948 | 12726.7551
February | 26994.4583 | 47.2511 | 179.1465 | 0 | 0.0008 | 22171.5591 | 11622.1622
March | 31474.8154 | 55.1839 | 209.592 | 0 | 0.001 | 25939.6309 | 13560.1941
April | 30047.9494 | 52.8651 | 201.5299 | 0 | 0.0009 | 24941.9905 | 12963.7882
May | 34293.9298 | 60.3662 | 230.2501 | 0 | 0.001 | 28496.5147 | 14798.7488
June | 35400.5324 | 62.3357 | 237.8503 | 0 | 0.0011 | 29437.1506 | 15278.4467
July | 35276.1585 | 62.1199 | 237.0398 | 0 | 0.0011 | 29336.8435 | 15225.0887
August | 37788.6435 | 66.5436 | 253.917 | 0 | 0.0012 | 31425.6289 | 16309.3999
September | 33729.6771 | 59.3865 | 226.5683 | 0 | 0.001 | 28040.8473 | 14556.6152
October | 32785.2029 | 57.6955 | 220.0029 | 0 | 0.001 | 27228.2763 | 14146.1959
November | 30232.243 | 53.1752 | 202.6541 | 0 | 0.0009 | 25081.1138 | 13041.8753
December | 28531.421 | 49.9602 | 189.4949 | 0 | 0.0009 | 23452.3143 | 12285.7745
Annual Sum or Average | 386174.0709 | 678.4747 | 2582.6157 | 0 | 0.0118 | 319632.0648 | 166515.0444
Minimum of Months | 26994.4583 | 47.2511 | 179.1465 | 0 | 0.0008 | 22171.5591 | 11622.1622
Maximum of Months | 37788.6435 | 66.5436 | 253.917 | 0 | 0.0012 | 31425.6289 | 16309.3999
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 163638000000 | 155880.648 | 23-JAN-16:10 | 48247.488 | 50956.166 | 5816.695 | 0 | 50851.859 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 150668000000 | 160484.48 | 22-FEB-16:10 | 48247.488 | 50956.166 | 6296.542 | 0 | 54975.844 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 176274000000 | 163488.498 | 27-MAR-15:20 | 48247.488 | 50956.166 | 6609.662 | 0 | 57666.742 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 169495000000 | 170159.286 | 03-APR-15:09 | 48247.488 | 50956.166 | 7328.288 | 0 | 63618.904 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 193650000000 | 179578.134 | 15-MAY-15:00 | 48247.488 | 50956.166 | 7808.203 | 0 | 72557.837 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 200042000000 | 189566.743 | 27-JUN-15:20 | 48247.488 | 50956.166 | 7874.088 | 0 | 82480.561 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 199360000000 | 185530.937 | 03-JUL-15:20 | 48247.488 | 50956.166 | 8167.472 | 0 | 78151.371 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 213555000000 | 194176.868 | 21-AUG-15:09 | 48247.488 | 50956.166 | 8941.601 | 0 | 86023.173 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 190553000000 | 186256.196 | 11-SEP-15:09 | 48247.488 | 50956.166 | 8906.694 | 0 | 78137.408 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 185031000000 | 178265.19 | 06-OCT-15:20 | 48247.488 | 50956.166 | 7518.918 | 0 | 71534.177 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 170440000000 | 162656.55 | 07-NOV-16:10 | 48247.488 | 50956.166 | 6553.282 | 0 | 56891.174 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 159372000000 | 151977.647 | 19-DEC-13:00 | 48247.488 | 51598.363 | 5120.365 | 0 | 47002.99 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2172080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 150668000000 | 151977.647 |  | 48247.488 | 50956.166 | 5120.365 | 0 | 47002.99 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 213555000000 | 194176.868 |  | 48247.488 | 51598.363 | 8941.601 | 0 | 86023.173 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 54023.98 | 661.35 | 0 | 54685.33
Cost per Total Building Area ($/m2) | 10.84 | 0.13 | 0 | 10.98
Cost per Net Conditioned Building Area ($/m2) | 10.84 | 0.13 | 0 | 10.98

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2363.58 | 474.41 | 474.41
Net Site Energy | 2363.58 | 474.41 | 474.41
Total Source Energy | 7734.1 | 1552.35 | 1552.35
Net Source Energy | 7734.1 | 1552.35 | 1552.35
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 303.14 | 0 | 0 | 0 | 0
Cooling | 572.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 69.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0.57 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 31.67 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2028.77 | 334.81 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 195.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 257223.42 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 132305.94 | 96496.28 | 35809.66 | 0.73 | 3.74
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 139460.24 | 103561.16 | 35899.08 | 0.74 | 3.81
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 144102.54 | 107285.65 | 36816.89 | 0.74 | 3.82
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 39617.89 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 40999.23 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 40836.46 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8555.58 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10308.08 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7901.08 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12910.6 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10583.72 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11748.56 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9818.01 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14141.59 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11484.75 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11551.19 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11668.02 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15213.23 | -
VAV_1_HEATC | Coil:Heating:Gas | 15129.08 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 14112.37 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 13672.2 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.49 | 12167.25 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.14 | 13394.49 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.42 | 13925.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1499.7 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 38030.638 | 48.2295 | 192.1084 | 0 | 0.0005 | 65523.4015 | 14929.3185
February | 33617.9069 | 42.5944 | 169.2713 | 0 | 0.0005 | 57734.0507 | 13192.0253
March | 39273.671 | 50.81 | 212.4495 | 0 | 0.0006 | 72466.1331 | 15546.7026
April | 36963.4259 | 48.3279 | 207.0497 | 0 | 0.0006 | 70626.5815 | 14697.4996
May | 42858.6857 | 56.2444 | 242.9955 | 0 | 0.0007 | 82888.9504 | 17068.4968
June | 46394.9565 | 60.9291 | 263.6615 | 0 | 0.0007 | 89938.5876 | 18482.4921
July | 46944.4582 | 61.6556 | 266.8521 | 0 | 0.0007 | 91026.9615 | 18702.0225
August | 49427.6729 | 64.9125 | 280.9052 | 0 | 0.0008 | 95820.6557 | 19690.7255
September | 41860.5785 | 54.9625 | 237.728 | 0 | 0.0007 | 81092.2738 | 16674.6032
October | 39841.2907 | 52.1822 | 224.4544 | 0 | 0.0006 | 76563.899 | 15853.6254
November | 36731.8586 | 47.7656 | 202.118 | 0 | 0.0006 | 68943.2172 | 14571.9732
December | 37187.1898 | 47.2147 | 188.6151 | 0 | 0.0005 | 64332.1885 | 14605.276
Annual Sum or Average | 489132.3325 | 635.8283 | 2688.2086 | 0 | 0.0076 | 916956.9005 | 194014.7608
Minimum of Months | 33617.9069 | 42.5944 | 169.2713 | 0 | 0.0005 | 57734.0507 | 13192.0253
Maximum of Months | 49427.6729 | 64.9125 | 280.9052 | 0 | 0.0008 | 95820.6557 | 19690.7255
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 144971000000 | 142154.457 | 03-JAN-08:00 | 48247.488 | 58341.44 | 3399.523 | 0 | 32150.759 | 0 | 15.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 127737000000 | 142508.655 | 23-FEB-13:00 | 48247.488 | 51598.363 | 4347.829 | 0 | 38306.534 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 160331000000 | 142143.925 | 29-MAR-07:00 | 48247.488 | 58341.44 | 3568.865 | 0 | 31976.853 | 0 | 9.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 156261000000 | 153029.627 | 17-APR-15:00 | 48247.488 | 50956.166 | 4906.355 | 0 | 48911.178 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 183392000000 | 182047.433 | 18-MAY-15:30 | 48247.488 | 50956.166 | 7563.389 | 0 | 75271.95 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 198989000000 | 183741.12 | 13-JUN-15:00 | 48247.488 | 50956.166 | 8093.525 | 0 | 76435.501 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 201397000000 | 194767.361 | 05-JUL-15:00 | 48247.488 | 50956.166 | 9229.97 | 0 | 86325.297 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 212003000000 | 191895.43 | 28-AUG-15:30 | 48247.488 | 50956.166 | 9447.375 | 0 | 83235.961 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 179417000000 | 180153.792 | 15-SEP-15:20 | 48247.488 | 50956.166 | 6268.274 | 0 | 74673.424 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 169398000000 | 162302.297 | 13-OCT-15:09 | 48247.488 | 50956.166 | 6300.785 | 0 | 56789.417 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 152537000000 | 149174.192 | 27-NOV-08:30 | 48247.488 | 58341.44 | 3758.256 | 0 | 38818.54 | 0 | 8.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 142335000000 | 140895.916 | 19-DEC-13:00 | 48247.488 | 51598.363 | 3890.63 | 0 | 37150.994 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2028770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 127737000000 | 140895.916 |  | 48247.488 | 50956.166 | 3399.523 | 0 | 31976.853 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 212003000000 | 194767.361 |  | 48247.488 | 58341.44 | 9447.375 | 0 | 86325.297 | 0 | 15.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 69125.94 | 2696.99 | 0 | 71822.93
Cost per Total Building Area ($/m2) | 13.87 | 0.54 | 0 | 14.42
Cost per Net Conditioned Building Area ($/m2) | 13.87 | 0.54 | 0 | 14.42

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2285.68 | 458.77 | 458.77
Net Site Energy | 2285.68 | 458.77 | 458.77
Total Source Energy | 6630.72 | 1330.89 | 1330.89
Net Source Energy | 6630.72 | 1330.89 | 1330.89
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 259.78 | 0 | 0 | 0 | 0
Cooling | 524.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 84.77 | 0 | 0 | 0 | 0 | 0
Pumps | 0.5 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 29.4 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1996.51 | 289.17 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 195.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 267851.51 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122993.32 | 92204.66 | 30788.66 | 0.75 | 3.85
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 143199.8 | 109506.5 | 33693.3 | 0.76 | 3.93
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 149840.41 | 115945.64 | 33894.77 | 0.77 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 35163.36 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41274.31 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 43329.64 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9633.9 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10271.06 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7815.21 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13043.56 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12839.9 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12584.81 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10861.72 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15012.29 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14064.9 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12705.63 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13063.82 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16338.43 | -
VAV_1_HEATC | Coil:Heating:Gas | 9149.13 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 7032.67 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 6151.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.44 | 12081.59 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.85 | 14730.31 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.44 | 15832.92 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1561.66 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29395.0929 | 46.809 | 145.716 | 0 | 0.0004 | 1076260 | 12208.9486
February | 26551.9043 | 42.6117 | 134.0107 | 0 | 0.0004 | 989819.8889 | 11061.4513
March | 31868.9785 | 52.7418 | 172.3991 | 0 | 0.0005 | 1273450 | 13438.0179
April | 30167.769 | 50.5959 | 168.0401 | 0 | 0.0005 | 1241280 | 12788.3894
May | 34814.277 | 58.6831 | 196.0508 | 0 | 0.0005 | 1448210 | 14787.8433
June | 41032.2694 | 69.2584 | 231.7476 | 0 | 0.0006 | 1711900 | 17438.5436
July | 42295.2045 | 71.4077 | 239.008 | 0 | 0.0006 | 1765540 | 17977.068
August | 43801.8864 | 73.9483 | 247.4991 | 0 | 0.0007 | 1828260 | 18617.1426
September | 37479.5661 | 63.2455 | 211.5644 | 0 | 0.0006 | 1562810 | 15927.0137
October | 32655.7827 | 54.8494 | 182.4827 | 0 | 0.0005 | 1347970 | 13851.2439
November | 29313.6074 | 48.4694 | 158.2622 | 0 | 0.0004 | 1169020 | 12356.1288
December | 29400.4853 | 46.4928 | 143.3931 | 0 | 0.0004 | 1059080 | 12178.3436
Annual Sum or Average | 408776.8236 | 679.1131 | 2230.1737 | 0 | 0.0061 | 16473600 | 172630.1348
Minimum of Months | 26551.9043 | 42.6117 | 134.0107 | 0 | 0.0004 | 989819.8889 | 11061.4513
Maximum of Months | 43801.8864 | 73.9483 | 247.4991 | 0 | 0.0007 | 1828260 | 18617.1426
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 130436000000 | 129713.504 | 27-JAN-13:30 | 48247.488 | 51598.363 | 4567.098 | 0 | 25292.034 | 0 | 8.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119960000000 | 133839.067 | 28-FEB-16:19 | 48247.488 | 50956.166 | 4538.861 | 0 | 30088.112 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 154335000000 | 150766.298 | 17-MAR-15:00 | 48247.488 | 50956.166 | 6067.133 | 0 | 45487.072 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 150436000000 | 152027.793 | 17-APR-15:00 | 48247.488 | 50956.166 | 6584.442 | 0 | 46231.258 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 175515000000 | 182555.42 | 30-MAY-15:00 | 48247.488 | 50956.166 | 10263.567 | 0 | 73079.76 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 207473000000 | 234786.219 | 28-JUN-15:00 | 48247.488 | 50956.166 | 23769.26 | 0 | 111804.864 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 213973000000 | 224754.868 | 11-JUL-15:50 | 48247.488 | 50956.166 | 16867.284 | 0 | 108675.491 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 221574000000 | 232090.541 | 01-AUG-15:50 | 48247.488 | 50956.166 | 23537.227 | 0 | 109341.22 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 189404000000 | 200452.997 | 11-SEP-15:30 | 48247.488 | 50956.166 | 12663.856 | 0 | 88577.047 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 163367000000 | 160555.584 | 02-OCT-15:09 | 48247.488 | 50956.166 | 7756.23 | 0 | 53587.259 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 141679000000 | 143867.033 | 13-NOV-13:00 | 48247.488 | 51598.363 | 5449.435 | 0 | 38563.307 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 128355000000 | 132728.703 | 13-DEC-13:09 | 48247.488 | 51598.363 | 4585.548 | 0 | 28286.108 | 0 | 11.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1996510000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119960000000 | 129713.504 |  | 48247.488 | 50956.166 | 4538.861 | 0 | 25292.034 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 221574000000 | 234786.219 |  | 48247.488 | 51598.363 | 23769.26 | 0 | 111804.864 | 0 | 11.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 57987.63 | 2373.76 | 0 | 60361.39
Cost per Total Building Area ($/m2) | 11.64 | 0.48 | 0 | 12.12
Cost per Net Conditioned Building Area ($/m2) | 11.64 | 0.48 | 0 | 12.12

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2297.11 | 461.07 | 461.07
Net Site Energy | 2297.11 | 461.07 | 461.07
Total Source Energy | 6645.64 | 1333.88 | 1333.88
Net Source Energy | 6645.64 | 1333.88 | 1333.88
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 440.7 | 0 | 0 | 0 | 0
Cooling | 370.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 62.83 | 0 | 0 | 0 | 0 | 0
Pumps | 0.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 35.47 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1820.95 | 476.17 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 195.85 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 238192.14 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 119558.55 | 88389.88 | 31168.66 | 0.74 | 3.79
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129995.59 | 98005.54 | 31990.05 | 0.75 | 3.87
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 134604.01 | 101851.73 | 32752.27 | 0.76 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 39001.19 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41349.52 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 41442.11 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7297.91 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8536.44 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6448.36 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10325.35 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9568 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10266.96 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8586.51 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11779.77 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10510.04 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10191.35 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10122.85 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12897.81 | -
VAV_1_HEATC | Coil:Heating:Gas | 20380.5 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 19116.9 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 18657.53 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.06 | 11362.02 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.9 | 12939.41 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.2 | 13512.74 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1388.74 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32097.747 | 55.2051 | 127.9355 | 0 | 0.0005 | 227511.4138 | 13516.7246
February | 27913.0965 | 49.0294 | 116.2636 | 0 | 0.0004 | 206766.5219 | 11848.8573
March | 31178.5128 | 57.5935 | 143.7294 | 0 | 0.0005 | 255643.0185 | 13496.2021
April | 29000.0949 | 54.7677 | 139.5614 | 0 | 0.0005 | 248241.1617 | 12663.9
May | 31816.6493 | 61.1392 | 158.2745 | 0 | 0.0006 | 281536.4745 | 13991.0325
June | 34184.9316 | 65.8622 | 170.8989 | 0 | 0.0006 | 303994.1221 | 15048.3445
July | 34490.4156 | 66.4575 | 172.4592 | 0 | 0.0006 | 306769.6055 | 15183.4433
August | 36799.0352 | 70.9112 | 184.0293 | 0 | 0.0007 | 327350.6018 | 16200.2495
September | 32098.593 | 61.8112 | 160.3149 | 0 | 0.0006 | 285167.171 | 14127.0319
October | 29764.354 | 56.5464 | 144.8831 | 0 | 0.0005 | 257710.1733 | 13028.6082
November | 28920.0267 | 53.0278 | 131.388 | 0 | 0.0005 | 233688.2185 | 12482.2127
December | 30172.6575 | 53.0263 | 125.8123 | 0 | 0.0005 | 223748.5174 | 12810.6051
Annual Sum or Average | 378436.1141 | 705.3776 | 1775.5501 | 0 | 0.0065 | 3158130 | 164397.2116
Minimum of Months | 27913.0965 | 49.0294 | 116.2636 | 0 | 0.0004 | 206766.5219 | 11848.8573
Maximum of Months | 36799.0352 | 70.9112 | 184.0293 | 0 | 0.0007 | 327350.6018 | 16200.2495
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 131181000000 | 124542.229 | 24-JAN-08:00 | 48247.488 | 58341.44 | 3255.46 | 0 | 14665.489 | 0 | 32.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119220000000 | 127538.554 | 22-FEB-08:09 | 48247.488 | 58341.44 | 3255.46 | 0 | 17665.669 | 0 | 28.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 147401000000 | 128633.19 | 30-MAR-07:00 | 48247.488 | 58341.44 | 3271.727 | 0 | 18756.824 | 0 | 15.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 143134000000 | 140198.222 | 20-APR-15:00 | 48247.488 | 50956.166 | 4185.345 | 0 | 36800.784 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 162331000000 | 159225.691 | 15-MAY-15:09 | 48247.488 | 50956.166 | 6256.945 | 0 | 53756.653 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 175280000000 | 171460.668 | 19-JUN-15:00 | 48247.488 | 50956.166 | 7842.833 | 0 | 64405.741 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 176880000000 | 190616.844 | 03-JUL-15:00 | 48247.488 | 50956.166 | 9630.427 | 0 | 81774.322 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 188747000000 | 172928.13 | 14-AUG-15:00 | 48247.488 | 50956.166 | 7401.801 | 0 | 66314.235 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 164425000000 | 165333.492 | 11-SEP-12:00 | 48247.488 | 51598.363 | 6796.299 | 0 | 58682.901 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 148593000000 | 144595.027 | 12-OCT-15:00 | 48247.488 | 50956.166 | 4289.79 | 0 | 41093.143 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 134742000000 | 128822.562 | 22-NOV-13:30 | 48247.488 | 51598.363 | 3657.817 | 0 | 25310.178 | 0 | 8.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 129011000000 | 129157.289 | 26-DEC-08:00 | 48247.488 | 58341.44 | 3255.46 | 0 | 19258.003 | 0 | 54.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1820950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119220000000 | 124542.229 |  | 48247.488 | 50956.166 | 3255.46 | 0 | 14665.489 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 188747000000 | 190616.844 |  | 48247.488 | 58341.44 | 9630.427 | 0 | 81774.322 | 0 | 54.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 50367.88 | 4576.91 | 0 | 54944.79
Cost per Total Building Area ($/m2) | 10.11 | 0.92 | 0 | 11.03
Cost per Net Conditioned Building Area ($/m2) | 10.11 | 0.92 | 0 | 11.03

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1852.5 | 371.82 | 371.82
Net Site Energy | 1852.5 | 371.82 | 371.82
Total Source Energy | 5383.5 | 1080.55 | 1080.55
Net Source Energy | 5383.5 | 1080.55 | 1080.55
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 139.99 | 0 | 0 | 0 | 0
Cooling | 238.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 52.8 | 0 | 0 | 0 | 0 | 0
Pumps | 0.38 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 34.74 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1677.77 | 174.73 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 195.85 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 222373.82 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 99416.78 | 77035.89 | 22380.89 | 0.77 | 3.99
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 113395.64 | 87267.21 | 26128.43 | 0.77 | 3.96
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 113670.72 | 87145.7 | 26525.02 | 0.77 | 3.94
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38159.22 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 39591.12 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 38166.09 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7959.23 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7765.55 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 5202.03 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9598.35 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10032.96 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9323.83 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7291.18 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10896.27 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10153.3 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8922.08 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7871.32 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11540.26 | -
VAV_1_HEATC | Coil:Heating:Gas | 6781.33 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 5706.59 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 5768.11 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.62 | 10538.11 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.31 | 11834.73 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.27 | 11760.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1296.51 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 12978.3377 | 11.2018 | 103.9849 | 0 | 0.0001 | 627371.7221 | 4809.0783
February | 11399.1465 | 9.8255 | 93.7194 | 0 | 0 | 565446.1458 | 4231.1979
March | 13304.218 | 11.4516 | 112.2302 | 0 | 0.0001 | 677139.9369 | 4947.0221
April | 12027.3352 | 10.3324 | 105.0631 | 0 | 0 | 633910.4441 | 4483.2242
May | 12983.1663 | 11.1359 | 116.5699 | 0 | 0.0001 | 703349.1877 | 4849.1457
June | 13029.8905 | 11.1658 | 118.8073 | 0 | 0.0001 | 716855.6959 | 4872.1435
July | 13126.4909 | 11.2417 | 120.9169 | 0 | 0.0001 | 729588.3532 | 4912.0132
August | 14698.7881 | 12.588 | 135.4425 | 0 | 0.0001 | 817233.503 | 5500.5051
September | 13014.5223 | 11.147 | 119.669 | 0 | 0.0001 | 722058.5042 | 4869.4536
October | 12891.626 | 11.0488 | 117.2744 | 0 | 0.0001 | 707605.2191 | 4819.6129
November | 12418.0824 | 10.6676 | 108.5594 | 0 | 0.0001 | 655006.0983 | 4629.1296
December | 12644.0715 | 10.8986 | 103.9485 | 0 | 0 | 627162.1121 | 4693.277
Annual Sum or Average | 154515.6754 | 132.7049 | 1356.1854 | 0 | 0.0006 | 8182730 | 57615.8031
Minimum of Months | 11399.1465 | 9.8255 | 93.7194 | 0 | 0 | 565446.1458 | 4231.1979
Maximum of Months | 14698.7881 | 12.588 | 135.4425 | 0 | 0.0001 | 817233.503 | 5500.5051
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 128635000000 | 127727.919 | 26-JAN-13:09 | 48247.488 | 51598.363 | 3621.706 | 0 | 24251.921 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 115938000000 | 126065.934 | 13-FEB-12:30 | 48247.488 | 50788.728 | 3695.278 | 0 | 23326 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 138839000000 | 125292.167 | 03-MAR-13:00 | 48247.488 | 51598.363 | 3467.39 | 0 | 21970.485 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 129975000000 | 129439.246 | 11-APR-15:00 | 48247.488 | 50956.166 | 3497.025 | 0 | 26730.127 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 144213000000 | 141259.869 | 30-MAY-07:00 | 48247.488 | 58341.44 | 3416.671 | 0 | 31245.83 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 146982000000 | 136945.091 | 29-JUN-07:00 | 48247.488 | 58341.44 | 3336.71 | 0 | 27011.013 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 149593000000 | 144025.382 | 11-JUL-07:00 | 48247.488 | 58341.44 | 3822.672 | 0 | 33605.342 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 167564000000 | 159176.166 | 08-AUG-15:00 | 48247.488 | 50956.166 | 5073.072 | 0 | 54891.001 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 148049000000 | 154123.712 | 25-SEP-15:20 | 48247.488 | 50956.166 | 6723.797 | 0 | 48187.822 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 145086000000 | 137681.506 | 19-OCT-12:00 | 48247.488 | 51598.363 | 4152.373 | 0 | 33674.841 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 134301000000 | 130443.625 | 20-NOV-13:09 | 48247.488 | 51598.363 | 3928.975 | 0 | 26660.359 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 128592000000 | 129831.361 | 19-DEC-13:09 | 48247.488 | 51598.363 | 4015.027 | 0 | 25962.043 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1677770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 115938000000 | 125292.167 |  | 48247.488 | 50788.728 | 3336.71 | 0 | 21970.485 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 167564000000 | 159176.166 |  | 48247.488 | 58341.44 | 6723.797 | 0 | 54891.001 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 61976.3 | 1506.48 | 0 | 63482.78
Cost per Total Building Area ($/m2) | 12.44 | 0.3 | 0 | 12.74
Cost per Net Conditioned Building Area ($/m2) | 12.44 | 0.3 | 0 | 12.74

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2115.38 | 424.59 | 424.59
Net Site Energy | 2115.38 | 424.59 | 424.59
Total Source Energy | 6799.17 | 1364.7 | 1364.7
Net Source Energy | 6799.17 | 1364.7 | 1364.7
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 276.75 | 0 | 0 | 0 | 0
Cooling | 344.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 74.61 | 0 | 0 | 0 | 0 | 0
Pumps | 0.53 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 32.13 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1806.51 | 308.87 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 195.85 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 235424.12 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 100808.91 | 78078.5 | 22730.42 | 0.77 | 3.99
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 120839.94 | 96509.45 | 24330.49 | 0.8 | 4.14
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 128851.16 | 102907.65 | 25943.5 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 33789.11 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41106.71 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 42373.26 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7070.19 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7623.6 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6018.42 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10027.42 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10387.75 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10210.54 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8908.05 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12172.34 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11399.84 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10232.52 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10907.3 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13360.81 | -
VAV_1_HEATC | Coil:Heating:Gas | 14477.46 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 12156.74 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 11459.24 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.69 | 10674.54 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.3 | 13694.61 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.78 | 14602.51 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1372.6 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 31939.4065 | 49.0991 | 189.112 | 0 | 0.0004 | 943038.6888 | 13144.1749
February | 27783.5761 | 43.936 | 176.0238 | 0 | 0.0003 | 877821.7183 | 11561.2754
March | 32461.9671 | 51.5833 | 208.0047 | 0 | 0.0004 | 1037320 | 13533.9279
April | 30954.6822 | 50.418 | 209.9065 | 0 | 0.0004 | 1046850 | 13033.3469
May | 35213.414 | 57.5776 | 240.8821 | 0 | 0.0005 | 1201340 | 14849.6549
June | 41175.8723 | 67.4361 | 282.6966 | 0 | 0.0005 | 1409880 | 17375.412
July | 42363.3169 | 69.3937 | 290.97 | 0 | 0.0005 | 1451140 | 17877.8278
August | 44515.7883 | 72.9169 | 305.729 | 0 | 0.0006 | 1524750 | 18785.9186
September | 36849.4006 | 60.3384 | 252.8804 | 0 | 0.0005 | 1261180 | 15548.4831
October | 32978.6479 | 53.7713 | 224.1647 | 0 | 0.0004 | 1117960 | 13891.4292
November | 30018.9024 | 47.8614 | 193.8567 | 0 | 0.0004 | 966768.5631 | 12532.0308
December | 30701.7737 | 47.6667 | 186.2031 | 0 | 0.0004 | 928551.9947 | 12683.712
Annual Sum or Average | 416956.7479 | 671.9985 | 2760.4297 | 0 | 0.0052 | 13766600 | 174817.1934
Minimum of Months | 27783.5761 | 43.936 | 176.0238 | 0 | 0.0003 | 877821.7183 | 11561.2754
Maximum of Months | 44515.7883 | 72.9169 | 305.729 | 0 | 0.0006 | 1524750 | 18785.9186
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 123749000000 | 118397.847 | 18-JAN-13:00 | 48247.488 | 51598.363 | 3743.719 | 0 | 14798.008 | 0 | 10.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 115191000000 | 121177.343 | 08-FEB-13:00 | 48247.488 | 51598.363 | 3939.973 | 0 | 17383.078 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 136121000000 | 124823.788 | 31-MAR-12:00 | 48247.488 | 51598.363 | 3794.4 | 0 | 21175.096 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 137372000000 | 144726.212 | 21-APR-15:30 | 48247.488 | 50956.166 | 5485.022 | 0 | 40029.096 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 157645000000 | 163741.203 | 31-MAY-15:00 | 48247.488 | 50956.166 | 7986.977 | 0 | 56542.132 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 185010000000 | 209142.605 | 27-JUN-15:00 | 48247.488 | 50956.166 | 21490.496 | 0 | 88440.015 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 190425000000 | 205450.002 | 24-JUL-15:00 | 48247.488 | 50956.166 | 21233.505 | 0 | 85004.403 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 200084000000 | 197865.034 | 04-AUG-15:50 | 48247.488 | 50956.166 | 17318.61 | 0 | 81334.33 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 165497000000 | 179229.092 | 01-SEP-15:09 | 48247.488 | 50956.166 | 9993.208 | 0 | 70023.79 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 146703000000 | 149635.065 | 03-OCT-15:09 | 48247.488 | 50956.166 | 6609.727 | 0 | 43813.244 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 126863000000 | 123673.96 | 10-NOV-13:09 | 48247.488 | 51598.363 | 4290.09 | 0 | 19529.578 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 121848000000 | 122717.858 | 05-DEC-13:00 | 48247.488 | 51598.363 | 3889.74 | 0 | 18973.069 | 0 | 9.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1806510000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 115191000000 | 118397.847 |  | 48247.488 | 50956.166 | 3743.719 | 0 | 14798.008 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 200084000000 | 209142.605 |  | 48247.488 | 51598.363 | 21490.496 | 0 | 88440.015 | 0 | 10.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51180.47 | 2371.33 | 0 | 53551.8
Cost per Total Building Area ($/m2) | 10.27 | 0.48 | 0 | 10.75
Cost per Net Conditioned Building Area ($/m2) | 10.27 | 0.48 | 0 | 10.75

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2152.71 | 432.08 | 432.08
Net Site Energy | 2152.71 | 432.08 | 432.08
Total Source Energy | 5513.81 | 1106.71 | 1106.71
Net Source Energy | 5513.81 | 1106.71 | 1106.71
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 535.55 | 0 | 0 | 0 | 0
Cooling | 128.51 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 63.33 | 0 | 0 | 0 | 0 | 0
Pumps | 0.75 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 37.99 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1579.16 | 573.54 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 195.85 | 5.83 | 0.39 | 0.223
Non-North Total or Average |  |  | 456.98 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 266507.34 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 102260.98 | 81671.27 | 20589.71 | 0.8 | 4.14
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 132002.9 | 105424.81 | 26578.09 | 0.8 | 4.14
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 125549.35 | 100270.65 | 25278.7 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 31393.81 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 43830.7 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 39621.09 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16736.19 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9535.07 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 4633.46 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13477.32 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19831.86 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11626.73 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7316.23 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15209.22 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19481.64 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10914.12 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7622.87 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15392.91 | -
VAV_1_HEATC | Coil:Heating:Gas | 9605.35 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 6802.88 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 7411.24 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.18 | 11589.09 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.97 | 14959.7 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.58 | 14228.32 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1553.83 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15730.0735 | 13.726 | 99.3643 | 0 | 0.0001 | 599391.0681 | 5747.3615
February | 12761.4816 | 11.0678 | 92.7402 | 0 | 0 | 559492.0099 | 4699.7168
March | 15000.6013 | 13.0233 | 106.5973 | 0 | 0.0001 | 643080.4762 | 5516.9575
April | 13247.952 | 11.4679 | 100.1763 | 0 | 0.0001 | 604370.2553 | 4890.7724
May | 13809.6027 | 11.9167 | 111.1075 | 0 | 0.0001 | 670346.4167 | 5118.5114
June | 13460.0999 | 11.5971 | 111.5173 | 0 | 0.0001 | 672831.376 | 4998.7982
July | 12978.4803 | 11.1641 | 110.7642 | 0 | 0.0001 | 668299.5102 | 4829.811
August | 14272.0389 | 12.281 | 121.0499 | 0 | 0.0001 | 730356.0027 | 5308.8952
September | 13144.5882 | 11.3029 | 112.9147 | 0 | 0.0001 | 681277.4974 | 4893.8624
October | 13539.6747 | 11.67 | 111.408 | 0 | 0.0001 | 672168.8028 | 5026.0056
November | 13725.5155 | 11.8905 | 102.1468 | 0 | 0.0001 | 616251.6572 | 5062.0699
December | 15077.4698 | 13.1478 | 96.8032 | 0 | 0.0001 | 583949.222 | 5513.6803
Annual Sum or Average | 166747.5785 | 144.255 | 1276.5898 | 0 | 0.0006 | 7701810 | 61606.4423
Minimum of Months | 12761.4816 | 11.0678 | 92.7402 | 0 | 0 | 559492.0099 | 4699.7168
Maximum of Months | 15730.0735 | 13.726 | 121.0499 | 0 | 0.0001 | 730356.0027 | 5747.3615
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 122898000000 | 112670.41 | 06-JAN-13:00 | 48247.488 | 51598.363 | 3727.6 | 0 | 9084.395 | 0 | 12.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 114717000000 | 128003.904 | 15-FEB-16:10 | 48247.488 | 50956.166 | 4157.429 | 0 | 24634.381 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 131856000000 | 122300.648 | 01-MAR-13:09 | 48247.488 | 51598.363 | 4257.908 | 0 | 18185.343 | 0 | 11.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 123919000000 | 124441.224 | 28-APR-12:09 | 48247.488 | 51598.363 | 3644.877 | 0 | 20941.302 | 0 | 9.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 137446000000 | 129630.079 | 26-MAY-12:00 | 48247.488 | 51598.363 | 3694.297 | 0 | 26081.49 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 137956000000 | 133718.34 | 16-JUN-15:00 | 48247.488 | 50956.166 | 4643.875 | 0 | 29862.371 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 137027000000 | 144173.174 | 03-JUL-12:00 | 48247.488 | 51598.363 | 4795.73 | 0 | 39523.152 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 149750000000 | 138843.646 | 15-AUG-12:09 | 48247.488 | 51598.363 | 4258.094 | 0 | 34731.26 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 139687000000 | 156344.587 | 28-SEP-15:09 | 48247.488 | 50956.166 | 7204.099 | 0 | 49928.394 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 137820000000 | 139305.201 | 31-OCT-12:50 | 48247.488 | 51598.363 | 5043.811 | 0 | 34407.099 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 126355000000 | 120670.615 | 14-NOV-13:09 | 48247.488 | 51598.363 | 4490.363 | 0 | 16325.283 | 0 | 9.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 119732000000 | 111974.245 | 01-DEC-13:00 | 48247.488 | 51598.363 | 3588.927 | 0 | 8522.02 | 0 | 17.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1579160000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 114717000000 | 111974.245 |  | 48247.488 | 50956.166 | 3588.927 | 0 | 8522.02 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 149750000000 | 156344.587 |  | 48247.488 | 51598.363 | 7204.099 | 0 | 49928.394 | 0 | 17.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 66576.8 | 4893.49 | 0 | 71470.29
Cost per Total Building Area ($/m2) | 13.36 | 0.98 | 0 | 14.35
Cost per Net Conditioned Building Area ($/m2) | 13.36 | 0.98 | 0 | 14.35

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2555.38 | 512.9 | 512.9
Net Site Energy | 2555.38 | 512.9 | 512.9
Total Source Energy | 7213.75 | 1447.91 | 1447.91
Net Source Energy | 7213.75 | 1447.91 | 1447.91
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 736.21 | 0 | 0 | 0 | 0
Cooling | 326.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 66.73 | 0 | 0 | 0 | 0 | 0
Pumps | 1.01 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.46 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1780.71 | 774.67 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 256672.34 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 125304.73 | 92405.53 | 32899.2 | 0.74 | 3.78
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 135458 | 102046.59 | 33411.4 | 0.75 | 3.87
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 141176.73 | 106825.55 | 34351.18 | 0.76 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38882.85 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41161.82 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 42205.1 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7930.56 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10450.02 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6815.47 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12930.75 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10468.52 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12419.38 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8940.96 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14577.94 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11573.21 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12274.83 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10520.8 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15635.8 | -
VAV_1_HEATC | Coil:Heating:Gas | 24629.28 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 23287.19 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 22696.98 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.31 | 11836.43 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.17 | 13459.35 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.55 | 14172.69 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1496.49 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 31740.6884 | 52.2719 | 129.6745 | 0 | 0.0005 | 8061.8595 | 13130.7089
February | 26551.6234 | 45.3257 | 117.3056 | 0 | 0.0005 | 7293.5767 | 11130.2962
March | 28218.5258 | 51.344 | 142.1888 | 0 | 0.0006 | 8841.9807 | 12119.1637
April | 25300.8773 | 47.6804 | 136.5705 | 0 | 0.0006 | 8493.1873 | 11016.5249
May | 27050.2268 | 52.9643 | 156.9859 | 0 | 0.0006 | 9763.4489 | 11959.9342
June | 29640.7803 | 59.0193 | 177.446 | 0 | 0.0007 | 11036.2267 | 13195.1682
July | 30119.9029 | 60.046 | 180.7159 | 0 | 0.0007 | 11239.6195 | 13415.1097
August | 32599.519 | 64.9726 | 195.5012 | 0 | 0.0008 | 12159.1864 | 14517.9813
September | 26655.4904 | 52.7624 | 157.8476 | 0 | 0.0006 | 9817.2196 | 11837.6138
October | 26531.1212 | 51.0732 | 149.1433 | 0 | 0.0006 | 9275.4266 | 11650.4337
November | 26393.0893 | 48.627 | 136.328 | 0 | 0.0006 | 8477.739 | 11390.4488
December | 28895.2179 | 49.0506 | 126.1368 | 0 | 0.0005 | 7842.5559 | 12087.5006
Annual Sum or Average | 339697.0629 | 635.1373 | 1805.8439 | 0 | 0.0074 | 112302.0267 | 147450.884
Minimum of Months | 25300.8773 | 45.3257 | 117.3056 | 0 | 0.0005 | 7293.5767 | 11016.5249
Maximum of Months | 32599.519 | 64.9726 | 195.5012 | 0 | 0.0008 | 12159.1864 | 14517.9813
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 127832000000 | 124492.774 | 09-JAN-08:00 | 48247.488 | 58341.44 | 3397.88 | 0 | 14452.396 | 0 | 53.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 115650000000 | 118233.194 | 15-FEB-13:00 | 48247.488 | 51598.363 | 3397.88 | 0 | 14966.856 | 0 | 22.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 140202000000 | 132372.51 | 09-MAR-13:00 | 48247.488 | 51598.363 | 3474.071 | 0 | 29041.494 | 0 | 11.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 134671000000 | 132164.726 | 04-APR-07:00 | 48247.488 | 58341.44 | 3397.88 | 0 | 22157.993 | 0 | 19.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 154813000000 | 148304.382 | 31-MAY-15:00 | 48247.488 | 50956.166 | 3819.345 | 0 | 45272.943 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 174995000000 | 180388.205 | 30-JUN-15:00 | 48247.488 | 50956.166 | 6795.541 | 0 | 74380.57 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 178220000000 | 187233.504 | 25-JUL-15:30 | 48247.488 | 50956.166 | 7814.029 | 0 | 80207.382 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 192801000000 | 186767.182 | 17-AUG-15:00 | 48247.488 | 50956.166 | 7274.578 | 0 | 80280.51 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 155666000000 | 157513.311 | 08-SEP-15:00 | 48247.488 | 50956.166 | 5789.767 | 0 | 52511.45 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 147075000000 | 143436.718 | 12-OCT-12:00 | 48247.488 | 51598.363 | 4708.838 | 0 | 38873.588 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 134426000000 | 134673.626 | 03-NOV-12:00 | 48247.488 | 51598.363 | 3895.177 | 0 | 30923.256 | 0 | 9.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 124355000000 | 116132.885 | 08-DEC-08:00 | 48247.488 | 58341.44 | 3397.88 | 0 | 6101.763 | 0 | 44.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1780710000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 115650000000 | 116132.885 |  | 48247.488 | 50956.166 | 3397.88 | 0 | 6101.763 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 192801000000 | 187233.504 |  | 48247.488 | 58341.44 | 7814.029 | 0 | 80280.51 | 0 | 53.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 39381.91 | 7509.79 | 0 | 46891.7
Cost per Total Building Area ($/m2) | 7.9 | 1.51 | 0 | 9.41
Cost per Net Conditioned Building Area ($/m2) | 7.9 | 1.51 | 0 | 9.41

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2169.96 | 435.54 | 435.54
Net Site Energy | 2169.96 | 435.54 | 435.54
Total Source Energy | 6107.03 | 1225.77 | 1225.77
Net Source Energy | 6107.03 | 1225.77 | 1225.77
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 453.08 | 0 | 0 | 0 | 0
Cooling | 216.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 75.48 | 0 | 0 | 0 | 0 | 0
Pumps | 0.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 37.89 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1678.99 | 490.97 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 225119.56 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 109879.73 | 87756.02 | 22123.71 | 0.8 | 4.14
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129691.98 | 103579.18 | 26112.8 | 0.8 | 4.14
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129785.87 | 103654.17 | 26131.7 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 34787.48 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 38081.77 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 36158.17 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6282.89 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8769.31 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 5408.93 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11796.93 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8790.21 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10809.88 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7889.72 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13562.85 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9543.09 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10195.46 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8913.64 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14381.37 | -
VAV_1_HEATC | Coil:Heating:Gas | 18167.18 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 16631.45 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 16623.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.64 | 12452.51 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.83 | 14697.8 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.84 | 14708.44 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1312.52 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 38479.2952 | 62.5989 | 149.9332 | 0 | 0.0006 | 155876.3976 | 16031.966
February | 33367.3142 | 55.3364 | 135.718 | 0 | 0.0005 | 141105.5726 | 14005.479
March | 38283.9775 | 64.3987 | 160.6338 | 0 | 0.0006 | 167016.8535 | 16158.3046
April | 34558.7287 | 59.4006 | 151.8675 | 0 | 0.0006 | 157911.013 | 14710.4099
May | 39890.3713 | 69.6363 | 181.097 | 0 | 0.0007 | 188310.7409 | 17085.0053
June | 43376.5725 | 75.9416 | 198.1115 | 0 | 0.0008 | 206004.3925 | 18599.6645
July | 45084.6031 | 78.9736 | 206.1379 | 0 | 0.0008 | 214350.857 | 19336.1451
August | 47264.507 | 82.777 | 216.0236 | 0 | 0.0008 | 224630.2635 | 20269.5993
September | 39643.1103 | 69.346 | 180.7393 | 0 | 0.0007 | 187939.7131 | 16992.9649
October | 36482.5176 | 62.9161 | 161.4516 | 0 | 0.0006 | 167877.8574 | 15549.777
November | 35661.6513 | 59.8355 | 148.8074 | 0 | 0.0006 | 154719.4904 | 15036.5902
December | 37412.1857 | 60.9463 | 146.227 | 0 | 0.0006 | 152023.888 | 15595.5535
Annual Sum or Average | 469504.8346 | 802.1069 | 2036.7479 | 0 | 0.008 | 2117770 | 199371.4593
Minimum of Months | 33367.3142 | 55.3364 | 135.718 | 0 | 0.0005 | 141105.5726 | 14005.479
Maximum of Months | 47264.507 | 82.777 | 216.0236 | 0 | 0.0008 | 224630.2635 | 20269.5993
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 123581000000 | 112250.912 | 26-JAN-16:10 | 48247.488 | 50956.166 | 4259.018 | 0 | 8778.54 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 111870000000 | 120701.588 | 14-FEB-16:10 | 48247.488 | 50956.166 | 4403.305 | 0 | 17086.189 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 132413000000 | 122862.933 | 02-MAR-13:00 | 48247.488 | 51598.363 | 4755.884 | 0 | 18252.758 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 125194000000 | 134734.732 | 21-APR-15:00 | 48247.488 | 50956.166 | 5735.221 | 0 | 29787.417 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 149295000000 | 149900.239 | 31-MAY-15:00 | 48247.488 | 50956.166 | 8191.517 | 0 | 42496.628 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 163323000000 | 165172.604 | 29-JUN-15:30 | 48247.488 | 50956.166 | 10923.661 | 0 | 55036.849 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 169940000000 | 174831.791 | 03-JUL-15:30 | 48247.488 | 50956.166 | 13074.382 | 0 | 62545.314 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 178090000000 | 171384.076 | 01-AUG-15:20 | 48247.488 | 50956.166 | 10884.887 | 0 | 61287.094 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 149001000000 | 152963.671 | 05-SEP-12:00 | 48247.488 | 51598.363 | 6971.633 | 0 | 46137.746 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 133096000000 | 136739.499 | 11-OCT-15:00 | 48247.488 | 50956.166 | 5356.647 | 0 | 32170.758 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 122663000000 | 119226.287 | 08-NOV-13:00 | 48247.488 | 51598.363 | 4830.717 | 0 | 14541.278 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 120526000000 | 111675.386 | 05-DEC-13:00 | 48247.488 | 51598.363 | 4616.952 | 0 | 7198.019 | 0 | 14.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1678990000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 111870000000 | 111675.386 |  | 48247.488 | 50956.166 | 4259.018 | 0 | 7198.019 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 178090000000 | 174831.791 |  | 48247.488 | 51598.363 | 13074.382 | 0 | 62545.314 | 0 | 14.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17415.2 | 3385.85 | 0 | 20801.05
Cost per Total Building Area ($/m2) | 3.5 | 0.68 | 0 | 4.18
Cost per Net Conditioned Building Area ($/m2) | 3.5 | 0.68 | 0 | 4.18

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2374.61 | 476.62 | 476.62
Net Site Energy | 2374.61 | 476.62 | 476.62
Total Source Energy | 3601.96 | 722.97 | 722.97
Net Source Energy | 3601.96 | 722.97 | 722.97
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 782.47 | 0 | 0 | 0 | 0
Cooling | 101.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 63.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.02 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1552.13 | 822.49 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 261860.9 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 99280.82 | 79291.15 | 19989.67 | 0.8 | 4.14
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129748.85 | 103624.6 | 26124.25 | 0.8 | 4.14
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129455.85 | 103390.59 | 26065.25 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 34137.88 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 45744.46 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 44565.35 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12580.06 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8999.73 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 5141.88 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11696.31 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15916.77 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11315.24 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8132.33 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13713.53 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16026.37 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10846.64 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8762.42 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14407.43 | -
VAV_1_HEATC | Coil:Heating:Gas | 17959.85 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 15129.17 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 15156.51 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6 | 11251.35 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.84 | 14704.25 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.82 | 14671.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1526.74 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13353.8201 | 16.2486 | 26.4064 | 0 | 0.0001 | 348544.2463 | 5063.7848
February | 10387.5619 | 13.163 | 23.8845 | 0 | 0.0001 | 315373.2109 | 3995.0655
March | 11364.5409 | 14.6936 | 27.9992 | 0 | 0.0001 | 369759.5436 | 4402.152
April | 9308.3632 | 12.4602 | 25.6473 | 0 | 0.0001 | 338774.7466 | 3651.1986
May | 8280.3019 | 12.0074 | 28.7104 | 0 | 0.0001 | 379381.2151 | 3346.8392
June | 7770.9774 | 11.7001 | 29.6983 | 0 | 0.0001 | 392488.4145 | 3187.1671
July | 7388.3772 | 11.4753 | 30.4785 | 0 | 0.0001 | 402839.6673 | 3067.8632
August | 7982.2727 | 12.4444 | 33.2264 | 0 | 0.0001 | 439164.0624 | 3319.4636
September | 7961.9487 | 11.6999 | 28.5909 | 0 | 0.0001 | 377820.32 | 3234.6731
October | 9329.5615 | 12.7017 | 27.0667 | 0 | 0.0001 | 357557.3358 | 3682.3434
November | 11257.8544 | 14.2815 | 25.9859 | 0 | 0.0001 | 343123.3861 | 4331.4634
December | 13061.0674 | 15.8829 | 25.7672 | 0 | 0.0001 | 340105.502 | 4951.7615
Annual Sum or Average | 117446.6471 | 158.7587 | 333.4617 | 0 | 0.0014 | 4404930 | 46233.7755
Minimum of Months | 7388.3772 | 11.4753 | 23.8845 | 0 | 0.0001 | 315373.2109 | 3067.8632
Maximum of Months | 13353.8201 | 16.2486 | 33.2264 | 0 | 0.0001 | 439164.0624 | 5063.7848
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 122813000000 | 110376.954 | 02-JAN-08:09 | 48247.488 | 58341.44 | 3497.589 | 0 | 0 | 0 | 290.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 111125000000 | 115246.493 | 21-FEB-13:00 | 48247.488 | 51598.363 | 3497.589 | 0 | 11878.367 | 0 | 24.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 130289000000 | 119746.432 | 29-MAR-12:00 | 48247.488 | 51598.363 | 3924.029 | 0 | 15966.524 | 0 | 10.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 119371000000 | 115996.429 | 18-APR-15:00 | 48247.488 | 50956.166 | 3687.572 | 0 | 13096.764 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 133679000000 | 131204.302 | 05-MAY-15:00 | 48247.488 | 50956.166 | 3662.533 | 0 | 28329.676 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 138298000000 | 133579.261 | 28-JUN-15:30 | 48247.488 | 50956.166 | 4239.831 | 0 | 30127.337 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 141945000000 | 145097.279 | 24-JUL-15:20 | 48247.488 | 50956.166 | 4980.157 | 0 | 40905.029 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 154744000000 | 142635.561 | 07-AUG-15:39 | 48247.488 | 50956.166 | 5213.396 | 0 | 38210.071 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 133129000000 | 140204.933 | 01-SEP-15:00 | 48247.488 | 50956.166 | 4324.964 | 0 | 36667.876 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 125989000000 | 125423.347 | 17-OCT-12:00 | 48247.488 | 51598.363 | 4153.775 | 0 | 21413.446 | 0 | 10.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 120903000000 | 115832.367 | 03-NOV-12:00 | 48247.488 | 51598.363 | 3497.589 | 0 | 12469.545 | 0 | 19.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 119840000000 | 110335.133 | 11-DEC-08:09 | 48247.488 | 58341.44 | 3497.589 | 0 | 0 | 0 | 248.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1552130000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 111125000000 | 110335.133 |  | 48247.488 | 50956.166 | 3497.589 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 154744000000 | 145097.279 |  | 48247.488 | 58341.44 | 5213.396 | 0 | 40905.029 | 0 | 290.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33749.04 | 6912.86 | 0 | 40661.89
Cost per Total Building Area ($/m2) | 6.77 | 1.39 | 0 | 8.16
Cost per Net Conditioned Building Area ($/m2) | 6.77 | 1.39 | 0 | 8.16

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2694.13 | 540.75 | 540.75
Net Site Energy | 2694.13 | 540.75 | 540.75
Total Source Energy | 7034.16 | 1411.86 | 1411.86
Net Source Energy | 7034.16 | 1411.86 | 1411.86
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 985.5 | 0 | 0 | 0 | 0
Cooling | 212.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 66.92 | 0 | 0 | 0 | 0 | 0
Pumps | 1.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.08 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1667.55 | 1026.57 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 251475.16 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122333.89 | 90414.44 | 31919.45 | 0.74 | 3.79
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 133512.44 | 101784.94 | 31727.5 | 0.76 | 3.92
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 138106.47 | 105194.25 | 32912.23 | 0.76 | 3.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 38196.15 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41867.96 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 42195.13 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7732.02 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9742.83 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6458.37 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12185.09 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10464.89 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11883.4 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9106.43 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13912.11 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11129.36 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11765.09 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10102.87 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14860.59 | -
VAV_1_HEATC | Coil:Heating:Gas | 34545.33 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 32903.43 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 32544.55 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.19 | 11617.37 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.27 | 13637.17 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.5 | 14077.74 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1466.18 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 55302.0129 | 88.8562 | 231.9758 | 0 | 0.0007 | 53388.0938 | 22836.259
February | 47277.1478 | 77.7059 | 208.7663 | 0 | 0.0006 | 48049.4879 | 19689.2006
March | 51302.4326 | 87.126 | 243.3505 | 0 | 0.0007 | 56013.8832 | 21633.6794
April | 44595.5178 | 78.244 | 226.5729 | 0 | 0.0007 | 52155.8042 | 19045.2617
May | 50179.2978 | 90.2072 | 267.9287 | 0 | 0.0008 | 61678.7139 | 21637.0357
June | 57058.704 | 103.6778 | 311.276 | 0 | 0.0009 | 71658.9794 | 24708.9045
July | 58584.1307 | 106.509 | 319.9539 | 0 | 0.001 | 73656.7913 | 25375.1602
August | 61363.1708 | 111.5371 | 334.9857 | 0 | 0.001 | 77117.2364 | 26576.5499
September | 50946.0189 | 92.1954 | 275.6787 | 0 | 0.0008 | 63463.6057 | 22025.953
October | 47704.8931 | 84.6288 | 247.9416 | 0 | 0.0008 | 57076.0666 | 20462.0278
November | 47045.2273 | 80.6164 | 227.4752 | 0 | 0.0007 | 52360.8181 | 19907.3388
December | 51928.9432 | 84.805 | 226.0304 | 0 | 0.0007 | 52022.1173 | 21574.2345
Annual Sum or Average | 623287.4969 | 1086.1088 | 3121.9356 | 0 | 0.0095 | 718641.5979 | 265471.605
Minimum of Months | 44595.5178 | 77.7059 | 208.7663 | 0 | 0.0006 | 48049.4879 | 19045.2617
Maximum of Months | 61363.1708 | 111.5371 | 334.9857 | 0 | 0.001 | 77117.2364 | 26576.5499
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 123883000000 | 110483.701 | 30-JAN-08:09 | 48247.488 | 58341.44 | 3386.156 | 0 | 0 | 0 | 508.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 111495000000 | 110315.429 | 06-FEB-08:09 | 48247.488 | 58341.44 | 3386.156 | 0 | 0 | 0 | 340.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 129976000000 | 123328.191 | 31-MAR-15:09 | 48247.488 | 50956.166 | 3386.156 | 0 | 20729.79 | 0 | 8.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 121024000000 | 128938.089 | 10-APR-07:00 | 48247.488 | 58341.44 | 3386.156 | 0 | 18932.418 | 0 | 30.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 143121000000 | 148115.512 | 30-MAY-15:00 | 48247.488 | 50956.166 | 4109.307 | 0 | 44794.111 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 166279000000 | 170854.307 | 08-JUN-12:00 | 48247.488 | 51598.363 | 5291.44 | 0 | 65708.576 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 170915000000 | 178176.313 | 03-JUL-15:30 | 48247.488 | 50956.166 | 7973.628 | 0 | 70990.591 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 178945000000 | 176469.443 | 04-AUG-15:50 | 48247.488 | 50956.166 | 6495.438 | 0 | 70761.911 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 147263000000 | 151631.759 | 06-SEP-12:30 | 48247.488 | 51598.363 | 5069.179 | 0 | 46708.289 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 132441000000 | 140397.056 | 30-OCT-12:09 | 48247.488 | 51598.363 | 4060.218 | 0 | 36480.917 | 0 | 10.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 121499000000 | 136105.16 | 02-NOV-07:00 | 48247.488 | 58341.44 | 3386.156 | 0 | 26111.166 | 0 | 18.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 120713000000 | 110416.945 | 26-DEC-08:09 | 48247.488 | 58341.44 | 3386.156 | 0 | 0 | 0 | 441.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1667550000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 111495000000 | 110315.429 |  | 48247.488 | 50956.166 | 3386.156 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 178945000000 | 178176.313 |  | 48247.488 | 58341.44 | 7973.628 | 0 | 70990.591 | 0 | 508.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40206.02 | 8555.43 | 0 | 48761.45
Cost per Total Building Area ($/m2) | 8.07 | 1.72 | 0 | 9.79
Cost per Net Conditioned Building Area ($/m2) | 8.07 | 1.72 | 0 | 9.79

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2318.77 | 465.41 | 465.41
Net Site Energy | 2318.77 | 465.41 | 465.41
Total Source Energy | 6102.76 | 1224.92 | 1224.92
Net Source Energy | 6102.76 | 1224.92 | 1224.92
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 673.76 | 0 | 0 | 0 | 0
Cooling | 146.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 69.52 | 0 | 0 | 0 | 0 | 0
Pumps | 1.06 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.94 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1604.07 | 714.7 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 215626.41 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 105715.9 | 84430.56 | 21285.34 | 0.8 | 4.14
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 126719.01 | 101204.8 | 25514.21 | 0.8 | 4.14
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 122000.83 | 97436.61 | 24564.23 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 34459.11 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 38516.98 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 34579.2 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5850.25 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8053.62 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 5000.75 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11022.64 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8384.52 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10075.82 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7434.9 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12766.12 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8914.57 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9316.83 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8121.88 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13372.26 | -
VAV_1_HEATC | Coil:Heating:Gas | 26980.62 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 25355.89 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 25720.24 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.39 | 11980.63 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.66 | 14360.88 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.37 | 13826.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1257.17 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 41054.473 | 65.0524 | 150.5723 | 0 | 0.0006 | 156527.8941 | 16934.6216
February | 35160.5886 | 56.8532 | 135.1252 | 0 | 0.0005 | 140478.7992 | 14615.251
March | 39030.2698 | 64.7594 | 158.9224 | 0 | 0.0006 | 165231.2872 | 16385.5248
April | 34513.1841 | 58.7256 | 148.4375 | 0 | 0.0006 | 154340.5997 | 14632.4897
May | 37283.0723 | 64.3599 | 165.3367 | 0 | 0.0006 | 171918.03 | 15897.1972
June | 39302.0497 | 68.5564 | 178.1396 | 0 | 0.0007 | 185235.1588 | 16827.8349
July | 42068.6294 | 73.6508 | 192.1331 | 0 | 0.0007 | 199787.8004 | 18038.7396
August | 44026.6423 | 77.0584 | 200.9653 | 0 | 0.0008 | 208971.7003 | 18876.3221
September | 36597.6809 | 63.6867 | 165.0575 | 0 | 0.0006 | 171630.9934 | 15654.9744
October | 36306.5548 | 62.1335 | 158.0797 | 0 | 0.0006 | 164368.6072 | 15427.7815
November | 36366.5874 | 60.1266 | 146.9229 | 0 | 0.0006 | 152753.8745 | 15246.3619
December | 39642.2336 | 62.9707 | 146.2371 | 0 | 0.0006 | 152022.4417 | 16367.3867
Annual Sum or Average | 461351.9659 | 777.9335 | 1945.9292 | 0 | 0.0077 | 2023270 | 194904.4855
Minimum of Months | 34513.1841 | 56.8532 | 135.1252 | 0 | 0.0005 | 140478.7992 | 14615.251
Maximum of Months | 44026.6423 | 77.0584 | 200.9653 | 0 | 0.0008 | 208971.7003 | 18876.3221
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 124097000000 | 114837.098 | 24-JAN-13:00 | 48247.488 | 51598.363 | 3668.145 | 0 | 11312.019 | 0 | 11.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 111373000000 | 110578.35 | 07-FEB-13:00 | 48247.488 | 51598.363 | 4265.487 | 0 | 6451.17 | 0 | 15.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 130997000000 | 121028.168 | 30-MAR-12:00 | 48247.488 | 51598.363 | 4144.687 | 0 | 17029.066 | 0 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 122363000000 | 126414.538 | 26-APR-15:00 | 48247.488 | 50956.166 | 4747.725 | 0 | 22454.719 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 136299000000 | 139608.788 | 24-MAY-15:00 | 48247.488 | 50956.166 | 6124.405 | 0 | 34272.289 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 146857000000 | 151281.45 | 27-JUN-15:00 | 48247.488 | 50956.166 | 8032.744 | 0 | 44036.612 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 158394000000 | 164396.695 | 17-JUL-15:30 | 48247.488 | 50956.166 | 11109.434 | 0 | 54075.167 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 165675000000 | 157857.771 | 30-AUG-15:30 | 48247.488 | 50956.166 | 9656.117 | 0 | 48989.56 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 136071000000 | 143861.707 | 01-SEP-15:00 | 48247.488 | 50956.166 | 6973.837 | 0 | 37675.776 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 130313000000 | 133588.905 | 05-OCT-15:20 | 48247.488 | 50956.166 | 5396.702 | 0 | 28980.109 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 121105000000 | 122180.269 | 10-NOV-13:00 | 48247.488 | 51598.363 | 4374.067 | 0 | 17951.725 | 0 | 8.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 120525000000 | 110645.58 | 11-DEC-08:09 | 48247.488 | 58341.44 | 3458.077 | 0 | 0 | 0 | 598.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1604070000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 111373000000 | 110578.35 |  | 48247.488 | 50956.166 | 3458.077 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 165675000000 | 164396.695 |  | 48247.488 | 58341.44 | 11109.434 | 0 | 54075.167 | 0 | 598.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16646.69 | 4937.85 | 0 | 21584.53
Cost per Total Building Area ($/m2) | 3.34 | 0.99 | 0 | 4.33
Cost per Net Conditioned Building Area ($/m2) | 3.34 | 0.99 | 0 | 4.33

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3052.57 | 612.7 | 612.7
Net Site Energy | 3052.57 | 612.7 | 612.7
Total Source Energy | 7190.91 | 1443.32 | 1443.32
Net Source Energy | 7190.91 | 1443.32 | 1443.32
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1364.24 | 0 | 0 | 0 | 0
Cooling | 186.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 70.5 | 0 | 0 | 0 | 0 | 0
Pumps | 1.76 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.34 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1644.99 | 1407.58 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 252078.66 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 120445.6 | 90017.12 | 30428.48 | 0.75 | 3.84
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 133101.53 | 102186.18 | 30915.35 | 0.77 | 3.95
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 136860.59 | 104963.14 | 31897.45 | 0.77 | 3.95
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 37877.66 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 41791.4 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 42036.23 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8593.08 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9756.7 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 6306.84 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12023.67 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11394.97 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11834.38 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8928.09 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13746.7 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11853.07 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11662.14 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9819.61 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14587.93 | -
VAV_1_HEATC | Coil:Heating:Gas | 39842.18 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 38172.83 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 37884.2 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.26 | 11745.76 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.36 | 13815.44 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.55 | 14172.02 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1469.7 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 46666.472 | 67.46 | 81.9469 | 0 | 0.0006 | 53802.1236 | 18550.6318
February | 37755.7337 | 56.8632 | 73.7375 | 0 | 0.0006 | 48426.6466 | 15226.8261
March | 36678.0368 | 59.4346 | 85.291 | 0 | 0.0006 | 56038.0013 | 15193.1386
April | 29866.7418 | 51.44 | 79.3595 | 0 | 0.0006 | 52155.336 | 12662.5377
May | 32889.3177 | 58.8994 | 94.7289 | 0 | 0.0007 | 62265.4806 | 14159.4245
June | 35795.8702 | 65.0578 | 106.2043 | 0 | 0.0008 | 69811.9275 | 15501.8613
July | 36522.6609 | 66.4725 | 108.6658 | 0 | 0.0008 | 71430.3026 | 15825.565
August | 39324.5268 | 71.54 | 116.8982 | 0 | 0.0009 | 76841.6473 | 17036.5829
September | 31092.4351 | 55.9131 | 90.3074 | 0 | 0.0007 | 59360.1248 | 13407.9684
October | 31020.1875 | 53.4153 | 82.3874 | 0 | 0.0006 | 54145.197 | 13150.4753
November | 34475.0648 | 55.6406 | 79.4382 | 0 | 0.0006 | 52191.4895 | 14259.1701
December | 41829.6719 | 62.4378 | 79.8672 | 0 | 0.0006 | 52449.1048 | 16816.2122
Annual Sum or Average | 433916.7192 | 724.5744 | 1078.8323 | 0 | 0.008 | 708917.3815 | 181790.3941
Minimum of Months | 29866.7418 | 51.44 | 73.7375 | 0 | 0.0006 | 48426.6466 | 12662.5377
Maximum of Months | 46666.472 | 71.54 | 116.8982 | 0 | 0.0009 | 76841.6473 | 18550.6318
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 124844000000 | 110987.167 | 02-JAN-08:09 | 48247.488 | 58341.44 | 3420.674 | 0 | 0 | 0 | 977.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 112370000000 | 110473.925 | 06-FEB-08:09 | 48247.488 | 58341.44 | 3420.674 | 0 | 0 | 0 | 464.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 130032000000 | 115690.78 | 23-MAR-15:00 | 48247.488 | 50956.166 | 3420.674 | 0 | 13056.423 | 0 | 10.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 121023000000 | 122687.005 | 14-APR-15:00 | 48247.488 | 50956.166 | 3427.662 | 0 | 20047.25 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 144482000000 | 147408.72 | 31-MAY-12:09 | 48247.488 | 51598.363 | 4480.289 | 0 | 43074.139 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 161993000000 | 169909.932 | 29-JUN-15:00 | 48247.488 | 50956.166 | 6498.172 | 0 | 64199.666 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 165749000000 | 169253.42 | 13-JUL-15:00 | 48247.488 | 50956.166 | 5742.935 | 0 | 64298.391 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 178305000000 | 166704.551 | 25-AUG-15:00 | 48247.488 | 50956.166 | 5776.933 | 0 | 61715.524 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 137741000000 | 146476.859 | 14-SEP-15:09 | 48247.488 | 50956.166 | 4663.992 | 0 | 42600.773 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 125640000000 | 126863.192 | 06-OCT-15:09 | 48247.488 | 50956.166 | 3758.388 | 0 | 23892.71 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 121106000000 | 120294.483 | 02-NOV-15:09 | 48247.488 | 50956.166 | 3795.815 | 0 | 17285.176 | 0 | 9.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 121704000000 | 110411.581 | 18-DEC-08:09 | 48247.488 | 58341.44 | 3420.674 | 0 | 0 | 0 | 401.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1644990000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 112370000000 | 110411.581 |  | 48247.488 | 50956.166 | 3420.674 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 178305000000 | 169909.932 |  | 48247.488 | 58341.44 | 6498.172 | 0 | 64298.391 | 0 | 977.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29447.86 | 11098.63 | 0 | 40546.49
Cost per Total Building Area ($/m2) | 5.91 | 2.23 | 0 | 8.14
Cost per Net Conditioned Building Area ($/m2) | 5.91 | 2.23 | 0 | 8.14

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2688.61 | 539.64 | 539.64
Net Site Energy | 2688.61 | 539.64 | 539.64
Total Source Energy | 6652.2 | 1335.2 | 1335.2
Net Source Energy | 6652.2 | 1335.2 | 1335.2
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1086.03 | 0 | 0 | 0 | 0
Cooling | 102.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 68.41 | 0 | 0 | 0 | 0 | 0
Pumps | 1.56 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 43.75 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1558.82 | 1129.78 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 195.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 224318.43 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 103217.77 | 82435.41 | 20782.35 | 0.8 | 4.14
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 124362.41 | 99322.69 | 25039.72 | 0.8 | 4.14
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 121544.55 | 97072.2 | 24472.36 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 34149.94 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 38264.24 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 35853.56 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7790.53 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8301.66 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 5067.78 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11070.3 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10699.54 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10444.34 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7660.03 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12910.36 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10668.86 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9767.67 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8308.45 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13567.79 | -
VAV_1_HEATC | Coil:Heating:Gas | 36858.39 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 35131.12 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 35360.3 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.24 | 11697.52 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.51 | 14093.81 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.34 | 13774.47 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1307.85 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43175.3764 | 64.6098 | 92.1254 | 0 | 0.0007 | 2183830 | 17400.19
February | 36215.6853 | 55.8236 | 83.1651 | 0 | 0.0006 | 1971760 | 14752.7811
March | 36972.6835 | 60.346 | 97.0385 | 0 | 0.0007 | 2301330 | 15385.5024
April | 31307.7524 | 52.5275 | 87.3337 | 0 | 0.0006 | 2071420 | 13166.1535
May | 32779.086 | 56.6559 | 97.4409 | 0 | 0.0007 | 2311410 | 13945.3561
June | 34708.5934 | 60.8421 | 106.2549 | 0 | 0.0007 | 2520610 | 14848.5126
July | 35365.7593 | 62.588 | 110.4148 | 0 | 0.0008 | 2619380 | 15187.0666
August | 36683.6351 | 64.8137 | 114.1438 | 0 | 0.0008 | 2707830 | 15742.6979
September | 31857.8134 | 55.5729 | 96.5443 | 0 | 0.0007 | 2290220 | 13602.6506
October | 32693.3059 | 55.3387 | 92.9583 | 0 | 0.0007 | 2204900 | 13795.8663
November | 34597.2188 | 56.0586 | 89.3204 | 0 | 0.0006 | 2118230 | 14357.346
December | 40543.1505 | 61.565 | 89.7426 | 0 | 0.0006 | 2127530 | 16425.8033
Annual Sum or Average | 426900.0602 | 706.7419 | 1156.4827 | 0 | 0.0081 | 27428400 | 178609.9265
Minimum of Months | 31307.7524 | 52.5275 | 83.1651 | 0 | 0.0006 | 1971760 | 13166.1535
Maximum of Months | 43175.3764 | 64.8137 | 114.1438 | 0 | 0.0008 | 2707830 | 17400.19
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 124112000000 | 112489.605 | 17-JAN-08:09 | 48247.488 | 58341.44 | 3406.259 | 0 | 0 | 1779 | 715.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 112060000000 | 112460.53 | 02-FEB-14:00 | 48247.488 | 48066.275 | 3420.319 | 0 | 12713.119 | 0 | 13.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 130790000000 | 119123.155 | 30-MAR-15:20 | 48247.488 | 50956.166 | 3833.547 | 0 | 16077.514 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 117724000000 | 115951.313 | 06-APR-15:00 | 48247.488 | 50956.166 | 3457.209 | 0 | 13282.011 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 131363000000 | 124593.594 | 16-MAY-15:00 | 48247.488 | 50956.166 | 3774.251 | 0 | 21607.25 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 143252000000 | 155582.893 | 26-JUN-15:20 | 48247.488 | 50956.166 | 7898.714 | 0 | 48472.085 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 148866000000 | 155782.64 | 21-JUL-15:00 | 48247.488 | 50956.166 | 8281.216 | 0 | 48289.33 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 153892000000 | 148830.401 | 09-AUG-15:00 | 48247.488 | 50956.166 | 6980.437 | 0 | 42637.87 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 130158000000 | 138677.734 | 12-SEP-12:00 | 48247.488 | 51598.363 | 5029.653 | 0 | 33793.789 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 125310000000 | 125105.507 | 06-OCT-15:09 | 48247.488 | 50956.166 | 4401.885 | 0 | 21491.528 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 120384000000 | 111894.439 | 03-NOV-07:10 | 48247.488 | 58341.44 | 3406.259 | 0 | 0 | 1779 | 120.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 120913000000 | 112448.753 | 18-DEC-08:09 | 48247.488 | 58341.44 | 3406.259 | 0 | 0 | 1779 | 674.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1558820000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 112060000000 | 111894.439 |  | 48247.488 | 48066.275 | 3406.259 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 153892000000 | 155782.64 |  | 48247.488 | 58341.44 | 8281.216 | 0 | 48472.085 | 1779 | 715.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34761.33 | 9130.64 | 0 | 43891.96
Cost per Total Building Area ($/m2) | 6.98 | 1.83 | 0 | 8.81
Cost per Net Conditioned Building Area ($/m2) | 6.98 | 1.83 | 0 | 8.81

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3199.54 | 642.2 | 642.2
Net Site Energy | 3199.54 | 642.2 | 642.2
Total Source Energy | 7141.53 | 1433.41 | 1433.41
Net Source Energy | 7141.53 | 1433.41 | 1433.41
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1596.96 | 0 | 0 | 0 | 0
Cooling | 93.97 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 73.02 | 0 | 0 | 0 | 0 | 0
Pumps | 1.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 47.08 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1555.49 | 1644.04 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 195.85 | 3.24 | 0.487 | 0.409
Non-North Total or Average |  |  | 456.98 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 252452.01 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 109135.66 | 85053.03 | 24082.64 | 0.78 | 4.02
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 127807.62 | 102074.23 | 25733.39 | 0.8 | 4.14
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 127418.77 | 101763.67 | 25655.1 | 0.8 | 4.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 34224.22 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 40615.36 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 38828.25 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10091.37 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10233.07 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 5393.73 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12888.91 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13521.69 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12836.02 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7974.15 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15075.93 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13582.34 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12352.65 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9240.07 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15745.95 | -
VAV_1_HEATC | Coil:Heating:Gas | 42112.55 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 39928.22 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 39961.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.25 | 11718.17 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.72 | 14484.25 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.7 | 14440.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1471.88 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 46457.1527 | 67.3075 | 82.0679 | 0 | 0.0006 | 53882.5569 | 18481.7686
February | 39262.9197 | 58.3128 | 74.01 | 0 | 0.0006 | 48600.9689 | 15756.2608
March | 38815.9294 | 61.386 | 85.3361 | 0 | 0.0006 | 56060.4259 | 15934.1001
April | 30453.8004 | 51.2657 | 77.0595 | 0 | 0.0006 | 50638.8057 | 12798.1204
May | 31004.6672 | 54.1236 | 84.7397 | 0 | 0.0006 | 55694.187 | 13214.1591
June | 31680.9303 | 57.1876 | 92.721 | 0 | 0.0007 | 60947.4254 | 13682.4203
July | 34112.4174 | 61.8891 | 100.8544 | 0 | 0.0007 | 66294.8229 | 14762.3929
August | 34474.514 | 62.2596 | 100.9921 | 0 | 0.0007 | 66384.3186 | 14891.7106
September | 29404.5793 | 51.7923 | 81.8704 | 0 | 0.0006 | 53810.26 | 12576.3534
October | 31265.6443 | 53.1681 | 80.8582 | 0 | 0.0006 | 53137.4233 | 13190.5046
November | 36338.6113 | 57.3628 | 79.5463 | 0 | 0.0006 | 52256.3939 | 14907.0695
December | 43347.7821 | 63.9058 | 80.1673 | 0 | 0.0006 | 52641.5712 | 17350.2369
Annual Sum or Average | 426618.9482 | 699.961 | 1020.2229 | 0 | 0.0076 | 670349.1597 | 177545.0972
Minimum of Months | 29404.5793 | 51.2657 | 74.01 | 0 | 0.0006 | 48600.9689 | 12576.3534
Maximum of Months | 46457.1527 | 67.3075 | 100.9921 | 0 | 0.0007 | 66384.3186 | 18481.7686
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 125030000000 | 110921.17 | 09-JAN-08:09 | 48247.488 | 58341.44 | 3498.963 | 0 | 0 | 0 | 833.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 112775000000 | 110693.504 | 02-FEB-08:09 | 48247.488 | 58341.44 | 3498.963 | 0 | 0 | 0 | 605.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 130084000000 | 110432.889 | 27-MAR-07:10 | 48247.488 | 58341.44 | 3498.963 | 0 | 0 | 0 | 344.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 117504000000 | 114801.661 | 04-APR-15:09 | 48247.488 | 50956.166 | 3575.576 | 0 | 12013.433 | 0 | 8.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 129234000000 | 126336.421 | 31-MAY-15:00 | 48247.488 | 50956.166 | 4199.241 | 0 | 22925.086 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 141424000000 | 148512.532 | 14-JUN-15:00 | 48247.488 | 50956.166 | 4933.383 | 0 | 44367.056 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 153832000000 | 165541.563 | 07-JUL-07:00 | 48247.488 | 58341.44 | 5480.17 | 0 | 53464.025 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 154040000000 | 153583.719 | 14-AUG-07:00 | 48247.488 | 58341.44 | 4758.856 | 0 | 42227.494 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 124863000000 | 146437.038 | 07-SEP-15:09 | 48247.488 | 50956.166 | 4464.932 | 0 | 42760.011 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 123301000000 | 120256.092 | 27-OCT-12:30 | 48247.488 | 51598.363 | 4371.012 | 0 | 16024.877 | 0 | 14.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 121257000000 | 110501.424 | 27-NOV-08:09 | 48247.488 | 58341.44 | 3498.963 | 0 | 0 | 0 | 413.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 122151000000 | 110587.338 | 11-DEC-08:09 | 48247.488 | 58341.44 | 3498.963 | 0 | 0 | 0 | 499.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1555490000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 112775000000 | 110432.889 |  | 48247.488 | 50956.166 | 3498.963 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 154040000000 | 165541.563 |  | 48247.488 | 58341.44 | 5480.17 | 0 | 53464.025 | 0 | 833.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27822.92 | 12947.09 | 0 | 40770.01
Cost per Total Building Area ($/m2) | 5.58 | 2.6 | 0 | 8.18
Cost per Net Conditioned Building Area ($/m2) | 5.58 | 2.6 | 0 | 8.18

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4342.71 | 871.65 | 871.65
Net Site Energy | 4342.71 | 871.65 | 871.65
Total Source Energy | 8611.09 | 1728.38 | 1728.38
Net Source Energy | 8611.09 | 1728.38 | 1728.38
Area [m2]
Total Building Area | 4982.19
Net Conditioned Building Area | 4982.19
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2731.09 | 0 | 0 | 0 | 0
Cooling | 74.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 552.57 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 27.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 806.04 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 96.25 | 0 | 0 | 0 | 0 | 0
Pumps | 2.88 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 51.6 | 0 | 0 | 0 | 174.59
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1560.02 | 2782.69 | 0 | 0 | 0 | 174.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_BOTTOM | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 40.7174
CORE_MID | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 983.54 | Yes | 2698.04 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
FIRSTFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 131.26 | Yes | 360.08 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 207.34 | Yes | 568.77 | 1 | 136.92 | 65.28 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 131.25 | Yes | 360.05 | 1 | 91.28 | 43.52 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 1660.73 | Yes | 2024.76 | 1 | 202.84 | 0 | 0 |  | 0
Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Conditioned Total | 9964.37 |  | 19741.41 |  | 1977.67 | 652.83 | 5.38 | 37.16 | 7.2575
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_BOT_ZN_5_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 983.54 | 0 | 180
PERIMETER_BOT_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 90 | 90 | E
PERIMETER_BOT_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 0 | 90 | N
PERIMETER_BOT_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 180 | 90 | S
PERIMETER_BOT_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 270 | 90 | W
PERIMETER_MID_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 90 | 90 | E
PERIMETER_MID_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 0 | 90 | N
PERIMETER_MID_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 180 | 90 | S
PERIMETER_MID_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 180 | 90 | S
PERIMETER_BOT_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 180 | 180
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 90 | 90 | E
PERIMETER_BOT_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.26 | 90 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 0 | 90 | N
PERIMETER_BOT_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 207.34 | 0 | 180
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 270 | 90 | W
PERIMETER_BOT_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 131.25 | 270 | 180
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 136.92 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 91.28 | 270 | 90 | W
PERIMETER_TOP_PLENUM_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 90 | 90 | E
PERIMETER_TOP_PLENUM_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 0 | 90 | N
PERIMETER_TOP_PLENUM_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.85 | 180 | 90 | S
PERIMETER_TOP_PLENUM_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40.57 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 1660.73 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 65.28 | 65.28 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 43.52 | 43.52 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 652.83 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 195.85 | 2.61 | 0.702 | 0.633
Non-North Total or Average |  |  | 456.98 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 345271.35 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 127932.51 | 102173.98 | 25758.54 | 0.8 | 4.14
VAV_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 173637.66 | 138676.63 | 34961.03 | 0.8 | 3.95
VAV_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 172003.75 | 137371.7 | 34632.05 | 0.8 | 3.95
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 32772.55 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 49675.41 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 49328.35 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22548.92 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14261.95 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7415.22 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16319.15 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27675.5 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17806.71 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12110.02 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 19388.85 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27310.78 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17373.28 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11942.08 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 19510.19 | -
VAV_1_HEATC | Coil:Heating:Gas | 55708.34 | 0.8
VAV_2_HEATC | Coil:Heating:Gas | 51472.39 | 0.8
VAV_3_HEATC | Coil:Heating:Gas | 51621.28 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.73 | 14498.41 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.49 | 18045.62 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.39 | 17875.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2013.05 | 0.85
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 8.44 | 0.85
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.38 | 845000 | 0.8 | 1.81 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 56119.1902 | 59.6043 | 181.3699 | 0 | 0.0007 | 36370.2169 | 20755.7814
February | 46091.5183 | 49.6486 | 163.4953 | 0 | 0.0006 | 32790.457 | 17153.9314
March | 41427.812 | 46.5718 | 187.6825 | 0 | 0.0007 | 37653.2765 | 15717.8283
April | 29583.3216 | 34.8734 | 167.8464 | 0 | 0.0006 | 33681.4225 | 11472.7866
May | 27832.1257 | 34.0731 | 184.3578 | 0 | 0.0006 | 36999.5575 | 10988.1844
June | 29526.8345 | 36.6801 | 206.7177 | 0 | 0.0007 | 41488.8089 | 11739.1585
July | 29688.0024 | 36.9256 | 208.7943 | 0 | 0.0007 | 41905.7243 | 11810.2098
August | 30318.1812 | 37.334 | 205.372 | 0 | 0.0007 | 41217.7056 | 12003.1289
September | 27900.4669 | 33.4301 | 169.6071 | 0 | 0.0006 | 34036.8066 | 10903.3363
October | 34960.3172 | 40.1521 | 176.1826 | 0 | 0.0006 | 35350.2017 | 13394.9725
November | 45577.3941 | 49.8382 | 177.2237 | 0 | 0.0006 | 35548.3364 | 17076.9835
December | 51405.0641 | 55.1631 | 177.9678 | 0 | 0.0007 | 35691.769 | 19099.2942
Annual Sum or Average | 450430.2281 | 514.2944 | 2206.6171 | 0 | 0.0078 | 442734.283 | 172115.5958
Minimum of Months | 27832.1257 | 33.4301 | 163.4953 | 0 | 0.0006 | 32790.457 | 10903.3363
Maximum of Months | 56119.1902 | 59.6043 | 208.7943 | 0 | 0.0007 | 41905.7243 | 20755.7814
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 128154000000 | 114124.003 | 02-JAN-08:09 | 48247.488 | 58341.44 | 4340.694 | 0 | 0 | 1779 | 1415.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 115541000000 | 113189.818 | 03-FEB-08:09 | 48247.488 | 58341.44 | 4340.694 | 0 | 0 | 1779 | 481.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 132675000000 | 113101.657 | 13-MAR-07:10 | 48247.488 | 58341.44 | 4340.694 | 0 | 0 | 1779 | 393.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 118680000000 | 111178.679 | 03-APR-07:10 | 48247.488 | 58341.44 | 4340.694 | 0 | 0 | 0 | 249.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 130372000000 | 127109.838 | 30-MAY-12:39 | 48247.488 | 51598.363 | 5113.592 | 0 | 22141.954 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 146190000000 | 151675.715 | 21-JUN-15:20 | 48247.488 | 50956.166 | 5885.108 | 0 | 46578.513 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 147659000000 | 150105.209 | 11-JUL-15:00 | 48247.488 | 50956.166 | 6235.803 | 0 | 44657.312 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 145235000000 | 148072.615 | 15-AUG-12:00 | 48247.488 | 51598.363 | 6169.11 | 0 | 42049.214 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 119932000000 | 117729.8 | 07-SEP-15:00 | 48247.488 | 50956.166 | 4591.844 | 0 | 13924.006 | 0 | 10.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 124560000000 | 113022.128 | 30-OCT-07:10 | 48247.488 | 58341.44 | 4340.694 | 0 | 0 | 1779 | 313.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 125258000000 | 113116.654 | 06-NOV-08:09 | 48247.488 | 58341.44 | 4340.694 | 0 | 0 | 1779 | 408.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 125764000000 | 113158.061 | 29-DEC-08:09 | 48247.488 | 58341.44 | 4340.694 | 0 | 0 | 1779 | 449.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1560020000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 115541000000 | 111178.679 |  | 48247.488 | 50956.166 | 4340.694 | 0 | 0 | 0 | 8.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 147659000000 | 151675.715 |  | 48247.488 | 58341.44 | 6235.803 | 0 | 46578.513 | 1779 | 1415.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 45219.84 | 11456.47 | 0 | 56676.31
Cost per Total Building Area ($/m2) | 9.08 | 2.3 | 0 | 11.38
Cost per Net Conditioned Building Area ($/m2) | 9.08 | 2.3 | 0 | 11.38

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720