## BuildingSummary
Building Summary Small Office new construction
|  | Value | Data Source
Program
| Building Name | Benchmark Small Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 511 | 2003 CBECS, ASHRAE Small Office 30% Advanced Energy Design Guide
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.244
| East | 0.198
| North | 0.198
| West | 0.198
| Total | 0.212
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones
| Floor to Ceiling Height (m) | 3.05
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 281.5
| Net Dimensions - Total Area (m2) | 222
| Wall to Skin Ratio | 0.32
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 598.76
| Net Dimensions - Total Area (m2) | 598.76
| Roof to Skin Ratio | 0.68
Window Dimensions (m2)
| South | 16.73
| East | 11.16
| North | 16.73
| West | 11.16
| Total Area (m2) | 55.78
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab w/carpet
| Dimensions - Total Area (m2) | 511
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 0
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.46
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.45 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 17.65

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 10.76 | 8.07 | 0 | 11.3562 | 10 | 0 | 80.5463 | 0 | 0
Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.45 | 20.64 | 18.5806 | 6.1058 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 61.0582 | 0 | 0.62247
Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3 | 11.16 | 18.5806 | 3.6221 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 36.2205 | 0 | 0.65537
Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.45 | 16.73 | 18.5806 | 6.1058 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 61.0582 | 0 | 0.62247
Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3 | 11.16 | 18.5806 | 3.6221 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 36.2205 | 0 | 0.65537
Attic | No | 1 | 567.98 | 720.19 | 1.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5 | 59.69 |  | 27.5104
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 201.9091 | 2559.5418 | 695.7164 | 2316.0945 |  | 1142.2145 | 186.9745 | 2251.0327 | 113.8618 | 294.7673 | 2213.0109 | 774.1455 | 580.2291 | 72.6764 | 77.7964 | 11.2727
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 5.1813 | 5.1813 | 5.1813 | 5.1813 | 5.1813 | 5.1813 | 5.1813 | 5.1813 | 5.1813 | 5.1813 | 5.2356 | 5.2356 | 6.5789 | 6.5789 | 6.5359 | 6.5789
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 9.7211 | 8.8067 | 7.8874 | 8.6642 | 7.0277 | 7.2764 | 4.407 | 9.0641 | 7.8625 | 5.6546 | 8.5608 | 7.4058 | 8.3295 | 5.8965 | 6.3341 | 5.1221
| PSZ-AC:2_COOLC DXCOIL | 7.5962 | 6.4891 | 6.6952 | 6.666 | 5.0803 | 5.4432 | 7.5126 | 7.0359 | 5.5916 | 6.2585 | 7.961 | 7.0058 | 8.5697 | 7.9333 | 8.7661 | 10.9125
| PSZ-AC:3_COOLC DXCOIL | 6.541 | 6.3166 | 6.1938 | 5.3064 | 4.0263 | 4.639 | 3.9178 | 5.754 | 4.8894 | 4.2021 | 5.4312 | 4.6073 | 5.4135 | 4.9102 | 4.9107 | 5.8064
| PSZ-AC:4_COOLC DXCOIL | 7.9996 | 6.9487 | 7.1248 | 6.8875 | 4.9198 | 5.588 | 3.2359 | 7.1771 | 5.398 | 4.2499 | 7.6786 | 6.7803 | 8.2384 | 7.6183 | 7.6453 | 9.0752
| PSZ-AC:5_COOLC DXCOIL | 7.4274 | 7.5016 | 7.4465 | 5.7367 | 4.4508 | 5.0905 | 5.238 | 6.4676 | 5.9861 | 5.0063 | 6.3484 | 5.7276 | 6.0268 | 5.4181 | 5.721 | 6.4722
Heating (kW)
| PSZ-AC:1_HEATC | 13.0058 | 13.6387 | 11.6214 | 13.4425 | 11.1228 | 11.3801 | 7.8518 | 15.0086 | 11.3861 | 10.1912 | 15.0906 | 11.6126 | 15.231 | 11.1822 | 12.9859 | 13.0881
| PSZ-AC:2_HEATC | 9.3827 | 9.3111 | 9.4526 | 9.6109 | 7.3685 | 8.3704 | 11.7447 | 10.5756 | 8.2117 | 10.4271 | 12.0404 | 10.3923 | 13.1557 | 12.6506 | 13.6724 | 19.5332
| PSZ-AC:3_HEATC | 8.5897 | 8.8252 | 8.8456 | 7.6342 | 6.2006 | 6.8724 | 6.2191 | 8.7271 | 6.6679 | 6.8557 | 8.776 | 6.6796 | 8.9163 | 7.7504 | 8.563 | 10.6756
| PSZ-AC:4_HEATC | 10.0965 | 10.1244 | 10.1913 | 10.002 | 7.1016 | 8.6105 | 5.6409 | 10.8037 | 7.9906 | 7.4132 | 11.7317 | 10.1351 | 12.7678 | 12.2712 | 13.2523 | 17.0215
| PSZ-AC:5_HEATC | 9.8313 | 10.4352 | 10.581 | 8.1143 | 6.745 | 7.4519 | 8.052 | 9.4891 | 7.921 | 7.9571 | 9.6291 | 7.9575 | 9.5544 | 8.3622 | 9.6324 | 11.5858
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.87 | 3.95 | 3.96 | 3.95 | 4.04 | 4.04 | 4.04 | 3.97 | 4.04 | 4.04 | 3.98 | 4.04 | 3.99 | 4.04 | 4.04 | 4.04
| PSZ-AC:2_COOLC DXCOIL | 3.79 | 3.85 | 3.93 | 3.85 | 3.91 | 4.01 | 4.04 | 3.85 | 4.04 | 4.04 | 3.84 | 4.04 | 3.85 | 4.04 | 3.88 | 4.04
| PSZ-AC:3_COOLC DXCOIL | 3.89 | 3.9 | 4.01 | 3.92 | 4.04 | 4.04 | 4.04 | 3.94 | 4.04 | 4.04 | 3.97 | 4.04 | 3.97 | 4.04 | 4.04 | 4.04
| PSZ-AC:4_COOLC DXCOIL | 3.82 | 3.88 | 3.96 | 3.87 | 3.9 | 4.02 | 3.99 | 3.85 | 4.04 | 3.98 | 3.84 | 4.04 | 3.85 | 4.04 | 3.99 | 4.04
| PSZ-AC:5_COOLC DXCOIL | 3.91 | 3.92 | 4.02 | 3.91 | 4.03 | 4.04 | 4.04 | 3.92 | 4.04 | 4.04 | 3.92 | 4.04 | 3.95 | 4.04 | 4.04 | 4.04
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC:1_FAN | 0.51 | 0.5 | 0.45 | 0.49 | 0.42 | 0.44 | 0.27 | 0.52 | 0.47 | 0.34 | 0.49 | 0.45 | 0.48 | 0.36 | 0.38 | 0.31
| PSZ-AC:2_FAN | 0.37 | 0.33 | 0.37 | 0.34 | 0.28 | 0.32 | 0.45 | 0.36 | 0.34 | 0.38 | 0.4 | 0.42 | 0.44 | 0.48 | 0.47 | 0.66
| PSZ-AC:3_FAN | 0.35 | 0.34 | 0.37 | 0.29 | 0.24 | 0.28 | 0.24 | 0.32 | 0.3 | 0.25 | 0.31 | 0.28 | 0.31 | 0.3 | 0.3 | 0.35
| PSZ-AC:4_FAN | 0.4 | 0.37 | 0.4 | 0.36 | 0.26 | 0.33 | 0.19 | 0.37 | 0.33 | 0.25 | 0.39 | 0.41 | 0.42 | 0.46 | 0.45 | 0.55
| PSZ-AC:5_FAN | 0.4 | 0.41 | 0.44 | 0.31 | 0.27 | 0.31 | 0.32 | 0.35 | 0.36 | 0.3 | 0.35 | 0.35 | 0.34 | 0.33 | 0.35 | 0.39
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.10257 | 0.12399 | 0.13036 | 0.11802 | 0.12895 | 0.10254 | 0.16331 | 0.076382 | 0.075528 | 0.073503 | 0.06712 | 0.075555 | 0.075214 | 0.077617 | 0.075022 | 0.10067
| Total Cost ($/m2) | 13.72 | 14.96 | 16.18 | 12.68 | 12.59 | 11.05 | 15.19 | 8.18 | 7.83 | 6.88 | 7.09 | 7.7 | 7.96 | 7.84 | 7.64 | 10.81
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011464 | 0.0080988 | 0.0083607 | 0.0098253 | 0.0084913 | 0.0078277 | 0.0086137 | 0.009718 | 0.0069327 | 0.0084353 | 0.0083312 | 0.0069154 | 0.0079093 | 0.0080499 | 0.0078808 | 0.0041074
| Total Cost ($/m2) | 0.25 | 0.51 | 0.38 | 0.78 | 0.24 | 0.42 | 0.53 | 1.35 | 0.64 | 1.14 | 1.67 | 0.99 | 2.1 | 1.75 | 2.54 | 2.31
Total Utility Costs
| Cost Intensity ($/m2) | 13.96 | 15.47 | 16.56 | 13.47 | 12.83 | 11.47 | 15.72 | 9.53 | 8.47 | 8.01 | 8.76 | 8.69 | 10.07 | 9.59 | 10.17 | 13.12
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 19200 | 12791.6667 | 13986.1111 | 6838.8889 | 3716.6667 | 7747.2222 | 1422.2222 | 5569.4444 | 4741.6667 | 1205.5556 | 4277.7778 | 2936.1111 | 3744.4444 | 1977.7778 | 1588.8889 | 1411.1111
| Interior Lighting | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222
| Exterior Lighting | 4222.2222 | 4219.4444 | 4219.4444 | 4219.4444 | 4216.6667 | 4213.8889 | 4216.6667 | 4213.8889 | 4216.6667 | 4208.3333 | 4216.6667 | 4213.8889 | 4213.8889 | 4211.1111 | 4208.3333 | 4183.3333
| Interior Equipment | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 10916.6667 | 10622.2222 | 11208.3333 | 9852.7778 | 7938.8889 | 9091.6667 | 7888.8889 | 10922.2222 | 9997.2222 | 8383.3333 | 11450 | 10944.4444 | 12138.8889 | 11427.7778 | 12222.2222 | 15288.8889
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 68363.8889 | 61658.3333 | 63436.1111 | 54936.1111 | 49894.4444 | 55077.7778 | 47552.7778 | 54727.7778 | 52977.7778 | 47819.4444 | 53966.6667 | 52116.6667 | 54119.4444 | 51638.8889 | 52047.2222 | 54905.5556
Gas (MJ)
| Heating | 280 | 21210 | 12320 | 29280 | 3030 | 16190 | 19460 | 59220 | 35660 | 56870 | 90690 | 60930 | 123550 | 98880 | 151840 | 273760
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10690 | 11090 | 10860 | 11470 | 11400 | 11130 | 11730 | 11770 | 11720 | 11930 | 12040 | 12030 | 12270 | 12310 | 12650 | 13100
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10970 | 32300 | 23180 | 40750 | 14430 | 27330 | 31190 | 70990 | 47370 | 68810 | 102730 | 72950 | 135820 | 111190 | 164480 | 286860
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 257070 | 254270 | 251550 | 238520 | 194050 | 225610 | 202380 | 268020 | 238090 | 240960 | 297000 | 260580 | 330650 | 297090 | 351850 | 484520
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 135.2218 | 90.0892 | 98.5014 | 48.165 | 26.1758 | 54.5622 | 10.0164 | 39.2245 | 33.3946 | 8.4905 | 30.1276 | 20.6785 | 26.3714 | 13.9291 | 11.1902 | 9.9382
| Interior Lighting (elec) | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046
| Exterior Lighting (elec) | 29.7363 | 29.7167 | 29.7167 | 29.7167 | 29.6972 | 29.6776 | 29.6972 | 29.6776 | 29.6972 | 29.6385 | 29.6972 | 29.6776 | 29.6776 | 29.658 | 29.6385 | 29.4624
| Interior Equipment (elec) | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 76.884 | 74.8102 | 78.9381 | 69.3912 | 55.912 | 64.0308 | 55.5599 | 76.9231 | 70.4085 | 59.0422 | 80.6401 | 77.0796 | 85.4918 | 80.4836 | 86.0787 | 107.6767
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 481.4735 | 434.2476 | 446.7681 | 386.9043 | 351.3968 | 387.902 | 334.9049 | 385.437 | 373.1121 | 336.783 | 380.0767 | 367.0475 | 381.1527 | 363.6826 | 366.5584 | 386.6891
Gas (MJ/m2)
| Heating (gas) | 0.54777 | 41.4939 | 24.102 | 57.2815 | 5.9277 | 31.6731 | 38.0703 | 115.8541 | 69.7629 | 111.2567 | 177.42 | 119.1995 | 241.7051 | 193.4424 | 297.0498 | 535.5662
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.9132 | 21.6958 | 21.2458 | 22.4392 | 22.3022 | 21.774 | 22.9478 | 23.0261 | 22.9282 | 23.3391 | 23.5543 | 23.5347 | 24.0042 | 24.0825 | 24.7476 | 25.628
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 21.461 | 63.1896 | 45.3478 | 79.7206 | 28.2299 | 53.4666 | 61.0181 | 138.8802 | 92.6716 | 134.6154 | 200.9743 | 142.7146 | 265.7094 | 217.5248 | 321.7779 | 561.1941
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 502.9149 | 497.4372 | 492.116 | 466.6249 | 379.6267 | 441.3687 | 395.923 | 524.3368 | 465.7837 | 471.3984 | 581.0314 | 509.7817 | 646.862 | 581.2074 | 688.3363 | 947.8832
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 16.4556 | 14.4009 | 12.9667 | 11.5344 | 12.5002 | 11.7081 | 11.3237 | 11.8607 | 11.2762 | 11.3929 | 11.8843 | 11.8377 | 11.9391 | 11.8551 | 11.8742 | 12.2484
| Feb | 16.8524 | 14.626 | 13.7261 | 11.4017 | 12.1853 | 11.519 | 12.1095 | 10.945 | 11.8563 | 10.6438 | 11.8843 | 11.2681 | 10.9805 | 11.2896 | 10.9278 | 12.2484
| Mar | 17.1285 | 14.7381 | 15.7935 | 12.6225 | 12.1672 | 12.3903 | 11.2611 | 12.5771 | 11.9484 | 11.3979 | 11.7595 | 12.1559 | 11.2597 | 11.9698 | 10.9804 | 12.2484
| Apr | 17.6832 | 16.0041 | 15.9775 | 14.2458 | 12.9248 | 14.3883 | 12.2363 | 13.2657 | 13.2294 | 11.1022 | 12.1871 | 12.9146 | 12.1278 | 11.5472 | 11.3488 | 12.167
| May | 18.291 | 18.3489 | 18.5517 | 15.7804 | 13.0545 | 15.6462 | 12.4101 | 14.9867 | 14.4713 | 12.5341 | 14.7079 | 13.8207 | 14.9172 | 12.747 | 13.002 | 13.7962
| Jun | 19.3707 | 18.4707 | 21.174 | 16.7223 | 13.115 | 18.0686 | 12.8584 | 17.7212 | 15.6802 | 13.1596 | 17.0048 | 14.8689 | 16.9358 | 15.2147 | 14.9049 | 15.1062
| Jul | 19.0278 | 19.0907 | 20.8976 | 18.0526 | 13.8044 | 17.8125 | 13.7736 | 18.3485 | 16.1619 | 14.0585 | 17.6026 | 15.8033 | 17.0981 | 15.4247 | 15.973 | 15.0399
| Aug | 19.2004 | 18.9723 | 20.8711 | 16.7328 | 14.4035 | 17.3614 | 13.0925 | 18.1913 | 16.1822 | 13.8646 | 17.4789 | 15.9199 | 16.8945 | 14.9722 | 15.3471 | 14.9862
| Sep | 18.7233 | 18.1062 | 19.3724 | 16.1913 | 14.4401 | 16.9004 | 14.8211 | 16.0109 | 14.606 | 13.5861 | 15.5044 | 14.2637 | 15.2877 | 13.8497 | 14.1906 | 12.439
| Oct | 18.3084 | 17.0731 | 16.6205 | 14.6758 | 13.4857 | 14.6761 | 12.8561 | 14.6065 | 13.3765 | 11.6046 | 13.7537 | 13.5424 | 12.5649 | 12.6405 | 11.8641 | 12.2484
| Nov | 17.2735 | 15.3635 | 15.001 | 12.6183 | 12.8532 | 12.7261 | 11.6723 | 13.4981 | 11.8438 | 11.3929 | 13.235 | 11.8954 | 11.9391 | 11.8551 | 11.8742 | 12.2484
| Dec | 16.3434 | 14.3654 | 12.7009 | 11.221 | 12.6227 | 12.0192 | 11.3277 | 11.8607 | 11.7693 | 11.3929 | 11.8843 | 11.8435 | 11.9391 | 11.8551 | 11.8742 | 12.2484
Time of Peak Electrical Demand
| Jan | 23-JAN-15:50 | 03-JAN-13:00 | 27-JAN-14:00 | 23-JAN-16:40 | 26-JAN-13:09 | 18-JAN-16:49 | 02-JAN-16:00 | 02-JAN-16:49 | 27-JAN-14:20 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-15:00 | 23-FEB-14:00 | 28-FEB-16:30 | 22-FEB-15:00 | 13-FEB-11:00 | 08-FEB-15:20 | 15-FEB-15:00 | 16-FEB-13:20 | 14-FEB-15:50 | 24-FEB-14:09 | 01-FEB-16:00 | 07-FEB-14:30 | 16-FEB-13:30 | 03-FEB-13:00 | 17-FEB-13:20 | 01-FEB-08:09
| Mar | 13-MAR-15:39 | 28-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-15:00 | 01-MAR-14:30 | 10-MAR-10:00 | 02-MAR-15:09 | 29-MAR-15:50 | 31-MAR-15:30 | 30-MAR-15:00 | 23-MAR-14:09 | 30-MAR-15:00 | 22-MAR-13:50 | 01-MAR-08:09
| Apr | 03-APR-14:39 | 21-APR-15:30 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:39 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 19-APR-15:00 | 28-APR-15:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:20 | 25-APR-13:30
| May | 19-MAY-15:20 | 18-MAY-15:30 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-08:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 17-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-15:30 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-15:50 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:20 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 21-JUN-15:50
| Jul | 13-JUL-15:20 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 03-JUL-15:30 | 24-JUL-14:00 | 03-JUL-14:00 | 19-JUL-12:00 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 11-JUL-15:00
| Aug | 21-AUG-15:20 | 28-AUG-15:00 | 01-AUG-15:00 | 17-AUG-15:39 | 08-AUG-09:00 | 04-AUG-15:00 | 15-AUG-12:09 | 09-AUG-14:00 | 01-AUG-15:20 | 07-AUG-15:20 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-14:30
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:00 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-15:20 | 29-SEP-14:39 | 01-SEP-15:00 | 06-SEP-10:00 | 01-SEP-15:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 08-SEP-15:39
| Oct | 06-OCT-15:50 | 06-OCT-15:00 | 02-OCT-15:20 | 12-OCT-15:00 | 19-OCT-10:00 | 06-OCT-13:00 | 31-OCT-13:09 | 12-OCT-14:50 | 11-OCT-15:00 | 03-OCT-14:50 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:20 | 06-OCT-14:00 | 03-OCT-07:10
| Nov | 07-NOV-14:00 | 03-NOV-14:30 | 13-NOV-15:39 | 22-NOV-14:00 | 09-NOV-16:00 | 10-NOV-16:40 | 14-NOV-16:00 | 03-NOV-13:00 | 08-NOV-14:00 | 06-NOV-16:49 | 02-NOV-14:39 | 10-NOV-16:49 | 06-NOV-16:00 | 01-NOV-07:10 | 06-NOV-16:49 | 01-NOV-07:10
| Dec | 15-DEC-15:30 | 19-DEC-15:30 | 11-DEC-15:00 | 05-DEC-14:00 | 19-DEC-13:09 | 05-DEC-16:30 | 07-DEC-16:00 | 01-DEC-16:40 | 05-DEC-16:49 | 01-DEC-16:19 | 01-DEC-16:19 | 04-DEC-16:00 | 06-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 828.31 | 841.46 | 747.65 | 709.8 | 571.68 | 739.1 | 563.9 | 782.08 | 684.54 | 375.02 | 801.08 | 702.2 | 817.94 | 767.61 | 823.59 | 1019.3
| Total Source Energy (MJ/m2) | 1620.46 | 1646.19 | 1462.66 | 1388.62 | 1118.41 | 1445.93 | 1103.18 | 1530.03 | 1339.2 | 733.67 | 1567.19 | 1373.74 | 1600.18 | 1501.71 | 1611.23 | 1994.1
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
| Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
Emissions
| Carbon Equivalent (kg) | 18946.3026 | 21149.1968 | 19567.9137 | 17657.2685 | 6091.1585 | 19069.3527 | 6119.7656 | 16049.1427 | 22495.5557 | 4723.6363 | 30624.0564 | 22605.3525 | 20973.7531 | 20875.9395 | 20781.036 | 20622.767
| CO2 (kg) | 43984.6284 | 53290.6539 | 46242.454 | 40530.2519 | 16319.4386 | 45422.5961 | 16462.11 | 36818.5882 | 52894.4531 | 11858.3019 | 71736.0024 | 53408.1877 | 49782.6342 | 49684.1959 | 49640.0802 | 53647.6831
| NOX (kg) | 77.0826 | 69.3616 | 77.2127 | 76.0916 | 14.0049 | 73.4474 | 14.1725 | 69.578 | 90.7156 | 16.5479 | 125.7371 | 90.4886 | 84.3555 | 83.1704 | 82.7262 | 62.055
| SO2 (kg) | 292.624 | 294.1187 | 255.0982 | 192.8375 | 145.1915 | 302.982 | 138.3832 | 199.8024 | 231.3556 | 36.9789 | 363.7108 | 227.6052 | 127.7655 | 137.9128 | 122.8806 | 279.5709
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0013 | 0.0008 | 0.0007 | 0.0007 | 0.0001 | 0.0006 | 0.0001 | 0.0008 | 0.0009 | 0.0002 | 0.0011 | 0.0009 | 0.0009 | 0.001 | 0.0009 | 0.001
| Water for Electricity (m3) | 36.2159 | 100.3253 | 1884.35 | 343.0005 | 876.0391 | 1511.02 | 834.932 | 12.4256 | 240.561 | 488.56 | 83.724 | 236.654 | 83.9621 | 3271.04 | 80.746 | 56.0965

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 257.07 | 502.93 | 502.93
Net Site Energy | 257.07 | 502.93 | 502.93
Total Source Energy | 828.31 | 1620.46 | 1620.46
Net Source Energy | 828.31 | 1620.46 | 1620.46
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 0.28 | 0 | 0 | 0 | 0
Cooling | 69.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 39.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.69 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 246.11 | 10.97 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 16.73 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9721.07 | 7297.71 | 2423.37 | 0.75 | 3.87
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7596.16 | 5503.66 | 2092.5 | 0.72 | 3.79
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6541.01 | 4942.37 | 1598.64 | 0.76 | 3.89
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7999.61 | 5866.52 | 2133.09 | 0.73 | 3.82
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7427.35 | 5653.09 | 1774.26 | 0.76 | 3.91
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13005.77 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 9382.68 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8589.7 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 10096.48 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 9831.32 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 592.33 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 424.95 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 404.65 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 460.97 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 467.3 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3258.6379 | 5.697 | 21.5715 | 0 | 0.0001 | 2669.7248 | 1402.2798
February | 3036.6044 | 5.3172 | 20.167 | 0 | 0.0001 | 2495.9196 | 1307.5655
March | 3571.0721 | 6.2554 | 23.7352 | 0 | 0.0001 | 2937.5232 | 1537.9444
April | 3487.0623 | 6.1104 | 23.1939 | 0 | 0.0001 | 2870.5338 | 1501.9816
May | 3917.7298 | 6.8691 | 26.0903 | 0 | 0.0001 | 3229.0048 | 1687.8887
June | 4070.5618 | 7.1402 | 27.1327 | 0 | 0.0001 | 3358.0079 | 1754.0461
July | 4010.8365 | 7.0342 | 26.725 | 0 | 0.0001 | 3307.5496 | 1728.1878
August | 4322.1389 | 7.5826 | 28.8182 | 0 | 0.0001 | 3566.6116 | 1862.5627
September | 3809.8661 | 6.6805 | 25.3759 | 0 | 0.0001 | 3140.5797 | 1641.4664
October | 3782.6609 | 6.6307 | 25.1785 | 0 | 0.0001 | 3116.1507 | 1629.5393
November | 3490.0308 | 6.1153 | 23.2112 | 0 | 0.0001 | 2872.67 | 1503.2287
December | 3227.4268 | 5.6501 | 21.4248 | 0 | 0.0001 | 2651.5768 | 1389.6117
Annual Sum or Average | 43984.6284 | 77.0826 | 292.624 | 0 | 0.0013 | 36215.8524 | 18946.3026
Minimum of Months | 3036.6044 | 5.3172 | 20.167 | 0 | 0.0001 | 2495.9196 | 1307.5655
Maximum of Months | 4322.1389 | 7.5826 | 28.8182 | 0 | 0.0001 | 3566.6116 | 1862.5627
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18142300000 | 16455.562 | 23-JAN-15:50 | 4950.048 | 3712.536 | 2350.196 | 0 | 5442.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 16961200000 | 16852.429 | 22-FEB-15:00 | 4950.048 | 3712.536 | 2350.196 | 0 | 5839.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 19962100000 | 17128.504 | 13-MAR-15:39 | 4950.048 | 3712.536 | 2350.196 | 0 | 6115.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19506900000 | 17683.182 | 03-APR-14:39 | 4950.048 | 3712.536 | 2350.196 | 0 | 6670.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 21942900000 | 18291.006 | 19-MAY-15:20 | 4950.048 | 3712.536 | 2350.196 | 0 | 7278.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 22819500000 | 19370.734 | 28-JUN-14:00 | 4950.048 | 3712.536 | 2350.196 | 0 | 8357.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 22476600000 | 19027.785 | 13-JUL-15:20 | 4950.048 | 3712.536 | 2350.196 | 0 | 8015.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 24237100000 | 19200.419 | 21-AUG-15:20 | 4950.048 | 3712.536 | 2350.196 | 0 | 8187.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21342000000 | 18723.292 | 11-SEP-14:00 | 4950.048 | 3712.536 | 2350.196 | 0 | 7710.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 21176000000 | 18308.405 | 06-OCT-15:50 | 4950.048 | 3712.536 | 2350.196 | 0 | 7295.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 19521400000 | 17273.495 | 07-NOV-14:00 | 4950.048 | 3712.536 | 2350.196 | 0 | 6260.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 18018900000 | 16343.37 | 15-DEC-15:30 | 4950.048 | 3712.536 | 2350.196 | 0 | 5330.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 246107000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 16961200000 | 16343.37 |  | 4950.048 | 3712.536 | 2350.196 | 0 | 5330.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 24237100000 | 19370.734 |  | 4950.048 | 3712.536 | 2350.196 | 0 | 8357.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7012.32 | 125.76 | 0 | 7138.08
Cost per Total Building Area ($/m2) | 13.72 | 0.25 | 0 | 13.96
Cost per Net Conditioned Building Area ($/m2) | 13.72 | 0.25 | 0 | 13.96

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 254.27 | 497.43 | 497.43
Net Site Energy | 254.27 | 497.43 | 497.43
Total Source Energy | 841.46 | 1646.19 | 1646.19
Net Source Energy | 841.46 | 1646.19 | 1646.19
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 21.21 | 0 | 0 | 0 | 0
Cooling | 46.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 38.24 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.09 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 221.97 | 32.3 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 16.73 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8806.72 | 6816.15 | 1990.57 | 0.77 | 3.95
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6489.15 | 4812.99 | 1676.16 | 0.74 | 3.85
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6316.63 | 4795.64 | 1520.99 | 0.76 | 3.9
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6948.74 | 5227.15 | 1721.59 | 0.75 | 3.88
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7501.61 | 5734.09 | 1767.52 | 0.76 | 3.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13638.69 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 9311.12 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8825.23 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 10124.43 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 10435.25 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 575.66 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 384.25 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 395.12 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 425.43 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 476.64 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4031.9332 | 5.1349 | 20.6712 | 0 | 0.0001 | 7050.5229 | 1585.5766
February | 3657.4727 | 4.6406 | 18.5071 | 0 | 0.0001 | 6312.3408 | 1436.0708
March | 3996.6722 | 5.2054 | 22.1063 | 0 | 0.0001 | 7540.5785 | 1586.5821
April | 3961.8529 | 5.1868 | 22.2888 | 0 | 0.0001 | 7602.943 | 1576.2117
May | 4754.2506 | 6.2291 | 26.8156 | 0 | 0.0001 | 9147.1124 | 1892.099
June | 5238.4473 | 6.8667 | 29.5902 | 0 | 0.0001 | 10093.5625 | 2085.2005
July | 5242.9119 | 6.8724 | 29.6136 | 0 | 0.0001 | 10101.5373 | 2086.9607
August | 5512.57 | 7.2265 | 31.1454 | 0 | 0.0001 | 10624.0869 | 2194.38
September | 4760.9718 | 6.2391 | 26.8699 | 0 | 0.0001 | 9165.6476 | 1894.925
October | 4409.1947 | 5.775 | 24.8402 | 0 | 0.0001 | 8473.2827 | 1754.5054
November | 3859.1748 | 5.0417 | 21.5617 | 0 | 0.0001 | 7354.8946 | 1533.9866
December | 3865.2016 | 4.9434 | 20.1086 | 0 | 0.0001 | 6858.7524 | 1522.6985
Annual Sum or Average | 53290.6539 | 69.3616 | 294.1187 | 0 | 0.0008 | 100325.2615 | 21149.1968
Minimum of Months | 3657.4727 | 4.6406 | 18.5071 | 0 | 0.0001 | 6312.3408 | 1436.0708
Maximum of Months | 5512.57 | 7.2265 | 31.1454 | 0 | 0.0001 | 10624.0869 | 2194.38
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15599300000 | 14400.931 | 03-JAN-13:00 | 4950.048 | 3712.536 | 2257.097 | 0 | 3481.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13966100000 | 14626.017 | 23-FEB-14:00 | 4950.048 | 3712.536 | 2257.097 | 0 | 3706.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 16683500000 | 14738.135 | 28-MAR-14:00 | 4950.048 | 3712.536 | 2257.097 | 0 | 3818.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 16821500000 | 16004.083 | 21-APR-15:30 | 4950.048 | 3712.536 | 2257.097 | 0 | 5084.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 20238000000 | 18348.878 | 18-MAY-15:30 | 4950.048 | 3712.536 | 2257.097 | 0 | 7429.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 22332000000 | 18470.67 | 13-JUN-15:30 | 4950.048 | 3712.536 | 2257.097 | 0 | 7550.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 22349700000 | 19090.726 | 05-JUL-15:00 | 4950.048 | 3712.536 | 2257.097 | 0 | 8171.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 23505800000 | 18972.28 | 28-AUG-15:00 | 4950.048 | 3712.536 | 2257.097 | 0 | 8052.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 20279000000 | 18106.221 | 15-SEP-14:00 | 4950.048 | 3712.536 | 2257.097 | 0 | 7186.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 18747200000 | 17073.076 | 06-OCT-15:00 | 4950.048 | 3712.536 | 2257.097 | 0 | 6153.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16272700000 | 15363.457 | 03-NOV-14:30 | 4950.048 | 3712.536 | 2257.097 | 0 | 4443.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15175000000 | 14365.41 | 19-DEC-15:30 | 4950.048 | 3712.536 | 2257.097 | 0 | 3445.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 221970000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13966100000 | 14365.41 |  | 4950.048 | 3712.536 | 2257.097 | 0 | 3445.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 23505800000 | 19090.726 |  | 4950.048 | 3712.536 | 2257.097 | 0 | 8171.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7645.1 | 261.59 | 0 | 7906.69
Cost per Total Building Area ($/m2) | 14.96 | 0.51 | 0 | 15.47
Cost per Net Conditioned Building Area ($/m2) | 14.96 | 0.51 | 0 | 15.47

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 251.55 | 492.11 | 492.11
Net Site Energy | 251.55 | 492.11 | 492.11
Total Source Energy | 747.65 | 1462.66 | 1462.66
Net Source Energy | 747.65 | 1462.66 | 1462.66
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12.32 | 0 | 0 | 0 | 0
Cooling | 50.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 40.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.86 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 228.37 | 23.18 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 16.73 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7887.35 | 6135.18 | 1752.17 | 0.78 | 3.96
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6695.16 | 5136.34 | 1558.81 | 0.77 | 3.93
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6193.82 | 4896.96 | 1296.85 | 0.79 | 4.01
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7124.75 | 5525.05 | 1599.71 | 0.78 | 3.96
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7446.54 | 5915.08 | 1531.46 | 0.79 | 4.02
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11621.42 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 9452.57 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8845.56 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 10191.27 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 10580.99 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 521.39 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 428.96 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 424.52 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 467.75 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 515.65 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3253.2368 | 5.3131 | 17.0858 | 0 | 0 | 126203.0088 | 1364.604
February | 2900.267 | 4.7699 | 15.473 | 0 | 0 | 114292.1484 | 1219.9161
March | 3559.403 | 5.9445 | 19.6448 | 0 | 0.0001 | 145111.863 | 1506.323
April | 3470.4597 | 5.828 | 19.3855 | 0 | 0.0001 | 143198.1557 | 1471.9201
May | 4038.7325 | 6.7891 | 22.6089 | 0 | 0.0001 | 167009.3499 | 1713.6271
June | 4722.1587 | 7.9461 | 26.4939 | 0 | 0.0001 | 195707.2563 | 2004.4297
July | 4759.6376 | 8.0093 | 26.7046 | 0 | 0.0001 | 197263.7091 | 2020.3445
August | 4974.0136 | 8.3711 | 27.9152 | 0 | 0.0001 | 206206.6063 | 2111.4514
September | 4284.3038 | 7.2059 | 24.0126 | 0 | 0.0001 | 177377.8764 | 1818.2266
October | 3725.3523 | 6.2584 | 20.8262 | 0 | 0.0001 | 153840.0957 | 1580.2627
November | 3232.0538 | 5.4132 | 17.949 | 0 | 0 | 132586.1451 | 1369.3403
December | 3322.8352 | 5.3641 | 16.9985 | 0 | 0 | 125554.993 | 1387.4681
Annual Sum or Average | 46242.454 | 77.2127 | 255.0982 | 0 | 0.0007 | 1884350 | 19567.9137
Minimum of Months | 2900.267 | 4.7699 | 15.473 | 0 | 0 | 114292.1484 | 1219.9161
Maximum of Months | 4974.0136 | 8.3711 | 27.9152 | 0 | 0.0001 | 206206.6063 | 2111.4514
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15295100000 | 12966.665 | 27-JAN-14:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 1945.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13851500000 | 13726.053 | 28-FEB-16:30 | 4950.048 | 3712.536 | 2358.272 | 0 | 2705.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17586700000 | 15793.518 | 17-MAR-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 4772.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 17354800000 | 15977.546 | 26-APR-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 4956.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 20240600000 | 18551.693 | 30-MAY-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 7530.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23718600000 | 21174.034 | 28-JUN-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 10153.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 23907200000 | 20897.614 | 11-JUL-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 9876.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 24991000000 | 20871.118 | 01-AUG-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 9850.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21497200000 | 19372.407 | 11-SEP-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 8351.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 18644500000 | 16620.498 | 02-OCT-15:20 | 4950.048 | 3712.536 | 2358.272 | 0 | 5599.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16068700000 | 15000.977 | 13-NOV-15:39 | 4950.048 | 3712.536 | 2358.272 | 0 | 3980.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15216500000 | 12700.869 | 11-DEC-15:00 | 4950.048 | 3712.536 | 2358.272 | 0 | 1680.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 228372000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13851500000 | 12700.869 |  | 4950.048 | 3712.536 | 2358.272 | 0 | 1680.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 24991000000 | 21174.034 |  | 4950.048 | 3712.536 | 2358.272 | 0 | 10153.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8269.42 | 193.8 | 0 | 8463.22
Cost per Total Building Area ($/m2) | 16.18 | 0.38 | 0 | 16.56
Cost per Net Conditioned Building Area ($/m2) | 16.18 | 0.38 | 0 | 16.56

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 238.52 | 466.63 | 466.63
Net Site Energy | 238.52 | 466.63 | 466.63
Total Source Energy | 709.8 | 1388.62 | 1388.62
Net Source Energy | 709.8 | 1388.62 | 1388.62
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 29.28 | 0 | 0 | 0 | 0
Cooling | 24.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 35.47 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.47 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 197.77 | 40.75 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 16.73 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8664.18 | 6698.09 | 1966.09 | 0.77 | 3.95
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6666.04 | 4960.14 | 1705.9 | 0.74 | 3.85
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5306.44 | 4056.15 | 1250.29 | 0.76 | 3.92
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6887.46 | 5163.01 | 1724.45 | 0.75 | 3.87
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5736.7 | 4373.49 | 1363.2 | 0.76 | 3.91
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13442.51 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 9610.92 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 7634.21 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 10001.98 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 8114.34 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 564.86 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.77 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 337.16 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 418.24 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 362.3 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3469.6211 | 6.1483 | 14.7158 | 0 | 0.0001 | 26171.5808 | 1477.799
February | 3023.2398 | 5.3979 | 13.0215 | 0 | 0 | 23158.7125 | 1291.4217
March | 3172.0607 | 5.9645 | 15.1375 | 0 | 0.0001 | 26925.2553 | 1382.7823
April | 2986.5019 | 5.6831 | 14.5832 | 0 | 0.0001 | 25939.8994 | 1308.1318
May | 3417.4072 | 6.546 | 16.8975 | 0 | 0.0001 | 30056.9045 | 1500.8347
June | 3769.6827 | 7.2299 | 18.6841 | 0 | 0.0001 | 33234.972 | 1656.3883
July | 3754.7669 | 7.201 | 18.6086 | 0 | 0.0001 | 33100.5649 | 1649.8036
August | 4040.4925 | 7.7519 | 20.0393 | 0 | 0.0001 | 35645.4364 | 1775.6237
September | 3537.966 | 6.7832 | 17.5244 | 0 | 0.0001 | 31172.0373 | 1554.3607
October | 3099.0849 | 5.9234 | 15.2605 | 0 | 0.0001 | 27144.9104 | 1359.8481
November | 2992.7307 | 5.5931 | 14.1143 | 0 | 0.0001 | 25104.8187 | 1301.4523
December | 3266.6975 | 5.8694 | 14.2508 | 0 | 0.0001 | 25345.3722 | 1398.8221
Annual Sum or Average | 40530.2519 | 76.0916 | 192.8375 | 0 | 0.0007 | 343000.4644 | 17657.2685
Minimum of Months | 2986.5019 | 5.3979 | 13.0215 | 0 | 0 | 23158.7125 | 1291.4217
Maximum of Months | 4040.4925 | 7.7519 | 20.0393 | 0 | 0.0001 | 35645.4364 | 1775.6237
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15090300000 | 11534.387 | 23-JAN-16:40 | 4950.048 | 3712.536 | 2080.337 | 0 | 791.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13353100000 | 11401.688 | 22-FEB-15:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 658.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15524800000 | 12622.491 | 28-MAR-15:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 1879.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14956700000 | 14245.822 | 14-APR-15:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 3502.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 17330500000 | 15780.427 | 15-MAY-14:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 5037.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 19163000000 | 16722.259 | 19-JUN-14:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 5979.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 19085500000 | 18052.649 | 03-JUL-15:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 7309.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 20552800000 | 16732.758 | 17-AUG-15:39 | 4950.048 | 3712.536 | 2080.337 | 0 | 5989.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17973500000 | 16191.286 | 11-SEP-13:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 5448.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15651500000 | 14675.81 | 12-OCT-15:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 3932.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14475200000 | 12618.292 | 22-NOV-14:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 1875.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 14613900000 | 11220.992 | 05-DEC-14:00 | 4950.048 | 3712.536 | 2080.337 | 0 | 478.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 197771000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13353100000 | 11220.992 |  | 4950.048 | 3712.536 | 2080.337 | 0 | 478.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20552800000 | 18052.649 |  | 4950.048 | 3712.536 | 2080.337 | 0 | 7309.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6483.73 | 400.38 | 0 | 6884.12
Cost per Total Building Area ($/m2) | 12.68 | 0.78 | 0 | 13.47
Cost per Net Conditioned Building Area ($/m2) | 12.68 | 0.78 | 0 | 13.47

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 194.05 | 379.63 | 379.63
Net Site Energy | 194.05 | 379.63 | 379.63
Total Source Energy | 571.68 | 1118.41 | 1118.41
Net Source Energy | 571.68 | 1118.41 | 1118.41
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3.03 | 0 | 0 | 0 | 0
Cooling | 13.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 28.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.4 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 179.62 | 14.43 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 16.73 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7027.68 | 5612.7 | 1414.99 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5080.32 | 3865.66 | 1214.66 | 0.76 | 3.91
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4026.28 | 3215.61 | 810.67 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4919.84 | 3725.57 | 1194.28 | 0.76 | 3.9
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4450.83 | 3543.23 | 907.61 | 0.8 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11122.79 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 7368.55 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 6200.55 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 7101.57 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 6744.96 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 492.43 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.28 | 319.43 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.24 | 282.12 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.26 | 305.91 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 309.69 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1347.8396 | 1.1588 | 11.6169 | 0 | 0 | 70091.0913 | 501.9321
February | 1196.4326 | 1.0278 | 10.4527 | 0 | 0 | 63067.6172 | 445.9781
March | 1371.8621 | 1.1778 | 12.1196 | 0 | 0 | 73125.3647 | 511.7801
April | 1259.0246 | 1.0804 | 11.2118 | 0 | 0 | 67648.6051 | 469.9574
May | 1349.0521 | 1.1572 | 12.0867 | 0 | 0 | 72927.8277 | 503.7853
June | 1362.4886 | 1.1686 | 12.2412 | 0 | 0 | 73859.6903 | 508.9069
July | 1416.9448 | 1.2152 | 12.7533 | 0 | 0 | 76950.1452 | 529.3169
August | 1573.5476 | 1.3492 | 14.2044 | 0 | 0 | 85705.4967 | 587.9445
September | 1421.4713 | 1.219 | 12.8044 | 0 | 0 | 77258.2467 | 531.0393
October | 1396.2284 | 1.1976 | 12.535 | 0 | 0 | 75632.3445 | 521.4807
November | 1305.777 | 1.1203 | 11.6601 | 0 | 0 | 70353.5831 | 487.5062
December | 1318.7698 | 1.133 | 11.5054 | 0 | 0 | 69419.0769 | 491.5309
Annual Sum or Average | 16319.4386 | 14.0049 | 145.1915 | 0 | 0.0001 | 876039.0893 | 6091.1585
Minimum of Months | 1196.4326 | 1.0278 | 10.4527 | 0 | 0 | 63067.6172 | 445.9781
Maximum of Months | 1573.5476 | 1.3492 | 14.2044 | 0 | 0 | 85705.4967 | 587.9445
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 14371300000 | 12500.178 | 26-JAN-13:09 | 4950.048 | 3712.536 | 1709.58 | 0 | 2128.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 12931200000 | 12185.265 | 13-FEB-11:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 1813.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 14993400000 | 12167.218 | 31-MAR-14:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 1795.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 13870500000 | 12924.832 | 11-APR-15:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 2552.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 14952900000 | 13054.471 | 30-MAY-08:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 2682.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 15144000000 | 13114.969 | 30-JUN-15:50 | 4950.048 | 3712.536 | 1709.58 | 0 | 2742.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 15777700000 | 13804.383 | 10-JUL-15:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 3432.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 17572800000 | 14403.483 | 08-AUG-09:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 4031.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 15840800000 | 14440.069 | 25-SEP-14:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 4067.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15507500000 | 13485.741 | 19-OCT-10:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 3113.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14425100000 | 12853.208 | 09-NOV-16:00 | 4950.048 | 3712.536 | 1709.58 | 0 | 1515.043 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 14233500000 | 12622.668 | 19-DEC-13:09 | 4950.048 | 3712.536 | 1709.58 | 0 | 2250.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 179621000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 12931200000 | 12167.218 |  | 4950.048 | 3712.536 | 1709.58 | 0 | 1515.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 17572800000 | 14440.069 |  | 4950.048 | 3712.536 | 1709.58 | 0 | 4067.905 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6433.81 | 122.53 | 0 | 6556.34
Cost per Total Building Area ($/m2) | 12.59 | 0.24 | 0 | 12.83
Cost per Net Conditioned Building Area ($/m2) | 12.59 | 0.24 | 0 | 12.83

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 225.61 | 441.37 | 441.37
Net Site Energy | 225.61 | 441.37 | 441.37
Total Source Energy | 739.1 | 1445.93 | 1445.93
Net Source Energy | 739.1 | 1445.93 | 1445.93
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16.19 | 0 | 0 | 0 | 0
Cooling | 27.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 32.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.13 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 198.28 | 27.33 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 16.73 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7276.37 | 5811.31 | 1465.06 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5443.22 | 4300.17 | 1143.05 | 0.79 | 4.01
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4638.96 | 3704.93 | 934.03 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5588 | 4431.38 | 1156.62 | 0.79 | 4.02
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5090.49 | 4065.55 | 1024.94 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11380.13 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 8370.35 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 6872.4 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 8610.55 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 7451.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 509.85 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 372.43 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.28 | 325.05 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 385.55 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 356.69 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3629.5269 | 5.6732 | 22.3712 | 0 | 0 | 111561.4116 | 1503.4172
February | 3068.1349 | 4.926 | 20.1351 | 0 | 0 | 100415.7642 | 1284.4154
March | 3538.0512 | 5.6931 | 23.3377 | 0 | 0 | 116387.6156 | 1482.4488
April | 3394.5674 | 5.5304 | 23.032 | 0 | 0 | 114865.6607 | 1429.4145
May | 3868.3355 | 6.308 | 26.3013 | 0 | 0 | 131170.6414 | 1629.5191
June | 4380.5947 | 7.1502 | 29.8487 | 0 | 0.0001 | 148862.5192 | 1846.0189
July | 4420.1414 | 7.215 | 30.12 | 0 | 0.0001 | 150215.6668 | 1862.7047
August | 4700.8186 | 7.6747 | 32.0475 | 0 | 0.0001 | 159828.6132 | 1981.1504
September | 4000.5753 | 6.5273 | 27.2344 | 0 | 0.0001 | 135824.0428 | 1685.5996
October | 3641.0773 | 5.9332 | 24.7162 | 0 | 0 | 123265.3556 | 1533.3462
November | 3298.3039 | 5.3266 | 21.938 | 0 | 0 | 109407.7258 | 1384.0034
December | 3482.4692 | 5.4897 | 21.8999 | 0 | 0 | 109212.8744 | 1447.3145
Annual Sum or Average | 45422.5961 | 73.4474 | 302.982 | 0 | 0.0006 | 1511020 | 19069.3527
Minimum of Months | 3068.1349 | 4.926 | 20.1351 | 0 | 0 | 100415.7642 | 1284.4154
Maximum of Months | 4700.8186 | 7.6747 | 32.0475 | 0 | 0.0001 | 159828.6132 | 1981.1504
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 14639500000 | 11708.09 | 18-JAN-16:49 | 4950.048 | 3712.536 | 1949.577 | 0 | 129.929 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13177000000 | 11518.955 | 08-FEB-15:20 | 4950.048 | 3712.536 | 1949.577 | 0 | 906.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15272900000 | 12390.294 | 31-MAR-15:00 | 4950.048 | 3712.536 | 1949.577 | 0 | 1778.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15073100000 | 14388.315 | 21-APR-15:39 | 4950.048 | 3712.536 | 1949.577 | 0 | 3776.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 17212700000 | 15646.178 | 31-MAY-15:00 | 4950.048 | 3712.536 | 1949.577 | 0 | 5034.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 19534300000 | 18068.633 | 27-JUN-15:00 | 4950.048 | 3712.536 | 1949.577 | 0 | 7456.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 19711900000 | 17812.455 | 24-JUL-15:00 | 4950.048 | 3712.536 | 1949.577 | 0 | 7200.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 20973400000 | 17361.416 | 04-AUG-15:00 | 4950.048 | 3712.536 | 1949.577 | 0 | 6749.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17823400000 | 16900.406 | 01-SEP-14:00 | 4950.048 | 3712.536 | 1949.577 | 0 | 6288.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16175400000 | 14676.141 | 06-OCT-13:00 | 4950.048 | 3712.536 | 1949.577 | 0 | 4063.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14356900000 | 12726.064 | 10-NOV-16:40 | 4950.048 | 3712.536 | 1949.577 | 0 | 1147.903 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 14331400000 | 12019.21 | 05-DEC-16:30 | 4950.048 | 3712.536 | 1949.577 | 0 | 441.048 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 198282000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13177000000 | 11518.955 |  | 4950.048 | 3712.536 | 1949.577 | 0 | 129.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20973400000 | 18068.633 |  | 4950.048 | 3712.536 | 1949.577 | 0 | 7456.472 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5647.75 | 213.93 | 0 | 5861.68
Cost per Total Building Area ($/m2) | 11.05 | 0.42 | 0 | 11.47
Cost per Net Conditioned Building Area ($/m2) | 11.05 | 0.42 | 0 | 11.47

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 202.38 | 395.92 | 395.92
Net Site Energy | 202.38 | 395.92 | 395.92
Total Source Energy | 563.9 | 1103.18 | 1103.18
Net Source Energy | 563.9 | 1103.18 | 1103.18
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 19.46 | 0 | 0 | 0 | 0
Cooling | 5.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 28.4 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.73 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 171.19 | 31.19 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 16.73 | 5.83 | 0.39 | 0.223
Non-North Total or Average |  |  | 42.95 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4407.02 | 3519.69 | 887.33 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7512.63 | 6000 | 1512.63 | 0.8 | 4.04
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3917.77 | 3128.95 | 788.82 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3235.88 | 2540.37 | 695.51 | 0.79 | 3.99
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5238 | 4183.36 | 1054.64 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 7851.76 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 11744.71 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 6219.05 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 5640.85 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 8052.03 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 308.8 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 526.41 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.24 | 274.52 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.19 | 218.36 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 367.03 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1582.7754 | 1.3725 | 11.5389 | 0 | 0 | 69612.9427 | 583.0058
February | 1271.024 | 1.0955 | 10.4634 | 0 | 0 | 63129.9667 | 471.827
March | 1484.3764 | 1.2807 | 11.9886 | 0 | 0 | 72331.1986 | 550.3219
April | 1298.6782 | 1.1177 | 10.9823 | 0 | 0 | 66261.6181 | 482.9812
May | 1330.493 | 1.1427 | 11.6794 | 0 | 0 | 70469.0978 | 496.1192
June | 1309.2884 | 1.1237 | 11.6329 | 0 | 0 | 70189.3176 | 488.6385
July | 1279.9018 | 1.0982 | 11.4207 | 0 | 0 | 68908.8089 | 477.8202
August | 1385.9749 | 1.1891 | 12.3815 | 0 | 0 | 74705.9772 | 517.4636
September | 1316.5575 | 1.1295 | 11.7665 | 0 | 0 | 70995.5444 | 491.5619
October | 1345.3389 | 1.1549 | 11.8968 | 0 | 0 | 71781.0235 | 501.9206
November | 1335.7389 | 1.1495 | 11.3136 | 0 | 0 | 68260.6797 | 496.8188
December | 1521.9629 | 1.3185 | 11.3187 | 0 | 0 | 68285.8289 | 561.2869
Annual Sum or Average | 16462.11 | 14.1725 | 138.3832 | 0 | 0.0001 | 834932.0042 | 6119.7656
Minimum of Months | 1271.024 | 1.0955 | 10.4634 | 0 | 0 | 63129.9667 | 471.827
Maximum of Months | 1582.7754 | 1.3725 | 12.3815 | 0 | 0 | 74705.9772 | 583.0058
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 14273300000 | 11323.694 | 02-JAN-16:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 12944000000 | 12109.465 | 15-FEB-15:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 1751.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 14830600000 | 11261.136 | 01-MAR-14:30 | 4950.048 | 3712.536 | 1695.109 | 0 | 903.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 13586100000 | 12236.279 | 13-APR-14:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 1878.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 14448800000 | 12410.102 | 17-MAY-13:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 2052.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 14391400000 | 12858.402 | 16-JUN-15:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 2500.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 14128900000 | 13773.641 | 03-JUL-12:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 3415.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 15317500000 | 13092.473 | 15-AUG-12:09 | 4950.048 | 3712.536 | 1695.109 | 0 | 2734.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 14556800000 | 14821.116 | 28-SEP-14:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 4463.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 14717800000 | 12856.08 | 31-OCT-13:09 | 4950.048 | 3712.536 | 1695.109 | 0 | 2498.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 13996000000 | 11672.284 | 14-NOV-16:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 348.59 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 14001200000 | 11327.676 | 07-DEC-16:00 | 4950.048 | 3712.536 | 1695.109 | 0 | 3.982 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 171192000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 12944000000 | 11261.136 |  | 4950.048 | 3712.536 | 1695.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 15317500000 | 14821.116 |  | 4950.048 | 3712.536 | 1695.109 | 0 | 4463.422 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7765.93 | 268.66 | 0 | 8034.59
Cost per Total Building Area ($/m2) | 15.19 | 0.53 | 0 | 15.72
Cost per Net Conditioned Building Area ($/m2) | 15.19 | 0.53 | 0 | 15.72

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 268.02 | 524.33 | 524.33
Net Site Energy | 268.02 | 524.33 | 524.33
Total Source Energy | 782.08 | 1530.03 | 1530.03
Net Source Energy | 782.08 | 1530.03 | 1530.03
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 59.22 | 0 | 0 | 0 | 0
Cooling | 20.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 39.32 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.77 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 197.02 | 70.99 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9064.13 | 7075.86 | 1988.27 | 0.78 | 3.97
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7035.85 | 5220.91 | 1814.94 | 0.74 | 3.85
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5754.04 | 4431.04 | 1323 | 0.77 | 3.94
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7177.08 | 5342.46 | 1834.62 | 0.74 | 3.85
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6467.65 | 4941.36 | 1526.29 | 0.76 | 3.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15008.61 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 10575.65 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8727.13 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 10803.7 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 9489.14 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 604.01 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 417.09 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 371.84 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 428.65 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 410.49 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3630.983 | 6.174 | 15.9071 | 0 | 0.0001 | 989.0268 | 1519.8582
February | 3070.0137 | 5.3524 | 14.1796 | 0 | 0.0001 | 881.6747 | 1297.1379
March | 3011.0893 | 5.6007 | 15.8459 | 0 | 0.0001 | 985.4181 | 1304.3422
April | 2558.1568 | 4.9446 | 14.4917 | 0 | 0.0001 | 901.2626 | 1125.1864
May | 2741.6383 | 5.4147 | 16.1684 | 0 | 0.0001 | 1005.5769 | 1216.4433
June | 3216.7975 | 6.3775 | 19.1049 | 0 | 0.0001 | 1188.2183 | 1429.4925
July | 3283.3875 | 6.5108 | 19.5075 | 0 | 0.0001 | 1213.261 | 1459.2026
August | 3568.2326 | 7.0794 | 21.2206 | 0 | 0.0001 | 1319.8078 | 1586.1372
September | 2874.7778 | 5.6932 | 17.0392 | 0 | 0.0001 | 1059.7438 | 1276.9353
October | 2742.1813 | 5.3624 | 15.8768 | 0 | 0.0001 | 987.4239 | 1211.802
November | 2755.8962 | 5.2114 | 14.9743 | 0 | 0.0001 | 931.2426 | 1201.603
December | 3365.4342 | 5.8569 | 15.4863 | 0 | 0.0001 | 962.9207 | 1421.0021
Annual Sum or Average | 36818.5882 | 69.578 | 199.8024 | 0 | 0.0008 | 12425.5771 | 16049.1427
Minimum of Months | 2558.1568 | 4.9446 | 14.1796 | 0 | 0.0001 | 881.6747 | 1125.1864
Maximum of Months | 3630.983 | 7.0794 | 21.2206 | 0 | 0.0001 | 1319.8078 | 1586.1372
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15682400000 | 11860.666 | 02-JAN-16:49 | 4950.048 | 3712.536 | 2232.082 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13980200000 | 10944.987 | 16-FEB-13:20 | 4950.048 | 3712.536 | 2232.082 | 0 | 50.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15625200000 | 12577.126 | 10-MAR-10:00 | 4950.048 | 3712.536 | 2232.082 | 0 | 1682.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14290800000 | 13265.694 | 04-APR-15:00 | 4950.048 | 3712.536 | 2232.082 | 0 | 2371.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15944800000 | 14986.686 | 31-MAY-15:00 | 4950.048 | 3712.536 | 2232.082 | 0 | 4092.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 18840900000 | 17721.173 | 30-JUN-15:00 | 4950.048 | 3712.536 | 2232.082 | 0 | 6826.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 19238000000 | 18348.524 | 25-JUL-12:00 | 4950.048 | 3712.536 | 2232.082 | 0 | 7453.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 20927400000 | 18191.267 | 09-AUG-14:00 | 4950.048 | 3712.536 | 2232.082 | 0 | 7296.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 16803700000 | 16010.851 | 08-SEP-15:20 | 4950.048 | 3712.536 | 2232.082 | 0 | 5116.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15657000000 | 14606.458 | 12-OCT-14:50 | 4950.048 | 3712.536 | 2232.082 | 0 | 3711.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14766200000 | 13498.112 | 03-NOV-13:00 | 4950.048 | 3712.536 | 2232.082 | 0 | 2603.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15268500000 | 11860.666 | 01-DEC-16:40 | 4950.048 | 3712.536 | 2232.082 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 197025000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13980200000 | 10944.987 |  | 4950.048 | 3712.536 | 2232.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20927400000 | 18348.524 |  | 4950.048 | 3712.536 | 2232.082 | 0 | 7453.857 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4180.22 | 689.88 | 0 | 4870.1
Cost per Total Building Area ($/m2) | 8.18 | 1.35 | 0 | 9.53
Cost per Net Conditioned Building Area ($/m2) | 8.18 | 1.35 | 0 | 9.53

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 238.09 | 465.79 | 465.79
Net Site Energy | 238.09 | 465.79 | 465.79
Total Source Energy | 684.54 | 1339.2 | 1339.2
Net Source Energy | 684.54 | 1339.2 | 1339.2
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 35.66 | 0 | 0 | 0 | 0
Cooling | 17.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 35.99 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.72 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 190.72 | 47.37 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7862.46 | 6279.4 | 1583.07 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5591.55 | 4465.72 | 1125.83 | 0.8 | 4.04
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4889.36 | 3904.92 | 984.45 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5398.04 | 4311.17 | 1086.87 | 0.8 | 4.04
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5986.07 | 4780.81 | 1205.26 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11386.14 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 8211.68 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 6667.92 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 7990.57 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 7921.03 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 550.92 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 391.8 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 342.6 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 378.24 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 419.44 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4559.6734 | 7.5389 | 18.4221 | 0 | 0.0001 | 19153.1884 | 1911.6153
February | 3901.4203 | 6.5396 | 16.2445 | 0 | 0.0001 | 16889.8532 | 1644.3806
March | 4357.6647 | 7.4082 | 18.7066 | 0 | 0.0001 | 19450.4427 | 1846.8714
April | 3871.3954 | 6.7042 | 17.2829 | 0 | 0.0001 | 17971.0313 | 1652.8104
May | 4414.4337 | 7.6993 | 20.0032 | 0 | 0.0001 | 20799.9687 | 1890.0137
June | 4728.7192 | 8.255 | 21.4682 | 0 | 0.0001 | 22323.3354 | 2025.3133
July | 4818.5213 | 8.4126 | 21.8808 | 0 | 0.0001 | 22752.3867 | 2063.8646
August | 5104.6254 | 8.9139 | 23.1895 | 0 | 0.0001 | 24113.2143 | 2186.5805
September | 4409.3193 | 7.6948 | 20.0042 | 0 | 0.0001 | 20801.0339 | 1888.262
October | 4105.1029 | 7.1229 | 18.4019 | 0 | 0.0001 | 19134.6202 | 1753.9573
November | 4130.1324 | 7.0166 | 17.7039 | 0 | 0.0001 | 18407.9126 | 1749.9694
December | 4493.4451 | 7.4097 | 18.0479 | 0 | 0.0001 | 18764.0107 | 1881.9174
Annual Sum or Average | 52894.4531 | 90.7156 | 231.3556 | 0 | 0.0009 | 240560.9982 | 22495.5557
Minimum of Months | 3871.3954 | 6.5396 | 16.2445 | 0 | 0.0001 | 16889.8532 | 1644.3806
Maximum of Months | 5104.6254 | 8.9139 | 23.1895 | 0 | 0.0001 | 24113.2143 | 2186.5805
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15184900000 | 11276.218 | 27-JAN-14:20 | 4950.048 | 3712.536 | 2083.004 | 0 | 530.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13390500000 | 11856.31 | 14-FEB-15:50 | 4950.048 | 3712.536 | 2083.004 | 0 | 1110.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15420500000 | 11948.437 | 02-MAR-15:09 | 4950.048 | 3712.536 | 2083.004 | 0 | 1202.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14247700000 | 13229.362 | 21-APR-15:00 | 4950.048 | 3712.536 | 2083.004 | 0 | 2483.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16490500000 | 14471.258 | 31-MAY-15:00 | 4950.048 | 3712.536 | 2083.004 | 0 | 3725.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 17698200000 | 15680.182 | 29-JUN-15:30 | 4950.048 | 3712.536 | 2083.004 | 0 | 4934.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 18038400000 | 16161.931 | 03-JUL-15:30 | 4950.048 | 3712.536 | 2083.004 | 0 | 5416.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 19117200000 | 16182.226 | 01-AUG-15:20 | 4950.048 | 3712.536 | 2083.004 | 0 | 5436.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 16491300000 | 14606.041 | 29-SEP-14:39 | 4950.048 | 3712.536 | 2083.004 | 0 | 3860.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15170200000 | 13376.499 | 11-OCT-15:00 | 4950.048 | 3712.536 | 2083.004 | 0 | 2630.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14594000000 | 11843.766 | 08-NOV-14:00 | 4950.048 | 3712.536 | 2083.004 | 0 | 1098.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 14876300000 | 11769.309 | 05-DEC-16:49 | 4950.048 | 3712.536 | 2083.004 | 0 | 57.721 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 190720000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13390500000 | 11276.218 |  | 4950.048 | 3712.536 | 2083.004 | 0 | 57.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 19117200000 | 16182.226 |  | 4950.048 | 3712.536 | 2083.004 | 0 | 5436.638 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4001.33 | 328.4 | 0 | 4329.74
Cost per Total Building Area ($/m2) | 7.83 | 0.64 | 0 | 8.47
Cost per Net Conditioned Building Area ($/m2) | 7.83 | 0.64 | 0 | 8.47

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 240.96 | 471.39 | 471.39
Net Site Energy | 240.96 | 471.39 | 471.39
Total Source Energy | 375.02 | 733.67 | 733.67
Net Source Energy | 375.02 | 733.67 | 733.67
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 56.87 | 0 | 0 | 0 | 0
Cooling | 4.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 30.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.93 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 172.15 | 68.81 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.193 | 0.203 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5654.63 | 4516.1 | 1138.53 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6258.5 | 4998.39 | 1260.12 | 0.8 | 4.04
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4202.06 | 3356 | 846.06 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4249.87 | 3323.49 | 926.38 | 0.78 | 3.98
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5006.32 | 3998.32 | 1008 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 10191.22 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 10427.06 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 6855.73 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 7413.2 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 7957.07 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 396.22 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 438.53 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 294.44 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 284.32 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 350.79 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1401.7435 | 1.7662 | 3.1586 | 0 | 0 | 41704.2751 | 538.0299
February | 1082.654 | 1.4177 | 2.7814 | 0 | 0 | 36734.6131 | 421.2881
March | 1175.2974 | 1.5677 | 3.2029 | 0 | 0 | 42305.7251 | 460.4153
April | 901.6514 | 1.2706 | 2.8905 | 0 | 0 | 38190.6157 | 360.4856
May | 787.2967 | 1.1958 | 3.0756 | 0 | 0 | 40647.5188 | 324.0196
June | 753.1891 | 1.1674 | 3.0917 | 0 | 0 | 40862.8626 | 312.4873
July | 755.7788 | 1.177 | 3.1378 | 0 | 0 | 41473.4834 | 314.1577
August | 823.0424 | 1.2843 | 3.4337 | 0 | 0 | 45384.766 | 342.3965
September | 754.458 | 1.1621 | 3.0506 | 0 | 0 | 40319.7331 | 312.2381
October | 863.981 | 1.2621 | 3.0546 | 0 | 0 | 40365.0516 | 350.2033
November | 1143.0758 | 1.509 | 3.0146 | 0 | 0 | 39816.115 | 446.1071
December | 1416.1339 | 1.768 | 3.0869 | 0 | 0 | 40755.2511 | 541.8077
Annual Sum or Average | 11858.3019 | 16.5479 | 36.9789 | 0 | 0.0002 | 488560.0106 | 4723.6363
Minimum of Months | 753.1891 | 1.1621 | 2.7814 | 0 | 0 | 36734.6131 | 312.2381
Maximum of Months | 1416.1339 | 1.768 | 3.4337 | 0 | 0 | 45384.766 | 541.8077
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 14695000000 | 11392.884 | 02-JAN-16:30 | 4950.048 | 3712.536 | 1764.3 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 12943800000 | 10643.774 | 24-FEB-14:09 | 4950.048 | 3712.536 | 1764.3 | 0 | 216.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 14906900000 | 11397.899 | 29-MAR-15:50 | 4950.048 | 3712.536 | 1764.3 | 0 | 971.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 13456900000 | 11102.159 | 19-APR-15:00 | 4950.048 | 3712.536 | 1764.3 | 0 | 675.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 14322600000 | 12534.118 | 05-MAY-15:00 | 4950.048 | 3712.536 | 1764.3 | 0 | 2107.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 14398500000 | 13159.637 | 28-JUN-15:20 | 4950.048 | 3712.536 | 1764.3 | 0 | 2732.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 14613600000 | 14058.521 | 24-JUL-14:00 | 4950.048 | 3712.536 | 1764.3 | 0 | 3631.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 15991800000 | 13864.56 | 07-AUG-15:20 | 4950.048 | 3712.536 | 1764.3 | 0 | 3437.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 14207100000 | 13586.144 | 01-SEP-15:00 | 4950.048 | 3712.536 | 1764.3 | 0 | 3159.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 14223100000 | 11604.576 | 03-OCT-14:50 | 4950.048 | 3712.536 | 1764.3 | 0 | 1177.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14029600000 | 11392.884 | 06-NOV-16:49 | 4950.048 | 3712.536 | 1764.3 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 14360600000 | 11392.884 | 01-DEC-16:19 | 4950.048 | 3712.536 | 1764.3 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 172149000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 12943800000 | 10643.774 |  | 4950.048 | 3712.536 | 1764.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 15991800000 | 14058.521 |  | 4950.048 | 3712.536 | 1764.3 | 0 | 3631.636 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 3514.87 | 580.43 | 0 | 4095.3
Cost per Total Building Area ($/m2) | 6.88 | 1.14 | 0 | 8.01
Cost per Net Conditioned Building Area ($/m2) | 6.88 | 1.14 | 0 | 8.01

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 297 | 581.04 | 581.04
Net Site Energy | 297 | 581.04 | 581.04
Total Source Energy | 801.08 | 1567.19 | 1567.19
Net Source Energy | 801.08 | 1567.19 | 1567.19
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 90.69 | 0 | 0 | 0 | 0
Cooling | 15.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 41.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.04 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 194.28 | 102.73 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8560.76 | 6701.91 | 1858.86 | 0.78 | 3.98
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7961.01 | 5876.5 | 2084.51 | 0.74 | 3.84
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5431.23 | 4233.5 | 1197.73 | 0.78 | 3.97
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7678.59 | 5671.25 | 2007.34 | 0.74 | 3.84
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6348.36 | 4859.67 | 1488.69 | 0.77 | 3.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15090.59 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 12040.37 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8776 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 11731.73 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 9629.15 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 574.09 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 466.04 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 360.71 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 450.12 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 404.71 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6828.5219 | 11.2087 | 30.0644 | 0 | 0.0001 | 6919.5837 | 2842.411
February | 5852.7119 | 9.7692 | 26.7411 | 0 | 0.0001 | 6154.9598 | 2451.7425
March | 6141.9304 | 10.5414 | 29.7971 | 0 | 0.0001 | 6858.801 | 2600.5626
April | 5092.497 | 9.0659 | 26.658 | 0 | 0.0001 | 6136.6997 | 2187.355
May | 5457.6967 | 9.87 | 29.4929 | 0 | 0.0001 | 6789.5174 | 2358.9419
June | 6239.0519 | 11.314 | 33.9007 | 0 | 0.0001 | 7804.2558 | 2699.6179
July | 6378.1811 | 11.5678 | 34.6656 | 0 | 0.0001 | 7980.3542 | 2759.9617
August | 6695.5348 | 12.145 | 36.4002 | 0 | 0.0001 | 8379.6756 | 2897.4424
September | 5567.8068 | 10.0906 | 30.2166 | 0 | 0.0001 | 6956.1395 | 2408.5858
October | 5334.7401 | 9.5769 | 28.4043 | 0 | 0.0001 | 6538.8087 | 2299.0316
November | 5621.2083 | 9.7537 | 27.9064 | 0 | 0.0001 | 6423.7463 | 2390.2192
December | 6526.1214 | 10.8342 | 29.4635 | 0 | 0.0001 | 6781.462 | 2728.1847
Annual Sum or Average | 71736.0024 | 125.7371 | 363.7108 | 0 | 0.0011 | 83724.0037 | 30624.0564
Minimum of Months | 5092.497 | 9.0659 | 26.658 | 0 | 0.0001 | 6136.6997 | 2187.355
Maximum of Months | 6828.5219 | 12.145 | 36.4002 | 0 | 0.0001 | 8379.6756 | 2897.4424
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16056400000 | 11884.258 | 02-JAN-16:30 | 4950.048 | 3712.536 | 2255.673 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14282100000 | 11884.258 | 01-FEB-16:00 | 4950.048 | 3712.536 | 2255.673 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15915300000 | 11759.543 | 31-MAR-15:30 | 4950.048 | 3712.536 | 2255.673 | 0 | 841.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14239700000 | 12187.149 | 28-APR-15:00 | 4950.048 | 3712.536 | 2255.673 | 0 | 1268.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15754600000 | 14707.926 | 30-MAY-15:00 | 4950.048 | 3712.536 | 2255.673 | 0 | 3789.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 18109200000 | 17004.822 | 08-JUN-12:00 | 4950.048 | 3712.536 | 2255.673 | 0 | 6086.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 18517800000 | 17602.639 | 03-JUL-14:00 | 4950.048 | 3712.536 | 2255.673 | 0 | 6684.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 19444400000 | 17478.897 | 04-AUG-15:00 | 4950.048 | 3712.536 | 2255.673 | 0 | 6560.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 16141200000 | 15504.355 | 06-SEP-10:00 | 4950.048 | 3712.536 | 2255.673 | 0 | 4586.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15172800000 | 13753.702 | 31-OCT-13:30 | 4950.048 | 3712.536 | 2255.673 | 0 | 2835.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14905800000 | 13235.048 | 02-NOV-14:39 | 4950.048 | 3712.536 | 2255.673 | 0 | 2316.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15735900000 | 11884.258 | 01-DEC-16:19 | 4950.048 | 3712.536 | 2255.673 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 194275000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14239700000 | 11759.543 |  | 4950.048 | 3712.536 | 2255.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 19444400000 | 17602.639 |  | 4950.048 | 3712.536 | 2255.673 | 0 | 6684.381 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 3622.26 | 855.86 | 0 | 4478.12
Cost per Total Building Area ($/m2) | 7.09 | 1.67 | 0 | 8.76
Cost per Net Conditioned Building Area ($/m2) | 7.09 | 1.67 | 0 | 8.76

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 260.58 | 509.78 | 509.78
Net Site Energy | 260.58 | 509.78 | 509.78
Total Source Energy | 702.2 | 1373.74 | 1373.74
Net Source Energy | 702.2 | 1373.74 | 1373.74
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 60.93 | 0 | 0 | 0 | 0
Cooling | 10.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 39.4 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.03 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 187.62 | 72.95 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.191 | 0.2 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7405.76 | 5914.65 | 1491.11 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7005.8 | 5595.22 | 1410.58 | 0.8 | 4.04
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4607.25 | 3679.6 | 927.65 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6780.32 | 5415.14 | 1365.18 | 0.8 | 4.04
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5727.58 | 4574.36 | 1153.22 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11612.56 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 10392.27 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 6679.64 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 10135.1 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 7957.47 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 518.92 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 490.9 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.28 | 322.83 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 475.1 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 401.33 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4959.1582 | 8.009 | 19.0058 | 0 | 0.0001 | 19758.7211 | 2060.4255
February | 4272.829 | 6.9803 | 16.807 | 0 | 0.0001 | 17473.3919 | 1783.0903
March | 4616.0877 | 7.7212 | 19.1318 | 0 | 0.0001 | 19891.6965 | 1943.9977
April | 3981.8518 | 6.8176 | 17.3544 | 0 | 0.0001 | 18044.8748 | 1692.3268
May | 4155.8214 | 7.2046 | 18.5951 | 0 | 0.0001 | 19335.5256 | 1775.0094
June | 4348.7652 | 7.5813 | 19.6871 | 0 | 0.0001 | 20471.2597 | 1861.5622
July | 4594.0612 | 8.0173 | 20.8429 | 0 | 0.0001 | 21673.1528 | 1967.3869
August | 4917.5714 | 8.5841 | 22.3228 | 0 | 0.0001 | 23212.0136 | 2106.1491
September | 4131.8736 | 7.1985 | 18.6798 | 0 | 0.0001 | 19423.7427 | 1768.2563
October | 4155.5386 | 7.1715 | 18.4174 | 0 | 0.0001 | 19150.5125 | 1771.6906
November | 4365.8358 | 7.2951 | 18.0541 | 0 | 0.0001 | 18771.1283 | 1837.8735
December | 4908.7939 | 7.9081 | 18.7071 | 0 | 0.0001 | 19447.9984 | 2037.5842
Annual Sum or Average | 53408.1877 | 90.4886 | 227.6052 | 0 | 0.0009 | 236654.018 | 22605.3525
Minimum of Months | 3981.8518 | 6.8176 | 16.807 | 0 | 0.0001 | 17473.3919 | 1692.3268
Maximum of Months | 4959.1582 | 8.5841 | 22.3228 | 0 | 0.0001 | 23212.0136 | 2106.1491
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15665000000 | 11837.66 | 02-JAN-16:49 | 4950.048 | 3712.536 | 2209.075 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13853100000 | 11268.088 | 07-FEB-14:30 | 4950.048 | 3712.536 | 2209.075 | 0 | 396.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15770400000 | 12155.885 | 30-MAR-15:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 1284.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14306200000 | 12914.563 | 26-APR-15:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 2042.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15329400000 | 13820.726 | 23-MAY-15:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 2949.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 16229900000 | 14868.863 | 27-JUN-15:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 3997.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 17182700000 | 15803.27 | 19-JUL-12:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 4931.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 18402800000 | 15919.903 | 30-AUG-13:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 5048.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 15399400000 | 14263.742 | 01-SEP-15:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 3392.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15182800000 | 13542.371 | 05-OCT-14:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 2670.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 14882000000 | 11895.384 | 10-NOV-16:49 | 4950.048 | 3712.536 | 2209.075 | 0 | 57.724 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15418600000 | 11843.545 | 04-DEC-16:00 | 4950.048 | 3712.536 | 2209.075 | 0 | 5.885 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 187622000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13853100000 | 11268.088 |  | 4950.048 | 3712.536 | 2209.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 18402800000 | 15919.903 |  | 4950.048 | 3712.536 | 2209.075 | 0 | 5048.244 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 3937.7 | 504.48 | 0 | 4442.18
Cost per Total Building Area ($/m2) | 7.7 | 0.99 | 0 | 8.69
Cost per Net Conditioned Building Area ($/m2) | 7.7 | 0.99 | 0 | 8.69

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 330.65 | 646.87 | 646.87
Net Site Energy | 330.65 | 646.87 | 646.87
Total Source Energy | 817.94 | 1600.18 | 1600.18
Net Source Energy | 817.94 | 1600.18 | 1600.18
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 123.55 | 0 | 0 | 0 | 0
Cooling | 13.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 43.7 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.27 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 194.83 | 135.82 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8329.49 | 6532.97 | 1796.52 | 0.78 | 3.99
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8569.73 | 6362.75 | 2206.98 | 0.74 | 3.85
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5413.54 | 4219.95 | 1193.59 | 0.78 | 3.97
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8238.4 | 6114.16 | 2124.24 | 0.74 | 3.85
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6026.76 | 4658.26 | 1368.5 | 0.77 | 3.95
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15230.98 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 13155.7 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8916.33 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 12767.81 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 9554.38 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 560.89 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 508.71 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 359.58 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 488.55 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 392.75 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5560.6807 | 8.3727 | 10.8531 | 0 | 0.0001 | 7127.6679 | 2242.4071
February | 4549.3349 | 7.0873 | 9.6521 | 0 | 0.0001 | 6340.2543 | 1857.259
March | 4325.6378 | 7.165 | 10.5653 | 0 | 0.0001 | 6942.3723 | 1806.6766
April | 3367.5347 | 5.9295 | 9.3697 | 0 | 0.0001 | 6158.3015 | 1440.1058
May | 3565.6779 | 6.4373 | 10.4386 | 0 | 0.0001 | 6861.5004 | 1540.0359
June | 3945.7787 | 7.152 | 11.6439 | 0 | 0.0001 | 7653.8885 | 1706.9209
July | 4015.8247 | 7.2809 | 11.857 | 0 | 0.0001 | 7793.9742 | 1737.4102
August | 4318.9365 | 7.8332 | 12.7608 | 0 | 0.0001 | 8388.1034 | 1868.8094
September | 3422.3579 | 6.192 | 10.0628 | 0 | 0.0001 | 6614.5242 | 1479.4199
October | 3514.926 | 6.2144 | 9.8623 | 0 | 0.0001 | 6482.2328 | 1505.5617
November | 4094.1574 | 6.7933 | 10.038 | 0 | 0.0001 | 6595.9334 | 1711.1126
December | 5101.787 | 7.8981 | 10.6619 | 0 | 0.0001 | 7003.3523 | 2078.0339
Annual Sum or Average | 49782.6342 | 84.3555 | 127.7655 | 0 | 0.0009 | 83962.1053 | 20973.7531
Minimum of Months | 3367.5347 | 5.9295 | 9.3697 | 0 | 0.0001 | 6158.3015 | 1440.1058
Maximum of Months | 5560.6807 | 8.3727 | 12.7608 | 0 | 0.0001 | 8388.1034 | 2242.4071
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16539200000 | 11939.059 | 02-JAN-16:40 | 4950.048 | 3712.536 | 2310.474 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14712100000 | 10980.48 | 16-FEB-13:30 | 4950.048 | 3712.536 | 2310.474 | 0 | 7.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 16109300000 | 11259.693 | 23-MAR-14:09 | 4950.048 | 3712.536 | 2310.474 | 0 | 286.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14289900000 | 12127.785 | 14-APR-15:00 | 4950.048 | 3712.536 | 2310.474 | 0 | 1154.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15921600000 | 14917.246 | 31-MAY-12:09 | 4950.048 | 3712.536 | 2310.474 | 0 | 3944.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 17760300000 | 16935.776 | 29-JUN-15:00 | 4950.048 | 3712.536 | 2310.474 | 0 | 5962.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 18085300000 | 17098.069 | 13-JUL-15:00 | 4950.048 | 3712.536 | 2310.474 | 0 | 6125.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 19464000000 | 16894.493 | 25-AUG-15:00 | 4950.048 | 3712.536 | 2310.474 | 0 | 5921.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 15348500000 | 15287.657 | 14-SEP-14:00 | 4950.048 | 3712.536 | 2310.474 | 0 | 4314.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15041500000 | 12564.868 | 06-OCT-14:00 | 4950.048 | 3712.536 | 2310.474 | 0 | 1591.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15305400000 | 11939.059 | 06-NOV-16:00 | 4950.048 | 3712.536 | 2310.474 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16250800000 | 11939.059 | 06-DEC-16:30 | 4950.048 | 3712.536 | 2310.474 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 194828000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14289900000 | 10980.48 |  | 4950.048 | 3712.536 | 2310.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 19464000000 | 17098.069 |  | 4950.048 | 3712.536 | 2310.474 | 0 | 6125.01 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4070.56 | 1074.24 | 0 | 5144.8
Cost per Total Building Area ($/m2) | 7.96 | 2.1 | 0 | 10.07
Cost per Net Conditioned Building Area ($/m2) | 7.96 | 2.1 | 0 | 10.07

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 297.09 | 581.21 | 581.21
Net Site Energy | 297.09 | 581.21 | 581.21
Total Source Energy | 767.61 | 1501.71 | 1501.71
Net Source Energy | 767.61 | 1501.71 | 1501.71
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 98.88 | 0 | 0 | 0 | 0
Cooling | 7.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.16 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 41.14 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.31 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 185.9 | 111.19 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 16.73 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5896.5 | 4709.27 | 1187.23 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7933.25 | 6335.93 | 1597.32 | 0.8 | 4.04
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4910.16 | 3921.53 | 988.64 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7618.33 | 6084.42 | 1533.91 | 0.8 | 4.04
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5418.06 | 4327.16 | 1090.9 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 11182.21 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 12650.61 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 7750.38 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 12271.24 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 8362.24 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 413.17 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 555.88 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 344.05 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 533.82 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 379.64 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5242.5214 | 8.067 | 11.9885 | 0 | 0.0001 | 284232.4741 | 2134.2416
February | 4394.4334 | 6.9223 | 10.6288 | 0 | 0.0001 | 252027.5374 | 1804.4784
March | 4348.7565 | 7.2075 | 11.81 | 0 | 0.0001 | 280099.4022 | 1820.245
April | 3625.6442 | 6.1741 | 10.4433 | 0 | 0.0001 | 247712.3973 | 1533.5333
May | 3680.9695 | 6.4208 | 11.1539 | 0 | 0.0001 | 264591.7855 | 1571.6688
June | 3796.4193 | 6.6821 | 11.7205 | 0 | 0.0001 | 278041.5975 | 1626.7568
July | 3958.0363 | 6.9805 | 12.2699 | 0 | 0.0001 | 291077.4131 | 1697.3583
August | 4143.4624 | 7.3076 | 12.845 | 0 | 0.0001 | 304718.9027 | 1776.8819
September | 3583.3515 | 6.2958 | 11.022 | 0 | 0.0001 | 261469.8316 | 1534.3699
October | 3763.8705 | 6.4801 | 11.0967 | 0 | 0.0001 | 263221.9734 | 1598.8215
November | 4144.6215 | 6.8528 | 11.1963 | 0 | 0.0001 | 265541.5596 | 1733.2152
December | 5002.1092 | 7.7798 | 11.738 | 0 | 0.0001 | 278309.8877 | 2044.3688
Annual Sum or Average | 49684.1959 | 83.1704 | 137.9128 | 0 | 0.001 | 3271040 | 20875.9395
Minimum of Months | 3583.3515 | 6.1741 | 10.4433 | 0 | 0.0001 | 247712.3973 | 1533.5333
Maximum of Months | 5242.5214 | 8.067 | 12.845 | 0 | 0.0001 | 304718.9027 | 2134.2416
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16153600000 | 11855.148 | 02-JAN-08:09 | 4950.048 | 3712.536 | 2226.564 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14323300000 | 11289.59 | 03-FEB-13:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 400.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15918700000 | 11969.754 | 30-MAR-15:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 1080.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14078100000 | 11547.2 | 06-APR-15:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 658.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15037400000 | 12746.968 | 17-MAY-15:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 1857.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 15801800000 | 15214.732 | 30-JUN-14:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 4325.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 16542600000 | 15424.727 | 21-JUL-15:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 4535.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 17317900000 | 14972.2 | 09-AUG-15:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 4083.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 14860000000 | 13849.66 | 12-SEP-13:00 | 4950.048 | 3712.536 | 2226.564 | 0 | 2960.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 14959500000 | 12640.468 | 06-OCT-15:20 | 4950.048 | 3712.536 | 2226.564 | 0 | 1751.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15091400000 | 11855.148 | 01-NOV-07:10 | 4950.048 | 3712.536 | 2226.564 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15817000000 | 11855.148 | 01-DEC-16:40 | 4950.048 | 3712.536 | 2226.564 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 185901000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14078100000 | 11289.59 |  | 4950.048 | 3712.536 | 2226.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 17317900000 | 15424.727 |  | 4950.048 | 3712.536 | 2226.564 | 0 | 4535.579 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4008.06 | 895.07 | 0 | 4903.13
Cost per Total Building Area ($/m2) | 7.84 | 1.75 | 0 | 9.59
Cost per Net Conditioned Building Area ($/m2) | 7.84 | 1.75 | 0 | 9.59

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 351.85 | 688.34 | 688.34
Net Site Energy | 351.85 | 688.34 | 688.34
Total Source Energy | 823.59 | 1611.23 | 1611.23
Net Source Energy | 823.59 | 1611.23 | 1611.23
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 151.84 | 0 | 0 | 0 | 0
Cooling | 5.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.65 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 187.37 | 164.48 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.153 | 0.159 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.153 | 0.159 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.153 | 0.159 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.153 | 0.159 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 16.73 | 3.24 | 0.487 | 0.409
Non-North Total or Average |  |  | 42.95 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6334.05 | 5058.72 | 1275.33 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8766.1 | 6609.34 | 2156.76 | 0.75 | 3.88
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4910.72 | 3921.97 | 988.75 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7645.28 | 6009.23 | 1636.05 | 0.79 | 3.99
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5720.98 | 4569.09 | 1151.89 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 12985.89 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 13672.42 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 8562.97 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 13252.26 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 9632.41 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 443.83 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 539.58 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 344.09 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 517.27 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 400.87 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5596.7729 | 8.4134 | 10.8792 | 0 | 0.0001 | 7144.7422 | 2255.6604
February | 4777.7293 | 7.2984 | 9.6657 | 0 | 0.0001 | 6348.467 | 1936.6764
March | 4687.2988 | 7.5533 | 10.7625 | 0 | 0.0001 | 7070.982 | 1937.5873
April | 3600.3639 | 6.1608 | 9.4358 | 0 | 0.0001 | 6201.0896 | 1522.5996
May | 3467.4846 | 6.152 | 9.7993 | 0 | 0.0001 | 6440.889 | 1487.2982
June | 3472.0558 | 6.2822 | 10.2097 | 0 | 0.0001 | 6711.1215 | 1500.9276
July | 3650.5402 | 6.6111 | 10.754 | 0 | 0.0001 | 7068.884 | 1578.6536
August | 3772.1473 | 6.8269 | 11.0978 | 0 | 0.0001 | 7294.848 | 1630.8177
September | 3310.1683 | 5.9268 | 9.5304 | 0 | 0.0001 | 6264.3231 | 1424.9768
October | 3645.8775 | 6.3366 | 9.8739 | 0 | 0.0001 | 6489.3727 | 1551.2046
November | 4350.3732 | 7.0654 | 10.1681 | 0 | 0.0001 | 6680.7254 | 1803.5735
December | 5309.2684 | 8.0991 | 10.7043 | 0 | 0.0001 | 7030.5695 | 2151.0602
Annual Sum or Average | 49640.0802 | 82.7262 | 122.8806 | 0 | 0.0009 | 80746.0141 | 20781.036
Minimum of Months | 3310.1683 | 5.9268 | 9.4358 | 0 | 0.0001 | 6201.0896 | 1424.9768
Maximum of Months | 5596.7729 | 8.4134 | 11.0978 | 0 | 0.0001 | 7294.848 | 2255.6604
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16578800000 | 11874.223 | 02-JAN-16:30 | 4950.048 | 3712.536 | 2245.638 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14731100000 | 10927.812 | 17-FEB-13:20 | 4950.048 | 3712.536 | 2245.638 | 0 | 19.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 16407700000 | 10980.383 | 22-MAR-13:50 | 4950.048 | 3712.536 | 2245.638 | 0 | 72.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14389200000 | 11348.842 | 04-APR-15:20 | 4950.048 | 3712.536 | 2245.638 | 0 | 440.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 14945600000 | 13001.972 | 31-MAY-15:00 | 4950.048 | 3712.536 | 2245.638 | 0 | 2093.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 15572700000 | 14904.947 | 14-JUN-15:00 | 4950.048 | 3712.536 | 2245.638 | 0 | 3996.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 16402800000 | 15972.966 | 06-JUL-15:00 | 4950.048 | 3712.536 | 2245.638 | 0 | 5064.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 16927100000 | 15347.07 | 11-AUG-15:30 | 4950.048 | 3712.536 | 2245.638 | 0 | 4438.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 14535900000 | 14190.646 | 07-SEP-14:00 | 4950.048 | 3712.536 | 2245.638 | 0 | 3282.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15058100000 | 11864.125 | 06-OCT-14:00 | 4950.048 | 3712.536 | 2245.638 | 0 | 955.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15502100000 | 11874.223 | 06-NOV-16:49 | 4950.048 | 3712.536 | 2245.638 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16313900000 | 11874.223 | 01-DEC-16:19 | 4950.048 | 3712.536 | 2245.638 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 187365000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14389200000 | 10927.812 |  | 4950.048 | 3712.536 | 2245.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 16927100000 | 15972.966 |  | 4950.048 | 3712.536 | 2245.638 | 0 | 5064.743 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 3904.7 | 1296.24 | 0 | 5200.94
Cost per Total Building Area ($/m2) | 7.64 | 2.54 | 0 | 10.17
Cost per Net Conditioned Building Area ($/m2) | 7.64 | 2.54 | 0 | 10.17

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 484.52 | 947.89 | 947.89
Net Site Energy | 484.52 | 947.89 | 947.89
Total Source Energy | 1019.3 | 1994.1 | 1994.1
Net Source Energy | 1019.3 | 1994.1 | 1994.1
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 273.76 | 0 | 0 | 0 | 0
Cooling | 5.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 15.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 55.04 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 13.1 | 0 | 0 | 0 | 17.63
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 197.66 | 286.86 | 0 | 0 | 0 | 17.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.58 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.58 | 8.07
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.23 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.58 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
ATTIC_SOFFIT_EAST | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 16.97 | 315 | 180
ATTIC_SOFFIT_SOUTH | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 16.97 | 225 | 180
ATTIC_SOFFIT_WEST | ATTIC-FLOOR-NONRES | 0.08 | 0.152 | 0.158 | 11.44 | 270 | 180
ATTIC_ROOF_EAST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 90 | 18.45
ATTIC_ROOF_NORTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 0 | 18.45
ATTIC_ROOF_SOUTH | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 197.51 | 180 | 18.45
ATTIC_ROOF_WEST | ATTIC-ROOF-NONRES | 0.3 | 4.035 | 16.833 | 101.87 | 270 | 18.45
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 67.3 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.91 | 3.91 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 16.73 | 2.61 | 0.702 | 0.633
Non-North Total or Average |  |  | 42.95 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5122.1 | 4090.79 | 1031.31 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10912.5 | 8715.33 | 2197.18 | 0.8 | 4.04
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5806.4 | 4637.32 | 1169.09 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9075.18 | 7247.94 | 1827.24 | 0.8 | 4.04
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6472.24 | 5169.09 | 1303.15 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 13088.06 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 19533.21 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 10675.58 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 17021.52 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 11585.83 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 358.91 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 764.64 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 406.85 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 635.9 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 453.51 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6830.4523 | 7.4196 | 25.527 | 0 | 0.0001 | 5120.0575 | 2551.6456
February | 5748.7988 | 6.3053 | 22.7533 | 0 | 0.0001 | 4564.0587 | 2156.9047
March | 5166.3198 | 5.8869 | 25.0593 | 0 | 0.0001 | 5027.8315 | 1972.2829
April | 3624.1196 | 4.3122 | 21.3991 | 0 | 0.0001 | 4294.2787 | 1411.6363
May | 3151.8265 | 3.9024 | 21.794 | 0 | 0.0001 | 4374.0805 | 1251.09
June | 3207.9767 | 3.9952 | 22.6701 | 0 | 0.0001 | 4549.9739 | 1276.9662
July | 3177.3228 | 3.9594 | 22.5032 | 0 | 0.0001 | 4516.501 | 1265.1305
August | 3320.3161 | 4.132 | 23.3986 | 0 | 0.0001 | 4696.1812 | 1321.2032
September | 3176.0706 | 3.8841 | 20.9503 | 0 | 0.0001 | 4204.5919 | 1253.2743
October | 4241.6878 | 4.9659 | 23.3481 | 0 | 0.0001 | 4685.0943 | 1639.6999
November | 5619.1911 | 6.2794 | 24.6711 | 0 | 0.0001 | 4949.3977 | 2126.1571
December | 6383.601 | 7.0126 | 25.4967 | 0 | 0.0001 | 5114.428 | 2396.7764
Annual Sum or Average | 53647.6831 | 62.055 | 279.5709 | 0 | 0.001 | 56096.4749 | 20622.767
Minimum of Months | 3151.8265 | 3.8841 | 20.9503 | 0 | 0.0001 | 4204.5919 | 1251.09
Maximum of Months | 6830.4523 | 7.4196 | 25.527 | 0 | 0.0001 | 5120.0575 | 2551.6456
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18041100000 | 12248.39 | 02-JAN-08:09 | 4950.048 | 3712.536 | 2619.806 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 16082000000 | 12248.39 | 01-FEB-08:09 | 4950.048 | 3712.536 | 2619.806 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17716100000 | 12248.39 | 01-MAR-08:09 | 4950.048 | 3712.536 | 2619.806 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15131400000 | 12167.036 | 25-APR-13:30 | 4950.048 | 3712.536 | 2619.806 | 0 | 884.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15412500000 | 13796.22 | 24-MAY-14:00 | 4950.048 | 3712.536 | 2619.806 | 0 | 2513.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 16032300000 | 15106.195 | 21-JUN-15:50 | 4950.048 | 3712.536 | 2619.806 | 0 | 3823.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 15914400000 | 15039.852 | 11-JUL-15:00 | 4950.048 | 3712.536 | 2619.806 | 0 | 3757.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 16547500000 | 14986.175 | 15-AUG-14:30 | 4950.048 | 3712.536 | 2619.806 | 0 | 3703.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 14815300000 | 12439.001 | 08-SEP-15:39 | 4950.048 | 3712.536 | 2619.806 | 0 | 1156.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16508400000 | 12248.39 | 03-OCT-07:10 | 4950.048 | 3712.536 | 2619.806 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 17439700000 | 12248.39 | 01-NOV-07:10 | 4950.048 | 3712.536 | 2619.806 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 18021200000 | 12248.39 | 01-DEC-08:09 | 4950.048 | 3712.536 | 2619.806 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 197662000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14815300000 | 12167.036 |  | 4950.048 | 3712.536 | 2619.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 18041100000 | 15106.195 |  | 4950.048 | 3712.536 | 2619.806 | 0 | 3823.805 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5527.53 | 1178.25 | 0 | 6705.78
Cost per Total Building Area ($/m2) | 10.81 | 2.31 | 0 | 13.12
Cost per Net Conditioned Building Area ($/m2) | 10.81 | 2.31 | 0 | 13.12

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_ZN Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_ZN Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_ZN Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_ZN Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720