## BuildingSummary
Building Summary Hospital new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Hospital
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, inpatient
Form
| Total Floor Area (m2) | 22422.1768 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3142
| Number of Floors | 5 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.1334
| East | 0.121
| North | 0.117
| West | 0.2315
| Total | 0.1461
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures and zone summary
| Floor to Ceiling Height (m) | 4.27
| Floor to Floor Height (m) | 4.27
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 5184.32
| Net Dimensions - Total Area (m2) | 4338.78
| Wall to Skin Ratio | 0.41902
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3739.134
| Net Dimensions - Total Area (m2) | 3739.134
| Roof to Skin Ratio | 0.58098
Window Dimensions (m2)
| South | 220.72
| East | 144.86
| North | 186.18
| West | 293.66
| Total Area (m2) | 845.42
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 8 in slab
| Dimensions - Total Area (m2) | 3739.134
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15534.17
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 44872.35
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.11 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Boiler | 2003 CBECS
| Cooling Type | Chiller, water cooled | 2003 CBECS
| Fan Control | CAV, VAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 4037.86

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 10.76 | 8.07 |  |  | 10 | 0 | 1006.2497 |  | 0
ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
ER_Exam2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.1785
ER_Exam4_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
ER_Exam5_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.94 | 1 | 11.836 | 8.07 |  |  | 10 | 0 | 10 |  | 0.23798
Lobby_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.78 | 62.63 | 18.5806 | 79.3735 | 13.988 | 8.07 |  |  | 10 | 0 | 793.7354 |  | 0.070849
Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.07 | 0 | 92.9031 | 6.125 | 10.76 | 0 |  |  | 0 | 0.25 | 142.2575 |  | 0.040809
ER_NurseStat_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.58 | 30.42 | 46.4516 | 26.6 | 10.76 | 8.07 |  |  |  |  | 2929.97 |  | 0.02282
OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.05 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.29758
OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.11903
OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.17855
OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 23.672 | 53.8 |  | 22.7124 |  |  | 793.0845 |  | 0
IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 10.45 | 2 | 8.608 | 32.28 |  |  |  |  | 49.5596 |  | 0.23803
IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 13.935 | 2 | 8.608 | 32.28 |  |  |  |  | 66.0874 |  | 0.41656
IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 10.45 | 2 | 8.608 | 32.28 |  |  |  |  | 49.5596 |  | 0.23803
ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.68 | 25.03 | 46.4516 | 13.3033 | 8.608 | 32.28 |  |  |  |  | 1465.3525 |  | 0.088583
ICU_NurseSat_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 10.76 | 8.07 |  |  | 10 | 0 | 359.9287 |  | 0
Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.07 | 0 | 92.9031 | 6.125 | 10.76 | 0 |  |  | 0 | 0.25 | 142.2575 |  | 0.040809
OR_NurseSat_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.14 | 35.76 | 18.5806 | 54.4998 | 10.76 | 8.07 |  |  | 10 | 0 | 544.9978 |  | 0.045864
PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 4.6452 | 104.9997 | 9.684 | 16.14 |  | 3.7854 | 8 | 0 | 839.9975 |  | 0
PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
NurseSat_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 18.5806 | 48.7497 | 10.76 | 8.07 |  |  | 10 | 0 | 487.497 |  | 0
Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 3.7161 | 71.2489 | 15.064 | 32.28 |  | 7.5708 | 10 | 0 | 712.4895 |  | 0
Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 4.304 | 53.8 |  | 3.7854 | 8 | 0 | 209.9994 |  | 0
PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
NurseSat_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 18.5806 | 48.7497 | 10.76 | 8.07 |  |  | 10 | 0 | 487.497 |  | 0
Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 3.7161 | 71.2489 | 15.064 | 32.28 |  | 7.5708 | 10 | 0 | 712.4895 |  | 0
Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.67 | 35.76 | 1.3935 | 499.9995 | 9.684 | 2.69 |  |  | 10 | 0 | 4999.9952 |  | 0.33831
NurseSat_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.08 | 0 | 18.5806 | 55.9999 | 10.76 | 8.07 |  |  | 10 | 0 | 559.9995 |  | 0.28049
Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2 | 0 | 23.2258 | 39.9999 | 12.912 | 197.984 | 570.28 | 567.81 | 8 | 0 | 319.9996 | 3775.576 | 0.32641
Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.56 | 17.98 | 18.5806 | 3.7512 | 11.836 | 8.07 |  |  | 10 | 0 | 37.5122 |  | 0.51678
Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 18.5806 | 3.7501 | 11.836 | 8.07 |  |  | 10 | 0 | 37.5014 |  | 0.37399
Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.55 | 17.98 | 18.5806 | 3.7501 | 11.836 | 8.07 |  |  | 10 | 0 | 37.5014 |  | 0.51682
Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.94 | 1 | 11.836 | 8.07 |  |  | 10 | 0 | 10 |  | 0.49297
Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.06 | 0 | 92.9031 | 5.4 | 10.76 | 0 |  |  | 0 | 0.25 | 125.42 |  | 0.29466
Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.32 | 845.54 |  | 1572.9423 |  |  |  | 1052.3412
4338.78
Data Source |  |  | 1.3142 | 8923.454 |  |  |  | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
|  |  | 3739.134 | 0.41902 | 0.58098
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 23973.96 | 1069.2 | 1069.2
Net Site Energy | 23973.96 | 1069.2 | 1069.2
Total Source Energy | 72663.79 | 3240.7 | 3240.7
Net Source Energy | 72663.79 | 3240.7 | 3240.7
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 204.86 | 0 | 0 | 0 | 0
Cooling | 5626.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2822.18 | 0 | 0 | 0 | 0 | 0
Pumps | 1652.66 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 903.65 | 0 | 0 | 0 | 0 | 24095.47
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 336.3 | 0 | 0 | 0 | 4037.86
Refrigeration | 217.1 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20891.79 | 3082.17 | 0 | 0 | 0 | 28133.33
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 20891.79 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 20891.79 | 100
Total On-Site and Utility Electric Sources | 20891.79 | 100
Total Electricity End Uses | 20891.79 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 6.88 | 0.25 | 0.25 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 6.88 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 6.88 | 0.25 | 0.25 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 6.88 | 0.25 | 0.25 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.25 | 0.25 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.25 | 0.25 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 6.88 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 6.88 | 0.25 | 0.25 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 6.88 | 0.25 | 0.25 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.25 | 0.25 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 6.88 | 0.25 | 0.25 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2360318.66 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5694968.8 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2197804.92
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 34.35 | 81422.75 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 51.82 | 122819.07 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31644 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21629.05 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 31018.95 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 301328.4366 | 516.6346 | 1914.6569 | 0 | 0.0088 | 236953.9504 | 128650.3987
February | 274270.7742 | 471.9907 | 1756.4816 | 0 | 0.008 | 217379.8908 | 117273.3453
March | 309225.2199 | 533.2862 | 1989.3298 | 0 | 0.0091 | 246197.7784 | 132333.7425
April | 305145.0542 | 527.5341 | 1973.1907 | 0 | 0.009 | 244201.4131 | 130716.3292
May | 337391.8639 | 584.1584 | 2188.6075 | 0 | 0.01 | 270862.0031 | 144617.828
June | 335216.3406 | 580.7929 | 2177.6524 | 0 | 0.0099 | 269506.5104 | 143725.5168
July | 355386.2606 | 616.088 | 2311.4276 | 0 | 0.0106 | 286062.8164 | 152408.422
August | 356162.5245 | 617.4141 | 2316.3217 | 0 | 0.0106 | 286668.4969 | 152739.3555
September | 336232.9249 | 582.4816 | 2183.6851 | 0 | 0.01 | 270253.0583 | 144154.1085
October | 331219.0815 | 573.1315 | 2145.8945 | 0 | 0.0098 | 265575.5803 | 141937.954
November | 303492.0637 | 524.0265 | 1957.3864 | 0 | 0.0089 | 242244.9816 | 129943.108
December | 300821.8941 | 517.6833 | 1926.5279 | 0 | 0.0088 | 238424.603 | 128626.237
Annual Sum or Average | 3845892.4387 | 6645.2219 | 24841.1621 | 0 | 0.1135 | 3074331.0826 | 1647126.3455
Minimum of Months | 274270.7742 | 471.9907 | 1756.4816 | 0 | 0.008 | 217379.8908 | 117273.3453
Maximum of Months | 356162.5245 | 617.4141 | 2316.3217 | 0 | 0.0106 | 286668.4969 | 152739.3555
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1610230000000 | 890206.414 | 06-JAN-13:00 | 228236.782 | 263066.793 | 93973.186 | 0 | 215773.978 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7586.673 | 0 | 0
February | 1477220000000 | 899790.315 | 23-FEB-12:00 | 228236.782 | 263066.793 | 96975.341 | 0 | 222409.759 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7532.639 | 0 | 0
March | 1673050000000 | 911184.172 | 14-MAR-10:39 | 228236.782 | 263066.793 | 92787.605 | 0 | 234211.107 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 11312.884 | 0 | 0
April | 1659480000000 | 926857.997 | 03-APR-13:00 | 228236.782 | 263066.793 | 99303.736 | 0 | 246924.418 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7757.267 | 0 | 0
May | 1840660000000 | 1001216.447 | 19-MAY-14:00 | 228236.782 | 263066.793 | 105065.754 | 0 | 315515.76 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7762.357 | 0 | 0
June | 1831450000000 | 1060041.448 | 27-JUN-14:00 | 228236.782 | 263066.793 | 104550.856 | 0 | 374748.857 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7869.158 | 0 | 0
July | 1943960000000 | 1037418.401 | 13-JUL-14:00 | 228236.782 | 263066.793 | 107582.029 | 0 | 349118.646 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7845.15 | 0 | 0
August | 1948070000000 | 1031392.112 | 21-AUG-14:30 | 228236.782 | 263066.793 | 99555.596 | 0 | 351046.648 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7917.291 | 0 | 0
September | 1836520000000 | 996191.526 | 12-SEP-13:00 | 228236.782 | 263066.793 | 102024.631 | 0 | 313476.889 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7817.431 | 0 | 0
October | 1804730000000 | 984236.507 | 06-OCT-14:00 | 228236.782 | 263066.793 | 104535.896 | 0 | 299052.851 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7775.184 | 0 | 0
November | 1646190000000 | 927186.354 | 01-NOV-15:00 | 228236.782 | 263066.793 | 97656.357 | 0 | 249008.133 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7649.288 | 0 | 0
December | 1620230000000 | 894341.896 | 15-DEC-15:00 | 228236.782 | 263066.793 | 97236.039 | 0 | 216670.74 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7562.54 | 0 | 0
Annual Sum or Average | 20891800000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1477220000000 | 890206.414 |  | 228236.782 | 263066.793 | 92787.605 | 0 | 215773.978 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 7532.639 | 0 | 0
Maximum of Months | 1948070000000 | 1060041.448 |  | 228236.782 | 263066.793 | 107582.029 | 0 | 374748.857 | 0 | 52722.812 | 28846.19 | 0 | 0 | 0 | 0 | 11312.884 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 431627.77 | 35320.05 | 0 | 466947.82
Cost per Total Building Area ($/m2) | 19.25 | 1.58 | 0 | 20.83
Cost per Net Conditioned Building Area ($/m2) | 19.25 | 1.58 | 0 | 20.83
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 24551.21 | 1094.95 | 1094.95
Net Site Energy | 24551.21 | 1094.95 | 1094.95
Total Source Energy | 5844.54 | 260.66 | 260.66
Net Source Energy | 5844.54 | 260.66 | 260.66
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2383.74 | 0 | 0 | 0 | 0
Cooling | 4353.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2852.37 | 0 | 0 | 0 | 0 | 0
Pumps | 1370.26 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 743.33 | 0 | 0 | 0 | 0 | 18260.93
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 427.39 | 0 | 0 | 0 | 4037.86
Refrigeration | 209.38 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19199.07 | 5352.14 | 0 | 0 | 0 | 22298.79
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 19199.07 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 19199.07 | 100
Total On-Site and Utility Electric Sources | 19199.07 | 100
Total Electricity End Uses | 19199.07 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 6.88 | 0.25 | 0.25 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 6.88 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 6.88 | 0.25 | 0.25 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 6.88 | 0.25 | 0.25 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.25 | 0.25 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.25 | 0.25 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 6.88 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 6.88 | 0.25 | 0.25 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 6.88 | 0.25 | 0.25 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.25 | 0.25 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 6.88 | 0.25 | 0.25 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2277232.06 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6154557.11 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2120439.03
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 34.25 | 81177.29 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 54.17 | 128390.81 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34197.7 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20867.68 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29927.04 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 363652.7728 | 458.3417 | 1797.269 | 0 | 0.0052 | 612990.1024 | 142390.3525
February | 316543.5319 | 398.6324 | 1559.7694 | 0 | 0.0045 | 531985.0492 | 123901.4471
March | 370780.6276 | 477.257 | 1971.5921 | 0 | 0.0056 | 672495.4848 | 146461.4584
April | 380977.7635 | 494.4746 | 2083.1268 | 0 | 0.0059 | 710558.0665 | 151016.8822
May | 420587.8646 | 547.3763 | 2320.5962 | 0 | 0.0065 | 791565.9862 | 166910.2822
June | 431715.5191 | 562.4213 | 2389.8764 | 0 | 0.0067 | 815200.3125 | 171398.8455
July | 463677.3531 | 604.3101 | 2570.3146 | 0 | 0.0072 | 876749.8911 | 184120.5268
August | 461211.9167 | 601.0602 | 2556.1332 | 0 | 0.0072 | 871912.3751 | 183136.796
September | 417024.8915 | 543.0621 | 2305.4601 | 0 | 0.0065 | 786404.4489 | 165537.9405
October | 400861.097 | 520.7626 | 2198.5856 | 0 | 0.0062 | 749943.4352 | 158960.5245
November | 361227.4952 | 465.7148 | 1931.3579 | 0 | 0.0055 | 658775.3805 | 142785.1131
December | 354368.7781 | 446.9782 | 1756.117 | 0 | 0.005 | 598956.1924 | 138798.7014
Annual Sum or Average | 4742629.611 | 6120.3911 | 25440.1982 | 0 | 0.0721 | 8677536.7248 | 1875418.8702
Minimum of Months | 316543.5319 | 398.6324 | 1559.7694 | 0 | 0.0045 | 531985.0492 | 123901.4471
Maximum of Months | 463677.3531 | 604.3101 | 2570.3146 | 0 | 0.0072 | 876749.8911 | 184120.5268
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1356240000000 | 863911.643 | 03-JAN-11:39 | 228236.782 | 263066.793 | 90405.752 | 0 | 192367.364 | 0 | 50871.887 | 27830.762 | 0 | 0 | 0 | 0 | 11132.303 | 0 | 0
February | 1177020000000 | 831115.494 | 15-FEB-14:00 | 228236.782 | 263066.793 | 91171.194 | 0 | 162487.759 | 0 | 50877.051 | 27830.762 | 0 | 0 | 0 | 0 | 7445.154 | 0 | 0
March | 1487900000000 | 854690.856 | 24-MAR-11:00 | 228236.782 | 263066.793 | 92361.868 | 0 | 184899.117 | 0 | 50869.623 | 27830.762 | 0 | 0 | 0 | 0 | 7425.912 | 0 | 0
April | 1572110000000 | 881176.441 | 20-APR-14:00 | 228236.782 | 263066.793 | 96066.306 | 0 | 207494.848 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7611.423 | 0 | 0
May | 1751340000000 | 989849.176 | 18-MAY-14:20 | 228236.782 | 263066.793 | 103658.034 | 0 | 308300.306 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7886.973 | 0 | 0
June | 1803630000000 | 981926.538 | 29-JUN-14:00 | 228236.782 | 263066.793 | 104100.389 | 0 | 299959.712 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7862.573 | 0 | 0
July | 1939810000000 | 1068266.121 | 18-JUL-13:30 | 228236.782 | 263066.793 | 104186.895 | 0 | 386117.157 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7958.205 | 0 | 0
August | 1929110000000 | 1035142.773 | 03-AUG-14:00 | 228236.782 | 263066.793 | 105386.526 | 0 | 351857.086 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7895.296 | 0 | 0
September | 1739920000000 | 1032742.923 | 15-SEP-14:00 | 228236.782 | 263066.793 | 99338.204 | 0 | 355514.042 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7886.813 | 0 | 0
October | 1659250000000 | 937707.858 | 30-OCT-13:00 | 228236.782 | 263066.793 | 94470.084 | 0 | 265592.788 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7641.122 | 0 | 0
November | 1457540000000 | 890751.065 | 27-NOV-14:00 | 228236.782 | 263066.793 | 93167.456 | 0 | 220032.227 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7547.518 | 0 | 0
December | 1325190000000 | 857243.022 | 06-DEC-14:00 | 228236.782 | 263066.793 | 91822.867 | 0 | 187955.506 | 0 | 50880.667 | 27830.762 | 0 | 0 | 0 | 0 | 7449.645 | 0 | 0
Annual Sum or Average | 19199100000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1177020000000 | 831115.494 |  | 228236.782 | 263066.793 | 90405.752 | 0 | 162487.759 | 0 | 50869.527 | 27830.762 | 0 | 0 | 0 | 0 | 7425.912 | 0 | 0
Maximum of Months | 1939810000000 | 1068266.121 |  | 228236.782 | 263066.793 | 105386.526 | 0 | 386117.157 | 0 | 50880.667 | 27830.762 | 0 | 0 | 0 | 0 | 11132.303 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 525080.96 | 43583.53 | 0 | 568664.49
Cost per Total Building Area ($/m2) | 23.42 | 1.94 | 0 | 25.36
Cost per Net Conditioned Building Area ($/m2) | 23.42 | 1.94 | 0 | 25.36
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 22951.48 | 1023.6 | 1023.6
Net Site Energy | 22951.48 | 1023.6 | 1023.6
Total Source Energy | 62949.33 | 2807.45 | 2807.45
Net Source Energy | 62949.33 | 2807.45 | 2807.45
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1741.72 | 0 | 0 | 0 | 0
Cooling | 3244.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3338.41 | 0 | 0 | 0 | 0 | 0
Pumps | 1185.6 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 645.14 | 0 | 0 | 0 | 0 | 22282.78
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 375.02 | 0 | 0 | 0 | 4037.86
Refrigeration | 210.49 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18293.73 | 4657.75 | 0 | 0 | 0 | 26320.65
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 18293.73 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 18293.73 | 100
Total On-Site and Utility Electric Sources | 18293.73 | 100
Total Electricity End Uses | 18293.73 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 6.88 | 0.25 | 0.25 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 6.88 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 6.88 | 0.25 | 0.25 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 6.88 | 0.25 | 0.25 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 6.88 | 0.25 | 0.25 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.25 | 0.25 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.25 | 0.25 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.25 | 0.25 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.25 | 0.25 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 6.88 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 6.88 | 0.25 | 0.25 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 6.88 | 0.25 | 0.25 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.25 | 0.25 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 6.88 | 0.25 | 0.25 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1886805.06 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6691690.82 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1756893.89
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 38.69 | 91697.32 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 64.22 | 152228.34 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37182.27 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17289.96 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 24796.11 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 294734.498 | 469.8203 | 1464.5319 | 0 | 0.004 | 10817000 | 122463.6825
February | 268254.1363 | 428.4176 | 1338.7985 | 0 | 0.0037 | 9888422.9479 | 111542.6933
March | 317023.5253 | 519.5113 | 1677.7295 | 0 | 0.0046 | 12392500 | 133156.9096
April | 308178.3274 | 509.7032 | 1664.8232 | 0 | 0.0045 | 12297400 | 129915.6571
May | 330754.5214 | 548.9043 | 1800.2517 | 0 | 0.0049 | 13297900 | 139621.1506
June | 340209.2894 | 565.6006 | 1858.9869 | 0 | 0.0051 | 13731800 | 143713.9684
July | 367974.8759 | 612.3175 | 2014.73 | 0 | 0.0055 | 14882200 | 155499.1975
August | 365622.5152 | 608.3289 | 2001.3135 | 0 | 0.0055 | 14783100 | 154497.6297
September | 335619.7928 | 557.7162 | 1832.0695 | 0 | 0.005 | 13532900 | 141749.5251
October | 323644.3231 | 535.4643 | 1749.6862 | 0 | 0.0048 | 12924300 | 136453.8623
November | 301313.2743 | 492.7654 | 1587.3454 | 0 | 0.0043 | 11724800 | 126457.0031
December | 296863.4071 | 469.0624 | 1445.0789 | 0 | 0.004 | 10673100 | 122928.4561
Annual Sum or Average | 3850192.486 | 6317.612 | 20435.3452 | 0 | 0.0559 | 150946000 | 1617999.7354
Minimum of Months | 268254.1363 | 428.4176 | 1338.7985 | 0 | 0.0037 | 9888422.9479 | 111542.6933
Maximum of Months | 367974.8759 | 612.3175 | 2014.73 | 0 | 0.0055 | 14882200 | 155499.1975
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1310960000000 | 786163.06 | 26-JAN-15:00 | 228236.782 | 263066.793 | 107868.355 | 0 | 114398.644 | 0 | 42177.879 | 23059.232 | 0 | 0 | 0 | 0 | 7355.375 | 0 | 0
February | 1198420000000 | 796920.459 | 28-FEB-15:00 | 228236.782 | 263066.793 | 108981.563 | 0 | 123939.731 | 0 | 42164.62 | 23059.232 | 0 | 0 | 0 | 0 | 7471.738 | 0 | 0
March | 1501900000000 | 824280.196 | 17-MAR-14:00 | 228236.782 | 263066.793 | 111706.401 | 0 | 148318.884 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7731.232 | 0 | 0
April | 1490380000000 | 829143.984 | 26-APR-14:00 | 228236.782 | 263066.793 | 112098.747 | 0 | 152757.145 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7764.414 | 0 | 0
May | 1611630000000 | 872892.845 | 30-MAY-14:00 | 228236.782 | 263066.793 | 120734.585 | 0 | 187767.037 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7867.545 | 0 | 0
June | 1664210000000 | 953864.053 | 28-JUN-14:00 | 228236.782 | 263066.793 | 133159.148 | 0 | 256252.55 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7928.676 | 0 | 0
July | 1803640000000 | 988410.212 | 18-JUL-14:00 | 228236.782 | 263066.793 | 126281.947 | 0 | 297618.922 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7985.664 | 0 | 0
August | 1791630000000 | 974952.171 | 02-AUG-14:00 | 228236.782 | 263066.793 | 130293.422 | 0 | 280153.16 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7981.91 | 0 | 0
September | 1640110000000 | 933994.865 | 12-SEP-14:00 | 228236.782 | 263066.793 | 125067.063 | 0 | 244421.044 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7983.08 | 0 | 0
October | 1566350000000 | 847524.328 | 03-OCT-11:00 | 228236.782 | 263066.793 | 107638.302 | 0 | 176045.578 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7316.769 | 0 | 0
November | 1420980000000 | 810927.656 | 13-NOV-15:00 | 228236.782 | 263066.793 | 109550.449 | 0 | 137194.426 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7659.102 | 0 | 0
December | 1293520000000 | 781204.041 | 11-DEC-15:00 | 228236.782 | 263066.793 | 106739.381 | 0 | 110577.232 | 0 | 42176.04 | 23059.232 | 0 | 0 | 0 | 0 | 7348.581 | 0 | 0
Annual Sum or Average | 18293700000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1198420000000 | 781204.041 |  | 228236.782 | 263066.793 | 106739.381 | 0 | 110577.232 | 0 | 42160.871 | 23059.232 | 0 | 0 | 0 | 0 | 7316.769 | 0 | 0
Maximum of Months | 1803640000000 | 988410.212 |  | 228236.782 | 263066.793 | 133159.148 | 0 | 297618.922 | 0 | 42177.879 | 23059.232 | 0 | 0 | 0 | 0 | 7985.664 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 344463.18 | 39363.01 | 0 | 383826.18
Cost per Total Building Area ($/m2) | 15.36 | 1.76 | 0 | 17.12
Cost per Net Conditioned Building Area ($/m2) | 15.36 | 1.76 | 0 | 17.12
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 22996.88 | 1025.63 | 1025.63
Net Site Energy | 22996.88 | 1025.63 | 1025.63
Total Source Energy | 63300.15 | 2823.1 | 2823.1
Net Source Energy | 63300.15 | 2823.1 | 2823.1
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3132.78 | 0 | 0 | 0 | 0
Cooling | 2662.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2649.41 | 0 | 0 | 0 | 0 | 0
Pumps | 1055.02 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 568.21 | 0 | 0 | 0 | 0 | 12220.06
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 515.2 | 0 | 0 | 0 | 4037.86
Refrigeration | 202.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16807.9 | 6188.98 | 0 | 0 | 0 | 16257.92
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 16807.9 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 16807.9 | 100
Total On-Site and Utility Electric Sources | 16807.9 | 100
Total Electricity End Uses | 16807.9 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.25 | 0.318 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.25 | 0.318 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.25 | 0.318 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.25 | 0.318 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.25 | 0.318 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.25 | 0.318 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.25 | 0.318 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.25 | 0.318 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.25 | 0.318 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.25 | 0.318 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.25 | 0.318 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.25 | 0.318 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2053896.43 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5665802.01 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1912480.61
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 31.45 | 74547.52 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 50.63 | 120011.1 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31481.94 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18821.12 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 26992 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 275069.3414 | 469.9826 | 1081.1232 | 0 | 0.0041 | 1922558.1874 | 115547.5005
February | 255574.7851 | 444.34 | 1042.0805 | 0 | 0.0039 | 1853216.2775 | 108066.4383
March | 279478.0878 | 511.0621 | 1262.8999 | 0 | 0.0047 | 2246194.3056 | 120497.6077
April | 283905.7899 | 528.6507 | 1329.4377 | 0 | 0.0049 | 2364632.9172 | 123283.227
May | 316404.4987 | 596.5506 | 1517.8214 | 0 | 0.0056 | 2699776.3433 | 138077.5091
June | 322270.5814 | 609.1358 | 1553.4388 | 0 | 0.0057 | 2763143.8785 | 140778.3091
July | 344776.0221 | 652.2918 | 1664.9488 | 0 | 0.0061 | 2961495.5667 | 150666.4514
August | 345698.152 | 654.1201 | 1669.8125 | 0 | 0.0061 | 2970147.6215 | 151077.1578
September | 321049.0799 | 606.5304 | 1546.0968 | 0 | 0.0057 | 2750081.7748 | 140217.3254
October | 296675.1553 | 554.8103 | 1400.9105 | 0 | 0.0051 | 2491782.3649 | 129048.2042
November | 268898.4094 | 486.6808 | 1190.4106 | 0 | 0.0044 | 2117214.8855 | 115471.1576
December | 276740.7311 | 481.547 | 1130.3831 | 0 | 0.0042 | 2010256.4129 | 117053.87
Annual Sum or Average | 3586540.6341 | 6595.7024 | 16389.3639 | 0 | 0.0605 | 29150500 | 1549784.7581
Minimum of Months | 255574.7851 | 444.34 | 1042.0805 | 0 | 0.0039 | 1853216.2775 | 108066.4383
Maximum of Months | 345698.152 | 654.1201 | 1669.8125 | 0 | 0.0061 | 2970147.6215 | 151077.1578
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1108530000000 | 764386.852 | 23-JAN-15:00 | 228236.782 | 263066.793 | 88174.013 | 0 | 106761.608 | 0 | 45889.457 | 25101.308 | 0 | 0 | 0 | 0 | 7156.89 | 0 | 0
February | 1068550000000 | 765470.045 | 17-FEB-11:39 | 228236.782 | 263066.793 | 86014.985 | 0 | 106761.608 | 0 | 45901.68 | 25101.308 | 0 | 0 | 0 | 0 | 10386.889 | 0 | 0
March | 1295130000000 | 784113.13 | 29-MAR-14:00 | 228236.782 | 263066.793 | 88779.492 | 0 | 125836.568 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7204.266 | 0 | 0
April | 1363420000000 | 811520.904 | 21-APR-13:00 | 228236.782 | 263066.793 | 91396.589 | 0 | 150251.823 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7579.686 | 0 | 0
May | 1556670000000 | 860244.668 | 31-MAY-14:00 | 228236.782 | 263066.793 | 93686.139 | 0 | 196568.442 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7697.284 | 0 | 0
June | 1593200000000 | 919515.31 | 08-JUN-14:00 | 228236.782 | 263066.793 | 94004.556 | 0 | 255465.236 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7752.714 | 0 | 0
July | 1707570000000 | 959655.489 | 03-JUL-11:00 | 228236.782 | 263066.793 | 93425.774 | 0 | 296087.617 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7849.294 | 0 | 0
August | 1712560000000 | 945170.326 | 17-AUG-14:00 | 228236.782 | 263066.793 | 95878.781 | 0 | 279084.538 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7914.202 | 0 | 0
September | 1585670000000 | 896804.582 | 01-SEP-13:00 | 228236.782 | 263066.793 | 92016.604 | 0 | 234826.358 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7668.814 | 0 | 0
October | 1436740000000 | 823207.778 | 20-OCT-14:00 | 228236.782 | 263066.793 | 90127.501 | 0 | 163323.71 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7463.763 | 0 | 0
November | 1220770000000 | 773408.579 | 22-NOV-11:39 | 228236.782 | 263066.793 | 86848.76 | 0 | 113740.457 | 0 | 45891.359 | 25101.308 | 0 | 0 | 0 | 0 | 10523.121 | 0 | 0
December | 1159090000000 | 769442.956 | 26-DEC-13:00 | 228236.782 | 263066.793 | 84630.868 | 0 | 115375.21 | 0 | 45903.657 | 25101.308 | 0 | 0 | 0 | 0 | 7128.34 | 0 | 0
Annual Sum or Average | 16807900000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1068550000000 | 764386.852 |  | 228236.782 | 263066.793 | 84630.868 | 0 | 106761.608 | 0 | 45887.922 | 25101.308 | 0 | 0 | 0 | 0 | 7128.34 | 0 | 0
Maximum of Months | 1712560000000 | 959655.489 |  | 228236.782 | 263066.793 | 95878.781 | 0 | 296087.617 | 0 | 45903.657 | 25101.308 | 0 | 0 | 0 | 0 | 10523.121 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 469231.95 | 63236.99 | 0 | 532468.94
Cost per Total Building Area ($/m2) | 20.93 | 2.82 | 0 | 23.75
Cost per Net Conditioned Building Area ($/m2) | 20.93 | 2.82 | 0 | 23.75
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 19070.77 | 850.53 | 850.53
Net Site Energy | 19070.77 | 850.53 | 850.53
Total Source Energy | 51997.36 | 2319.01 | 2319.01
Net Source Energy | 51997.36 | 2319.01 | 2319.01
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 468.9 | 0 | 0 | 0 | 0
Cooling | 1956.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2448.12 | 0 | 0 | 0 | 0 | 0
Pumps | 831.53 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 453.33 | 0 | 0 | 0 | 0 | 8281.66
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 498.17 | 0 | 0 | 0 | 4037.86
Refrigeration | 203.59 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15562.69 | 3508.08 | 0 | 0 | 0 | 12319.52
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 15562.69 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 15562.69 | 100
Total On-Site and Utility Electric Sources | 15562.69 | 100
Total Electricity End Uses | 15562.69 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.25 | 0.318 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.25 | 0.318 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.25 | 0.318 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.25 | 0.318 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.25 | 0.318 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.25 | 0.318 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.25 | 0.318 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.25 | 0.318 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.25 | 0.318 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.25 | 0.318 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.25 | 0.318 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.25 | 0.318 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1235939.44 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5011823.06 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1150841.97
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 29.53 | 70006.34 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 45.99 | 108999.87 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27848.11 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11325.67 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 16242.53 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 124883.2908 | 107.887 | 983.0658 | 0 | 0.0005 | 5931059.7773 | 46221.6119
February | 111875.0016 | 96.597 | 889.9872 | 0 | 0.0004 | 5369532.0508 | 41435.442
March | 127572.4511 | 110.0211 | 1038.0643 | 0 | 0.0005 | 6263011.5524 | 47320.133
April | 123166.0339 | 106.1554 | 1013.9312 | 0 | 0.0005 | 6117452.7333 | 45721.4355
May | 130648.6506 | 112.5434 | 1086.4798 | 0 | 0.0005 | 6555208.5907 | 48532.5245
June | 128491.3432 | 110.655 | 1073.9175 | 0 | 0.0005 | 6479434.6224 | 47747.5496
July | 133753.0595 | 115.1635 | 1121.969 | 0 | 0.0005 | 6769366.5473 | 49715.2417
August | 138106.1303 | 118.892 | 1161.9862 | 0 | 0.0005 | 7010822.1156 | 51343.9377
September | 129788.9557 | 111.759 | 1087.1702 | 0 | 0.0005 | 6559403.7141 | 48237.0892
October | 131686.8484 | 113.4446 | 1093.8936 | 0 | 0.0005 | 6599934.7818 | 48914.4657
November | 124969.7297 | 107.7472 | 1022.1227 | 0 | 0.0005 | 6166850.0132 | 46370.6894
December | 126648.1195 | 109.3518 | 1007.6777 | 0 | 0.0005 | 6079591.3173 | 46907.5121
Annual Sum or Average | 1531589.6142 | 1320.2172 | 12580.2652 | 0 | 0.006 | 75901700 | 568467.6324
Minimum of Months | 111875.0016 | 96.597 | 889.9872 | 0 | 0.0004 | 5369532.0508 | 41435.442
Maximum of Months | 138106.1303 | 118.892 | 1161.9862 | 0 | 0.0005 | 7010822.1156 | 51343.9377
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1216090000000 | 726447.894 | 26-JAN-13:00 | 228236.782 | 263066.793 | 83599.533 | 0 | 101328.556 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7468.417 | 0 | 0
February | 1100960000000 | 714907.978 | 13-FEB-11:50 | 228236.782 | 263066.793 | 81005.41 | 0 | 90475.983 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 9375.197 | 0 | 0
March | 1284150000000 | 719962.563 | 31-MAR-14:50 | 228236.782 | 263066.793 | 87013.458 | 0 | 91596.03 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7301.688 | 0 | 0
April | 1254310000000 | 738492.967 | 11-APR-13:00 | 228236.782 | 263066.793 | 83447.878 | 0 | 113583.976 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7409.726 | 0 | 0
May | 1344060000000 | 766402.291 | 30-MAY-14:39 | 228236.782 | 263066.793 | 85080.9 | 0 | 139900.104 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7369.9 | 0 | 0
June | 1328530000000 | 759568.098 | 28-JUN-12:00 | 228236.782 | 263066.793 | 84685.751 | 0 | 133336.348 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7494.612 | 0 | 0
July | 1387970000000 | 787462.998 | 20-JUL-14:00 | 228236.782 | 263066.793 | 87933.151 | 0 | 158062.233 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7416.226 | 0 | 0
August | 1437480000000 | 820681.741 | 09-AUG-14:00 | 228236.782 | 263066.793 | 101212.304 | 0 | 177963.311 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7454.739 | 0 | 0
September | 1344920000000 | 783997.945 | 25-SEP-14:00 | 228236.782 | 263066.793 | 88925.651 | 0 | 153379.587 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7641.32 | 0 | 0
October | 1353230000000 | 746564.599 | 05-OCT-10:39 | 228236.782 | 263066.793 | 82979.346 | 0 | 118479.153 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 11054.712 | 0 | 0
November | 1264440000000 | 725379.523 | 09-NOV-15:00 | 228236.782 | 263066.793 | 85486.775 | 0 | 98542.781 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7298.58 | 0 | 0
December | 1246540000000 | 728258.423 | 19-DEC-12:00 | 228236.782 | 263066.793 | 83527.641 | 0 | 103272.568 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7406.827 | 0 | 0
Annual Sum or Average | 15562700000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1100960000000 | 714907.978 |  | 228236.782 | 263066.793 | 81005.41 | 0 | 90475.983 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 7298.58 | 0 | 0
Maximum of Months | 1437480000000 | 820681.741 |  | 228236.782 | 263066.793 | 101212.304 | 0 | 177963.311 | 0 | 27643.011 | 15104.801 | 0 | 0 | 0 | 0 | 11054.712 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 187625.86 | 29582.08 | 0 | 217207.94
Cost per Total Building Area ($/m2) | 8.37 | 1.32 | 0 | 9.69
Cost per Net Conditioned Building Area ($/m2) | 8.37 | 1.32 | 0 | 9.69
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 21369.39 | 953.04 | 953.04
Net Site Energy | 21369.39 | 953.04 | 953.04
Total Source Energy | 64033.24 | 2855.79 | 2855.79
Net Source Energy | 64033.24 | 2855.79 | 2855.79
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2012.85 | 0 | 0 | 0 | 0
Cooling | 2210.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2979.35 | 0 | 0 | 0 | 0 | 0
Pumps | 853.46 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 459.4 | 0 | 0 | 0 | 0 | 16648.77
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 438.12 | 0 | 0 | 0 | 4037.86
Refrigeration | 205.16 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16377.41 | 4991.98 | 0 | 0 | 0 | 20686.64
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 16377.41 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 16377.41 | 100
Total On-Site and Utility Electric Sources | 16377.41 | 100
Total Electricity End Uses | 16377.41 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.25 | 0.318 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.25 | 0.318 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.25 | 0.318 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.25 | 0.318 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.25 | 0.318 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.25 | 0.318 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.25 | 0.318 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.25 | 0.318 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.25 | 0.318 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.25 | 0.318 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.25 | 0.318 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.25 | 0.318 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.25 | 0.318 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.25 | 0.318 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.25 | 0.318 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.25 | 0.318 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1551859.81 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5901745.43 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1445010.45
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 34.35 | 81417.64 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 57.41 | 136072.45 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32792.95 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14220.65 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 20394.31 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 301294.7561 | 459.0517 | 1745.2652 | 0 | 0.0034 | 8702887.957 | 123565.4211
February | 274596.0575 | 431.4052 | 1713.0992 | 0 | 0.0033 | 8543032.747 | 113970.3631
March | 308342.8332 | 486.0265 | 1938.7027 | 0 | 0.0037 | 9668154.1245 | 128143.5213
April | 319149.3332 | 512.7043 | 2097.2959 | 0 | 0.004 | 10459400 | 133636.9532
May | 339813.9932 | 547.0683 | 2244.0611 | 0 | 0.0042 | 11191400 | 142411.1108
June | 349736.7832 | 564.5416 | 2323.6743 | 0 | 0.0044 | 11588500 | 146725.3623
July | 365580.693 | 590.38 | 2431.4175 | 0 | 0.0046 | 12125800 | 153399.7413
August | 370321.0181 | 598.1319 | 2463.8533 | 0 | 0.0046 | 12287600 | 155398.857
September | 339610.9637 | 547.8081 | 2252.746 | 0 | 0.0042 | 11234700 | 142436.8878
October | 330992.9597 | 531.4904 | 2172.8669 | 0 | 0.0041 | 10836300 | 138571.2308
November | 296554.7261 | 468.582 | 1875.2679 | 0 | 0.0036 | 9351853.1521 | 123362.6579
December | 298235.5106 | 458.6702 | 1767.7701 | 0 | 0.0034 | 8815288.3563 | 122755.5967
Annual Sum or Average | 3894229.6277 | 6195.8603 | 25026.0201 | 0 | 0.0474 | 124805000 | 1624377.7033
Minimum of Months | 274596.0575 | 431.4052 | 1713.0992 | 0 | 0.0033 | 8543032.747 | 113970.3631
Maximum of Months | 370321.0181 | 598.1319 | 2463.8533 | 0 | 0.0046 | 12287600 | 155398.857
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1142030000000 | 733112.167 | 18-JAN-14:00 | 228236.782 | 263066.793 | 97117.821 | 0 | 83868.108 | 0 | 34695.136 | 18965.762 | 0 | 0 | 0 | 0 | 7161.765 | 0 | 0
February | 1121050000000 | 743482.57 | 08-FEB-15:00 | 228236.782 | 263066.793 | 98846.088 | 0 | 92478.044 | 0 | 34691.508 | 18965.762 | 0 | 0 | 0 | 0 | 7197.593 | 0 | 0
March | 1268690000000 | 758998.318 | 31-MAR-14:00 | 228236.782 | 263066.793 | 100732.285 | 0 | 105934.832 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7372.101 | 0 | 0
April | 1372530000000 | 799671.796 | 21-APR-14:00 | 228236.782 | 263066.793 | 104721.324 | 0 | 142204.961 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7786.411 | 0 | 0
May | 1468580000000 | 820621.77 | 31-MAY-14:00 | 228236.782 | 263066.793 | 107623.241 | 0 | 160220.667 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7818.763 | 0 | 0
June | 1520690000000 | 882018.244 | 27-JUN-14:00 | 228236.782 | 263066.793 | 116028.072 | 0 | 213195.9 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7835.173 | 0 | 0
July | 1591200000000 | 876282.117 | 25-JUL-14:00 | 228236.782 | 263066.793 | 115095.996 | 0 | 208271.774 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7955.248 | 0 | 0
August | 1612430000000 | 904164.936 | 02-AUG-13:30 | 228236.782 | 263066.793 | 110591.197 | 0 | 240600.815 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 8013.825 | 0 | 0
September | 1474270000000 | 858121.166 | 01-SEP-14:00 | 228236.782 | 263066.793 | 113513.462 | 0 | 191748.914 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7899.691 | 0 | 0
October | 1421980000000 | 797650.388 | 03-OCT-14:00 | 228236.782 | 263066.793 | 104066.889 | 0 | 140856.66 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7767.74 | 0 | 0
November | 1227190000000 | 745891.574 | 10-NOV-15:39 | 228236.782 | 263066.793 | 99840.567 | 0 | 93869.528 | 0 | 34689.897 | 18965.762 | 0 | 0 | 0 | 0 | 7222.245 | 0 | 0
December | 1156780000000 | 742517.245 | 05-DEC-14:00 | 228236.782 | 263066.793 | 97604.538 | 0 | 92698.874 | 0 | 34693.611 | 18965.762 | 0 | 0 | 0 | 0 | 7250.885 | 0 | 0
Annual Sum or Average | 16377400000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1121050000000 | 733112.167 |  | 228236.782 | 263066.793 | 97117.821 | 0 | 83868.108 | 0 | 34689.762 | 18965.762 | 0 | 0 | 0 | 0 | 7161.765 | 0 | 0
Maximum of Months | 1612430000000 | 904164.936 |  | 228236.782 | 263066.793 | 116028.072 | 0 | 240600.815 | 0 | 34695.136 | 18965.762 | 0 | 0 | 0 | 0 | 8013.825 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 399628.65 | 39833.06 | 0 | 439461.72
Cost per Total Building Area ($/m2) | 17.82 | 1.78 | 0 | 19.6
Cost per Net Conditioned Building Area ($/m2) | 17.82 | 1.78 | 0 | 19.6
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 19277.46 | 859.75 | 859.75
Net Site Energy | 19277.46 | 859.75 | 859.75
Total Source Energy | 49654.47 | 2214.52 | 2214.52
Net Source Energy | 49654.47 | 2214.52 | 2214.52
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1882.85 | 0 | 0 | 0 | 0
Cooling | 989.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2473.6 | 0 | 0 | 0 | 0 | 0
Pumps | 616.55 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 332.96 | 0 | 0 | 0 | 0 | 4390.28
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 573.28 | 0 | 0 | 0 | 4037.86
Refrigeration | 197.57 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14280.32 | 4997.14 | 0 | 0 | 0 | 8428.14
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 14280.32 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 14280.32 | 100
Total On-Site and Utility Electric Sources | 14280.32 | 100
Total Electricity End Uses | 14280.32 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 6.88 | 0.39 | 0.39 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 6.88 | 0.39 | 0.39 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 6.88 | 0.39 | 0.39 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 6.88 | 0.39 | 0.39 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.39 | 0.39 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.39 | 0.39 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 6.88 | 0.39 | 0.39 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 6.88 | 0.39 | 0.39 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.39 | 0.39 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.39 | 0.39 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.39 | 0.39 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.39 | 0.39 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.39 | 0.39 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.39 | 0.39 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.39 | 0.39 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.39 | 0.39 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.39 | 0.39 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 6.88 | 0.39 | 0.39 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 6.88 | 0.39 | 0.39 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.39 | 0.39 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 6.88 | 0.39 | 0.39 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 6.88 | 0.39 | 0.39 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.88 | 0.39 | 0.39 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 6.88 | 0.39 | 0.39 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.88 | 0.39 | 0.39 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 6.88 | 0.39 | 0.39 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 6.88 | 0.39 | 0.39 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 6.88 | 0.39 | 0.39 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.39 | 0.39 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 6.88 | 0.39 | 0.39 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 6.88 | 0.39 | 0.39 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 6.88 | 0.39 | 0.39 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 6.88 | 0.39 | 0.39 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1156487.53 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5217126.4 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1076860.52
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 30.17 | 71520.2 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 46.76 | 110843.9 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28988.88 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10597.61 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 15198.38 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 132792.0232 | 115.6163 | 884.8434 | 0 | 0.0005 | 5337828.6533 | 48659.165
February | 112911.7738 | 97.8084 | 841.6614 | 0 | 0.0004 | 5077748.6415 | 41646.8305
March | 126406.7487 | 109.5378 | 935.1761 | 0 | 0.0005 | 5641893.6428 | 46602.7735
April | 119464.3516 | 103.3113 | 921.4877 | 0 | 0.0005 | 5559470.4561 | 44158.2356
May | 125064.1631 | 107.959 | 999.5668 | 0 | 0.0005 | 6030673.1748 | 46334.5558
June | 122728.5842 | 105.8466 | 998.12 | 0 | 0.0005 | 6022010.9894 | 45521.7938
July | 126066.2175 | 108.6714 | 1034.8887 | 0 | 0.0005 | 6243886.9231 | 46789.1345
August | 129280.8485 | 111.4338 | 1062.8153 | 0 | 0.0005 | 6412384.7759 | 47986.9266
September | 124721.0693 | 107.5156 | 1023.171 | 0 | 0.0005 | 6173186.8349 | 46287.8262
October | 127157.3294 | 109.7212 | 1024.2954 | 0 | 0.0005 | 6179898.8692 | 47134.4501
November | 122809.5234 | 106.2536 | 938.4587 | 0 | 0.0005 | 5661823.1949 | 45367.783
December | 128623.7412 | 111.861 | 879.6387 | 0 | 0.0005 | 5306536.2052 | 47200.6362
Annual Sum or Average | 1498026.3738 | 1295.5361 | 11544.1233 | 0 | 0.0057 | 69647300 | 553690.111
Minimum of Months | 112911.7738 | 97.8084 | 841.6614 | 0 | 0.0004 | 5077748.6415 | 41646.8305
Maximum of Months | 132792.0232 | 115.6163 | 1062.8153 | 0 | 0.0005 | 6412384.7759 | 48659.165
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1094460000000 | 681481.083 | 27-JAN-15:00 | 228236.782 | 263066.793 | 83163.58 | 0 | 60114.262 | 0 | 25875.001 | 14133.794 | 0 | 0 | 0 | 0 | 6890.871 | 0 | 0
February | 1041130000000 | 705508.123 | 15-FEB-15:00 | 228236.782 | 263066.793 | 84953.003 | 0 | 81899.432 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7347.519 | 0 | 0
March | 1156800000000 | 685466.261 | 01-MAR-12:00 | 228236.782 | 263066.793 | 82749.332 | 0 | 64351.506 | 0 | 25875.609 | 14133.794 | 0 | 0 | 0 | 0 | 7052.445 | 0 | 0
April | 1139900000000 | 708190.027 | 13-APR-14:00 | 228236.782 | 263066.793 | 86842.069 | 0 | 82782.493 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7257.297 | 0 | 0
May | 1236510000000 | 721887.857 | 26-MAY-13:00 | 228236.782 | 263066.793 | 85523.615 | 0 | 97702.242 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7353.832 | 0 | 0
June | 1234740000000 | 728715.528 | 16-JUN-14:00 | 228236.782 | 263066.793 | 89497.982 | 0 | 100414.556 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7494.822 | 0 | 0
July | 1280230000000 | 756426.069 | 03-JUL-12:00 | 228236.782 | 263066.793 | 87131.299 | 0 | 130246.36 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7740.242 | 0 | 0
August | 1314780000000 | 746684.708 | 15-AUG-11:00 | 228236.782 | 263066.793 | 84559.762 | 0 | 123220.777 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7596 | 0 | 0
September | 1265740000000 | 781900.925 | 28-SEP-14:00 | 228236.782 | 263066.793 | 93164.451 | 0 | 149547.1 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7881.205 | 0 | 0
October | 1267110000000 | 720628.787 | 31-OCT-12:00 | 228236.782 | 263066.793 | 84316.875 | 0 | 97630.727 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 7373.016 | 0 | 0
November | 1160890000000 | 698583.676 | 16-NOV-15:00 | 228236.782 | 263066.793 | 82528.993 | 0 | 77670.124 | 0 | 25890.735 | 14133.794 | 0 | 0 | 0 | 0 | 7056.454 | 0 | 0
December | 1088040000000 | 681146.641 | 07-DEC-15:39 | 228236.782 | 263066.793 | 82745.78 | 0 | 60114.262 | 0 | 25876.401 | 14133.794 | 0 | 0 | 0 | 0 | 6972.829 | 0 | 0
Annual Sum or Average | 14280300000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1041130000000 | 681146.641 |  | 228236.782 | 263066.793 | 82528.993 | 0 | 60114.262 | 0 | 25870.799 | 14133.794 | 0 | 0 | 0 | 0 | 6890.871 | 0 | 0
Maximum of Months | 1314780000000 | 781900.925 |  | 228236.782 | 263066.793 | 93164.451 | 0 | 149547.1 | 0 | 25890.735 | 14133.794 | 0 | 0 | 0 | 0 | 7881.205 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 513270.14 | 42432.52 | 0 | 555702.67
Cost per Total Building Area ($/m2) | 22.89 | 1.89 | 0 | 24.78
Cost per Net Conditioned Building Area ($/m2) | 22.89 | 1.89 | 0 | 24.78
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 25116.9 | 1120.18 | 1120.18
Net Site Energy | 25116.9 | 1120.18 | 1120.18
Total Source Energy | 67202.67 | 2997.14 | 2997.14
Net Source Energy | 67202.67 | 2997.14 | 2997.14
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 5979.23 | 0 | 0 | 0 | 0
Cooling | 2143.26 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2680.79 | 0 | 0 | 0 | 0 | 0
Pumps | 861.64 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 459.05 | 0 | 0 | 0 | 0 | 9734.13
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 584.18 | 0 | 0 | 0 | 4037.86
Refrigeration | 197.96 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16012.49 | 9104.41 | 0 | 0 | 0 | 13771.99
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 16012.49 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 16012.49 | 100
Total On-Site and Utility Electric Sources | 16012.49 | 100
Total Electricity End Uses | 16012.49 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.39 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.39 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.39 | 0.495 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.39 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.39 | 0.495 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2093167.18 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6063486.82 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1949047.48
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 31.76 | 75283.71 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 51.76 | 122682.13 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33691.66 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19180.98 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 27508.09 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 276057.3282 | 447.5795 | 1088.9213 | 0 | 0.0046 | 67695.1582 | 113557.2537
February | 238173.5579 | 393.2454 | 978.6233 | 0 | 0.0041 | 60841.4205 | 98621.7153
March | 246845.6907 | 437.7182 | 1180.7555 | 0 | 0.0049 | 73421.0408 | 104969.8607
April | 230352.9913 | 430.4134 | 1223.0121 | 0 | 0.005 | 76056.7257 | 99962.6248
May | 264170.025 | 508.8053 | 1486.5119 | 0 | 0.006 | 92448.3266 | 116027.9627
June | 281572.5234 | 548.1009 | 1616.3381 | 0 | 0.0065 | 100524.2168 | 124199.7075
July | 299391.8505 | 583.9323 | 1724.949 | 0 | 0.007 | 107279.3645 | 132164.3653
August | 305024.947 | 595.05 | 1758.1275 | 0 | 0.0071 | 109342.8646 | 134663.033
September | 267143.8937 | 517.9944 | 1522.3574 | 0 | 0.0062 | 94678.6948 | 117650.6175
October | 254584.4233 | 480.5852 | 1378.6949 | 0 | 0.0056 | 85739.9612 | 110925.5859
November | 243513.4286 | 439.2296 | 1205.7876 | 0 | 0.0049 | 74980.3108 | 104231.3211
December | 259208.2853 | 429.7813 | 1075.0229 | 0 | 0.0045 | 66835.404 | 107496.7857
Annual Sum or Average | 3166038.9451 | 5812.4355 | 16239.1015 | 0 | 0.0664 | 1009843.4886 | 1364470.8331
Minimum of Months | 230352.9913 | 393.2454 | 978.6233 | 0 | 0.0041 | 60841.4205 | 98621.7153
Maximum of Months | 305024.947 | 595.05 | 1758.1275 | 0 | 0.0071 | 109342.8646 | 134663.033
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1073400000000 | 743301.404 | 09-JAN-12:00 | 228236.782 | 263066.793 | 85549.876 | 0 | 87192.829 | 0 | 46804.533 | 25581.248 | 0 | 0 | 0 | 0 | 6869.343 | 0 | 0
February | 964726000000 | 753216.104 | 15-FEB-15:00 | 228236.782 | 263066.793 | 88027.021 | 0 | 94579.128 | 0 | 46777.235 | 25581.248 | 0 | 0 | 0 | 0 | 6947.897 | 0 | 0
March | 1164190000000 | 797471.792 | 09-MAR-15:00 | 228236.782 | 263066.793 | 88768.687 | 0 | 137538.251 | 0 | 46765.12 | 25581.248 | 0 | 0 | 0 | 0 | 7514.911 | 0 | 0
April | 1205990000000 | 789407.814 | 04-APR-14:00 | 228236.782 | 263066.793 | 89760.119 | 0 | 128538.428 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 7460.57 | 0 | 0
May | 1465900000000 | 875441.162 | 31-MAY-14:00 | 228236.782 | 263066.793 | 90393.402 | 0 | 213848.473 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 7550.589 | 0 | 0
June | 1593950000000 | 978356.735 | 30-JUN-14:00 | 228236.782 | 263066.793 | 99443.178 | 0 | 307297.524 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 7967.336 | 0 | 0
July | 1701060000000 | 1016565.858 | 25-JUL-11:00 | 228236.782 | 263066.793 | 95428.273 | 0 | 349589.645 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 7899.243 | 0 | 0
August | 1733780000000 | 1018915.371 | 17-AUG-14:20 | 228236.782 | 263066.793 | 98631.093 | 0 | 348670.768 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 7964.813 | 0 | 0
September | 1501260000000 | 867456.716 | 27-SEP-14:00 | 228236.782 | 263066.793 | 89735.888 | 0 | 206550.776 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 7521.355 | 0 | 0
October | 1359530000000 | 837785.085 | 03-OCT-10:39 | 228236.782 | 263066.793 | 88522.492 | 0 | 174393.707 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 11220.188 | 0 | 0
November | 1188920000000 | 807064.954 | 03-NOV-13:00 | 228236.782 | 263066.793 | 90100.568 | 0 | 145852.502 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 7463.188 | 0 | 0
December | 1059770000000 | 665235.623 | 08-DEC-11:09 | 228236.782 | 263066.793 | 85745.287 | 0 | 7280.937 | 0 | 46813.753 | 25581.248 | 0 | 0 | 0 | 0 | 8510.823 | 0 | 0
Annual Sum or Average | 16012500000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 964726000000 | 665235.623 |  | 228236.782 | 263066.793 | 85549.876 | 0 | 7280.937 | 0 | 46763.874 | 25581.248 | 0 | 0 | 0 | 0 | 6869.343 | 0 | 0
Maximum of Months | 1733780000000 | 1018915.371 |  | 228236.782 | 263066.793 | 99443.178 | 0 | 349589.645 | 0 | 46813.753 | 25581.248 | 0 | 0 | 0 | 0 | 11220.188 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 253038.92 | 89569.54 | 0 | 342608.46
Cost per Total Building Area ($/m2) | 11.29 | 3.99 | 0 | 15.28
Cost per Net Conditioned Building Area ($/m2) | 11.29 | 3.99 | 0 | 15.28
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 22462.46 | 1001.79 | 1001.79
Net Site Energy | 22462.46 | 1001.79 | 1001.79
Total Source Energy | 58536.57 | 2610.65 | 2610.65
Net Source Energy | 58536.57 | 2610.65 | 2610.65
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4072.91 | 0 | 0 | 0 | 0
Cooling | 1385.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3204.48 | 0 | 0 | 0 | 0 | 0
Pumps | 535.31 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 284.39 | 0 | 0 | 0 | 0 | 8993.34
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 571.11 | 0 | 0 | 0 | 4037.86
Refrigeration | 197.7 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15277.43 | 7185.03 | 0 | 0 | 0 | 13031.2
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 15277.43 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 15277.43 | 100
Total On-Site and Utility Electric Sources | 15277.43 | 100
Total Electricity End Uses | 15277.43 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.39 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.39 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.39 | 0.495 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.39 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.39 | 0.495 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1228036.9 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5880180.08 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1143483.54
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 37.65 | 89240.2 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 61.4 | 145543.33 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32673.12 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11253.26 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 16138.67 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 360402.0437 | 577.3194 | 1355.6376 | 0 | 0.0054 | 1409306.5724 | 149275.6765
February | 320223.3905 | 521.6713 | 1251.6672 | 0 | 0.005 | 1301287.1316 | 133488.6628
March | 356378.7158 | 591.1717 | 1450.3623 | 0 | 0.0057 | 1507937.6959 | 149600.1772
April | 346917.713 | 590.6443 | 1493.9492 | 0 | 0.0059 | 1553362.9189 | 147116.356
May | 383264.9087 | 659.456 | 1687.9755 | 0 | 0.0066 | 1755152.1455 | 163209.6502
June | 388314.7267 | 670.0453 | 1720.5019 | 0 | 0.0067 | 1788985.527 | 165546.4768
July | 406227.0261 | 701.3858 | 1802.2063 | 0 | 0.007 | 1873944.9493 | 173225.2723
August | 410342.2925 | 708.6113 | 1821.114 | 0 | 0.0071 | 1893606.0951 | 174991.9135
September | 378728.8307 | 652.8752 | 1674.6231 | 0 | 0.0065 | 1741276.4652 | 161398.0766
October | 362267.9881 | 617.0746 | 1561.6533 | 0 | 0.0061 | 1623761.5944 | 153654.9059
November | 339197.5405 | 559.6016 | 1363.8265 | 0 | 0.0054 | 1417944.7726 | 142086.8096
December | 361428.0378 | 577.1963 | 1349.9346 | 0 | 0.0054 | 1403364.1664 | 149527.341
Annual Sum or Average | 4413693.2142 | 7427.0529 | 18533.4515 | 0 | 0.0729 | 19269900 | 1863121.3183
Minimum of Months | 320223.3905 | 521.6713 | 1251.6672 | 0 | 0.005 | 1301287.1316 | 133488.6628
Maximum of Months | 410342.2925 | 708.6113 | 1821.114 | 0 | 0.0071 | 1893606.0951 | 174991.9135
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1117320000000 | 712898.791 | 27-JAN-15:39 | 228236.782 | 263066.793 | 108497.489 | 0 | 63833.401 | 0 | 27471.828 | 15008.221 | 0 | 0 | 0 | 0 | 6784.276 | 0 | 0
February | 1031680000000 | 734418.494 | 14-FEB-15:00 | 228236.782 | 263066.793 | 109542.363 | 0 | 83959.64 | 0 | 27467.69 | 15008.221 | 0 | 0 | 0 | 0 | 7137.006 | 0 | 0
March | 1195510000000 | 736601.17 | 02-MAR-15:09 | 228236.782 | 263066.793 | 109438.898 | 0 | 86225.543 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7158.192 | 0 | 0
April | 1231520000000 | 769385.107 | 21-APR-14:00 | 228236.782 | 263066.793 | 114798.395 | 0 | 113398.21 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7409.964 | 0 | 0
May | 1391510000000 | 789069.89 | 31-MAY-14:00 | 228236.782 | 263066.793 | 114881.907 | 0 | 132693.515 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7715.93 | 0 | 0
June | 1418330000000 | 825824.199 | 29-JUN-14:00 | 228236.782 | 263066.793 | 123341.508 | 0 | 160832.093 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7872.06 | 0 | 0
July | 1485690000000 | 829190.271 | 31-JUL-14:00 | 228236.782 | 263066.793 | 121719.286 | 0 | 165883.547 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7808.9 | 0 | 0
August | 1501270000000 | 843410.14 | 01-AUG-14:00 | 228236.782 | 263066.793 | 123175.711 | 0 | 178492.66 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7963.231 | 0 | 0
September | 1380500000000 | 787808.974 | 05-SEP-12:39 | 228236.782 | 263066.793 | 106589.744 | 0 | 140031.396 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7409.296 | 0 | 0
October | 1287340000000 | 763354.288 | 13-OCT-14:00 | 228236.782 | 263066.793 | 112957.573 | 0 | 109188.523 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 7429.654 | 0 | 0
November | 1124160000000 | 726572.722 | 08-NOV-15:39 | 228236.782 | 263066.793 | 109271.573 | 0 | 76415.315 | 0 | 27466.989 | 15008.221 | 0 | 0 | 0 | 0 | 7107.049 | 0 | 0
December | 1112600000000 | 711362.977 | 08-DEC-15:30 | 228236.782 | 263066.793 | 106927.415 | 0 | 63833.401 | 0 | 27475.278 | 15008.221 | 0 | 0 | 0 | 0 | 6815.087 | 0 | 0
Annual Sum or Average | 15277400000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1031680000000 | 711362.977 |  | 228236.782 | 263066.793 | 106589.744 | 0 | 63833.401 | 0 | 27466.742 | 15008.221 | 0 | 0 | 0 | 0 | 6784.276 | 0 | 0
Maximum of Months | 1501270000000 | 843410.14 |  | 228236.782 | 263066.793 | 123341.508 | 0 | 178492.66 | 0 | 27475.278 | 15008.221 | 0 | 0 | 0 | 0 | 7963.231 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 156904.06 | 50496.49 | 0 | 207400.55
Cost per Total Building Area ($/m2) | 7 | 2.25 | 0 | 9.25
Cost per Net Conditioned Building Area ($/m2) | 7 | 2.25 | 0 | 9.25
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 21621.04 | 964.27 | 964.27
Net Site Energy | 21621.04 | 964.27 | 964.27
Total Source Energy | 32714.2 | 1459.01 | 1459.01
Net Source Energy | 32714.2 | 1459.01 | 1459.01
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4453.71 | 0 | 0 | 0 | 0
Cooling | 845.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2560.21 | 0 | 0 | 0 | 0 | 0
Pumps | 480.15 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 256.79 | 0 | 0 | 0 | 0 | 3898.56
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 620.12 | 0 | 0 | 0 | 4037.86
Refrigeration | 194.2 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14006.2 | 7614.84 | 0 | 0 | 0 | 7936.42
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 14006.2 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 14006.2 | 100
Total On-Site and Utility Electric Sources | 14006.2 | 100
Total Electricity End Uses | 14006.2 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.39 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.39 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.39 | 0.495 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.39 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.39 | 0.495 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1326363.06 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5565779.1 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1235039.7
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 31 | 73469.68 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 48.94 | 115996.95 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30926.16 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12154.28 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 17430.86 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 112235.1072 | 137.1612 | 225.7476 | 0 | 0.001 | 2979831.2036 | 42623.5919
February | 90300.4512 | 114.459 | 207.8314 | 0 | 0.0009 | 2744227.0845 | 34732.9873
March | 98863.9718 | 126.9252 | 237.8309 | 0 | 0.001 | 3140648.3722 | 38199.4525
April | 84198.3652 | 113.3453 | 236.0603 | 0 | 0.001 | 3118215.6155 | 33094.9966
May | 79086.6843 | 113.0877 | 264.0201 | 0 | 0.0011 | 3488574.8206 | 31795.202
June | 76526.1793 | 112.0015 | 271.9138 | 0 | 0.0011 | 3593210.9408 | 31041.5977
July | 79674.1512 | 117.7023 | 290.0809 | 0 | 0.0012 | 3833414.4822 | 32435.6343
August | 81343.0359 | 120.5074 | 298.326 | 0 | 0.0012 | 3942414.7468 | 33151.4271
September | 77317.51 | 112.3422 | 269.5058 | 0 | 0.0011 | 3561291.2463 | 31275.0314
October | 83158.1259 | 115.4828 | 255.7323 | 0 | 0.001 | 3378619.8355 | 33065.0258
November | 96020.2002 | 122.6042 | 226.7113 | 0 | 0.001 | 2993688.7941 | 37028.8958
December | 111147.1523 | 136.1217 | 225.4111 | 0 | 0.001 | 2975453.3766 | 42241.4827
Annual Sum or Average | 1069870.9345 | 1441.7405 | 3009.1715 | 0 | 0.0125 | 39749600 | 420685.3251
Minimum of Months | 76526.1793 | 112.0015 | 207.8314 | 0 | 0.0009 | 2744227.0845 | 31041.5977
Maximum of Months | 112235.1072 | 137.1612 | 298.326 | 0 | 0.0012 | 3942414.7468 | 42623.5919
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1049980000000 | 642331.039 | 27-JAN-15:00 | 228236.782 | 263066.793 | 83637.739 | 0 | 14748.672 | 0 | 29708.193 | 16209.896 | 0 | 0 | 0 | 0 | 6722.964 | 0 | 0
February | 966958000000 | 698155.954 | 22-FEB-15:00 | 228236.782 | 263066.793 | 85137.235 | 0 | 68944.398 | 0 | 29668.712 | 16209.896 | 0 | 0 | 0 | 0 | 6892.138 | 0 | 0
March | 1106640000000 | 708049.195 | 29-MAR-14:00 | 228236.782 | 263066.793 | 87847.437 | 0 | 75873.845 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7154.489 | 0 | 0
April | 1098740000000 | 701029.401 | 19-APR-14:00 | 228236.782 | 263066.793 | 87898.591 | 0 | 68944.398 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7012.988 | 0 | 0
May | 1229240000000 | 738558.134 | 05-MAY-14:00 | 228236.782 | 263066.793 | 88289.958 | 0 | 105634.905 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7459.848 | 0 | 0
June | 1266110000000 | 752705.544 | 28-JUN-14:00 | 228236.782 | 263066.793 | 94714.06 | 0 | 113243.812 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7574.248 | 0 | 0
July | 1350750000000 | 780000.425 | 24-JUL-14:00 | 228236.782 | 263066.793 | 93487.49 | 0 | 141564.211 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7775.302 | 0 | 0
August | 1389150000000 | 767525.91 | 07-AUG-14:00 | 228236.782 | 263066.793 | 93676.462 | 0 | 129010.378 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7665.646 | 0 | 0
September | 1254860000000 | 773495.27 | 01-SEP-14:00 | 228236.782 | 263066.793 | 90832.745 | 0 | 137769.99 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7719.112 | 0 | 0
October | 1190490000000 | 713200.218 | 17-OCT-14:00 | 228236.782 | 263066.793 | 87175.757 | 0 | 81576.951 | 0 | 29659.952 | 16209.896 | 0 | 0 | 0 | 0 | 7274.087 | 0 | 0
November | 1054860000000 | 699447.949 | 03-NOV-11:39 | 228236.782 | 263066.793 | 83270.686 | 0 | 68944.398 | 0 | 29686.414 | 16209.896 | 0 | 0 | 0 | 0 | 10032.98 | 0 | 0
December | 1048430000000 | 583756.809 | 01-DEC-11:09 | 228236.782 | 263066.793 | 82115.453 | 0 | 0 | 0 | 1862.663 | 0 | 0 | 0 | 0 | 0 | 8475.118 | 0 | 0
Annual Sum or Average | 14006200000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 966958000000 | 583756.809 |  | 228236.782 | 263066.793 | 82115.453 | 0 | 0 | 0 | 1862.663 | 0 | 0 | 0 | 0 | 0 | 6722.964 | 0 | 0
Maximum of Months | 1389150000000 | 780000.425 |  | 228236.782 | 263066.793 | 94714.06 | 0 | 141564.211 | 0 | 29708.193 | 16209.896 | 0 | 0 | 0 | 0 | 10032.98 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 255353.11 | 63759.54 | 0 | 319112.64
Cost per Total Building Area ($/m2) | 11.39 | 2.84 | 0 | 14.23
Cost per Net Conditioned Building Area ($/m2) | 11.39 | 2.84 | 0 | 14.23
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 26854.78 | 1197.68 | 1197.68
Net Site Energy | 26854.78 | 1197.68 | 1197.68
Total Source Energy | 66830.33 | 2980.54 | 2980.54
Net Source Energy | 66830.33 | 2980.54 | 2980.54
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 8385.82 | 0 | 0 | 0 | 0
Cooling | 1624.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2679.47 | 0 | 0 | 0 | 0 | 0
Pumps | 729.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 385.58 | 0 | 0 | 0 | 0 | 7737.58
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 644.77 | 0 | 0 | 0 | 4037.86
Refrigeration | 194.79 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15283.17 | 11571.61 | 0 | 0 | 0 | 11775.44
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 15283.17 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 15283.17 | 100
Total On-Site and Utility Electric Sources | 15283.17 | 100
Total Electricity End Uses | 15283.17 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.39 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.39 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.39 | 0.495 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.39 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.39 | 0.495 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2081491.07 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6249485.47 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1938175.29
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 31.85 | 75487.53 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 51.72 | 122592.97 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34725.16 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19073.98 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 27354.64 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 480605.6189 | 767.4458 | 1987.4392 | 0 | 0.0062 | 457391.3329 | 198004.4207
February | 419989.4791 | 680.4496 | 1795.5083 | 0 | 0.0056 | 413236.9908 | 173967.9667
March | 452410.6124 | 752.8548 | 2053.2749 | 0 | 0.0063 | 472595.1356 | 189297.9741
April | 424653.8046 | 738.301 | 2116.9507 | 0 | 0.0065 | 487300.6971 | 180708.7098
May | 491085.7636 | 876.0418 | 2581.4595 | 0 | 0.0078 | 594257.6438 | 211105.0188
June | 534940.3648 | 961.1728 | 2853.3469 | 0 | 0.0086 | 656856.0348 | 230616.6228
July | 570787.7304 | 1026.6515 | 3050.9615 | 0 | 0.0092 | 702349.4309 | 246172.8566
August | 575297.7238 | 1034.6788 | 3074.5612 | 0 | 0.0093 | 707782.1109 | 248109.8681
September | 511731.2709 | 917.4311 | 2717.3218 | 0 | 0.0082 | 625539.5922 | 220415.9761
October | 468443.6863 | 824.6628 | 2396.5679 | 0 | 0.0073 | 551680.3361 | 200321.2027
November | 428480.7239 | 723.4686 | 2007.2259 | 0 | 0.0062 | 462012.5342 | 180282.9462
December | 466714.6773 | 753.3698 | 1978.5864 | 0 | 0.0062 | 455367.8804 | 193056.4706
Annual Sum or Average | 5825141.4558 | 10056.5282 | 28613.2042 | 0 | 0.0875 | 6586369.7198 | 2472060.0331
Minimum of Months | 419989.4791 | 680.4496 | 1795.5083 | 0 | 0.0056 | 413236.9908 | 173967.9667
Maximum of Months | 575297.7238 | 1034.6788 | 3074.5612 | 0 | 0.0093 | 707782.1109 | 248109.8681
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1061340000000 | 661379.492 | 17-JAN-15:09 | 228236.782 | 263066.793 | 85861.188 | 0 | 5606.015 | 0 | 46534.891 | 25438.551 | 0 | 0 | 0 | 0 | 6635.273 | 0 | 0
February | 958885000000 | 674841.731 | 28-FEB-11:09 | 228236.782 | 263066.793 | 86157.782 | 0 | 16891.253 | 0 | 46531.544 | 25438.551 | 0 | 0 | 0 | 0 | 8519.026 | 0 | 0
March | 1096620000000 | 768442.165 | 31-MAR-14:00 | 228236.782 | 263066.793 | 89700.274 | 0 | 108195.979 | 0 | 46503.433 | 25438.551 | 0 | 0 | 0 | 0 | 7300.354 | 0 | 0
April | 1130740000000 | 770743.205 | 28-APR-10:39 | 228236.782 | 263066.793 | 88951.232 | 0 | 108195.979 | 0 | 46507.149 | 25438.551 | 0 | 0 | 0 | 0 | 10346.719 | 0 | 0
May | 1378930000000 | 834361.518 | 30-MAY-14:00 | 228236.782 | 263066.793 | 90018.53 | 0 | 173460.005 | 0 | 46503.433 | 25438.551 | 0 | 0 | 0 | 0 | 7637.424 | 0 | 0
June | 1524180000000 | 975473.531 | 08-JUN-12:00 | 228236.782 | 263066.793 | 94885.638 | 0 | 309432.576 | 0 | 46503.433 | 25438.551 | 0 | 0 | 0 | 0 | 7909.759 | 0 | 0
July | 1629750000000 | 962917.133 | 13-JUL-12:00 | 228236.782 | 263066.793 | 96630.156 | 0 | 295099.916 | 0 | 46503.433 | 25438.551 | 0 | 0 | 0 | 0 | 7941.502 | 0 | 0
August | 1642360000000 | 1013904.738 | 04-AUG-14:00 | 228236.782 | 263066.793 | 98168.526 | 0 | 344678.533 | 0 | 46503.433 | 25438.551 | 0 | 0 | 0 | 0 | 7812.12 | 0 | 0
September | 1451520000000 | 852214.224 | 07-SEP-12:00 | 228236.782 | 263066.793 | 91244.596 | 0 | 190314.111 | 0 | 46503.433 | 25438.551 | 0 | 0 | 0 | 0 | 7409.958 | 0 | 0
October | 1280130000000 | 811818.33 | 31-OCT-11:20 | 228236.782 | 263066.793 | 88578.048 | 0 | 151384.571 | 0 | 46504.678 | 25438.551 | 0 | 0 | 0 | 0 | 8608.908 | 0 | 0
November | 1072070000000 | 809381.017 | 02-NOV-11:09 | 228236.782 | 263066.793 | 88055.888 | 0 | 149471.063 | 0 | 46508.851 | 25438.551 | 0 | 0 | 0 | 0 | 8603.089 | 0 | 0
December | 1056650000000 | 674282.498 | 12-DEC-12:00 | 228236.782 | 263066.793 | 86498.032 | 0 | 17849.747 | 0 | 46552.926 | 25438.551 | 0 | 0 | 0 | 0 | 6639.667 | 0 | 0
Annual Sum or Average | 15283200000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 958885000000 | 661379.492 |  | 228236.782 | 263066.793 | 85861.188 | 0 | 5606.015 | 0 | 46503.433 | 25438.551 | 0 | 0 | 0 | 0 | 6635.273 | 0 | 0
Maximum of Months | 1642360000000 | 1013904.738 |  | 228236.782 | 263066.793 | 98168.526 | 0 | 344678.533 | 0 | 46552.926 | 25438.551 | 0 | 0 | 0 | 0 | 10346.719 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 413147.17 | 98482.86 | 0 | 511630.03
Cost per Total Building Area ($/m2) | 18.43 | 4.39 | 0 | 22.82
Cost per Net Conditioned Building Area ($/m2) | 18.43 | 4.39 | 0 | 22.82
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 24262.7 | 1082.08 | 1082.08
Net Site Energy | 24262.7 | 1082.08 | 1082.08
Total Source Energy | 59249.58 | 2642.45 | 2642.45
Net Source Energy | 59249.58 | 2642.45 | 2642.45
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 6365.48 | 0 | 0 | 0 | 0
Cooling | 1035.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3141.43 | 0 | 0 | 0 | 0 | 0
Pumps | 441.46 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 232.75 | 0 | 0 | 0 | 0 | 6637
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 641.61 | 0 | 0 | 0 | 4037.86
Refrigeration | 193.76 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14714.6 | 9548.1 | 0 | 0 | 0 | 10674.86
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 14714.6 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 14714.6 | 100
Total On-Site and Utility Electric Sources | 14714.6 | 100
Total Electricity End Uses | 14714.6 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.39 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.39 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.39 | 0.495 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.39 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.39 | 0.495 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1220812.78 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6111521.11 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1136756.81
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 37.23 | 88240.28 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 60.4 | 143169 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33958.57 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11187.06 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 16043.74 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 380003.8638 | 595.297 | 1356.722 | 0 | 0.0055 | 1410330.4556 | 156078.0316
February | 333342.4437 | 528.8317 | 1226.025 | 0 | 0.0049 | 1274523.0328 | 137563.4657
March | 364967.1197 | 591.6493 | 1410.7895 | 0 | 0.0056 | 1466695.9139 | 151854.8052
April | 342854.9797 | 573.4636 | 1420.9012 | 0 | 0.0056 | 1477340.7314 | 144386.7222
May | 361996.5501 | 616.3161 | 1558.8803 | 0 | 0.0061 | 1620876.2821 | 153510.7268
June | 369624.0322 | 635.552 | 1625.5535 | 0 | 0.0064 | 1690243.1608 | 157358.3215
July | 399753.5176 | 689.3902 | 1769.0568 | 0 | 0.0069 | 1839470.6229 | 170384.5236
August | 398221.3771 | 686.5382 | 1761.1408 | 0 | 0.0069 | 1831238.1159 | 169710.9055
September | 358869.9135 | 615.1977 | 1568.1748 | 0 | 0.0061 | 1630568.6823 | 152597.2761
October | 354503.7104 | 595.9231 | 1485.2832 | 0 | 0.0058 | 1544300.829 | 149584.2419
November | 347135.73 | 561.305 | 1334.0799 | 0 | 0.0053 | 1386935.6803 | 144294.5254
December | 376723.9947 | 588.2662 | 1334.7674 | 0 | 0.0054 | 1387492.9662 | 154545.2398
Annual Sum or Average | 4387997.2324 | 7277.73 | 17851.3744 | 0 | 0.0705 | 18560000 | 1841868.7853
Minimum of Months | 333342.4437 | 528.8317 | 1226.025 | 0 | 0.0049 | 1274523.0328 | 137563.4657
Maximum of Months | 399753.5176 | 689.3902 | 1769.0568 | 0 | 0.0069 | 1839470.6229 | 170384.5236
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1118130000000 | 711937.539 | 24-JAN-13:00 | 228236.782 | 263066.793 | 103879.653 | 0 | 67519.998 | 0 | 27307.608 | 14919.933 | 0 | 0 | 0 | 0 | 7006.773 | 0 | 0
February | 1010460000000 | 709058.138 | 07-FEB-15:20 | 228236.782 | 263066.793 | 105273.878 | 0 | 63457.891 | 0 | 27311.407 | 14919.933 | 0 | 0 | 0 | 0 | 6791.455 | 0 | 0
March | 1162810000000 | 738068.512 | 30-MAR-14:00 | 228236.782 | 263066.793 | 108083.493 | 0 | 89265.189 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7190.719 | 0 | 0
April | 1171250000000 | 751688.876 | 25-APR-14:00 | 228236.782 | 263066.793 | 109454.336 | 0 | 101268.516 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7436.912 | 0 | 0
May | 1285050000000 | 770721.823 | 23-MAY-14:00 | 228236.782 | 263066.793 | 112783.472 | 0 | 116863.427 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7545.812 | 0 | 0
June | 1340050000000 | 800760.938 | 28-JUN-13:00 | 228236.782 | 263066.793 | 115422.291 | 0 | 143981.555 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7827.98 | 0 | 0
July | 1458350000000 | 814316.181 | 25-JUL-12:00 | 228236.782 | 263066.793 | 105066.254 | 0 | 168399.57 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7321.246 | 0 | 0
August | 1451830000000 | 815154.726 | 30-AUG-13:00 | 228236.782 | 263066.793 | 116518.563 | 0 | 157184.362 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7922.689 | 0 | 0
September | 1292730000000 | 781144.244 | 06-SEP-14:00 | 228236.782 | 263066.793 | 111803.918 | 0 | 128165.021 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7646.193 | 0 | 0
October | 1224340000000 | 768312.319 | 05-OCT-14:00 | 228236.782 | 263066.793 | 111274.285 | 0 | 115978.521 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 7530.4 | 0 | 0
November | 1099580000000 | 727575.658 | 10-NOV-13:00 | 228236.782 | 263066.793 | 105002.648 | 0 | 81874.309 | 0 | 27307.322 | 14919.933 | 0 | 0 | 0 | 0 | 7167.87 | 0 | 0
December | 1100020000000 | 708091.54 | 21-DEC-15:00 | 228236.782 | 263066.793 | 104257.628 | 0 | 63457.891 | 0 | 27318.257 | 14919.933 | 0 | 0 | 0 | 0 | 6834.257 | 0 | 0
Annual Sum or Average | 14714600000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1010460000000 | 708091.54 |  | 228236.782 | 263066.793 | 103879.653 | 0 | 63457.891 | 0 | 27305.604 | 14919.933 | 0 | 0 | 0 | 0 | 6791.455 | 0 | 0
Maximum of Months | 1458350000000 | 815154.726 |  | 228236.782 | 263066.793 | 116518.563 | 0 | 168399.57 | 0 | 27318.257 | 14919.933 | 0 | 0 | 0 | 0 | 7922.689 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 151130.74 | 66979.32 | 0 | 218110.05
Cost per Total Building Area ($/m2) | 6.74 | 2.99 | 0 | 9.73
Cost per Net Conditioned Building Area ($/m2) | 6.74 | 2.99 | 0 | 9.73
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 29341.68 | 1308.6 | 1308.6
Net Site Energy | 29341.68 | 1308.6 | 1308.6
Total Source Energy | 67280.1 | 3000.6 | 3000.6
Net Source Energy | 67280.1 | 3000.6 | 3000.6
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 11076.3 | 0 | 0 | 0 | 0
Cooling | 1478.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2680.63 | 0 | 0 | 0 | 0 | 0
Pumps | 659.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 345.38 | 0 | 0 | 0 | 0 | 6970.85
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 697.09 | 0 | 0 | 0 | 4037.86
Refrigeration | 193.33 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15027.28 | 14314.4 | 0 | 0 | 0 | 11008.72
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 15027.28 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 15027.28 | 100
Total On-Site and Utility Electric Sources | 15027.28 | 100
Total Electricity End Uses | 15027.28 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.39 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.39 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.39 | 0.495 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.39 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.39 | 0.495 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1949321.58 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6362681.97 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1815105.99
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 31.8 | 75380.22 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 51.8 | 122777.41 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35354.14 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17862.83 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 25617.69 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 392748.4084 | 570.24 | 697.7832 | 0 | 0.0054 | 458144.4886 | 156361.6094
February | 333648.7356 | 495.8792 | 630.0568 | 0 | 0.0048 | 413748.3348 | 133926.9586
March | 327399.775 | 519.5153 | 725.461 | 0 | 0.0055 | 476590.9999 | 134565.6761
April | 291124.4352 | 495.1174 | 753.0669 | 0 | 0.0056 | 494891.7759 | 122826.0182
May | 323060.4566 | 571.4982 | 907.5312 | 0 | 0.0067 | 596494.892 | 138409.203
June | 344328.509 | 615.3378 | 987.5174 | 0 | 0.0072 | 649092.051 | 148115.2817
July | 364053.6963 | 651.4347 | 1046.8451 | 0 | 0.0077 | 688091.1738 | 156681.1334
August | 368265.3817 | 658.8488 | 1058.5579 | 0 | 0.0077 | 695789.5195 | 158482.0712
September | 317540.4247 | 563.9677 | 899.3001 | 0 | 0.0066 | 591093.6416 | 136257.8306
October | 297167.9838 | 505.9959 | 770.6544 | 0 | 0.0057 | 506452.305 | 125433.1758
November | 310510.2244 | 492.1431 | 686.1739 | 0 | 0.0052 | 450778.5356 | 127569.1626
December | 369912.8424 | 548.0065 | 692.7757 | 0 | 0.0053 | 454924.4662 | 148314.2711
Annual Sum or Average | 4039760.8729 | 6687.9847 | 9855.7236 | 0 | 0.0734 | 6476092.1838 | 1686942.3919
Minimum of Months | 291124.4352 | 492.1431 | 630.0568 | 0 | 0.0048 | 413748.3348 | 122826.0182
Maximum of Months | 392748.4084 | 658.8488 | 1058.5579 | 0 | 0.0077 | 695789.5195 | 158482.0712
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1063090000000 | 592417.712 | 13-JAN-11:39 | 228236.782 | 263066.793 | 85084.029 | 0 | 0 | 0 | 7226.13 | 0 | 0 | 0 | 0 | 0 | 8803.979 | 0 | 0
February | 960072000000 | 592131.814 | 03-FEB-11:39 | 228236.782 | 263066.793 | 84811.764 | 0 | 0 | 0 | 7209.572 | 0 | 0 | 0 | 0 | 0 | 8806.902 | 0 | 0
March | 1105890000000 | 757168.817 | 23-MAR-14:00 | 228236.782 | 263066.793 | 90146.309 | 0 | 101325.804 | 0 | 43555.607 | 23823.266 | 0 | 0 | 0 | 0 | 7014.255 | 0 | 0
April | 1148360000000 | 758552.039 | 14-APR-14:00 | 228236.782 | 263066.793 | 91297.963 | 0 | 101335.022 | 0 | 43555.331 | 23823.266 | 0 | 0 | 0 | 0 | 7236.882 | 0 | 0
May | 1384120000000 | 826531.931 | 31-MAY-11:00 | 228236.782 | 263066.793 | 92440.455 | 0 | 167780.672 | 0 | 43555.331 | 23823.266 | 0 | 0 | 0 | 0 | 7628.632 | 0 | 0
June | 1506170000000 | 933099.367 | 29-JUN-14:00 | 228236.782 | 263066.793 | 100297.923 | 0 | 266224.967 | 0 | 43555.331 | 23823.266 | 0 | 0 | 0 | 0 | 7894.305 | 0 | 0
July | 1596660000000 | 957553.524 | 13-JUL-14:00 | 228236.782 | 263066.793 | 95341.183 | 0 | 295672.521 | 0 | 43555.331 | 23823.266 | 0 | 0 | 0 | 0 | 7857.648 | 0 | 0
August | 1614530000000 | 936598.086 | 25-AUG-14:00 | 228236.782 | 263066.793 | 97095.626 | 0 | 273006.296 | 0 | 43555.331 | 23823.266 | 0 | 0 | 0 | 0 | 7813.991 | 0 | 0
September | 1371590000000 | 829886.584 | 14-SEP-14:00 | 228236.782 | 263066.793 | 95958.159 | 0 | 167543.82 | 0 | 43555.331 | 23823.266 | 0 | 0 | 0 | 0 | 7702.433 | 0 | 0
October | 1175180000000 | 765596.639 | 06-OCT-14:00 | 228236.782 | 263066.793 | 91575.356 | 0 | 107970.802 | 0 | 43555.331 | 23823.266 | 0 | 0 | 0 | 0 | 7368.309 | 0 | 0
November | 1046000000000 | 757357.804 | 02-NOV-15:30 | 228236.782 | 263066.793 | 90246.215 | 0 | 101325.804 | 0 | 43556.904 | 23823.266 | 0 | 0 | 0 | 0 | 7102.04 | 0 | 0
December | 1055620000000 | 591099.718 | 20-DEC-11:09 | 228236.782 | 263066.793 | 85481.934 | 0 | 0 | 0 | 6021.429 | 0 | 0 | 0 | 0 | 0 | 8292.781 | 0 | 0
Annual Sum or Average | 15027300000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 960072000000 | 591099.718 |  | 228236.782 | 263066.793 | 84811.764 | 0 | 0 | 0 | 6021.429 | 0 | 0 | 0 | 0 | 0 | 7014.255 | 0 | 0
Maximum of Months | 1614530000000 | 957553.524 |  | 228236.782 | 263066.793 | 100297.923 | 0 | 295672.521 | 0 | 43556.904 | 23823.266 | 0 | 0 | 0 | 0 | 8806.902 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 218516.05 | 113098.91 | 0 | 331614.97
Cost per Total Building Area ($/m2) | 9.75 | 5.04 | 0 | 14.79
Cost per Net Conditioned Building Area ($/m2) | 9.75 | 5.04 | 0 | 14.79
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 26610.04 | 1186.77 | 1186.77
Net Site Energy | 26610.04 | 1186.77 | 1186.77
Total Source Energy | 62573.48 | 2790.69 | 2790.69
Net Source Energy | 62573.48 | 2790.69 | 2790.69
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 9304 | 0 | 0 | 0 | 0
Cooling | 730.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2939.39 | 0 | 0 | 0 | 0 | 0
Pumps | 347.84 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 180.22 | 0 | 0 | 0 | 0 | 4537.54
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 706.59 | 0 | 0 | 0 | 4037.86
Refrigeration | 190.67 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14058.44 | 12551.6 | 0 | 0 | 0 | 8575.4
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 14058.44 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 14058.44 | 100
Total On-Site and Utility Electric Sources | 14058.44 | 100
Total Electricity End Uses | 14058.44 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.39 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.39 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.39 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.39 | 0.495 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.39 | 0.495 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.39 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.39 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.39 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.39 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.39 | 0.495 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1171314.77 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6267139.03 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1090666.87
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 35 | 82950.05 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 56.57 | 134093.58 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34823.25 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10733.48 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 15393.24 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 380717.8069 | 567.149 | 803.0382 | 0 | 0.0058 | 19035500 | 153184.7395
February | 330163.8789 | 501.3623 | 730.8446 | 0 | 0.0053 | 17326200 | 133764.4695
March | 336511.0337 | 538.0664 | 842.7778 | 0 | 0.006 | 19985200 | 138952.2674
April | 301832.3002 | 496.5555 | 806.3362 | 0 | 0.0057 | 19123500 | 125980.0934
May | 311493.8075 | 529.4488 | 893.6228 | 0 | 0.0062 | 21196400 | 131655.8231
June | 320152.3207 | 552.8044 | 949.7044 | 0 | 0.0066 | 22528000 | 136150.4715
July | 340055.0911 | 591.1646 | 1023.1895 | 0 | 0.0071 | 24271700 | 145000.5809
August | 340076.1093 | 590.8171 | 1021.8638 | 0 | 0.0071 | 24240200 | 144972.4169
September | 310987.6678 | 534.6996 | 914.2715 | 0 | 0.0064 | 21687100 | 132032.6187
October | 313162.8967 | 521.472 | 859.3033 | 0 | 0.006 | 20380700 | 131315.984
November | 320101.8028 | 507.6636 | 786.6183 | 0 | 0.0056 | 18652700 | 131773.9428
December | 367880.7797 | 554.3788 | 798.9366 | 0 | 0.0058 | 18939600 | 148633.7581
Annual Sum or Average | 3973135.4954 | 6485.5819 | 10430.5071 | 0 | 0.0736 | 247367000 | 1653417.1659
Minimum of Months | 301832.3002 | 496.5555 | 730.8446 | 0 | 0.0053 | 17326200 | 125980.0934
Maximum of Months | 380717.8069 | 591.1646 | 1023.1895 | 0 | 0.0071 | 24271700 | 153184.7395
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1081830000000 | 600681.416 | 05-JAN-11:39 | 228236.782 | 263066.793 | 93291.955 | 0 | 0 | 0 | 7282.464 | 0 | 0 | 0 | 0 | 0 | 8803.422 | 0 | 0
February | 984687000000 | 699179.909 | 02-FEB-14:00 | 228236.782 | 263066.793 | 96948.634 | 0 | 63301.607 | 0 | 26210.137 | 14315.003 | 0 | 0 | 0 | 0 | 7100.954 | 0 | 0
March | 1135800000000 | 717942.895 | 30-MAR-14:00 | 228236.782 | 263066.793 | 100495.345 | 0 | 78463.297 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7164.147 | 0 | 0
April | 1086830000000 | 709974.861 | 06-APR-14:00 | 228236.782 | 263066.793 | 99014.368 | 0 | 72053.966 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7086.422 | 0 | 0
May | 1204640000000 | 737415.219 | 16-MAY-14:00 | 228236.782 | 263066.793 | 101877.725 | 0 | 96326.821 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7390.567 | 0 | 0
June | 1280320000000 | 806931.256 | 30-JUN-14:00 | 228236.782 | 263066.793 | 110834.511 | 0 | 156336.495 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7940.145 | 0 | 0
July | 1379420000000 | 802860.808 | 21-JUL-14:00 | 228236.782 | 263066.793 | 111907.671 | 0 | 151266.33 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7866.702 | 0 | 0
August | 1377630000000 | 784258.12 | 09-AUG-14:00 | 228236.782 | 263066.793 | 107700.198 | 0 | 136946.704 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7791.113 | 0 | 0
September | 1232530000000 | 759094.368 | 01-SEP-14:00 | 228236.782 | 263066.793 | 104638.165 | 0 | 115015.998 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7620.099 | 0 | 0
October | 1158280000000 | 731062.087 | 06-OCT-14:00 | 228236.782 | 263066.793 | 102225.174 | 0 | 89697.478 | 0 | 26201.528 | 14315.003 | 0 | 0 | 0 | 0 | 7319.329 | 0 | 0
November | 1060080000000 | 696012.578 | 21-NOV-11:39 | 228236.782 | 263066.793 | 95613.716 | 0 | 58702.275 | 0 | 26225.043 | 14315.003 | 0 | 0 | 0 | 0 | 9852.967 | 0 | 0
December | 1076380000000 | 599529.952 | 12-DEC-11:09 | 228236.782 | 263066.793 | 92990.928 | 0 | 0 | 0 | 6985.552 | 0 | 0 | 0 | 0 | 0 | 8249.897 | 0 | 0
Annual Sum or Average | 14058400000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 984687000000 | 599529.952 |  | 228236.782 | 263066.793 | 92990.928 | 0 | 0 | 0 | 6985.552 | 0 | 0 | 0 | 0 | 0 | 7086.422 | 0 | 0
Maximum of Months | 1379420000000 | 806931.256 |  | 228236.782 | 263066.793 | 111907.671 | 0 | 156336.495 | 0 | 26225.043 | 14315.003 | 0 | 0 | 0 | 0 | 9852.967 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 270578.8 | 103853.44 | 0 | 374432.24
Cost per Total Building Area ($/m2) | 12.07 | 4.63 | 0 | 16.7
Cost per Net Conditioned Building Area ($/m2) | 12.07 | 4.63 | 0 | 16.7
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 31083.78 | 1386.29 | 1386.29
Net Site Energy | 31083.78 | 1386.29 | 1386.29
Total Source Energy | 66660.43 | 2972.96 | 2972.96
Net Source Energy | 66660.43 | 2972.96 | 2972.96
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 13807.55 | 0 | 0 | 0 | 0
Cooling | 762.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2712.24 | 0 | 0 | 0 | 0 | 0
Pumps | 411.95 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 207.05 | 0 | 0 | 0 | 0 | 3571.91
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 783.43 | 0 | 0 | 0 | 4037.86
Refrigeration | 188.53 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13951.79 | 17131.99 | 0 | 0 | 0 | 7609.78
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 13951.79 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 13951.79 | 100
Total On-Site and Utility Electric Sources | 13951.79 | 100
Total Electricity End Uses | 13951.79 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 3.24 | 0.49 | 0.49 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 3.24 | 0.49 | 0.49 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 3.24 | 0.49 | 0.49 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 3.24 | 0.49 | 0.49 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.49 | 0.49 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.49 | 0.49 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 3.24 | 0.49 | 0.49 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 3.24 | 0.49 | 0.49 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.49 | 0.49 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.49 | 0.49 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.49 | 0.49 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.49 | 0.49 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.49 | 0.49 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.49 | 0.49 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.49 | 0.49 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.49 | 0.49 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.49 | 0.49 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 3.24 | 0.49 | 0.49 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 3.24 | 0.49 | 0.49 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.49 | 0.49 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 3.24 | 0.49 | 0.49 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 3.24 | 0.49 | 0.49 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 3.24 | 0.49 | 0.49 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 3.24 | 0.49 | 0.49 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 3.24 | 0.49 | 0.49 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 3.24 | 0.49 | 0.49 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 3.24 | 0.49 | 0.49 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 3.24 | 0.49 | 0.49 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.49 | 0.49 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 3.24 | 0.49 | 0.49 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 3.24 | 0.49 | 0.49 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 3.24 | 0.49 | 0.49 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 3.24 | 0.49 | 0.49 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1656405.45 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6410966.29 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1542357.86
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 32.41 | 76831.25 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 52.31 | 123981.31 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35622.43 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15178.66 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 21768.23 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 399744.8004 | 577.2178 | 699.8573 | 0 | 0.0054 | 459486.513 | 158843.0112
February | 348373.3266 | 510.0897 | 632.8762 | 0 | 0.0049 | 415554.9275 | 139103.9353
March | 352297.9168 | 537.3648 | 710.1066 | 0 | 0.0054 | 466396.1548 | 142728.859
April | 292486.7595 | 475.1261 | 683.9517 | 0 | 0.0051 | 449376.3481 | 121268.4171
May | 294231.4256 | 505.3243 | 777.1332 | 0 | 0.0057 | 510728.395 | 124607.4145
June | 306173.1897 | 543.1049 | 864.9125 | 0 | 0.0063 | 568488.6645 | 131315.6796
July | 337500.3453 | 601.2342 | 961.7438 | 0 | 0.007 | 632143.8276 | 144996.3661
August | 327644.0757 | 581.9978 | 928.193 | 0 | 0.0068 | 610084.737 | 140601.5227
September | 290132.5227 | 505.9664 | 791.3201 | 0 | 0.0058 | 520083.9987 | 123605.7955
October | 293331.5086 | 488.5834 | 725.278 | 0 | 0.0054 | 476585.9073 | 122773.83
November | 323633.8068 | 502.2709 | 680.4236 | 0 | 0.0052 | 446947.6775 | 131940.6789
December | 385259.0622 | 562.7781 | 695.5873 | 0 | 0.0054 | 456723.8731 | 153706.084
Annual Sum or Average | 3950808.7399 | 6391.0584 | 9151.3834 | 0 | 0.0686 | 6012601.0243 | 1635491.5939
Minimum of Months | 290132.5227 | 475.1261 | 632.8762 | 0 | 0.0049 | 415554.9275 | 121268.4171
Maximum of Months | 399744.8004 | 601.2342 | 961.7438 | 0 | 0.007 | 632143.8276 | 158843.0112
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1066200000000 | 593823.822 | 27-JAN-11:39 | 228236.782 | 263066.793 | 86681.188 | 0 | 0 | 0 | 6997.616 | 0 | 0 | 0 | 0 | 0 | 8841.443 | 0 | 0
February | 964264000000 | 593332.228 | 02-FEB-11:39 | 228236.782 | 263066.793 | 85587.383 | 0 | 0 | 0 | 7670.678 | 0 | 0 | 0 | 0 | 0 | 8770.592 | 0 | 0
March | 1082240000000 | 591550.506 | 07-MAR-11:09 | 228236.782 | 263066.793 | 86798.196 | 0 | 0 | 0 | 5114.139 | 0 | 0 | 0 | 0 | 0 | 8334.596 | 0 | 0
April | 1042740000000 | 733603.155 | 04-APR-14:00 | 228236.782 | 263066.793 | 91903.475 | 0 | 86100.013 | 0 | 37021.701 | 20243.447 | 0 | 0 | 0 | 0 | 7030.944 | 0 | 0
May | 1185110000000 | 750929.026 | 31-MAY-14:00 | 228236.782 | 263066.793 | 95116.008 | 0 | 99955.433 | 0 | 37021.701 | 20243.447 | 0 | 0 | 0 | 0 | 7288.864 | 0 | 0
June | 1319140000000 | 862474.088 | 14-JUN-14:00 | 228236.782 | 263066.793 | 98790.084 | 0 | 207466.269 | 0 | 37021.701 | 20243.447 | 0 | 0 | 0 | 0 | 7649.011 | 0 | 0
July | 1466840000000 | 877515.716 | 07-JUL-14:00 | 228236.782 | 263066.793 | 103530.585 | 0 | 217684.12 | 0 | 37021.701 | 20243.447 | 0 | 0 | 0 | 0 | 7732.288 | 0 | 0
August | 1415660000000 | 862589.661 | 11-AUG-14:00 | 228236.782 | 263066.793 | 98881.725 | 0 | 207409.134 | 0 | 37021.701 | 20243.447 | 0 | 0 | 0 | 0 | 7730.079 | 0 | 0
September | 1206820000000 | 817099.11 | 08-SEP-11:00 | 228236.782 | 263066.793 | 92814.46 | 0 | 168448.41 | 0 | 37021.701 | 20243.447 | 0 | 0 | 0 | 0 | 7267.517 | 0 | 0
October | 1105880000000 | 735122.015 | 06-OCT-14:00 | 228236.782 | 263066.793 | 93365.37 | 0 | 86100.013 | 0 | 37021.701 | 20243.447 | 0 | 0 | 0 | 0 | 7087.909 | 0 | 0
November | 1037110000000 | 686989.791 | 09-NOV-11:39 | 228236.782 | 263066.793 | 88452.693 | 0 | 40236.131 | 0 | 37057.286 | 20243.447 | 0 | 0 | 0 | 0 | 9696.659 | 0 | 0
December | 1059790000000 | 593772.067 | 20-DEC-11:39 | 228236.782 | 263066.793 | 86665.103 | 0 | 0 | 0 | 6964.868 | 0 | 0 | 0 | 0 | 0 | 8838.52 | 0 | 0
Annual Sum or Average | 13951800000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 964264000000 | 591550.506 |  | 228236.782 | 263066.793 | 85587.383 | 0 | 0 | 0 | 5114.139 | 0 | 0 | 0 | 0 | 0 | 7030.944 | 0 | 0
Maximum of Months | 1466840000000 | 877515.716 |  | 228236.782 | 263066.793 | 103530.585 | 0 | 217684.12 | 0 | 37057.286 | 20243.447 | 0 | 0 | 0 | 0 | 9696.659 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 203656.26 | 135084 | 0 | 338740.26
Cost per Total Building Area ($/m2) | 9.08 | 6.02 | 0 | 15.11
Cost per Net Conditioned Building Area ($/m2) | 9.08 | 6.02 | 0 | 15.11
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 38335.46 | 1709.71 | 1709.71
Net Site Energy | 38335.46 | 1709.71 | 1709.71
Total Source Energy | 74597.71 | 3326.95 | 3326.95
Net Source Energy | 74597.71 | 3326.95 | 3326.95
Area (m2)
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 21706.8 | 0 | 0 | 0 | 0
Cooling | 392.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5639.82 | 2541.01 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2597.54 | 0 | 0 | 0 | 0 | 0
Pumps | 247.38 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 107.21 | 0 | 0 | 0 | 0 | 1986.35
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 887.89 | 0 | 0 | 0 | 4037.86
Refrigeration | 185.8 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13199.75 | 25135.7 | 0 | 0 | 0 | 6024.21
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 13199.75 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 13199.75 | 100
Total On-Site and Utility Electric Sources | 13199.75 | 100
Total Electricity End Uses | 13199.75 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 501.68 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 11.86 | 2.62 | 0.49 | 0.49 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 2.62 | 0.49 | 0.49 | No | LOBBY_FLR_1_WALL_1_WEST
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 2.62 | 0.49 | 0.49 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 24.53 | 2.62 | 0.49 | 0.49 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 2.62 | 0.49 | 0.49 | No | IC_PATROOM2_FLR_2_WALL_NORTH
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 2.62 | 0.49 | 0.49 | No | IC_PATROOM2_FLR_2_WALL_WEST
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 29.43 | 2.62 | 0.49 | 0.49 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 2.62 | 0.49 | 0.49 | No | ICU_FLR_2_WALL_WEST
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 2.62 | 0.49 | 0.49 | No | OR_NURSESAT_FLR_2_WALL_SOUTH
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 2.62 | 0.49 | 0.49 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM2_FLR_3_WALL_EAST
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 2.62 | 0.49 | 0.49 | No | PATROOM2_FLR_3_WALL_SOUTH
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 2.62 | 0.49 | 0.49 | No | PATROOM3_MULT10_FLR_3_WALL_EAST
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 2.62 | 0.49 | 0.49 | No | PATROOM4_FLR_3_WALL_NORTH
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM4_FLR_3_WALL_EAST
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 2.62 | 0.49 | 0.49 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 2.62 | 0.49 | 0.49 | No | PATROOM6_FLR_3_WALL_SOUTH
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM6_FLR_3_WALL_WEST
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 2.62 | 0.49 | 0.49 | No | PATROOM7_MULT10_FLR_3_WALL_WEST
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 2.62 | 0.49 | 0.49 | No | PATROOM8_FLR_3_WALL_NORTH
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM8_FLR_3_WALL_WEST
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 49.05 | 2.62 | 0.49 | 0.49 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM2_FLR_4_WALL_EAST
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 2.62 | 0.49 | 0.49 | No | PATROOM2_FLR_4_WALL_SOUTH
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 47.41 | 2.62 | 0.49 | 0.49 | No | PATROOM3_MULT10_FLR_4_WALL_EAST
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 2.62 | 0.49 | 0.49 | No | PATROOM4_FLR_4_WALL_NORTH
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM4_FLR_4_WALL_EAST
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 49.05 | 2.62 | 0.49 | 0.49 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 2.62 | 0.49 | 0.49 | No | PATROOM6_FLR_4_WALL_SOUTH
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM6_FLR_4_WALL_WEST
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 47.41 | 2.62 | 0.49 | 0.49 | No | PATROOM7_MULT10_FLR_4_WALL_WEST
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 2.62 | 0.49 | 0.49 | No | PATROOM8_FLR_4_WALL_NORTH
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 2.62 | 0.49 | 0.49 | No | PATROOM8_FLR_4_WALL_WEST
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 2.62 | 0.49 | 0.49 | No | DINING_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 2.62 | 0.49 | 0.49 | No | OFFICE1_FLR_5_WALL_SOUTH
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 2.62 | 0.49 | 0.49 | No | OFFICE1_FLR_5_WALL_WEST
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 40.87 | 2.62 | 0.49 | 0.49 | No | OFFICE2_MULT5_FLR_5_WALL_WEST
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 2.62 | 0.49 | 0.49 | No | OFFICE3_FLR_5_WALL_NORTH
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 2.62 | 0.49 | 0.49 | No | OFFICE3_FLR_5_WALL_WEST
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 17.77 | 2.62 | 0.49 | 0.49 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1063870.55 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 6796614.73 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 990620.44
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 3.78 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
VAV_1 FAN | Fan:VariableVolume | 0.42 | 1000 | 31.48 | 74622.38 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.42 | 1000 | 49.64 | 117653.72 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37765.28 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9748.9 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 13981.23 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 435339.2654 | 466.9555 | 1502.7884 | 0 | 0.0056 | 301385.6836 | 161715.8671
February | 385305.9796 | 414.6245 | 1358.0236 | 0 | 0.005 | 272361.3276 | 143335.544
March | 371918.7372 | 410.2094 | 1519.8575 | 0 | 0.0055 | 304879.5566 | 139892.8729
April | 292232.9733 | 334.3848 | 1446.6364 | 0 | 0.0051 | 290255.398 | 111776.6774
May | 256399.323 | 309.6766 | 1610.139 | 0 | 0.0055 | 323131.9557 | 100578.0371
June | 258403.512 | 317.2871 | 1731.3032 | 0 | 0.0059 | 347465.7479 | 102162.8766
July | 268610.5933 | 330.7046 | 1818.1946 | 0 | 0.0062 | 364907.3723 | 106334.4739
August | 262848.1754 | 322.0332 | 1746.1988 | 0 | 0.0059 | 350452.9438 | 103810.6493
September | 253363.4923 | 301.8899 | 1504.8804 | 0 | 0.0052 | 301993.8825 | 98753.1624
October | 312439.1306 | 354.9626 | 1493.4609 | 0 | 0.0053 | 299639.2317 | 119114.0354
November | 379420.8416 | 413.6071 | 1448.4875 | 0 | 0.0053 | 290537.1062 | 141964.2308
December | 417800.0599 | 450.4835 | 1491.2192 | 0 | 0.0055 | 299080.1367 | 155560.8092
Annual Sum or Average | 3894082.0835 | 4426.8186 | 18671.1893 | 0 | 0.0659 | 3746090.3426 | 1484999.2362
Minimum of Months | 253363.4923 | 301.8899 | 1358.0236 | 0 | 0.005 | 272361.3276 | 98753.1624
Maximum of Months | 435339.2654 | 466.9555 | 1818.1946 | 0 | 0.0062 | 364907.3723 | 161715.8671
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1061970000000 | 592268.421 | 24-JAN-11:39 | 228236.782 | 263066.793 | 82325.589 | 0 | 0 | 0 | 9834.221 | 0 | 0 | 0 | 0 | 0 | 8805.036 | 0 | 0
February | 959695000000 | 592301.858 | 09-FEB-11:39 | 228236.782 | 263066.793 | 82368.116 | 0 | 0 | 0 | 9833.955 | 0 | 0 | 0 | 0 | 0 | 8796.212 | 0 | 0
March | 1074280000000 | 591908.913 | 24-MAR-10:39 | 228236.782 | 263066.793 | 83485.276 | 0 | 0 | 0 | 8221.657 | 0 | 0 | 0 | 0 | 0 | 8898.405 | 0 | 0
April | 1022750000000 | 623673.483 | 25-APR-14:00 | 228236.782 | 263066.793 | 88995.95 | 0 | 4295.536 | 0 | 23805.215 | 8656.479 | 0 | 0 | 0 | 0 | 6616.729 | 0 | 0
May | 1138590000000 | 701442.239 | 24-MAY-14:00 | 228236.782 | 263066.793 | 93004.947 | 0 | 73246.919 | 0 | 23804.935 | 13001.893 | 0 | 0 | 0 | 0 | 7079.97 | 0 | 0
June | 1224330000000 | 739747.937 | 21-JUN-14:00 | 228236.782 | 263066.793 | 93977.727 | 0 | 110163.724 | 0 | 23804.935 | 13001.893 | 0 | 0 | 0 | 0 | 7496.083 | 0 | 0
July | 1285790000000 | 734047.582 | 21-JUL-14:00 | 228236.782 | 263066.793 | 94093.143 | 0 | 104362.755 | 0 | 23804.935 | 13001.893 | 0 | 0 | 0 | 0 | 7481.281 | 0 | 0
August | 1234860000000 | 732525.866 | 15-AUG-14:50 | 228236.782 | 263066.793 | 92510.044 | 0 | 104364.871 | 0 | 23804.935 | 13001.893 | 0 | 0 | 0 | 0 | 7540.549 | 0 | 0
September | 1064110000000 | 678251.664 | 07-SEP-14:00 | 228236.782 | 263066.793 | 87929.628 | 0 | 55300.028 | 0 | 23806.249 | 13001.893 | 0 | 0 | 0 | 0 | 6910.29 | 0 | 0
October | 1055810000000 | 650670.944 | 03-OCT-14:00 | 228236.782 | 263066.793 | 87363.283 | 0 | 28444.126 | 0 | 23814.601 | 13001.893 | 0 | 0 | 0 | 0 | 6743.467 | 0 | 0
November | 1023740000000 | 591153.765 | 01-NOV-11:39 | 228236.782 | 263066.793 | 83185.405 | 0 | 0 | 0 | 7792.73 | 0 | 0 | 0 | 0 | 0 | 8872.056 | 0 | 0
December | 1053840000000 | 592273.919 | 08-DEC-11:39 | 228236.782 | 263066.793 | 82336.416 | 0 | 0 | 0 | 9837.686 | 0 | 0 | 0 | 0 | 0 | 8796.242 | 0 | 0
Annual Sum or Average | 13199800000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 959695000000 | 591153.765 |  | 228236.782 | 263066.793 | 82325.589 | 0 | 0 | 0 | 7792.73 | 0 | 0 | 0 | 0 | 0 | 6616.729 | 0 | 0
Maximum of Months | 1285790000000 | 739747.937 |  | 228236.782 | 263066.793 | 94093.143 | 0 | 110163.724 | 0 | 23814.601 | 13001.893 | 0 | 0 | 0 | 0 | 8898.405 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 320606.3 | 104003.78 | 0 | 424610.08
Cost per Total Building Area ($/m2) | 14.3 | 4.64 | 0 | 18.94
Cost per Net Conditioned Building Area ($/m2) | 14.3 | 4.64 | 0 | 18.94

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.39 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 2360.3187 | 2277.2321 | 1886.8051 | 2053.8964 | 1235.9394 | 1551.8598 | 1156.4875 | 2093.1672 | 1228.0369 | 1326.3631 | 2081.4911 | 1220.8128 | 1949.3216 | 1171.3148 | 1656.4054 | 1063.8706
| TOWERWATERSYS COOLTOWER | 2197.8049 | 2120.439 | 1756.8939 | 1912.4806 | 1150.842 | 1445.0104 | 1076.8605 | 1949.0475 | 1143.4835 | 1235.0397 | 1938.1753 | 1136.7568 | 1815.106 | 1090.6669 | 1542.3579 | 990.6204
Heating (kW)
| HEATSYS1 BOILER | 5694.9688 | 6154.5571 | 6691.6908 | 5665.802 | 5011.8231 | 5901.7454 | 5217.1264 | 6063.4868 | 5880.1801 | 5565.7791 | 6249.4855 | 6111.5211 | 6362.682 | 6267.139 | 6410.9663 | 6796.6147
HVAC Efficiency
| Air Conditioning (COP) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb
Fan Max Flow Rate (m3/s )
| DINING_FLR_5 EXHAUST FAN | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78
| KITCHEN_FLR_5 EXHAUST FAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VAV_1 FAN | 34.35 | 34.25 | 38.69 | 31.45 | 29.53 | 34.35 | 30.17 | 31.76 | 37.65 | 31 | 31.85 | 37.23 | 31.8 | 35 | 32.41 | 31.48
| VAV_2 FAN | 51.82 | 54.17 | 64.22 | 50.63 | 45.99 | 57.41 | 46.76 | 51.76 | 61.4 | 48.94 | 51.72 | 60.4 | 51.8 | 56.57 | 52.31 | 49.64
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.074377 | 0.098457 | 0.067786 | 0.1005 | 0.043402 | 0.087844 | 0.12939 | 0.056889 | 0.036973 | 0.065633 | 0.097318 | 0.036975 | 0.052349 | 0.069288 | 0.05255 | 0.08744
| Total Cost ($/m2) | 19.25 | 23.42 | 15.36 | 20.93 | 8.37 | 17.82 | 22.89 | 11.29 | 7 | 11.39 | 18.43 | 6.74 | 9.75 | 12.07 | 9.08 | 14.3
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011459 | 0.0081432 | 0.0084511 | 0.010218 | 0.0084326 | 0.0079794 | 0.0084914 | 0.009838 | 0.007028 | 0.0083731 | 0.0085107 | 0.0070149 | 0.0079011 | 0.0082741 | 0.0078849 | 0.0041377
| Total Cost ($/m2) | 1.58 | 1.94 | 1.76 | 2.82 | 1.32 | 1.78 | 1.89 | 3.99 | 2.25 | 2.84 | 4.39 | 2.99 | 5.04 | 4.63 | 6.02 | 4.64
Total Utility Costs
| Cost Intensity ($/m2) | 20.83 | 25.36 | 17.12 | 23.75 | 9.69 | 19.6 | 24.78 | 15.28 | 9.25 | 14.23 | 22.82 | 9.73 | 14.79 | 16.7 | 15.11 | 18.94
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1562888.8889 | 1209422.2222 | 901194.4445 | 739627.7778 | 543422.2222 | 613955.5556 | 274955.5556 | 595350 | 384933.3333 | 234738.8889 | 451230.5556 | 287613.8889 | 410780.5556 | 202922.2222 | 211730.5556 | 108897.2222
| Interior Lighting | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667 | 1566616.6667
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 783938.8889 | 792325 | 927336.1111 | 735947.2222 | 680033.3333 | 827597.2222 | 687111.1111 | 744663.8889 | 890133.3333 | 711169.4445 | 744297.2222 | 872619.4445 | 744619.4445 | 816497.2222 | 753400 | 721538.8889
| Pumps | 459072.2222 | 380627.7778 | 329333.3333 | 293061.1111 | 230980.5556 | 237072.2222 | 171263.8889 | 239344.4444 | 148697.2222 | 133375 | 202530.5556 | 122627.7778 | 183150 | 96622.2222 | 114430.5556 | 68716.6667
| Heat Rejection | 251013.8889 | 206480.5556 | 179205.5556 | 157836.1111 | 125925 | 127611.1111 | 92488.8889 | 127513.8889 | 78997.2222 | 71330.5556 | 107105.5556 | 64652.7778 | 95938.8889 | 50061.1111 | 57513.8889 | 29780.5556
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 60305.5556 | 58161.1111 | 58469.4444 | 56338.8889 | 56552.7778 | 56988.8889 | 54880.5556 | 54988.8889 | 54916.6667 | 53944.4444 | 54108.3333 | 53822.2222 | 53702.7778 | 52963.8889 | 52369.4444 | 51611.1111
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5803275 | 5333075 | 5081591.6667 | 4668861.1111 | 4322969.4445 | 4549280.5556 | 3966755.5556 | 4447913.8889 | 4243730.5556 | 3890611.1111 | 4245325 | 4087388.8889 | 4174244.4445 | 3905122.2223 | 3875497.2223 | 3666597.2223
Gas (MJ)
| Heating | 204860 | 2383740 | 1741720 | 3132780 | 468900 | 2012850 | 1882850 | 5979230 | 4072910 | 4453710 | 8385820 | 6365480 | 11076300 | 9304000 | 13807550 | 21706800
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010 | 2541010
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 336300 | 427390 | 375020 | 515200 | 498170 | 438120 | 573280 | 584180 | 571110 | 620120 | 644770 | 641610 | 697090 | 706590 | 783430 | 887890
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3082170 | 5352140 | 4657750 | 6188980 | 3508080 | 4991980 | 4997140 | 9104410 | 7185030 | 7614840 | 11571610 | 9548100 | 14314400 | 12551600 | 17131990 | 25135700
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 23973960 | 24551210 | 22951480 | 22996880 | 19070770 | 21369390 | 19277460 | 25116900 | 22462460 | 21621040 | 26854780 | 24262700 | 29341680 | 26610040 | 31083780 | 38335460
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 250.9294 | 194.1786 | 144.6912 | 118.7508 | 87.2491 | 98.5736 | 44.1455 | 95.5863 | 61.8029 | 37.6885 | 72.4473 | 46.1778 | 65.9528 | 32.5802 | 33.9944 | 17.484
| Interior Lighting (elec) | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309
| Exterior Lighting (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (elec) | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279 | 251.5279
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 125.8652 | 127.2116 | 148.8883 | 118.1599 | 109.1827 | 132.8748 | 110.319 | 119.5594 | 142.9152 | 114.1817 | 119.5005 | 140.1033 | 119.5523 | 131.0926 | 120.962 | 115.8466
| Pumps (elec) | 73.7063 | 61.1116 | 52.8761 | 47.0524 | 37.0851 | 38.0631 | 27.4973 | 38.4279 | 23.8741 | 21.414 | 32.5173 | 19.6885 | 29.4056 | 15.5132 | 18.3724 | 11.0328
| Heat Rejection (elec) | 40.3015 | 33.1515 | 28.7723 | 25.3414 | 20.2179 | 20.4886 | 14.8495 | 20.473 | 12.6834 | 11.4525 | 17.1963 | 10.3803 | 15.4035 | 8.0376 | 9.2341 | 4.7814
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 9.6824 | 9.3381 | 9.3876 | 9.0455 | 9.0798 | 9.1498 | 8.8113 | 8.8287 | 8.8171 | 8.661 | 8.6874 | 8.6414 | 8.6222 | 8.5036 | 8.4082 | 8.2864
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 931.7441 | 856.2512 | 815.8743 | 749.6084 | 694.0738 | 730.4092 | 636.882 | 714.1343 | 681.3516 | 624.6566 | 681.6076 | 656.2502 | 670.1953 | 626.9864 | 622.23 | 588.6901
Gas (MJ/m2)
| Heating (gas) | 9.1365 | 106.3114 | 77.6782 | 139.7175 | 20.9123 | 89.7702 | 83.9724 | 266.6652 | 181.646 | 198.6291 | 373.9956 | 283.8914 | 493.9872 | 414.9452 | 615.7971 | 968.0924
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254 | 113.3254
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 14.9985 | 19.061 | 16.7254 | 22.9772 | 22.2177 | 19.5395 | 25.5675 | 26.0536 | 25.4707 | 27.6565 | 28.7558 | 28.6149 | 31.0892 | 31.5129 | 34.9399 | 39.5986
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 137.4604 | 238.6978 | 207.729 | 276.0197 | 156.4554 | 222.6352 | 222.8653 | 406.0437 | 320.4421 | 339.611 | 516.0773 | 425.8317 | 638.4019 | 559.7835 | 764.0624 | 1121.0165
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1069.2045 | 1094.949 | 1023.6034 | 1025.6281 | 850.5292 | 953.0444 | 859.7473 | 1120.178 | 1001.7938 | 964.2676 | 1197.685 | 1082.0819 | 1308.5972 | 1186.7699 | 1386.2924 | 1709.707
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 890.2064 | 863.9116 | 786.1631 | 764.3869 | 726.4479 | 733.1122 | 681.4811 | 743.3014 | 712.8988 | 642.331 | 661.3795 | 711.9375 | 592.4177 | 600.6814 | 593.8238 | 592.2684
| Feb | 899.7903 | 831.1155 | 796.9205 | 765.47 | 714.908 | 743.4826 | 705.5081 | 753.2161 | 734.4185 | 698.156 | 674.8417 | 709.0581 | 592.1318 | 699.1799 | 593.3322 | 592.3019
| Mar | 911.1842 | 854.6909 | 824.2802 | 784.1131 | 719.9626 | 758.9983 | 685.4663 | 797.4718 | 736.6012 | 708.0492 | 768.4422 | 738.0685 | 757.1688 | 717.9429 | 591.5505 | 591.9089
| Apr | 926.858 | 881.1764 | 829.144 | 811.5209 | 738.493 | 799.6718 | 708.19 | 789.4078 | 769.3851 | 701.0294 | 770.7432 | 751.6889 | 758.552 | 709.9749 | 733.6032 | 623.6735
| May | 1001.2164 | 989.8492 | 872.8928 | 860.2447 | 766.4023 | 820.6218 | 721.8879 | 875.4412 | 789.0699 | 738.5581 | 834.3615 | 770.7218 | 826.5319 | 737.4152 | 750.929 | 701.4422
| Jun | 1060.0414 | 981.9265 | 953.8641 | 919.5153 | 759.5681 | 882.0182 | 728.7155 | 978.3567 | 825.8242 | 752.7055 | 975.4735 | 800.7609 | 933.0994 | 806.9313 | 862.4741 | 739.7479
| Jul | 1037.4184 | 1068.2661 | 988.4102 | 959.6555 | 787.463 | 876.2821 | 756.4261 | 1016.5659 | 829.1903 | 780.0004 | 962.9171 | 814.3162 | 957.5535 | 802.8608 | 877.5157 | 734.0476
| Aug | 1031.3921 | 1035.1428 | 974.9522 | 945.1703 | 820.6817 | 904.1649 | 746.6847 | 1018.9154 | 843.4101 | 767.5259 | 1013.9047 | 815.1547 | 936.5981 | 784.2581 | 862.5897 | 732.5259
| Sep | 996.1915 | 1032.7429 | 933.9949 | 896.8046 | 783.9979 | 858.1212 | 781.9009 | 867.4567 | 787.809 | 773.4953 | 852.2142 | 781.1442 | 829.8866 | 759.0944 | 817.0991 | 678.2517
| Oct | 984.2365 | 937.7079 | 847.5243 | 823.2078 | 746.5646 | 797.6504 | 720.6288 | 837.7851 | 763.3543 | 713.2002 | 811.8183 | 768.3123 | 765.5966 | 731.0621 | 735.122 | 650.6709
| Nov | 927.1864 | 890.7511 | 810.9277 | 773.4086 | 725.3795 | 745.8916 | 698.5837 | 807.065 | 726.5727 | 699.4479 | 809.381 | 727.5757 | 757.3578 | 696.0126 | 686.9898 | 591.1538
| Dec | 894.3419 | 857.243 | 781.204 | 769.443 | 728.2584 | 742.5172 | 681.1466 | 665.2356 | 711.363 | 583.7568 | 674.2825 | 708.0915 | 591.0997 | 599.53 | 593.7721 | 592.2739
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-11:39 | 26-JAN-15:00 | 23-JAN-15:00 | 26-JAN-13:00 | 18-JAN-14:00 | 27-JAN-15:00 | 09-JAN-12:00 | 27-JAN-15:39 | 27-JAN-15:00 | 17-JAN-15:09 | 24-JAN-13:00 | 13-JAN-11:39 | 05-JAN-11:39 | 27-JAN-11:39 | 24-JAN-11:39
| Feb | 23-FEB-12:00 | 15-FEB-14:00 | 28-FEB-15:00 | 17-FEB-11:39 | 13-FEB-11:50 | 08-FEB-15:00 | 15-FEB-15:00 | 15-FEB-15:00 | 14-FEB-15:00 | 22-FEB-15:00 | 28-FEB-11:09 | 07-FEB-15:20 | 03-FEB-11:39 | 02-FEB-14:00 | 02-FEB-11:39 | 09-FEB-11:39
| Mar | 14-MAR-10:39 | 24-MAR-11:00 | 17-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:50 | 31-MAR-14:00 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-15:09 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 07-MAR-11:09 | 24-MAR-10:39
| Apr | 03-APR-13:00 | 20-APR-14:00 | 26-APR-14:00 | 21-APR-13:00 | 11-APR-13:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-14:00 | 21-APR-14:00 | 19-APR-14:00 | 28-APR-10:39 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 25-APR-14:00
| May | 19-MAY-14:00 | 18-MAY-14:20 | 30-MAY-14:00 | 31-MAY-14:00 | 30-MAY-14:39 | 31-MAY-14:00 | 26-MAY-13:00 | 31-MAY-14:00 | 31-MAY-14:00 | 05-MAY-14:00 | 30-MAY-14:00 | 23-MAY-14:00 | 31-MAY-11:00 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 29-JUN-14:00 | 28-JUN-14:00 | 08-JUN-14:00 | 28-JUN-12:00 | 27-JUN-14:00 | 16-JUN-14:00 | 30-JUN-14:00 | 29-JUN-14:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 21-JUN-14:00
| Jul | 13-JUL-14:00 | 18-JUL-13:30 | 18-JUL-14:00 | 03-JUL-11:00 | 20-JUL-14:00 | 25-JUL-14:00 | 03-JUL-12:00 | 25-JUL-11:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-12:00 | 25-JUL-12:00 | 13-JUL-14:00 | 21-JUL-14:00 | 07-JUL-14:00 | 21-JUL-14:00
| Aug | 21-AUG-14:30 | 03-AUG-14:00 | 02-AUG-14:00 | 17-AUG-14:00 | 09-AUG-14:00 | 02-AUG-13:30 | 15-AUG-11:00 | 17-AUG-14:20 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-14:00 | 09-AUG-14:00 | 11-AUG-14:00 | 15-AUG-14:50
| Sep | 12-SEP-13:00 | 15-SEP-14:00 | 12-SEP-14:00 | 01-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 27-SEP-14:00 | 05-SEP-12:39 | 01-SEP-14:00 | 07-SEP-12:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-14:00 | 08-SEP-11:00 | 07-SEP-14:00
| Oct | 06-OCT-14:00 | 30-OCT-13:00 | 03-OCT-11:00 | 20-OCT-14:00 | 05-OCT-10:39 | 03-OCT-14:00 | 31-OCT-12:00 | 03-OCT-10:39 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-11:20 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 03-OCT-14:00
| Nov | 01-NOV-15:00 | 27-NOV-14:00 | 13-NOV-15:00 | 22-NOV-11:39 | 09-NOV-15:00 | 10-NOV-15:39 | 16-NOV-15:00 | 03-NOV-13:00 | 08-NOV-15:39 | 03-NOV-11:39 | 02-NOV-11:09 | 10-NOV-13:00 | 02-NOV-15:30 | 21-NOV-11:39 | 09-NOV-11:39 | 01-NOV-11:39
| Dec | 15-DEC-15:00 | 06-DEC-14:00 | 11-DEC-15:00 | 26-DEC-13:00 | 19-DEC-12:00 | 05-DEC-14:00 | 07-DEC-15:39 | 08-DEC-11:09 | 08-DEC-15:30 | 01-DEC-11:09 | 12-DEC-12:00 | 21-DEC-15:00 | 20-DEC-11:09 | 12-DEC-11:09 | 20-DEC-11:39 | 08-DEC-11:39
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 24095.47 | 18260.93 | 22282.78 | 12220.06 | 8281.66 | 16648.77 | 4390.28 | 9734.13 | 8993.34 | 3898.56 | 7737.58 | 6637 | 6970.85 | 4537.54 | 3571.91 | 1986.35
| Water Systems | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86
| Total Building | 28133.33 | 22298.79 | 26320.65 | 16257.92 | 12319.52 | 20686.64 | 8428.14 | 13771.99 | 13031.2 | 7936.42 | 11775.44 | 10674.86 | 11008.72 | 8575.4 | 7609.78 | 6024.21
Emissions
| Carbon Equivalent (kg) | 1647126.3455 | 1875418.8702 | 1617999.7354 | 1549784.7581 | 568467.6324 | 1624377.7033 | 553690.111 | 1364470.8331 | 1863121.3183 | 420685.3251 | 2472060.0331 | 1841868.7853 | 1686942.3919 | 1653417.1659 | 1635491.5939 | 1484999.2362
| CO2 (kg) | 3845892.4387 | 4742629.611 | 3850192.486 | 3586540.6341 | 1531589.6142 | 3894229.6277 | 1498026.3738 | 3166038.9451 | 4413693.2142 | 1069870.9345 | 5825141.4558 | 4387997.2324 | 4039760.8729 | 3973135.4954 | 3950808.7399 | 3894082.0835
| NOX (kg) | 6645.2219 | 6120.3911 | 6317.612 | 6595.7024 | 1320.2172 | 6195.8603 | 1295.5361 | 5812.4355 | 7427.0529 | 1441.7405 | 10056.5282 | 7277.73 | 6687.9847 | 6485.5819 | 6391.0584 | 4426.8186
| SO2 (kg) | 24841.1621 | 25440.1982 | 20435.3452 | 16389.3639 | 12580.2652 | 25026.0201 | 11544.1233 | 16239.1015 | 18533.4515 | 3009.1715 | 28613.2042 | 17851.3744 | 9855.7236 | 10430.5071 | 9151.3834 | 18671.1893
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1135 | 0.0721 | 0.0559 | 0.0605 | 0.006 | 0.0474 | 0.0057 | 0.0664 | 0.0729 | 0.0125 | 0.0875 | 0.0705 | 0.0734 | 0.0736 | 0.0686 | 0.0659
| Water Environmental Factors (m3) | 3074.3311 | 8677.5367 | 150946 | 29150.5 | 75901.7 | 124805 | 69647.3 | 1009.8435 | 19269.9 | 39749.6 | 6586.3697 | 18560 | 6476.0922 | 247367 | 6012.601 | 3746.0903

## Picture
DOE Commercial Building Benchmark - Hospital

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 60.1 | 3133.79
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
BLDG_LIGHT_EXTD_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.2 | 104.6 | 5454.14
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 13.6
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 | 8.5 | 46.7 | 2435.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 3.8
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4
BLDG_OCC_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 13.5 | 90.4 | 4713.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.7
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 96.7 | 5042.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8
BLDG_EQUIP_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 99.9 | 5209.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
INFIL_SCH | fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 77 | 4015
|  |  | Sat, WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ER_Exam1_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam1_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam1_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam1_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam2_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam2_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam2_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam2_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam3_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam3_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam3_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam3_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam5_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam5_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam5_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
ER_Exam5_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR1_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR1_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR1_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR1_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR2_Mult5_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR2_Mult5_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR2_Mult5_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR2_Mult5_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR3_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR3_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR3_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR3_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR4_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR4_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR4_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
OR4_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom1_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom3_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom4_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom5_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PhysTherapy_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PhysTherapy_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PhysTherapy_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PhysTherapy_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom7_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom8_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Lab_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom1_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom2_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom3_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom4_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom5_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Radiology_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Radiology_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Radiology_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Radiology_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom6_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom7_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
PatRoom8_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Lab_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_5 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_5 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen_Flr_5 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720