## BuildingSummary
Building Summary Large Hotel new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Large Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 8 in slab
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.31 | See Benchmark Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZVAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Air cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 7180

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 10.76 | 5.38 | 0 | 0 | 0 | 0.6 | 1187.298 | 0 | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.84 | 23.3 | 11.6129 | 5.7755 | 16.14 | 10.76 | 0 | 0 | 3.8 | 0.6 | 62.1888 | 0 | 0.55659
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 11.6129 | 6.6883 | 16.14 | 10.76 | 0 | 0 | 3.8 | 0.6 | 72.0174 | 0 | 0.093963
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8 | 0 | 0 | 0 | 16.14 | 5.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10502
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 9.684 | 2.69 | 0 | 0 | 0 | 0.3 | 28.428 | 0 | 0.10502
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.75 | 0 | 23.2258 | 3.3601 | 6.456 | 32.28 | 0 | 378.54 | 2.5 | 0.3 | 31.8121 | 235.9735 | 0.30182
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.17 | 65.62 | 1.3935 | 135.5247 | 13.988 | 5.38 | 0 | 0 | 3.8 | 0.9 | 684.9678 | 0 | 0.49598
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.79 | 85.24 | 3.0965 | 422.479 | 11.836 | 8.07 | 0 | 0 | 2.5 | 0.3 | 1448.6546 | 0 | 0.096077
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 37.8547 | 2.5 | 0.3 | 15.456 | 0 | 0.36556
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 37.854 | 2.5 | 0.3 | 15.456 | 0 | 0.3656
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 11.836 | 10.52 | 0 | 18.927 | 2.5 | 0.3 | 11.106 | 0 | 0.16235
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 11.836 | 10.52 | 0 | 18.927 | 2.5 | 0.3 | 11.109 | 0 | 0.1623
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 37.854 | 2.5 | 0.3 | 15.456 | 0 | 0.36556
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 37.854 | 2.5 | 0.3 | 15.456 | 0 | 0.3656
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 5.38 | 0 | 0 | 0 | 0 | 0.3 | 116.82 | 0 | 0.044299
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 37.854 | 2.5 | 0.3 | 15.456 | 0 | 0.72262
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 37.854 | 2.5 | 0.3 | 15.456 | 0 | 0.72268
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.18 | 6.75 | 16.3533 | 1.5 | 11.836 | 10.52 | 0 | 18.927 | 2.5 | 0.3 | 11.109 | 0 | 1.2767
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.55 | 32.21 | 1.3935 | 237.997 | 13.988 | 107.6 | 0 | 0 | 3.8 | 0.9 | 1202.8826 | 0 | 0.46211
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.55 | 32.21 | 1.3935 | 237.997 | 13.988 | 107.6 | 0 | 0 | 3.8 | 0.9 | 1202.8826 | 0 | 0.46211
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.33 | 26.38 | 18.5806 | 5.5596 | 12.912 | 376.6 | 1796.92 | 503.4582 | 0 | 0 | 0 | 2831.682 | 0.65892
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5 | 28.22 | 92.9031 | 4.436 | 5.38 | 0 | 0 | 0 | 0 | 0.3 | 123.636 | 0 | 0.4762
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.84 | 1214.31 |  | 1400.3727 |  |  |  | 4610.6199
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16298.65 | 1436.6 | 1436.6
Net Site Energy | 16298.65 | 1436.6 | 1436.6
Total Source Energy | 50232.94 | 4427.65 | 4427.65
Net Source Energy | 50232.94 | 4427.65 | 4427.65
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 95.34 | 0 | 0 | 0 | 0
Cooling | 6056.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2232.32 | 0 | 0 | 0 | 0 | 0
Pumps | 505.53 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 735.53 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14577.45 | 1721.2 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 14577.45 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 14577.45 | 100
Total On-Site and Utility Electric Sources | 14577.45 | 100
Total Electricity End Uses | 14577.45 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 6.88 | 0.25 | 0.25 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 6.88 | 0.25 | 0.25 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 6.88 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 6.88 | 0.25 | 0.25 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 6.88 | 0.25 | 0.25 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 6.88 | 0.25 | 0.25 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.25 | 0.25 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.25 | 0.25 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1738481.16 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2752539.65 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.19 | 2247.31 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.24 | 2355.95 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 7.29 | 13822.18 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.04 | 15245.15 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.92 | 1743.07 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.92 | 1750.32 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.4 | 760.66 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.42 | 793.25 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.54 | 2917.67 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 61.69 | 116970.51 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.4 | 760.66 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15294.44 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15930.77 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.19 | 0.06684 | 0.000324 | 0.000646
ROOM_2_FLR_3 FAN COIL | 1.24 | 0.06684 | 0.000326 | 0.000671
ROOM_3_MULT19_FLR_3 FAN COIL | 7.29 | 0.74936 | 0.002156 | 0.004509
ROOM_4_MULT19_FLR_3 FAN COIL | 8.04 | 0.74936 | 0.002207 | 0.004787
ROOM_5_FLR_3 FAN COIL | 0.91922 | 0.06684 | 0.00032 | 0.000525
ROOM_6_FLR_3 FAN COIL | 0.92305 | 0.06684 | 0.000322 | 0.000524
ROOM_1_FLR_6 FAN COIL | 0.40114 | 0.01671 | 0.000107 | 0.000211
ROOM_2_FLR_6 FAN COIL | 0.41833 | 0.01671 | 0.000108 | 0.000219
ROOM_3_MULT9_FLR_6 FAN COIL | 1.54 | 0.08874 | 0.000557 | 0.000889
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 197863.2011 | 341.4767 | 1274.829 | 0 | 0.0058 | 157771.9531 | 84700.5348
February | 180883.8832 | 312.7317 | 1169.826 | 0 | 0.0053 | 144777.2924 | 77488.0373
March | 203596.2602 | 352.2765 | 1318.8946 | 0 | 0.006 | 163226.1844 | 87245.4612
April | 209366.6561 | 362.9722 | 1361.8738 | 0 | 0.0062 | 168545.8294 | 89789.4769
May | 236722.916 | 411.2062 | 1546.1737 | 0 | 0.0071 | 191355.4528 | 101602.4486
June | 238496.0571 | 414.7124 | 1561.1085 | 0 | 0.0071 | 193204.1197 | 102406.1794
July | 260313.3003 | 453.0681 | 1707.21 | 0 | 0.0078 | 211286.0883 | 111816.0675
August | 256877.8598 | 446.9678 | 1683.727 | 0 | 0.0077 | 208379.7214 | 110328.27
September | 242233.4374 | 421.18 | 1585.3263 | 0 | 0.0072 | 196201.316 | 104007.8195
October | 232335.2868 | 403.3154 | 1515.3967 | 0 | 0.0069 | 187546.2641 | 99692.2851
November | 203882.0317 | 353.1733 | 1323.9122 | 0 | 0.006 | 163847.4756 | 87408.2313
December | 198565.1356 | 343.376 | 1284.7662 | 0 | 0.0059 | 159002.3087 | 85069.9491
Annual Sum or Average | 2661136.0252 | 4616.4562 | 17333.0441 | 0 | 0.0792 | 2145144.0057 | 1141554.7606
Minimum of Months | 180883.8832 | 312.7317 | 1169.826 | 0 | 0.0053 | 144777.2924 | 77488.0373
Maximum of Months | 260313.3003 | 453.0681 | 1707.21 | 0 | 0.0078 | 211286.0883 | 111816.0675
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1072150000000 | 650861.169 | 06-JAN-20:00 | 115409.096 | 215842.575 | 76865.296 | 0 | 220623.396 | 3589.95 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2429.206 | 0 | 0
February | 983842000000 | 647857.515 | 23-FEB-20:10 | 115409.096 | 215842.575 | 77989.998 | 0 | 215968.04 | 3589.95 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2956.207 | 0 | 0
March | 1109210000000 | 678331.203 | 13-MAR-19:10 | 115409.096 | 215842.575 | 79016.204 | 0 | 245412.141 | 3589.95 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2959.587 | 0 | 0
April | 1145360000000 | 719638.203 | 01-APR-17:10 | 87035.741 | 233515.839 | 82679.856 | 0 | 297978.463 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2326.653 | 0 | 0
May | 1300370000000 | 749856.717 | 15-MAY-17:19 | 77122.967 | 233515.839 | 82929.595 | 0 | 337858.061 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2328.604 | 0 | 0
June | 1312930000000 | 832414.02 | 27-JUN-17:19 | 77122.967 | 233515.839 | 84613.397 | 0 | 418729.25 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2330.916 | 0 | 0
July | 1435810000000 | 787671.119 | 12-JUL-17:19 | 77122.967 | 233515.839 | 84492.853 | 0 | 374107.535 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2330.273 | 0 | 0
August | 1416060000000 | 799686.248 | 21-AUG-17:30 | 77122.967 | 233515.839 | 84249.323 | 0 | 386367.895 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2328.573 | 0 | 0
September | 1333300000000 | 769286.359 | 09-SEP-17:10 | 87035.741 | 233515.839 | 84170.565 | 0 | 346135.399 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2327.164 | 0 | 0
October | 1274480000000 | 755604.399 | 07-OCT-17:10 | 87035.741 | 233515.839 | 82869.318 | 0 | 333758.825 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2323.026 | 0 | 0
November | 1113430000000 | 687124.456 | 01-NOV-20:00 | 115409.096 | 215842.575 | 78450.786 | 0 | 254773.356 | 3589.95 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2957.044 | 0 | 0
December | 1080510000000 | 646857.916 | 15-DEC-20:10 | 115409.096 | 215842.575 | 76832.354 | 0 | 216653.98 | 3589.95 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2428.311 | 0 | 0
Annual Sum or Average | 14577400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 983842000000 | 646857.916 |  | 77122.967 | 215842.575 | 76832.354 | 0 | 215968.04 | 0 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2323.026 | 0 | 0
Maximum of Months | 1435810000000 | 832414.02 |  | 115409.096 | 233515.839 | 84613.397 | 0 | 418729.25 | 3589.95 | 16101.65 | 0 | 0 | 0 | 0 | 0 | 2959.587 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 307203.72 | 19727.8 | 0 | 326931.52
Cost per Total Building Area ($/m2) | 27.08 | 1.74 | 0 | 28.82
Cost per Net Conditioned Building Area ($/m2) | 27.08 | 1.74 | 0 | 28.82
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 15919.09 | 1403.15 | 1403.15
Net Site Energy | 15919.09 | 1403.15 | 1403.15
Total Source Energy | 2882.84 | 254.1 | 254.1
Net Source Energy | 2882.84 | 254.1 | 254.1
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 852.01 | 0 | 0 | 0 | 0
Cooling | 4677.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2364.39 | 0 | 0 | 0 | 0 | 0
Pumps | 453.77 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 897.61 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.64 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13279.12 | 2639.97 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 13279.12 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 13279.12 | 100
Total On-Site and Utility Electric Sources | 13279.12 | 100
Total Electricity End Uses | 13279.12 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 6.88 | 0.25 | 0.25 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 6.88 | 0.25 | 0.25 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 6.88 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 6.88 | 0.25 | 0.25 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 6.88 | 0.25 | 0.25 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 6.88 | 0.25 | 0.25 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.25 | 0.25 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.25 | 0.25 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1754049.95 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3023844.75 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.27 | 2402.36 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.29 | 2449.78 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.54 | 16189.92 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.29 | 15729.02 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1 | 1899.43 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.96 | 1811.38 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.43 | 814.46 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.44 | 828.62 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.88 | 3567.42 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 64.33 | 121989.26 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.43 | 814.47 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16801.94 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16073.44 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.27 | 0.06684 | 0.000569 | 0.000671
ROOM_2_FLR_3 FAN COIL | 1.29 | 0.06684 | 0.000574 | 0.000681
ROOM_3_MULT19_FLR_3 FAN COIL | 8.54 | 0.74936 | 0.003751 | 0.004979
ROOM_4_MULT19_FLR_3 FAN COIL | 8.29 | 0.74936 | 0.003857 | 0.004775
ROOM_5_FLR_3 FAN COIL | 1 | 0.06684 | 0.000569 | 0.00055
ROOM_6_FLR_3 FAN COIL | 0.95525 | 0.06684 | 0.000574 | 0.000527
ROOM_1_FLR_6 FAN COIL | 0.42951 | 0.01671 | 0.000185 | 0.00022
ROOM_2_FLR_6 FAN COIL | 0.43698 | 0.01671 | 0.000186 | 0.000223
ROOM_3_MULT9_FLR_6 FAN COIL | 1.88 | 0.08874 | 0.000961 | 0.001019
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 229622.9795 | 292.9037 | 1183.7487 | 0 | 0.0034 | 403755.6299 | 90360.1713
February | 195075.6269 | 248.7211 | 1004.0475 | 0 | 0.0029 | 342462.2001 | 76750.5018
March | 237288.9898 | 307.0655 | 1284.6563 | 0 | 0.0036 | 438194.3221 | 93941.8427
April | 255866.7049 | 332.8543 | 1409.719 | 0 | 0.004 | 480860.9583 | 101522.0378
May | 292933.7652 | 381.7715 | 1623.706 | 0 | 0.0046 | 553855.9266 | 116319.2495
June | 309957.4388 | 404.4143 | 1724.4579 | 0 | 0.0049 | 588225.0263 | 123137.8948
July | 344711.6253 | 450.0922 | 1922.4724 | 0 | 0.0054 | 655770.6821 | 136987.6886
August | 335466.0693 | 437.9268 | 1869.6018 | 0 | 0.0053 | 637735.6896 | 133301.4883
September | 296530.7116 | 386.7387 | 1647.556 | 0 | 0.0046 | 561992.5605 | 117783.5468
October | 270705.4489 | 352.439 | 1495.4116 | 0 | 0.0042 | 510092.3314 | 107445.9481
November | 237051.7397 | 307.2498 | 1290.2529 | 0 | 0.0036 | 440105.5561 | 93911.2456
December | 219726.776 | 280.7929 | 1139.9128 | 0 | 0.0032 | 388806.432 | 86531.9516
Annual Sum or Average | 3224937.8758 | 4182.9698 | 17595.543 | 0 | 0.0497 | 6001857.3151 | 1277993.5669
Minimum of Months | 195075.6269 | 248.7211 | 1004.0475 | 0 | 0.0029 | 342462.2001 | 76750.5018
Maximum of Months | 344711.6253 | 450.0922 | 1922.4724 | 0 | 0.0054 | 655770.6821 | 136987.6886
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 893310000000 | 628692.555 | 02-JAN-20:10 | 115409.096 | 215842.575 | 79752.873 | 0 | 194902.56 | 3589.95 | 16244.609 | 0 | 0 | 0 | 0 | 0 | 2950.892 | 0 | 0
February | 757698000000 | 585974.337 | 20-FEB-20:10 | 108704.859 | 214470.86 | 79470.862 | 0 | 160581.621 | 3589.95 | 16244.343 | 0 | 0 | 0 | 0 | 0 | 2911.842 | 0 | 0
March | 969506000000 | 674229.982 | 25-MAR-17:19 | 87035.741 | 233515.839 | 84660.427 | 0 | 250453.168 | 0 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2320.491 | 0 | 0
April | 1063910000000 | 714952.785 | 29-APR-17:10 | 87035.741 | 233515.839 | 86428.329 | 0 | 289401.991 | 0 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2326.568 | 0 | 0
May | 1225410000000 | 782236.744 | 26-MAY-19:10 | 115409.096 | 215842.575 | 85193.685 | 0 | 343517.039 | 3589.95 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2440.082 | 0 | 0
June | 1301450000000 | 784811.552 | 13-JUN-17:19 | 77122.967 | 233515.839 | 88546.313 | 0 | 367052.01 | 0 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2330.106 | 0 | 0
July | 1450890000000 | 836272.995 | 05-JUL-17:19 | 77122.967 | 233515.839 | 88756.972 | 0 | 418303.606 | 0 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2329.294 | 0 | 0
August | 1410990000000 | 853214.65 | 06-AUG-19:10 | 108704.859 | 214470.86 | 85400.145 | 0 | 421878.192 | 3589.95 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2926.327 | 0 | 0
September | 1243410000000 | 816603.662 | 16-SEP-17:10 | 87035.741 | 233515.839 | 86707.746 | 0 | 390774.722 | 0 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2325.298 | 0 | 0
October | 1128580000000 | 711385.246 | 29-OCT-17:10 | 80331.504 | 230772.41 | 82846.355 | 0 | 298909.552 | 0 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2281.109 | 0 | 0
November | 973734000000 | 671974.489 | 27-NOV-20:10 | 115409.096 | 215842.575 | 80356.19 | 0 | 237578.951 | 3589.95 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2953.411 | 0 | 0
December | 860235000000 | 665249.882 | 02-DEC-18:19 | 87035.741 | 233515.839 | 82425.723 | 0 | 240124.837 | 3589.95 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2313.475 | 0 | 0
Annual Sum or Average | 13279100000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 757698000000 | 585974.337 |  | 77122.967 | 214470.86 | 79470.862 | 0 | 160581.621 | 0 | 16244.317 | 0 | 0 | 0 | 0 | 0 | 2281.109 | 0 | 0
Maximum of Months | 1450890000000 | 853214.65 |  | 115409.096 | 233515.839 | 88756.972 | 0 | 421878.192 | 3589.95 | 16244.609 | 0 | 0 | 0 | 0 | 0 | 2953.411 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 378332.78 | 21542.89 | 0 | 399875.67
Cost per Total Building Area ($/m2) | 33.35 | 1.9 | 0 | 35.25
Cost per Net Conditioned Building Area ($/m2) | 33.35 | 1.9 | 0 | 35.25
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 15518.9 | 1367.87 | 1367.87
Net Site Energy | 15518.9 | 1367.87 | 1367.87
Total Source Energy | 44696.39 | 3939.64 | 3939.64
Net Source Energy | 44696.39 | 3939.64 | 3939.64
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 424.87 | 0 | 0 | 0 | 0
Cooling | 4323.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.46 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2828.34 | 0 | 0 | 0 | 0 | 0
Pumps | 464.43 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 804.49 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13399.2 | 2119.7 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 13399.2 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 13399.2 | 100
Total On-Site and Utility Electric Sources | 13399.2 | 100
Total Electricity End Uses | 13399.2 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 6.88 | 0.25 | 0.25 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 6.88 | 0.25 | 0.25 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 6.88 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 6.88 | 0.25 | 0.25 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 6.88 | 0.25 | 0.25 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 6.88 | 0.25 | 0.25 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.25 | 0.25 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.25 | 0.25 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1670965.66 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3013045.77 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.59 | 3021.4 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.59 | 3020.46 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 11.02 | 20897.81 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 9.95 | 18862.7 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.32 | 2512.08 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.24 | 2354.43 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.53 | 1006.19 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.53 | 1004.82 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.52 | 4788 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 74.28 | 140856.79 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.53 | 1006.19 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16741.94 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15312.09 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.59 | 0.06684 | 0.000434 | 0.000738
ROOM_2_FLR_3 FAN COIL | 1.59 | 0.06684 | 0.00043 | 0.000737
ROOM_3_MULT19_FLR_3 FAN COIL | 11.02 | 0.74936 | 0.00295 | 0.005403
ROOM_4_MULT19_FLR_3 FAN COIL | 9.95 | 0.74936 | 0.002888 | 0.004826
ROOM_5_FLR_3 FAN COIL | 1.32 | 0.06684 | 0.00044 | 0.000621
ROOM_6_FLR_3 FAN COIL | 1.24 | 0.06684 | 0.000436 | 0.000584
ROOM_1_FLR_6 FAN COIL | 0.53062 | 0.01671 | 0.000143 | 0.00024
ROOM_2_FLR_6 FAN COIL | 0.5299 | 0.01671 | 0.000142 | 0.00024
ROOM_3_MULT9_FLR_6 FAN COIL | 2.52 | 0.08874 | 0.000761 | 0.001157
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 191478.3461 | 312.8033 | 1006.2734 | 0 | 0.0028 | 7432764.6585 | 80326.5352
February | 175774.4086 | 287.1339 | 923.6355 | 0 | 0.0025 | 6822364.6721 | 73737.0936
March | 213021.6019 | 352.5726 | 1152.5908 | 0 | 0.0031 | 8513766.4778 | 89826.7968
April | 217868.8427 | 362.0396 | 1189.2662 | 0 | 0.0032 | 8784748.0344 | 92016.8349
May | 241798.071 | 402.8981 | 1327.8048 | 0 | 0.0036 | 9808145.741 | 102234.0154
June | 261815.1565 | 437.3135 | 1445.4069 | 0 | 0.0039 | 10676900 | 110804.7524
July | 290906.0812 | 486.5351 | 1610.5721 | 0 | 0.0044 | 11897000 | 123180.3181
August | 282468.8128 | 472.1946 | 1562.2011 | 0 | 0.0042 | 11539600 | 119584.4792
September | 255823.4532 | 426.9573 | 1409.8099 | 0 | 0.0038 | 10413900 | 108233.7534
October | 229566.3786 | 381.9918 | 1256.8371 | 0 | 0.0034 | 9283899.2776 | 97009.2619
November | 201335.1114 | 333.4069 | 1090.6368 | 0 | 0.003 | 8056144.0763 | 84916.7081
December | 190902.9054 | 310.3693 | 992.4424 | 0 | 0.0027 | 7330524.3394 | 79934.0674
Annual Sum or Average | 2752759.1696 | 4566.216 | 14967.4769 | 0 | 0.0408 | 110560000 | 1161804.6163
Minimum of Months | 175774.4086 | 287.1339 | 923.6355 | 0 | 0.0025 | 6822364.6721 | 73737.0936
Maximum of Months | 290906.0812 | 486.5351 | 1610.5721 | 0 | 0.0044 | 11897000 | 123180.3181
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 900808000000 | 584787.935 | 26-JAN-20:10 | 115409.096 | 215842.575 | 99115.622 | 0 | 132436.846 | 3589.95 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2910.881 | 0 | 0
February | 826831000000 | 588074.888 | 08-FEB-20:19 | 115409.096 | 215842.575 | 98846.786 | 0 | 136001.535 | 3589.95 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2901.982 | 0 | 0
March | 1031820000000 | 658228.674 | 17-MAR-17:19 | 77122.967 | 233515.839 | 100377.258 | 0 | 229454.026 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2275.619 | 0 | 0
April | 1064660000000 | 689007.698 | 01-APR-17:10 | 87035.741 | 233515.839 | 100614.673 | 0 | 250069.812 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2288.669 | 0 | 0
May | 1188690000000 | 759024.263 | 27-MAY-17:19 | 87035.741 | 233515.839 | 104593.983 | 0 | 316116.086 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2279.65 | 0 | 0
June | 1293980000000 | 833725.464 | 28-JUN-17:49 | 77122.967 | 233515.839 | 109436.888 | 0 | 395853.467 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2313.337 | 0 | 0
July | 1441840000000 | 841333.004 | 19-JUL-17:19 | 77122.967 | 233515.839 | 107833.55 | 0 | 405045.583 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2332.101 | 0 | 0
August | 1398540000000 | 827457.618 | 05-AUG-17:30 | 87035.741 | 233515.839 | 105525.128 | 0 | 383564.91 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2333.037 | 0 | 0
September | 1262110000000 | 792325.003 | 09-SEP-17:10 | 87035.741 | 233515.839 | 106142.598 | 0 | 347815.59 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2332.27 | 0 | 0
October | 1125150000000 | 669598.151 | 02-OCT-17:10 | 77122.967 | 233515.839 | 99520.661 | 0 | 241682.348 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2273.37 | 0 | 0
November | 976358000000 | 593395.464 | 12-NOV-18:10 | 80331.504 | 230772.41 | 96596.364 | 0 | 164394.005 | 3589.95 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2228.267 | 0 | 0
December | 888417000000 | 586979.569 | 11-DEC-20:00 | 115409.096 | 215842.575 | 97742.184 | 0 | 136001.535 | 3589.95 | 15483.389 | 0 | 0 | 0 | 0 | 0 | 2910.84 | 0 | 0
Annual Sum or Average | 13399200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 826831000000 | 584787.935 |  | 77122.967 | 215842.575 | 96596.364 | 0 | 132436.846 | 0 | 15482.964 | 0 | 0 | 0 | 0 | 0 | 2228.267 | 0 | 0
Maximum of Months | 1441840000000 | 841333.004 |  | 115409.096 | 233515.839 | 109436.888 | 0 | 405045.583 | 3589.95 | 15483.389 | 0 | 0 | 0 | 0 | 0 | 2910.881 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 265676.72 | 18059.39 | 0 | 283736.11
Cost per Total Building Area ($/m2) | 23.42 | 1.59 | 0 | 25.01
Cost per Net Conditioned Building Area ($/m2) | 23.42 | 1.59 | 0 | 25.01
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 15172.7 | 1337.36 | 1337.36
Net Site Energy | 15172.7 | 1337.36 | 1337.36
Total Source Energy | 43530.74 | 3836.9 | 3836.9
Net Source Energy | 43530.74 | 3836.9 | 3836.9
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1361.49 | 0 | 0 | 0 | 0
Cooling | 3220.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.45 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2430.45 | 0 | 0 | 0 | 0 | 0
Pumps | 433.21 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1053.73 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11867.14 | 3305.56 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 11867.14 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 11867.14 | 100
Total On-Site and Utility Electric Sources | 11867.14 | 100
Total Electricity End Uses | 11867.14 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.25 | 0.318 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.25 | 0.318 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.25 | 0.318 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.25 | 0.318 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.25 | 0.318 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.25 | 0.318 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.25 | 0.318 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.25 | 0.318 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1678159.07 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3039421.73 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.25 | 2379.57 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.26 | 2380.23 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 9.11 | 17278 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 7.96 | 15094.84 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.07 | 2030.55 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1 | 1891.46 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.43 | 809.97 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.43 | 809.57 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.01 | 3808.28 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 65.6 | 124398.03 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.43 | 809.98 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16888.5 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15378.01 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.25 | 0.06684 | 0.000531 | 0.000636
ROOM_2_FLR_3 FAN COIL | 1.26 | 0.06684 | 0.000534 | 0.000635
ROOM_3_MULT19_FLR_3 FAN COIL | 9.11 | 0.74936 | 0.0036 | 0.004984
ROOM_4_MULT19_FLR_3 FAN COIL | 7.96 | 0.74936 | 0.003669 | 0.004382
ROOM_5_FLR_3 FAN COIL | 1.07 | 0.06684 | 0.000524 | 0.000555
ROOM_6_FLR_3 FAN COIL | 0.99748 | 0.06684 | 0.000528 | 0.000521
ROOM_1_FLR_6 FAN COIL | 0.42715 | 0.01671 | 0.000181 | 0.00021
ROOM_2_FLR_6 FAN COIL | 0.42694 | 0.01671 | 0.000183 | 0.00021
ROOM_3_MULT9_FLR_6 FAN COIL | 2.01 | 0.08874 | 0.000964 | 0.001029
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 178717.0322 | 314.1729 | 745.6475 | 0 | 0.0028 | 1326083.4362 | 75887.4166
February | 166211.4594 | 295.9345 | 711.8324 | 0 | 0.0026 | 1265985.9913 | 70923.1721
March | 185552.4108 | 343.075 | 856.9427 | 0 | 0.0032 | 1524196.1642 | 80349.3497
April | 194703.0139 | 364.5626 | 921.5993 | 0 | 0.0034 | 1639241.5822 | 84733.7462
May | 220774.4816 | 417.4407 | 1064.916 | 0 | 0.0039 | 1894196.4208 | 96455.0301
June | 231424.2331 | 438.64 | 1121.4948 | 0 | 0.0041 | 1994844.7394 | 101205.9824
July | 256447.8586 | 486.9453 | 1247.0537 | 0 | 0.0046 | 2218189.0684 | 112230.1416
August | 250771.7076 | 476.0081 | 1218.6709 | 0 | 0.0045 | 2167701.9768 | 109731.359
September | 230488.8465 | 436.9164 | 1117.204 | 0 | 0.0041 | 1987212.8853 | 100801.4816
October | 203967.3825 | 383.8175 | 974.805 | 0 | 0.0036 | 1733896.3825 | 88941.7803
November | 178434.3743 | 328.6753 | 817.9959 | 0 | 0.003 | 1454911.5079 | 77152.6219
December | 179325.9584 | 320.3431 | 773.1874 | 0 | 0.0029 | 1375116.1137 | 76616.9564
Annual Sum or Average | 2476818.759 | 4606.5314 | 11571.3495 | 0 | 0.0426 | 20581600 | 1075029.0377
Minimum of Months | 166211.4594 | 295.9345 | 711.8324 | 0 | 0.0026 | 1265985.9913 | 70923.1721
Maximum of Months | 256447.8586 | 486.9453 | 1247.0537 | 0 | 0.0046 | 2218189.0684 | 112230.1416
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 764607000000 | 575607.831 | 24-JAN-20:00 | 115409.096 | 215842.575 | 86184.8 | 0 | 136587.013 | 3589.95 | 15549.318 | 0 | 0 | 0 | 0 | 0 | 2445.079 | 0 | 0
February | 729956000000 | 571007.107 | 25-FEB-18:00 | 87035.741 | 233515.839 | 92447.6 | 0 | 136587.013 | 3589.95 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2282.082 | 0 | 0
March | 878837000000 | 579022.757 | 27-MAR-19:00 | 115409.096 | 215842.575 | 89067.13 | 0 | 136587.013 | 3589.95 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2978.111 | 0 | 0
April | 945171000000 | 630389.053 | 15-APR-17:00 | 87035.741 | 233515.839 | 88322.821 | 0 | 203636.354 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2329.415 | 0 | 0
May | 1092180000000 | 708541.921 | 31-MAY-17:30 | 77122.967 | 233515.839 | 88132.392 | 0 | 291893.863 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2327.978 | 0 | 0
June | 1150210000000 | 748902.183 | 08-JUN-19:10 | 115409.096 | 215842.575 | 87012.851 | 0 | 312122.078 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2966.701 | 0 | 0
July | 1278990000000 | 817336.352 | 02-JUL-17:19 | 80331.504 | 230772.41 | 90240.859 | 0 | 398150.238 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2292.458 | 0 | 0
August | 1249880000000 | 745766.54 | 14-AUG-17:19 | 77122.967 | 233515.839 | 88946.278 | 0 | 328304.037 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2328.536 | 0 | 0
September | 1145810000000 | 678122.535 | 01-SEP-17:19 | 77122.967 | 233515.839 | 86635.595 | 0 | 262974.695 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2324.557 | 0 | 0
October | 999748000000 | 633609.611 | 21-OCT-17:10 | 87035.741 | 233515.839 | 85822.93 | 0 | 209365.109 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2321.11 | 0 | 0
November | 838888000000 | 577270.943 | 28-NOV-20:10 | 115409.096 | 215842.575 | 87841.527 | 0 | 136587.013 | 3589.95 | 15549.391 | 0 | 0 | 0 | 0 | 0 | 2451.392 | 0 | 0
December | 792879000000 | 577320.53 | 04-DEC-20:10 | 115409.096 | 215842.575 | 87369.145 | 0 | 136587.013 | 3589.95 | 15549.279 | 0 | 0 | 0 | 0 | 0 | 2973.472 | 0 | 0
Annual Sum or Average | 11867100000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 729956000000 | 571007.107 |  | 77122.967 | 215842.575 | 85822.93 | 0 | 136587.013 | 0 | 15548.882 | 0 | 0 | 0 | 0 | 0 | 2282.082 | 0 | 0
Maximum of Months | 1278990000000 | 817336.352 |  | 115409.096 | 233515.839 | 92447.6 | 0 | 398150.238 | 3589.95 | 15549.391 | 0 | 0 | 0 | 0 | 0 | 2978.111 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 344401.38 | 34180.66 | 0 | 378582.04
Cost per Total Building Area ($/m2) | 30.36 | 3.01 | 0 | 33.37
Cost per Net Conditioned Building Area ($/m2) | 30.36 | 3.01 | 0 | 33.37
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 13105.51 | 1155.15 | 1155.15
Net Site Energy | 13105.51 | 1155.15 | 1155.15
Total Source Energy | 36343.88 | 3203.43 | 3203.43
Net Source Energy | 36343.88 | 3203.43 | 3203.43
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 191.96 | 0 | 0 | 0 | 0
Cooling | 2593.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.41 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2255.05 | 0 | 0 | 0 | 0 | 0
Pumps | 367.9 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1023.38 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.88 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10999.83 | 2105.67 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10999.83 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10999.83 | 100
Total On-Site and Utility Electric Sources | 10999.83 | 100
Total Electricity End Uses | 10999.83 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.25 | 0.318 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.25 | 0.318 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.25 | 0.318 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.25 | 0.318 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.25 | 0.318 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.25 | 0.318 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.25 | 0.318 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.25 | 0.318 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1255688.2 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2704789.19 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.15 | 2175.55 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.05 | 1988.5 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.99 | 17054.43 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 6.17 | 11704.64 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.98 | 1850.16 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.86 | 1621.89 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.38 | 729.78 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.36 | 673.78 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.9 | 3605.84 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 60.35 | 114438.35 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.38 | 729.78 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15029.12 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11506.64 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.15 | 0.06684 | 0.000275 | 0.00054
ROOM_2_FLR_3 FAN COIL | 1.05 | 0.06684 | 0.000275 | 0.000496
ROOM_3_MULT19_FLR_3 FAN COIL | 8.99 | 0.74936 | 0.001907 | 0.004327
ROOM_4_MULT19_FLR_3 FAN COIL | 6.17 | 0.74936 | 0.001909 | 0.003031
ROOM_5_FLR_3 FAN COIL | 0.9757 | 0.06684 | 0.000276 | 0.000458
ROOM_6_FLR_3 FAN COIL | 0.85532 | 0.06684 | 0.000276 | 0.000402
ROOM_1_FLR_6 FAN COIL | 0.38485 | 0.01671 | 9.7e-05 | 0.000178
ROOM_2_FLR_6 FAN COIL | 0.35532 | 0.01671 | 9.7e-05 | 0.000165
ROOM_3_MULT9_FLR_6 FAN COIL | 1.9 | 0.08874 | 0.000522 | 0.000886
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 85325.1842 | 73.611 | 689.8645 | 0 | 0.0003 | 4162180.9713 | 31635.9389
February | 77175.623 | 66.5641 | 626.8626 | 0 | 0.0003 | 3782081.1548 | 28623.146
March | 86590.3426 | 74.6191 | 714.9979 | 0 | 0.0003 | 4313876.6513 | 32150.4935
April | 84616.5908 | 72.8757 | 706.3082 | 0 | 0.0003 | 4261476.6392 | 31440.8627
May | 89965.7284 | 77.4366 | 759.2046 | 0 | 0.0004 | 4580655.5255 | 33453.5932
June | 88342.3331 | 76.0216 | 748.6643 | 0 | 0.0004 | 4517071.8813 | 32859.5751
July | 96110.3877 | 82.6836 | 818.5513 | 0 | 0.0004 | 4938750.7513 | 35761.3344
August | 97859.6794 | 84.1813 | 834.7366 | 0 | 0.0004 | 5036410.1051 | 36416.1481
September | 92983.2022 | 79.9975 | 791.1696 | 0 | 0.0004 | 4773539.9984 | 34595.4699
October | 92416.5608 | 79.5346 | 781.9359 | 0 | 0.0004 | 4717812.1751 | 34371.1827
November | 85218.7543 | 73.3893 | 712.2379 | 0 | 0.0003 | 4297256.572 | 31667.3638
December | 86456.7625 | 74.5415 | 707.1961 | 0 | 0.0003 | 4266780.0481 | 32080.4583
Annual Sum or Average | 1063061.1492 | 915.456 | 8891.7297 | 0 | 0.0042 | 53647900 | 395055.5666
Minimum of Months | 77175.623 | 66.5641 | 626.8626 | 0 | 0.0003 | 3782081.1548 | 28623.146
Maximum of Months | 97859.6794 | 84.1813 | 834.7366 | 0 | 0.0004 | 5036410.1051 | 36416.1481
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 853403000000 | 534196.031 | 12-JAN-20:10 | 115409.096 | 215842.575 | 82579.39 | 0 | 102201.695 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2895.803 | 0 | 0
February | 775469000000 | 534856.282 | 23-FEB-20:10 | 115409.096 | 215842.575 | 83207.476 | 0 | 102201.695 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2927.969 | 0 | 0
March | 884507000000 | 536546.433 | 31-MAR-19:10 | 115409.096 | 215842.575 | 85413.444 | 0 | 102201.695 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2412.152 | 0 | 0
April | 873763000000 | 572717.408 | 11-APR-17:10 | 77122.967 | 233515.839 | 79722.509 | 0 | 168419.189 | 0 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2259.383 | 0 | 0
May | 939206000000 | 566402.854 | 30-MAY-19:10 | 115409.096 | 215842.575 | 77792.792 | 0 | 139657.327 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2433.593 | 0 | 0
June | 926169000000 | 564505.523 | 28-JUN-19:10 | 115409.096 | 215842.575 | 77461.548 | 0 | 137565.498 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2959.335 | 0 | 0
July | 1012630000000 | 584347.017 | 29-JUL-17:19 | 87035.741 | 233515.839 | 79856.878 | 0 | 169939.582 | 0 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2321.455 | 0 | 0
August | 1032650000000 | 620134.893 | 08-AUG-17:10 | 77122.967 | 233515.839 | 79795.159 | 0 | 215699.835 | 0 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2323.571 | 0 | 0
September | 978755000000 | 579780.156 | 23-SEP-17:10 | 87035.741 | 233515.839 | 80486.021 | 0 | 164772.928 | 0 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2292.106 | 0 | 0
October | 967329000000 | 560713.138 | 07-OCT-17:10 | 87035.741 | 233515.839 | 80570.099 | 0 | 145590.252 | 0 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2323.685 | 0 | 0
November | 881099000000 | 534718.618 | 02-NOV-20:00 | 115409.096 | 215842.575 | 83020.038 | 0 | 102201.695 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2977.742 | 0 | 0
December | 874850000000 | 534369.884 | 21-DEC-20:10 | 115409.096 | 215842.575 | 82698.492 | 0 | 102201.695 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2950.554 | 0 | 0
Annual Sum or Average | 10999800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 775469000000 | 534196.031 |  | 77122.967 | 215842.575 | 77461.548 | 0 | 102201.695 | 0 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2259.383 | 0 | 0
Maximum of Months | 1032650000000 | 620134.893 |  | 115409.096 | 233515.839 | 85413.444 | 0 | 215699.835 | 3589.95 | 11677.521 | 0 | 0 | 0 | 0 | 0 | 2977.742 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 135575.96 | 17746.31 | 0 | 153322.27
Cost per Total Building Area ($/m2) | 11.95 | 1.56 | 0 | 13.51
Cost per Net Conditioned Building Area ($/m2) | 11.95 | 1.56 | 0 | 13.51
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 15847.49 | 1396.83 | 1396.83
Net Site Energy | 15847.49 | 1396.83 | 1396.83
Total Source Energy | 50623.65 | 4462.09 | 4462.09
Net Source Energy | 50623.65 | 4462.09 | 4462.09
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 632.7 | 0 | 0 | 0 | 0
Cooling | 4160.26 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2786.51 | 0 | 0 | 0 | 0 | 0
Pumps | 678.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 916.73 | 0 | 0 | 0 | 7180.08
Refrigeration | 75.78 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13407.72 | 2439.77 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 13407.72 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 13407.72 | 100
Total On-Site and Utility Electric Sources | 13407.72 | 100
Total Electricity End Uses | 13407.72 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.25 | 0.318 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.25 | 0.318 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.25 | 0.318 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.25 | 0.318 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.25 | 0.318 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.25 | 0.318 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.25 | 0.318 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.25 | 0.318 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.25 | 0.318 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.25 | 0.318 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.25 | 0.318 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.25 | 0.318 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2399675.83 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2995041.55 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.52 | 2879.53 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.51 | 2855.8 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 10.7 | 20292.21 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 9.4 | 17822.6 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.25 | 2360.97 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.15 | 2176.77 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.51 | 970.28 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.51 | 964.2 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.43 | 4608.95 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 73.49 | 139346.48 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.51 | 970.28 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16641.9 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21989.71 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.52 | 0.06684 | 0.000422 | 0.000669
ROOM_2_FLR_3 FAN COIL | 1.51 | 0.06684 | 0.00042 | 0.000661
ROOM_3_MULT19_FLR_3 FAN COIL | 10.7 | 0.74936 | 0.002885 | 0.004927
ROOM_4_MULT19_FLR_3 FAN COIL | 9.4 | 0.74936 | 0.002848 | 0.004301
ROOM_5_FLR_3 FAN COIL | 1.25 | 0.06684 | 0.000418 | 0.000546
ROOM_6_FLR_3 FAN COIL | 1.15 | 0.06684 | 0.000416 | 0.000502
ROOM_1_FLR_6 FAN COIL | 0.51168 | 0.01671 | 0.000146 | 0.00022
ROOM_2_FLR_6 FAN COIL | 0.50848 | 0.01671 | 0.000146 | 0.000218
ROOM_3_MULT9_FLR_6 FAN COIL | 2.43 | 0.08874 | 0.000781 | 0.001051
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 212690.6771 | 334.0669 | 1326.1285 | 0 | 0.0025 | 6613250.3226 | 88268.22
February | 205590.5252 | 328.1817 | 1331.3631 | 0 | 0.0025 | 6639558.6529 | 85869.0226
March | 230393.7462 | 368.383 | 1497.7004 | 0 | 0.0028 | 7469111.4298 | 96291.8009
April | 254826.2008 | 411.6674 | 1696.179 | 0 | 0.0032 | 8459091.3383 | 106941.6919
May | 276488.0952 | 447.5141 | 1848.3764 | 0 | 0.0035 | 9218153.2115 | 116121.0233
June | 297387.3717 | 482.4934 | 1998.9238 | 0 | 0.0038 | 9968999.0969 | 125018.196
July | 318981.2169 | 517.9795 | 2148.3123 | 0 | 0.004 | 10714000 | 134142.9156
August | 316477.5176 | 513.8243 | 2130.6084 | 0 | 0.004 | 10625700 | 133080.7139
September | 287623.2096 | 466.3756 | 1930.6989 | 0 | 0.0036 | 9628738.758 | 120884.7709
October | 263382.0567 | 425.9831 | 1757.7707 | 0 | 0.0033 | 8766276.3399 | 110583.6197
November | 223697.5061 | 358.5974 | 1462.8294 | 0 | 0.0028 | 7295241.9927 | 93588.8917
December | 214747.5387 | 339.4052 | 1358.7637 | 0 | 0.0026 | 6776079.6719 | 89340.8993
Annual Sum or Average | 3102285.6618 | 4994.4714 | 20487.6546 | 0 | 0.0386 | 102174000 | 1300131.7658
Minimum of Months | 205590.5252 | 328.1817 | 1326.1285 | 0 | 0.0025 | 6613250.3226 | 85869.0226
Maximum of Months | 318981.2169 | 517.9795 | 2148.3123 | 0 | 0.004 | 10714000 | 134142.9156
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 867817000000 | 546534.149 | 18-JAN-18:10 | 77122.967 | 233515.839 | 101802.341 | 0 | 106077.232 | 3589.95 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2265.236 | 0 | 0
February | 871270000000 | 607515.596 | 27-FEB-18:10 | 77122.967 | 233515.839 | 98642.612 | 0 | 170221.683 | 3589.95 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2261.96 | 0 | 0
March | 980127000000 | 643528.802 | 30-MAR-19:10 | 115409.096 | 215842.575 | 95194.422 | 0 | 188437.688 | 3589.95 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2894.487 | 0 | 0
April | 1110040000000 | 670385.55 | 21-APR-17:10 | 77122.967 | 233515.839 | 98465.435 | 0 | 236833.708 | 0 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2287.016 | 0 | 0
May | 1209640000000 | 712272.606 | 31-MAY-17:19 | 77122.967 | 233515.839 | 101384.987 | 0 | 275813.269 | 0 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2274.959 | 0 | 0
June | 1308170000000 | 781223.818 | 27-JUN-17:19 | 77122.967 | 233515.839 | 106329.525 | 0 | 339815.614 | 0 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2279.288 | 0 | 0
July | 1405940000000 | 769823.238 | 25-JUL-19:10 | 115409.096 | 215842.575 | 102443.618 | 0 | 307977.774 | 3589.95 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2399.641 | 0 | 0
August | 1394350000000 | 781516.921 | 02-AUG-17:19 | 77122.967 | 233515.839 | 103629.116 | 0 | 342763.286 | 0 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2325.128 | 0 | 0
September | 1263520000000 | 731299.172 | 01-SEP-17:10 | 77122.967 | 233515.839 | 102273.228 | 0 | 293928.716 | 0 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2297.838 | 0 | 0
October | 1150350000000 | 656720.866 | 03-OCT-17:10 | 77122.967 | 233515.839 | 97889.856 | 0 | 223758.159 | 0 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2273.46 | 0 | 0
November | 957311000000 | 611755.094 | 10-NOV-18:19 | 77122.967 | 233515.839 | 96429.645 | 0 | 176668.963 | 3589.95 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2267.146 | 0 | 0
December | 889185000000 | 601599.499 | 05-DEC-18:19 | 77122.967 | 233515.839 | 96318.894 | 0 | 166632.334 | 3589.95 | 22160.714 | 0 | 0 | 0 | 0 | 0 | 2258.801 | 0 | 0
Annual Sum or Average | 13407700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 867817000000 | 546534.149 |  | 77122.967 | 215842.575 | 95194.422 | 0 | 106077.232 | 0 | 22160.584 | 0 | 0 | 0 | 0 | 0 | 2258.801 | 0 | 0
Maximum of Months | 1405940000000 | 781516.921 |  | 115409.096 | 233515.839 | 106329.525 | 0 | 342763.286 | 3589.95 | 22160.714 | 0 | 0 | 0 | 0 | 0 | 2894.487 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 330438.14 | 19622.2 | 0 | 350060.33
Cost per Total Building Area ($/m2) | 29.13 | 1.73 | 0 | 30.86
Cost per Net Conditioned Building Area ($/m2) | 29.13 | 1.73 | 0 | 30.86
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 12970.89 | 1143.28 | 1143.28
Net Site Energy | 12970.89 | 1143.28 | 1143.28
Total Source Energy | 34251.22 | 3018.98 | 3018.98
Net Source Energy | 34251.22 | 3018.98 | 3018.98
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 895.14 | 0 | 0 | 0 | 0
Cooling | 1510.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2387.47 | 0 | 0 | 0 | 0 | 0
Pumps | 347.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1156.94 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10028.46 | 2942.42 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10028.46 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10028.46 | 100
Total On-Site and Utility Electric Sources | 10028.46 | 100
Total Electricity End Uses | 10028.46 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 6.88 | 0.34 | 0.34 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 6.88 | 0.34 | 0.34 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 6.88 | 0.34 | 0.34 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.34 | 0.34 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.34 | 0.34 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.34 | 0.34 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 6.88 | 0.34 | 0.34 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 6.88 | 0.34 | 0.34 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 6.88 | 0.34 | 0.34 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.34 | 0.34 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 6.88 | 0.34 | 0.34 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 6.88 | 0.34 | 0.34 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 6.88 | 0.34 | 0.34 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.34 | 0.34 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.34 | 0.34 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.34 | 0.34 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 6.88 | 0.34 | 0.34 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 6.88 | 0.34 | 0.34 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.34 | 0.34 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 6.88 | 0.34 | 0.34 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 6.88 | 0.34 | 0.34 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 6.88 | 0.34 | 0.34 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 6.88 | 0.34 | 0.34 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1280580.77 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2804642.07 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.3 | 2467.67 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.06 | 2012.45 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 11.05 | 20951.75 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 5.66 | 10727.26 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.02 | 1930.48 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.78 | 1484.35 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.42 | 795.49 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.35 | 662.81 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.31 | 4382.48 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 62.69 | 118881.01 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.42 | 795.49 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15583.95 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11734.75 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.3 | 0.06684 | 0.000431 | 0.000602
ROOM_2_FLR_3 FAN COIL | 1.06 | 0.06684 | 0.000428 | 0.000495
ROOM_3_MULT19_FLR_3 FAN COIL | 11.05 | 0.74936 | 0.002947 | 0.005171
ROOM_4_MULT19_FLR_3 FAN COIL | 5.66 | 0.74936 | 0.002882 | 0.002779
ROOM_5_FLR_3 FAN COIL | 1.02 | 0.06684 | 0.000438 | 0.000469
ROOM_6_FLR_3 FAN COIL | 0.78278 | 0.06684 | 0.000434 | 0.000361
ROOM_1_FLR_6 FAN COIL | 0.41951 | 0.01671 | 0.000142 | 0.000192
ROOM_2_FLR_6 FAN COIL | 0.34954 | 0.01671 | 0.000141 | 0.000161
ROOM_3_MULT9_FLR_6 FAN COIL | 2.31 | 0.08874 | 0.000756 | 0.001056
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 87017.1809 | 75.57 | 614.2073 | 0 | 0.0003 | 3705372.9093 | 31990.7148
February | 76678.2409 | 66.2985 | 593.5941 | 0 | 0.0003 | 3581248.7864 | 28349.5003
March | 84768.5305 | 73.3451 | 647.0028 | 0 | 0.0003 | 3903434.8135 | 31312.5108
April | 82447.6932 | 71.2194 | 650.3383 | 0 | 0.0003 | 3923643.9912 | 30519.4416
May | 86980.1017 | 75.0311 | 704.5953 | 0 | 0.0003 | 4251062.2826 | 32253.6519
June | 84473.0641 | 72.8039 | 695.8486 | 0 | 0.0003 | 4198334.7898 | 31359.2761
July | 89200.8076 | 76.8327 | 742.9973 | 0 | 0.0004 | 4482832.9156 | 33139.405
August | 88607.2852 | 76.318 | 738.6811 | 0 | 0.0004 | 4456793.4568 | 32920.8172
September | 87103.2227 | 75.0148 | 727.5193 | 0 | 0.0003 | 4389454.5761 | 32366.2045
October | 87633.5879 | 75.5214 | 723.0375 | 0 | 0.0003 | 4362380.5087 | 32536.0909
November | 82322.1943 | 71.0896 | 653.183 | 0 | 0.0003 | 3940822.0059 | 30484.6854
December | 85235.1877 | 73.9433 | 615.7911 | 0 | 0.0003 | 3714990.2624 | 31378.7962
Annual Sum or Average | 1022467.0967 | 882.9877 | 8106.7957 | 0 | 0.0039 | 48910400 | 378611.0947
Minimum of Months | 76678.2409 | 66.2985 | 593.5941 | 0 | 0.0003 | 3581248.7864 | 28349.5003
Maximum of Months | 89200.8076 | 76.8327 | 742.9973 | 0 | 0.0004 | 4482832.9156 | 33139.405
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 759741000000 | 508074.99 | 15-JAN-18:00 | 80331.504 | 230772.41 | 87636.105 | 0 | 91587.265 | 3589.95 | 11907.724 | 0 | 0 | 0 | 0 | 0 | 2250.031 | 0 | 0
February | 734291000000 | 539713.282 | 15-FEB-20:00 | 115409.096 | 215842.575 | 85784.349 | 0 | 104227.726 | 3589.95 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2953.96 | 0 | 0
March | 800351000000 | 529643.755 | 25-MAR-17:49 | 87035.741 | 233515.839 | 90656.11 | 0 | 104227.726 | 0 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2302.713 | 0 | 0
April | 804494000000 | 542061.133 | 12-APR-19:10 | 115409.096 | 215842.575 | 88141.218 | 0 | 104227.726 | 3589.95 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2944.941 | 0 | 0
May | 871627000000 | 542504.398 | 24-MAY-19:19 | 115409.096 | 215842.575 | 88544.993 | 0 | 104227.726 | 3589.95 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2984.432 | 0 | 0
June | 860816000000 | 542827.738 | 21-JUN-19:30 | 115409.096 | 215842.575 | 88880.475 | 0 | 104227.726 | 3589.95 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2972.289 | 0 | 0
July | 919149000000 | 635684.111 | 02-JUL-17:10 | 80331.504 | 230772.41 | 85194.815 | 0 | 225191.015 | 0 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2288.739 | 0 | 0
August | 913810000000 | 546534.363 | 26-AUG-17:10 | 87035.741 | 233515.839 | 83585.612 | 0 | 128173.952 | 0 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2317.592 | 0 | 0
September | 900003000000 | 613294.397 | 28-SEP-17:10 | 77122.967 | 233515.839 | 85632.648 | 0 | 202808.051 | 0 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2309.264 | 0 | 0
October | 894452000000 | 540671.319 | 03-OCT-19:10 | 115409.096 | 215842.575 | 87265.356 | 0 | 104227.726 | 3589.95 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2430.99 | 0 | 0
November | 808017000000 | 538974.955 | 02-NOV-20:00 | 115409.096 | 215842.575 | 85033.648 | 0 | 104227.726 | 3589.95 | 11906.404 | 0 | 0 | 0 | 0 | 0 | 2965.557 | 0 | 0
December | 761713000000 | 495357.863 | 06-DEC-20:00 | 115409.096 | 215842.575 | 84876.014 | 0 | 60785.017 | 3589.95 | 11909.694 | 0 | 0 | 0 | 0 | 0 | 2945.517 | 0 | 0
Annual Sum or Average | 10028500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 734291000000 | 495357.863 |  | 77122.967 | 215842.575 | 83585.612 | 0 | 60785.017 | 0 | 11905.627 | 0 | 0 | 0 | 0 | 0 | 2250.031 | 0 | 0
Maximum of Months | 919149000000 | 635684.111 |  | 115409.096 | 233515.839 | 90656.11 | 0 | 225191.015 | 3589.95 | 11909.694 | 0 | 0 | 0 | 0 | 0 | 2984.432 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 402376.35 | 24941.51 | 0 | 427317.86
Cost per Total Building Area ($/m2) | 35.47 | 2.2 | 0 | 37.66
Cost per Net Conditioned Building Area ($/m2) | 35.47 | 2.2 | 0 | 37.66
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16151.7 | 1423.65 | 1423.65
Net Site Energy | 16151.7 | 1423.65 | 1423.65
Total Source Energy | 46104.25 | 4063.74 | 4063.74
Net Source Energy | 46104.25 | 4063.74 | 4063.74
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2624.96 | 0 | 0 | 0 | 0
Cooling | 2718.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2546.93 | 0 | 0 | 0 | 0 | 0
Pumps | 411.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1176.41 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.1 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11459.99 | 4691.71 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 11459.99 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 11459.99 | 100
Total On-Site and Utility Electric Sources | 11459.99 | 100
Total Electricity End Uses | 11459.99 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.39 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.39 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.39 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1758057.93 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3194678.9 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.49 | 2820.49 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.45 | 2745.39 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 10.13 | 19201.37 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.04 | 15239.82 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.24 | 2349.06 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.14 | 2158.32 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.49 | 927.97 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.48 | 906.84 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.24 | 4239.34 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 67.39 | 127796.06 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.49 | 927.97 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17751.18 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16110.17 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.49 | 0.06684 | 0.000606 | 0.000755
ROOM_2_FLR_3 FAN COIL | 1.45 | 0.06684 | 0.000606 | 0.000737
ROOM_3_MULT19_FLR_3 FAN COIL | 10.13 | 0.74936 | 0.00417 | 0.005539
ROOM_4_MULT19_FLR_3 FAN COIL | 8.04 | 0.74936 | 0.004173 | 0.004509
ROOM_5_FLR_3 FAN COIL | 1.24 | 0.06684 | 0.000599 | 0.000637
ROOM_6_FLR_3 FAN COIL | 1.14 | 0.06684 | 0.000599 | 0.00059
ROOM_1_FLR_6 FAN COIL | 0.48937 | 0.01671 | 0.000207 | 0.000243
ROOM_2_FLR_6 FAN COIL | 0.47823 | 0.01671 | 0.000207 | 0.000238
ROOM_3_MULT9_FLR_6 FAN COIL | 2.24 | 0.08874 | 0.001111 | 0.001154
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 172489.4601 | 291.9853 | 748.437 | 0 | 0.0031 | 46533.739 | 72081.0198
February | 151032.6972 | 261.1295 | 685.5138 | 0 | 0.0028 | 42623.7396 | 63614.2799
March | 163125.5923 | 298.8266 | 833.1033 | 0 | 0.0034 | 51807.0745 | 70242.8933
April | 159991.5548 | 303.8013 | 876.2655 | 0 | 0.0036 | 54494.854 | 69873.1812
May | 184404.2314 | 357.0994 | 1048.3027 | 0 | 0.0042 | 65196.0654 | 81169.6874
June | 202772.8525 | 396.0989 | 1171.6557 | 0 | 0.0047 | 72868.7068 | 89568.5473
July | 223977.3251 | 438.5312 | 1299.7625 | 0 | 0.0053 | 80836.352 | 99027.4249
August | 224513.8095 | 439.6928 | 1303.4897 | 0 | 0.0053 | 81068.1893 | 99274.7874
September | 187488.3568 | 365.5871 | 1079.7238 | 0 | 0.0044 | 67150.9868 | 82757.2266
October | 177241.8185 | 339.7082 | 988.1434 | 0 | 0.004 | 61453.5426 | 77695.0246
November | 159643.9554 | 296.6104 | 838.3012 | 0 | 0.0034 | 52131.7491 | 69124.2118
December | 164179.967 | 284.5481 | 748.9836 | 0 | 0.0031 | 46570.4247 | 69214.7193
Annual Sum or Average | 2170861.6206 | 4073.6189 | 11621.6823 | 0 | 0.0473 | 722735.4239 | 943643.0034
Minimum of Months | 151032.6972 | 261.1295 | 685.5138 | 0 | 0.0028 | 42623.7396 | 63614.2799
Maximum of Months | 224513.8095 | 439.6928 | 1303.4897 | 0 | 0.0053 | 81068.1893 | 99274.7874
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 737858000000 | 513053.239 | 08-JAN-20:00 | 108704.859 | 214470.86 | 90507.308 | 0 | 76592.582 | 3589.95 | 16284.709 | 0 | 0 | 0 | 0 | 0 | 2902.971 | 0 | 0
February | 675859000000 | 505416.725 | 15-FEB-18:10 | 77122.967 | 233515.839 | 93759.073 | 0 | 78870.277 | 3589.95 | 16281.482 | 0 | 0 | 0 | 0 | 0 | 2277.136 | 0 | 0
March | 821474000000 | 582959.331 | 09-MAR-20:10 | 115409.096 | 215842.575 | 85793.976 | 0 | 143090.06 | 3589.95 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2952.63 | 0 | 0
April | 864092000000 | 588532.341 | 25-APR-19:10 | 115409.096 | 215842.575 | 93455.908 | 0 | 141571.556 | 3589.95 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2382.211 | 0 | 0
May | 1033780000000 | 673868.713 | 15-MAY-17:10 | 77122.967 | 233515.839 | 89766.939 | 0 | 254858.144 | 0 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2323.779 | 0 | 0
June | 1155440000000 | 843270.178 | 30-JUN-17:19 | 77122.967 | 233515.839 | 93647.131 | 0 | 420373.496 | 0 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2329.7 | 0 | 0
July | 1281770000000 | 850087.405 | 24-JUL-17:30 | 77122.967 | 233515.839 | 93030.967 | 0 | 427807.784 | 0 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2328.803 | 0 | 0
August | 1285450000000 | 852257.816 | 17-AUG-17:19 | 77122.967 | 233515.839 | 93045.841 | 0 | 429964.204 | 0 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2327.92 | 0 | 0
September | 1064770000000 | 680917.17 | 09-SEP-17:10 | 87035.741 | 233515.839 | 92736.922 | 0 | 249022.953 | 0 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2324.67 | 0 | 0
October | 974432000000 | 634205.439 | 02-OCT-19:00 | 115409.096 | 215842.575 | 85595.759 | 0 | 194534.5 | 3589.95 | 16281.286 | 0 | 0 | 0 | 0 | 0 | 2952.273 | 0 | 0
November | 826622000000 | 593633.749 | 04-NOV-18:00 | 87035.741 | 233515.839 | 88033.663 | 0 | 162858.958 | 3589.95 | 16281.218 | 0 | 0 | 0 | 0 | 0 | 2318.38 | 0 | 0
December | 738439000000 | 494013.677 | 02-DEC-18:00 | 87035.741 | 233515.839 | 94258.392 | 0 | 57048.669 | 3589.95 | 16285.964 | 0 | 0 | 0 | 0 | 0 | 2279.122 | 0 | 0
Annual Sum or Average | 11460000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 675859000000 | 494013.677 |  | 77122.967 | 214470.86 | 85595.759 | 0 | 57048.669 | 0 | 16281.044 | 0 | 0 | 0 | 0 | 0 | 2277.136 | 0 | 0
Maximum of Months | 1285450000000 | 852257.816 |  | 115409.096 | 233515.839 | 94258.392 | 0 | 429964.204 | 3589.95 | 16285.964 | 0 | 0 | 0 | 0 | 0 | 2952.63 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 221273.95 | 46337.16 | 0 | 267611.12
Cost per Total Building Area ($/m2) | 19.5 | 4.08 | 0 | 23.59
Cost per Net Conditioned Building Area ($/m2) | 19.5 | 4.08 | 0 | 23.59
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 15824.91 | 1394.84 | 1394.84
Net Site Energy | 15824.91 | 1394.84 | 1394.84
Total Source Energy | 45032.32 | 3969.25 | 3969.25
Net Source Energy | 45032.32 | 3969.25 | 3969.25
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1314.42 | 0 | 0 | 0 | 0
Cooling | 3081.86 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.41 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3016.55 | 0 | 0 | 0 | 0 | 0
Pumps | 586.14 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1153.15 | 0 | 0 | 0 | 7180.08
Refrigeration | 75.9 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12466.99 | 3357.92 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12466.99 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12466.99 | 100
Total On-Site and Utility Electric Sources | 12466.99 | 100
Total Electricity End Uses | 12466.99 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.39 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.39 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.39 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2181979.64 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3008183.55 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.78 | 3377.87 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.77 | 3356.57 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 11.32 | 21474.02 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 9.82 | 18627.12 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.41 | 2670.97 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.32 | 2508.78 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.59 | 1116.83 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.59 | 1113.21 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.48 | 4701.87 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 79.29 | 150349.9 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.59 | 1116.83 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16714.92 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19994.82 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.78 | 0.06684 | 0.000538 | 0.000672
ROOM_2_FLR_3 FAN COIL | 1.77 | 0.06684 | 0.000541 | 0.000668
ROOM_3_MULT19_FLR_3 FAN COIL | 11.32 | 0.74936 | 0.003586 | 0.004425
ROOM_4_MULT19_FLR_3 FAN COIL | 9.82 | 0.74936 | 0.003653 | 0.003764
ROOM_5_FLR_3 FAN COIL | 1.41 | 0.06684 | 0.000538 | 0.00053
ROOM_6_FLR_3 FAN COIL | 1.32 | 0.06684 | 0.000541 | 0.000495
ROOM_1_FLR_6 FAN COIL | 0.58897 | 0.01671 | 0.000185 | 0.000219
ROOM_2_FLR_6 FAN COIL | 0.58706 | 0.01671 | 0.000187 | 0.000219
ROOM_3_MULT9_FLR_6 FAN COIL | 2.48 | 0.08874 | 0.000978 | 0.00093
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 253680.4713 | 422.4046 | 1041.0247 | 0 | 0.0041 | 1082361.8735 | 106645.787
February | 234106.7041 | 393.7383 | 981.95 | 0 | 0.0039 | 1020969.1641 | 98802.1956
March | 268036.112 | 454.7376 | 1145.5599 | 0 | 0.0045 | 1191107.4606 | 113507.6483
April | 279609.0843 | 480.7988 | 1229.8077 | 0 | 0.0048 | 1278748.5969 | 119038.9778
May | 314071.5113 | 543.0579 | 1397.62 | 0 | 0.0055 | 1453258.7995 | 134005.0271
June | 321032.9271 | 556.2143 | 1434.6576 | 0 | 0.0056 | 1491778.2104 | 137085.0689
July | 347645.8287 | 602.8121 | 1556.2336 | 0 | 0.0061 | 1618197.8759 | 148497.065
August | 340927.6074 | 591.145 | 1526.063 | 0 | 0.006 | 1586825.8217 | 145625.6236
September | 312995.1822 | 542.2951 | 1398.7746 | 0 | 0.0055 | 1454466.5419 | 133653.5162
October | 291033.6285 | 501.5727 | 1286.1671 | 0 | 0.005 | 1337358.3348 | 124013.5333
November | 255492.3568 | 433.5978 | 1092.7142 | 0 | 0.0043 | 1136161.5912 | 108209.4978
December | 252588.6705 | 419.8927 | 1032.7887 | 0 | 0.0041 | 1073793.8876 | 106118.7378
Annual Sum or Average | 3471220.0843 | 5942.2669 | 15123.361 | 0 | 0.0592 | 15725000 | 1475202.6784
Minimum of Months | 234106.7041 | 393.7383 | 981.95 | 0 | 0.0039 | 1020969.1641 | 98802.1956
Maximum of Months | 347645.8287 | 602.8121 | 1556.2336 | 0 | 0.0061 | 1618197.8759 | 148497.065
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 858110000000 | 562210.582 | 25-JAN-18:10 | 77122.967 | 233515.839 | 111103.82 | 0 | 114445.81 | 3589.95 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2266.495 | 0 | 0
February | 809437000000 | 617493.27 | 14-FEB-18:10 | 77122.967 | 233515.839 | 111569.08 | 0 | 169270.534 | 3589.95 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2259.199 | 0 | 0
March | 944324000000 | 634714.989 | 18-MAR-17:00 | 87035.741 | 233515.839 | 114141.37 | 0 | 177593.464 | 0 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2262.875 | 0 | 0
April | 1013810000000 | 645886.985 | 24-APR-19:40 | 115409.096 | 215842.575 | 110452.916 | 0 | 177534.658 | 3589.95 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2892.091 | 0 | 0
May | 1152160000000 | 673035.527 | 31-MAY-17:10 | 77122.967 | 233515.839 | 109424.701 | 0 | 230527.417 | 0 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2278.902 | 0 | 0
June | 1182700000000 | 706548.672 | 20-JUN-17:10 | 77122.967 | 233515.839 | 111099.955 | 0 | 262380.913 | 0 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2263.297 | 0 | 0
July | 1282930000000 | 723610.016 | 31-JUL-17:30 | 77122.967 | 233515.839 | 112390.965 | 0 | 278153.182 | 0 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2261.362 | 0 | 0
August | 1258050000000 | 724044.864 | 01-AUG-17:10 | 77122.967 | 233515.839 | 110751.574 | 0 | 280164.661 | 0 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2324.123 | 0 | 0
September | 1153120000000 | 679183.652 | 02-SEP-17:10 | 87035.741 | 233515.839 | 110017.617 | 0 | 226139.076 | 0 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2309.68 | 0 | 0
October | 1060270000000 | 643800.586 | 13-OCT-19:00 | 115409.096 | 215842.575 | 108816.207 | 0 | 177593.464 | 3589.95 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2383.594 | 0 | 0
November | 900763000000 | 616809.04 | 09-NOV-20:00 | 115409.096 | 215842.575 | 108428.754 | 0 | 150462.632 | 3589.95 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2910.333 | 0 | 0
December | 851317000000 | 531643.742 | 09-DEC-18:10 | 87035.741 | 233515.839 | 110355.574 | 0 | 74714.987 | 3589.95 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2265.951 | 0 | 0
Annual Sum or Average | 12467000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 809437000000 | 531643.742 |  | 77122.967 | 215842.575 | 108428.754 | 0 | 74714.987 | 0 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2259.199 | 0 | 0
Maximum of Months | 1282930000000 | 724044.864 |  | 115409.096 | 233515.839 | 114141.37 | 0 | 280164.661 | 3589.95 | 20165.7 | 0 | 0 | 0 | 0 | 0 | 2910.333 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 128075.38 | 23806.12 | 0 | 151881.49
Cost per Total Building Area ($/m2) | 11.29 | 2.1 | 0 | 13.39
Cost per Net Conditioned Building Area ($/m2) | 11.29 | 2.1 | 0 | 13.39
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 14229.08 | 1254.18 | 1254.18
Net Site Energy | 14229.08 | 1254.18 | 1254.18
Total Source Energy | 22153.1 | 1952.63 | 1952.63
Net Source Energy | 22153.1 | 1952.63 | 1952.63
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1921.68 | 0 | 0 | 0 | 0
Cooling | 1469.71 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2564.37 | 0 | 0 | 0 | 0 | 0
Pumps | 360.04 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1240.22 | 0 | 0 | 0 | 7180.08
Refrigeration | 76.29 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10176.84 | 4052.24 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10176.84 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10176.84 | 100
Total On-Site and Utility Electric Sources | 10176.84 | 100
Total Electricity End Uses | 10176.84 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.39 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.39 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.39 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1421313.5 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3002371.17 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.49 | 2821.67 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.27 | 2404.01 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 11.89 | 22547.41 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 6.27 | 11897.35 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.19 | 2263.09 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.96 | 1821.32 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.48 | 906.98 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.41 | 785.61 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.55 | 4829.08 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 66.91 | 126884.05 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.48 | 906.99 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16682.63 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13024.37 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.49 | 0.06684 | 0.000475 | 0.000688
ROOM_2_FLR_3 FAN COIL | 1.27 | 0.06684 | 0.000477 | 0.000591
ROOM_3_MULT19_FLR_3 FAN COIL | 11.89 | 0.74936 | 0.003271 | 0.005611
ROOM_4_MULT19_FLR_3 FAN COIL | 6.27 | 0.74936 | 0.003327 | 0.003155
ROOM_5_FLR_3 FAN COIL | 1.19 | 0.06684 | 0.00048 | 0.000551
ROOM_6_FLR_3 FAN COIL | 0.96049 | 0.06684 | 0.000483 | 0.000446
ROOM_1_FLR_6 FAN COIL | 0.47831 | 0.01671 | 0.000163 | 0.000218
ROOM_2_FLR_6 FAN COIL | 0.4143 | 0.01671 | 0.000164 | 0.00019
ROOM_3_MULT9_FLR_6 FAN COIL | 2.55 | 0.08874 | 0.000878 | 0.001169
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 67133.8109 | 85.8806 | 159.5316 | 0 | 0.0007 | 2106620.3591 | 25906.4152
February | 55725.2559 | 74.2454 | 151.3143 | 0 | 0.0006 | 1998652.1423 | 21820.8614
March | 61818.2261 | 82.9558 | 171.6418 | 0 | 0.0007 | 2267245.2811 | 24270.1982
April | 55871.149 | 78.0849 | 174.9846 | 0 | 0.0007 | 2311887.3873 | 22268.3973
May | 56113.5632 | 81.5749 | 195.8637 | 0 | 0.0008 | 2588178.4695 | 22702.5125
June | 54608.973 | 80.7117 | 199.0659 | 0 | 0.0008 | 2630656.9775 | 22235.5911
July | 57364.9368 | 85.7316 | 215.1559 | 0 | 0.0009 | 2843399.256 | 23459.1385
August | 57407.1888 | 85.9008 | 215.9919 | 0 | 0.0009 | 2854459.6689 | 23487.7822
September | 54268.0035 | 80.1207 | 197.2673 | 0 | 0.0008 | 2606878.735 | 22087.4356
October | 54795.1493 | 78.6288 | 184.6886 | 0 | 0.0007 | 2440380.0391 | 22058.8454
November | 58739.7271 | 78.6813 | 162.179 | 0 | 0.0007 | 2142227.0218 | 23046.2099
December | 66374.4802 | 85.0097 | 158.3685 | 0 | 0.0007 | 2091279.5585 | 25624.1525
Annual Sum or Average | 700220.4639 | 977.5263 | 2186.053 | 0 | 0.0089 | 28881900 | 278967.5397
Minimum of Months | 54268.0035 | 74.2454 | 151.3143 | 0 | 0.0006 | 1998652.1423 | 21820.8614
Maximum of Months | 67133.8109 | 85.9008 | 215.9919 | 0 | 0.0009 | 2854459.6689 | 25906.4152
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 742290000000 | 475338.818 | 27-JAN-20:00 | 115409.096 | 215842.575 | 90300.809 | 0 | 34594.188 | 3589.95 | 13202.135 | 0 | 0 | 0 | 0 | 0 | 2400.065 | 0 | 0
February | 704247000000 | 536851.269 | 21-FEB-20:10 | 115409.096 | 215842.575 | 92100.753 | 0 | 94335.433 | 3589.95 | 13195.594 | 0 | 0 | 0 | 0 | 0 | 2377.869 | 0 | 0
March | 798888000000 | 559725.223 | 28-MAR-19:10 | 115409.096 | 215842.575 | 93588.1 | 0 | 115682.1 | 3589.95 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2418.155 | 0 | 0
April | 814619000000 | 560657.349 | 18-APR-19:10 | 115409.096 | 215842.575 | 94528.613 | 0 | 115682.1 | 3589.95 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2409.767 | 0 | 0
May | 911973000000 | 569557.844 | 05-MAY-17:00 | 77122.967 | 233515.839 | 89291.434 | 0 | 154112.928 | 0 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2319.428 | 0 | 0
June | 926940000000 | 602342.453 | 17-JUN-17:19 | 87035.741 | 233515.839 | 90739.012 | 0 | 175533.001 | 0 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2323.612 | 0 | 0
July | 1001900000000 | 624424.233 | 31-JUL-17:10 | 77122.967 | 233515.839 | 90774.047 | 0 | 207491.914 | 0 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2324.218 | 0 | 0
August | 1005800000000 | 620712.187 | 05-AUG-17:10 | 87035.741 | 233515.839 | 91081.979 | 0 | 193559.902 | 0 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2323.479 | 0 | 0
September | 918562000000 | 718338.219 | 02-SEP-17:10 | 87035.741 | 233515.839 | 94250.097 | 0 | 288032.668 | 0 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2308.626 | 0 | 0
October | 859894000000 | 560645.671 | 02-OCT-19:10 | 115409.096 | 215842.575 | 93999.198 | 0 | 115682.1 | 3589.95 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2927.504 | 0 | 0
November | 754837000000 | 550994.54 | 04-NOV-18:00 | 87035.741 | 233515.839 | 95647.791 | 0 | 115682.1 | 3589.95 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2327.871 | 0 | 0
December | 736885000000 | 501360.894 | 23-DEC-18:00 | 87035.741 | 233515.839 | 94401.566 | 0 | 67317.075 | 3589.95 | 13203.558 | 0 | 0 | 0 | 0 | 0 | 2297.165 | 0 | 0
Annual Sum or Average | 10176800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 704247000000 | 475338.818 |  | 77122.967 | 215842.575 | 89291.434 | 0 | 34594.188 | 0 | 13195.248 | 0 | 0 | 0 | 0 | 0 | 2297.165 | 0 | 0
Maximum of Months | 1005800000000 | 718338.219 |  | 115409.096 | 233515.839 | 95647.791 | 0 | 288032.668 | 3589.95 | 13203.558 | 0 | 0 | 0 | 0 | 0 | 2927.504 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 189569.18 | 33853.2 | 0 | 223422.38
Cost per Total Building Area ($/m2) | 16.71 | 2.98 | 0 | 19.69
Cost per Net Conditioned Building Area ($/m2) | 16.71 | 2.98 | 0 | 19.69
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16993.58 | 1497.85 | 1497.85
Net Site Energy | 16993.58 | 1497.85 | 1497.85
Total Source Energy | 45238.16 | 3987.4 | 3987.4
Net Source Energy | 45238.16 | 3987.4 | 3987.4
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3946.63 | 0 | 0 | 0 | 0
Cooling | 2145.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.4 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2583.58 | 0 | 0 | 0 | 0 | 0
Pumps | 361.32 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1284.09 | 0 | 0 | 0 | 7180.08
Refrigeration | 75.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10872.53 | 6121.05 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10872.53 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10872.53 | 100
Total On-Site and Utility Electric Sources | 10872.53 | 100
Total Electricity End Uses | 10872.53 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.39 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.39 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.39 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1757118.33 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3386959.48 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.5 | 2840.31 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.44 | 2731.68 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 10.5 | 19907.6 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.07 | 15306.94 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.24 | 2352.13 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.12 | 2127.74 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.49 | 929.5 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.47 | 898.7 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.29 | 4351.24 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 68.35 | 129608.29 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.49 | 929.51 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18819.58 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16101.56 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.5 | 0.06684 | 0.00079 | 0.00075
ROOM_2_FLR_3 FAN COIL | 1.44 | 0.06684 | 0.000789 | 0.000724
ROOM_3_MULT19_FLR_3 FAN COIL | 10.5 | 0.74936 | 0.0054 | 0.005629
ROOM_4_MULT19_FLR_3 FAN COIL | 8.07 | 0.74936 | 0.005403 | 0.004476
ROOM_5_FLR_3 FAN COIL | 1.24 | 0.06684 | 0.000778 | 0.000629
ROOM_6_FLR_3 FAN COIL | 1.12 | 0.06684 | 0.000777 | 0.000573
ROOM_1_FLR_6 FAN COIL | 0.49018 | 0.01671 | 0.000267 | 0.00024
ROOM_2_FLR_6 FAN COIL | 0.47394 | 0.01671 | 0.000267 | 0.000232
ROOM_3_MULT9_FLR_6 FAN COIL | 2.29 | 0.08874 | 0.001436 | 0.001166
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 309832.5317 | 506.7726 | 1353.3161 | 0 | 0.0042 | 311474.2428 | 128797.1968
February | 274397.0604 | 455.9985 | 1241.6124 | 0 | 0.0038 | 285776.6307 | 114753.6973
March | 298852.9413 | 508.8455 | 1425.4424 | 0 | 0.0044 | 328107.1475 | 126148.2207
April | 301359.5177 | 530.7946 | 1543.392 | 0 | 0.0047 | 355283.0424 | 128896.7771
May | 351647.4747 | 629.0315 | 1858.8655 | 0 | 0.0056 | 427917.2491 | 151329.7089
June | 384478.3832 | 691.6653 | 2055.8272 | 0 | 0.0062 | 473263.7587 | 165831.7277
July | 422981.6835 | 762.0228 | 2268.2481 | 0 | 0.0069 | 522165.7793 | 182543.1555
August | 412613.7611 | 743.2415 | 2212.0325 | 0 | 0.0067 | 509224.4517 | 178058.8999
September | 361669.3375 | 650.0718 | 1930.5048 | 0 | 0.0058 | 444413.0466 | 155940.2108
October | 328303.2762 | 583.8757 | 1715.0983 | 0 | 0.0052 | 394816.9799 | 140958.8322
November | 286672.8804 | 494.4063 | 1405.1092 | 0 | 0.0043 | 323436.2556 | 121609.1929
December | 301239.773 | 497.6849 | 1345.5597 | 0 | 0.0042 | 309697.13 | 125700.0904
Annual Sum or Average | 4034048.6208 | 7054.411 | 20355.008 | 0 | 0.062 | 4685575.7143 | 1720567.7101
Minimum of Months | 274397.0604 | 455.9985 | 1241.6124 | 0 | 0.0038 | 285776.6307 | 114753.6973
Maximum of Months | 422981.6835 | 762.0228 | 2268.2481 | 0 | 0.0069 | 522165.7793 | 182543.1555
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 722753000000 | 461955.68 | 17-JAN-20:10 | 115409.096 | 215842.575 | 91368.028 | 0 | 17074.503 | 3589.95 | 16278.635 | 0 | 0 | 0 | 0 | 0 | 2392.894 | 0 | 0
February | 663123000000 | 471339.903 | 27-FEB-20:00 | 115409.096 | 215842.575 | 91867.618 | 0 | 25436.09 | 3589.95 | 16277.585 | 0 | 0 | 0 | 0 | 0 | 2916.99 | 0 | 0
March | 761348000000 | 588073.461 | 31-MAR-19:49 | 115409.096 | 215842.575 | 91550.79 | 0 | 143013.585 | 3589.95 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2395.031 | 0 | 0
April | 824408000000 | 586448.205 | 28-APR-19:10 | 115409.096 | 215842.575 | 96389.378 | 0 | 136549.689 | 3589.95 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2395.084 | 0 | 0
May | 992950000000 | 670091.038 | 30-MAY-17:10 | 77122.967 | 233515.839 | 91150.846 | 0 | 249705.401 | 0 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2323.55 | 0 | 0
June | 1098170000000 | 703944.814 | 19-JUN-17:19 | 77122.967 | 233515.839 | 91810.932 | 0 | 282897.53 | 0 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2325.111 | 0 | 0
July | 1211650000000 | 783316.998 | 13-JUL-17:10 | 77122.967 | 233515.839 | 95055.615 | 0 | 359020.095 | 0 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2330.048 | 0 | 0
August | 1181620000000 | 812742.258 | 04-AUG-17:19 | 77122.967 | 233515.839 | 93535.244 | 0 | 389968.405 | 0 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2327.368 | 0 | 0
September | 1031230000000 | 649106.341 | 06-SEP-17:10 | 77122.967 | 233515.839 | 90820.376 | 0 | 229052.526 | 0 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2322.199 | 0 | 0
October | 916143000000 | 589388.621 | 30-OCT-20:00 | 115409.096 | 215842.575 | 87833.652 | 0 | 147482.71 | 3589.95 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2958.204 | 0 | 0
November | 750509000000 | 588710.155 | 02-NOV-20:49 | 115409.096 | 215842.575 | 91623.576 | 0 | 143013.585 | 3589.95 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2958.939 | 0 | 0
December | 718629000000 | 483934.541 | 12-DEC-20:10 | 115409.096 | 215842.575 | 91620.039 | 0 | 38786.485 | 3589.95 | 16277.887 | 0 | 0 | 0 | 0 | 0 | 2408.509 | 0 | 0
Annual Sum or Average | 10872500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 663123000000 | 461955.68 |  | 77122.967 | 215842.575 | 87833.652 | 0 | 17074.503 | 0 | 16272.434 | 0 | 0 | 0 | 0 | 0 | 2322.199 | 0 | 0
Maximum of Months | 1211650000000 | 812742.258 |  | 115409.096 | 233515.839 | 96389.378 | 0 | 389968.405 | 3589.95 | 16278.635 | 0 | 0 | 0 | 0 | 0 | 2958.939 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 290448.15 | 52336.09 | 0 | 342784.24
Cost per Total Building Area ($/m2) | 25.6 | 4.61 | 0 | 30.21
Cost per Net Conditioned Building Area ($/m2) | 25.6 | 4.61 | 0 | 30.21
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 15626.21 | 1377.33 | 1377.33
Net Site Energy | 15626.21 | 1377.33 | 1377.33
Total Source Energy | 41886.34 | 3691.96 | 3691.96
Net Source Energy | 41886.34 | 3691.96 | 3691.96
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2306.23 | 0 | 0 | 0 | 0
Cooling | 1994.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3036.17 | 0 | 0 | 0 | 0 | 0
Pumps | 338.55 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1278.46 | 0 | 0 | 0 | 7180.08
Refrigeration | 75.74 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11151.18 | 4475.03 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 11151.18 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 11151.18 | 100
Total On-Site and Utility Electric Sources | 11151.18 | 100
Total Electricity End Uses | 11151.18 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.39 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.39 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.39 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1341299.81 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3218282.03 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.81 | 3422.88 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.75 | 3321.92 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 12.09 | 22933.47 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 9.49 | 17989.23 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.37 | 2601.23 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.23 | 2334.96 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.59 | 1126.02 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.58 | 1098.6 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.64 | 5009.04 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 79.85 | 151419.07 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.59 | 1126.03 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17882.33 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12291.16 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.81 | 0.06684 | 0.000735 | 0.000682
ROOM_2_FLR_3 FAN COIL | 1.75 | 0.06684 | 0.00073 | 0.000662
ROOM_3_MULT19_FLR_3 FAN COIL | 12.09 | 0.74936 | 0.004939 | 0.004713
ROOM_4_MULT19_FLR_3 FAN COIL | 9.49 | 0.74936 | 0.004849 | 0.003632
ROOM_5_FLR_3 FAN COIL | 1.37 | 0.06684 | 0.000735 | 0.000517
ROOM_6_FLR_3 FAN COIL | 1.23 | 0.06684 | 0.00073 | 0.000461
ROOM_1_FLR_6 FAN COIL | 0.59382 | 0.01671 | 0.000252 | 0.000221
ROOM_2_FLR_6 FAN COIL | 0.57935 | 0.01671 | 0.000251 | 0.000216
ROOM_3_MULT9_FLR_6 FAN COIL | 2.64 | 0.08874 | 0.001341 | 0.000992
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 253542.0531 | 413.0059 | 990.8337 | 0 | 0.0039 | 1030113.1628 | 105688.2933
February | 226874.3483 | 373.1715 | 906.1336 | 0 | 0.0036 | 942082.0662 | 94925.6258
March | 254072.0011 | 424.0553 | 1048.0373 | 0 | 0.0041 | 1089659.965 | 106908.3528
April | 253311.0638 | 430.9736 | 1089.2181 | 0 | 0.0043 | 1132533.8377 | 107391.3597
May | 272274.8063 | 467.4412 | 1193.5118 | 0 | 0.0047 | 1241003.3411 | 115843.359
June | 278104.7928 | 479.9794 | 1232.7568 | 0 | 0.0048 | 1281826.7223 | 118571.9027
July | 312164.1753 | 540.0727 | 1390.8249 | 0 | 0.0054 | 1446195.2394 | 133221.8972
August | 300962.0032 | 520.5966 | 1340.3987 | 0 | 0.0052 | 1393760.9609 | 128431.8156
September | 274314.4001 | 473.194 | 1214.6372 | 0 | 0.0047 | 1262984.2256 | 116931.9576
October | 265004.714 | 452.9557 | 1150.7958 | 0 | 0.0045 | 1196574.3515 | 112553.6005
November | 241006.2809 | 402.8484 | 997.3905 | 0 | 0.0039 | 1037006.0049 | 101469.4404
December | 249889.7731 | 406.4059 | 973.0395 | 0 | 0.0039 | 1011608.6392 | 104102.0351
Annual Sum or Average | 3181520.4119 | 5384.7002 | 13527.5779 | 0 | 0.0532 | 14065300 | 1346039.6397
Minimum of Months | 226874.3483 | 373.1715 | 906.1336 | 0 | 0.0036 | 942082.0662 | 94925.6258
Maximum of Months | 312164.1753 | 540.0727 | 1390.8249 | 0 | 0.0054 | 1446195.2394 | 133221.8972
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 816686000000 | 551094.027 | 27-JAN-18:00 | 77122.967 | 233515.839 | 112963.994 | 0 | 109169.708 | 3589.95 | 12462.533 | 0 | 0 | 0 | 0 | 0 | 2269.035 | 0 | 0
February | 746894000000 | 557995.815 | 11-FEB-18:00 | 87035.741 | 233515.839 | 113440.027 | 0 | 105680.369 | 3589.95 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2271.856 | 0 | 0
March | 863896000000 | 591303.354 | 26-MAR-17:10 | 80331.504 | 230772.41 | 105502.897 | 0 | 160011.001 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2223.509 | 0 | 0
April | 897886000000 | 579686.804 | 26-APR-19:10 | 115409.096 | 215842.575 | 104100.232 | 0 | 125384.876 | 3589.95 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2898.042 | 0 | 0
May | 983882000000 | 631941.958 | 23-MAY-17:19 | 77122.967 | 233515.839 | 109024.725 | 0 | 197538.064 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2278.329 | 0 | 0
June | 1016250000000 | 665541.783 | 27-JUN-17:10 | 77122.967 | 233515.839 | 110470.121 | 0 | 229696.914 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2273.908 | 0 | 0
July | 1146560000000 | 692054.036 | 16-JUL-17:10 | 80331.504 | 230772.41 | 110121.032 | 0 | 256122.366 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2244.691 | 0 | 0
August | 1104990000000 | 692496.755 | 29-AUG-17:10 | 77122.967 | 233515.839 | 111609.628 | 0 | 255508.212 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2278.075 | 0 | 0
September | 1001310000000 | 651792.598 | 02-SEP-17:10 | 87035.741 | 233515.839 | 111194.808 | 0 | 205308.166 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2276.01 | 0 | 0
October | 948659000000 | 602913.91 | 05-OCT-17:10 | 77122.967 | 233515.839 | 107335.926 | 0 | 170214.233 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2262.912 | 0 | 0
November | 822151000000 | 561676.654 | 04-NOV-18:00 | 87035.741 | 233515.839 | 113644.318 | 0 | 109169.708 | 3589.95 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2259.066 | 0 | 0
December | 802016000000 | 500417.435 | 21-DEC-18:10 | 77122.967 | 233515.839 | 110381.522 | 0 | 61080.223 | 3589.95 | 12462.776 | 0 | 0 | 0 | 0 | 0 | 2264.158 | 0 | 0
Annual Sum or Average | 11151200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 746894000000 | 500417.435 |  | 77122.967 | 215842.575 | 104100.232 | 0 | 61080.223 | 0 | 12462.033 | 0 | 0 | 0 | 0 | 0 | 2223.509 | 0 | 0
Maximum of Months | 1146560000000 | 692496.755 |  | 115409.096 | 233515.839 | 113644.318 | 0 | 256122.366 | 3589.95 | 12462.776 | 0 | 0 | 0 | 0 | 0 | 2898.042 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 114578.14 | 31572.33 | 0 | 146150.46
Cost per Total Building Area ($/m2) | 10.1 | 2.78 | 0 | 12.88
Cost per Net Conditioned Building Area ($/m2) | 10.1 | 2.78 | 0 | 12.88
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 18578.71 | 1637.57 | 1637.57
Net Site Energy | 18578.71 | 1637.57 | 1637.57
Total Source Energy | 45512.82 | 4011.61 | 4011.61
Net Source Energy | 45512.82 | 4011.61 | 4011.61
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 5554.36 | 0 | 0 | 0 | 0
Cooling | 2018.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2619.01 | 0 | 0 | 0 | 0 | 0
Pumps | 336.94 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1377.14 | 0 | 0 | 0 | 7180.08
Refrigeration | 75.68 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10756.87 | 7821.84 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10756.87 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10756.87 | 100
Total On-Site and Utility Electric Sources | 10756.87 | 100
Total Electricity End Uses | 10756.87 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.39 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.39 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.39 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1709055.77 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3498707.21 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.51 | 2863.65 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.43 | 2708.05 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 10.99 | 20848.4 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.01 | 15197.2 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.25 | 2368.19 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.11 | 2095.5 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.49 | 932.41 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.47 | 886.2 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.4 | 4545.08 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 69.26 | 131334.9 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.49 | 932.42 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19440.51 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15661.13 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.51 | 0.06684 | 0.00088 | 0.000739
ROOM_2_FLR_3 FAN COIL | 1.43 | 0.06684 | 0.000887 | 0.000703
ROOM_3_MULT19_FLR_3 FAN COIL | 10.99 | 0.74936 | 0.005926 | 0.005696
ROOM_4_MULT19_FLR_3 FAN COIL | 8.01 | 0.74936 | 0.006059 | 0.004294
ROOM_5_FLR_3 FAN COIL | 1.25 | 0.06684 | 0.000866 | 0.00062
ROOM_6_FLR_3 FAN COIL | 1.11 | 0.06684 | 0.000873 | 0.000555
ROOM_1_FLR_6 FAN COIL | 0.49172 | 0.01671 | 0.000298 | 0.000236
ROOM_2_FLR_6 FAN COIL | 0.46735 | 0.01671 | 0.0003 | 0.000225
ROOM_3_MULT9_FLR_6 FAN COIL | 2.4 | 0.08874 | 0.001587 | 0.001183
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 245911.272 | 367.1176 | 469.7038 | 0 | 0.0036 | 308456.5917 | 98865.4818
February | 210518.6507 | 323.2769 | 431.396 | 0 | 0.0033 | 283351.6539 | 85496.2761
March | 213581.108 | 349.2818 | 507.0349 | 0 | 0.0038 | 333147.7872 | 88776.2093
April | 204301.5447 | 353.9032 | 549.4671 | 0 | 0.004 | 361119.9031 | 86811.4172
May | 235439.6709 | 418.2128 | 666.9802 | 0 | 0.0049 | 438394.1784 | 101033.8316
June | 249700.6812 | 446.8882 | 718.2672 | 0 | 0.0053 | 472117.2221 | 107473.2235
July | 271016.567 | 485.9638 | 782.6001 | 0 | 0.0057 | 514406.8123 | 116736.3361
August | 266488.9386 | 477.9077 | 769.7293 | 0 | 0.0056 | 505947.0564 | 114792.1005
September | 226617.2505 | 404.3871 | 647.9966 | 0 | 0.0047 | 425923.8315 | 97424.2975
October | 208261.7535 | 362.1832 | 564.7413 | 0 | 0.0042 | 371164.1865 | 88629.8989
November | 200926.6044 | 328.642 | 477.172 | 0 | 0.0036 | 313526.6362 | 83521.5343
December | 232660.2417 | 354.9577 | 469.2134 | 0 | 0.0036 | 308178.569 | 94266.6754
Annual Sum or Average | 2765424.2833 | 4672.722 | 7054.3018 | 0 | 0.0523 | 4635734.4284 | 1163827.2821
Minimum of Months | 200926.6044 | 323.2769 | 431.396 | 0 | 0.0033 | 283351.6539 | 83521.5343
Maximum of Months | 271016.567 | 485.9638 | 782.6001 | 0 | 0.0057 | 514406.8123 | 116736.3361
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 715750000000 | 429550.245 | 30-JAN-20:10 | 115409.096 | 215842.575 | 91519.313 | 0 | 0 | 3589.95 | 287.264 | 0 | 0 | 0 | 0 | 0 | 2902.046 | 0 | 0
February | 657496000000 | 455334.922 | 27-FEB-20:00 | 115409.096 | 215842.575 | 91774.857 | 0 | 9921.281 | 3589.95 | 15895.107 | 0 | 0 | 0 | 0 | 0 | 2902.056 | 0 | 0
March | 773044000000 | 570302.87 | 25-MAR-17:30 | 87035.741 | 233515.839 | 96120.007 | 0 | 135505.95 | 0 | 15832.282 | 0 | 0 | 0 | 0 | 0 | 2293.051 | 0 | 0
April | 837952000000 | 592367.431 | 01-APR-17:10 | 87035.741 | 233515.839 | 90875.566 | 0 | 162793.288 | 0 | 15832.007 | 0 | 0 | 0 | 0 | 0 | 2314.99 | 0 | 0
May | 1017260000000 | 773873.728 | 27-MAY-17:10 | 87035.741 | 233515.839 | 96172.619 | 0 | 338988.525 | 0 | 15832.007 | 0 | 0 | 0 | 0 | 0 | 2328.996 | 0 | 0
June | 1095510000000 | 774752.01 | 29-JUN-17:19 | 77122.967 | 233515.839 | 96050.401 | 0 | 349901.701 | 0 | 15832.007 | 0 | 0 | 0 | 0 | 0 | 2329.094 | 0 | 0
July | 1193640000000 | 819483.461 | 15-JUL-17:10 | 87035.741 | 233515.839 | 95952.705 | 0 | 384817.927 | 0 | 15832.007 | 0 | 0 | 0 | 0 | 0 | 2329.241 | 0 | 0
August | 1174010000000 | 786122.446 | 25-AUG-17:19 | 77122.967 | 233515.839 | 94495.233 | 0 | 362828.845 | 0 | 15832.007 | 0 | 0 | 0 | 0 | 0 | 2327.554 | 0 | 0
September | 988324000000 | 621874.307 | 14-SEP-17:10 | 77122.967 | 233515.839 | 92612.117 | 0 | 200468.747 | 0 | 15832.007 | 0 | 0 | 0 | 0 | 0 | 2322.629 | 0 | 0
October | 861259000000 | 586354.41 | 06-OCT-19:40 | 115409.096 | 215842.575 | 94160.016 | 0 | 139101.726 | 3589.95 | 15832.007 | 0 | 0 | 0 | 0 | 0 | 2419.04 | 0 | 0
November | 727515000000 | 531915.346 | 02-NOV-20:10 | 115409.096 | 215842.575 | 94400.004 | 0 | 83908.96 | 3589.95 | 15832.179 | 0 | 0 | 0 | 0 | 0 | 2932.581 | 0 | 0
December | 715105000000 | 428328.646 | 08-DEC-20:00 | 115409.096 | 215842.575 | 90818.63 | 0 | 0 | 3589.95 | 292.235 | 0 | 0 | 0 | 0 | 0 | 2376.16 | 0 | 0
Annual Sum or Average | 10756900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 657496000000 | 428328.646 |  | 77122.967 | 215842.575 | 90818.63 | 0 | 0 | 0 | 287.264 | 0 | 0 | 0 | 0 | 0 | 2293.051 | 0 | 0
Maximum of Months | 1193640000000 | 819483.461 |  | 115409.096 | 233515.839 | 96172.619 | 0 | 384817.927 | 3589.95 | 15895.107 | 0 | 0 | 0 | 0 | 0 | 2932.581 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 164315.83 | 61971.85 | 0 | 226287.69
Cost per Total Building Area ($/m2) | 14.48 | 5.46 | 0 | 19.95
Cost per Net Conditioned Building Area ($/m2) | 14.48 | 5.46 | 0 | 19.95
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16796.95 | 1480.52 | 1480.52
Net Site Energy | 16796.95 | 1480.52 | 1480.52
Total Source Energy | 43462.7 | 3830.9 | 3830.9
Net Source Energy | 43462.7 | 3830.9 | 3830.9
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3975.49 | 0 | 0 | 0 | 0
Cooling | 1532.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2920.3 | 0 | 0 | 0 | 0 | 0
Pumps | 302.33 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1394.02 | 0 | 0 | 0 | 7180.08
Refrigeration | 75.52 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10537.1 | 6259.85 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10537.1 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10537.1 | 100
Total On-Site and Utility Electric Sources | 10537.1 | 100
Total Electricity End Uses | 10537.1 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.39 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.39 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.39 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.39 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.39 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.39 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.39 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.39 | 0.495 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1350160.88 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3406491.88 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.67 | 3169.95 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.55 | 2939.33 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 12.55 | 23805.08 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 8.53 | 16170.92 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.37 | 2602.11 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.18 | 2228.32 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.55 | 1036.71 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.51 | 966.55 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.73 | 5183.26 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 76.62 | 145294.34 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.55 | 1036.71 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18928.12 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12372.36 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.67 | 0.06684 | 0.000867 | 0.000665
ROOM_2_FLR_3 FAN COIL | 1.55 | 0.06684 | 0.000873 | 0.000617
ROOM_3_MULT19_FLR_3 FAN COIL | 12.55 | 0.74936 | 0.005785 | 0.00512
ROOM_4_MULT19_FLR_3 FAN COIL | 8.53 | 0.74936 | 0.005893 | 0.003386
ROOM_5_FLR_3 FAN COIL | 1.37 | 0.06684 | 0.000856 | 0.000543
ROOM_6_FLR_3 FAN COIL | 1.18 | 0.06684 | 0.000862 | 0.000463
ROOM_1_FLR_6 FAN COIL | 0.54672 | 0.01671 | 0.000296 | 0.000215
ROOM_2_FLR_6 FAN COIL | 0.50972 | 0.01671 | 0.000298 | 0.000201
ROOM_3_MULT9_FLR_6 FAN COIL | 2.73 | 0.08874 | 0.001572 | 0.00108
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 239884.7247 | 371.2467 | 556.2318 | 0 | 0.004 | 13188000 | 97862.5516
February | 211973.8917 | 334.9288 | 516.3844 | 0 | 0.0037 | 12244500 | 87140.904
March | 228970.4858 | 378.0038 | 616.4474 | 0 | 0.0043 | 14620200 | 95695.9205
April | 216945.5428 | 366.5501 | 614.445 | 0 | 0.0043 | 14574100 | 91482.0098
May | 235356.396 | 405.1203 | 693.5801 | 0 | 0.0048 | 16452300 | 99966.9614
June | 245413.5399 | 426.1047 | 736.501 | 0 | 0.0051 | 17470900 | 104593.7428
July | 265833.1989 | 463.5862 | 805.1139 | 0 | 0.0056 | 19098800 | 113492.4571
August | 259221.8559 | 451.8478 | 784.3352 | 0 | 0.0055 | 18605900 | 110649.6793
September | 236480.4547 | 410.2086 | 708.297 | 0 | 0.0049 | 16801800 | 100749.224
October | 226783.5704 | 387.0322 | 656.2675 | 0 | 0.0046 | 15566700 | 96003.6239
November | 213491.4036 | 351.6632 | 571.9297 | 0 | 0.004 | 13564200 | 89150.576
December | 233591.4194 | 365.8952 | 557.5085 | 0 | 0.004 | 13219100 | 95719.3203
Annual Sum or Average | 2813946.4838 | 4712.1877 | 7817.0416 | 0 | 0.0548 | 185407000 | 1182506.9708
Minimum of Months | 211973.8917 | 334.9288 | 516.3844 | 0 | 0.0037 | 12244500 | 87140.904
Maximum of Months | 265833.1989 | 463.5862 | 805.1139 | 0 | 0.0056 | 19098800 | 113492.4571
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 749505000000 | 468994.178 | 14-JAN-18:40 | 87035.741 | 233515.839 | 105845.283 | 0 | 24182.854 | 3589.95 | 12559.077 | 0 | 0 | 0 | 0 | 0 | 2265.435 | 0 | 0
February | 695887000000 | 532334.136 | 02-FEB-18:10 | 77122.967 | 233515.839 | 107671.752 | 0 | 95601.975 | 3589.95 | 12544.257 | 0 | 0 | 0 | 0 | 0 | 2287.396 | 0 | 0
March | 830900000000 | 568313.268 | 30-MAR-19:19 | 115409.096 | 215842.575 | 108133.457 | 0 | 109890.919 | 3589.95 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2904.038 | 0 | 0
April | 828280000000 | 567073.288 | 14-APR-19:49 | 115409.096 | 215842.575 | 107423.289 | 0 | 109890.919 | 3589.95 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2374.226 | 0 | 0
May | 935021000000 | 594209.151 | 16-MAY-17:10 | 77122.967 | 233515.839 | 103151.233 | 0 | 165597.47 | 0 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2278.409 | 0 | 0
June | 992914000000 | 698491.951 | 24-JUN-17:00 | 87035.741 | 233515.839 | 108498.673 | 0 | 254588.72 | 0 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2309.745 | 0 | 0
July | 1085430000000 | 702215.104 | 21-JUL-17:10 | 77122.967 | 233515.839 | 107659.27 | 0 | 269085.213 | 0 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2288.583 | 0 | 0
August | 1057420000000 | 679916.275 | 09-AUG-17:10 | 77122.967 | 233515.839 | 106078.161 | 0 | 248361.162 | 0 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2294.913 | 0 | 0
September | 954888000000 | 657628.401 | 01-SEP-17:10 | 77122.967 | 233515.839 | 105571.577 | 0 | 226580.679 | 0 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2294.106 | 0 | 0
October | 884691000000 | 574495.536 | 06-OCT-17:10 | 77122.967 | 233515.839 | 101651.306 | 0 | 147384.701 | 0 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2277.49 | 0 | 0
November | 770888000000 | 546540.051 | 21-NOV-20:10 | 115409.096 | 215842.575 | 104704.237 | 0 | 92074.944 | 3589.95 | 12544.457 | 0 | 0 | 0 | 0 | 0 | 2374.793 | 0 | 0
December | 751273000000 | 480595.733 | 20-DEC-20:00 | 115409.096 | 215842.575 | 102430.933 | 0 | 27877.694 | 3589.95 | 12552.498 | 0 | 0 | 0 | 0 | 0 | 2892.987 | 0 | 0
Annual Sum or Average | 10537100000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 695887000000 | 468994.178 |  | 77122.967 | 215842.575 | 101651.306 | 0 | 24182.854 | 0 | 12543.232 | 0 | 0 | 0 | 0 | 0 | 2265.435 | 0 | 0
Maximum of Months | 1085430000000 | 702215.104 |  | 115409.096 | 233515.839 | 108498.673 | 0 | 269085.213 | 3589.95 | 12559.077 | 0 | 0 | 0 | 0 | 0 | 2904.038 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 207531.02 | 52151.25 | 0 | 259682.27
Cost per Total Building Area ($/m2) | 18.29 | 4.6 | 0 | 22.89
Cost per Net Conditioned Building Area ($/m2) | 18.29 | 4.6 | 0 | 22.89
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 19389.41 | 1709.03 | 1709.03
Net Site Energy | 19389.41 | 1709.03 | 1709.03
Total Source Energy | 44828.25 | 3951.27 | 3951.27
Net Source Energy | 44828.25 | 3951.27 | 3951.27
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 6881.06 | 0 | 0 | 0 | 0
Cooling | 1303.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2704.11 | 0 | 0 | 0 | 0 | 0
Pumps | 297.82 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1530.59 | 0 | 0 | 0 | 7180.08
Refrigeration | 75.41 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10087.43 | 9301.99 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10087.43 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10087.43 | 100
Total On-Site and Utility Electric Sources | 10087.43 | 100
Total Electricity End Uses | 10087.43 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 3.24 | 0.49 | 0.49 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 3.24 | 0.49 | 0.49 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 3.24 | 0.49 | 0.49 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.49 | 0.49 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.49 | 0.49 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.49 | 0.49 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 3.24 | 0.49 | 0.49 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 3.24 | 0.49 | 0.49 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 3.24 | 0.49 | 0.49 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.49 | 0.49 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 3.24 | 0.49 | 0.49 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 3.24 | 0.49 | 0.49 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 3.24 | 0.49 | 0.49 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.49 | 0.49 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.49 | 0.49 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.49 | 0.49 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 3.24 | 0.49 | 0.49 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 3.24 | 0.49 | 0.49 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.49 | 0.49 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 3.24 | 0.49 | 0.49 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 3.24 | 0.49 | 0.49 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 3.24 | 0.49 | 0.49 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 3.24 | 0.49 | 0.49 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1580837.31 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3518942.31 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.64 | 3101.52 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.53 | 2902.48 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 11.63 | 22059.49 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 7.86 | 14900.35 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.35 | 2557.8 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.19 | 2260.29 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.52 | 993.11 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.49 | 936.34 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.5 | 4737.18 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 70.71 | 134076.1 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.52 | 993.11 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19552.94 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14486.19 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.64 | 0.06684 | 0.000933 | 0.000754
ROOM_2_FLR_3 FAN COIL | 1.53 | 0.06684 | 0.000941 | 0.000709
ROOM_3_MULT19_FLR_3 FAN COIL | 11.63 | 0.74936 | 0.006258 | 0.005606
ROOM_4_MULT19_FLR_3 FAN COIL | 7.86 | 0.74936 | 0.006407 | 0.003885
ROOM_5_FLR_3 FAN COIL | 1.35 | 0.06684 | 0.000918 | 0.000625
ROOM_6_FLR_3 FAN COIL | 1.19 | 0.06684 | 0.000926 | 0.000555
ROOM_1_FLR_6 FAN COIL | 0.52372 | 0.01671 | 0.000316 | 0.000238
ROOM_2_FLR_6 FAN COIL | 0.49378 | 0.01671 | 0.000318 | 0.000225
ROOM_3_MULT9_FLR_6 FAN COIL | 2.5 | 0.08874 | 0.001679 | 0.001165
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 250778.1138 | 373.0624 | 474.6988 | 0 | 0.0037 | 311729.213 | 100695.8772
February | 219693.416 | 332.1158 | 433.1021 | 0 | 0.0033 | 284443.9685 | 88720.5184
March | 224699.0321 | 355.417 | 494.2028 | 0 | 0.0037 | 324660.499 | 92245.9439
April | 201016.8338 | 337.7581 | 506.5892 | 0 | 0.0038 | 332896.8611 | 84416.3091
May | 214787.6142 | 374.4541 | 585.4396 | 0 | 0.0043 | 384771.4506 | 91495.2387
June | 226288.9187 | 402.1628 | 641.723 | 0 | 0.0047 | 421793.8792 | 97126.5386
July | 251674.6536 | 449.4053 | 720.6381 | 0 | 0.0053 | 473671.7349 | 108225.7515
August | 239731.7999 | 427.1594 | 683.4455 | 0 | 0.005 | 449221.69 | 103002.1138
September | 209579.591 | 369.8328 | 585.7608 | 0 | 0.0043 | 385000.5918 | 89702.8667
October | 205748.7314 | 352.7945 | 541.5862 | 0 | 0.004 | 355925.5857 | 87080.7456
November | 209270.6271 | 335.5306 | 474.979 | 0 | 0.0036 | 312054.3166 | 86343.908
December | 242527.8027 | 365.2612 | 473.6439 | 0 | 0.0036 | 311062.5429 | 97810.5803
Annual Sum or Average | 2695797.1343 | 4474.9541 | 6615.8088 | 0 | 0.0492 | 4347232.3333 | 1126866.3917
Minimum of Months | 201016.8338 | 332.1158 | 433.1021 | 0 | 0.0033 | 284443.9685 | 84416.3091
Maximum of Months | 251674.6536 | 449.4053 | 720.6381 | 0 | 0.0053 | 473671.7349 | 108225.7515
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 723344000000 | 430237.224 | 13-JAN-20:10 | 115409.096 | 215842.575 | 92582.692 | 0 | 0 | 3589.95 | 447.87 | 0 | 0 | 0 | 0 | 0 | 2365.041 | 0 | 0
February | 660031000000 | 466887.309 | 28-FEB-18:10 | 77122.967 | 233515.839 | 98496.896 | 0 | 37237.761 | 3589.95 | 14660.723 | 0 | 0 | 0 | 0 | 0 | 2263.171 | 0 | 0
March | 753350000000 | 474432.941 | 22-MAR-17:10 | 77122.967 | 233515.839 | 99589.502 | 0 | 47270.689 | 0 | 14675.409 | 0 | 0 | 0 | 0 | 0 | 2258.535 | 0 | 0
April | 772462000000 | 569338.021 | 15-APR-17:00 | 87035.741 | 233515.839 | 103172.765 | 0 | 128665.9 | 0 | 14657.077 | 0 | 0 | 0 | 0 | 0 | 2290.699 | 0 | 0
May | 892833000000 | 582318.712 | 30-MAY-19:00 | 115409.096 | 215842.575 | 101764.562 | 0 | 128665.9 | 3589.95 | 14657.063 | 0 | 0 | 0 | 0 | 0 | 2389.566 | 0 | 0
June | 978741000000 | 671423.363 | 14-JUN-17:19 | 77122.967 | 233515.839 | 97109.297 | 0 | 246691.352 | 0 | 14657.063 | 0 | 0 | 0 | 0 | 0 | 2326.845 | 0 | 0
July | 1099120000000 | 730165.797 | 06-JUL-18:10 | 102647.053 | 206602.679 | 99237.935 | 0 | 304057.89 | 0 | 14657.063 | 0 | 0 | 0 | 0 | 0 | 2963.177 | 0 | 0
August | 1042390000000 | 720145.208 | 12-AUG-17:10 | 87035.741 | 233515.839 | 99077.056 | 0 | 283531.5 | 0 | 14657.063 | 0 | 0 | 0 | 0 | 0 | 2328.009 | 0 | 0
September | 893365000000 | 614799.998 | 08-SEP-19:10 | 115409.096 | 215842.575 | 91555.286 | 0 | 171316.094 | 3589.95 | 14657.063 | 0 | 0 | 0 | 0 | 0 | 2429.934 | 0 | 0
October | 825899000000 | 572037.485 | 07-OCT-17:10 | 87035.741 | 233515.839 | 94192.516 | 0 | 140322.813 | 0 | 14657.063 | 0 | 0 | 0 | 0 | 0 | 2313.513 | 0 | 0
November | 724099000000 | 498652.268 | 02-NOV-20:00 | 115409.096 | 215842.575 | 96369.398 | 0 | 49877.361 | 3589.95 | 14658.367 | 0 | 0 | 0 | 0 | 0 | 2905.522 | 0 | 0
December | 721797000000 | 430798.162 | 27-DEC-20:00 | 115409.096 | 215842.575 | 92590.951 | 0 | 0 | 3589.95 | 474.289 | 0 | 0 | 0 | 0 | 0 | 2891.302 | 0 | 0
Annual Sum or Average | 10087400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 660031000000 | 430237.224 |  | 77122.967 | 206602.679 | 91555.286 | 0 | 0 | 0 | 447.87 | 0 | 0 | 0 | 0 | 0 | 2258.535 | 0 | 0
Maximum of Months | 1099120000000 | 730165.797 |  | 115409.096 | 233515.839 | 103172.765 | 0 | 304057.89 | 3589.95 | 14675.409 | 0 | 0 | 0 | 0 | 0 | 2963.177 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 152624.44 | 73546.17 | 0 | 226170.6
Cost per Total Building Area ($/m2) | 13.45 | 6.48 | 0 | 19.94
Cost per Net Conditioned Building Area ($/m2) | 13.45 | 6.48 | 0 | 19.94
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 24609.59 | 2169.15 | 2169.15
Net Site Energy | 24609.59 | 2169.15 | 2169.15
Total Source Energy | 51250.55 | 4517.34 | 4517.34
Net Source Energy | 51250.55 | 4517.34 | 4517.34
Area (m2)
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 12173.52 | 0 | 0 | 0 | 0
Cooling | 995.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 55.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4196.77 | 890.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2808.77 | 0 | 0 | 0 | 0 | 0
Pumps | 244.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1716.34 | 0 | 0 | 0 | 7180.08
Refrigeration | 74.61 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9829.39 | 14780.2 | 0 | 0 | 0 | 7180.08
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 9829.39 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 9829.39 | 100
Total On-Site and Utility Electric Sources | 9829.39 | 100
Total Electricity End Uses | 9829.39 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 1.919 | 2.69 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 1.919 | 2.69 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.25 | 0.564 | 0.63 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.3 | 1.285 | 1.59 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.25 | 0.564 | 0.63 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.25 | 0.564 | 0.63 | 167.42 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 2.62 | 0.49 | 0.49 | No | RETAIL_1_FLR_1_WALL_SOUTH
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 2.62 | 0.49 | 0.49 | No | CAFE_FLR_1_WALL_SOUTH
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 2.62 | 0.49 | 0.49 | No | LOBBY_FLR_1_WALL_1_SOUTH
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 2.62 | 0.49 | 0.49 | No | ROOM_1_FLR_3_WALL_SOUTH
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 2.62 | 0.49 | 0.49 | No | ROOM_1_FLR_3_WALL_WEST
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 2.62 | 0.49 | 0.49 | No | ROOM_2_FLR_3_WALL_NORTH
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 34.33 | 2.62 | 0.49 | 0.49 | No | ROOM_2_FLR_3_WALL_WEST
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 279.51 | 2.62 | 0.49 | 0.49 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 279.6 | 2.62 | 0.49 | 0.49 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 2.62 | 0.49 | 0.49 | No | ROOM_5_FLR_3_WALL_EAST
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 18.39 | 2.62 | 0.49 | 0.49 | No | ROOM_5_FLR_3_WALL_SOUTH
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 18.39 | 2.62 | 0.49 | 0.49 | No | ROOM_6_FLR_3_WALL_NORTH
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 34.33 | 2.62 | 0.49 | 0.49 | No | ROOM_6_FLR_3_WALL_EAST
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 23.29 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_1_NORTH
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 8.59 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_2_NORTH
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 8.58 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_1_SOUTH
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 23.29 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_FLR_3_WALL_2_SOUTH
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 2.62 | 0.49 | 0.49 | No | ROOM_1_FLR_6_WALL_SOUTH
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 2.62 | 0.49 | 0.49 | No | ROOM_1_FLR_6_WALL_WEST
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 2.62 | 0.49 | 0.49 | No | ROOM_2_FLR_6_WALL_NORTH
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 2.62 | 0.49 | 0.49 | No | ROOM_2_FLR_6_WALL_WEST
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 60.74 | 2.62 | 0.49 | 0.49 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 2.62 | 0.49 | 0.49 | No | BANQUET_FLR_6_WALL_NORTH
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 2.62 | 0.49 | 0.49 | No | DINING_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 2.62 | 0.49 | 0.49 | No | KITCHEN_FLR_6_WALL_NORTH
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 2.62 | 0.49 | 0.49 | No | KITCHEN_FLR_6_WALL_EAST
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 2.62 | 0.49 | 0.49 | No | KITCHEN_FLR_6_WALL_1_SOUTH
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_FLR_6_WALL_1_NORTH
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_FLR_6_WALL_2_NORTH
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_FLR_6_WALL_2_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1409958.45 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3869042.87 | 0.8
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.33 | 125 | 0.24 | 89.28 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.65 | 3123.12 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.41 | 2678.5 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 13.6 | 25784.63 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 7.81 | 14808.72 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.42 | 2684.9 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 1.17 | 2209.22 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.51 | 973.66 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 0.44 | 843.12 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.15 | 287.61 | 2.91 | 5518.6 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 2.38 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
FLR_3_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 72.51 | 137497.64 | 1 | Fan Energy
FLR_6_DOAS FAN | Fan:ConstantVolume | 0.17 | 320 | 0.51 | 973.66 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 170.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21498.27 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12920.32 | 0.9
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| Supply Air Maximum Flow Rate [m3/s] | Maximum Outdoor Air Flow Rate [m3/s] | Maximum Hot Water Flow [m3/s] | Maximum Cold Water Flow [m3/s]
ROOM_1_FLR_3 FAN COIL | 1.65 | 0.06684 | 0.001089 | 0.000731
ROOM_2_FLR_3 FAN COIL | 1.41 | 0.06684 | 0.001094 | 0.000627
ROOM_3_MULT19_FLR_3 FAN COIL | 13.6 | 0.74936 | 0.007473 | 0.006113
ROOM_4_MULT19_FLR_3 FAN COIL | 7.81 | 0.74936 | 0.007559 | 0.003388
ROOM_5_FLR_3 FAN COIL | 1.42 | 0.06684 | 0.001089 | 0.000626
ROOM_6_FLR_3 FAN COIL | 1.17 | 0.06684 | 0.001094 | 0.000513
ROOM_1_FLR_6 FAN COIL | 0.51347 | 0.01671 | 0.000376 | 0.000227
ROOM_2_FLR_6 FAN COIL | 0.44462 | 0.01671 | 0.000378 | 0.000196
ROOM_3_MULT9_FLR_6 FAN COIL | 2.91 | 0.08874 | 0.002046 | 0.001286
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 284137.9661 | 307.4574 | 1036.9969 | 0 | 0.0038 | 207987.5615 | 105962.0328
February | 247674.3913 | 269.5488 | 936.2964 | 0 | 0.0034 | 187799.4961 | 92602.0261
March | 236644.8724 | 265.4361 | 1059.6877 | 0 | 0.0038 | 212594.0766 | 89692.5478
April | 200702.1628 | 234.8186 | 1101.634 | 0 | 0.0038 | 221056.1312 | 77562.0495
May | 198872.1371 | 242.3297 | 1293.5227 | 0 | 0.0044 | 259598.9318 | 78340.1646
June | 203624.6464 | 250.5974 | 1376.2501 | 0 | 0.0047 | 276209.8454 | 80593.4174
July | 213484.3029 | 263.2797 | 1454.357 | 0 | 0.0049 | 291887.439 | 84580.1625
August | 201794.916 | 248.0303 | 1357.2861 | 0 | 0.0046 | 272402.802 | 79820.6939
September | 185984.9838 | 224.7793 | 1171.0574 | 0 | 0.004 | 235015.0524 | 72979.3832
October | 206973.0309 | 239.5318 | 1081.1632 | 0 | 0.0038 | 216938.0909 | 79581.6947
November | 243112.9648 | 268.4173 | 999.2376 | 0 | 0.0036 | 200445.9793 | 91486.378
December | 271636.3359 | 296.026 | 1035.2275 | 0 | 0.0038 | 207645.0933 | 101622.4593
Annual Sum or Average | 2694642.7104 | 3110.2525 | 13902.7166 | 0 | 0.0486 | 2789580.4997 | 1034823.0098
Minimum of Months | 185984.9838 | 224.7793 | 936.2964 | 0 | 0.0034 | 187799.4961 | 72979.3832
Maximum of Months | 284137.9661 | 307.4574 | 1454.357 | 0 | 0.0049 | 291887.439 | 105962.0328
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 732867000000 | 435021.998 | 19-JAN-20:10 | 115409.096 | 215842.575 | 96876.955 | 0 | 0 | 3589.95 | 412.724 | 0 | 0 | 0 | 0 | 0 | 2890.698 | 0 | 0
February | 661732000000 | 441091.282 | 28-FEB-18:10 | 77122.967 | 233515.839 | 99035.633 | 0 | 12324.821 | 3589.95 | 13245.377 | 0 | 0 | 0 | 0 | 0 | 2256.695 | 0 | 0
March | 749098000000 | 507878.75 | 31-MAR-17:10 | 77122.967 | 233515.839 | 103875.343 | 0 | 78005.455 | 0 | 13091.339 | 0 | 0 | 0 | 0 | 0 | 2267.806 | 0 | 0
April | 778915000000 | 559921.751 | 25-APR-19:10 | 115409.096 | 215842.575 | 103730.369 | 0 | 109479.225 | 0 | 13091.276 | 0 | 0 | 0 | 0 | 0 | 2369.21 | 0 | 0
May | 914725000000 | 577182.854 | 24-MAY-19:10 | 115409.096 | 215842.575 | 100931.468 | 0 | 129006.151 | 0 | 13091.194 | 0 | 0 | 0 | 0 | 0 | 2902.369 | 0 | 0
June | 973255000000 | 633855.719 | 20-JUN-17:19 | 77122.967 | 233515.839 | 101794.595 | 0 | 206041.198 | 0 | 13091.194 | 0 | 0 | 0 | 0 | 0 | 2289.926 | 0 | 0
July | 1028500000000 | 674759.514 | 29-JUL-17:19 | 87035.741 | 233515.839 | 102392.362 | 0 | 236400.877 | 0 | 13091.194 | 0 | 0 | 0 | 0 | 0 | 2323.501 | 0 | 0
August | 959841000000 | 612134.259 | 15-AUG-17:10 | 77122.967 | 233515.839 | 99642.753 | 0 | 186448.66 | 0 | 13091.194 | 0 | 0 | 0 | 0 | 0 | 2312.845 | 0 | 0
September | 828101000000 | 563961.233 | 01-SEP-19:10 | 115409.096 | 215842.575 | 102447.732 | 0 | 114757.902 | 0 | 13091.216 | 0 | 0 | 0 | 0 | 0 | 2412.713 | 0 | 0
October | 764405000000 | 518251.481 | 01-OCT-17:10 | 80331.504 | 230772.41 | 102569.864 | 0 | 89251.589 | 0 | 13091.624 | 0 | 0 | 0 | 0 | 0 | 2234.491 | 0 | 0
November | 706293000000 | 434406.216 | 13-NOV-20:00 | 115409.096 | 215842.575 | 96293.097 | 0 | 0 | 3589.95 | 376.131 | 0 | 0 | 0 | 0 | 0 | 2895.367 | 0 | 0
December | 731660000000 | 433850.373 | 18-DEC-20:00 | 115409.096 | 215842.575 | 95591.068 | 0 | 0 | 3589.95 | 527.292 | 0 | 0 | 0 | 0 | 0 | 2890.393 | 0 | 0
Annual Sum or Average | 9829390000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 661732000000 | 433850.373 |  | 77122.967 | 215842.575 | 95591.068 | 0 | 0 | 0 | 376.131 | 0 | 0 | 0 | 0 | 0 | 2234.491 | 0 | 0
Maximum of Months | 1028500000000 | 674759.514 |  | 115409.096 | 233515.839 | 103875.343 | 0 | 236400.877 | 3589.95 | 13245.377 | 0 | 0 | 0 | 0 | 0 | 2902.369 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 245877.03 | 61087.9 | 0 | 306964.93
Cost per Total Building Area ($/m2) | 21.67 | 5.38 | 0 | 27.06
Cost per Net Conditioned Building Area ($/m2) | 21.67 | 5.38 | 0 | 27.06

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821 | 0.77821
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773 | 1.773
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.34 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211 | 0.5211
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 1738.4812 | 1754.05 | 1670.9657 | 1678.1591 | 1255.6882 | 2399.6758 | 1280.5808 | 1758.0579 | 2181.9796 | 1421.3135 | 1757.1183 | 1341.2998 | 1709.0558 | 1350.1609 | 1580.8373 | 1409.9585
Heating (kW)
| HEATSYS1 BOILER | 2752.5397 | 3023.8448 | 3013.0458 | 3039.4217 | 2704.7892 | 2995.0415 | 2804.6421 | 3194.6789 | 3008.1836 | 3002.3712 | 3386.9595 | 3218.282 | 3498.7072 | 3406.4919 | 3518.9423 | 3869.0429
HVAC Efficiency
| Air Conditioning (COP) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb
Fan Max Flow Rate (m3/s )
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 1.19 | 1.27 | 1.59 | 1.25 | 1.15 | 1.52 | 1.3 | 1.49 | 1.78 | 1.49 | 1.5 | 1.81 | 1.51 | 1.67 | 1.64 | 1.65
| ROOM_2_FLR_3 FAN COILFAN | 1.24 | 1.29 | 1.59 | 1.26 | 1.05 | 1.51 | 1.06 | 1.45 | 1.77 | 1.27 | 1.44 | 1.75 | 1.43 | 1.55 | 1.53 | 1.41
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 7.29 | 8.54 | 11.02 | 9.11 | 8.99 | 10.7 | 11.05 | 10.13 | 11.32 | 11.89 | 10.5 | 12.09 | 10.99 | 12.55 | 11.63 | 13.6
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 8.04 | 8.29 | 9.95 | 7.96 | 6.17 | 9.4 | 5.66 | 8.04 | 9.82 | 6.27 | 8.07 | 9.49 | 8.01 | 8.53 | 7.86 | 7.81
| ROOM_5_FLR_3 FAN COILFAN | 0.92 | 1 | 1.32 | 1.07 | 0.98 | 1.25 | 1.02 | 1.24 | 1.41 | 1.19 | 1.24 | 1.37 | 1.25 | 1.37 | 1.35 | 1.42
| ROOM_6_FLR_3 FAN COILFAN | 0.92 | 0.96 | 1.24 | 1 | 0.86 | 1.15 | 0.78 | 1.14 | 1.32 | 0.96 | 1.12 | 1.23 | 1.11 | 1.18 | 1.19 | 1.17
| ROOM_1_FLR_6 FAN COILFAN | 0.4 | 0.43 | 0.53 | 0.43 | 0.38 | 0.51 | 0.42 | 0.49 | 0.59 | 0.48 | 0.49 | 0.59 | 0.49 | 0.55 | 0.52 | 0.51
| ROOM_2_FLR_6 FAN COILFAN | 0.42 | 0.44 | 0.53 | 0.43 | 0.36 | 0.51 | 0.35 | 0.48 | 0.59 | 0.41 | 0.47 | 0.58 | 0.47 | 0.51 | 0.49 | 0.44
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.54 | 1.88 | 2.52 | 2.01 | 1.9 | 2.43 | 2.31 | 2.24 | 2.48 | 2.55 | 2.29 | 2.64 | 2.4 | 2.73 | 2.5 | 2.91
| DINING_FLR_6 EXHAUST FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| KITCHEN_FLR_6 EXHAUST FAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FLR_3_DOAS FAN | 61.69 | 64.33 | 74.28 | 65.6 | 60.35 | 73.49 | 62.69 | 67.39 | 79.29 | 66.91 | 68.35 | 79.85 | 69.26 | 76.62 | 70.71 | 72.51
| FLR_6_DOAS FAN | 0.4 | 0.43 | 0.53 | 0.43 | 0.38 | 0.51 | 0.42 | 0.49 | 0.59 | 0.48 | 0.49 | 0.59 | 0.49 | 0.55 | 0.52 | 0.51
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.075866 | 0.10257 | 0.07138 | 0.10448 | 0.044371 | 0.088723 | 0.14444 | 0.06951 | 0.036983 | 0.067059 | 0.09617 | 0.03699 | 0.054992 | 0.070903 | 0.054469 | 0.090052
| Total Cost ($/m2) | 27.08 | 33.35 | 23.42 | 30.36 | 11.95 | 29.13 | 35.47 | 19.5 | 11.29 | 16.71 | 25.6 | 10.1 | 14.48 | 18.29 | 13.45 | 21.67
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011462 | 0.0081603 | 0.0085198 | 0.01034 | 0.0084279 | 0.0080426 | 0.0084765 | 0.0098764 | 0.0070895 | 0.0083542 | 0.0085502 | 0.0070552 | 0.0079229 | 0.0083311 | 0.0079065 | 0.0041331
| Total Cost ($/m2) | 1.74 | 1.9 | 1.59 | 3.01 | 1.56 | 1.73 | 2.2 | 4.08 | 2.1 | 2.98 | 4.61 | 2.78 | 5.46 | 4.6 | 6.48 | 5.38
Total Utility Costs
| Cost Intensity ($/m2) | 28.82 | 35.25 | 25.01 | 33.37 | 13.51 | 30.86 | 37.66 | 23.59 | 13.39 | 19.69 | 30.21 | 12.88 | 19.95 | 22.89 | 19.94 | 27.06
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1682233.3333 | 1299369.4445 | 1201027.7778 | 894563.8889 | 720408.3333 | 1155627.7778 | 419675 | 755213.8889 | 856072.2222 | 408252.7778 | 595883.3333 | 553952.7778 | 560769.4444 | 425686.1111 | 362125 | 276613.8889
| Interior Lighting | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111
| Exterior Lighting | 15691.6667 | 15686.1111 | 15683.3333 | 15680.5556 | 15669.4444 | 15663.8889 | 15672.2222 | 15663.8889 | 15669.4444 | 15638.8889 | 15666.6667 | 15658.3333 | 15655.5556 | 15652.7778 | 15644.4444 | 15547.2222
| Interior Equipment | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445 | 1165769.4445
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 620088.8889 | 656775 | 785650 | 675125 | 626402.7778 | 774030.5556 | 663186.1111 | 707480.5556 | 837930.5556 | 712325 | 717661.1111 | 843380.5556 | 727502.7778 | 811194.4445 | 751141.6667 | 780213.8889
| Pumps | 140425 | 126047.2222 | 129008.3333 | 120336.1111 | 102194.4444 | 188513.8889 | 96425 | 114352.7778 | 162816.6667 | 100011.1111 | 100366.6667 | 94041.6667 | 93594.4444 | 83980.5556 | 82727.7778 | 67808.3333
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21372.2222 | 21288.8889 | 21152.7778 | 21244.4444 | 21355.5556 | 21050 | 21244.4444 | 21138.8889 | 21083.3333 | 21191.6667 | 21091.6667 | 21038.8889 | 21022.2222 | 20977.7778 | 20947.2222 | 20725
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4049291.6667 | 3688644.4445 | 3722000 | 3296427.7778 | 3055508.3334 | 3724366.6667 | 2785683.3334 | 3183330.5556 | 3463052.7778 | 2826900 | 3020147.2222 | 3097550 | 2988019.4445 | 2926972.2222 | 2802063.8889 | 2730386.1111
Gas (MJ)
| Heating | 95340 | 852010 | 424870 | 1361490 | 191960 | 632700 | 895140 | 2624960 | 1314420 | 1921680 | 3946630 | 2306230 | 5554360 | 3975490 | 6881060 | 12173520
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340 | 890340
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 735530 | 897610 | 804490 | 1053730 | 1023380 | 916730 | 1156940 | 1176410 | 1153150 | 1240220 | 1284090 | 1278460 | 1377140 | 1394020 | 1530590 | 1716340
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1721200 | 2639970 | 2119700 | 3305560 | 2105670 | 2439770 | 2942420 | 4691710 | 3357920 | 4052240 | 6121050 | 4475030 | 7821840 | 6259850 | 9301990 | 14780200
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 16298650 | 15919090 | 15518900 | 15172700 | 13105510 | 15847490 | 12970890 | 16151700 | 15824910 | 14229080 | 16993580 | 15626210 | 18578710 | 16796950 | 19389410 | 24609590
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 533.7933 | 412.3059 | 381.1009 | 283.8561 | 228.5944 | 366.6949 | 133.168 | 239.6387 | 271.6422 | 129.5436 | 189.0811 | 175.776 | 177.939 | 135.0754 | 114.9067 | 87.773
| Interior Lighting (elec) | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025
| Exterior Lighting (elec) | 4.9792 | 4.9774 | 4.9765 | 4.9756 | 4.9721 | 4.9703 | 4.973 | 4.9703 | 4.9721 | 4.9624 | 4.9712 | 4.9686 | 4.9677 | 4.9668 | 4.9642 | 4.9333
| Interior Equipment (elec) | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913 | 369.913
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 196.7618 | 208.4028 | 249.2964 | 214.2255 | 198.7653 | 245.6094 | 210.4371 | 224.4923 | 265.8857 | 226.0295 | 227.7227 | 267.615 | 230.8456 | 257.402 | 238.3465 | 247.5715
| Pumps (elec) | 44.5586 | 39.9963 | 40.9359 | 38.1841 | 32.4276 | 59.8178 | 30.5968 | 36.2855 | 51.6637 | 31.7348 | 31.8476 | 29.8406 | 29.6987 | 26.6481 | 26.2505 | 21.5164
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 6.7817 | 6.7552 | 6.712 | 6.7411 | 6.7764 | 6.6794 | 6.7411 | 6.7076 | 6.69 | 6.7244 | 6.6926 | 6.6759 | 6.6706 | 6.6565 | 6.6468 | 6.5763
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1284.89 | 1170.4522 | 1181.0364 | 1045.9971 | 969.5504 | 1181.7873 | 883.9316 | 1010.1099 | 1098.8692 | 897.0101 | 958.3298 | 982.8907 | 948.1353 | 928.7643 | 889.1293 | 866.3851
Gas (MJ/m2)
| Heating (gas) | 8.4035 | 75.0981 | 37.449 | 120.0049 | 16.9198 | 55.7676 | 78.8997 | 231.37 | 115.856 | 169.3813 | 347.8651 | 203.2764 | 489.5741 | 350.4088 | 606.5125 | 1073.0021
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766 | 78.4766
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 64.8313 | 79.1174 | 70.9096 | 92.8782 | 90.2031 | 80.8027 | 101.9754 | 103.6915 | 101.6413 | 109.3158 | 113.1827 | 112.6864 | 121.3843 | 122.8721 | 134.9097 | 151.2822
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 151.7105 | 232.693 | 186.8352 | 291.3597 | 185.5986 | 215.0469 | 259.3517 | 413.5381 | 295.9748 | 357.1738 | 539.5234 | 394.4395 | 689.435 | 551.7576 | 819.8988 | 1302.7609
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1436.6006 | 1403.1453 | 1367.8716 | 1337.3567 | 1155.1498 | 1396.8343 | 1143.2841 | 1423.6481 | 1394.844 | 1254.1839 | 1497.8533 | 1377.3302 | 1637.5703 | 1480.5219 | 1709.0273 | 2169.146
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 650.8612 | 628.6926 | 584.7879 | 575.6078 | 534.196 | 546.5341 | 508.075 | 513.0532 | 562.2106 | 475.3388 | 461.9557 | 551.094 | 429.5502 | 468.9942 | 430.2372 | 435.022
| Feb | 647.8575 | 585.9743 | 588.0749 | 571.0071 | 534.8563 | 607.5156 | 539.7133 | 505.4167 | 617.4933 | 536.8513 | 471.3399 | 557.9958 | 455.3349 | 532.3341 | 466.8873 | 441.0913
| Mar | 678.3312 | 674.23 | 658.2287 | 579.0228 | 536.5464 | 643.5288 | 529.6438 | 582.9593 | 634.715 | 559.7252 | 588.0735 | 591.3034 | 570.3029 | 568.3133 | 474.4329 | 507.8788
| Apr | 719.6382 | 714.9528 | 689.0077 | 630.3891 | 572.7174 | 670.3855 | 542.0611 | 588.5323 | 645.887 | 560.6573 | 586.4482 | 579.6868 | 592.3674 | 567.0733 | 569.338 | 559.9218
| May | 749.8567 | 782.2367 | 759.0243 | 708.5419 | 566.4029 | 712.2726 | 542.5044 | 673.8687 | 673.0355 | 569.5578 | 670.091 | 631.942 | 773.8737 | 594.2092 | 582.3187 | 577.1829
| Jun | 832.414 | 784.8116 | 833.7255 | 748.9022 | 564.5055 | 781.2238 | 542.8277 | 843.2702 | 706.5487 | 602.3425 | 703.9448 | 665.5418 | 774.752 | 698.492 | 671.4234 | 633.8557
| Jul | 787.6711 | 836.273 | 841.333 | 817.3364 | 584.347 | 769.8232 | 635.6841 | 850.0874 | 723.61 | 624.4242 | 783.317 | 692.054 | 819.4835 | 702.2151 | 730.1658 | 674.7595
| Aug | 799.6862 | 853.2147 | 827.4576 | 745.7665 | 620.1349 | 781.5169 | 546.5344 | 852.2578 | 724.0449 | 620.7122 | 812.7423 | 692.4968 | 786.1224 | 679.9163 | 720.1452 | 612.1343
| Sep | 769.2864 | 816.6037 | 792.325 | 678.1225 | 579.7802 | 731.2992 | 613.2944 | 680.9172 | 679.1837 | 718.3382 | 649.1063 | 651.7926 | 621.8743 | 657.6284 | 614.8 | 563.9612
| Oct | 755.6044 | 711.3852 | 669.5982 | 633.6096 | 560.7131 | 656.7209 | 540.6713 | 634.2054 | 643.8006 | 560.6457 | 589.3886 | 602.9139 | 586.3544 | 574.4955 | 572.0375 | 518.2515
| Nov | 687.1245 | 671.9745 | 593.3955 | 577.2709 | 534.7186 | 611.7551 | 538.975 | 593.6337 | 616.809 | 550.9945 | 588.7102 | 561.6767 | 531.9153 | 546.5401 | 498.6523 | 434.4062
| Dec | 646.8579 | 665.2499 | 586.9796 | 577.3205 | 534.3699 | 601.5995 | 495.3579 | 494.0137 | 531.6437 | 501.3609 | 483.9345 | 500.4174 | 428.3286 | 480.5957 | 430.7982 | 433.8504
Time of Peak Electrical Demand
| Jan | 06-JAN-20:00 | 02-JAN-20:10 | 26-JAN-20:10 | 24-JAN-20:00 | 12-JAN-20:10 | 18-JAN-18:10 | 15-JAN-18:00 | 08-JAN-20:00 | 25-JAN-18:10 | 27-JAN-20:00 | 17-JAN-20:10 | 27-JAN-18:00 | 30-JAN-20:10 | 14-JAN-18:40 | 13-JAN-20:10 | 19-JAN-20:10
| Feb | 23-FEB-20:10 | 20-FEB-20:10 | 08-FEB-20:19 | 25-FEB-18:00 | 23-FEB-20:10 | 27-FEB-18:10 | 15-FEB-20:00 | 15-FEB-18:10 | 14-FEB-18:10 | 21-FEB-20:10 | 27-FEB-20:00 | 11-FEB-18:00 | 27-FEB-20:00 | 02-FEB-18:10 | 28-FEB-18:10 | 28-FEB-18:10
| Mar | 13-MAR-19:10 | 25-MAR-17:19 | 17-MAR-17:19 | 27-MAR-19:00 | 31-MAR-19:10 | 30-MAR-19:10 | 25-MAR-17:49 | 09-MAR-20:10 | 18-MAR-17:00 | 28-MAR-19:10 | 31-MAR-19:49 | 26-MAR-17:10 | 25-MAR-17:30 | 30-MAR-19:19 | 22-MAR-17:10 | 31-MAR-17:10
| Apr | 01-APR-17:10 | 29-APR-17:10 | 01-APR-17:10 | 15-APR-17:00 | 11-APR-17:10 | 21-APR-17:10 | 12-APR-19:10 | 25-APR-19:10 | 24-APR-19:40 | 18-APR-19:10 | 28-APR-19:10 | 26-APR-19:10 | 01-APR-17:10 | 14-APR-19:49 | 15-APR-17:00 | 25-APR-19:10
| May | 15-MAY-17:19 | 26-MAY-19:10 | 27-MAY-17:19 | 31-MAY-17:30 | 30-MAY-19:10 | 31-MAY-17:19 | 24-MAY-19:19 | 15-MAY-17:10 | 31-MAY-17:10 | 05-MAY-17:00 | 30-MAY-17:10 | 23-MAY-17:19 | 27-MAY-17:10 | 16-MAY-17:10 | 30-MAY-19:00 | 24-MAY-19:10
| Jun | 27-JUN-17:19 | 13-JUN-17:19 | 28-JUN-17:49 | 08-JUN-19:10 | 28-JUN-19:10 | 27-JUN-17:19 | 21-JUN-19:30 | 30-JUN-17:19 | 20-JUN-17:10 | 17-JUN-17:19 | 19-JUN-17:19 | 27-JUN-17:10 | 29-JUN-17:19 | 24-JUN-17:00 | 14-JUN-17:19 | 20-JUN-17:19
| Jul | 12-JUL-17:19 | 05-JUL-17:19 | 19-JUL-17:19 | 02-JUL-17:19 | 29-JUL-17:19 | 25-JUL-19:10 | 02-JUL-17:10 | 24-JUL-17:30 | 31-JUL-17:30 | 31-JUL-17:10 | 13-JUL-17:10 | 16-JUL-17:10 | 15-JUL-17:10 | 21-JUL-17:10 | 06-JUL-18:10 | 29-JUL-17:19
| Aug | 21-AUG-17:30 | 06-AUG-19:10 | 05-AUG-17:30 | 14-AUG-17:19 | 08-AUG-17:10 | 02-AUG-17:19 | 26-AUG-17:10 | 17-AUG-17:19 | 01-AUG-17:10 | 05-AUG-17:10 | 04-AUG-17:19 | 29-AUG-17:10 | 25-AUG-17:19 | 09-AUG-17:10 | 12-AUG-17:10 | 15-AUG-17:10
| Sep | 09-SEP-17:10 | 16-SEP-17:10 | 09-SEP-17:10 | 01-SEP-17:19 | 23-SEP-17:10 | 01-SEP-17:10 | 28-SEP-17:10 | 09-SEP-17:10 | 02-SEP-17:10 | 02-SEP-17:10 | 06-SEP-17:10 | 02-SEP-17:10 | 14-SEP-17:10 | 01-SEP-17:10 | 08-SEP-19:10 | 01-SEP-19:10
| Oct | 07-OCT-17:10 | 29-OCT-17:10 | 02-OCT-17:10 | 21-OCT-17:10 | 07-OCT-17:10 | 03-OCT-17:10 | 03-OCT-19:10 | 02-OCT-19:00 | 13-OCT-19:00 | 02-OCT-19:10 | 30-OCT-20:00 | 05-OCT-17:10 | 06-OCT-19:40 | 06-OCT-17:10 | 07-OCT-17:10 | 01-OCT-17:10
| Nov | 01-NOV-20:00 | 27-NOV-20:10 | 12-NOV-18:10 | 28-NOV-20:10 | 02-NOV-20:00 | 10-NOV-18:19 | 02-NOV-20:00 | 04-NOV-18:00 | 09-NOV-20:00 | 04-NOV-18:00 | 02-NOV-20:49 | 04-NOV-18:00 | 02-NOV-20:10 | 21-NOV-20:10 | 02-NOV-20:00 | 13-NOV-20:00
| Dec | 15-DEC-20:10 | 02-DEC-18:19 | 11-DEC-20:00 | 04-DEC-20:10 | 21-DEC-20:10 | 05-DEC-18:19 | 06-DEC-20:00 | 02-DEC-18:00 | 09-DEC-18:10 | 23-DEC-18:00 | 12-DEC-20:10 | 21-DEC-18:10 | 08-DEC-20:00 | 20-DEC-20:00 | 27-DEC-20:00 | 18-DEC-20:00
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08
| Total Building | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08 | 7180.08
Emissions
| Carbon Equivalent (kg) | 1141554.7606 | 1277993.5669 | 1161804.6163 | 1075029.0377 | 395055.5666 | 1300131.7658 | 378611.0947 | 943643.0034 | 1475202.6784 | 278967.5397 | 1720567.7101 | 1346039.6397 | 1163827.2821 | 1182506.9708 | 1126866.3917 | 1034823.0098
| CO2 (kg) | 2661136.0252 | 3224937.8758 | 2752759.1696 | 2476818.759 | 1063061.1492 | 3102285.6618 | 1022467.0967 | 2170861.6206 | 3471220.0843 | 700220.4639 | 4034048.6208 | 3181520.4119 | 2765424.2833 | 2813946.4838 | 2695797.1343 | 2694642.7104
| NOX (kg) | 4616.4562 | 4182.9698 | 4566.216 | 4606.5314 | 915.456 | 4994.4714 | 882.9877 | 4073.6189 | 5942.2669 | 977.5263 | 7054.411 | 5384.7002 | 4672.722 | 4712.1877 | 4474.9541 | 3110.2525
| SO2 (kg) | 17333.0441 | 17595.543 | 14967.4769 | 11571.3495 | 8891.7297 | 20487.6546 | 8106.7957 | 11621.6823 | 15123.361 | 2186.053 | 20355.008 | 13527.5779 | 7054.3018 | 7817.0416 | 6615.8088 | 13902.7166
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0792 | 0.0497 | 0.0408 | 0.0426 | 0.0042 | 0.0386 | 0.0039 | 0.0473 | 0.0592 | 0.0089 | 0.062 | 0.0532 | 0.0523 | 0.0548 | 0.0492 | 0.0486
| Water Environmental Factors (m3) | 2145.144 | 6001.8573 | 110560 | 20581.6 | 53647.9 | 102174 | 48910.4 | 722.7354 | 15725 | 28881.9 | 4685.5757 | 14065.3 | 4635.7344 | 185407 | 4347.2323 | 2789.5805

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.19 | 49.33 | 2572.21
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.38
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | 15.19 | 90.86 | 4737.7
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | 14.91
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laundry_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Laundry_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Laundry_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_5_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720