## BuildingSummary
Building Summary Large Office new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Large Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 46320 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 12 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.38
| East | 0.38
| North | 0.38
| West | 0.38
| Total | 0.38
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11589.72
| Net Dimensions - Total Area (m2) | 6953.64
| Wall to Skin Ratio | 0.765
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3563
| Net Dimensions - Total Area (m2) | 3563
| Roof to Skin Ratio | 0.235
Window Dimensions (m2)
| South | 1390.85
| East | 927.23
| North | 1390.85
| West | 927.23
| Total Area (m2) | 4636.16
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 8 in slab
| Dimensions - Total Area (m2) | 3563
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 8523.53
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 92640.76
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.11 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Water cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | boiler
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 1504

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 10.76 | 4.842 | 0 | 0 | 10 | 0 | 958.824 | 0 | 0
Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.25388
Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.25387
Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0
Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.25388
Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.25387
Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0
Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.65051
Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.65928
Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.65051
Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.65928
Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0.39663
Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074437
Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074437
Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96713
Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.72 | 4636.08 |  | 2397.06 |  |  |  | 967.5482 |  |  | 23970.5998
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 25252.01 | 545.16 | 545.16
Net Site Energy | 25252.01 | 545.16 | 545.16
Total Source Energy | 82659.06 | 1784.51 | 1784.51
Net Source Energy | 82659.06 | 1784.51 | 1784.51
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 322.8 | 0 | 0 | 0 | 0
Cooling | 6869.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4208.16 | 0 | 0 | 0 | 0 | 0
Pumps | 1614.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 901.61 | 0 | 0 | 0 | 0 | 23731.16
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 172.41 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24756.79 | 495.21 | 0 | 0 | 0 | 25235.11
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 24756.79 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 24756.79 | 100
Total On-Site and Utility Electric Sources | 24756.79 | 100
Total Electricity End Uses | 24756.79 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 1159.04 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 772.69 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1159.04 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 772.69 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4030372.32 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 13768839.26 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3948859.17
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 9.04 | 24285.78 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 16.47 | 44233.02 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 172.66 | 463827.34 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 18.73 | 50327.02 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 78692.22 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 36932.78 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 55732.64 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.012374 | 568957.55 | 20143.56
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013882 | 638292.97 | 22598.33
CORE_MID VAV BOX REHEAT COIL | 0.14529 | 6680387.87 | 236514.65
CORE_TOP VAV BOX REHEAT COIL | 0.015819 | 727345.73 | 25751.19
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002242 | 103087.92 | 3649.76
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002027 | 93178.68 | 3298.93
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.002094 | 96272.94 | 3408.48
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002293 | 105441.07 | 3733.07
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.02333 | 1072699.72 | 37978.21
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.021397 | 983819.9 | 34831.48
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.021748 | 999982.35 | 35403.7
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.024564 | 1129472.85 | 39988.23
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002668 | 122694.94 | 4343.93
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002151 | 98907.46 | 3501.75
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002337 | 107468.27 | 3804.84
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.002667 | 122625.01 | 4341.46
VAV_5_HEATC | 0.00099 | 45521.17 | 710.96
VAV_1_HEATC | 0.000134 | 6173.76 | 103.03
VAV_2_HEATC | 0.00135 | 62090.57 | 1036.42
VAV_3_HEATC | 9.6e-05 | 4418.54 | 73.87
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.005896 | 9.04 | 24.74 | 12.8 | 7.22 | 0.009644 | 0.0085
VAV_1_COOLC | 0.011076 | 16.47 | 24.94 | 12.8 | 7.22 | 0.00975 | 0.0085
VAV_2_COOLC | 0.11448 | 172.66 | 24.92 | 12.8 | 7.22 | 0.009671 | 0.0085
VAV_3_COOLC | 0.013108 | 18.73 | 24.88 | 12.8 | 7.22 | 0.01002 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 354371.0756 | 619.4186 | 2344.8901 | 0 | 0.0107 | 290208.0729 | 152483.1204
February | 320195.9999 | 561.187 | 2130.5925 | 0 | 0.0097 | 263687.3326 | 137928.5897
March | 373126.8285 | 654.9501 | 2490.6235 | 0 | 0.0114 | 308246.3939 | 160828.8872
April | 345747.6536 | 608.8174 | 2323.0267 | 0 | 0.0106 | 287505.6003 | 149220.6296
May | 383393.2328 | 675.3933 | 2578.2196 | 0 | 0.0117 | 319089.3399 | 165496.7639
June | 386918.7358 | 681.7783 | 2603.2999 | 0 | 0.0119 | 322193.505 | 167036.0644
July | 386327.6244 | 680.7764 | 2599.6348 | 0 | 0.0118 | 321739.9269 | 166784.8493
August | 411566.5919 | 725.224 | 2769.2513 | 0 | 0.0126 | 342732.2411 | 177678.1965
September | 377695.6389 | 665.4869 | 2540.9321 | 0 | 0.0116 | 314474.6175 | 163050.4019
October | 367512.0522 | 647.2393 | 2470.0263 | 0 | 0.0113 | 305698.835 | 158623.6638
November | 345497.251 | 608.1908 | 2319.8824 | 0 | 0.0106 | 287116.3123 | 149093.9478
December | 340546.2654 | 596.8 | 2265.5812 | 0 | 0.0103 | 280393.8233 | 146689.3524
Annual Sum or Average | 4392898.95 | 7725.2621 | 29435.9606 | 0 | 0.1342 | 3643086.0008 | 1894914.4669
Minimum of Months | 320195.9999 | 561.187 | 2130.5925 | 0 | 0.0097 | 263687.3326 | 137928.5897
Maximum of Months | 411566.5919 | 725.224 | 2769.2513 | 0 | 0.0126 | 342732.2411 | 177678.1965
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1972130000000 | 1596665.665 | 06-JAN-14:15 | 448566.543 | 336424.909 | 247853.784 | 0 | 419253.525 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1791900000000 | 1629911.404 | 23-FEB-11:00 | 448566.543 | 336424.909 | 252020.298 | 0 | 448332.75 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2094710000000 | 1633328.23 | 13-MAR-14:00 | 448566.543 | 336424.909 | 249334.123 | 0 | 454435.751 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1953760000000 | 1675040.994 | 03-APR-13:00 | 448566.543 | 336424.909 | 257139.879 | 0 | 488342.759 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2168390000000 | 1752594.19 | 15-MAY-15:00 | 448566.543 | 336424.909 | 259525.7 | 0 | 563510.134 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2189480000000 | 1839886.077 | 26-JUN-15:30 | 448566.543 | 336424.909 | 261098.035 | 0 | 649229.686 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2186400000000 | 1785353.476 | 13-JUL-15:45 | 448566.543 | 336424.909 | 258870.579 | 0 | 596924.54 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2329060000000 | 1852360.99 | 21-AUG-14:30 | 448566.543 | 336424.909 | 267150.819 | 0 | 655651.814 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 2137030000000 | 1768676.436 | 11-SEP-14:00 | 448566.543 | 336424.909 | 263984.662 | 0 | 575133.417 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 2077390000000 | 1737092.307 | 06-OCT-15:45 | 448566.543 | 336424.909 | 257965.741 | 0 | 549568.209 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1951110000000 | 1647992.111 | 01-NOV-11:30 | 448566.543 | 336424.909 | 249769.884 | 0 | 468663.87 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1905430000000 | 1589634.968 | 15-DEC-15:45 | 448566.543 | 336424.909 | 246944.672 | 0 | 413131.939 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 24756800000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1791900000000 | 1589634.968 |  | 448566.543 | 336424.909 | 246944.672 | 0 | 413131.939 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2329060000000 | 1852360.99 |  | 448566.543 | 336424.909 | 267150.819 | 0 | 655651.814 | 0 | 92738.128 | 51828.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 572940.94 | 5639.16 | 0 | 578580.09
Cost per Total Building Area ($/m2) | 12.37 | 0.12 | 0 | 12.49
Cost per Net Conditioned Building Area ($/m2) | 12.37 | 0.12 | 0 | 12.49
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 27128.33 | 585.67 | 585.67
Net Site Energy | 27128.33 | 585.67 | 585.67
Total Source Energy | 3021.81 | 65.24 | 65.24
Net Source Energy | 3021.81 | 65.24 | 65.24
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2560.94 | 0 | 0 | 0 | 0
Cooling | 6178.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4428.41 | 0 | 0 | 0 | 0 | 0
Pumps | 1696.39 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 895.94 | 0 | 0 | 0 | 0 | 20718.75
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 206.29 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24361.1 | 2767.22 | 0 | 0 | 0 | 22222.7
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 24361.1 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 24361.1 | 100
Total On-Site and Utility Electric Sources | 24361.1 | 100
Total Electricity End Uses | 24361.1 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 1159.04 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 772.69 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1159.04 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 772.69 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3962919.58 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 14304333.32 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3882770.64
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.34 | 19706.56 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 16.83 | 45200.49 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 178.69 | 480032.18 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 19.51 | 52403.69 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 81752.7 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 36314.67 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 54799.89 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.010004 | 459982.95 | 16285.39
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013701 | 629953.88 | 22303.09
CORE_MID VAV BOX REHEAT COIL | 0.14486 | 6660427.4 | 235807.96
CORE_TOP VAV BOX REHEAT COIL | 0.015884 | 730365.56 | 25858.1
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002295 | 105527.07 | 3736.12
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002026 | 93153.84 | 3298.05
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.002535 | 116566.01 | 4126.94
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002389 | 109851.96 | 3889.23
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.024181 | 1111840.69 | 39363.97
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.021752 | 1000138.81 | 35409.24
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.027097 | 1245918.01 | 44110.89
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.025803 | 1186404.4 | 42003.85
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002799 | 128699.39 | 4556.52
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002189 | 100644.49 | 3563.25
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.002913 | 133949.28 | 4742.38
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.002817 | 129528.39 | 4585.87
VAV_5_HEATC | 0.000347 | 15976.17 | 260.97
VAV_1_HEATC | 0.000654 | 30061.2 | 493.19
VAV_2_HEATC | 0.006278 | 288660.46 | 4744.99
VAV_3_HEATC | 0.00058 | 26683.37 | 439.89
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.004754 | 7.34 | 24.64 | 12.8 | 7.22 | 0.009671 | 0.0085
VAV_1_COOLC | 0.010878 | 16.83 | 24.98 | 12.8 | 7.22 | 0.009517 | 0.0085
VAV_2_COOLC | 0.11359 | 178.69 | 24.96 | 12.8 | 7.22 | 0.009428 | 0.0085
VAV_3_COOLC | 0.012922 | 19.51 | 24.92 | 12.8 | 7.22 | 0.009687 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 485452.493 | 624.2616 | 2572.983 | 0 | 0.0073 | 877622.7123 | 191680.8091
February | 435851.2994 | 560.1536 | 2305.5506 | 0 | 0.0065 | 786402.2868 | 172054.0292
March | 497879.4594 | 647.6579 | 2742.7119 | 0 | 0.0077 | 935550.2232 | 197543.4964
April | 449270.1022 | 587.9232 | 2523.9247 | 0 | 0.0071 | 860936.6276 | 178707.6633
May | 491970.0192 | 645.8541 | 2792.5579 | 0 | 0.0078 | 952579.167 | 195957.1699
June | 510344.2445 | 670.4501 | 2903.5013 | 0 | 0.0082 | 990425.5129 | 203336.9976
July | 511168.4148 | 671.5828 | 2908.8895 | 0 | 0.0082 | 992263.7111 | 203671.8079
August | 547764.9121 | 719.5923 | 3116.1438 | 0 | 0.0088 | 1062960.7927 | 218244.2075
September | 470624.0232 | 618.1326 | 2675.6127 | 0 | 0.0075 | 912688.8885 | 187493.6644
October | 467459.3568 | 612.4716 | 2636.5515 | 0 | 0.0074 | 899358.0527 | 186038.9713
November | 453576.9574 | 591.6041 | 2520.7375 | 0 | 0.0071 | 859840.8799 | 180168.8037
December | 486767.9421 | 625.9594 | 2580.0412 | 0 | 0.0073 | 880030.2368 | 192201.0063
Annual Sum or Average | 5808129.224 | 7575.6433 | 32279.2056 | 0 | 0.091 | 11010700 | 2307098.6267
Minimum of Months | 435851.2994 | 560.1536 | 2305.5506 | 0 | 0.0065 | 786402.2868 | 172054.0292
Maximum of Months | 547764.9121 | 719.5923 | 3116.1438 | 0 | 0.0088 | 1062960.7927 | 218244.2075
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1941740000000 | 1561221.91 | 03-JAN-11:00 | 448566.543 | 336424.909 | 250071.712 | 0 | 384006.537 | 0 | 91190.844 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1739920000000 | 1530597.143 | 21-FEB-11:30 | 448566.543 | 336424.909 | 251555.926 | 0 | 351896.491 | 0 | 91191.91 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2069910000000 | 1555342.654 | 29-MAR-13:00 | 448566.543 | 336424.909 | 250071.712 | 0 | 378130.857 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1904820000000 | 1585962.069 | 10-APR-13:30 | 448566.543 | 336424.909 | 250071.712 | 0 | 408750.271 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2107580000000 | 1742363.828 | 30-MAY-12:00 | 448566.543 | 336424.909 | 263130.853 | 0 | 552092.889 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2191320000000 | 1725140.108 | 29-JUN-15:00 | 448566.543 | 336424.909 | 259392.512 | 0 | 538607.51 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2195390000000 | 1852529.176 | 18-JUL-12:15 | 448566.543 | 336424.909 | 262559.16 | 0 | 662829.93 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2351800000000 | 1793128.193 | 31-AUG-15:00 | 448566.543 | 336424.909 | 268707.094 | 0 | 597281.013 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 2019330000000 | 1776195.935 | 15-SEP-14:45 | 448566.543 | 336424.909 | 256913.931 | 0 | 592141.917 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1989830000000 | 1662253.614 | 30-OCT-14:30 | 448566.543 | 336424.909 | 251746.323 | 0 | 483367.205 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1902400000000 | 1602376.933 | 27-NOV-16:00 | 448566.543 | 336424.909 | 250071.712 | 0 | 425165.135 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1947070000000 | 1550886.83 | 06-DEC-14:45 | 448566.543 | 336424.909 | 250071.712 | 0 | 373666 | 0 | 91196.302 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 24361100000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1739920000000 | 1530597.143 |  | 448566.543 | 336424.909 | 250071.712 | 0 | 351896.491 | 0 | 91187.27 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2351800000000 | 1852529.176 |  | 448566.543 | 336424.909 | 268707.094 | 0 | 662829.93 | 0 | 91196.302 | 50961.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 710892.82 | 22287.67 | 0 | 733180.49
Cost per Total Building Area ($/m2) | 15.35 | 0.48 | 0 | 15.83
Cost per Net Conditioned Building Area ($/m2) | 15.35 | 0.48 | 0 | 15.83
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 27972.83 | 603.9 | 603.9
Net Site Energy | 27972.83 | 603.9 | 603.9
Total Source Energy | 82698.04 | 1785.35 | 1785.35
Net Source Energy | 82698.04 | 1785.35 | 1785.35
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2604.24 | 0 | 0 | 0 | 0
Cooling | 6037.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5292.15 | 0 | 0 | 0 | 0 | 0
Pumps | 1743.55 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 946.84 | 0 | 0 | 0 | 0 | 32127.44
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 186.7 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25181.9 | 2790.93 | 0 | 0 | 0 | 33631.38
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 25181.9 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 25181.9 | 100
Total On-Site and Utility Electric Sources | 25181.9 | 100
Total Electricity End Uses | 25181.9 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 1159.04 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 772.69 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 1159.04 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 772.69 | 6.88 | 0.25 | 0.25 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 115.9 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 77.27 | 6.88 | 0.25 | 0.25 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3955618.7 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15950694.6 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3875617.42
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 6.74 | 18106.76 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 19.08 | 51245.54 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 211.41 | 567931.52 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 24.12 | 64782.72 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 91162.05 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 36247.77 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 54698.93 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.008863 | 407520.4 | 14427.99
CORE_BOTTOM VAV BOX REHEAT COIL | 0.01393 | 640518.77 | 22677.14
CORE_MID VAV BOX REHEAT COIL | 0.15712 | 7224377.93 | 255774.25
CORE_TOP VAV BOX REHEAT COIL | 0.018364 | 844397.52 | 29895.33
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002759 | 126836.53 | 4490.56
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002348 | 107966.66 | 3822.49
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003298 | 151641.98 | 5368.78
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002749 | 126395.23 | 4474.94
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.029588 | 1360437.52 | 48165.38
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.025536 | 1174133.62 | 41569.41
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.035884 | 1649946.86 | 58415.26
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.029867 | 1373270.83 | 48619.73
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.003467 | 159429.26 | 5644.49
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002644 | 121564.56 | 4303.91
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003927 | 180576.56 | 6393.19
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003307 | 152066.24 | 5383.8
VAV_5_HEATC | 0.000226 | 10377.89 | 170.62
VAV_1_HEATC | 0.000307 | 14110.27 | 234.32
VAV_2_HEATC | 0.002523 | 115997.98 | 1931.08
VAV_3_HEATC | 0.000199 | 9128 | 152.3
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003704 | 6.74 | 25.41 | 12.8 | 7.22 | 0.008646 | 0.0085
VAV_1_COOLC | 0.010477 | 19.08 | 25.54 | 12.8 | 7.22 | 0.008592 | 0.0085
VAV_2_COOLC | 0.11479 | 211.41 | 25.43 | 12.8 | 7.22 | 0.008579 | 0.0085
VAV_3_COOLC | 0.012907 | 24.12 | 25.31 | 12.8 | 7.22 | 0.008551 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 429173.5627 | 700.5282 | 2251.239 | 0 | 0.0062 | 16628600 | 179982.7975
February | 388341.7077 | 635.5802 | 2049.3576 | 0 | 0.0056 | 15137500 | 163031.0948
March | 435128.4722 | 723.1543 | 2375.8393 | 0 | 0.0065 | 17549600 | 183785.2076
April | 395879.2362 | 663.437 | 2201.4116 | 0 | 0.006 | 16261400 | 167764.9274
May | 427701.8992 | 720.9043 | 2408.2991 | 0 | 0.0065 | 17789900 | 181669.0192
June | 446872.52 | 754.6068 | 2526.2991 | 0 | 0.0069 | 18661600 | 189952.4038
July | 453088.3038 | 765.35 | 2563.2252 | 0 | 0.0069 | 18934400 | 192619.5243
August | 470122.6921 | 794.0923 | 2659.3618 | 0 | 0.0072 | 19644500 | 199858.0545
September | 416402.8363 | 702.9996 | 2352.9246 | 0 | 0.0064 | 17380900 | 176984.9704
October | 412224.3069 | 691.8181 | 2299.4581 | 0 | 0.0062 | 16985700 | 174791.6206
November | 398200.2065 | 661.436 | 2171.7046 | 0 | 0.0059 | 16041700 | 168152.8262
December | 438142.1936 | 711.2311 | 2269.8083 | 0 | 0.0062 | 16765500 | 183345.9244
Annual Sum or Average | 5111277.9373 | 8525.1378 | 28128.9284 | 0 | 0.0766 | 207781000 | 2161938.3709
Minimum of Months | 388341.7077 | 635.5802 | 2049.3576 | 0 | 0.0056 | 15137500 | 163031.0948
Maximum of Months | 470122.6921 | 794.0923 | 2659.3618 | 0 | 0.0072 | 19644500 | 199858.0545
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2015290000000 | 1535843.357 | 26-JAN-15:30 | 448566.543 | 336424.909 | 297154.336 | 0 | 311802.152 | 0 | 91027.938 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1834580000000 | 1550941.411 | 28-FEB-15:45 | 448566.543 | 336424.909 | 297267.123 | 0 | 326795.947 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2126910000000 | 1590914.919 | 17-MAR-15:00 | 448566.543 | 336424.909 | 300073.097 | 0 | 363963.482 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1970790000000 | 1597125.61 | 26-APR-15:45 | 448566.543 | 336424.909 | 300412.934 | 0 | 369834.336 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2156030000000 | 1663714.526 | 30-MAY-15:15 | 448566.543 | 336424.909 | 309573.499 | 0 | 427262.686 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2261680000000 | 1779387.98 | 28-JUN-15:00 | 448566.543 | 336424.909 | 325295.252 | 0 | 527214.387 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2294740000000 | 1829375.307 | 11-JUL-15:00 | 448566.543 | 336424.909 | 322481.214 | 0 | 580015.754 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2380800000000 | 1806268.298 | 02-AUG-14:00 | 448566.543 | 336424.909 | 320041.959 | 0 | 559347.998 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 2106460000000 | 1753740.68 | 05-SEP-14:15 | 448566.543 | 336424.909 | 315116.824 | 0 | 511745.516 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 2058570000000 | 1615968.332 | 03-OCT-15:45 | 448566.543 | 336424.909 | 295446.518 | 0 | 393643.474 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1944160000000 | 1584521.519 | 13-NOV-15:15 | 448566.543 | 336424.909 | 300202.781 | 0 | 357440.398 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 2031890000000 | 1530912.339 | 13-DEC-13:15 | 448566.543 | 336424.909 | 295542.427 | 0 | 308456.158 | 0 | 91054.824 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 25181900000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1834580000000 | 1530912.339 |  | 448566.543 | 336424.909 | 295446.518 | 0 | 308456.158 | 0 | 91019.409 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2380800000000 | 1829375.307 |  | 448566.543 | 336424.909 | 325295.252 | 0 | 580015.754 | 0 | 91054.824 | 50867.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 520872.58 | 23007.69 | 0 | 543880.26
Cost per Total Building Area ($/m2) | 11.24 | 0.5 | 0 | 11.74
Cost per Net Conditioned Building Area ($/m2) | 11.24 | 0.5 | 0 | 11.74
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 26205.47 | 565.74 | 565.74
Net Site Energy | 26205.47 | 565.74 | 565.74
Total Source Energy | 81438.67 | 1758.16 | 1758.16
Net Source Energy | 81438.67 | 1758.16 | 1758.16
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2717.21 | 0 | 0 | 0 | 0
Cooling | 5132.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4509.94 | 0 | 0 | 0 | 0 | 0
Pumps | 1626.24 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 818.41 | 0 | 0 | 0 | 0 | 17660.68
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 239.02 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 23249.25 | 2956.23 | 0 | 0 | 0 | 19164.62
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 23249.25 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 23249.25 | 100
Total On-Site and Utility Electric Sources | 23249.25 | 100
Total Electricity End Uses | 23249.25 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 1159.04 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 772.69 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 1159.04 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 772.69 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3854530.79 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 14224117.32 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3776573.98
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.05 | 18944.52 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 17.21 | 46229.06 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 182.58 | 490466.86 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 19.83 | 53261.17 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 81294.25 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35321.44 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 53301.07 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.0093 | 427599.43 | 15138.87
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013575 | 624176.72 | 22098.56
CORE_MID VAV BOX REHEAT COIL | 0.14411 | 6626329.37 | 234600.75
CORE_TOP VAV BOX REHEAT COIL | 0.015566 | 715721.35 | 25339.63
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002107 | 96875.45 | 3429.81
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002079 | 95570.06 | 3383.59
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.002623 | 120590.92 | 4269.44
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.00231 | 106229.36 | 3760.98
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.020685 | 951100.82 | 33673.09
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.022499 | 1034516.22 | 36626.35
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.02839 | 1305373.17 | 46215.86
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.025078 | 1153075.83 | 40823.88
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002582 | 118701.81 | 4202.56
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002247 | 103313.8 | 3657.76
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003019 | 138828.01 | 4915.11
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.002732 | 125600.27 | 4446.79
VAV_5_HEATC | 0.000465 | 21385.25 | 345.87
VAV_1_HEATC | 0.000859 | 39502.03 | 643.91
VAV_2_HEATC | 0.008336 | 383267.34 | 6261.18
VAV_3_HEATC | 0.000791 | 36360.11 | 595.81
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.004381 | 7.05 | 24.5 | 12.8 | 7.22 | 0.009673 | 0.0085
VAV_1_COOLC | 0.010545 | 17.21 | 24.84 | 12.8 | 7.22 | 0.009458 | 0.0085
VAV_2_COOLC | 0.11088 | 182.58 | 24.82 | 12.8 | 7.22 | 0.009415 | 0.0085
VAV_3_COOLC | 0.012445 | 19.83 | 24.79 | 12.8 | 7.22 | 0.009618 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 405160.3903 | 740.4197 | 1828.5318 | 0 | 0.0068 | 3252222.9157 | 174642.5101
February | 342846.9088 | 634.8047 | 1587.8012 | 0 | 0.0058 | 2824142.1662 | 148545.5132
March | 407316.1076 | 770.081 | 1964.3506 | 0 | 0.0072 | 3494045.7607 | 177947.1967
April | 370666.612 | 707.6291 | 1821.1248 | 0 | 0.0067 | 3239349.6909 | 162567.4114
May | 392687.9435 | 755.7136 | 1958.9474 | 0 | 0.0071 | 3484558.7361 | 172783.7594
June | 402809.1162 | 776.7613 | 2017.1331 | 0 | 0.0074 | 3588073.0431 | 177382.0844
July | 402181.44 | 775.5549 | 2014.0092 | 0 | 0.0073 | 3582516.22 | 177106.042
August | 425853.1295 | 821.2147 | 2132.6094 | 0 | 0.0078 | 3793482.2759 | 187531.3069
September | 383014.9588 | 737.9859 | 1915.0443 | 0 | 0.007 | 3406472.1902 | 168609.5931
October | 379822.7293 | 726.4623 | 1872.7449 | 0 | 0.0068 | 3331181.9255 | 166708.1142
November | 372212.221 | 701.5353 | 1784.3818 | 0 | 0.0065 | 3173910.0235 | 162410.0029
December | 384451.5897 | 710.1347 | 1772.1295 | 0 | 0.0065 | 3151981.1324 | 166414.2472
Annual Sum or Average | 4669023.1468 | 8858.2971 | 22668.808 | 0 | 0.083 | 40321900 | 2042647.7815
Minimum of Months | 342846.9088 | 634.8047 | 1587.8012 | 0 | 0.0058 | 2824142.1662 | 148545.5132
Maximum of Months | 425853.1295 | 821.2147 | 2132.6094 | 0 | 0.0078 | 3793482.2759 | 187531.3069
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1875200000000 | 1472677.571 | 24-JAN-16:00 | 448566.543 | 336424.909 | 254968.271 | 0 | 294346.178 | 0 | 88804.136 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1628370000000 | 1468678.485 | 21-FEB-15:00 | 448566.543 | 336424.909 | 254968.271 | 0 | 290449.718 | 0 | 88701.51 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2014630000000 | 1496308.457 | 29-MAR-14:00 | 448566.543 | 336424.909 | 254968.271 | 0 | 318085.982 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1867780000000 | 1545323.866 | 20-APR-15:00 | 448566.543 | 336424.909 | 261623.778 | 0 | 360445.884 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2009160000000 | 1630073.465 | 31-MAY-15:00 | 448566.543 | 336424.909 | 265211.076 | 0 | 441608.184 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2068850000000 | 1668290.407 | 08-JUN-15:30 | 448566.543 | 336424.909 | 261830.023 | 0 | 483206.18 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2065640000000 | 1756923.513 | 03-JUL-14:30 | 448566.543 | 336424.909 | 275449.199 | 0 | 558220.111 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2187290000000 | 1715122.308 | 14-AUG-14:30 | 448566.543 | 336424.909 | 271844.502 | 0 | 520023.601 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1964140000000 | 1675450.261 | 05-SEP-15:00 | 448566.543 | 336424.909 | 272970.979 | 0 | 479225.077 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1920730000000 | 1553228.123 | 12-OCT-15:00 | 448566.543 | 336424.909 | 262498.329 | 0 | 367475.589 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1830050000000 | 1484013.481 | 21-NOV-14:00 | 448566.543 | 336424.909 | 257128.315 | 0 | 303630.08 | 0 | 88696.102 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1817400000000 | 1478778.097 | 26-DEC-14:45 | 448566.543 | 336424.909 | 254968.271 | 0 | 300473.397 | 0 | 88777.443 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 23249200000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1628370000000 | 1468678.485 |  | 448566.543 | 336424.909 | 254968.271 | 0 | 290449.718 | 0 | 88695.219 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2187290000000 | 1756923.513 |  | 448566.543 | 336424.909 | 275449.199 | 0 | 558220.111 | 0 | 88804.136 | 49567.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 620935.16 | 28530.28 | 0 | 649465.43
Cost per Total Building Area ($/m2) | 13.41 | 0.62 | 0 | 14.02
Cost per Net Conditioned Building Area ($/m2) | 13.41 | 0.62 | 0 | 14.02
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 22895.11 | 494.28 | 494.28
Net Site Energy | 22895.11 | 494.28 | 494.28
Total Source Energy | 68309.79 | 1474.72 | 1474.72
Net Source Energy | 68309.79 | 1474.72 | 1474.72
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1040.62 | 0 | 0 | 0 | 0
Cooling | 4362.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4115.87 | 0 | 0 | 0 | 0 | 0
Pumps | 1272.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 708.34 | 0 | 0 | 0 | 0 | 14055.83
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 232.76 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21621.73 | 1273.38 | 0 | 0 | 0 | 15559.77
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 21621.73 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 21621.73 | 100
Total On-Site and Utility Electric Sources | 21621.73 | 100
Total Electricity End Uses | 21621.73 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 1159.04 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 772.69 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 1159.04 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 772.69 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3182655.36 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 13550759.03 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3118287.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 6.69 | 17974.09 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 16.14 | 43362.39 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 174.22 | 468029.58 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 17.22 | 46266.93 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 77445.84 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29164.63 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 44010.27 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.009126 | 419594.23 | 14855.45
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013506 | 621022.54 | 21986.89
CORE_MID VAV BOX REHEAT COIL | 0.14472 | 6654063.88 | 235582.67
CORE_TOP VAV BOX REHEAT COIL | 0.014209 | 653345.66 | 23131.26
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001677 | 77128.42 | 2730.68
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.00196 | 90110.64 | 3190.31
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.002712 | 124706.53 | 4415.15
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.00216 | 99300.39 | 3515.66
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.018505 | 850837.29 | 30123.32
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.021135 | 971773.26 | 34404.98
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.02983 | 1371572.8 | 48559.61
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.023437 | 1077618.18 | 38152.35
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001721 | 79145.81 | 2802.1
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002031 | 93373.68 | 3305.83
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003053 | 140365.71 | 4969.55
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.002476 | 113842.47 | 4030.52
VAV_5_HEATC | 0.000141 | 6471.12 | 107.2
VAV_1_HEATC | 0.000221 | 10147.9 | 168.81
VAV_2_HEATC | 0.001886 | 86738.22 | 1445.27
VAV_3_HEATC | 0.000209 | 9600.32 | 159.85
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003559 | 6.69 | 24.22 | 12.8 | 7.22 | 0.008778 | 0.0085
VAV_1_COOLC | 0.008681 | 16.14 | 24.52 | 12.8 | 7.22 | 0.008712 | 0.0085
VAV_2_COOLC | 0.092812 | 174.22 | 24.52 | 12.8 | 7.22 | 0.008663 | 0.0085
VAV_3_COOLC | 0.009101 | 17.22 | 24.52 | 12.8 | 7.22 | 0.008625 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 166544.3903 | 143.1511 | 1441.1146 | 0 | 0.0007 | 8695085.4813 | 62038.0771
February | 149729.1784 | 128.6198 | 1309.5667 | 0 | 0.0006 | 7901430.1892 | 55816.9565
March | 172885.3102 | 148.3971 | 1532.5285 | 0 | 0.0007 | 9246770.2442 | 64511.5805
April | 155111.485 | 133.0084 | 1398.661 | 0 | 0.0006 | 8439140.8186 | 57951.6051
May | 164547.2347 | 141.0092 | 1499.9191 | 0 | 0.0007 | 9050160.2496 | 61526.2683
June | 162640.4987 | 139.3191 | 1492.5717 | 0 | 0.0007 | 9005861.8525 | 60843.9271
July | 157767.54 | 135.0859 | 1458.4088 | 0 | 0.0007 | 8799766.2085 | 59053.1584
August | 173532.7432 | 148.5896 | 1603.2595 | 0 | 0.0007 | 9673765.2811 | 64951.4555
September | 157655.6565 | 135.0204 | 1451.9555 | 0 | 0.0007 | 8760809.8185 | 58994.7465
October | 160145.8806 | 137.2208 | 1462.7821 | 0 | 0.0007 | 8826094.4394 | 59889.6487
November | 156979.4328 | 134.6436 | 1409.5263 | 0 | 0.0006 | 8504678.6673 | 58631.2546
December | 162759.1445 | 139.8498 | 1416.8934 | 0 | 0.0007 | 8548975.4275 | 60654.0992
Annual Sum or Average | 1940298.4948 | 1663.9146 | 17477.1873 | 0 | 0.0079 | 105453000 | 724862.7775
Minimum of Months | 149729.1784 | 128.6198 | 1309.5667 | 0 | 0.0006 | 7901430.1892 | 55816.9565
Maximum of Months | 173532.7432 | 148.5896 | 1603.2595 | 0 | 0.0007 | 9673765.2811 | 64951.4555
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1782820000000 | 1422448.285 | 26-JAN-13:15 | 448566.543 | 336424.909 | 244912.952 | 0 | 278368.755 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1620090000000 | 1426881.052 | 13-FEB-11:00 | 448566.543 | 336424.909 | 246537.245 | 0 | 281177.229 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1895940000000 | 1422313.146 | 31-MAR-14:30 | 448566.543 | 336424.909 | 246887.957 | 0 | 276258.61 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1730340000000 | 1446416.397 | 11-APR-13:00 | 448566.543 | 336424.909 | 243673.789 | 0 | 303576.03 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1855620000000 | 1487963.4 | 30-MAY-10:00 | 448566.543 | 336424.909 | 246282.103 | 0 | 342514.719 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1846540000000 | 1460727.472 | 28-JUN-12:00 | 448566.543 | 336424.909 | 242687.021 | 0 | 318873.873 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1804280000000 | 1485565.949 | 10-JUL-09:00 | 448566.543 | 336424.909 | 245071.675 | 0 | 341327.695 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1983490000000 | 1534624.138 | 08-AUG-15:30 | 448566.543 | 336424.909 | 248542.266 | 0 | 386915.293 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1796300000000 | 1513365.75 | 25-SEP-14:00 | 448566.543 | 336424.909 | 251986.993 | 0 | 362212.179 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1809680000000 | 1465875.708 | 05-OCT-10:00 | 448566.543 | 336424.909 | 246715.556 | 0 | 319993.574 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1743780000000 | 1430550.298 | 20-NOV-13:15 | 448566.543 | 336424.909 | 247058.174 | 0 | 284325.546 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1752860000000 | 1430344.173 | 19-DEC-13:15 | 448566.543 | 336424.909 | 246901.736 | 0 | 284275.859 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 21621700000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1620090000000 | 1422313.146 |  | 448566.543 | 336424.909 | 242687.021 | 0 | 276258.61 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1983490000000 | 1534624.138 |  | 448566.543 | 336424.909 | 251986.993 | 0 | 386915.293 | 0 | 73247.609 | 40927.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 317368.7 | 10939.9 | 0 | 328308.6
Cost per Total Building Area ($/m2) | 6.85 | 0.24 | 0 | 7.09
Cost per Net Conditioned Building Area ($/m2) | 6.85 | 0.24 | 0 | 7.09
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 30907.33 | 667.25 | 667.25
Net Site Energy | 30907.33 | 667.25 | 667.25
Total Source Energy | 104921.35 | 2265.12 | 2265.12
Net Source Energy | 104921.35 | 2265.12 | 2265.12
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2057.06 | 0 | 0 | 0 | 0
Cooling | 7758.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5222.77 | 0 | 0 | 0 | 0 | 0
Pumps | 2964.76 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1531.86 | 0 | 0 | 0 | 0 | 48264.88
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 210.21 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 28640.06 | 2267.27 | 0 | 0 | 0 | 49768.82
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 28640.06 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 28640.06 | 100
Total On-Site and Utility Electric Sources | 28640.06 | 100
Total Electricity End Uses | 28640.06 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 1159.04 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 772.69 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 1159.04 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 772.69 | 3.24 | 0.25 | 0.318 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 115.9 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 77.27 | 3.24 | 0.25 | 0.318 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 6760922.31 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15391343.86 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 6624184.55
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.21 | 19380.13 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 19.03 | 51116.06 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 210.42 | 565269.22 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 23.42 | 62926.36 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 87965.23 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 61954.5 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 93491.12 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.009124 | 419507.1 | 14852.37
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013865 | 637502.44 | 22570.35
CORE_MID VAV BOX REHEAT COIL | 0.15352 | 7058948.35 | 249917.33
CORE_TOP VAV BOX REHEAT COIL | 0.017484 | 803932.28 | 28462.68
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002315 | 106432.24 | 3768.16
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002264 | 104112.4 | 3686.03
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003055 | 140469.19 | 4973.22
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002565 | 117954.51 | 4176.1
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.026606 | 1223350.61 | 43311.91
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.024752 | 1138093.24 | 40293.43
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.033355 | 1533653.84 | 54297.99
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.02788 | 1281910.15 | 45385.17
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002882 | 132509.06 | 4691.39
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002544 | 116951.53 | 4140.59
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003628 | 166814.14 | 5905.94
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003086 | 141912.33 | 5024.31
VAV_5_HEATC | 0.000311 | 14279.97 | 233.37
VAV_1_HEATC | 0.000511 | 23495.85 | 387.5
VAV_2_HEATC | 0.004592 | 211148.2 | 3493.02
VAV_3_HEATC | 0.000399 | 18366.42 | 304.71
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.006682 | 7.21 | 25.07 | 12.8 | 7.22 | 0.008473 | 0.004236
VAV_1_COOLC | 0.017803 | 19.03 | 25.3 | 12.8 | 7.22 | 0.008466 | 0.004233
VAV_2_COOLC | 0.19626 | 210.42 | 25.23 | 12.8 | 7.22 | 0.008467 | 0.004233
VAV_3_COOLC | 0.021752 | 23.42 | 25.17 | 12.8 | 7.22 | 0.008438 | 0.004219
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 521900.3962 | 834.3331 | 3391.2818 | 0 | 0.0064 | 16912500 | 218110.0313
February | 477966.929 | 771.7329 | 3177.5566 | 0 | 0.006 | 15846900 | 200543.0124
March | 560415.6163 | 906.7841 | 3743.8054 | 0 | 0.007 | 18671000 | 235336.8458
April | 520106.9836 | 849.6539 | 3550.5808 | 0 | 0.0067 | 17707600 | 219250.9355
May | 557907.2935 | 913.37 | 3827.0994 | 0 | 0.0072 | 19086700 | 235389.8825
June | 569950.7619 | 934.0778 | 3919.0298 | 0 | 0.0073 | 19545300 | 240574.221
July | 567481.7065 | 930.163 | 3903.2896 | 0 | 0.0073 | 19466800 | 239545.7233
August | 593511.7287 | 972.7858 | 4081.9246 | 0 | 0.0076 | 20357700 | 250529.0384
September | 538931.7673 | 883.131 | 3704.7013 | 0 | 0.0069 | 18476300 | 227469.7203
October | 532638.2912 | 870.0037 | 3634.985 | 0 | 0.0068 | 18128500 | 224520.8714
November | 512745.204 | 830.1924 | 3430.4394 | 0 | 0.0065 | 17108200 | 215374.7866
December | 519796.9267 | 833.131 | 3397.9212 | 0 | 0.0064 | 16945700 | 217455.522
Annual Sum or Average | 6473353.6049 | 10529.3588 | 43762.6148 | 0 | 0.0822 | 218253000 | 2724100.5905
Minimum of Months | 477966.929 | 771.7329 | 3177.5566 | 0 | 0.006 | 15846900 | 200543.0124
Maximum of Months | 593511.7287 | 972.7858 | 4081.9246 | 0 | 0.0076 | 20357700 | 250529.0384
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2219330000000 | 1806558.667 | 30-JAN-13:45 | 448566.543 | 336424.909 | 297318.939 | 0 | 481739.589 | 0 | 155566.265 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 2079500000000 | 1807474.221 | 27-FEB-13:45 | 448566.543 | 336424.909 | 298281.644 | 0 | 481739.589 | 0 | 155519.114 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2450080000000 | 1806101.82 | 31-MAR-14:30 | 448566.543 | 336424.909 | 296910.032 | 0 | 481739.589 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 2323660000000 | 1809614.592 | 21-APR-14:00 | 448566.543 | 336424.909 | 300422.804 | 0 | 481739.589 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2504640000000 | 1830595.27 | 31-MAY-15:00 | 448566.543 | 336424.909 | 303095.856 | 0 | 500047.215 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2564810000000 | 1910816.52 | 27-JUN-15:00 | 448566.543 | 336424.909 | 322851.071 | 0 | 560513.25 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2554510000000 | 1932686.914 | 25-JUL-14:30 | 448566.543 | 336424.909 | 347633.837 | 0 | 557600.878 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2671410000000 | 1926223.315 | 02-AUG-13:30 | 448566.543 | 336424.909 | 313712.604 | 0 | 585058.511 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 2424540000000 | 1879214.983 | 01-SEP-14:00 | 448566.543 | 336424.909 | 315286.568 | 0 | 536476.216 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 2378900000000 | 1813049.164 | 03-OCT-14:00 | 448566.543 | 336424.909 | 302743.546 | 0 | 482853.419 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 2245000000000 | 1806776.178 | 09-NOV-13:15 | 448566.543 | 336424.909 | 297583.835 | 0 | 481739.589 | 0 | 155518.88 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 2223680000000 | 1805778.25 | 05-DEC-13:30 | 448566.543 | 336424.909 | 296568.744 | 0 | 481739.589 | 0 | 155536.044 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 28640100000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 2079500000000 | 1805778.25 |  | 448566.543 | 336424.909 | 296568.744 | 0 | 481739.589 | 0 | 155518.325 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2671410000000 | 1932686.914 |  | 448566.543 | 336424.909 | 347633.837 | 0 | 585058.511 | 0 | 155566.265 | 86942.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 739062.54 | 17467.29 | 0 | 756529.82
Cost per Total Building Area ($/m2) | 15.96 | 0.38 | 0 | 16.33
Cost per Net Conditioned Building Area ($/m2) | 15.96 | 0.38 | 0 | 16.33
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 25933.13 | 559.86 | 559.86
Net Site Energy | 25933.13 | 559.86 | 559.86
Total Source Energy | 72028.07 | 1555 | 1555
Net Source Energy | 72028.07 | 1555 | 1555
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3850.58 | 0 | 0 | 0 | 0
Cooling | 4169.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4260.26 | 0 | 0 | 0 | 0 | 0
Pumps | 1441.7 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 787.58 | 0 | 0 | 0 | 0 | 12186.72
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 260.73 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21821.82 | 4111.31 | 0 | 0 | 0 | 13690.66
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 21821.82 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 21821.82 | 100
Total On-Site and Utility Electric Sources | 21821.82 | 100
Total Electricity End Uses | 21821.82 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 115.9 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 77.27 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 115.9 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 77.27 | 6.88 | 0.34 | 0.34 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 1159.04 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 772.69 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 1159.04 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 772.69 | 6.88 | 0.34 | 0.34 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 115.9 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 77.27 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 115.9 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 77.27 | 6.88 | 0.34 | 0.34 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3288826.41 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 13719737.08 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3222310.82
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 6.73 | 18088.87 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 16.3 | 43788.58 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 175.62 | 471767.56 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 15.79 | 42425.55 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 78411.59 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30137.54 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 45478.42 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.009213 | 423628.07 | 14998.27
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013217 | 607706.32 | 21515.43
CORE_MID VAV BOX REHEAT COIL | 0.14245 | 6549670.4 | 231886.69
CORE_TOP VAV BOX REHEAT COIL | 0.011928 | 548460.88 | 19417.89
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001446 | 66503.89 | 2354.53
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.001905 | 87576.12 | 3100.57
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003416 | 157057.21 | 5560.51
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.00232 | 106653.15 | 3775.98
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.014939 | 686883.21 | 24318.64
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.020047 | 921770.33 | 32634.66
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.037859 | 1740755.44 | 61630.28
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.024997 | 1149372.92 | 40692.78
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.001958 | 90027.03 | 3187.35
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.00184 | 84593 | 2994.96
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003742 | 172072.69 | 6092.12
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.002556 | 117502.63 | 4160.1
VAV_5_HEATC | 0.000227 | 10432.02 | 171.62
VAV_1_HEATC | 0.000386 | 17754.07 | 293.69
VAV_2_HEATC | 0.003523 | 161974.28 | 2684.79
VAV_3_HEATC | 0.000421 | 19343.42 | 319.44
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003386 | 6.73 | 23.73 | 12.8 | 7.22 | 0.008695 | 0.0085
VAV_1_COOLC | 0.008489 | 16.3 | 24.23 | 12.8 | 7.22 | 0.008656 | 0.0085
VAV_2_COOLC | 0.090852 | 175.62 | 24.26 | 12.8 | 7.22 | 0.008614 | 0.0085
VAV_3_COOLC | 0.015233 | 15.79 | 24.18 | 12.8 | 7.22 | 0.008498 | 0.004249
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 198725.0183 | 172.0155 | 1504.1478 | 0 | 0.0008 | 9074628.6095 | 73368.1587
February | 164345.7147 | 141.716 | 1340.7131 | 0 | 0.0006 | 8089012.3383 | 60970.7908
March | 192935.7001 | 166.4287 | 1563.3154 | 0 | 0.0008 | 9432012.8804 | 71544.9836
April | 170538.5598 | 146.8707 | 1424.4141 | 0 | 0.0007 | 8594137.8594 | 63369.5135
May | 174031.5584 | 149.5979 | 1503.8777 | 0 | 0.0007 | 9073764.8149 | 64820.8864
June | 170532.0102 | 146.4795 | 1493.3463 | 0 | 0.0007 | 9010293.5006 | 63577.556
July | 162382.0499 | 139.3586 | 1443.534 | 0 | 0.0007 | 8709821.2745 | 60604.8657
August | 176689.1535 | 151.6703 | 1564.7766 | 0 | 0.0007 | 9441339.1587 | 65926.4845
September | 161020.9387 | 138.1897 | 1431.57 | 0 | 0.0007 | 8637634.7141 | 60097.2811
October | 167986.9097 | 144.3562 | 1459.8143 | 0 | 0.0007 | 8807933.9534 | 62594.3876
November | 172751.2951 | 148.8529 | 1429.1962 | 0 | 0.0007 | 8622939.2203 | 64149.9348
December | 193557.1376 | 167.4531 | 1480.9711 | 0 | 0.0007 | 8934867.2422 | 71508.8352
Annual Sum or Average | 2105496.0461 | 1812.9891 | 17639.6768 | 0 | 0.0083 | 106428000 | 782533.6778
Minimum of Months | 161020.9387 | 138.1897 | 1340.7131 | 0 | 0.0006 | 8089012.3383 | 60097.2811
Maximum of Months | 198725.0183 | 172.0155 | 1564.7766 | 0 | 0.0008 | 9441339.1587 | 73368.1587
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1860640000000 | 1383182.672 | 04-JAN-16:00 | 448566.543 | 336424.909 | 241373.076 | 0 | 234340.495 | 3997.501 | 76187.318 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1658550000000 | 1418381.666 | 15-FEB-15:00 | 448566.543 | 336424.909 | 243746.911 | 0 | 271661.804 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1933920000000 | 1398203.648 | 01-MAR-13:15 | 448566.543 | 336424.909 | 244556.93 | 0 | 250669.676 | 0 | 75692.76 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1762120000000 | 1415392.545 | 13-APR-14:00 | 448566.543 | 336424.909 | 245431.277 | 0 | 266988.317 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1860460000000 | 1431018.861 | 25-MAY-15:00 | 448566.543 | 336424.909 | 243687.1 | 0 | 284358.809 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1847450000000 | 1434599.087 | 16-JUN-15:00 | 448566.543 | 336424.909 | 246045.458 | 0 | 285580.677 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1785840000000 | 1487339.419 | 03-JUL-13:15 | 448566.543 | 336424.909 | 249721.888 | 0 | 334644.579 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 1935830000000 | 1461786.008 | 15-AUG-12:15 | 448566.543 | 336424.909 | 245153.181 | 0 | 313659.876 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1771040000000 | 1516824.887 | 28-SEP-14:00 | 448566.543 | 336424.909 | 258065.491 | 0 | 355786.445 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1805960000000 | 1439326.147 | 31-OCT-13:15 | 448566.543 | 336424.909 | 246393.222 | 0 | 289959.973 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1768030000000 | 1407552.374 | 16-NOV-15:00 | 448566.543 | 336424.909 | 241373.076 | 0 | 263022.945 | 0 | 75872.071 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1831980000000 | 1383058.727 | 27-DEC-16:00 | 448566.543 | 336424.909 | 241373.076 | 0 | 234340.495 | 3997.501 | 76063.373 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 21821800000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1658550000000 | 1383058.727 |  | 448566.543 | 336424.909 | 241373.076 | 0 | 234340.495 | 0 | 75688.67 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1935830000000 | 1516824.887 |  | 448566.543 | 336424.909 | 258065.491 | 0 | 355786.445 | 3997.501 | 76187.318 | 42292.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 859586.07 | 35124.01 | 0 | 894710.08
Cost per Total Building Area ($/m2) | 18.56 | 0.76 | 0 | 19.32
Cost per Net Conditioned Building Area ($/m2) | 18.56 | 0.76 | 0 | 19.32
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 29062.74 | 627.43 | 627.43
Net Site Energy | 29062.74 | 627.43 | 627.43
Total Source Energy | 91711.25 | 1979.93 | 1979.93
Net Source Energy | 91711.25 | 1979.93 | 1979.93
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4653.58 | 0 | 0 | 0 | 0
Cooling | 5255.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5050.04 | 0 | 0 | 0 | 0 | 0
Pumps | 1832.21 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 843.85 | 0 | 0 | 0 | 0 | 17520.65
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 264.73 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24144.42 | 4918.31 | 0 | 0 | 0 | 19024.6
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 24144.42 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 24144.42 | 100
Total On-Site and Utility Electric Sources | 24144.42 | 100
Total Electricity End Uses | 24144.42 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4177685.03 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15902170.45 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4093192.52
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.15 | 19201.29 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 18.33 | 49234.53 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 198.37 | 532890.97 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 20.92 | 56197.9 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 90884.72 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 38282.7 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 57769.7 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.009731 | 447445.17 | 15841.5
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013943 | 641086.65 | 22697.24
CORE_MID VAV BOX REHEAT COIL | 0.14924 | 6861903.64 | 242941.09
CORE_TOP VAV BOX REHEAT COIL | 0.015691 | 721492.62 | 25543.96
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002136 | 98192.07 | 3476.42
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.00264 | 121376.73 | 4297.26
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003258 | 149819.14 | 5304.25
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002976 | 136831.6 | 4844.43
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.023983 | 1102739.97 | 39041.77
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.028672 | 1318323.47 | 46674.36
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.035642 | 1638811.5 | 58021.02
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.032538 | 1496112.92 | 52968.87
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002753 | 126601.64 | 4482.25
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002841 | 130651.54 | 4625.63
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003723 | 171197.29 | 6061.13
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003472 | 159629.51 | 5651.58
VAV_5_HEATC | 0.00057 | 26207.18 | 421.67
VAV_1_HEATC | 0.001041 | 47883.04 | 778.53
VAV_2_HEATC | 0.010031 | 461202.53 | 7521.47
VAV_3_HEATC | 0.000971 | 44662.22 | 729.9
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.004501 | 7.15 | 24.38 | 12.8 | 7.22 | 0.009614 | 0.0085
VAV_1_COOLC | 0.011345 | 18.33 | 24.71 | 12.8 | 7.22 | 0.009385 | 0.0085
VAV_2_COOLC | 0.12107 | 198.37 | 24.7 | 12.8 | 7.22 | 0.00931 | 0.0085
VAV_3_COOLC | 0.01293 | 20.92 | 24.69 | 12.8 | 7.22 | 0.009385 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 375258.9386 | 682.6853 | 1890.2992 | 0 | 0.0077 | 117547.845 | 161155.0179
February | 334844.9711 | 622.3025 | 1759.2736 | 0 | 0.0072 | 109404.6572 | 145000.7004
March | 374933.7523 | 718.8163 | 2091.4271 | 0 | 0.0085 | 130067.8322 | 164373.1706
April | 341364.5131 | 663.9734 | 1956.7142 | 0 | 0.0079 | 121692.92 | 150526.2867
May | 355880.3737 | 703.6353 | 2103.018 | 0 | 0.0085 | 130795.4446 | 157972.0325
June | 365559.9806 | 728.5459 | 2192.091 | 0 | 0.0088 | 136336.994 | 162796.5369
July | 367676.0018 | 733.6736 | 2209.8073 | 0 | 0.0089 | 137439.1239 | 163822.1294
August | 394130.4673 | 785.992 | 2366.2103 | 0 | 0.0095 | 147166.4856 | 175566.26
September | 340157.5431 | 674.3227 | 2019.9025 | 0 | 0.0081 | 125626.6788 | 151155.0354
October | 350697.7368 | 686.9911 | 2037.0694 | 0 | 0.0082 | 126691.9146 | 155086.5654
November | 346886.2421 | 666.7779 | 1944.5482 | 0 | 0.0079 | 120933.8396 | 152235.5141
December | 367531.0666 | 679.8607 | 1913.4021 | 0 | 0.0078 | 118988.436 | 158863.509
Annual Sum or Average | 4314921.5871 | 8347.5767 | 24483.7629 | 0 | 0.0991 | 1522692.1715 | 1898552.7581
Minimum of Months | 334844.9711 | 622.3025 | 1759.2736 | 0 | 0.0072 | 109404.6572 | 145000.7004
Maximum of Months | 394130.4673 | 785.992 | 2366.2103 | 0 | 0.0095 | 147166.4856 | 175566.26
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1863890000000 | 1512414.815 | 04-JAN-13:45 | 448566.543 | 336424.909 | 279697.918 | 0 | 297674.811 | 0 | 96327.482 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1734760000000 | 1513099.747 | 16-FEB-13:15 | 448566.543 | 336424.909 | 280452.043 | 0 | 297674.811 | 0 | 96258.29 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2062410000000 | 1565142.427 | 09-MAR-15:00 | 448566.543 | 336424.909 | 276612.858 | 0 | 353685.426 | 0 | 96129.538 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1929610000000 | 1559751.004 | 04-APR-15:00 | 448566.543 | 336424.909 | 276247.372 | 0 | 348663.918 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2073950000000 | 1676750.504 | 31-MAY-15:00 | 448566.543 | 336424.909 | 277506.505 | 0 | 464404.286 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2161810000000 | 1799525.369 | 30-JUN-15:15 | 448566.543 | 336424.909 | 287102.063 | 0 | 577583.592 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2179290000000 | 1845444.195 | 25-JUL-13:30 | 448566.543 | 336424.909 | 288209.851 | 0 | 622394.631 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2333530000000 | 1904831.195 | 09-AUG-14:45 | 448566.543 | 336424.909 | 289699.346 | 0 | 680292.136 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1991990000000 | 1676316.759 | 05-SEP-10:30 | 448566.543 | 336424.909 | 282704.078 | 0 | 458772.968 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 2008880000000 | 1617350.532 | 12-OCT-14:30 | 448566.543 | 336424.909 | 285090.469 | 0 | 397420.35 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1917580000000 | 1589079.288 | 03-NOV-13:00 | 448566.543 | 336424.909 | 280985.38 | 0 | 373254.196 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1886730000000 | 1512657.145 | 06-DEC-13:30 | 448566.543 | 336424.909 | 279970.61 | 0 | 297674.811 | 0 | 96297.12 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 24144400000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1734760000000 | 1512414.815 |  | 448566.543 | 336424.909 | 276247.372 | 0 | 297674.811 | 0 | 96125.109 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2333530000000 | 1904831.195 |  | 448566.543 | 336424.909 | 289699.346 | 0 | 680292.136 | 0 | 96327.482 | 53723.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 447282.92 | 47803.97 | 0 | 495086.9
Cost per Total Building Area ($/m2) | 9.66 | 1.03 | 0 | 10.69
Cost per Net Conditioned Building Area ($/m2) | 9.66 | 1.03 | 0 | 10.69
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 31668.18 | 683.68 | 683.68
Net Site Energy | 31668.18 | 683.68 | 683.68
Total Source Energy | 97726.83 | 2109.8 | 2109.8
Net Source Energy | 97726.83 | 2109.8 | 2109.8
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3041.22 | 0 | 0 | 0 | 0
Cooling | 7085.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5885.78 | 0 | 0 | 0 | 0 | 0
Pumps | 2908.38 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1324.97 | 0 | 0 | 0 | 0 | 35479.47
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 259.85 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 28367.11 | 3301.07 | 0 | 0 | 0 | 36983.41
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 28367.11 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 28367.11 | 100
Total On-Site and Utility Electric Sources | 28367.11 | 100
Total Electricity End Uses | 28367.11 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 6352414.12 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15053524.66 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 6223938.33
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.8 | 20951.51 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 21.41 | 57514.87 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 230.53 | 619296.67 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 23.61 | 63417.61 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 86034.51 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 58211.08 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 87842.21 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.008781 | 403759.7 | 14294.84
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013338 | 613294.4 | 21713.28
CORE_MID VAV BOX REHEAT COIL | 0.14273 | 6562888.46 | 232354.66
CORE_TOP VAV BOX REHEAT COIL | 0.014306 | 657785.35 | 23288.45
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.0023 | 105757.16 | 3744.26
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002545 | 117024.36 | 4143.17
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.002941 | 135245.86 | 4788.29
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002981 | 137055.7 | 4852.37
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.024489 | 1125990.89 | 39864.95
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.027674 | 1272431.87 | 45049.6
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.032041 | 1473226.42 | 52158.59
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.032623 | 1500018.77 | 53107.16
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002782 | 127915.54 | 4528.76
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002698 | 124047.94 | 4391.83
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003322 | 152735.71 | 5407.51
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003472 | 159645.49 | 5652.14
VAV_5_HEATC | 0.000413 | 19000.39 | 307.86
VAV_1_HEATC | 0.000703 | 32335.18 | 530.23
VAV_2_HEATC | 0.006594 | 303194.15 | 4985.14
VAV_3_HEATC | 0.000656 | 30171.32 | 496.35
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.006157 | 7.8 | 24.13 | 12.8 | 7.22 | 0.008447 | 0.004224
VAV_1_COOLC | 0.017272 | 21.41 | 24.62 | 12.8 | 7.22 | 0.008437 | 0.004218
VAV_2_COOLC | 0.18558 | 230.53 | 24.61 | 12.8 | 7.22 | 0.008408 | 0.004204
VAV_3_COOLC | 0.018834 | 23.61 | 24.61 | 12.8 | 7.22 | 0.008246 | 0.004123
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 639943.5766 | 1091.0354 | 2763.9413 | 0 | 0.0108 | 2873872.1438 | 271526.1146
February | 567578.665 | 975.0104 | 2491.1736 | 0 | 0.0097 | 2590304.889 | 241542.8096
March | 656135.7039 | 1133.6854 | 2915.3024 | 0 | 0.0114 | 3031354.3006 | 279872.0586
April | 619338.5036 | 1078.1972 | 2795.5989 | 0 | 0.0109 | 2906938.4855 | 264969.9843
May | 665346.6355 | 1164.4242 | 3036.463 | 0 | 0.0118 | 3157434.7502 | 285255.0251
June | 665511.0723 | 1166.1713 | 3045.1118 | 0 | 0.0119 | 3166437.3708 | 285468.6639
July | 653590.4376 | 1145.7576 | 2993.1373 | 0 | 0.0117 | 3112395.095 | 280401.9166
August | 694895.2681 | 1217.8446 | 3180.5556 | 0 | 0.0124 | 3307278.81 | 298090.9181
September | 626211.283 | 1096.2094 | 2859.3536 | 0 | 0.0111 | 2973271.1236 | 268503.541
October | 649656.5417 | 1130.9053 | 2932.0596 | 0 | 0.0114 | 3048833.4255 | 277933.7977
November | 615067.0335 | 1060.9189 | 2723.0475 | 0 | 0.0106 | 2831434.4207 | 262177.123
December | 618974.3775 | 1055.4822 | 2674.4411 | 0 | 0.0105 | 2780813.5614 | 262648.2768
Annual Sum or Average | 7672249.0984 | 13315.6418 | 34410.1857 | 0 | 0.1343 | 35780400 | 3278390.2293
Minimum of Months | 567578.665 | 975.0104 | 2491.1736 | 0 | 0.0097 | 2590304.889 | 241542.8096
Maximum of Months | 694895.2681 | 1217.8446 | 3180.5556 | 0 | 0.0124 | 3307278.81 | 298090.9181
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2278440000000 | 1796094.548 | 27-JAN-13:45 | 448566.543 | 336424.909 | 330641.469 | 0 | 452631.938 | 0 | 146140.498 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 2053620000000 | 1796269.412 | 14-FEB-13:00 | 448566.543 | 336424.909 | 330828.605 | 0 | 452631.938 | 0 | 146128.227 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2403290000000 | 1796327.004 | 01-MAR-13:00 | 448566.543 | 336424.909 | 330887.435 | 0 | 452631.938 | 0 | 146126.989 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 2304660000000 | 1797238.734 | 21-APR-15:30 | 448566.543 | 336424.909 | 331800.158 | 0 | 452631.938 | 0 | 146125.996 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2503250000000 | 1814356.155 | 31-MAY-15:00 | 448566.543 | 336424.909 | 332974.274 | 0 | 468575.243 | 0 | 146125.996 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2510390000000 | 1890646.448 | 29-JUN-15:30 | 448566.543 | 336424.909 | 377808.544 | 0 | 500031.266 | 0 | 146125.996 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2467540000000 | 1905469.793 | 03-JUL-15:15 | 448566.543 | 336424.909 | 376921.348 | 0 | 515741.807 | 0 | 146125.996 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2622050000000 | 1891100.191 | 01-AUG-14:30 | 448566.543 | 336424.909 | 349739.255 | 0 | 528554.298 | 0 | 146125.996 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 2357250000000 | 1835874.744 | 05-SEP-13:45 | 448566.543 | 336424.909 | 332468.569 | 0 | 490599.536 | 0 | 146125.996 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 2417150000000 | 1798831.688 | 02-OCT-10:00 | 448566.543 | 336424.909 | 333391.747 | 0 | 452631.938 | 0 | 146127.36 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 2244800000000 | 1795634.242 | 01-NOV-13:30 | 448566.543 | 336424.909 | 330193.692 | 0 | 452631.938 | 0 | 146127.97 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 2204660000000 | 1794597.808 | 05-DEC-13:30 | 448566.543 | 336424.909 | 329095.918 | 0 | 452631.938 | 0 | 146189.309 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 28367100000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 2053620000000 | 1794597.808 |  | 448566.543 | 336424.909 | 329095.918 | 0 | 452631.938 | 0 | 146125.996 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2622050000000 | 1905469.793 |  | 448566.543 | 336424.909 | 377808.544 | 0 | 528554.298 | 0 | 146189.309 | 81689.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 291174.14 | 22823.25 | 0 | 313997.39
Cost per Total Building Area ($/m2) | 6.29 | 0.49 | 0 | 6.78
Cost per Net Conditioned Building Area ($/m2) | 6.29 | 0.49 | 0 | 6.78
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 27556.89 | 594.92 | 594.92
Net Site Energy | 27556.89 | 594.92 | 594.92
Total Source Energy | 44742.19 | 965.93 | 965.93
Net Source Energy | 44742.19 | 965.93 | 965.93
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4740.14 | 0 | 0 | 0 | 0
Cooling | 4280.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4717.37 | 0 | 0 | 0 | 0 | 0
Pumps | 1564.75 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 813.83 | 0 | 0 | 0 | 0 | 12289.86
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 278.17 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 22538.58 | 5018.31 | 0 | 0 | 0 | 13793.8
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 22538.58 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 22538.58 | 100
Total On-Site and Utility Electric Sources | 22538.58 | 100
Total Electricity End Uses | 22538.58 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3439732.3 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15032510.42 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3370164.68
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 6.98 | 18753 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 17.88 | 48034.17 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 192.63 | 517476.14 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 18.1 | 48633.38 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 85914.41 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31520.39 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 47565.17 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.00942 | 433122.86 | 15334.42
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013515 | 621430.02 | 22001.31
CORE_MID VAV BOX REHEAT COIL | 0.14455 | 6646226 | 235305.17
CORE_TOP VAV BOX REHEAT COIL | 0.012897 | 593025.95 | 20995.69
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.001676 | 77064.89 | 2728.43
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002377 | 109297.03 | 3869.59
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003816 | 175478.17 | 6212.69
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002743 | 126136.18 | 4465.77
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.017612 | 809805.95 | 28670.64
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.025432 | 1169350.44 | 41400.07
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.042428 | 1950861.55 | 69068.94
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.029915 | 1375483.5 | 48698.07
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002199 | 101109.29 | 3579.71
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002376 | 109261.7 | 3868.34
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.004223 | 194187.07 | 6875.06
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003087 | 141917.31 | 5024.49
VAV_5_HEATC | 0.000407 | 18722.48 | 304.11
VAV_1_HEATC | 0.000719 | 33047.24 | 541.69
VAV_2_HEATC | 0.006828 | 313940.61 | 5158.71
VAV_3_HEATC | 0.000719 | 33042.2 | 541.76
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003593 | 6.98 | 23.77 | 12.8 | 7.22 | 0.008851 | 0.0085
VAV_1_COOLC | 0.009444 | 17.88 | 24.29 | 12.8 | 7.22 | 0.008767 | 0.0085
VAV_2_COOLC | 0.10085 | 192.63 | 24.31 | 12.8 | 7.22 | 0.008718 | 0.0085
VAV_3_COOLC | 0.009483 | 18.1 | 24.25 | 12.8 | 7.22 | 0.008744 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 136932.6024 | 187.7378 | 405.6368 | 0 | 0.0017 | 5358746.4944 | 54187.2067
February | 113038.667 | 160.0035 | 366.9386 | 0 | 0.0015 | 4848253.9612 | 45270.028
March | 125213.5654 | 180.1126 | 424.8214 | 0 | 0.0017 | 5613428.3844 | 50453.865
April | 107966.8254 | 159.1422 | 390.8122 | 0 | 0.0016 | 5164535.2113 | 43915.4762
May | 102900.8917 | 158.4603 | 415.7974 | 0 | 0.0016 | 5495526.3649 | 42581.6147
June | 98313.2432 | 153.8035 | 412.6341 | 0 | 0.0016 | 5453975.9982 | 40941.0828
July | 93728.7703 | 148.0428 | 402.4036 | 0 | 0.0016 | 5318900.3572 | 39183.1026
August | 101711.9902 | 160.4167 | 435.1745 | 0 | 0.0017 | 5752036.9409 | 42495.2539
September | 99133.7894 | 152.3364 | 398.5148 | 0 | 0.0016 | 5267069.9885 | 40988.1763
October | 110088.4977 | 162.6017 | 400.6131 | 0 | 0.0016 | 5294093.0687 | 44814.0443
November | 121241.9725 | 171.5157 | 392.9329 | 0 | 0.0016 | 5191695.9436 | 48544.6628
December | 134387.0382 | 183.6217 | 394.0983 | 0 | 0.0016 | 5206223.5154 | 53112.8129
Annual Sum or Average | 1344657.8535 | 1977.7949 | 4840.3777 | 0 | 0.0193 | 63964500 | 546487.326
Minimum of Months | 93728.7703 | 148.0428 | 366.9386 | 0 | 0.0015 | 4848253.9612 | 39183.1026
Maximum of Months | 136932.6024 | 187.7378 | 435.1745 | 0 | 0.0017 | 5752036.9409 | 54187.2067
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1888210000000 | 1423032.09 | 09-JAN-16:00 | 448566.543 | 336424.909 | 265063.448 | 0 | 245093.073 | 3997.501 | 79653.206 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1708330000000 | 1423323.238 | 24-FEB-13:45 | 448566.543 | 336424.909 | 269814.504 | 0 | 245093.073 | 0 | 79190.798 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1977950000000 | 1451257.737 | 29-MAR-14:30 | 448566.543 | 336424.909 | 269035.882 | 0 | 273838.727 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1819780000000 | 1447359.348 | 18-APR-15:30 | 448566.543 | 336424.909 | 270284.324 | 0 | 268691.896 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 1936410000000 | 1488310.206 | 05-MAY-15:00 | 448566.543 | 336424.909 | 265993.052 | 0 | 313934.026 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 1921770000000 | 1515174.602 | 28-JUN-14:30 | 448566.543 | 336424.909 | 273795.428 | 0 | 332996.046 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1874170000000 | 1567606.401 | 31-JUL-15:00 | 448566.543 | 336424.909 | 277639.628 | 0 | 381583.645 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2026790000000 | 1551779.608 | 07-AUG-14:00 | 448566.543 | 336424.909 | 278497.825 | 0 | 364898.656 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1855910000000 | 1553820.855 | 01-SEP-15:45 | 448566.543 | 336424.909 | 276191.962 | 0 | 369245.766 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1865430000000 | 1466538.053 | 02-OCT-14:45 | 448566.543 | 336424.909 | 273240.651 | 0 | 284914.274 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1829350000000 | 1436373.427 | 03-NOV-16:00 | 448566.543 | 336424.909 | 265063.448 | 0 | 258747.322 | 3997.501 | 79340.294 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1834470000000 | 1422990.452 | 22-DEC-16:15 | 448566.543 | 336424.909 | 265063.448 | 0 | 245093.073 | 3997.501 | 79611.568 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 22538600000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1708330000000 | 1422990.452 |  | 448566.543 | 336424.909 | 265063.448 | 0 | 245093.073 | 0 | 79158.264 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2026790000000 | 1567606.401 |  | 448566.543 | 336424.909 | 278497.825 | 0 | 381583.645 | 3997.501 | 79653.206 | 44233.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 436184.95 | 42205.5 | 0 | 478390.44
Cost per Total Building Area ($/m2) | 9.42 | 0.91 | 0 | 10.33
Cost per Net Conditioned Building Area ($/m2) | 9.42 | 0.91 | 0 | 10.33
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 29794.62 | 643.23 | 643.23
Net Site Energy | 29794.62 | 643.23 | 643.23
Total Source Energy | 90186.87 | 1947.02 | 1947.02
Net Source Energy | 90186.87 | 1947.02 | 1947.02
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 6014.58 | 0 | 0 | 0 | 0
Cooling | 4625.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5174.58 | 0 | 0 | 0 | 0 | 0
Pumps | 1787.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 742.2 | 0 | 0 | 0 | 0 | 15112.72
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 287.32 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 23492.72 | 6301.89 | 0 | 0 | 0 | 16616.67
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 23492.72 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 23492.72 | 100
Total On-Site and Utility Electric Sources | 23492.72 | 100
Total Electricity End Uses | 23492.72 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4128281.96 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15963894.33 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4044788.62
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.21 | 19367.09 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 18.45 | 49549.97 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 199.06 | 534736.78 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 20.64 | 55435.03 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 91237.49 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37829.99 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 57086.55 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.00965 | 443701.72 | 15708.96
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013916 | 639856.57 | 22653.69
CORE_MID VAV BOX REHEAT COIL | 0.14736 | 6775727.97 | 239890.1
CORE_TOP VAV BOX REHEAT COIL | 0.015165 | 697270.86 | 24686.41
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002068 | 95076.97 | 3366.14
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002541 | 116818.05 | 4135.86
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003287 | 151146.89 | 5351.25
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002877 | 132295.3 | 4683.83
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.023512 | 1081079.35 | 38274.89
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.027739 | 1275427.48 | 45155.65
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.036232 | 1665928.83 | 58981.09
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.031594 | 1452699.58 | 51431.85
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.003095 | 142306.64 | 5038.27
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002723 | 125223.59 | 4433.46
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003749 | 172401.82 | 6103.77
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003355 | 154267.62 | 5461.74
VAV_5_HEATC | 0.000796 | 36596.84 | 569.13
VAV_1_HEATC | 0.001496 | 68783.32 | 1105.33
VAV_2_HEATC | 0.014596 | 671141.29 | 10822.19
VAV_3_HEATC | 0.001439 | 66143.63 | 1068.4
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.004467 | 7.21 | 24.21 | 12.8 | 7.22 | 0.009688 | 0.0085
VAV_1_COOLC | 0.011245 | 18.45 | 24.58 | 12.8 | 7.22 | 0.009448 | 0.0085
VAV_2_COOLC | 0.11968 | 199.06 | 24.58 | 12.8 | 7.22 | 0.00937 | 0.0085
VAV_3_COOLC | 0.012677 | 20.64 | 24.58 | 12.8 | 7.22 | 0.00949 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 693080.2417 | 1190.876 | 3370.5037 | 0 | 0.0103 | 775835.8391 | 293586.8016
February | 616908.8948 | 1075.8268 | 3094.9802 | 0 | 0.0094 | 712437.8773 | 262834.4677
March | 707112.7682 | 1252.2518 | 3662.136 | 0 | 0.0111 | 843019.3633 | 303093.8284
April | 673730.9273 | 1208.5644 | 3581.7489 | 0 | 0.0108 | 824535.5225 | 290260.429
May | 713611.0205 | 1291.9093 | 3864.5392 | 0 | 0.0117 | 889650.9595 | 308570.6047
June | 722955.1683 | 1314.46 | 3948.9181 | 0 | 0.0119 | 909083.12 | 313149.7788
July | 724393.6923 | 1317.6198 | 3960.0386 | 0 | 0.0119 | 911643.8944 | 313824.9216
August | 762500.7233 | 1386.3597 | 4164.9167 | 0 | 0.0126 | 958808.3098 | 330278.9249
September | 684036.2119 | 1240.1078 | 3714.8104 | 0 | 0.0112 | 855184.3499 | 295948.6338
October | 692785.6036 | 1246.3147 | 3704.4459 | 0 | 0.0112 | 852785.7168 | 298810.9284
November | 667120.1232 | 1183.2791 | 3466.1149 | 0 | 0.0105 | 797898.0822 | 286128.5974
December | 697556.9803 | 1207.6828 | 3446.9149 | 0 | 0.0105 | 793437.7826 | 296354.6018
Annual Sum or Average | 8355792.3553 | 14915.2522 | 43980.0676 | 0 | 0.1332 | 10124300 | 3592842.5181
Minimum of Months | 616908.8948 | 1075.8268 | 3094.9802 | 0 | 0.0094 | 712437.8773 | 262834.4677
Maximum of Months | 762500.7233 | 1386.3597 | 4164.9167 | 0 | 0.0126 | 958808.3098 | 330278.9249
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1800270000000 | 1503747.575 | 17-JAN-13:15 | 448566.543 | 336424.909 | 276119.382 | 0 | 294154.667 | 0 | 95394.222 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1653160000000 | 1507033.539 | 16-FEB-14:15 | 448566.543 | 336424.909 | 279676.544 | 0 | 294154.667 | 0 | 95123.025 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1956160000000 | 1515731.538 | 31-MAR-14:00 | 448566.543 | 336424.909 | 277405.812 | 0 | 305257.179 | 0 | 94989.245 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1913270000000 | 1527778.798 | 03-APR-13:00 | 448566.543 | 336424.909 | 276020.203 | 0 | 318651.91 | 0 | 95027.382 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2064370000000 | 1659384.746 | 30-MAY-15:00 | 448566.543 | 336424.909 | 282656.815 | 0 | 443659.384 | 0 | 94989.245 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2109460000000 | 1783430.985 | 08-JUN-12:00 | 448566.543 | 336424.909 | 284397.647 | 0 | 565964.791 | 0 | 94989.245 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2115400000000 | 1777780.064 | 13-JUL-13:30 | 448566.543 | 336424.909 | 287453.483 | 0 | 557258.034 | 0 | 94989.245 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2224840000000 | 1839011.747 | 04-AUG-15:30 | 448566.543 | 336424.909 | 287248.689 | 0 | 618694.51 | 0 | 94989.245 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1984390000000 | 1641694.809 | 06-SEP-12:45 | 448566.543 | 336424.909 | 284292.084 | 0 | 424334.178 | 0 | 94989.245 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1978830000000 | 1581447.414 | 30-OCT-11:00 | 448566.543 | 336424.909 | 281575.839 | 0 | 366794.957 | 0 | 94997.315 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1851460000000 | 1573680.2 | 02-NOV-14:30 | 448566.543 | 336424.909 | 277229.63 | 0 | 363381.825 | 0 | 94989.441 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1841110000000 | 1507515.777 | 12-DEC-16:15 | 448566.543 | 336424.909 | 275976.661 | 0 | 294154.667 | 3997.501 | 95307.645 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 23492700000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1653160000000 | 1503747.575 |  | 448566.543 | 336424.909 | 275976.661 | 0 | 294154.667 | 0 | 94989.245 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2224840000000 | 1839011.747 |  | 448566.543 | 336424.909 | 287453.483 | 0 | 618694.51 | 3997.501 | 95394.222 | 53087.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 594735.46 | 52620.19 | 0 | 647355.66
Cost per Total Building Area ($/m2) | 12.84 | 1.14 | 0 | 13.98
Cost per Net Conditioned Building Area ($/m2) | 12.84 | 1.14 | 0 | 13.98
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 31703.74 | 684.44 | 684.44
Net Site Energy | 31703.74 | 684.44 | 684.44
Total Source Energy | 94778.04 | 2046.14 | 2046.14
Net Source Energy | 94778.04 | 2046.14 | 2046.14
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4392.64 | 0 | 0 | 0 | 0
Cooling | 6182.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5874.12 | 0 | 0 | 0 | 0 | 0
Pumps | 2681.46 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1124.7 | 0 | 0 | 0 | 0 | 28379.59
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 286.14 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 27024.96 | 4678.78 | 0 | 0 | 0 | 29883.53
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 27024.96 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 27024.96 | 100
Total On-Site and Utility Electric Sources | 27024.96 | 100
Total Electricity End Uses | 27024.96 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 5967871.97 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15218290.64 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 5847173.44
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.84 | 21063.58 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 21.22 | 57002.53 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 229.76 | 617210.22 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 22.87 | 61425.36 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 86976.19 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 54687.29 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 82524.7 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.008812 | 405170.63 | 14344.79
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013283 | 610735.67 | 21622.69
CORE_MID VAV BOX REHEAT COIL | 0.14309 | 6579193.06 | 232931.92
CORE_TOP VAV BOX REHEAT COIL | 0.013756 | 632511.35 | 22393.64
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002153 | 98997.63 | 3504.94
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002411 | 110854.37 | 3924.72
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003129 | 143890.09 | 5094.33
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002871 | 132000.08 | 4673.37
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.022834 | 1049927.1 | 37171.96
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.026259 | 1207373.05 | 42746.23
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.034475 | 1585176.81 | 56122.12
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.031552 | 1450739.51 | 51362.46
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.002866 | 131780.06 | 4665.58
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002506 | 115225.69 | 4079.49
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003524 | 162048.96 | 5737.23
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003338 | 153466.44 | 5433.38
VAV_5_HEATC | 0.00064 | 29419.19 | 464.88
VAV_1_HEATC | 0.001159 | 53270.23 | 862.27
VAV_2_HEATC | 0.01119 | 514531.82 | 8356.48
VAV_3_HEATC | 0.00113 | 51978.91 | 843.87
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003156 | 7.84 | 23.82 | 12.8 | 7.22 | 0.008541 | 0.0085
VAV_1_COOLC | 0.008942 | 21.22 | 24.42 | 12.8 | 7.22 | 0.008511 | 0.0085
VAV_2_COOLC | 0.18382 | 229.76 | 24.42 | 12.8 | 7.22 | 0.008476 | 0.004238
VAV_3_COOLC | 0.018136 | 22.87 | 24.44 | 12.8 | 7.22 | 0.008313 | 0.004156
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 620538.4622 | 1045.2267 | 2611.2556 | 0 | 0.0103 | 2715028.2456 | 262044.3936
February | 546389.7789 | 929.3028 | 2347.791 | 0 | 0.0092 | 2441155.225 | 231612.4588
March | 641073.4173 | 1101.4462 | 2814.7441 | 0 | 0.011 | 2926752.4579 | 272837.7522
April | 588044.4996 | 1019.5371 | 2631.7141 | 0 | 0.0103 | 2736499.8262 | 251171.4617
May | 633585.8371 | 1104.1964 | 2866.3839 | 0 | 0.0112 | 2980550.2564 | 271182.7229
June | 634727.0431 | 1109.8785 | 2891.5366 | 0 | 0.0113 | 3006728.4658 | 272033.444
July | 629056.9663 | 1102.1036 | 2877.2872 | 0 | 0.0112 | 2991925.0506 | 269813.223
August | 663004.4526 | 1161.0902 | 3029.9148 | 0 | 0.0118 | 3150630.5462 | 284325.9022
September | 616520.3553 | 1076.3216 | 2799.2808 | 0 | 0.0109 | 2910786.4511 | 264061.5624
October | 626142.8878 | 1086.3686 | 2806.4258 | 0 | 0.011 | 2918172.989 | 267520.6786
November | 592679.2737 | 1015.4728 | 2586.965 | 0 | 0.0101 | 2689890.5808 | 251964.2289
December | 597400.3482 | 1007.2398 | 2519.2293 | 0 | 0.0099 | 2619351.5868 | 252370.2792
Annual Sum or Average | 7389163.3221 | 12758.1844 | 32782.5283 | 0 | 0.1281 | 34087500 | 3150938.1076
Minimum of Months | 546389.7789 | 929.3028 | 2347.791 | 0 | 0.0092 | 2441155.225 | 231612.4588
Maximum of Months | 663004.4526 | 1161.0902 | 3029.9148 | 0 | 0.0118 | 3150630.5462 | 284325.9022
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2152510000000 | 1747587.918 | 26-JAN-14:15 | 448566.543 | 336424.909 | 323294.19 | 0 | 425231.952 | 0 | 137326.173 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1935380000000 | 1750159.256 | 23-FEB-13:45 | 448566.543 | 336424.909 | 325868.316 | 0 | 425231.952 | 0 | 137323.385 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2320360000000 | 1750942.149 | 27-MAR-13:45 | 448566.543 | 336424.909 | 326689.905 | 0 | 425231.952 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 2169530000000 | 1749967.64 | 26-APR-10:00 | 448566.543 | 336424.909 | 325714.085 | 0 | 425231.952 | 0 | 137286 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2363020000000 | 1761945.152 | 24-MAY-15:30 | 448566.543 | 336424.909 | 326874.389 | 0 | 436050.471 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2383770000000 | 1830752.985 | 27-JUN-15:15 | 448566.543 | 336424.909 | 368739.371 | 0 | 462993.322 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2372030000000 | 1846441.607 | 18-JUL-13:00 | 448566.543 | 336424.909 | 367133.433 | 0 | 480287.882 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2497860000000 | 1844923.768 | 30-AUG-13:45 | 448566.543 | 336424.909 | 368461.42 | 0 | 477442.056 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 2307710000000 | 1777491.75 | 06-SEP-14:30 | 448566.543 | 336424.909 | 331384.012 | 0 | 447087.446 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 2313560000000 | 1769066.88 | 05-OCT-14:00 | 448566.543 | 336424.909 | 332945.681 | 0 | 437100.908 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 2132580000000 | 1750841.477 | 01-NOV-13:30 | 448566.543 | 336424.909 | 326581.083 | 0 | 425231.952 | 0 | 137292.838 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 2076650000000 | 1748613.692 | 22-DEC-13:30 | 448566.543 | 336424.909 | 324276.661 | 0 | 425231.952 | 0 | 137369.476 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 27025000000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1935380000000 | 1747587.918 |  | 448566.543 | 336424.909 | 323294.19 | 0 | 425231.952 | 0 | 137284.688 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2497860000000 | 1846441.607 |  | 448566.543 | 336424.909 | 368739.371 | 0 | 480287.882 | 0 | 137369.476 | 76744.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 277406.77 | 32457.59 | 0 | 309864.35
Cost per Total Building Area ($/m2) | 5.99 | 0.7 | 0 | 6.69
Cost per Net Conditioned Building Area ($/m2) | 5.99 | 0.7 | 0 | 6.69
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 31414.24 | 678.19 | 678.19
Net Site Energy | 31414.24 | 678.19 | 678.19
Total Source Energy | 88150.54 | 1903.06 | 1903.06
Net Source Energy | 88150.54 | 1903.06 | 1903.06
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 8145.27 | 0 | 0 | 0 | 0
Cooling | 4114.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5408.22 | 0 | 0 | 0 | 0 | 0
Pumps | 1627.06 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 650.2 | 0 | 0 | 0 | 0 | 13352.45
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 306.83 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 22962.13 | 8452.11 | 0 | 0 | 0 | 14856.39
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 22962.13 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 22962.13 | 100
Total On-Site and Utility Electric Sources | 22962.13 | 100
Total Electricity End Uses | 22962.13 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4013544.12 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 16018707.6 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3932371.31
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 6.98 | 18756.24 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 18.44 | 49545.58 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 199.07 | 534782.7 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 20.7 | 55597.87 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 91550.76 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 36778.58 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 55499.94 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.009273 | 426391.53 | 15096.11
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013665 | 628313.82 | 22245.03
CORE_MID VAV BOX REHEAT COIL | 0.14463 | 6650133.27 | 235443.51
CORE_TOP VAV BOX REHEAT COIL | 0.015344 | 705496.45 | 24977.63
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002017 | 92744.95 | 3283.57
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002524 | 116045.38 | 4108.51
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.003433 | 157836.52 | 5588.1
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002858 | 131394.9 | 4651.95
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.022873 | 1051707.33 | 37234.99
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.027533 | 1265989.18 | 44821.5
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.037979 | 1746279.68 | 61825.86
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.031389 | 1443277.17 | 51098.26
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.00339 | 155885.85 | 5519.03
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002701 | 124173.17 | 4396.27
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003924 | 180435.56 | 6388.2
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003328 | 153013.85 | 5417.35
VAV_5_HEATC | 0.00093 | 42757.7 | 647.26
VAV_1_HEATC | 0.001751 | 80494.7 | 1274.4
VAV_2_HEATC | 0.01715 | 788577.02 | 12628.51
VAV_3_HEATC | 0.001691 | 77759.55 | 1248.92
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.004195 | 6.98 | 24.21 | 12.8 | 7.22 | 0.009559 | 0.0085
VAV_1_COOLC | 0.010948 | 18.44 | 24.59 | 12.8 | 7.22 | 0.009336 | 0.0085
VAV_2_COOLC | 0.11617 | 199.07 | 24.59 | 12.8 | 7.22 | 0.009243 | 0.0085
VAV_3_COOLC | 0.012643 | 20.7 | 24.58 | 12.8 | 7.22 | 0.009501 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 483505.9483 | 773.2609 | 1091.0243 | 0 | 0.0082 | 716777.5931 | 199304.5047
February | 411679.4481 | 683.7719 | 1011.5954 | 0 | 0.0075 | 664718.718 | 172123.2656
March | 471043.6821 | 818.0253 | 1273.5608 | 0 | 0.0094 | 837016.0828 | 200351.4548
April | 435166.0851 | 775.3513 | 1240.4832 | 0 | 0.0091 | 815356.6791 | 186967.9961
May | 468052.8709 | 846.9836 | 1376.6798 | 0 | 0.01 | 904927.7609 | 202343.8564
June | 461111.873 | 838.9957 | 1371.1531 | 0 | 0.01 | 901312.0392 | 199780.2637
July | 462236.2778 | 841.9502 | 1377.4552 | 0 | 0.01 | 905458.0413 | 200354.2729
August | 487674.1492 | 887.5753 | 1450.95 | 0 | 0.0106 | 953766.5513 | 211312.406
September | 432652.4274 | 782.7312 | 1271.9313 | 0 | 0.0093 | 836073.1316 | 187021.5365
October | 450500.5298 | 801.6418 | 1280.8369 | 0 | 0.0094 | 841876.7745 | 193457.8074
November | 442956.851 | 765.5923 | 1185.7156 | 0 | 0.0087 | 779267.0663 | 188055.603
December | 467073.2742 | 768.7568 | 1124.8513 | 0 | 0.0084 | 739107.6194 | 194612.3663
Annual Sum or Average | 5473653.4169 | 9584.6362 | 15056.2369 | 0 | 0.1107 | 9895658.0576 | 2335685.3333
Minimum of Months | 411679.4481 | 683.7719 | 1011.5954 | 0 | 0.0075 | 664718.718 | 172123.2656
Maximum of Months | 487674.1492 | 887.5753 | 1450.95 | 0 | 0.0106 | 953766.5513 | 211312.406
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1663230000000 | 1367735.144 | 30-JAN-16:00 | 448566.543 | 336424.909 | 275958.949 | 0 | 179316.859 | 0 | 92895.427 | 34572.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1542430000000 | 1408966.271 | 17-FEB-15:00 | 448566.543 | 336424.909 | 275958.949 | 0 | 216234.241 | 0 | 92654.781 | 39126.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1942230000000 | 1496068.058 | 23-MAR-13:30 | 448566.543 | 336424.909 | 281116.444 | 0 | 285979.191 | 0 | 92368.598 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1891970000000 | 1517534.52 | 14-APR-15:30 | 448566.543 | 336424.909 | 280494.87 | 0 | 308084.607 | 0 | 92351.218 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2099820000000 | 1611706.654 | 31-MAY-12:15 | 448566.543 | 336424.909 | 281509.6 | 0 | 401242.01 | 0 | 92351.218 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2091430000000 | 1748947.782 | 29-JUN-14:00 | 448566.543 | 336424.909 | 289013.076 | 0 | 530979.663 | 0 | 92351.218 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2101050000000 | 1770169.498 | 13-JUL-15:00 | 448566.543 | 336424.909 | 284134.132 | 0 | 557080.323 | 0 | 92351.218 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2213140000000 | 1756517.111 | 25-AUG-15:00 | 448566.543 | 336424.909 | 285955.115 | 0 | 541606.953 | 0 | 92351.218 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1940040000000 | 1626616.304 | 14-SEP-14:00 | 448566.543 | 336424.909 | 285894.131 | 0 | 411767.13 | 0 | 92351.218 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1953510000000 | 1527231.518 | 06-OCT-14:00 | 448566.543 | 336424.909 | 282264.244 | 0 | 316011.47 | 0 | 92351.979 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1808230000000 | 1503273.989 | 02-NOV-14:00 | 448566.543 | 336424.909 | 280451.446 | 0 | 293854.497 | 0 | 92364.22 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1715040000000 | 1429090.689 | 01-DEC-14:00 | 448566.543 | 336424.909 | 275958.949 | 0 | 229742.878 | 0 | 92568.857 | 45828.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 22962100000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1542430000000 | 1367735.144 |  | 448566.543 | 336424.909 | 275958.949 | 0 | 179316.859 | 0 | 92351.218 | 34572.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2213140000000 | 1770169.498 |  | 448566.543 | 336424.909 | 289013.076 | 0 | 557080.323 | 0 | 92895.427 | 51612.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 374948.98 | 66673.76 | 0 | 441622.74
Cost per Total Building Area ($/m2) | 8.09 | 1.44 | 0 | 9.53
Cost per Net Conditioned Building Area ($/m2) | 8.09 | 1.44 | 0 | 9.53
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 33161.71 | 715.92 | 715.92
Net Site Energy | 33161.71 | 715.92 | 715.92
Total Source Energy | 98051.29 | 2116.81 | 2116.81
Net Source Energy | 98051.29 | 2116.81 | 2116.81
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 6912.28 | 0 | 0 | 0 | 0
Cooling | 5421.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5752.67 | 0 | 0 | 0 | 0 | 0
Pumps | 2597.32 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1005.4 | 0 | 0 | 0 | 0 | 22387.98
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 310.38 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25939.05 | 7222.66 | 0 | 0 | 0 | 23891.93
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 25939.05 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 25939.05 | 100
Total On-Site and Utility Electric Sources | 25939.05 | 100
Total Electricity End Uses | 25939.05 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 1159.04 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 772.69 | 3.24 | 0.39 | 0.495 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 115.9 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 77.27 | 3.24 | 0.39 | 0.495 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 5965006.71 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 15618109.61 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 5844366.12
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.47 | 20071.93 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 20.18 | 54223.47 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 218.84 | 587893.26 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 21.88 | 58764.91 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 89261.25 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 54661.03 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 82485.07 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.008868 | 407769.62 | 14436.81
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013312 | 612088.7 | 21670.59
CORE_MID VAV BOX REHEAT COIL | 0.14342 | 6594380.41 | 233469.61
CORE_TOP VAV BOX REHEAT COIL | 0.014986 | 689052.59 | 24395.44
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002035 | 93566.98 | 3312.68
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002388 | 109782.95 | 3886.79
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.00342 | 157267.5 | 5567.95
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.002803 | 128865.97 | 4562.41
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.021574 | 991986.02 | 35120.6
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.026021 | 1196458.64 | 42359.82
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.037937 | 1744329.67 | 61756.82
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.030799 | 1416139.78 | 50137.48
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.003326 | 152926.55 | 5414.26
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002448 | 112549.91 | 3984.75
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.003839 | 176534.69 | 6250.09
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003231 | 148574.13 | 5260.17
VAV_5_HEATC | 0.000846 | 38911.8 | 593.24
VAV_1_HEATC | 0.001571 | 72238.01 | 1155.27
VAV_2_HEATC | 0.015309 | 703908.53 | 11321.75
VAV_3_HEATC | 0.001539 | 70777.15 | 1138.23
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003108 | 7.47 | 23.57 | 12.8 | 7.22 | 0.008546 | 0.0085
VAV_1_COOLC | 0.008879 | 20.18 | 24.27 | 12.8 | 7.22 | 0.008517 | 0.0085
VAV_2_COOLC | 0.18379 | 218.84 | 24.28 | 12.8 | 7.22 | 0.008482 | 0.004241
VAV_3_COOLC | 0.018167 | 21.88 | 24.26 | 12.8 | 7.22 | 0.008304 | 0.004152
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 546467.4366 | 894.4039 | 1443.2003 | 0 | 0.0102 | 34226900 | 227641.3738
February | 486628.3059 | 811.934 | 1341.1106 | 0 | 0.0094 | 31808300 | 204209.5307
March | 564396.1118 | 969.8695 | 1657.3485 | 0 | 0.0116 | 39313300 | 239568.2026
April | 511521.2862 | 888.6155 | 1536.826 | 0 | 0.0107 | 36455900 | 218053.1871
May | 554564.2622 | 973.9295 | 1704.2619 | 0 | 0.0118 | 40429300 | 237420.5066
June | 562308.3083 | 992.4643 | 1745.9069 | 0 | 0.0121 | 41417900 | 241212.901
July | 555324.5094 | 983.8846 | 1737.7723 | 0 | 0.012 | 41225500 | 238579.2229
August | 586097.8273 | 1037.0448 | 1829.1462 | 0 | 0.0127 | 43393000 | 251668.4627
September | 541698.0452 | 953.0022 | 1670.7561 | 0 | 0.0116 | 39634700 | 232073.495
October | 542651.3277 | 944.362 | 1636.3836 | 0 | 0.0114 | 38817800 | 231484.5845
November | 513266.8185 | 877.9287 | 1492.4549 | 0 | 0.0104 | 35401300 | 217471.132
December | 535586.7146 | 885.25 | 1445.764 | 0 | 0.0102 | 34289100 | 223945.3875
Annual Sum or Average | 6500510.9538 | 11212.6889 | 19240.9313 | 0 | 0.1341 | 456413000 | 2763327.9863
Minimum of Months | 486628.3059 | 811.934 | 1341.1106 | 0 | 0.0094 | 31808300 | 204209.5307
Maximum of Months | 586097.8273 | 1037.0448 | 1829.1462 | 0 | 0.0127 | 43393000 | 251668.4627
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1945200000000 | 1568493.341 | 24-JAN-13:00 | 448566.543 | 336424.909 | 302006.697 | 0 | 267206.19 | 0 | 137581.696 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1807740000000 | 1731652.8 | 03-FEB-13:00 | 448566.543 | 336424.909 | 307644.09 | 0 | 425027.791 | 0 | 137282.162 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 2234270000000 | 1735531.272 | 28-MAR-15:45 | 448566.543 | 336424.909 | 311584.446 | 0 | 425027.791 | 0 | 137220.278 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 2071880000000 | 1731117.642 | 05-APR-15:45 | 448566.543 | 336424.909 | 307169.428 | 0 | 425027.791 | 0 | 137221.665 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2297690000000 | 1733596.538 | 16-MAY-15:45 | 448566.543 | 336424.909 | 309651.178 | 0 | 425027.791 | 0 | 137218.811 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2353880000000 | 1818395.801 | 26-JUN-15:30 | 448566.543 | 336424.909 | 349474.2 | 0 | 470004.033 | 0 | 137218.811 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2342940000000 | 1828251.69 | 21-JUL-15:45 | 448566.543 | 336424.909 | 352734.136 | 0 | 476599.986 | 0 | 137218.811 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2466130000000 | 1771159.831 | 11-AUG-15:00 | 448566.543 | 336424.909 | 313852.479 | 0 | 458389.784 | 0 | 137218.811 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 2252540000000 | 1757447.055 | 01-SEP-15:00 | 448566.543 | 336424.909 | 316264.444 | 0 | 442265.043 | 0 | 137218.811 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 2206110000000 | 1736367.22 | 06-OCT-13:00 | 448566.543 | 336424.909 | 312420.82 | 0 | 425027.791 | 0 | 137219.851 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 2011940000000 | 1704426.403 | 21-NOV-13:00 | 448566.543 | 336424.909 | 302006.697 | 0 | 403362.73 | 0 | 137358.218 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1948730000000 | 1627934.343 | 01-DEC-13:00 | 448566.543 | 336424.909 | 302011.392 | 0 | 326825.792 | 0 | 137398.402 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 25939100000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1807740000000 | 1568493.341 |  | 448566.543 | 336424.909 | 302006.697 | 0 | 267206.19 | 0 | 137218.811 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2466130000000 | 1828251.69 |  | 448566.543 | 336424.909 | 352734.136 | 0 | 476599.986 | 0 | 137581.696 | 76707.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 538655.67 | 58697.16 | 0 | 597352.83
Cost per Total Building Area ($/m2) | 11.63 | 1.27 | 0 | 12.9
Cost per Net Conditioned Building Area ($/m2) | 11.63 | 1.27 | 0 | 12.9
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 33053.02 | 713.57 | 713.57
Net Site Energy | 33053.02 | 713.57 | 713.57
Total Source Energy | 89730.43 | 1937.17 | 1937.17
Net Source Energy | 89730.43 | 1937.17 | 1937.17
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 9841.27 | 0 | 0 | 0 | 0
Cooling | 3738.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 5820.01 | 0 | 0 | 0 | 0 | 0
Pumps | 1559.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 592.76 | 0 | 0 | 0 | 0 | 10765.29
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 339.03 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 22872.72 | 10180.3 | 0 | 0 | 0 | 12269.23
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 22872.72 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 22872.72 | 100
Total On-Site and Utility Electric Sources | 22872.72 | 100
Total Electricity End Uses | 22872.72 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 115.9 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 77.27 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 115.9 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 77.27 | 3.24 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 1159.04 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 772.69 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 1159.04 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 772.69 | 3.24 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 115.9 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 77.27 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 115.9 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 77.27 | 3.24 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3866961.33 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 16559465.64 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3788753.12
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.09 | 19040.66 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 19.4 | 52114.81 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 210.21 | 564697.34 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 21.07 | 56608.64 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 94641.32 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35435.35 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 53472.96 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.009217 | 423798.95 | 15004.32
CORE_BOTTOM VAV BOX REHEAT COIL | 0.013586 | 624667.81 | 22115.94
CORE_MID VAV BOX REHEAT COIL | 0.14592 | 6709358.04 | 237540.32
CORE_TOP VAV BOX REHEAT COIL | 0.015838 | 728228.83 | 25782.45
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002076 | 95477.27 | 3380.31
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.00275 | 126456.22 | 4477.1
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.00366 | 168279.38 | 5957.82
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.003155 | 145068.82 | 5136.06
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.021996 | 1011353.97 | 35806.31
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.029988 | 1378844.34 | 48817.06
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.040661 | 1869572.77 | 66190.97
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.03479 | 1599665.58 | 56635.09
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.00351 | 161382.93 | 5713.65
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002828 | 130017.63 | 4603.19
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.004051 | 186274.76 | 6594.93
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003596 | 165327 | 5853.29
VAV_5_HEATC | 0.000979 | 45025.07 | 675.76
VAV_1_HEATC | 0.001831 | 84209.4 | 1330.66
VAV_2_HEATC | 0.017924 | 824158.5 | 13180.45
VAV_3_HEATC | 0.00179 | 82298.36 | 1316.8
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003847 | 7.09 | 23.62 | 12.8 | 7.22 | 0.00936 | 0.0085
VAV_1_COOLC | 0.010513 | 19.4 | 24.17 | 12.8 | 7.22 | 0.009129 | 0.0085
VAV_2_COOLC | 0.11238 | 210.21 | 24.19 | 12.8 | 7.22 | 0.00905 | 0.0085
VAV_3_COOLC | 0.011956 | 21.07 | 24.15 | 12.8 | 7.22 | 0.009382 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 490483.4975 | 788.1396 | 1118.8808 | 0 | 0.0084 | 735096.8399 | 202536.2468
February | 436819.4036 | 715.9939 | 1042.327 | 0 | 0.0078 | 684869.6448 | 181722.9905
March | 479149.4489 | 821.0793 | 1259.5848 | 0 | 0.0093 | 827785.7202 | 202745.5024
April | 434977.7939 | 768.1146 | 1217.4749 | 0 | 0.0089 | 800206.8811 | 186227.4314
May | 465709.2936 | 834.1917 | 1341.9432 | 0 | 0.0098 | 882062.4261 | 200513.3431
June | 456589.2108 | 828.1544 | 1349.1984 | 0 | 0.0098 | 886870.6664 | 197571.0803
July | 454155.6332 | 825.2627 | 1346.964 | 0 | 0.0098 | 885407.6401 | 196663.5535
August | 477161.2942 | 864.9641 | 1408.3482 | 0 | 0.0103 | 925749.815 | 206424.7089
September | 442931.9327 | 794.2503 | 1279.1041 | 0 | 0.0094 | 840761.3873 | 190788.4592
October | 453374.8209 | 801.9996 | 1273.5199 | 0 | 0.0093 | 837048.9987 | 194237.4222
November | 470487.6781 | 801.4198 | 1221.1316 | 0 | 0.009 | 802494.4478 | 198620.0017
December | 482253.9235 | 787.0466 | 1139.6074 | 0 | 0.0085 | 748772.7629 | 200297.5351
Annual Sum or Average | 5544093.9309 | 9630.6165 | 14998.0843 | 0 | 0.1104 | 9857127.2303 | 2358348.2752
Minimum of Months | 434977.7939 | 715.9939 | 1042.327 | 0 | 0.0078 | 684869.6448 | 181722.9905
Maximum of Months | 490483.4975 | 864.9641 | 1408.3482 | 0 | 0.0103 | 925749.815 | 206424.7089
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1705740000000 | 1420360.242 | 13-JAN-14:00 | 448566.543 | 336424.909 | 290234.177 | 0 | 219825.241 | 0 | 89233.141 | 36076.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1589190000000 | 1493229.168 | 28-FEB-13:30 | 448566.543 | 336424.909 | 293864.134 | 0 | 275534.65 | 0 | 89111.547 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1920810000000 | 1491952.904 | 31-MAR-13:00 | 448566.543 | 336424.909 | 296169.758 | 0 | 275534.65 | 0 | 89044.91 | 46212.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1856820000000 | 1506019.254 | 04-APR-14:00 | 448566.543 | 336424.909 | 294408.934 | 0 | 287907.518 | 0 | 88983.965 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2046760000000 | 1546089.955 | 31-MAY-15:00 | 448566.543 | 336424.909 | 296076.852 | 0 | 326313.248 | 0 | 88981.019 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2057920000000 | 1671089.308 | 14-JUN-14:00 | 448566.543 | 336424.909 | 299481.939 | 0 | 447907.513 | 0 | 88981.019 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 2054520000000 | 1712221.193 | 07-JUL-15:30 | 448566.543 | 336424.909 | 305755.056 | 0 | 482766.281 | 0 | 88981.019 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2148130000000 | 1692323.323 | 11-AUG-15:30 | 448566.543 | 336424.909 | 302448.058 | 0 | 466175.409 | 0 | 88981.019 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1950920000000 | 1636221.981 | 07-SEP-14:00 | 448566.543 | 336424.909 | 300429.235 | 0 | 412092.89 | 0 | 88981.019 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1942310000000 | 1519337.911 | 06-OCT-14:30 | 448566.543 | 336424.909 | 297996.616 | 0 | 297638.681 | 0 | 88983.777 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1862130000000 | 1493903.696 | 07-NOV-16:00 | 448566.543 | 336424.909 | 290234.177 | 0 | 275534.65 | 3997.501 | 89418.532 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1737470000000 | 1385637.968 | 01-DEC-15:30 | 448566.543 | 336424.909 | 290234.177 | 0 | 197568.845 | 0 | 89301.662 | 23541.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 22872700000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1589190000000 | 1385637.968 |  | 448566.543 | 336424.909 | 290234.177 | 0 | 197568.845 | 0 | 88981.019 | 23541.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2148130000000 | 1712221.193 |  | 448566.543 | 336424.909 | 305755.056 | 0 | 482766.281 | 3997.501 | 89418.532 | 49727.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 372173.13 | 80215.74 | 0 | 452388.87
Cost per Total Building Area ($/m2) | 8.03 | 1.73 | 0 | 9.77
Cost per Net Conditioned Building Area ($/m2) | 8.03 | 1.73 | 0 | 9.77
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 39926.08 | 861.95 | 861.95
Net Site Energy | 39926.08 | 861.95 | 861.95
Total Source Energy | 98106.26 | 2117.99 | 2117.99
Net Source Energy | 98106.26 | 2117.99 | 2117.99
Area (m2)
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 17569.51 | 0 | 0 | 0 | 0
Cooling | 2842.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 62.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5962.19 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 6336.96 | 0 | 0 | 0 | 0 | 0
Pumps | 1188.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 448.86 | 0 | 0 | 0 | 0 | 8543.88
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 377.95 | 0 | 0 | 0 | 1503.95
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21978.62 | 17947.46 | 0 | 0 | 0 | 10047.82
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 21978.62 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 21978.62 | 100
Total On-Site and Utility Electric Sources | 21978.62 | 100
Total Electricity End Uses | 21978.62 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BASEMENT_WALL_NORTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 0 | 90 | N
BASEMENT_WALL_EAST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 90 | 90 | E
BASEMENT_WALL_SOUTH | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.919 | 2.69 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | ASHRAE 90.1-2004_SEC 5.5-5_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 3563.11 | 0 | 180
PERIMETER_BOT_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_3_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_2_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_1_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_4_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 133.74 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 270 | 90 | W
GROUNDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 594.21 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 594.21 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_EAST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_WEST | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 59.42 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_SOUTH | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 89.13 | 0 | 90 | N
BUILDING_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 3563.11 | 0 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 115.9 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_3_WALL_NORTH
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 77.27 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_2_WALL_EAST
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 115.9 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 77.27 | 2.62 | 0.49 | 0.49 | No | PERIMETER_BOT_ZN_4_WALL_WEST
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 1159.04 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_3_WALL_NORTH
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 772.69 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_2_WALL_EAST
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 1159.04 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_1_WALL_SOUTH
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 772.69 | 2.62 | 0.49 | 0.49 | No | PERIMETER_MID_ZN_4_WALL_WEST
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 115.9 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_3_WALL_NORTH
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 77.27 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_2_WALL_EAST
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 115.9 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 77.27 | 2.62 | 0.49 | 0.49 | No | PERIMETER_TOP_ZN_4_WALL_WEST
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3686647.81 | 4.45
HEATSYS1 BOILER | Boiler:HotWater | 18090189.79 | 0.8
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3612086.39
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
VAV_5 FAN | Fan:VariableVolume | 0.28 | 750 | 7.08 | 19031.18 | 1 | Fan Energy
VAV_1 FAN | Fan:VariableVolume | 0.28 | 750 | 19.78 | 53138.7 | 1 | Fan Energy
VAV_2 FAN | Fan:VariableVolume | 0.28 | 750 | 216.67 | 582063.32 | 1 | Fan Energy
VAV_3 FAN | Fan:VariableVolume | 0.28 | 750 | 23.71 | 63695.21 | 1 | Fan Energy
| Type | Control | Head (pa) | Power (W) | Motor Efficiency (W/W)
SHWSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 103389.78 | 0.88
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33783.02 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 50979.56 | 0.87
| Type | Storage Volume (m3) | Input(W) | Thermal Efficiency (W/W) | Recovery Efficiency (W/W) | Energy Factor
SHWSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.91 | 0.59
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
BASEMENT VAV BOX REHEAT COIL | 0.009541 | 438712.22 | 15532.31
CORE_BOTTOM VAV BOX REHEAT COIL | 0.014006 | 644016.08 | 22800.96
CORE_MID VAV BOX REHEAT COIL | 0.15094 | 6940118.73 | 245710.25
CORE_TOP VAV BOX REHEAT COIL | 0.018683 | 859026.28 | 30413.25
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | 0.002219 | 102012.4 | 3611.68
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | 0.002824 | 129833.75 | 4596.68
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | 0.004553 | 209335.18 | 7411.37
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | 0.00304 | 139771.38 | 4948.51
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 0.025337 | 1165011.43 | 41246.45
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 0.030761 | 1414412.54 | 50076.33
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 0.05112 | 2350501.1 | 83217.91
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 0.033664 | 1547848.87 | 54800.55
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | 0.004004 | 184125.22 | 6518.83
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | 0.002912 | 133884.66 | 4740.1
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | 0.004989 | 229388.47 | 8121.34
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | 0.003358 | 154378.91 | 5465.68
VAV_5_HEATC | 0.00135 | 62063.69 | 888.46
VAV_1_HEATC | 0.002559 | 117661.89 | 1791.99
VAV_2_HEATC | 0.025127 | 1155357.82 | 17863.11
VAV_3_HEATC | 0.002452 | 112729.17 | 1769.04
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_5_COOLC | 0.003358 | 7.08 | 23.44 | 12.8 | 7.22 | 0.008615 | 0.0085
VAV_1_COOLC | 0.009795 | 19.78 | 24.03 | 12.8 | 7.22 | 0.008577 | 0.0085
VAV_2_COOLC | 0.10753 | 216.67 | 24.07 | 12.8 | 7.22 | 0.008569 | 0.0085
VAV_3_COOLC | 0.01155 | 23.71 | 24 | 12.8 | 7.22 | 0.008511 | 0.0085
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 543907.185 | 607.2884 | 2377.167 | 0 | 0.0085 | 476892.7108 | 205720.5492
February | 448760.285 | 508.598 | 2119.1512 | 0 | 0.0075 | 425168.457 | 170894.3018
March | 460368.4212 | 542.6486 | 2611.1057 | 0 | 0.009 | 523965.6782 | 178530.2424
April | 395214.5673 | 481.5284 | 2569.5769 | 0 | 0.0088 | 515691.9206 | 155676.3586
May | 418128.9344 | 518.8303 | 2914.8652 | 0 | 0.0099 | 585019.4873 | 166146.3412
June | 405888.6937 | 506.5296 | 2889.9433 | 0 | 0.0098 | 580026.5655 | 161726.9298
July | 390341.0814 | 487.2709 | 2782.2561 | 0 | 0.0094 | 558413.6174 | 155554.1191
August | 420083.0891 | 522.2466 | 2949.23 | 0 | 0.01 | 591919.6416 | 167075.4064
September | 397715.7263 | 488.988 | 2678.1478 | 0 | 0.0091 | 537495.8344 | 157340.5586
October | 420526.8771 | 505.1793 | 2583.7375 | 0 | 0.0089 | 518509.9132 | 164540.5898
November | 447946.9569 | 516.4566 | 2299.0063 | 0 | 0.008 | 461293.25 | 171935.7611
December | 489594.917 | 554.706 | 2308.3939 | 0 | 0.0082 | 463135.7283 | 186418.3194
Annual Sum or Average | 5238476.7342 | 6240.2707 | 31082.5808 | 0 | 0.107 | 6237532.8045 | 2041559.4776
Minimum of Months | 390341.0814 | 481.5284 | 2119.1512 | 0 | 0.0075 | 425168.457 | 155554.1191
Maximum of Months | 543907.185 | 607.2884 | 2949.23 | 0 | 0.01 | 591919.6416 | 205720.5492
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1680380000000 | 1446276.442 | 19-JAN-14:00 | 448566.543 | 336424.909 | 300812.769 | 0 | 237785.469 | 0 | 85335.55 | 37351.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 1498130000000 | 1470253.435 | 28-FEB-14:00 | 448566.543 | 336424.909 | 301470.715 | 0 | 262686.674 | 0 | 85067.352 | 36037.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 1846250000000 | 1485211.733 | 29-MAR-14:00 | 448566.543 | 336424.909 | 305174.627 | 0 | 262686.674 | 0 | 84950.345 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 1817100000000 | 1490945.511 | 24-APR-14:00 | 448566.543 | 336424.909 | 306863.083 | 0 | 266818.401 | 0 | 84863.941 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 2061380000000 | 1545859.998 | 24-MAY-14:00 | 448566.543 | 336424.909 | 308454.619 | 0 | 320170.003 | 0 | 84835.291 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 2043790000000 | 1601611.741 | 21-JUN-15:45 | 448566.543 | 336424.909 | 311173.963 | 0 | 373202.401 | 0 | 84835.291 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 1967630000000 | 1594359.318 | 11-JUL-15:00 | 448566.543 | 336424.909 | 311813.123 | 0 | 365310.819 | 0 | 84835.291 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 2085690000000 | 1580037.596 | 15-AUG-14:30 | 448566.543 | 336424.909 | 310103.979 | 0 | 352698.241 | 0 | 84835.291 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 1893920000000 | 1504294.383 | 07-SEP-15:45 | 448566.543 | 336424.909 | 304099.431 | 0 | 282945.804 | 0 | 84849.062 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 1827030000000 | 1485278.487 | 06-OCT-07:15 | 448566.543 | 336424.909 | 300812.769 | 0 | 262686.674 | 3997.501 | 85381.456 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 1625420000000 | 1384649.65 | 14-NOV-16:00 | 448566.543 | 336424.909 | 300812.769 | 0 | 185154.053 | 3997.501 | 85434.395 | 24259.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 1631910000000 | 1400781.372 | 18-DEC-10:00 | 448566.543 | 336424.909 | 300812.769 | 0 | 194061.527 | 3997.501 | 85997.87 | 30920.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 21978600000000 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1498130000000 | 1384649.65 |  | 448566.543 | 336424.909 | 300812.769 | 0 | 185154.053 | 0 | 84835.291 | 24259.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2085690000000 | 1601611.741 |  | 448566.543 | 336424.909 | 311813.123 | 0 | 373202.401 | 3997.501 | 85997.87 | 47408.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 593026.49 | 73961.33 | 0 | 666987.82
Cost per Total Building Area ($/m2) | 12.8 | 1.6 | 0 | 14.4
Cost per Net Conditioned Building Area ($/m2) | 12.8 | 1.6 | 0 | 14.4

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 4.7 | 40.9 | 9.2 | 45.9 | 52.3 | 5.8 | 2.4 | 104 | 2.6 | 13.1 | 92.3 | 20.8 | 26.2 | 3.1 | 3.6 | 0.18
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.34 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab | 8-in slab
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 4030.3723 | 3962.9196 | 3955.6187 | 3854.5308 | 3182.6554 | 6760.9223 | 3288.8264 | 4177.685 | 6352.4141 | 3439.7323 | 4128.282 | 5967.872 | 4013.5441 | 5965.0067 | 3866.9613 | 3686.6478
| TOWERWATERSYS COOLTOWER | 3948.8592 | 3882.7706 | 3875.6174 | 3776.574 | 3118.287 | 6624.1845 | 3222.3108 | 4093.1925 | 6223.9383 | 3370.1647 | 4044.7886 | 5847.1734 | 3932.3713 | 5844.3661 | 3788.7531 | 3612.0864
Heating (kW)
| HEATSYS1 BOILER | 13768.8393 | 14304.3333 | 15950.6946 | 14224.1173 | 13550.759 | 15391.3439 | 13719.7371 | 15902.1704 | 15053.5247 | 15032.5104 | 15963.8943 | 15218.2906 | 16018.7076 | 15618.1096 | 16559.4656 | 18090.1898
HVAC Efficiency
| Air Conditioning (COP) | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45 | 4.45
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
Fan Max Flow Rate (m3/s )
| VAV_5 FAN | 9.04 | 7.34 | 6.74 | 7.05 | 6.69 | 7.21 | 6.73 | 7.15 | 7.8 | 6.98 | 7.21 | 7.84 | 6.98 | 7.47 | 7.09 | 7.08
| VAV_1 FAN | 16.47 | 16.83 | 19.08 | 17.21 | 16.14 | 19.03 | 16.3 | 18.33 | 21.41 | 17.88 | 18.45 | 21.22 | 18.44 | 20.18 | 19.4 | 19.78
| VAV_2 FAN | 172.66 | 178.69 | 211.41 | 182.58 | 174.22 | 210.42 | 175.62 | 198.37 | 230.53 | 192.63 | 199.06 | 229.76 | 199.07 | 218.84 | 210.21 | 216.67
| VAV_3 FAN | 18.73 | 19.51 | 24.12 | 19.83 | 17.22 | 23.42 | 15.79 | 20.92 | 23.61 | 18.1 | 20.64 | 22.87 | 20.7 | 21.88 | 21.07 | 23.71
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.083314 | 0.10505 | 0.074464 | 0.096148 | 0.052842 | 0.092899 | 0.14181 | 0.066691 | 0.036952 | 0.06967 | 0.091137 | 0.036953 | 0.058784 | 0.074758 | 0.058577 | 0.097135
| Total Cost ($/m2) | 12.37 | 15.35 | 11.24 | 13.41 | 6.85 | 15.96 | 18.56 | 9.66 | 6.29 | 9.42 | 12.84 | 5.99 | 8.09 | 11.63 | 8.03 | 12.8
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011387 | 0.0080542 | 0.0082437 | 0.0096509 | 0.0085912 | 0.0077041 | 0.0085433 | 0.0097196 | 0.0069139 | 0.0084103 | 0.0083499 | 0.0069372 | 0.0078884 | 0.0081268 | 0.0078795 | 0.004121
| Total Cost ($/m2) | 0.12 | 0.48 | 0.5 | 0.62 | 0.24 | 0.38 | 0.76 | 1.03 | 0.49 | 0.91 | 1.14 | 0.7 | 1.44 | 1.27 | 1.73 | 1.6
Total Utility Costs
| Cost Intensity ($/m2) | 12.49 | 15.83 | 11.74 | 14.02 | 7.09 | 16.33 | 19.32 | 10.69 | 6.78 | 10.33 | 13.98 | 6.69 | 9.53 | 12.9 | 9.77 | 14.4
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1908230.5556 | 1716116.6667 | 1676952.7778 | 1425619.4445 | 1211755.5556 | 2155086.1111 | 1158330.5556 | 1459988.8889 | 1968230.5556 | 1188991.6667 | 1284927.7778 | 1717333.3333 | 1142872.2222 | 1505952.7778 | 1038361.1111 | 789675
| Interior Lighting | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889
| Exterior Lighting | 17477.7778 | 17447.2222 | 17444.4444 | 17472.2222 | 17469.4444 | 17452.7778 | 17433.3333 | 17450 | 17447.2222 | 17422.2222 | 17427.7778 | 17430.5556 | 17441.6667 | 17419.4444 | 17413.8889 | 17311.1111
| Interior Equipment | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889 | 1656163.8889
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 1168933.3333 | 1230113.8889 | 1470041.6667 | 1252761.1111 | 1143297.2222 | 1450769.4445 | 1183405.5556 | 1402788.8889 | 1634938.8889 | 1310380.5556 | 1437383.3333 | 1631700 | 1502283.3333 | 1597963.8889 | 1616669.4445 | 1760266.6667
| Pumps | 448591.6667 | 471219.4444 | 484319.4444 | 451733.3333 | 353552.7778 | 823544.4445 | 400472.2222 | 508947.2222 | 807883.3333 | 434652.7778 | 496647.2222 | 744850 | 451961.1111 | 721477.7778 | 433230.5556 | 330033.3333
| Heat Rejection | 250447.2222 | 248872.2222 | 263011.1111 | 227336.1111 | 196761.1111 | 425516.6667 | 218772.2222 | 234402.7778 | 368047.2222 | 226063.8889 | 206166.6667 | 312416.6667 | 180611.1111 | 279277.7778 | 164655.5556 | 124683.3333
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 6876886.1112 | 6766972.2223 | 6994972.2223 | 6458125.0001 | 6006036.1112 | 7955572.2223 | 6061616.6667 | 6706783.3334 | 7879752.7778 | 6260716.6667 | 6525755.5556 | 7506933.3334 | 6378369.4445 | 7205291.6667 | 6353533.3334 | 6105172.2223
Gas (MJ)
| Heating | 322800 | 2560940 | 2604240 | 2717210 | 1040620 | 2057060 | 3850580 | 4653580 | 3041220 | 4740140 | 6014580 | 4392640 | 8145270 | 6912280 | 9841270 | 17569510
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 172410 | 206290 | 186700 | 239020 | 232760 | 210210 | 260730 | 264730 | 259850 | 278170 | 287320 | 286140 | 306830 | 310380 | 339030 | 377950
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 495210 | 2767220 | 2790930 | 2956230 | 1273380 | 2267270 | 4111310 | 4918310 | 3301070 | 5018310 | 6301890 | 4678780 | 8452110 | 7222660 | 10180300 | 17947460
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 25252010 | 27128330 | 27972830 | 26205470 | 22895110 | 30907330 | 25933130 | 29062740 | 31668180 | 27556890 | 29794620 | 31703740 | 31414240 | 33161710 | 33053020 | 39926080
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 148.3069 | 133.3758 | 130.332 | 110.7985 | 94.1771 | 167.4924 | 90.025 | 113.4697 | 152.97 | 92.4079 | 99.864 | 133.4704 | 88.8235 | 117.042 | 80.701 | 61.3732
| Interior Lighting (elec) | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088
| Exterior Lighting (elec) | 1.3584 | 1.356 | 1.3558 | 1.3579 | 1.3577 | 1.3564 | 1.3549 | 1.3562 | 1.356 | 1.354 | 1.3545 | 1.3547 | 1.3556 | 1.3538 | 1.3534 | 1.3454
| Interior Equipment (elec) | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163 | 128.7163
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 90.849 | 95.6039 | 114.251 | 97.3641 | 88.8566 | 112.7532 | 91.9738 | 109.0241 | 127.0667 | 101.8422 | 111.7128 | 126.815 | 116.7568 | 124.1931 | 125.6469 | 136.8072
| Pumps (elec) | 34.8644 | 36.623 | 37.6411 | 35.1085 | 27.478 | 64.0055 | 31.1245 | 39.5552 | 62.7883 | 33.781 | 38.5992 | 57.8894 | 35.1262 | 56.0729 | 33.6705 | 25.65
| Heat Rejection (elec) | 19.4647 | 19.3422 | 20.4411 | 17.6685 | 15.2922 | 33.071 | 17.0029 | 18.2177 | 28.6045 | 17.5696 | 16.0232 | 24.2809 | 14.037 | 21.7053 | 12.797 | 9.6903
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 534.4686 | 525.9262 | 543.6462 | 501.9227 | 466.7865 | 618.3036 | 471.1062 | 521.2483 | 612.411 | 486.5802 | 507.1789 | 583.4356 | 495.7241 | 559.9922 | 493.7939 | 474.4914
Gas (MJ/m2)
| Heating (gas) | 6.9689 | 55.2875 | 56.2223 | 58.6612 | 22.4657 | 44.4094 | 83.1293 | 100.4651 | 65.6562 | 102.3338 | 129.8474 | 94.8317 | 175.8464 | 149.2276 | 212.4609 | 379.3041
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7221 | 4.4535 | 4.0306 | 5.1601 | 5.025 | 4.5382 | 5.6288 | 5.7152 | 5.6098 | 6.0053 | 6.2029 | 6.1774 | 6.6241 | 6.7007 | 7.3192 | 8.1595
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10.691 | 59.7409 | 60.2527 | 63.8214 | 27.4907 | 48.9476 | 88.7581 | 106.1803 | 71.266 | 108.3391 | 136.05 | 101.0091 | 182.4707 | 155.9283 | 219.7801 | 387.4636
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 545.1598 | 585.6673 | 603.899 | 565.7438 | 494.2772 | 667.2512 | 559.8644 | 627.4288 | 683.677 | 594.9193 | 643.2292 | 684.4447 | 678.1948 | 715.9205 | 713.574 | 861.9549
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1596.6657 | 1561.2219 | 1535.8434 | 1472.6776 | 1422.4483 | 1806.5587 | 1383.1827 | 1512.4148 | 1796.0945 | 1423.0321 | 1503.7476 | 1747.5879 | 1367.7351 | 1568.4933 | 1420.3602 | 1446.2764
| Feb | 1629.9114 | 1530.5971 | 1550.9414 | 1468.6785 | 1426.8811 | 1807.4742 | 1418.3817 | 1513.0997 | 1796.2694 | 1423.3232 | 1507.0335 | 1750.1593 | 1408.9663 | 1731.6528 | 1493.2292 | 1470.2534
| Mar | 1633.3282 | 1555.3427 | 1590.9149 | 1496.3085 | 1422.3131 | 1806.1018 | 1398.2036 | 1565.1424 | 1796.327 | 1451.2577 | 1515.7315 | 1750.9421 | 1496.0681 | 1735.5313 | 1491.9529 | 1485.2117
| Apr | 1675.041 | 1585.9621 | 1597.1256 | 1545.3239 | 1446.4164 | 1809.6146 | 1415.3925 | 1559.751 | 1797.2387 | 1447.3593 | 1527.7788 | 1749.9676 | 1517.5345 | 1731.1176 | 1506.0193 | 1490.9455
| May | 1752.5942 | 1742.3638 | 1663.7145 | 1630.0735 | 1487.9634 | 1830.5953 | 1431.0189 | 1676.7505 | 1814.3562 | 1488.3102 | 1659.3847 | 1761.9452 | 1611.7067 | 1733.5965 | 1546.09 | 1545.86
| Jun | 1839.8861 | 1725.1401 | 1779.388 | 1668.2904 | 1460.7275 | 1910.8165 | 1434.5991 | 1799.5254 | 1890.6464 | 1515.1746 | 1783.431 | 1830.753 | 1748.9478 | 1818.3958 | 1671.0893 | 1601.6117
| Jul | 1785.3535 | 1852.5292 | 1829.3753 | 1756.9235 | 1485.5659 | 1932.6869 | 1487.3394 | 1845.4442 | 1905.4698 | 1567.6064 | 1777.7801 | 1846.4416 | 1770.1695 | 1828.2517 | 1712.2212 | 1594.3593
| Aug | 1852.361 | 1793.1282 | 1806.2683 | 1715.1223 | 1534.6241 | 1926.2233 | 1461.786 | 1904.8312 | 1891.1002 | 1551.7796 | 1839.0117 | 1844.9238 | 1756.5171 | 1771.1598 | 1692.3233 | 1580.0376
| Sep | 1768.6764 | 1776.1959 | 1753.7407 | 1675.4503 | 1513.3657 | 1879.215 | 1516.8249 | 1676.3168 | 1835.8747 | 1553.8209 | 1641.6948 | 1777.4917 | 1626.6163 | 1757.4471 | 1636.222 | 1504.2944
| Oct | 1737.0923 | 1662.2536 | 1615.9683 | 1553.2281 | 1465.8757 | 1813.0492 | 1439.3261 | 1617.3505 | 1798.8317 | 1466.5381 | 1581.4474 | 1769.0669 | 1527.2315 | 1736.3672 | 1519.3379 | 1485.2785
| Nov | 1647.9921 | 1602.3769 | 1584.5215 | 1484.0135 | 1430.5503 | 1806.7762 | 1407.5524 | 1589.0793 | 1795.6342 | 1436.3734 | 1573.6802 | 1750.8415 | 1503.274 | 1704.4264 | 1493.9037 | 1384.6497
| Dec | 1589.635 | 1550.8868 | 1530.9123 | 1478.7781 | 1430.3442 | 1805.7783 | 1383.0587 | 1512.6571 | 1794.5978 | 1422.9905 | 1507.5158 | 1748.6137 | 1429.0907 | 1627.9343 | 1385.638 | 1400.7814
Time of Peak Electrical Demand
| Jan | 06-JAN-14:15 | 03-JAN-11:00 | 26-JAN-15:30 | 24-JAN-16:00 | 26-JAN-13:15 | 30-JAN-13:45 | 04-JAN-16:00 | 04-JAN-13:45 | 27-JAN-13:45 | 09-JAN-16:00 | 17-JAN-13:15 | 26-JAN-14:15 | 30-JAN-16:00 | 24-JAN-13:00 | 13-JAN-14:00 | 19-JAN-14:00
| Feb | 23-FEB-11:00 | 21-FEB-11:30 | 28-FEB-15:45 | 21-FEB-15:00 | 13-FEB-11:00 | 27-FEB-13:45 | 15-FEB-15:00 | 16-FEB-13:15 | 14-FEB-13:00 | 24-FEB-13:45 | 16-FEB-14:15 | 23-FEB-13:45 | 17-FEB-15:00 | 03-FEB-13:00 | 28-FEB-13:30 | 28-FEB-14:00
| Mar | 13-MAR-14:00 | 29-MAR-13:00 | 17-MAR-15:00 | 29-MAR-14:00 | 31-MAR-14:30 | 31-MAR-14:30 | 01-MAR-13:15 | 09-MAR-15:00 | 01-MAR-13:00 | 29-MAR-14:30 | 31-MAR-14:00 | 27-MAR-13:45 | 23-MAR-13:30 | 28-MAR-15:45 | 31-MAR-13:00 | 29-MAR-14:00
| Apr | 03-APR-13:00 | 10-APR-13:30 | 26-APR-15:45 | 20-APR-15:00 | 11-APR-13:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:30 | 18-APR-15:30 | 03-APR-13:00 | 26-APR-10:00 | 14-APR-15:30 | 05-APR-15:45 | 04-APR-14:00 | 24-APR-14:00
| May | 15-MAY-15:00 | 30-MAY-12:00 | 30-MAY-15:15 | 31-MAY-15:00 | 30-MAY-10:00 | 31-MAY-15:00 | 25-MAY-15:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 24-MAY-15:30 | 31-MAY-12:15 | 16-MAY-15:45 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 26-JUN-15:30 | 29-JUN-15:00 | 28-JUN-15:00 | 08-JUN-15:30 | 28-JUN-12:00 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:15 | 29-JUN-15:30 | 28-JUN-14:30 | 08-JUN-12:00 | 27-JUN-15:15 | 29-JUN-14:00 | 26-JUN-15:30 | 14-JUN-14:00 | 21-JUN-15:45
| Jul | 13-JUL-15:45 | 18-JUL-12:15 | 11-JUL-15:00 | 03-JUL-14:30 | 10-JUL-09:00 | 25-JUL-14:30 | 03-JUL-13:15 | 25-JUL-13:30 | 03-JUL-15:15 | 31-JUL-15:00 | 13-JUL-13:30 | 18-JUL-13:00 | 13-JUL-15:00 | 21-JUL-15:45 | 07-JUL-15:30 | 11-JUL-15:00
| Aug | 21-AUG-14:30 | 31-AUG-15:00 | 02-AUG-14:00 | 14-AUG-14:30 | 08-AUG-15:30 | 02-AUG-13:30 | 15-AUG-12:15 | 09-AUG-14:45 | 01-AUG-14:30 | 07-AUG-14:00 | 04-AUG-15:30 | 30-AUG-13:45 | 25-AUG-15:00 | 11-AUG-15:00 | 11-AUG-15:30 | 15-AUG-14:30
| Sep | 11-SEP-14:00 | 15-SEP-14:45 | 05-SEP-14:15 | 05-SEP-15:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 05-SEP-10:30 | 05-SEP-13:45 | 01-SEP-15:45 | 06-SEP-12:45 | 06-SEP-14:30 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:45
| Oct | 06-OCT-15:45 | 30-OCT-14:30 | 03-OCT-15:45 | 12-OCT-15:00 | 05-OCT-10:00 | 03-OCT-14:00 | 31-OCT-13:15 | 12-OCT-14:30 | 02-OCT-10:00 | 02-OCT-14:45 | 30-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-13:00 | 06-OCT-14:30 | 06-OCT-07:15
| Nov | 01-NOV-11:30 | 27-NOV-16:00 | 13-NOV-15:15 | 21-NOV-14:00 | 20-NOV-13:15 | 09-NOV-13:15 | 16-NOV-15:00 | 03-NOV-13:00 | 01-NOV-13:30 | 03-NOV-16:00 | 02-NOV-14:30 | 01-NOV-13:30 | 02-NOV-14:00 | 21-NOV-13:00 | 07-NOV-16:00 | 14-NOV-16:00
| Dec | 15-DEC-15:45 | 06-DEC-14:45 | 13-DEC-13:15 | 26-DEC-14:45 | 19-DEC-13:15 | 05-DEC-13:30 | 27-DEC-16:00 | 06-DEC-13:30 | 05-DEC-13:30 | 22-DEC-16:15 | 12-DEC-16:15 | 22-DEC-13:30 | 01-DEC-14:00 | 01-DEC-13:00 | 01-DEC-15:30 | 18-DEC-10:00
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 23731.16 | 20718.75 | 32127.44 | 17660.68 | 14055.83 | 48264.88 | 12186.72 | 17520.65 | 35479.47 | 12289.86 | 15112.72 | 28379.59 | 13352.45 | 22387.98 | 10765.29 | 8543.88
| Water Systems | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95 | 1503.95
| Total Building | 25235.11 | 22222.7 | 33631.38 | 19164.62 | 15559.77 | 49768.82 | 13690.66 | 19024.6 | 36983.41 | 13793.8 | 16616.67 | 29883.53 | 14856.39 | 23891.93 | 12269.23 | 10047.82
Emissions
| Carbon Equivalent (kg) | 1894914.4669 | 2307098.6267 | 2161938.3709 | 2042647.7815 | 724862.7775 | 2724100.5905 | 782533.6778 | 1898552.7581 | 3278390.2293 | 546487.326 | 3592842.5181 | 3150938.1076 | 2335685.3333 | 2763327.9863 | 2358348.2752 | 2041559.4776
| CO2 (kg) | 4392898.95 | 5808129.224 | 5111277.9373 | 4669023.1468 | 1940298.4948 | 6473353.6049 | 2105496.0461 | 4314921.5871 | 7672249.0984 | 1344657.8535 | 8355792.3553 | 7389163.3221 | 5473653.4169 | 6500510.9538 | 5544093.9309 | 5238476.7342
| NOX (kg) | 7725.2621 | 7575.6433 | 8525.1378 | 8858.2971 | 1663.9146 | 10529.3588 | 1812.9891 | 8347.5767 | 13315.6418 | 1977.7949 | 14915.2522 | 12758.1844 | 9584.6362 | 11212.6889 | 9630.6165 | 6240.2707
| SO2 (kg) | 29435.9606 | 32279.2056 | 28128.9284 | 22668.808 | 17477.1873 | 43762.6148 | 17639.6768 | 24483.7629 | 34410.1857 | 4840.3777 | 43980.0676 | 32782.5283 | 15056.2369 | 19240.9313 | 14998.0843 | 31082.5808
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1342 | 0.091 | 0.0766 | 0.083 | 0.0079 | 0.0822 | 0.0083 | 0.0991 | 0.1343 | 0.0193 | 0.1332 | 0.1281 | 0.1107 | 0.1341 | 0.1104 | 0.107
| Water Environmental Factors (m3) | 3643.086 | 11010.7 | 207781 | 207781 | 105453 | 218253 | 106428 | 1522.6922 | 35780.4 | 63964.5 | 10124.3 | 34087.5 | 9895.6581 | 456413 | 9857.1272 | 6237.5328

## Picture
DOE Commercial Building Benchmark - Large Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 432 | 2992 | 156011.43
|  |  | SummerDesign | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312
|  |  | Sat | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 440
|  |  | Sun, Hol, Other | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 13 | 13 | 13 | 392
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 657 | 4644 | 242151.43
|  |  | Sat | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 648
|  |  | WinterDesign | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792
|  |  | Sun, Hol, Other | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 711
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 100 | 5214.29
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 126984
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temperature Schedules (oF)
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4 | 55.4
|  |  | SummerDesign | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
|  |  | Sat | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4
|  |  | Sun, Hol, Other | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4 | 91.4
|  |  | Sat | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4
|  |  | WinterDesign | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4
|  |  | Sun, Hol, Other | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4 | 91.4