## BuildingSummary
Building Summary Retail new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Retail
| Available Fuel Types | gas, electricity
| Principal Building Activity | Retail
Form
| Total Floor Area (m2) | 2294 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.254
| East | 0
| North | 0
| West | 0
| Total | 0.071
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Back, CoreRetail, FrontRetail, PointofSale, FrontEntry
| Floor to Ceiling Height (m) | 6.1
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1177
| Net Dimensions - Total Area (m2) | 1093.1
| Wall to Skin Ratio | 0.34
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2294
| Net Dimensions - Total Area (m2) | 2294
| Roof to Skin Ratio | 0.66
Window Dimensions (m2)
| South | 83.9
| East | 0
| North | 0
| West | 0
| Total Area (m2) | 83.9
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2294
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Internal Mass | 244.23
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 7764.95
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.27 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (L ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Back_Space | Yes | 1 | 379.89 | 2317.33 | 6.1 | 416.17 | 0 | 27.8709 | 13.6303 | 8.608 | 8.07 | 0 | 0 | 3.8 | 0.6 | 279.7292 | 0 | 0.37388
Core_Retail | Yes | 1 | 1600.48 | 9762.95 | 6.1 | 356.86 | 0 | 11.6129 | 137.8193 | 18.292 | 3.228 | 0 | 0 | 3.8 | 0.6 | 1484.0012 | 0 | 0.2182
Point_of_Sale | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8 | 38.05 | 11.6129 | 12.9864 | 18.292 | 21.52 | 0 | 0 | 3.8 | 0.6 | 139.8344 | 0 | 0.40297
Front_Retail | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8 | 38.05 | 11.6129 | 12.9864 | 18.292 | 3.228 | 0 | 0 | 3.8 | 0.6 | 139.8344 | 0 | 0.40297
Front_Entry | Yes | 1 | 12 | 73.2 | 6.1 | 24.38 | 7.83 | 11.6129 | 1.0333 | 11.836 | 0 | 0 | 0 | 3.8 | 0.6 | 11.1267 | 0 | 0.54091
Total Conditioned Zones |  |  | 2293.99 | 13993.36 |  | 1177.01 | 83.93 |  | 178.4558
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## Query (hidden)
01-Miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1852.75 | 807.65 | 807.65
Net Site Energy | 1852.75 | 807.65 | 807.65
Total Source Energy | 6134.53 | 2674.17 | 2674.17
Net Source Energy | 6134.53 | 2674.17 | 2674.17
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0.02 | 4.96 | 0 | 0 | 0 | 0
Cooling | 718.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 380.34 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1847.79 | 4.96 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1847.79 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1847.79 | 100
Total On-Site and Utility Electric Sources | 1847.79 | 100
Total Electricity End Uses | 1847.79 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 6.88 | 0.25 | 0.25 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 6.88 | 0.25 | 0.25 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 7.83 | 6.88 | 0.25 | 0.25 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 49855.94 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 222496.27 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27071.42 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24254.75 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.1 | 189.36 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.55 | 3636.67 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 9.09 | 12979.42 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.34 | 1915.48 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.04 | 1484.51 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 2329.7
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 40598.68
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 121415.72
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 20104.01
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 20155.1
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22617.4305 | 39.7263 | 151.1751 | 0 | 0.0007 | 18709.8652 | 9751.3854
February | 21102.2487 | 37.1907 | 142.0373 | 0 | 0.0006 | 17579.0407 | 9110.7225
March | 24681.462 | 43.499 | 166.1309 | 0 | 0.0008 | 20560.9516 | 10656.0471
April | 26305.2766 | 46.3921 | 177.3071 | 0 | 0.0008 | 21944.1779 | 11360.253
May | 29633.4678 | 52.2617 | 199.7403 | 0 | 0.0009 | 24720.5949 | 12797.5727
June | 30728.4315 | 54.1928 | 207.1208 | 0 | 0.0009 | 25634.0268 | 13270.4461
July | 32553.0981 | 57.4108 | 219.4197 | 0 | 0.001 | 27156.1856 | 14058.4505
August | 33058.0495 | 58.3014 | 222.8232 | 0 | 0.001 | 27577.4222 | 14276.5199
September | 30048.1679 | 52.9931 | 202.5356 | 0 | 0.0009 | 25066.5428 | 12976.666
October | 28478.5427 | 50.2249 | 191.9557 | 0 | 0.0009 | 23757.1426 | 12298.8043
November | 24602.2464 | 43.3887 | 165.8281 | 0 | 0.0008 | 20523.4896 | 10624.7787
December | 22400.0983 | 39.5005 | 150.9502 | 0 | 0.0007 | 18682.145 | 9673.3138
Annual Sum or Average | 326208.5199 | 575.0821 | 2197.024 | 0 | 0.01 | 271911.5849 | 140854.9599
Minimum of Months | 21102.2487 | 37.1907 | 142.0373 | 0 | 0.0006 | 17579.0407 | 9110.7225
Maximum of Months | 33058.0495 | 58.3014 | 222.8232 | 0 | 0.001 | 27577.4222 | 14276.5199
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 127144000000 | 112583.246 | 23-JAN-15:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 47413.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119459000000 | 118847.217 | 22-FEB-15:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 53677.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 139723000000 | 121657.45 | 13-MAR-15:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 56488.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 149123000000 | 128573.235 | 15-APR-15:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 63403.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 167990000000 | 136953.061 | 24-MAY-14:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 71783.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 174197000000 | 144807.141 | 28-JUN-14:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 79637.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 184541000000 | 142162.997 | 13-JUL-14:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 76993.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 187404000000 | 143168.827 | 21-AUG-14:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 77999.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 170341000000 | 137517.03 | 11-SEP-14:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 72347.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 161443000000 | 134481.051 | 06-OCT-15:00 | 34382.155 | 10771.038 | 20016.08 | 0 | 69311.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 139469000000 | 121701.075 | 01-NOV-17:40 | 34382.155 | 10771.038 | 20016.08 | 0 | 53364.518 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 126956000000 | 112859.8 | 15-DEC-17:30 | 34382.155 | 10771.038 | 20016.08 | 0 | 44523.243 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1847790000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119459000000 | 112583.246 |  | 34382.155 | 10771.038 | 20016.08 | 0 | 44523.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 187404000000 | 144807.141 |  | 34382.155 | 10771.038 | 20016.08 | 0 | 79637.868 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43938.23 | 56.75 | 0 | 43994.97
Cost per Total Building Area ($/m2) | 19.15 | 0.02 | 0 | 19.18
Cost per Net Conditioned Building Area ($/m2) | 19.15 | 0.02 | 0 | 19.18
02-Houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1806.82 | 787.63 | 787.63
Net Site Energy | 1806.82 | 787.63 | 787.63
Total Source Energy | 237.26 | 103.43 | 103.43
Net Source Energy | 237.26 | 103.43 | 103.43
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 1.02 | 217.27 | 0 | 0 | 0 | 0
Cooling | 466.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 372.86 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1589.55 | 217.27 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1589.55 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1589.55 | 100
Total On-Site and Utility Electric Sources | 1589.55 | 100
Total Electricity End Uses | 1589.55 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 6.88 | 0.25 | 0.25 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 6.88 | 0.25 | 0.25 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 7.83 | 6.88 | 0.25 | 0.25 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 46280.5 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 206470.12 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25086.8 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23435.43 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.16 | 297.24 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.44 | 3491.48 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 8.76 | 12517.08 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.32 | 1882.72 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.08 | 1542.68 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 3644.42
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 61483.02
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 195563.67
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 31466.93
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 31466.93
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 27511.5735 | 34.7472 | 136.9786 | 0 | 0.0004 | 46719.2993 | 10781.6027
February | 24628.2694 | 31.06 | 121.9856 | 0 | 0.0003 | 41605.413 | 9645.7907
March | 26500.5413 | 34.4766 | 146.0388 | 0 | 0.0004 | 49814.4596 | 10515.1003
April | 27988.5156 | 36.7512 | 158.9847 | 0 | 0.0004 | 54231.8687 | 11149.19
May | 34236.0931 | 44.9982 | 195.0804 | 0 | 0.0005 | 66544.7987 | 13643.4934
June | 38863.0981 | 51.082 | 221.4779 | 0 | 0.0006 | 75549.3612 | 15487.708
July | 41765.0255 | 54.8963 | 238.0157 | 0 | 0.0007 | 81190.6706 | 16644.183
August | 41210.0569 | 54.1669 | 234.853 | 0 | 0.0007 | 80111.8189 | 16423.0172
September | 35500.1937 | 46.6618 | 202.3129 | 0 | 0.0006 | 69011.9184 | 14147.5245
October | 30470.418 | 40.0216 | 173.2432 | 0 | 0.0005 | 59095.6939 | 12139.3292
November | 25684.5658 | 33.5445 | 143.3554 | 0 | 0.0004 | 48899.7186 | 10208.0191
December | 26532.8223 | 33.6385 | 133.8915 | 0 | 0.0004 | 45667.0111 | 10414.4743
Annual Sum or Average | 380891.1731 | 496.0447 | 2106.2178 | 0 | 0.0059 | 718442.0322 | 151199.4325
Minimum of Months | 24628.2694 | 31.06 | 121.9856 | 0 | 0.0003 | 41605.413 | 9645.7907
Maximum of Months | 41765.0255 | 54.8963 | 238.0157 | 0 | 0.0007 | 81190.6706 | 16644.183
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 103367000000 | 98042.072 | 03-JAN-13:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 33454.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 92052100000 | 100181.616 | 23-FEB-15:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 35594.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 110215000000 | 108691.074 | 25-MAR-16:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 44103.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 119988000000 | 125066.158 | 29-APR-15:09 | 34382.155 | 10771.038 | 19433.961 | 0 | 60479.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 147230000000 | 134333.881 | 18-MAY-15:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 69746.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 167153000000 | 135545.156 | 13-JUN-14:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 70958.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 179635000000 | 143106.974 | 05-JUL-15:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 78519.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 177248000000 | 142088.437 | 31-AUG-15:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 77501.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 152689000000 | 139252.648 | 16-SEP-14:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 74665.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 130749000000 | 121288.516 | 06-OCT-15:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 56701.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 108191000000 | 105160.935 | 27-NOV-17:00 | 34382.155 | 10771.038 | 19433.961 | 0 | 37406.497 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 101038000000 | 103834.902 | 02-DEC-13:50 | 34382.155 | 10771.038 | 19433.961 | 0 | 39247.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1589550000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 92052100000 | 98042.072 |  | 34382.155 | 10771.038 | 19433.961 | 0 | 33454.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 179635000000 | 143106.974 |  | 34382.155 | 10771.038 | 19433.961 | 0 | 78519.82 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 54390.67 | 1748.31 | 0 | 56138.98
Cost per Total Building Area ($/m2) | 23.71 | 0.76 | 0 | 24.47
Cost per Net Conditioned Building Area ($/m2) | 23.71 | 0.76 | 0 | 24.47
03-Phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1825.85 | 795.93 | 795.93
Net Site Energy | 1825.85 | 795.93 | 795.93
Total Source Energy | 5516.93 | 2404.95 | 2404.95
Net Source Energy | 5516.93 | 2404.95 | 2404.95
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0.42 | 124.69 | 0 | 0 | 0 | 0
Cooling | 519.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 432.68 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1701.16 | 124.69 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1701.16 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1701.16 | 100
Total On-Site and Utility Electric Sources | 1701.16 | 100
Total Electricity End Uses | 1701.16 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_NR_EXT-WALL | 0.08 | 2.61 | 4.28 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 6.88 | 0.25 | 0.25 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 38.05 | 6.88 | 0.25 | 0.25 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 7.83 | 6.88 | 0.25 | 0.25 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 49603.42 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 156916.3 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27890.21 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28829.31 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.14 | 259.7 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3 | 4280.78 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 9.48 | 13541.88 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.68 | 2406.93 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.54 | 2200.26 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 3069.83
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 52266.3
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 169903.42
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 26355.42
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 26371.77
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22197.4641 | 36.0636 | 115.2169 | 0 | 0.0003 | 851031.0879 | 9291.9066
February | 20018.6944 | 32.753 | 105.566 | 0 | 0.0003 | 779758.0759 | 8403.0462
March | 24370.6587 | 40.8863 | 135.8429 | 0 | 0.0004 | 1003450.1571 | 10332.2539
April | 25647.9464 | 43.336 | 145.1822 | 0 | 0.0004 | 1072452.8617 | 10904.8035
May | 30293.9172 | 51.2016 | 171.5938 | 0 | 0.0005 | 1267554.9497 | 12881.7191
June | 36822.2623 | 62.2356 | 208.5723 | 0 | 0.0006 | 1540713.2886 | 15657.7321
July | 39010.539 | 65.9341 | 220.9674 | 0 | 0.0006 | 1632274.9353 | 16588.2412
August | 38332.0148 | 64.7873 | 217.124 | 0 | 0.0006 | 1603884.1982 | 16299.716
September | 33331.0276 | 56.3348 | 188.7969 | 0 | 0.0005 | 1394633.4083 | 14173.1732
October | 26729.0149 | 45.1726 | 151.3738 | 0 | 0.0004 | 1118190.1632 | 11365.452
November | 22199.3438 | 37.2807 | 124.0087 | 0 | 0.0003 | 916034.5946 | 9415.4543
December | 23012.3884 | 36.909 | 115.9843 | 0 | 0.0003 | 856673.6674 | 9584.6341
Annual Sum or Average | 341965.2715 | 572.8947 | 1900.2295 | 0 | 0.0052 | 14036700 | 144898.1321
Minimum of Months | 20018.6944 | 32.753 | 105.566 | 0 | 0.0003 | 779758.0759 | 8403.0462
Maximum of Months | 39010.539 | 65.9341 | 220.9674 | 0 | 0.0006 | 1632274.9353 | 16588.2412
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 103140000000 | 91891.836 | 28-JAN-14:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 24308.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 94502100000 | 97269.596 | 28-FEB-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 29686.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 121612000000 | 114454.918 | 17-MAR-15:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 46871.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 129975000000 | 118787.128 | 01-APR-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 51204.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 153620000000 | 142515.426 | 27-MAY-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 74932.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 186725000000 | 165028.652 | 28-JUN-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 97445.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 197822000000 | 161329.976 | 19-JUL-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 93746.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 194381000000 | 163805.024 | 01-AUG-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 96221.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 169021000000 | 147007.862 | 09-SEP-15:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 79424.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 135518000000 | 119873.211 | 02-OCT-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 52290.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 111018000000 | 106741.6 | 13-NOV-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 39158.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 103824000000 | 86518.416 | 09-DEC-16:00 | 34382.155 | 10771.038 | 22429.833 | 0 | 18935.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1701160000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 94502100000 | 86518.416 |  | 34382.155 | 10771.038 | 22429.833 | 0 | 18935.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 197822000000 | 165028.652 |  | 34382.155 | 10771.038 | 22429.833 | 0 | 97445.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 47984.5 | 1009.34 | 0 | 48993.84
Cost per Total Building Area ($/m2) | 20.92 | 0.44 | 0 | 21.36
Cost per Net Conditioned Building Area ($/m2) | 20.92 | 0.44 | 0 | 21.36
04-Atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1687.39 | 735.57 | 735.57
Net Site Energy | 1687.39 | 735.57 | 735.57
Total Source Energy | 4823.45 | 2102.65 | 2102.65
Net Source Energy | 4823.45 | 2102.65 | 2102.65
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0.87 | 375.41 | 0 | 0 | 0 | 0
Cooling | 231.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 330.6 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1311.98 | 375.41 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1311.98 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1311.98 | 100
Total On-Site and Utility Electric Sources | 1311.98 | 100
Total Electricity End Uses | 1311.98 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 3.24 | 0.25 | 0.318 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 3.24 | 0.25 | 0.318 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 7.83 | 3.24 | 0.25 | 0.318 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40658.68 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 184982.84 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22800.71 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20709.53 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.14 | 271.48 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.04 | 2913.55 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 7.78 | 11117.51 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.23 | 1756.05 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.97 | 1379.49 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 3218.87
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 55440.57
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 205019.27
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 29139.73
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 29139.14
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23972.0862 | 40.3524 | 91.2472 | 0 | 0.0003 | 162257.7206 | 10013.8892
February | 20736.3627 | 35.604 | 82.3543 | 0 | 0.0003 | 146452.3644 | 8726.7238
March | 20445.33 | 37.6739 | 93.7947 | 0 | 0.0003 | 166826.1305 | 8841.5527
April | 20181.9151 | 38.28 | 97.9367 | 0 | 0.0004 | 174203.9821 | 8828.44
May | 22657.2005 | 43.7265 | 113.6322 | 0 | 0.0004 | 202129.1621 | 9980.6357
June | 25369.2417 | 48.988 | 127.3687 | 0 | 0.0005 | 226563.9186 | 11177.8471
July | 27443.2204 | 52.9928 | 137.7814 | 0 | 0.0005 | 245085.905 | 12091.6552
August | 27489.7076 | 53.0826 | 138.0148 | 0 | 0.0005 | 245501.0659 | 12112.1377
September | 23919.1267 | 46.1878 | 120.0883 | 0 | 0.0004 | 213613.4439 | 10538.9174
October | 20261.3026 | 38.6521 | 99.4077 | 0 | 0.0004 | 176822.4564 | 8883.6216
November | 19405.8696 | 35.4396 | 87.4624 | 0 | 0.0003 | 155560.2754 | 8362.5814
December | 22464.3106 | 38.7705 | 90.195 | 0 | 0.0003 | 160398.0148 | 9472.3456
Annual Sum or Average | 274345.6736 | 509.7501 | 1279.2835 | 0 | 0.0047 | 2275414.4397 | 119030.3474
Minimum of Months | 19405.8696 | 35.4396 | 82.3543 | 0 | 0.0003 | 146452.3644 | 8362.5814
Maximum of Months | 27489.7076 | 53.0826 | 138.0148 | 0 | 0.0005 | 245501.0659 | 12112.1377
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 93556300000 | 68695.243 | 23-JAN-16:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 6375.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 84443000000 | 74994.299 | 18-FEB-16:40 | 34382.155 | 10771.038 | 17166.594 | 0 | 12674.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 96190400000 | 82662.927 | 28-MAR-15:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 20343.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 100444000000 | 102258.8 | 15-APR-15:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 39939.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 116546000000 | 110218.308 | 31-MAY-16:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 47898.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 130635000000 | 119081.179 | 19-JUN-14:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 56761.392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 141314000000 | 130597.261 | 03-JUL-15:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 68277.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 141554000000 | 122715.59 | 17-AUG-14:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 60395.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 123167000000 | 111296.813 | 11-SEP-13:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 48977.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 101954000000 | 101330.349 | 12-OCT-15:00 | 34382.155 | 10771.038 | 17166.594 | 0 | 39010.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 89694600000 | 78009.267 | 22-NOV-15:30 | 34382.155 | 10771.038 | 17166.594 | 0 | 15689.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 92484000000 | 66634.081 | 01-DEC-17:30 | 34382.155 | 10771.038 | 17166.594 | 0 | 1147.009 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1311980000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 84443000000 | 66634.081 |  | 34382.155 | 10771.038 | 17166.594 | 0 | 1147.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 141554000000 | 130597.261 |  | 34382.155 | 10771.038 | 17166.594 | 0 | 68277.474 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37074.33 | 3543.66 | 0 | 40617.98
Cost per Total Building Area ($/m2) | 16.16 | 1.54 | 0 | 17.71
Cost per Net Conditioned Building Area ($/m2) | 16.16 | 1.54 | 0 | 17.71
05-Los Angeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1190.6 | 519.01 | 519.01
Net Site Energy | 1190.6 | 519.01 | 519.01
Total Source Energy | 3531.81 | 1539.59 | 1539.59
Net Source Energy | 3531.81 | 1539.59 | 1539.59
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0.14 | 76.43 | 0 | 0 | 0 | 0
Cooling | 96.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 268.56 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1114.17 | 76.43 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1114.17 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1114.17 | 100
Total On-Site and Utility Electric Sources | 1114.17 | 100
Total Electricity End Uses | 1114.17 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 3.24 | 0.25 | 0.318 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 3.24 | 0.25 | 0.318 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 7.83 | 3.24 | 0.25 | 0.318 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23525.64 | 3.05
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 107149.36 | 3.05
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18806.38 | 3.05
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14188.16 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.09 | 169.85 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.42 | 2030.26 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 6.47 | 9246.99 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.14 | 1622.99 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.86 | 1224.44 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 2082.29
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 38199.05
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 135199.3
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 18896.84
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 18892.28
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8715.4721 | 7.5137 | 71.4035 | 0 | 0 | 430804.584 | 3234.2888
February | 7731.501 | 6.658 | 64.6745 | 0 | 0 | 390210.8014 | 2873.2047
March | 8438.6673 | 7.2505 | 73.5363 | 0 | 0 | 443689.21 | 3144.9932
April | 7915.5911 | 6.7896 | 71.0276 | 0 | 0 | 428560.2968 | 2956.3019
May | 8240.9619 | 7.057 | 76.0322 | 0 | 0 | 458763.885 | 3084.1821
June | 8168.2415 | 6.991 | 76.032 | 0 | 0 | 458764.7442 | 3059.0128
July | 8779.1965 | 7.513 | 81.8761 | 0 | 0 | 494027.5503 | 3288.2954
August | 9349.8357 | 8.0014 | 87.1915 | 0 | 0 | 526099.9245 | 3502.0117
September | 8586.1257 | 7.3479 | 80.0568 | 0 | 0 | 483049.8874 | 3215.9226
October | 8252.2686 | 7.0654 | 76.368 | 0 | 0 | 460790.2957 | 3089.1197
November | 7897.9525 | 6.776 | 70.5908 | 0 | 0 | 425923.7704 | 2948.8645
December | 8471.2005 | 7.2896 | 71.8125 | 0 | 0 | 433281.4344 | 3150.9939
Annual Sum or Average | 100547.0144 | 86.253 | 900.6019 | 0 | 0.0004 | 5433966.3842 | 37547.1914
Minimum of Months | 7731.501 | 6.658 | 64.6745 | 0 | 0 | 390210.8014 | 2873.2047
Maximum of Months | 9349.8357 | 8.0014 | 87.1915 | 0 | 0 | 526099.9245 | 3502.0117
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 88331100000 | 79483.672 | 26-JAN-14:09 | 34382.155 | 10771.038 | 14124.681 | 0 | 20205.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 80007900000 | 74158.721 | 13-FEB-11:50 | 34382.155 | 10771.038 | 14124.681 | 0 | 14880.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 90973000000 | 77190.965 | 31-MAR-14:00 | 34382.155 | 10771.038 | 14124.681 | 0 | 17913.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 87871000000 | 85411.729 | 11-APR-15:00 | 34382.155 | 10771.038 | 14124.681 | 0 | 26133.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 94063800000 | 82963.362 | 30-MAY-14:20 | 34382.155 | 10771.038 | 14124.681 | 0 | 23685.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 94064000000 | 82827.936 | 30-JUN-14:00 | 34382.155 | 10771.038 | 14124.681 | 0 | 23550.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 101294000000 | 86306.716 | 10-JUL-14:00 | 34382.155 | 10771.038 | 14124.681 | 0 | 27028.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 107870000000 | 92977.074 | 08-AUG-14:00 | 34382.155 | 10771.038 | 14124.681 | 0 | 33699.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 99043400000 | 89503.408 | 23-SEP-13:00 | 34382.155 | 10771.038 | 14124.681 | 0 | 30225.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 94479300000 | 83445.223 | 19-OCT-11:09 | 34382.155 | 10771.038 | 14124.681 | 0 | 24167.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 87330400000 | 79680.577 | 20-NOV-11:00 | 34382.155 | 10771.038 | 14124.681 | 0 | 20402.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 88839000000 | 79431.471 | 19-DEC-13:09 | 34382.155 | 10771.038 | 14124.681 | 0 | 20153.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1114170000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 80007900000 | 74158.721 |  | 34382.155 | 10771.038 | 14124.681 | 0 | 14880.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 107870000000 | 92977.074 |  | 34382.155 | 10771.038 | 14124.681 | 0 | 33699.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40611.35 | 670.29 | 0 | 41281.65
Cost per Total Building Area ($/m2) | 17.7 | 0.29 | 0 | 18
Cost per Net Conditioned Building Area ($/m2) | 17.7 | 0.29 | 0 | 18
06-Las Vegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1630.23 | 710.65 | 710.65
Net Site Energy | 1630.23 | 710.65 | 710.65
Total Source Energy | 5374.44 | 2342.83 | 2342.83
Net Source Energy | 5374.44 | 2342.83 | 2342.83
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0.35 | 183.86 | 0 | 0 | 0 | 0
Cooling | 314.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 382.26 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1446.37 | 183.86 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1446.37 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1446.37 | 100
Total On-Site and Utility Electric Sources | 1446.37 | 100
Total Electricity End Uses | 1446.37 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 3.24 | 0.25 | 0.318 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 38.05 | 3.24 | 0.25 | 0.318 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 7.83 | 3.24 | 0.25 | 0.318 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40180.81 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 148495.54 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24408.91 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19425.16 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.13 | 244.88 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.43 | 3467.6 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 8.97 | 12815.17 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.47 | 2106.49 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.17 | 1676.39 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 2784.21
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 48305.67
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 178764.19
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 24934.94
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 24937.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24675.3395 | 38.0895 | 147.5783 | 0 | 0.0003 | 735930.3565 | 10171.087
February | 20514.7775 | 32.7607 | 132.974 | 0 | 0.0003 | 663146.8551 | 8569.7855
March | 23184.3396 | 37.1076 | 151.0652 | 0 | 0.0003 | 753371.4203 | 9693.6683
April | 24110.8541 | 39.4478 | 165.16 | 0 | 0.0003 | 823695.1193 | 10170.1599
May | 27992.5668 | 45.8644 | 192.3677 | 0 | 0.0004 | 959389.256 | 11814.3313
June | 34293.8954 | 56.2395 | 236.1472 | 0 | 0.0004 | 1177731.0333 | 14479.0875
July | 37014.6964 | 60.7014 | 254.8826 | 0 | 0.0005 | 1271169.5783 | 15627.8259
August | 37091.0981 | 60.8267 | 255.4087 | 0 | 0.0005 | 1273793.3899 | 15660.0831
September | 31233.6095 | 51.2209 | 215.0742 | 0 | 0.0004 | 1072633.7943 | 13187.0165
October | 24890.8019 | 40.7213 | 170.4785 | 0 | 0.0003 | 850219.3816 | 10498.8804
November | 21574.5053 | 34.6847 | 142.0208 | 0 | 0.0003 | 708272.3115 | 9036.5554
December | 23952.048 | 37.3657 | 146.9436 | 0 | 0.0003 | 732781.1437 | 9913.7659
Annual Sum or Average | 330528.5321 | 535.0304 | 2210.1009 | 0 | 0.0042 | 11022100 | 138822.2465
Minimum of Months | 20514.7775 | 32.7607 | 132.974 | 0 | 0.0003 | 663146.8551 | 8569.7855
Maximum of Months | 37091.0981 | 60.8267 | 255.4087 | 0 | 0.0005 | 1273793.3899 | 15660.0831
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 96571800000 | 68631.004 | 02-JAN-16:49 | 34382.155 | 10771.038 | 20310.526 | 0 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 87020800000 | 73216.057 | 08-FEB-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 7997.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 98860400000 | 88347.369 | 31-MAR-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 23128.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 108089000000 | 108554.554 | 21-APR-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 43335.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 125895000000 | 120626.601 | 31-MAY-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 55407.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 154547000000 | 144614.623 | 27-JUN-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 79395.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 166808000000 | 141006.581 | 24-JUL-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 75787.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 167152000000 | 136353.88 | 04-AUG-14:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 71135.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 140755000000 | 131867.788 | 01-SEP-14:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 66648.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 111569000000 | 107619.736 | 03-OCT-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 42400.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 92942400000 | 75575.747 | 10-NOV-15:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 10356.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 96158500000 | 73504.579 | 05-DEC-14:00 | 34382.155 | 10771.038 | 20065.648 | 0 | 8285.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1446370000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 87020800000 | 68631.004 |  | 34382.155 | 10771.038 | 20065.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 167152000000 | 144614.623 |  | 34382.155 | 10771.038 | 20310.526 | 0 | 79395.782 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 39892.02 | 1395.66 | 0 | 41287.68
Cost per Total Building Area ($/m2) | 17.39 | 0.61 | 0 | 18
Cost per Net Conditioned Building Area ($/m2) | 17.39 | 0.61 | 0 | 18
07-San Francisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1326.96 | 578.45 | 578.45
Net Site Energy | 1326.96 | 578.45 | 578.45
Total Source Energy | 3538.33 | 1542.43 | 1542.43
Net Source Energy | 3538.33 | 1542.43 | 1542.43
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0.91 | 283.88 | 0 | 0 | 0 | 0
Cooling | 38.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 255.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1043.08 | 283.88 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1043.08 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1043.08 | 100
Total On-Site and Utility Electric Sources | 1043.08 | 100
Total Electricity End Uses | 1043.08 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 38.05 | 6.88 | 0.39 | 0.39 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 38.05 | 6.88 | 0.39 | 0.39 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 7.83 | 6.88 | 0.39 | 0.39 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25926.57 | 3.05
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 89857.78 | 3.05
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21417.41 | 3.05
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17633.5 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.12 | 218.35 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.57 | 2237.46 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 5.43 | 7754.73 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.29 | 1848.32 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.07 | 1521.77 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 2685.77
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 42921.4
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 160756.49
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 23131.6
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 23126.97
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10914.8725 | 9.5213 | 69.4833 | 0 | 0 | 419143.6998 | 3989.6465
February | 8404.4163 | 7.2776 | 63.1177 | 0 | 0 | 380791.5028 | 3101.3522
March | 9482.6825 | 8.2126 | 70.9744 | 0 | 0 | 428190.0489 | 3498.5124
April | 8478.7512 | 7.3183 | 67.9041 | 0 | 0 | 409685.684 | 3141.6829
May | 8268.1425 | 7.1089 | 71.1603 | 0 | 0 | 429350.2692 | 3078.7253
June | 7939.261 | 6.8144 | 70.4403 | 0 | 0 | 425013.9495 | 2962.7023
July | 8054.845 | 6.9041 | 73.1549 | 0 | 0 | 441398.7714 | 3010.9882
August | 8326.6031 | 7.1383 | 75.4053 | 0 | 0 | 454976.0443 | 3111.9098
September | 8103.4069 | 6.9476 | 73.2679 | 0 | 0 | 442079.1967 | 3028.1401
October | 8261.3009 | 7.0987 | 71.8825 | 0 | 0 | 433710.4123 | 3078.5607
November | 8419.394 | 7.2685 | 67.1694 | 0 | 0 | 405251.5049 | 3118.8975
December | 10540.1977 | 9.1825 | 69.238 | 0 | 0 | 417674.1275 | 3859.2224
Annual Sum or Average | 105193.8734 | 90.7927 | 843.198 | 0 | 0.0004 | 5087265.2115 | 38980.3403
Minimum of Months | 7939.261 | 6.8144 | 63.1177 | 0 | 0 | 380791.5028 | 2962.7023
Maximum of Months | 10914.8725 | 9.5213 | 75.4053 | 0 | 0 | 454976.0443 | 3989.6465
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85940200000 | 62113.768 | 17-JAN-17:19 | 34382.155 | 10771.038 | 13362.282 | 0 | 431.009 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 78076600000 | 69281.797 | 15-FEB-16:10 | 34382.155 | 10771.038 | 13362.282 | 0 | 10766.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 87795000000 | 62566.591 | 01-MAR-13:39 | 34382.155 | 10771.038 | 13362.282 | 0 | 4051.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 84001000000 | 74727.832 | 29-APR-14:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 16212.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 88032900000 | 76712.766 | 17-MAY-13:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 18197.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 87143800000 | 79511.709 | 16-JUN-14:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 20996.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 90503300000 | 88432.101 | 03-JUL-12:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 29916.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 93287200000 | 81737.399 | 15-AUG-11:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 23221.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 90642800000 | 96450.345 | 28-SEP-14:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 37934.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 88926900000 | 75789.171 | 13-OCT-15:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 17273.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 83091800000 | 63257.13 | 14-NOV-16:00 | 34382.155 | 10771.038 | 13362.282 | 0 | 1574.371 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 85638900000 | 61978.19 | 02-DEC-17:00 | 34382.155 | 10771.038 | 13580.634 | 77.078 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1043080000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 78076600000 | 61978.19 |  | 34382.155 | 10771.038 | 13362.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 93287200000 | 96450.345 |  | 34382.155 | 10771.038 | 13580.634 | 77.078 | 37934.869 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43538.65 | 2456.87 | 0 | 45995.53
Cost per Total Building Area ($/m2) | 18.98 | 1.07 | 0 | 20.05
Cost per Net Conditioned Building Area ($/m2) | 18.98 | 1.07 | 0 | 20.05
08-Baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1975.84 | 861.31 | 861.31
Net Site Energy | 1975.84 | 861.31 | 861.31
Total Source Energy | 5307.53 | 2313.66 | 2313.66
Net Source Energy | 5307.53 | 2313.66 | 2313.66
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 1.59 | 707.76 | 0 | 0 | 0 | 0
Cooling | 185.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 332.03 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1268.08 | 707.76 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1268.08 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1268.08 | 100
Total On-Site and Utility Electric Sources | 1268.08 | 100
Total Electricity End Uses | 1268.08 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 3.24 | 0.39 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 44026.73 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 177313.62 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22663.01 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22135.59 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.15 | 291.38 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.16 | 3084.89 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 7.41 | 10579.62 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.21 | 1731.27 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.04 | 1491.18 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 3567
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 61087.55
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 226956.11
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 32524.35
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 32521.53
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26456.0935 | 41.5864 | 97.1375 | 0 | 0.0004 | 6038.1772 | 10763.2565
February | 21981.6698 | 35.6007 | 86.4936 | 0 | 0.0004 | 5377.047 | 9038.6995
March | 19954.6755 | 35.4197 | 95.6446 | 0 | 0.0004 | 5947.3275 | 8488.8338
April | 16744.0942 | 31.692 | 91.1395 | 0 | 0.0004 | 5667.9221 | 7303.2653
May | 17790.3122 | 35.1789 | 105.1539 | 0 | 0.0004 | 6539.9616 | 7897.3691
June | 21181.2739 | 42.3427 | 127.7278 | 0 | 0.0005 | 7944.0652 | 9444.5751
July | 23330.0903 | 46.6463 | 140.73 | 0 | 0.0006 | 8752.7393 | 10403.4502
August | 23796.527 | 47.5768 | 143.5322 | 0 | 0.0006 | 8927.02 | 10611.2561
September | 18470.9218 | 36.8433 | 110.9356 | 0 | 0.0004 | 6899.6465 | 8228.6273
October | 17828.6903 | 34.357 | 100.4235 | 0 | 0.0004 | 6245.4863 | 7832.3129
November | 18474.3544 | 33.3961 | 91.8845 | 0 | 0.0004 | 5713.7408 | 7914.3276
December | 24029.8431 | 39.0389 | 95.2212 | 0 | 0.0004 | 5919.6699 | 9891.9624
Annual Sum or Average | 250038.5461 | 459.6789 | 1286.0239 | 0 | 0.0053 | 79972.8034 | 107817.9357
Minimum of Months | 16744.0942 | 31.692 | 86.4936 | 0 | 0.0004 | 5377.047 | 7303.2653
Maximum of Months | 26456.0935 | 47.5768 | 143.5322 | 0 | 0.0006 | 8927.02 | 10763.2565
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 95743800000 | 65664.039 | 24-JAN-17:00 | 34382.155 | 10771.038 | 17178.329 | 165.232 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 85260600000 | 65498.807 | 02-FEB-17:40 | 34382.155 | 10771.038 | 17178.329 | 0 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 94303200000 | 82011.721 | 09-MAR-15:09 | 34382.155 | 10771.038 | 16886.952 | 0 | 19971.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 89872900000 | 85203.021 | 04-APR-15:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 23162.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 103700000000 | 101644.063 | 15-MAY-15:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 39603.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 125964000000 | 127020.554 | 30-JUN-16:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 64980.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 138787000000 | 130962.125 | 25-JUL-12:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 68921.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 141550000000 | 131727.543 | 09-AUG-14:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 69687.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 109404000000 | 111587.729 | 09-SEP-14:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 49547.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 99031000000 | 96369.143 | 03-OCT-14:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 34328.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 90599400000 | 88673.716 | 04-NOV-12:00 | 34382.155 | 10771.038 | 16886.952 | 0 | 26633.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 93864700000 | 65693.327 | 15-DEC-16:00 | 34382.155 | 10771.038 | 17178.329 | 194.52 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1268080000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 85260600000 | 65498.807 |  | 34382.155 | 10771.038 | 16886.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 141550000000 | 131727.543 |  | 34382.155 | 10771.038 | 17178.329 | 194.52 | 69687.398 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27208.82 | 6823.99 | 0 | 34032.81
Cost per Total Building Area ($/m2) | 11.86 | 2.97 | 0 | 14.84
Cost per Net Conditioned Building Area ($/m2) | 11.86 | 2.97 | 0 | 14.84
09-Albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1669.53 | 727.78 | 727.78
Net Site Energy | 1669.53 | 727.78 | 727.78
Total Source Energy | 4606.21 | 2007.94 | 2007.94
Net Source Energy | 4606.21 | 2007.94 | 2007.94
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0.81 | 419.27 | 0 | 0 | 0 | 0
Cooling | 165.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 335.16 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1250.26 | 419.27 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1250.26 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1250.26 | 100
Total On-Site and Utility Electric Sources | 1250.26 | 100
Total Electricity End Uses | 1250.26 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 3.24 | 0.39 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33930.14 | 3.05
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 126796.39 | 3.05
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22129.27 | 3.05
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18384.62 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.16 | 298.86 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.05 | 2928.17 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 7.66 | 10942.53 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.34 | 1909.76 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.11 | 1586.59 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 3025.38
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 47885.98
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 170710.34
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 26051.38
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 26051.38
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 30233.2943 | 48.4917 | 114.0554 | 0 | 0.0005 | 118571.2549 | 12528.4459
February | 25795.3087 | 42.3471 | 102.5823 | 0 | 0.0004 | 106651.3553 | 10784.8714
March | 27994.4341 | 46.8791 | 116.3173 | 0 | 0.0005 | 120937.8804 | 11794.7375
April | 26039.0581 | 44.9718 | 115.5918 | 0 | 0.0005 | 120193.1679 | 11104.9833
May | 29480.5903 | 51.5959 | 134.5517 | 0 | 0.0005 | 139912.1731 | 12639.4407
June | 31505.1049 | 55.2751 | 144.5278 | 0 | 0.0006 | 150286.5832 | 13520.7659
July | 34207.582 | 60.0185 | 156.9357 | 0 | 0.0006 | 163188.9258 | 14680.7538
August | 33728.3637 | 59.1777 | 154.7372 | 0 | 0.0006 | 160902.7919 | 14475.0893
September | 29176.5798 | 51.1778 | 133.7807 | 0 | 0.0005 | 139111.2292 | 12520.2739
October | 26973.9361 | 46.6133 | 119.8876 | 0 | 0.0005 | 124660.1261 | 11506.325
November | 26862.4128 | 44.6545 | 109.833 | 0 | 0.0004 | 114193.7654 | 11285.5186
December | 30416.2073 | 48.6248 | 113.8778 | 0 | 0.0005 | 118385.4452 | 12588.5206
Annual Sum or Average | 352412.8722 | 599.8273 | 1516.6782 | 0 | 0.006 | 1576994.6984 | 149429.7258
Minimum of Months | 25795.3087 | 42.3471 | 102.5823 | 0 | 0.0004 | 106651.3553 | 10784.8714
Maximum of Months | 34207.582 | 60.0185 | 156.9357 | 0 | 0.0006 | 163188.9258 | 14680.7538
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94004700000 | 67466.055 | 26-JAN-17:30 | 34382.155 | 10771.038 | 17367.049 | 0 | 1778.529 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 84554500000 | 74209.391 | 14-FEB-15:00 | 34382.155 | 10771.038 | 17367.049 | 0 | 11689.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 95881000000 | 75903.692 | 02-MAR-15:39 | 34382.155 | 10771.038 | 17367.049 | 0 | 13383.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 95290600000 | 92028.011 | 22-APR-13:00 | 34382.155 | 10771.038 | 17367.049 | 0 | 29507.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 110924000000 | 98789.59 | 31-MAY-16:00 | 34382.155 | 10771.038 | 17367.049 | 0 | 36269.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 119149000000 | 109183.734 | 29-JUN-14:09 | 34382.155 | 10771.038 | 17367.049 | 0 | 46663.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 129378000000 | 113400.45 | 31-JUL-14:00 | 34382.155 | 10771.038 | 17367.049 | 0 | 50880.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 127566000000 | 110927.617 | 01-AUG-14:09 | 34382.155 | 10771.038 | 17367.049 | 0 | 48407.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 110289000000 | 98253.041 | 02-SEP-14:00 | 34382.155 | 10771.038 | 17367.049 | 0 | 35732.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 98832000000 | 87186.972 | 13-OCT-14:00 | 34382.155 | 10771.038 | 17367.049 | 0 | 24666.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 90534200000 | 72429.182 | 08-NOV-17:10 | 34382.155 | 10771.038 | 17367.049 | 0 | 6741.656 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 93857400000 | 67181.963 | 05-DEC-16:49 | 34382.155 | 10771.038 | 17367.049 | 0 | 1494.437 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1250260000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 84554500000 | 67181.963 |  | 34382.155 | 10771.038 | 17367.049 | 0 | 1494.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 129378000000 | 113400.45 |  | 34382.155 | 10771.038 | 17367.049 | 0 | 50880.208 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13017.4 | 2868.24 | 0 | 15885.65
Cost per Total Building Area ($/m2) | 5.67 | 1.25 | 0 | 6.92
Cost per Net Conditioned Building Area ($/m2) | 5.67 | 1.25 | 0 | 6.92
10-Seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1738.07 | 757.66 | 757.66
Net Site Energy | 1738.07 | 757.66 | 757.66
Total Source Energy | 2598.07 | 1132.55 | 1132.55
Net Source Energy | 2598.07 | 1132.55 | 1132.55
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 1.5 | 660.99 | 0 | 0 | 0 | 0
Cooling | 44.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 282.68 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1077.08 | 660.99 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1077.08 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1077.08 | 100
Total On-Site and Utility Electric Sources | 1077.08 | 100
Total Electricity End Uses | 1077.08 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-5.7 CI_EXT-WALL | 0.08 | 0.856 | 0.98 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 3.24 | 0.39 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31925.86 | 3.05
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 96487.11 | 3.05
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22337.95 | 3.05
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18392.23 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.13 | 251.14 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.93 | 2755.2 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 5.83 | 8326.84 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.35 | 1927.77 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.11 | 1587.25 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 3046.9
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 53211.84
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 198863.39
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 27712.44
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 27711.12
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11189.5692 | 13.1587 | 19.2125 | 0 | 0.0001 | 253490.9295 | 4194.2156
February | 8458.2417 | 10.3615 | 17.1708 | 0 | 0.0001 | 226657.7804 | 3214.8434
March | 8860.2684 | 11.0765 | 19.408 | 0 | 0.0001 | 256235.8641 | 3391.4834
April | 6708.8442 | 8.9428 | 18.2447 | 0 | 0.0001 | 240987.6347 | 2627.5103
May | 5359.1939 | 7.9011 | 19.41 | 0 | 0.0001 | 256500.5919 | 2180.0362
June | 4758.9917 | 7.3716 | 19.5052 | 0 | 0.0001 | 257802.2511 | 1973.9457
July | 4787.6961 | 7.6091 | 20.8552 | 0 | 0.0001 | 275664.6544 | 2006.5222
August | 4874.4285 | 7.7841 | 21.4699 | 0 | 0.0001 | 283793.9557 | 2046.846
September | 5068.4616 | 7.6883 | 19.7346 | 0 | 0.0001 | 260816.3566 | 2084.8792
October | 6120.0978 | 8.5066 | 18.8688 | 0 | 0.0001 | 249286.8161 | 2434.2545
November | 8830.0388 | 10.8852 | 18.3615 | 0 | 0.0001 | 242388.6581 | 3363.4685
December | 11186.2497 | 13.1513 | 19.1844 | 0 | 0.0001 | 253118.7369 | 4192.5949
Annual Sum or Average | 86202.0816 | 114.4369 | 231.4256 | 0 | 0.001 | 3056744.2297 | 33710.5999
Minimum of Months | 4758.9917 | 7.3716 | 17.1708 | 0 | 0.0001 | 226657.7804 | 1973.9457
Maximum of Months | 11189.5692 | 13.1587 | 21.4699 | 0 | 0.0001 | 283793.9557 | 4194.2156
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 89320300000 | 63332.249 | 09-JAN-17:49 | 34382.155 | 10771.038 | 14848.195 | 163.577 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 79865300000 | 63498.915 | 21-FEB-17:40 | 34382.155 | 10771.038 | 14597.054 | 0 | 581.384 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 90287500000 | 69128.791 | 29-MAR-15:00 | 34382.155 | 10771.038 | 14597.054 | 0 | 9378.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 84914600000 | 71322.213 | 29-APR-15:50 | 34382.155 | 10771.038 | 14597.054 | 0 | 11571.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 90380800000 | 79100.984 | 15-MAY-16:00 | 34382.155 | 10771.038 | 14597.054 | 0 | 19350.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 90839400000 | 85500.702 | 28-JUN-14:00 | 34382.155 | 10771.038 | 14597.054 | 0 | 25750.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 97133400000 | 93436.576 | 24-JUL-14:00 | 34382.155 | 10771.038 | 14597.054 | 0 | 33686.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 99997900000 | 89842.09 | 07-AUG-14:00 | 34382.155 | 10771.038 | 14597.054 | 0 | 30091.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 91901500000 | 105086.247 | 02-SEP-15:00 | 34382.155 | 10771.038 | 14597.054 | 0 | 45335.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 87838900000 | 70136.87 | 17-OCT-15:39 | 34382.155 | 10771.038 | 14597.054 | 0 | 10386.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 85408300000 | 64852.951 | 04-NOV-16:49 | 34382.155 | 10771.038 | 14597.054 | 0 | 1935.42 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 89189100000 | 63348.465 | 13-DEC-17:00 | 34382.155 | 10771.038 | 14848.195 | 179.793 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1077080000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 79865300000 | 63332.249 |  | 34382.155 | 10771.038 | 14597.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 99997900000 | 105086.247 |  | 34382.155 | 10771.038 | 14848.195 | 179.793 | 45335.999 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22684.45 | 5582.67 | 0 | 28267.12
Cost per Total Building Area ($/m2) | 9.89 | 2.43 | 0 | 12.32
Cost per Net Conditioned Building Area ($/m2) | 9.89 | 2.43 | 0 | 12.32
11-Chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2247.91 | 979.91 | 979.91
Net Site Energy | 2247.91 | 979.91 | 979.91
Total Source Energy | 5449.86 | 2375.71 | 2375.71
Net Source Energy | 5449.86 | 2375.71 | 2375.71
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 2.38 | 1027.4 | 0 | 0 | 0 | 0
Cooling | 139.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 330.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1220.51 | 1027.4 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1220.51 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1220.51 | 100
Total On-Site and Utility Electric Sources | 1220.51 | 100
Total Electricity End Uses | 1220.51 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 3.24 | 0.39 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 46430.14 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 169419.41 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22616.29 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22993 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.18 | 337.18 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.2 | 3146.91 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 6.96 | 9943.11 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.2 | 1710.91 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.1 | 1568.77 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 4058.42
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 64353.21
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 245478.08
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 36091.19
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 36086.51
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 46853.1236 | 72.8153 | 181.7541 | 0 | 0.0006 | 41825.6402 | 19111.6532
February | 39171.6841 | 62.3633 | 160.8636 | 0 | 0.0005 | 37020.9845 | 16120.418
March | 39410.8327 | 65.118 | 176.0768 | 0 | 0.0005 | 40526.2649 | 16445.8104
April | 32731.161 | 57.1825 | 164.8249 | 0 | 0.0005 | 37941.4344 | 13954.9502
May | 35147.3445 | 63.4581 | 189.3078 | 0 | 0.0006 | 43580.0993 | 15181.515
June | 40155.514 | 73.0905 | 219.8207 | 0 | 0.0007 | 50605.1712 | 17401.1717
July | 44455.552 | 80.9482 | 243.5451 | 0 | 0.0007 | 56066.8346 | 19267.5201
August | 42766.0459 | 77.8602 | 234.2196 | 0 | 0.0007 | 53919.9949 | 18534.1585
September | 35524.6946 | 64.5022 | 193.5151 | 0 | 0.0006 | 44549.1353 | 15379.1945
October | 33635.219 | 59.6486 | 174.6931 | 0 | 0.0005 | 40214.252 | 14425.174
November | 36238.908 | 60.7389 | 167.0721 | 0 | 0.0005 | 38455.0723 | 15204.594
December | 44487.0018 | 70.2739 | 179.3843 | 0 | 0.0006 | 41282.3776 | 18255.0953
Annual Sum or Average | 470577.0812 | 807.9997 | 2285.0772 | 0 | 0.007 | 525987.2611 | 199281.2548
Minimum of Months | 32731.161 | 57.1825 | 160.8636 | 0 | 0.0005 | 37020.9845 | 13954.9502
Maximum of Months | 46853.1236 | 80.9482 | 243.5451 | 0 | 0.0007 | 56066.8346 | 19267.5201
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 97053200000 | 65272.97 | 28-JAN-17:00 | 34382.155 | 10771.038 | 16706.878 | 245.615 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 85904400000 | 65046.1 | 01-FEB-17:00 | 34382.155 | 10771.038 | 16706.878 | 18.745 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 94038100000 | 71133.896 | 31-MAR-14:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 9611.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 88040200000 | 76037.759 | 07-APR-14:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 14514.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 101124000000 | 101354.186 | 30-MAY-15:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 39831.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 117425000000 | 120785.298 | 08-JUN-12:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 59262.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 130099000000 | 123907.935 | 13-JUL-14:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 62385.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 125117000000 | 121441.443 | 04-AUG-15:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 59918.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 103373000000 | 102374.267 | 05-SEP-14:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 40851.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 93314100000 | 84857.926 | 31-OCT-16:49 | 34382.155 | 10771.038 | 16369.702 | 0 | 20167.747 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 89232100000 | 83085.592 | 02-NOV-14:00 | 34382.155 | 10771.038 | 16369.702 | 0 | 21562.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 95792600000 | 65164.673 | 14-DEC-17:00 | 34382.155 | 10771.038 | 16706.878 | 137.318 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1220510000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 85904400000 | 65046.1 |  | 34382.155 | 10771.038 | 16369.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 130099000000 | 123907.935 |  | 34382.155 | 10771.038 | 16706.878 | 245.615 | 62385.04 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17640.47 | 8491.34 | 0 | 26131.81
Cost per Total Building Area ($/m2) | 7.69 | 3.7 | 0 | 11.39
Cost per Net Conditioned Building Area ($/m2) | 7.69 | 3.7 | 0 | 11.39
12-Boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1893.5 | 825.42 | 825.42
Net Site Energy | 1893.5 | 825.42 | 825.42
Total Source Energy | 4764.67 | 2077.02 | 2077.02
Net Source Energy | 4764.67 | 2077.02 | 2077.02
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 1.45 | 681.93 | 0 | 0 | 0 | 0
Cooling | 92.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 368.69 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1211.58 | 681.93 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1211.58 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1211.58 | 100
Total On-Site and Utility Electric Sources | 1211.58 | 100
Total Electricity End Uses | 1211.58 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-7.6 CI_EXT-WALL | 0.08 | 0.698 | 0.78 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 3.24 | 0.39 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 45789.01 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 123303.23 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23783.08 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22321.16 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.21 | 389.41 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.77 | 3951.59 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 7.45 | 10641.07 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.44 | 2052.48 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.35 | 1926.32 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 3935.19
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 64673.87
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 240433.1
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 34948.5
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 34948.5
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 34092.3377 | 53.0654 | 119.8677 | 0 | 0.0005 | 124601.2571 | 13969.1027
February | 28929.5532 | 45.8634 | 106.2292 | 0 | 0.0004 | 110431.0836 | 11935.4883
March | 30038.3235 | 49.1086 | 118.3514 | 0 | 0.0005 | 123044.5454 | 12538.8375
April | 26237.5931 | 44.4571 | 111.8318 | 0 | 0.0004 | 116277.894 | 11105.5397
May | 27205.7724 | 47.0145 | 120.9211 | 0 | 0.0005 | 125734.7206 | 11605.2749
June | 28316.4661 | 49.5003 | 128.9234 | 0 | 0.0005 | 134059.2842 | 12134.6256
July | 31823.9986 | 55.8364 | 146.0001 | 0 | 0.0006 | 151817.6436 | 13657.7943
August | 31435.388 | 55.1403 | 144.1399 | 0 | 0.0006 | 149883.2011 | 13489.6133
September | 27645.396 | 48.1519 | 124.9195 | 0 | 0.0005 | 129894.8067 | 11829.8582
October | 27228.1563 | 46.4048 | 117.5113 | 0 | 0.0005 | 122185.005 | 11551.2263
November | 28708.1533 | 46.7074 | 111.8842 | 0 | 0.0004 | 116319.1392 | 11961.3616
December | 34207.9528 | 53.0553 | 119.2452 | 0 | 0.0005 | 123952.6672 | 13997.828
Annual Sum or Average | 355869.091 | 594.3053 | 1469.8249 | 0 | 0.0058 | 1528201.2477 | 149776.5503
Minimum of Months | 26237.5931 | 44.4571 | 106.2292 | 0 | 0.0004 | 110431.0836 | 11105.5397
Maximum of Months | 34207.9528 | 55.8364 | 146.0001 | 0 | 0.0006 | 151817.6436 | 13997.828
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 98785400000 | 67281.348 | 09-JAN-17:00 | 34382.155 | 10771.038 | 18960.871 | 0 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 87551100000 | 67397.419 | 15-FEB-17:00 | 34382.155 | 10771.038 | 18960.871 | 116.07 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 97551200000 | 79765.723 | 30-MAR-16:49 | 34382.155 | 10771.038 | 18571.456 | 0 | 16041.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 92186500000 | 87336.412 | 25-APR-14:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 23611.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 99684000000 | 96258.839 | 23-MAY-15:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 32534.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 106284000000 | 106628.651 | 28-JUN-13:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 42904.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 120363000000 | 110805.499 | 17-JUL-15:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 47080.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 118829000000 | 111256.858 | 30-AUG-13:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 47532.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 102982000000 | 105082.3 | 02-SEP-14:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 41357.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 96869700000 | 92729.794 | 05-OCT-14:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 29005.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 92219200000 | 67742.024 | 10-NOV-13:00 | 34382.155 | 10771.038 | 18571.456 | 0 | 4017.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 98271200000 | 67352.141 | 09-DEC-17:00 | 34382.155 | 10771.038 | 18960.871 | 70.793 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1211580000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 87551100000 | 67281.348 |  | 34382.155 | 10771.038 | 18571.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 120363000000 | 111256.858 |  | 34382.155 | 10771.038 | 18960.871 | 116.07 | 47532.209 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12620.59 | 4686.98 | 0 | 17307.58
Cost per Total Building Area ($/m2) | 5.5 | 2.04 | 0 | 7.54
Cost per Net Conditioned Building Area ($/m2) | 5.5 | 2.04 | 0 | 7.54
13-Minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2642.79 | 1152.05 | 1152.05
Net Site Energy | 2642.79 | 1152.05 | 1152.05
Total Source Energy | 5745.72 | 2504.68 | 2504.68
Net Source Energy | 5745.72 | 2504.68 | 2504.68
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 3.51 | 1423.26 | 0 | 0 | 0 | 0
Cooling | 120.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 346.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1219.53 | 1423.26 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1219.53 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1219.53 | 100
Total On-Site and Utility Electric Sources | 1219.53 | 100
Total Electricity End Uses | 1219.53 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 3.24 | 0.39 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 48445.47 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 157087.18 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21778.66 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23992.09 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.19 | 368.55 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.41 | 3445.92 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 6.84 | 9765.65 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.21 | 1722.46 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.21 | 1722.23 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 4401.73
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 70427
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 272177.51
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 39677.82
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 39674.16
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42226.3096 | 58.6368 | 66.3199 | 0 | 0.0005 | 43527.1697 | 16555.7463
February | 33834.7799 | 48.6572 | 58.5885 | 0 | 0.0005 | 38464.6229 | 13425.5984
March | 29247.5742 | 45.7639 | 62.7043 | 0 | 0.0005 | 41190.3495 | 11959.4025
April | 22319.0036 | 38.158 | 58.3846 | 0 | 0.0004 | 38369.3649 | 9435.5414
May | 23383.3032 | 42.0659 | 67.9687 | 0 | 0.0005 | 44676.6642 | 10085.0999
June | 25277.4762 | 46.0809 | 75.4526 | 0 | 0.0006 | 49598.2163 | 10960.114
July | 26986.4569 | 49.2319 | 80.6694 | 0 | 0.0006 | 53027.6227 | 11704.5084
August | 27028.0057 | 49.3157 | 80.8197 | 0 | 0.0006 | 53126.4472 | 11723.2949
September | 21649.8972 | 39.1455 | 63.5746 | 0 | 0.0005 | 41789.146 | 9356.4094
October | 23131.79 | 39.5455 | 60.504 | 0 | 0.0004 | 39762.2063 | 9778.9552
November | 28141.8425 | 43.845 | 59.7192 | 0 | 0.0005 | 39228.4477 | 11489.2259
December | 38245.9997 | 54.6849 | 65.1979 | 0 | 0.0005 | 42801.8339 | 15145.7556
Annual Sum or Average | 341472.4387 | 555.1313 | 799.9035 | 0 | 0.006 | 525562.0913 | 141619.6519
Minimum of Months | 21649.8972 | 38.158 | 58.3846 | 0 | 0.0004 | 38369.3649 | 9356.4094
Maximum of Months | 42226.3096 | 58.6368 | 80.8197 | 0 | 0.0006 | 53126.4472 | 16555.7463
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 101002000000 | 65661.747 | 04-JAN-17:00 | 34382.155 | 10771.038 | 17024.814 | 316.456 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 89254300000 | 65570.001 | 01-FEB-17:00 | 34382.155 | 10771.038 | 17024.814 | 224.71 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 95579100000 | 65498.95 | 01-MAR-17:00 | 34382.155 | 10771.038 | 17024.814 | 153.658 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 89033200000 | 75018.394 | 14-APR-15:00 | 34382.155 | 10771.038 | 16656.268 | 0 | 13208.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 103669000000 | 120765.945 | 27-MAY-14:00 | 34382.155 | 10771.038 | 16656.268 | 0 | 58956.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 115089000000 | 118898.678 | 29-JUN-14:00 | 34382.155 | 10771.038 | 16656.268 | 0 | 57089.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 123047000000 | 123195.333 | 15-JUL-14:00 | 34382.155 | 10771.038 | 16656.268 | 0 | 61385.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 123276000000 | 116145.059 | 25-AUG-15:00 | 34382.155 | 10771.038 | 16656.268 | 0 | 54335.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 96968600000 | 101200.886 | 14-SEP-14:00 | 34382.155 | 10771.038 | 16656.268 | 0 | 39391.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 92265200000 | 87841.573 | 07-OCT-15:09 | 34382.155 | 10771.038 | 16656.268 | 0 | 26032.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 91026700000 | 66514.147 | 02-NOV-16:00 | 34382.155 | 10771.038 | 16656.268 | 0 | 1537.402 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 99318400000 | 65519.818 | 14-DEC-17:00 | 34382.155 | 10771.038 | 17024.814 | 174.527 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1219530000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 89033200000 | 65498.95 |  | 34382.155 | 10771.038 | 16656.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 123276000000 | 123195.333 |  | 34382.155 | 10771.038 | 17024.814 | 316.456 | 61385.872 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20902.56 | 11220.12 | 0 | 32122.68
Cost per Total Building Area ($/m2) | 9.11 | 4.89 | 0 | 14
Cost per Net Conditioned Building Area ($/m2) | 9.11 | 4.89 | 0 | 14
14-Helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2297.47 | 1001.52 | 1001.52
Net Site Energy | 2297.47 | 1001.52 | 1001.52
Total Source Energy | 5383.19 | 2346.65 | 2346.65
Net Source Energy | 5383.19 | 2346.65 | 2346.65
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 2.5 | 1091.79 | 0 | 0 | 0 | 0
Cooling | 56.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 397.78 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1205.68 | 1091.79 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1205.68 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1205.68 | 100
Total On-Site and Utility Electric Sources | 1205.68 | 100
Total Electricity End Uses | 1205.68 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-9.5 CI_EXT-WALL | 0.08 | 0.591 | 0.65 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 38.05 | 3.24 | 0.39 | 0.495 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 7.83 | 3.24 | 0.39 | 0.495 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 48102.99 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 131033.2 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23682.7 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23680.12 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.22 | 418.2 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.91 | 4151.29 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 7.92 | 11308.17 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.43 | 2043.82 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.43 | 2043.59 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 4463.56
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 73337.94
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 281869.7
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 40310.68
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 40307.52
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 38610.4511 | 56.4101 | 77.4357 | 0 | 0.0006 | 1835327.2315 | 15428.183
February | 31940.0723 | 47.8641 | 68.3957 | 0 | 0.0005 | 1621330.7012 | 12878.7388
March | 29402.8024 | 47.1176 | 74.0136 | 0 | 0.0005 | 1755136.4405 | 12151.0545
April | 24931.9527 | 41.502 | 68.361 | 0 | 0.0005 | 1621364.6335 | 10453.1449
May | 24095.5017 | 41.6103 | 71.4947 | 0 | 0.0005 | 1695929.2084 | 10247.5073
June | 25240.8187 | 44.4033 | 77.8408 | 0 | 0.0005 | 1846585.9902 | 10813.385
July | 26908.3279 | 47.7358 | 84.4265 | 0 | 0.0006 | 2002874.4806 | 11566.3372
August | 26388.4718 | 46.7357 | 82.514 | 0 | 0.0006 | 1957492.1926 | 11335.3585
September | 23886.6112 | 41.756 | 72.7063 | 0 | 0.0005 | 1724745.8807 | 10207.6206
October | 25248.9017 | 42.4905 | 70.8968 | 0 | 0.0005 | 1681581.8634 | 10630.5808
November | 28481.8178 | 45.2715 | 70.3562 | 0 | 0.0005 | 1668339.8222 | 11734.6542
December | 36408.4345 | 54.0469 | 76.1076 | 0 | 0.0006 | 1804037.7174 | 14630.8313
Annual Sum or Average | 341544.1639 | 556.9439 | 894.549 | 0 | 0.0063 | 21214700 | 142077.3962
Minimum of Months | 23886.6112 | 41.502 | 68.361 | 0 | 0.0005 | 1621330.7012 | 10207.6206
Maximum of Months | 38610.4511 | 56.4101 | 84.4265 | 0 | 0.0006 | 2002874.4806 | 15428.183
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 104306000000 | 68630.855 | 06-JAN-17:00 | 34382.155 | 10771.038 | 19965.064 | 345.313 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 92144100000 | 68285.541 | 04-FEB-17:30 | 34382.155 | 10771.038 | 19965.064 | 0 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 99748600000 | 69906.733 | 30-MAR-16:00 | 34382.155 | 10771.038 | 19546.864 | 0 | 5206.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 92146000000 | 65698.871 | 06-APR-15:00 | 34382.155 | 10771.038 | 19546.864 | 0 | 998.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 96383700000 | 87952.324 | 16-MAY-16:00 | 34382.155 | 10771.038 | 19546.864 | 0 | 23252.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 104946000000 | 112254.301 | 30-JUN-15:00 | 34382.155 | 10771.038 | 19546.864 | 0 | 47554.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 113828000000 | 110719.481 | 21-JUL-16:00 | 34382.155 | 10771.038 | 19546.864 | 0 | 46019.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 111249000000 | 105587.074 | 09-AUG-16:00 | 34382.155 | 10771.038 | 19546.864 | 0 | 40887.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 98021400000 | 98097.946 | 02-SEP-15:39 | 34382.155 | 10771.038 | 19546.864 | 0 | 33397.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 95568300000 | 82518.321 | 06-OCT-16:00 | 34382.155 | 10771.038 | 19546.864 | 0 | 17818.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 94815700000 | 68285.541 | 14-NOV-17:30 | 34382.155 | 10771.038 | 19965.064 | 0 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 102528000000 | 68544.305 | 12-DEC-17:00 | 34382.155 | 10771.038 | 19965.064 | 258.763 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1205680000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 92144100000 | 65698.871 |  | 34382.155 | 10771.038 | 19546.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 113828000000 | 112254.301 |  | 34382.155 | 10771.038 | 19965.064 | 345.313 | 47554.244 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25464.94 | 8749 | 0 | 34213.94
Cost per Total Building Area ($/m2) | 11.1 | 3.81 | 0 | 14.91
Cost per Net Conditioned Building Area ($/m2) | 11.1 | 3.81 | 0 | 14.91
15-Duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2931.53 | 1277.92 | 1277.92
Net Site Energy | 2931.53 | 1277.92 | 1277.92
Total Source Energy | 6023.9 | 2625.94 | 2625.94
Net Source Energy | 6023.9 | 2625.94 | 2625.94
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 4.25 | 1727.84 | 0 | 0 | 0 | 0
Cooling | 54.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 396.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1203.69 | 1727.84 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1203.69 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1203.69 | 100
Total On-Site and Utility Electric Sources | 1203.69 | 100
Total Electricity End Uses | 1203.69 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-11.4 CI_EXT-WALL | 0.08 | 0.512 | 0.55 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 38.05 | 3.24 | 0.49 | 0.49 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 38.05 | 3.24 | 0.49 | 0.49 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 7.83 | 3.24 | 0.49 | 0.49 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 50944.66 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 151022.62 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22603.65 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23603.04 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.21 | 402.01 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.75 | 3923.79 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 7.59 | 10841.16 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.36 | 1940.56 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.36 | 1940.4 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 4701.12
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 77347.85
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 306184.92
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 43002.17
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 42999.57
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43272.1555 | 60.5155 | 69.3509 | 0 | 0.0005 | 45519.4387 | 17006.5492
February | 36979.2162 | 52.5244 | 61.9014 | 0 | 0.0005 | 40635.4153 | 14610.7186
March | 34056.158 | 51.2701 | 66.4432 | 0 | 0.0005 | 43636.0408 | 13732.7684
April | 25392.89 | 41.5066 | 60.2172 | 0 | 0.0004 | 39565.701 | 10552.8008
May | 23071.2911 | 40.1799 | 62.7483 | 0 | 0.0005 | 41240.2493 | 9823.9081
June | 22457.2492 | 40.6976 | 66.2461 | 0 | 0.0005 | 43545.5153 | 9714.1487
July | 24811.2607 | 45.1747 | 73.8776 | 0 | 0.0005 | 48562.7107 | 10752.5848
August | 24564.4663 | 44.5307 | 72.509 | 0 | 0.0005 | 47662.3381 | 10627.0254
September | 22015.8108 | 38.9775 | 61.9478 | 0 | 0.0005 | 40716.6773 | 9435.2467
October | 24955.1125 | 41.7827 | 62.408 | 0 | 0.0005 | 41009.7896 | 10465.6573
November | 31240.4371 | 47.7151 | 63.1767 | 0 | 0.0005 | 41494.6431 | 12662.7327
December | 41054.116 | 58.3296 | 68.779 | 0 | 0.0005 | 45150.3637 | 16222.3934
Annual Sum or Average | 353870.1635 | 563.2045 | 789.6052 | 0 | 0.0059 | 518738.8829 | 145606.5343
Minimum of Months | 22015.8108 | 38.9775 | 60.2172 | 0 | 0.0004 | 39565.701 | 9435.2467
Maximum of Months | 43272.1555 | 60.5155 | 73.8776 | 0 | 0.0005 | 48562.7107 | 17006.5492
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 105624000000 | 67754.537 | 11-JAN-17:00 | 34382.155 | 10771.038 | 19047.923 | 386.136 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 94291400000 | 67508.296 | 06-FEB-17:00 | 34382.155 | 10771.038 | 19047.923 | 139.896 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 101254000000 | 67368.4 | 03-MAR-17:00 | 34382.155 | 10771.038 | 19047.923 | 0 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 91809200000 | 67720.795 | 04-APR-14:00 | 34382.155 | 10771.038 | 18645.913 | 0 | 3921.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 95694900000 | 84460.215 | 31-MAY-15:00 | 34382.155 | 10771.038 | 18645.913 | 0 | 20661.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 101044000000 | 104435.077 | 14-JUN-14:00 | 34382.155 | 10771.038 | 18645.913 | 0 | 40635.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 112686000000 | 114610.39 | 08-JUL-15:39 | 34382.155 | 10771.038 | 18645.913 | 0 | 50811.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 110597000000 | 113963.822 | 12-AUG-14:00 | 34382.155 | 10771.038 | 18645.913 | 0 | 50164.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 94480000000 | 94079.703 | 07-SEP-14:00 | 34382.155 | 10771.038 | 18645.913 | 0 | 30280.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 95160100000 | 87043.64 | 07-OCT-14:00 | 34382.155 | 10771.038 | 18645.913 | 0 | 23244.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 96285200000 | 67481.098 | 27-NOV-17:00 | 34382.155 | 10771.038 | 19047.923 | 112.697 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 104768000000 | 67534.308 | 14-DEC-17:00 | 34382.155 | 10771.038 | 19047.923 | 165.907 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1203690000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 91809200000 | 67368.4 |  | 34382.155 | 10771.038 | 18645.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 112686000000 | 114610.39 |  | 34382.155 | 10771.038 | 19047.923 | 386.136 | 50811.284 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20167.36 | 13587.55 | 0 | 33754.91
Cost per Total Building Area ($/m2) | 8.79 | 5.92 | 0 | 14.71
Cost per Net Conditioned Building Area ($/m2) | 8.79 | 5.92 | 0 | 14.71
16-Fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 4151.44 | 1809.7 | 1809.7
Net Site Energy | 4151.44 | 1809.7 | 1809.7
Total Source Energy | 7622.26 | 3322.7 | 3322.7
Net Source Energy | 7622.26 | 3322.7 | 3322.7
Area (m2)
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 8.17 | 2905.92 | 0 | 0 | 0 | 0
Cooling | 29.16 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 49.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 459.72 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1245.52 | 2905.92 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1245.52 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1245.52 | 100
Total On-Site and Utility Electric Sources | 1245.52 | 100
Total Electricity End Uses | 1245.52 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
BACK_SPACE_WALL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 379.89 | 90 | 180
BACK_SPACE_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 379.89 | 90 | 0
CORE_RETAIL_WALL_WEST_2 | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 178.43 | 270 | 90 | W
CORE_RETAIL_WALL_EAST_2 | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 178.43 | 90 | 90 | E
CORE_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1600.48 | 180 | 0
POINT_OF_SALE_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 150.81 | 180 | 0
FRONT_RETAIL_WALLL_EAST | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 36.58 | 90 | 90 | E
FRONT_RETAIL_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 153.22 | 180 | 90 | S
FRONT_RETAIL_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 150.81 | 90 | 0
FRONT_ENTRY_WALL_SOUTH | MASS_R-13.3 CI_EXT-WALL | 0.08 | 0.454 | 0.49 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | UNHEATED - 8IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.627 | 2.69 | 12 | 180 | 180
FRONT_ENTRY_ROOF | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 12 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
POINT_OF_SALE_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 38.05 | 2.62 | 0.49 | 0.49 | No | POINT_OF_SALE_WALL_SOUTH
FRONT_RETAIL_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 38.05 | 2.62 | 0.49 | 0.49 | No | FRONT_RETAIL_WALL_SOUTH
FRONT_ENTRY_WALL_SOUTH_GLAZING | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 7.83 | 2.62 | 0.49 | 0.49 | No | FRONT_ENTRY_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 50643.79 | 2.96
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 136410.34 | 2.96
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24782.21 | 2.96
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24782.21 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.07 | 125 | 0.24 | 453 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 3.06 | 4370.56 | 1 | General
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 8.24 | 11772.21 | 1 | General
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.5 | 2138.71 | 1 | General
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.5 | 2138.71 | 1 | General
Nominal Capacity [W]
FRONT_ENTRY UNIT HEATER COIL | 5486.93
Nominal Capacity [W]
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 91566
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 370820.59
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 51363.77
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 51363.77
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 53550.5454 | 56.3556 | 162.1774 | 0 | 0.0006 | 32518.0465 | 19725.6541
February | 46031.4046 | 48.7073 | 144.9428 | 0 | 0.0005 | 29064.2425 | 16996.6632
March | 39863.9693 | 43.5396 | 153.94 | 0 | 0.0006 | 30877.7084 | 14928.4196
April | 27309.153 | 31.27 | 135.6439 | 0 | 0.0005 | 27215.893 | 10448.876
May | 20873.4871 | 25.5046 | 137.228 | 0 | 0.0005 | 27540.7206 | 8233.2761
June | 20152.1325 | 25.1007 | 142.4764 | 0 | 0.0005 | 28595.605 | 8022.2348
July | 20755.8828 | 25.9218 | 148.1894 | 0 | 0.0005 | 29742.4309 | 8273.2025
August | 20749.1341 | 25.7416 | 144.549 | 0 | 0.0005 | 29011.2611 | 8244.0896
September | 21759.6341 | 26.1136 | 133.1437 | 0 | 0.0005 | 26719.4703 | 8509.911
October | 30556.5648 | 34.6177 | 144.0165 | 0 | 0.0005 | 28894.1938 | 11634.3246
November | 43492.7398 | 46.799 | 153.2263 | 0 | 0.0006 | 30730.6144 | 16179.0132
December | 50176.4466 | 53.3042 | 162.4082 | 0 | 0.0006 | 32567.8969 | 18559.6455
Annual Sum or Average | 395271.0941 | 442.9758 | 1761.9416 | 0 | 0.0063 | 353478.0832 | 149755.3102
Minimum of Months | 20152.1325 | 25.1007 | 133.1437 | 0 | 0.0005 | 26719.4703 | 8022.2348
Maximum of Months | 53550.5454 | 56.3556 | 162.4082 | 0 | 0.0006 | 32567.8969 | 19725.6541
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 114581000000 | 70330.221 | 13-JAN-09:09 | 34382.155 | 10771.038 | 20873.185 | 1136.559 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 102411000000 | 70179.859 | 03-FEB-09:09 | 34382.155 | 10771.038 | 20873.185 | 986.197 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 108801000000 | 69193.662 | 02-MAR-17:00 | 34382.155 | 10771.038 | 20873.185 | 0 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 95898100000 | 68698.589 | 25-APR-13:39 | 34382.155 | 10771.038 | 20420.181 | 0 | 3125.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 97042700000 | 79238.582 | 24-MAY-14:00 | 34382.155 | 10771.038 | 20420.181 | 0 | 13665.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 100760000000 | 92682.635 | 20-JUN-16:00 | 34382.155 | 10771.038 | 20420.181 | 0 | 27109.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 104801000000 | 98006.423 | 29-JUL-16:00 | 34382.155 | 10771.038 | 20420.181 | 0 | 32433.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 102224000000 | 91725.304 | 15-AUG-16:00 | 34382.155 | 10771.038 | 20420.181 | 0 | 26151.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 94148900000 | 70286.175 | 09-SEP-15:09 | 34382.155 | 10771.038 | 20420.181 | 0 | 4712.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 101812000000 | 69616.796 | 27-OCT-08:09 | 34382.155 | 10771.038 | 20873.185 | 423.134 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 108283000000 | 69785.612 | 09-NOV-09:09 | 34382.155 | 10771.038 | 20873.185 | 591.95 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 114757000000 | 70172.651 | 29-DEC-09:09 | 34382.155 | 10771.038 | 20873.185 | 978.989 | 0 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1245520000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 94148900000 | 68698.589 |  | 34382.155 | 10771.038 | 20420.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 114757000000 | 98006.423 |  | 34382.155 | 10771.038 | 20873.185 | 1136.559 | 32433.048 | 3167.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33065.86 | 11951.56 | 0 | 45017.41
Cost per Total Building Area ($/m2) | 14.41 | 5.21 | 0 | 19.62
Cost per Net Conditioned Building Area ($/m2) | 14.41 | 5.21 | 0 | 19.62

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.39 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 5 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 49.8559 | 46.2805 | 49.6034 | 40.6587 | 23.5256 | 40.1808 | 25.9266 | 44.0267 | 33.9301 | 31.9259 | 46.4301 | 45.789 | 48.4455 | 48.103 | 50.9447 | 50.6438
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 222.4963 | 206.4701 | 156.9163 | 184.9828 | 107.1494 | 148.4955 | 89.8578 | 177.3136 | 126.7964 | 96.4871 | 169.4194 | 123.3032 | 157.0872 | 131.0332 | 151.0226 | 136.4103
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 27.0714 | 25.0868 | 27.8902 | 22.8007 | 18.8064 | 24.4089 | 21.4174 | 22.663 | 22.1293 | 22.3379 | 22.6163 | 23.7831 | 21.7787 | 23.6827 | 22.6036 | 24.7822
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 24.2548 | 23.4354 | 28.8293 | 20.7095 | 14.1882 | 19.4252 | 17.6335 | 22.1356 | 18.3846 | 18.3922 | 22.993 | 22.3212 | 23.9921 | 23.6801 | 23.603 | 24.7822
Heating (kW)
| FRONT_ENTRY UNIT HEATER COIL | 2.3297 | 3.6444 | 3.0698 | 3.2189 | 2.0823 | 2.7842 | 2.6858 | 3.567 | 3.0254 | 3.0469 | 4.0584 | 3.9352 | 4.4017 | 4.4636 | 4.7011 | 5.4869
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 40.5987 | 61.483 | 52.2663 | 55.4406 | 38.199 | 48.3057 | 42.9214 | 61.0876 | 47.886 | 53.2118 | 64.3532 | 64.6739 | 70.427 | 73.3379 | 77.3478 | 91.566
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 121.4157 | 195.5637 | 169.9034 | 205.0193 | 135.1993 | 178.7642 | 160.7565 | 226.9561 | 170.7103 | 198.8634 | 245.4781 | 240.4331 | 272.1775 | 281.8697 | 306.1849 | 370.8206
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 20.104 | 31.4669 | 26.3554 | 29.1397 | 18.8968 | 24.9349 | 23.1316 | 32.5243 | 26.0514 | 27.7124 | 36.0912 | 34.9485 | 39.6778 | 40.3107 | 43.0022 | 51.3638
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 20.1551 | 31.4669 | 26.3718 | 29.1391 | 18.8923 | 24.9377 | 23.127 | 32.5215 | 26.0514 | 27.7111 | 36.0865 | 34.9485 | 39.6742 | 40.3075 | 42.9996 | 51.3638
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | None | None | None | Fixed Dry Bulb | None | None | None | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | None | None
Fan Max Flow Rate (m3/s )
| FRONT_ENTRY UNIT HEATERFAN | 0.1 | 0.16 | 0.14 | 0.14 | 0.09 | 0.13 | 0.12 | 0.15 | 0.16 | 0.13 | 0.18 | 0.21 | 0.19 | 0.22 | 0.21 | 0.24
| PSZ-AC:1_UNITARY_PACKAGE_FAN | 2.55 | 2.44 | 3 | 2.04 | 1.42 | 2.43 | 1.57 | 2.16 | 2.05 | 1.93 | 2.2 | 2.77 | 2.41 | 2.91 | 2.75 | 3.06
| PSZ-AC:2_UNITARY_PACKAGE_FAN | 9.09 | 8.76 | 9.48 | 7.78 | 6.47 | 8.97 | 5.43 | 7.41 | 7.66 | 5.83 | 6.96 | 7.45 | 6.84 | 7.92 | 7.59 | 8.24
| PSZ-AC:3_UNITARY_PACKAGE_FAN | 1.34 | 1.32 | 1.68 | 1.23 | 1.14 | 1.47 | 1.29 | 1.21 | 1.34 | 1.35 | 1.2 | 1.44 | 1.21 | 1.43 | 1.36 | 1.5
| PSZ-AC:4_UNITARY_PACKAGE_FAN | 1.04 | 1.08 | 1.54 | 0.97 | 0.86 | 1.17 | 1.07 | 1.04 | 1.11 | 1.11 | 1.1 | 1.35 | 1.21 | 1.43 | 1.36 | 1.5
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.085604 | 0.12318 | 0.10154 | 0.10173 | 0.13122 | 0.099291 | 0.15027 | 0.077244 | 0.037482 | 0.07582 | 0.052032 | 0.0375 | 0.061703 | 0.076035 | 0.060317 | 0.095572
| Total Cost ($/m2) | 19.15 | 23.71 | 20.92 | 16.16 | 17.7 | 17.39 | 18.98 | 11.86 | 5.67 | 9.89 | 7.69 | 5.5 | 9.11 | 11.1 | 8.79 | 14.41
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011442 | 0.0080467 | 0.0080948 | 0.0094394 | 0.00877 | 0.0075909 | 0.0086546 | 0.0096417 | 0.006841 | 0.0084459 | 0.0082649 | 0.0068731 | 0.0078834 | 0.0080134 | 0.0078639 | 0.0041128
| Total Cost ($/m2) | 0.02 | 0.76 | 0.44 | 1.54 | 0.29 | 0.61 | 1.07 | 2.97 | 1.25 | 2.43 | 3.7 | 2.04 | 4.89 | 3.81 | 5.92 | 5.21
Total Utility Costs
| Cost Intensity ($/m2) | 19.18 | 24.47 | 21.36 | 17.71 | 18 | 18 | 20.05 | 14.84 | 6.92 | 12.32 | 11.39 | 7.54 | 14 | 14.91 | 14.71 | 19.62
Energy - End Uses
Electricity (kWh)
| Heating | 5.5556 | 283.3333 | 116.6667 | 241.6667 | 38.8889 | 97.2222 | 252.7778 | 441.6667 | 225 | 416.6667 | 661.1111 | 402.7778 | 975 | 694.4444 | 1180.5556 | 2269.4444
| Cooling | 199580.5556 | 129655.5556 | 144208.3333 | 64338.8889 | 26833.3333 | 87475 | 10591.6667 | 51558.3333 | 45952.7778 | 12258.3333 | 38613.8889 | 25722.2222 | 33438.8889 | 15722.2222 | 15138.8889 | 8100
| Interior Lighting | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667
| Exterior Lighting | 13844.4444 | 13838.8889 | 13836.1111 | 13833.3333 | 13825 | 13819.4444 | 13827.7778 | 13819.4444 | 13825 | 13797.2222 | 13822.2222 | 13813.8889 | 13813.8889 | 13808.3333 | 13802.7778 | 13716.6667
| Interior Equipment | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 105650 | 103572.2222 | 120188.8889 | 91833.3333 | 74600 | 106183.3333 | 70880.5556 | 92230.5556 | 93100 | 78522.2222 | 91741.6667 | 102413.8889 | 96338.8889 | 110494.4444 | 110047.2222 | 127700
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 513275 | 441541.6667 | 472544.4444 | 364438.8889 | 309491.6667 | 401769.4444 | 289744.4444 | 352244.4444 | 347294.4444 | 299188.8889 | 339030.5556 | 336550 | 338758.3333 | 334911.1111 | 334358.3333 | 345977.7778
Gas (MJ)
| Heating | 4960 | 217270 | 124690 | 375410 | 76430 | 183860 | 283880 | 707760 | 419270 | 660990 | 1027400 | 681930 | 1423260 | 1091790 | 1727840 | 2905920
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4960 | 217270 | 124690 | 375410 | 76430 | 183860 | 283880 | 707760 | 419270 | 660990 | 1027400 | 681930 | 1423260 | 1091790 | 1727840 | 2905920
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1852750 | 1806820 | 1825850 | 1687390 | 1190600 | 1630230 | 1326960 | 1975840 | 1669530 | 1738070 | 2247910 | 1893500 | 2642790 | 2297470 | 2931530 | 4151440
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.0087184 | 0.44464 | 0.18309 | 0.37925 | 0.061029 | 0.15257 | 0.39669 | 0.69312 | 0.3531 | 0.65388 | 1.0375 | 0.63209 | 1.5301 | 1.0898 | 1.8527 | 3.5615
| Cooling (elec) | 313.2054 | 203.4708 | 226.3087 | 100.9682 | 42.11 | 137.2761 | 16.6217 | 80.9114 | 72.1145 | 19.2372 | 60.5975 | 40.3663 | 52.4763 | 24.6732 | 23.7577 | 12.7115
| Interior Lighting (elec) | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829
| Exterior Lighting (elec) | 21.7263 | 21.7176 | 21.7133 | 21.7089 | 21.6958 | 21.6871 | 21.7002 | 21.6871 | 21.6958 | 21.6522 | 21.6915 | 21.6784 | 21.6784 | 21.6697 | 21.6609 | 21.5258
| Interior Equipment (elec) | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 165.7985 | 162.5378 | 188.6146 | 144.1157 | 117.0711 | 166.6354 | 111.2341 | 144.7391 | 146.1035 | 123.2263 | 143.9719 | 160.72 | 151.1864 | 173.4009 | 172.6991 | 200.4019
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 805.4917 | 692.9193 | 741.5725 | 571.9205 | 485.6909 | 630.5041 | 454.7012 | 552.7836 | 545.0155 | 469.5225 | 532.0468 | 528.154 | 531.6196 | 525.5821 | 524.7146 | 542.9492
Gas (MJ/m2)
| Heating (gas) | 2.1622 | 94.7127 | 54.3551 | 163.6494 | 33.3175 | 80.1486 | 123.7494 | 308.5279 | 182.7689 | 288.1399 | 447.8659 | 297.2681 | 620.4299 | 475.9349 | 753.2029 | 1266.7536
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2.1622 | 94.7127 | 54.3551 | 163.6494 | 33.3175 | 80.1486 | 123.7494 | 308.5279 | 182.7689 | 288.1399 | 447.8659 | 297.2681 | 620.4299 | 475.9349 | 753.2029 | 1266.7536
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 807.6539 | 787.632 | 795.9276 | 735.5699 | 519.0084 | 710.6526 | 578.4506 | 861.3115 | 727.7843 | 757.6624 | 979.9127 | 825.4177 | 1152.0495 | 1001.517 | 1277.9175 | 1809.7027
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 112.5832 | 98.0421 | 91.8918 | 68.6952 | 79.4837 | 68.631 | 62.1138 | 65.664 | 67.4661 | 63.3322 | 65.273 | 67.2813 | 65.6617 | 68.6309 | 67.7545 | 70.3302
| Feb | 118.8472 | 100.1816 | 97.2696 | 74.9943 | 74.1587 | 73.2161 | 69.2818 | 65.4988 | 74.2094 | 63.4989 | 65.0461 | 67.3974 | 65.57 | 68.2855 | 67.5083 | 70.1799
| Mar | 121.6574 | 108.6911 | 114.4549 | 82.6629 | 77.191 | 88.3474 | 62.5666 | 82.0117 | 75.9037 | 69.1288 | 71.1339 | 79.7657 | 65.4989 | 69.9067 | 67.3684 | 69.1937
| Apr | 128.5732 | 125.0662 | 118.7871 | 102.2588 | 85.4117 | 108.5546 | 74.7278 | 85.203 | 92.028 | 71.3222 | 76.0378 | 87.3364 | 75.0184 | 65.6989 | 67.7208 | 68.6986
| May | 136.9531 | 134.3339 | 142.5154 | 110.2183 | 82.9634 | 120.6266 | 76.7128 | 101.6441 | 98.7896 | 79.101 | 101.3542 | 96.2588 | 120.7659 | 87.9523 | 84.4602 | 79.2386
| Jun | 144.8071 | 135.5452 | 165.0287 | 119.0812 | 82.8279 | 144.6146 | 79.5117 | 127.0206 | 109.1837 | 85.5007 | 120.7853 | 106.6287 | 118.8987 | 112.2543 | 104.4351 | 92.6826
| Jul | 142.163 | 143.107 | 161.33 | 130.5973 | 86.3067 | 141.0066 | 88.4321 | 130.9621 | 113.4005 | 93.4366 | 123.9079 | 110.8055 | 123.1953 | 110.7195 | 114.6104 | 98.0064
| Aug | 143.1688 | 142.0884 | 163.805 | 122.7156 | 92.9771 | 136.3539 | 81.7374 | 131.7275 | 110.9276 | 89.8421 | 121.4414 | 111.2569 | 116.1451 | 105.5871 | 113.9638 | 91.7253
| Sep | 137.517 | 139.2526 | 147.0079 | 111.2968 | 89.5034 | 131.8678 | 96.4503 | 111.5877 | 98.253 | 105.0862 | 102.3743 | 105.0823 | 101.2009 | 98.0979 | 94.0797 | 70.2862
| Oct | 134.4811 | 121.2885 | 119.8732 | 101.3303 | 83.4452 | 107.6197 | 75.7892 | 96.3691 | 87.187 | 70.1369 | 84.8579 | 92.7298 | 87.8416 | 82.5183 | 87.0436 | 69.6168
| Nov | 121.7011 | 105.1609 | 106.7416 | 78.0093 | 79.6806 | 75.5757 | 63.2571 | 88.6737 | 72.4292 | 64.853 | 83.0856 | 67.742 | 66.5141 | 68.2855 | 67.4811 | 69.7856
| Dec | 112.8598 | 103.8349 | 86.5184 | 66.6341 | 79.4315 | 73.5046 | 61.9782 | 65.6933 | 67.182 | 63.3485 | 65.1647 | 67.3521 | 65.5198 | 68.5443 | 67.5343 | 70.1727
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 03-JAN-13:00 | 28-JAN-14:00 | 23-JAN-16:00 | 26-JAN-14:09 | 02-JAN-16:49 | 17-JAN-17:19 | 24-JAN-17:00 | 26-JAN-17:30 | 09-JAN-17:49 | 28-JAN-17:00 | 09-JAN-17:00 | 04-JAN-17:00 | 06-JAN-17:00 | 11-JAN-17:00 | 13-JAN-09:09
| Feb | 22-FEB-15:00 | 23-FEB-15:00 | 28-FEB-16:00 | 18-FEB-16:40 | 13-FEB-11:50 | 08-FEB-15:00 | 15-FEB-16:10 | 02-FEB-17:40 | 14-FEB-15:00 | 21-FEB-17:40 | 01-FEB-17:00 | 15-FEB-17:00 | 01-FEB-17:00 | 04-FEB-17:30 | 06-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-15:00 | 25-MAR-16:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-15:00 | 01-MAR-13:39 | 09-MAR-15:09 | 02-MAR-15:39 | 29-MAR-15:00 | 31-MAR-14:00 | 30-MAR-16:49 | 01-MAR-17:00 | 30-MAR-16:00 | 03-MAR-17:00 | 02-MAR-17:00
| Apr | 15-APR-15:00 | 29-APR-15:09 | 01-APR-16:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 29-APR-14:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-15:50 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 25-APR-13:39
| May | 24-MAY-14:00 | 18-MAY-15:00 | 27-MAY-16:00 | 31-MAY-16:00 | 30-MAY-14:20 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-15:00 | 31-MAY-16:00 | 15-MAY-16:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-16:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-16:00 | 29-JUN-14:09 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 05-JUL-15:00 | 19-JUL-16:00 | 03-JUL-15:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:39 | 29-JUL-16:00
| Aug | 21-AUG-14:00 | 31-AUG-15:00 | 01-AUG-16:00 | 17-AUG-14:00 | 08-AUG-14:00 | 04-AUG-14:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-14:09 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
| Sep | 11-SEP-14:00 | 16-SEP-14:00 | 09-SEP-15:00 | 11-SEP-13:00 | 23-SEP-13:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:00 | 02-SEP-14:00 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 02-SEP-15:39 | 07-SEP-14:00 | 09-SEP-15:09
| Oct | 06-OCT-15:00 | 06-OCT-15:00 | 02-OCT-16:00 | 12-OCT-15:00 | 19-OCT-11:09 | 03-OCT-15:00 | 13-OCT-15:00 | 03-OCT-14:00 | 13-OCT-14:00 | 17-OCT-15:39 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-15:09 | 06-OCT-16:00 | 07-OCT-14:00 | 27-OCT-08:09
| Nov | 01-NOV-17:40 | 27-NOV-17:00 | 13-NOV-16:00 | 22-NOV-15:30 | 20-NOV-11:00 | 10-NOV-15:00 | 14-NOV-16:00 | 04-NOV-12:00 | 08-NOV-17:10 | 04-NOV-16:49 | 02-NOV-14:00 | 10-NOV-13:00 | 02-NOV-16:00 | 14-NOV-17:30 | 27-NOV-17:00 | 09-NOV-09:09
| Dec | 15-DEC-17:30 | 02-DEC-13:50 | 09-DEC-16:00 | 01-DEC-17:30 | 19-DEC-13:09 | 05-DEC-14:00 | 02-DEC-17:00 | 15-DEC-16:00 | 05-DEC-16:49 | 13-DEC-17:00 | 14-DEC-17:00 | 09-DEC-17:00 | 14-DEC-17:00 | 12-DEC-17:00 | 14-DEC-17:00 | 29-DEC-09:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 140854.9599 | 151199.4325 | 144898.1321 | 119030.3474 | 37547.1914 | 138822.2465 | 38980.3403 | 107817.9357 | 149429.7258 | 33710.5999 | 199281.2548 | 149776.5503 | 141619.6519 | 142077.3962 | 145606.5343 | 149755.3102
| CO2 (kg) | 326208.5199 | 380891.1731 | 341965.2715 | 274345.6736 | 100547.0144 | 330528.5321 | 105193.8734 | 250038.5461 | 352412.8722 | 86202.0816 | 470577.0812 | 355869.091 | 341472.4387 | 341544.1639 | 353870.1635 | 395271.0941
| NOX (kg) | 575.0821 | 496.0447 | 572.8947 | 509.7501 | 86.253 | 535.0304 | 90.7927 | 459.6789 | 599.8273 | 114.4369 | 807.9997 | 594.3053 | 555.1313 | 556.9439 | 563.2045 | 442.9758
| SO2 (kg) | 2197.024 | 2106.2178 | 1900.2295 | 1279.2835 | 900.6019 | 2210.1009 | 843.198 | 1286.0239 | 1516.6782 | 231.4256 | 2285.0772 | 1469.8249 | 799.9035 | 894.549 | 789.6052 | 1761.9416
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.01 | 0.0059 | 0.0052 | 0.0047 | 0.0004 | 0.0042 | 0.0004 | 0.0053 | 0.006 | 0.001 | 0.007 | 0.0058 | 0.006 | 0.0063 | 0.0059 | 0.0063
| Water Environmental Factors (m3) | 271.9116 | 718.442 | 14036.7 | 2275.4144 | 5433.9664 | 11022.1 | 5087.2652 | 79.9728 | 1576.9947 | 3056.7442 | 525.9873 | 1528.2012 | 525.5621 | 21214.7 | 518.7389 | 353.4781

## Picture
DOE Commercial Building Benchmark - Retail
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400 | 16800 | 876000