## BuildingSummary
Building Summary - Secondary School new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Secondary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 19592 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.28
| Total | 0.34
| Skylight/TDD Percentage | 1.12%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Flat built-up | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6384
| Net Dimensions - Total Area (m2) | 4088.16
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | Insulation Entirely Above Deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11902
| Net Dimensions - Total Area (m2) | 11768.6976
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| South | 753.18
| East | 291.61
| North | 753.18
| West | 291.2
| Total Area (m2) | 2089.17
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 133.8
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 10 cm concrete slab-on-grade
| Dimensions - Total Area (m2) | 11902
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 6792
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 39184
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.26 | See Benchmark Technical Report
HVAC
| System Type | MZ VAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | Air cooled chiller, PACU (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Fan Control | Variable, constant (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 815.28

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.017006
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.017006
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.017006
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200 | 70 | 0 | 0 | 5.38 | 4 | 0 | 0 | 2.5 | 0.3 | 342 | 0 | 0.047735
LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60 | 21 | 0 | 0 | 13.988 | 4 | 0 | 0 | 2.5 | 0.3 | 63 | 0 | 0.07774
BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116 | 40.6 | 10 | 21 | 9.684 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1503
OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208 | 72.8 | 20 | 26.6 | 11.836 | 10.8 | 0 | 0 | 2.5 | 0.3 | 226.1 | 0 | 0.10638
GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.28 | 1 | 1976 | 15.064 | 5 | 0 | 0 | 0 | 1.5 | 2964 | 0 | 0.13605
AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608 | 266.35 | 3.33 | 374.7748 | 15.064 | 5 | 0 | 0 | 0 | 1.5 | 1872 | 0 | 0.20232
AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512 | 106.4 | 1 | 988 | 9.684 | 5 | 0 | 0 | 2.5 | 0.3 | 2766.4 | 0 | 0.20655
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6.67 | 32.3838 | 12.912 | 222.194 | 1678.56 | 503.4582 | 0 | 0 | 0 | 2831.682 | 0.045349
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200 | 70 | 1.3935 | 447.7782 | 15.064 | 76.934 | 0 | 0 | 3.8 | 0.9 | 2263.1573 | 0 | 0.087209
MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.14 | 4 | 0 | 0 | 0 | 0.25439 | 87 | 0 | 0
Total Conditioned Zones |  |  | 11902 | 64456 |  | 3752 | 1374.23 |  | 4829.9568
Second Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 20 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 20 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200 | 70 | 0 | 0 | 5.38 | 4 | 0 | 0 | 2.5 | 0.3 | 342 | 0 | 0.31983
LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60 | 21 | 0 | 0 | 13.988 | 4 | 0 | 0 | 2.5 | 0.3 | 63 | 0 | 0.34983
BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116 | 40.6 | 10 | 21 | 9.684 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42239
OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208 | 72.8 | 20 | 26.6 | 11.836 | 10.8 | 0 | 0 | 2.5 | 0.3 | 226.1 | 0 | 0.37847
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236 | 83.01 | 4.35 | 49.6552 | 13.988 | 10 | 0 | 0 | 5 | 0.6 | 377.8759 | 0 | 0.34854
MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.14 | 4 | 0 | 0 | 0 | 0.5 | 171 | 0 | 0
Total Conditioned Zones |  |  | 7690 | 30760 |  | 2632 | 921.61 |  | 1060.6752
Building Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384 | 2295.84 |  | 5890.632
4088.16
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## Query (hidden)
01-Miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16692.17 | 851.99 | 851.99
Net Site Energy | 16692.17 | 851.99 | 851.99
Total Source Energy | 53704.39 | 2741.14 | 2741.14
Net Source Energy | 53704.39 | 2741.14 | 2741.14
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 141.29 | 0 | 0 | 0 | 0
Cooling | 6332.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3029.35 | 0 | 0 | 0 | 0 | 0
Pumps | 207.86 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 61.91 | 0 | 0 | 0 | 815.28
Refrigeration | 167.22 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15944.51 | 747.66 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 15944.51 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 15944.51 | 100
Total On-Site and Utility Electric Sources | 15944.51 | 100
Total Electricity End Uses | 15944.51 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 21 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 21 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 53.2 | 6.88 | 0.25 | 0.25 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 53.2 | 6.88 | 0.25 | 0.25 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 12.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 49.41 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 33.6 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 36.4 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 33.6 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1659534.04 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 6657979.66 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 606325.99 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 284914.3 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 332147.53 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 116258.91 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 150820.19 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 22.76 | 53959.95 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 22.72 | 53848.1 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 24.99 | 59244.58 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 33.1 | 78468.72 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 24.42 | 46300.31 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.89 | 28228.68 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 13.38 | 25363.48 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.68 | 8877.77 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 6.07 | 11516.94 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001507 | 69285.67 | 2453.01
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001885 | 86688.4 | 3069.14
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004196 | 192953.82 | 6831.4
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005577 | 256451.89 | 9079.51
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001598 | 73465.64 | 2601
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00249 | 114502.11 | 4053.87
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001584 | 72840.52 | 2578.87
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00199 | 91521.35 | 3240.25
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004345 | 199803.23 | 7073.9
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005985 | 275192.38 | 9743
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001498 | 68880.81 | 2438.68
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001881 | 86503.17 | 3062.59
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004181 | 192251.62 | 6806.54
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005548 | 255091.05 | 9031.33
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001591 | 73148.18 | 2589.76
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002487 | 114340.34 | 4048.14
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001584 | 72842.14 | 2578.93
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001991 | 91547.29 | 3241.17
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004345 | 199800.74 | 7073.81
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005988 | 275329.93 | 9747.87
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001499 | 68926.66 | 2440.3
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001889 | 86849.43 | 3074.85
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004215 | 193784.78 | 6860.82
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007003 | 322014.76 | 11400.72
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001608 | 73921.9 | 2617.16
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002559 | 117655.64 | 4165.52
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001593 | 73262.5 | 2593.81
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002001 | 92024.44 | 3258.06
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004447 | 204460.91 | 7238.8
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007397 | 340117.55 | 12041.63
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005747 | 264236.72 | 9355.12
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009103 | 418553.17 | 14818.59
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001271 | 58428.41 | 2068.62
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00185 | 85053.18 | 3011.25
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001556 | 71557.4 | 2533.44
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002219 | 102014.58 | 3611.76
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004339 | 199519.62 | 7063.86
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005874 | 270077.56 | 9561.91
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009369 | 430789.54 | 15251.81
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001573 | 72312.17 | 2560.16
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002412 | 110901.48 | 3926.39
VAV_POD_1_HEATC | 0.000913 | 41979.85 | 688.26
VAV_POD_2_HEATC | 0.000915 | 42053.49 | 689.41
VAV_POD_3_HEATC | 0.000837 | 38500.35 | 633.41
VAV_OTHER_HEATC | 0.00036 | 16543.27 | 275.65
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.014215 | 22.76 | 21.87 | 12.8 | 7.22 | 0.010546 | 0.0085
VAV_POD_2_COOLC | 0.0142 | 22.72 | 21.88 | 12.8 | 7.22 | 0.01055 | 0.0085
VAV_POD_3_COOLC | 0.014932 | 24.99 | 21.63 | 12.8 | 7.22 | 0.010397 | 0.0085
VAV_OTHER_COOLC | 0.016176 | 33.1 | 20.68 | 12.8 | 7.22 | 0.009787 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 283595.18
PSZ-AC_2:6_HEATC | 161549.17
PSZ-AC_3:7_HEATC | 155354.45
PSZ-AC_4:8_HEATC | 54377.46
PSZ-AC_5:9_HEATC | 70542.71
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 214340.3116 | 372.6116 | 1402.2289 | 0 | 0.0064 | 173540.9764 | 92024.3734
February | 196059.0539 | 342.8847 | 1298.7932 | 0 | 0.0059 | 160741.2651 | 84381.2898
March | 227975.2363 | 398.3786 | 1507.6739 | 0 | 0.0069 | 186592.5174 | 98085.1647
April | 220319.7029 | 386.2676 | 1467.0152 | 0 | 0.0067 | 181561.4765 | 94918.3344
May | 271615.99 | 476.6677 | 1812.2487 | 0 | 0.0083 | 224288.7937 | 117064.6122
June | 279818.4562 | 491.2539 | 1868.4831 | 0 | 0.0085 | 231248.6592 | 120619.0003
July | 239811.2613 | 420.7972 | 1599.6089 | 0 | 0.0073 | 197971.8718 | 103351.4493
August | 251844.5324 | 441.7664 | 1678.7287 | 0 | 0.0077 | 207763.8391 | 108522.8442
September | 266208.1951 | 467.347 | 1777.5024 | 0 | 0.0081 | 219988.6283 | 114750.8865
October | 252870.2363 | 443.6318 | 1686.0862 | 0 | 0.0077 | 208674.4713 | 108971.4578
November | 230263.769 | 403.6806 | 1533.0625 | 0 | 0.007 | 189735.6406 | 99200.3326
December | 200438.2568 | 350.4149 | 1326.792 | 0 | 0.0061 | 164206.3507 | 86253.168
Annual Sum or Average | 2851565.0016 | 4995.7018 | 18958.2237 | 0 | 0.0865 | 2346314.4901 | 1228142.9132
Minimum of Months | 196059.0539 | 342.8847 | 1298.7932 | 0 | 0.0059 | 160741.2651 | 84381.2898
Maximum of Months | 279818.4562 | 491.2539 | 1868.4831 | 0 | 0.0085 | 231248.6592 | 120619.0003
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1179310000000 | 1176831.506 | 06-JAN-12:00 | 218037.744 | 160954.2 | 223520.097 | 0 | 553765.751 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5309.161 | 0 | 0
February | 1092330000000 | 1217110.334 | 23-FEB-11:00 | 218037.744 | 160954.2 | 224630.602 | 0 | 592936.622 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5306.613 | 0 | 0
March | 1268000000000 | 1257882.219 | 13-MAR-15:09 | 218037.744 | 146554.272 | 223630.077 | 0 | 649109.167 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5306.406 | 0 | 0
April | 1233810000000 | 1319400.113 | 03-APR-13:00 | 218037.744 | 151354.248 | 227212.397 | 0 | 702246.549 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5304.623 | 0 | 0
May | 1524170000000 | 1440810.592 | 24-MAY-14:00 | 218037.744 | 146554.272 | 225551.502 | 0 | 830115.87 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5306.652 | 0 | 0
June | 1571460000000 | 1552528.04 | 26-JUN-15:09 | 218037.744 | 146554.272 | 224448.507 | 0 | 942928.319 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5314.645 | 0 | 0
July | 1345330000000 | 1282420.315 | 10-JUL-12:00 | 121132.08 | 86203.896 | 223092.951 | 0 | 831690.536 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5056.299 | 0 | 0
August | 1411870000000 | 1358135.915 | 21-AUG-13:00 | 121132.08 | 86203.896 | 223092.951 | 0 | 907402.268 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5060.168 | 0 | 0
September | 1494940000000 | 1440189.326 | 26-SEP-15:00 | 218037.744 | 146475.648 | 224110.733 | 0 | 831011.994 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5308.654 | 0 | 0
October | 1418060000000 | 1410553.208 | 06-OCT-15:09 | 218037.744 | 146475.648 | 225038.439 | 0 | 800447.109 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5309.715 | 0 | 0
November | 1289360000000 | 1273428.844 | 01-NOV-11:39 | 218037.744 | 159932.088 | 224164.501 | 0 | 648281.433 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 7768.526 | 0 | 0
December | 1115870000000 | 1164945.174 | 15-DEC-16:10 | 218037.744 | 146475.648 | 223191.101 | 0 | 556688.828 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5307.299 | 0 | 0
Annual Sum or Average | 15944500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1092330000000 | 1164945.174 |  | 121132.08 | 86203.896 | 223092.951 | 0 | 553765.751 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 5056.299 | 0 | 0
Maximum of Months | 1571460000000 | 1552528.04 |  | 218037.744 | 160954.2 | 227212.397 | 0 | 942928.319 | 0 | 15244.553 | 0 | 0 | 0 | 0 | 0 | 7768.526 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 392774.77 | 8563.18 | 0 | 401337.94
Cost per Total Building Area ($/m2) | 20.05 | 0.44 | 0 | 20.48
Cost per Net Conditioned Building Area ($/m2) | 20.05 | 0.44 | 0 | 20.48
02-Houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 17396.13 | 887.92 | 887.92
Net Site Energy | 17396.13 | 887.92 | 887.92
Total Source Energy | 2932.97 | 149.7 | 149.7
Net Source Energy | 2932.97 | 149.7 | 149.7
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2059.35 | 0 | 0 | 0 | 0
Cooling | 5008.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3111.03 | 0 | 0 | 0 | 0 | 0
Pumps | 216.14 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 82.07 | 0 | 0 | 0 | 815.28
Refrigeration | 167.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14710.26 | 2685.87 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 14710.26 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 14710.26 | 100
Total On-Site and Utility Electric Sources | 14710.26 | 100
Total Electricity End Uses | 14710.26 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 21 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 21 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 53.2 | 6.88 | 0.25 | 0.25 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 53.2 | 6.88 | 0.25 | 0.25 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 12.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 49.41 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 33.6 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 36.4 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 33.6 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1622258.49 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7078480.78 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 589171.07 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 284253.77 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 326443.13 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 113884.55 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 145592.92 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 23.69 | 56153.04 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 23.64 | 56034.74 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 25.87 | 61311.69 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 33.79 | 80087.27 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 23.73 | 44990.33 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 15.23 | 28873.39 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 13.15 | 24927.88 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.59 | 8696.46 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.86 | 11117.78 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001556 | 71534.6 | 2532.63
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002047 | 94113.11 | 3332.01
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004486 | 206286.64 | 7303.44
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006264 | 288031.88 | 10197.58
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001397 | 64249.49 | 2274.71
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002608 | 119931.48 | 4246.09
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001561 | 71761.06 | 2540.65
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002078 | 95540.52 | 3382.55
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004098 | 188442.73 | 6671.69
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006211 | 285570.85 | 10110.44
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001547 | 71153.38 | 2519.14
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002043 | 93932.32 | 3325.61
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004465 | 205311.81 | 7268.93
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00624 | 286920.02 | 10158.21
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001389 | 63880.78 | 2261.66
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002603 | 119707.83 | 4238.18
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001561 | 71761.12 | 2540.65
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002078 | 95563.33 | 3383.36
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004098 | 188431.85 | 6671.3
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006213 | 285670.52 | 10113.97
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001548 | 71198.72 | 2520.74
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00205 | 94273.97 | 3337.71
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004499 | 206864.77 | 7323.91
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007691 | 353636.37 | 12520.26
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001406 | 64662.8 | 2289.34
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002676 | 123031.47 | 4355.85
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001569 | 72160.69 | 2554.8
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002089 | 96034.96 | 3400.05
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004187 | 192527.77 | 6816.32
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007558 | 347537.04 | 12304.32
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005089 | 233993.77 | 8284.39
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009499 | 436772.63 | 15463.64
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001296 | 59583.26 | 2109.51
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002025 | 93130.92 | 3297.24
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001457 | 67002.99 | 2372.2
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002329 | 107103.89 | 3791.94
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004469 | 205491.86 | 7275.3
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006414 | 294917 | 10441.34
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009734 | 447569.19 | 15845.89
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001316 | 60492.6 | 2141.7
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002448 | 112556.07 | 3984.97
VAV_POD_1_HEATC | 0.002222 | 102170.32 | 1625.14
VAV_POD_2_HEATC | 0.002224 | 102247.89 | 1625.83
VAV_POD_3_HEATC | 0.002148 | 98787.2 | 1587.47
VAV_OTHER_HEATC | 0.001456 | 66937.32 | 1095.88
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.013877 | 23.69 | 22.26 | 12.8 | 7.22 | 0.010057 | 0.0085
VAV_POD_2_COOLC | 0.013863 | 23.64 | 22.27 | 12.8 | 7.22 | 0.01006 | 0.0085
VAV_POD_3_COOLC | 0.01462 | 25.87 | 22.04 | 12.8 | 7.22 | 0.009959 | 0.0085
VAV_OTHER_COOLC | 0.015827 | 33.79 | 20.99 | 12.8 | 7.22 | 0.009497 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 363791.98
PSZ-AC_2:6_HEATC | 210230.46
PSZ-AC_3:7_HEATC | 201566.91
PSZ-AC_4:8_HEATC | 70319.62
PSZ-AC_5:9_HEATC | 89898.4
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 285593.8161 | 361.6581 | 1435.2979 | 0 | 0.0041 | 489541.9891 | 112045.1142
February | 249789.958 | 316.006 | 1250.985 | 0 | 0.0036 | 426676.228 | 97958.1625
March | 273324.9606 | 354.2571 | 1487.5809 | 0 | 0.0042 | 507414.1374 | 108280.413
April | 260690.2415 | 340.7345 | 1458.7771 | 0 | 0.0041 | 497602.0391 | 103642.8215
May | 331139.9938 | 433.945 | 1868.8187 | 0 | 0.0053 | 637475.9294 | 131797.1563
June | 366562.7864 | 480.7284 | 2073.8197 | 0 | 0.0058 | 707405.7214 | 145942.6332
July | 319843.5704 | 419.3434 | 1807.8941 | 0 | 0.0051 | 616694.7168 | 127327.0879
August | 329743.2638 | 432.0741 | 1860.3691 | 0 | 0.0052 | 634593.4798 | 131236.0242
September | 315543.785 | 413.6897 | 1783.3622 | 0 | 0.005 | 608326.4987 | 125613.2831
October | 293248.3753 | 383.5769 | 1644.9926 | 0 | 0.0046 | 561123.11 | 116624.0362
November | 263817.6822 | 342.7828 | 1447.715 | 0 | 0.0041 | 493819.7178 | 104623.3265
December | 270770.6693 | 343.7009 | 1372.201 | 0 | 0.0039 | 468025.2902 | 106334.5597
Annual Sum or Average | 3560069.1024 | 4622.4969 | 19491.8134 | 0 | 0.055 | 6648698.8576 | 1411424.6184
Minimum of Months | 249789.958 | 316.006 | 1250.985 | 0 | 0.0036 | 426676.228 | 97958.1625
Maximum of Months | 366562.7864 | 480.7284 | 2073.8197 | 0 | 0.0058 | 707405.7214 | 145942.6332
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1083110000000 | 1112231.301 | 03-JAN-12:09 | 218037.744 | 160954.2 | 224783.608 | 0 | 488233.366 | 0 | 14911.568 | 0 | 0 | 0 | 0 | 0 | 5310.815 | 0 | 0
February | 944022000000 | 1010407.561 | 23-FEB-13:00 | 218037.744 | 151354.248 | 224783.608 | 0 | 396031.558 | 0 | 14903.122 | 0 | 0 | 0 | 0 | 0 | 5297.28 | 0 | 0
March | 1122650000000 | 1093240.156 | 29-MAR-11:00 | 218037.744 | 160954.2 | 224783.608 | 0 | 469256.611 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5305.019 | 0 | 0
April | 1100950000000 | 1170128.207 | 20-APR-15:09 | 218037.744 | 146554.272 | 224783.608 | 0 | 560543.861 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5305.747 | 0 | 0
May | 1410420000000 | 1471253.219 | 18-MAY-14:09 | 218037.744 | 146554.272 | 226558.627 | 0 | 859888.298 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5311.304 | 0 | 0
June | 1565140000000 | 1440480.22 | 13-JUN-14:00 | 218037.744 | 146554.272 | 226850.778 | 0 | 828829.992 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5304.459 | 0 | 0
July | 1364440000000 | 1411425.403 | 18-JUL-11:00 | 121132.08 | 95803.848 | 224783.608 | 0 | 949739.087 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5063.805 | 0 | 0
August | 1404040000000 | 1324132.465 | 31-AUG-10:00 | 121132.08 | 95803.848 | 224783.608 | 0 | 862450.14 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5059.815 | 0 | 0
September | 1345920000000 | 1528592.28 | 15-SEP-14:39 | 218037.744 | 145532.16 | 224863.842 | 0 | 919938.352 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5317.208 | 0 | 0
October | 1241490000000 | 1303041.791 | 30-OCT-12:00 | 218037.744 | 159932.088 | 225088.505 | 0 | 679768.773 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5311.707 | 0 | 0
November | 1092580000000 | 1182513.469 | 27-NOV-16:00 | 218037.744 | 146475.648 | 224783.608 | 0 | 573001.994 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5311.501 | 0 | 0
December | 1035510000000 | 1073383.054 | 19-DEC-14:00 | 218037.744 | 150332.136 | 224783.608 | 0 | 460020.191 | 0 | 14904.9 | 0 | 0 | 0 | 0 | 0 | 5304.475 | 0 | 0
Annual Sum or Average | 14710300000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 944022000000 | 1010407.561 |  | 121132.08 | 95803.848 | 224783.608 | 0 | 396031.558 | 0 | 14902.974 | 0 | 0 | 0 | 0 | 0 | 5059.815 | 0 | 0
Maximum of Months | 1565140000000 | 1528592.28 |  | 218037.744 | 160954.2 | 226850.778 | 0 | 949739.087 | 0 | 14911.568 | 0 | 0 | 0 | 0 | 0 | 5317.208 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 467704.07 | 21728.49 | 0 | 489432.56
Cost per Total Building Area ($/m2) | 23.87 | 1.11 | 0 | 24.98
Cost per Net Conditioned Building Area ($/m2) | 23.87 | 1.11 | 0 | 24.98
03-Phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 17573.13 | 896.95 | 896.95
Net Site Energy | 17573.13 | 896.95 | 896.95
Total Source Energy | 51043.16 | 2605.31 | 2605.31
Net Source Energy | 51043.16 | 2605.31 | 2605.31
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1575.24 | 0 | 0 | 0 | 0
Cooling | 5043.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.62 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3588.03 | 0 | 0 | 0 | 0 | 0
Pumps | 375.41 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 72.79 | 0 | 0 | 0 | 815.28
Refrigeration | 166.29 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15380.64 | 2192.49 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 15380.64 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 15380.64 | 100
Total On-Site and Utility Electric Sources | 15380.64 | 100
Total Electricity End Uses | 15380.64 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 6.88 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 15.4 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 6.88 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 74.2 | 6.88 | 0.25 | 0.25 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 6.88 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 6.88 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 21 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 21 | 6.88 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 6.88 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 6.88 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 53.2 | 6.88 | 0.25 | 0.25 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 53.2 | 6.88 | 0.25 | 0.25 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 12.6 | 6.88 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 49.41 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 33.6 | 6.88 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 36.4 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_NORTH | 33.6 | 6.88 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3034269.5 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 8033472.59 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 623801.1 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 297294.66 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 285805.85 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 103929.16 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 141367.94 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 29.03 | 68814.23 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 28.99 | 68720.34 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 31.26 | 74095.18 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 40.16 | 95181.98 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 25.12 | 47634.75 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 17.96 | 34055.88 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.73 | 27933 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.8 | 9105.21 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 6.39 | 12113.23 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001848 | 84955.77 | 3007.8
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002475 | 113819.35 | 4029.7
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005392 | 247923.17 | 8777.55
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00785 | 360936.32 | 12778.71
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001415 | 65063.27 | 2303.52
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002992 | 137586.81 | 4871.17
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001794 | 82510.01 | 2921.21
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00245 | 112634.54 | 3987.75
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004625 | 212635.42 | 7528.21
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007334 | 337206.36 | 11938.56
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001844 | 84800.78 | 3002.31
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002473 | 113689.85 | 4025.11
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005383 | 247501.79 | 8762.63
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007828 | 359937.14 | 12743.33
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001406 | 64645.73 | 2288.74
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002986 | 137287.39 | 4860.57
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001794 | 82504.99 | 2921.03
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00245 | 112648.72 | 3988.25
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004624 | 212605.78 | 7527.16
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007335 | 337253.84 | 11940.25
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001845 | 84837.78 | 3003.62
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00248 | 114013.03 | 4036.55
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005416 | 249028.55 | 8816.69
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009285 | 426910.5 | 15114.48
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001424 | 65455.88 | 2317.42
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.003058 | 140622.46 | 4978.64
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.0018 | 82761.46 | 2930.11
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002459 | 113073.52 | 4003.29
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004693 | 215795.9 | 7640.11
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008645 | 397475.14 | 14072.34
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005243 | 241086.83 | 8535.52
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.0109 | 501162.46 | 17743.32
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001525 | 70102.82 | 2481.94
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002529 | 116280.2 | 4116.82
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001665 | 76549.27 | 2710.18
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002799 | 128708.98 | 4556.86
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00524 | 240947.77 | 8530.59
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007877 | 362167.57 | 12822.3
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.011163 | 513262.94 | 18171.73
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001199 | 55112.5 | 1951.22
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002663 | 122461.82 | 4335.68
VAV_POD_1_HEATC | 0.001308 | 60148.36 | 982.83
VAV_POD_2_HEATC | 0.001309 | 60207.74 | 983.74
VAV_POD_3_HEATC | 0.001236 | 56808.42 | 930.97
VAV_OTHER_HEATC | 0.00066 | 30343.68 | 503.81
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.024972 | 29.03 | 22.86 | 12.8 | 7.22 | 0.008296 | 0.004148
VAV_POD_2_COOLC | 0.024947 | 28.99 | 22.86 | 12.8 | 7.22 | 0.008296 | 0.004148
VAV_POD_3_COOLC | 0.026689 | 31.26 | 22.65 | 12.8 | 7.22 | 0.008338 | 0.004169
VAV_OTHER_COOLC | 0.032222 | 40.16 | 21.41 | 12.8 | 7.22 | 0.008361 | 0.00418
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 324970.09
PSZ-AC_2:6_HEATC | 197752.3
PSZ-AC_3:7_HEATC | 190562.38
PSZ-AC_4:8_HEATC | 62116.86
PSZ-AC_5:9_HEATC | 82637.92
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 226841.0056 | 364.3064 | 1146.7848 | 0 | 0.0032 | 8470313.5712 | 94527.7796
February | 205496.6131 | 332.5167 | 1056.8878 | 0 | 0.0029 | 7806457.1113 | 85885.0124
March | 253824.9022 | 421.0141 | 1379.9319 | 0 | 0.0038 | 10193100 | 107124.5112
April | 240185.9249 | 402.3367 | 1334.3231 | 0 | 0.0036 | 9856400.8749 | 101767.2558
May | 285791.1057 | 480.6593 | 1601.6326 | 0 | 0.0043 | 11831100 | 121285.3421
June | 327562.2899 | 551.5773 | 1840.5367 | 0 | 0.005 | 13595900 | 139079.6224
July | 291296.3509 | 490.406 | 1636.0128 | 0 | 0.0044 | 12085000 | 123670.9948
August | 295821.9551 | 497.8729 | 1660.3297 | 0 | 0.0045 | 12264700 | 125576.9767
September | 294617.9752 | 495.9337 | 1654.203 | 0 | 0.0045 | 12219400 | 125074.7023
October | 261450.6932 | 438.2958 | 1454.9046 | 0 | 0.004 | 10747100 | 110811.3965
November | 235419.0893 | 389.8616 | 1275.3597 | 0 | 0.0035 | 9420627.0221 | 99293.4874
December | 228982.5458 | 365.2908 | 1139.8525 | 0 | 0.0031 | 8418976.7112 | 95171.9452
Annual Sum or Average | 3147290.451 | 5230.0712 | 17180.7592 | 0 | 0.0468 | 126909000 | 1329269.0264
Minimum of Months | 205496.6131 | 332.5167 | 1056.8878 | 0 | 0.0029 | 7806457.1113 | 85885.0124
Maximum of Months | 327562.2899 | 551.5773 | 1840.5367 | 0 | 0.005 | 13595900 | 139079.6224
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1026550000000 | 1010502.967 | 26-JAN-16:10 | 218037.744 | 146554.272 | 259272.362 | 0 | 353512.07 | 0 | 27867.726 | 0 | 0 | 0 | 0 | 0 | 5258.793 | 0 | 0
February | 946097000000 | 1051148.333 | 28-FEB-16:00 | 218037.744 | 146554.272 | 259272.362 | 0 | 394187.406 | 0 | 27842.346 | 0 | 0 | 0 | 0 | 0 | 5254.203 | 0 | 0
March | 1235340000000 | 1165901.769 | 17-MAR-15:09 | 218037.744 | 146554.272 | 259272.362 | 0 | 509249.32 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 4945.97 | 0 | 0
April | 1194540000000 | 1194451.422 | 26-APR-15:09 | 218037.744 | 146554.272 | 259272.362 | 0 | 537802.058 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 4942.885 | 0 | 0
May | 1433860000000 | 1328070.113 | 30-MAY-15:00 | 218037.744 | 146554.272 | 259668.075 | 0 | 670701.63 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 5266.291 | 0 | 0
June | 1647740000000 | 1543931.828 | 28-JUN-15:00 | 218037.744 | 146554.272 | 262000.454 | 0 | 884333.181 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 5164.077 | 0 | 0
July | 1464640000000 | 1351699.787 | 11-JUL-15:00 | 121132.08 | 81403.92 | 259332.922 | 0 | 856948.767 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 5039.997 | 0 | 0
August | 1486410000000 | 1318682.524 | 01-AUG-15:00 | 121132.08 | 81403.92 | 259323.207 | 0 | 823955.118 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 5026.098 | 0 | 0
September | 1480920000000 | 1422537.239 | 08-SEP-15:00 | 218037.744 | 146475.648 | 259998.919 | 0 | 765130.859 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 5051.968 | 0 | 0
October | 1302490000000 | 1199005.491 | 02-OCT-15:00 | 218037.744 | 146475.648 | 259386.146 | 0 | 542000.013 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 5263.839 | 0 | 0
November | 1141730000000 | 1112069.838 | 13-NOV-16:10 | 218037.744 | 146475.648 | 259272.362 | 0 | 455176.812 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 5265.171 | 0 | 0
December | 1020330000000 | 1002158.28 | 11-DEC-16:10 | 218037.744 | 146475.648 | 259272.362 | 0 | 345239.038 | 0 | 27869.932 | 0 | 0 | 0 | 0 | 0 | 5263.557 | 0 | 0
Annual Sum or Average | 15380600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 946097000000 | 1002158.28 |  | 121132.08 | 81403.92 | 259272.362 | 0 | 345239.038 | 0 | 27842.101 | 0 | 0 | 0 | 0 | 0 | 4942.885 | 0 | 0
Maximum of Months | 1647740000000 | 1543931.828 |  | 218037.744 | 146554.272 | 262000.454 | 0 | 884333.181 | 0 | 27869.932 | 0 | 0 | 0 | 0 | 0 | 5266.291 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 351817.57 | 18192.19 | 0 | 370009.76
Cost per Total Building Area ($/m2) | 17.96 | 0.93 | 0 | 18.89
Cost per Net Conditioned Building Area ($/m2) | 17.96 | 0.93 | 0 | 18.89
04-Atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16906.56 | 862.93 | 862.93
Net Site Energy | 16906.56 | 862.93 | 862.93
Total Source Energy | 47352.04 | 2416.91 | 2416.91
Net Source Energy | 47352.04 | 2416.91 | 2416.91
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3546.35 | 0 | 0 | 0 | 0
Cooling | 3097.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3047.8 | 0 | 0 | 0 | 0 | 0
Pumps | 196.1 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 100.04 | 0 | 0 | 0 | 815.28
Refrigeration | 166.79 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12715.71 | 4190.85 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12715.71 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12715.71 | 100
Total On-Site and Utility Electric Sources | 12715.71 | 100
Total Electricity End Uses | 12715.71 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 21 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 21 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 53.2 | 3.24 | 0.25 | 0.318 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 53.2 | 3.24 | 0.25 | 0.318 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 12.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 49.41 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 33.6 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 36.4 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 33.6 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1458626.61 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 6595784.12 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 589018.79 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 256410.84 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 314844.47 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 116250.64 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 139633.65 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 22.29 | 52843.01 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 22.19 | 52593.19 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 24.5 | 58061.76 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 31.97 | 75777.63 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 23.72 | 44978.7 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.43 | 27372.03 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 12.68 | 24042.18 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.68 | 8877.14 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.62 | 10662.72 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00139 | 63892.23 | 2262.06
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001865 | 85730.13 | 3035.22
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004258 | 195775.28 | 6931.29
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006045 | 277930.23 | 9839.93
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001237 | 56860.8 | 2013.12
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002416 | 111097.58 | 3933.34
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001351 | 62104.71 | 2198.78
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001852 | 85151.53 | 3014.73
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003466 | 159381.22 | 5642.78
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00552 | 253832.56 | 8986.77
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001378 | 63351.13 | 2242.9
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001859 | 85456.61 | 3025.53
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004191 | 192724.37 | 6823.28
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006001 | 275919.45 | 9768.74
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001226 | 56389.08 | 1996.42
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00241 | 110813.35 | 3923.27
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001351 | 62106.88 | 2198.85
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001853 | 85191.65 | 3016.15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003466 | 159377.91 | 5642.67
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005525 | 254035.29 | 8993.95
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001379 | 63402.89 | 2244.74
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001867 | 85830.78 | 3038.78
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004228 | 194397.81 | 6882.52
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007468 | 343399.02 | 12157.81
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001245 | 57229.62 | 2026.18
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002484 | 114209.93 | 4043.53
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001364 | 62719.75 | 2220.55
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001865 | 85730.48 | 3035.23
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003588 | 164992.8 | 5841.46
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006815 | 313342.03 | 11093.66
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004416 | 203053.05 | 7188.96
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008753 | 402455.4 | 14248.66
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001205 | 55392.56 | 1961.14
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00193 | 88763.21 | 3142.6
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001223 | 56224.91 | 1990.61
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002064 | 94882.57 | 3359.25
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004137 | 190207.01 | 6734.15
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006059 | 278609.2 | 9863.97
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00883 | 406021.68 | 14374.93
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001218 | 56014.65 | 1983.16
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002323 | 106813.49 | 3781.66
VAV_POD_1_HEATC | 0.002807 | 129044.51 | 1967.79
VAV_POD_2_HEATC | 0.00281 | 129202.92 | 1968.55
VAV_POD_3_HEATC | 0.002735 | 125735.2 | 1949
VAV_OTHER_HEATC | 0.001979 | 90986.68 | 1474.6
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.012452 | 22.29 | 22.07 | 12.8 | 7.22 | 0.01006 | 0.0085
VAV_POD_2_COOLC | 0.012424 | 22.19 | 22.08 | 12.8 | 7.22 | 0.010067 | 0.0085
VAV_POD_3_COOLC | 0.013123 | 24.5 | 21.79 | 12.8 | 7.22 | 0.009956 | 0.0085
VAV_OTHER_COOLC | 0.014318 | 31.97 | 20.87 | 12.8 | 7.22 | 0.009494 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 392336.38
PSZ-AC_2:6_HEATC | 219414.63
PSZ-AC_3:7_HEATC | 209713.08
PSZ-AC_4:8_HEATC | 77432.77
PSZ-AC_5:9_HEATC | 93007.83
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 253112.9194 | 428.4732 | 975.244 | 0 | 0.0037 | 1734227.8379 | 105955.4117
February | 213286.775 | 367.7267 | 854.4993 | 0 | 0.0032 | 1519591.3133 | 89899.9746
March | 214942.4318 | 396.0461 | 985.9631 | 0 | 0.0036 | 1753664.2954 | 92949.5858
April | 199698.9773 | 378.0837 | 965.6718 | 0 | 0.0035 | 1717672.5593 | 87292.7583
May | 227788.0382 | 435.704 | 1123.2667 | 0 | 0.0041 | 1998033.0647 | 99981.1655
June | 253361.53 | 486.4403 | 1258.2978 | 0 | 0.0046 | 2238238.9166 | 111374.0428
July | 218574.4392 | 418.9747 | 1082.2156 | 0 | 0.004 | 1925020.7992 | 96019.6879
August | 230657.1573 | 441.8773 | 1140.7744 | 0 | 0.0042 | 2029181.4529 | 101303.7765
September | 235742.0772 | 452.3208 | 1169.3652 | 0 | 0.0043 | 2080044.536 | 103601.9017
October | 207591.9097 | 392.5282 | 1001.3936 | 0 | 0.0037 | 1781207.5497 | 90696.8579
November | 205523.6947 | 373.2838 | 916.25 | 0 | 0.0034 | 1629617.4735 | 88377.146
December | 227453.4378 | 395.158 | 925.9944 | 0 | 0.0035 | 1646767.6795 | 96148.8654
Annual Sum or Average | 2687733.3877 | 4966.6168 | 12398.9359 | 0 | 0.0457 | 22053300 | 1163601.1743
Minimum of Months | 199698.9773 | 367.7267 | 854.4993 | 0 | 0.0032 | 1519591.3133 | 87292.7583
Maximum of Months | 253361.53 | 486.4403 | 1258.2978 | 0 | 0.0046 | 2238238.9166 | 111374.0428
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 999939000000 | 757461.878 | 24-JAN-16:10 | 218037.744 | 146554.272 | 216127.278 | 0 | 157959.797 | 0 | 13479.029 | 0 | 0 | 0 | 0 | 0 | 5303.757 | 0 | 0
February | 876182000000 | 764785.128 | 21-FEB-13:00 | 218037.744 | 151354.248 | 216127.278 | 0 | 160535.014 | 0 | 13427.957 | 0 | 0 | 0 | 0 | 0 | 5302.886 | 0 | 0
March | 1011150000000 | 868159.271 | 28-MAR-15:00 | 218037.744 | 146554.272 | 216201.465 | 0 | 268690.76 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5271.516 | 0 | 0
April | 990394000000 | 1030609.03 | 13-APR-15:09 | 218037.744 | 146554.272 | 216132.335 | 0 | 431186.934 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5294.23 | 0 | 0
May | 1152050000000 | 1194510.336 | 15-MAY-14:00 | 218037.744 | 146554.272 | 219669.58 | 0 | 591548.104 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5297.122 | 0 | 0
June | 1290550000000 | 1310713 | 08-JUN-15:09 | 218037.744 | 146554.272 | 216514.406 | 0 | 710895.875 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5307.188 | 0 | 0
July | 1109950000000 | 1266964.375 | 03-JUL-11:00 | 121132.08 | 95803.848 | 216263.895 | 0 | 815305.111 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5055.926 | 0 | 0
August | 1170010000000 | 1168702.445 | 17-AUG-14:00 | 121132.08 | 81403.92 | 216127.278 | 0 | 731580.845 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5054.807 | 0 | 0
September | 1199330000000 | 1228220.754 | 11-SEP-13:00 | 218037.744 | 150332.136 | 217242.684 | 0 | 623899.848 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5304.827 | 0 | 0
October | 1027030000000 | 1093508.611 | 12-OCT-15:00 | 218037.744 | 146475.648 | 216260.885 | 0 | 494044.683 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5286.136 | 0 | 0
November | 939622000000 | 822920.433 | 22-NOV-16:10 | 218037.744 | 146475.648 | 216127.278 | 0 | 223585.262 | 0 | 13406.278 | 0 | 0 | 0 | 0 | 0 | 5288.222 | 0 | 0
December | 949511000000 | 792718.629 | 26-DEC-12:00 | 218037.744 | 159932.088 | 216127.278 | 0 | 179828.741 | 0 | 13483.687 | 0 | 0 | 0 | 0 | 0 | 5309.091 | 0 | 0
Annual Sum or Average | 12715700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 876182000000 | 757461.878 |  | 121132.08 | 81403.92 | 216127.278 | 0 | 157959.797 | 0 | 13403.514 | 0 | 0 | 0 | 0 | 0 | 5054.807 | 0 | 0
Maximum of Months | 1290550000000 | 1310713 |  | 218037.744 | 159932.088 | 219669.58 | 0 | 815305.111 | 0 | 13483.687 | 0 | 0 | 0 | 0 | 0 | 5309.091 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 357204.84 | 40686.41 | 0 | 397891.25
Cost per Total Building Area ($/m2) | 18.23 | 2.08 | 0 | 20.31
Cost per Net Conditioned Building Area ($/m2) | 18.23 | 2.08 | 0 | 20.31
05-Los Angeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 12528.65 | 639.48 | 639.48
Net Site Energy | 12528.65 | 639.48 | 639.48
Total Source Energy | 35968.65 | 1835.88 | 1835.88
Net Source Energy | 35968.65 | 1835.88 | 1835.88
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 763.18 | 0 | 0 | 0 | 0
Cooling | 2037.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2505.64 | 0 | 0 | 0 | 0 | 0
Pumps | 208.98 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 94.02 | 0 | 0 | 0 | 815.28
Refrigeration | 167.56 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11126.99 | 1401.66 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 11126.99 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 11126.99 | 100
Total On-Site and Utility Electric Sources | 11126.99 | 100
Total Electricity End Uses | 11126.99 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 21 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 21 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 53.2 | 3.24 | 0.25 | 0.318 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 53.2 | 3.24 | 0.25 | 0.318 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 12.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 49.41 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 33.6 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 36.4 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 33.6 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1767198.92 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 5776679.77 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 376812.83 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 206888.93 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 176745.62 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73172.09 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 82124.19 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 19.61 | 46493.23 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 19.49 | 46200.35 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 21.86 | 51810.44 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 28.08 | 66565.14 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 21.37 | 40521.96 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 12.5 | 23699.66 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 10.68 | 20246.67 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.42 | 8382.05 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.96 | 9407.54 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001399 | 64334.44 | 2277.72
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001807 | 83085.94 | 2941.6
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004368 | 200828.42 | 7110.2
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005938 | 273036.96 | 9666.69
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001192 | 54809.36 | 1940.49
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002175 | 99993.11 | 3540.19
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001156 | 53175.22 | 1882.63
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001569 | 72152.01 | 2554.49
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002774 | 127547.07 | 4515.72
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004374 | 201106.91 | 7120.06
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001388 | 63803.06 | 2258.9
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001802 | 82840.67 | 2932.92
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004284 | 196994.08 | 6974.44
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005885 | 270580.66 | 9579.73
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001181 | 54290.72 | 1922.13
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002167 | 99643.96 | 3527.83
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001156 | 53173.35 | 1882.57
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00157 | 72185.97 | 2555.7
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002773 | 127519.74 | 4514.75
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004378 | 201288.45 | 7126.48
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001389 | 63852.67 | 2260.66
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00181 | 83208.23 | 2945.93
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00432 | 198643.31 | 7032.83
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007351 | 338020.64 | 11967.39
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001197 | 55022.69 | 1948.04
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002239 | 102939.84 | 3644.52
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001169 | 53739.1 | 1902.6
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001582 | 72734.01 | 2575.1
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002882 | 132536.8 | 4692.38
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005873 | 270049.44 | 9560.92
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004139 | 190329.57 | 6738.49
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007756 | 356601.99 | 12625.25
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001229 | 56496.45 | 2000.22
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001858 | 85424.68 | 3024.4
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.000951 | 43741.05 | 1548.62
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001602 | 73680 | 2608.59
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004081 | 187637.03 | 6643.16
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005746 | 264209.17 | 9354.15
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007673 | 352794.22 | 12490.44
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001181 | 54315.02 | 1922.99
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002085 | 95882.1 | 3394.64
VAV_POD_1_HEATC | 0.001197 | 55047.23 | 893.13
VAV_POD_2_HEATC | 0.001201 | 55239.37 | 895.99
VAV_POD_3_HEATC | 0.001121 | 51558.87 | 840.5
VAV_OTHER_HEATC | 0.000665 | 30586.2 | 505.94
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.016494 | 19.61 | 21.44 | 12.8 | 7.22 | 0.008493 | 0.004247
VAV_POD_2_COOLC | 0.016403 | 19.49 | 21.46 | 12.8 | 7.22 | 0.008493 | 0.004247
VAV_POD_3_COOLC | 0.008123 | 21.86 | 21.19 | 12.8 | 7.22 | 0.008529 | 0.0085
VAV_OTHER_COOLC | 0.022365 | 28.08 | 20.43 | 12.8 | 7.22 | 0.008491 | 0.004246
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 258140.76
PSZ-AC_2:6_HEATC | 150881.56
PSZ-AC_3:7_HEATC | 128979.21
PSZ-AC_4:8_HEATC | 53396.96
PSZ-AC_5:9_HEATC | 59929.71
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 89091.9788 | 76.8456 | 723.0131 | 0 | 0.0003 | 4362187.7706 | 33040.7679
February | 78954.7665 | 68.0767 | 645.2409 | 0 | 0.0003 | 3892978.6808 | 29294.9819
March | 92434.6568 | 79.559 | 780.517 | 0 | 0.0004 | 4709245.5108 | 34373.1168
April | 83539.8582 | 71.7606 | 730.9224 | 0 | 0.0003 | 4410110.1278 | 31143.3006
May | 92105.3639 | 79.0362 | 820.564 | 0 | 0.0004 | 4951026.3859 | 34381.3297
June | 91066.6316 | 78.1063 | 818.2031 | 0 | 0.0004 | 4936805.4848 | 34014.6197
July | 73776.1823 | 63.3503 | 649.6649 | 0 | 0.0003 | 3919847.7438 | 27516.1625
August | 82861.6725 | 71.1344 | 732.7988 | 0 | 0.0003 | 4421459.533 | 30914.3043
September | 89064.2831 | 76.3769 | 802.367 | 0 | 0.0004 | 4841262.3851 | 33273.2882
October | 90340.9988 | 77.5053 | 807.8696 | 0 | 0.0004 | 4874442.8765 | 33731.9499
November | 87954.65 | 75.587 | 763.4552 | 0 | 0.0004 | 4606379.5795 | 32770.524
December | 86211.7718 | 74.2491 | 719.7075 | 0 | 0.0003 | 4342321.2246 | 32033.8384
Annual Sum or Average | 1037402.8142 | 891.5875 | 8994.3237 | 0 | 0.0042 | 54268100 | 386488.1839
Minimum of Months | 73776.1823 | 63.3503 | 645.2409 | 0 | 0.0003 | 3892978.6808 | 27516.1625
Maximum of Months | 92434.6568 | 79.559 | 820.564 | 0 | 0.0004 | 4951026.3859 | 34381.3297
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 894412000000 | 865465.619 | 26-JAN-12:00 | 218037.744 | 160954.2 | 190714.396 | 0 | 274251.913 | 0 | 16233.208 | 0 | 0 | 0 | 0 | 0 | 5274.159 | 0 | 0
February | 798207000000 | 846323.762 | 13-FEB-11:00 | 218037.744 | 160954.2 | 191098.664 | 0 | 254717.385 | 0 | 16232.604 | 0 | 0 | 0 | 0 | 0 | 5283.165 | 0 | 0
March | 965572000000 | 824011.439 | 30-MAR-11:00 | 218037.744 | 160954.2 | 190741.848 | 0 | 232776.596 | 0 | 16231.818 | 0 | 0 | 0 | 0 | 0 | 5269.233 | 0 | 0
April | 904238000000 | 914198.757 | 11-APR-15:00 | 218037.744 | 146554.272 | 190820.819 | 0 | 337266.79 | 0 | 16231.152 | 0 | 0 | 0 | 0 | 0 | 5287.98 | 0 | 0
May | 1015150000000 | 937218.229 | 30-MAY-09:09 | 218037.744 | 160954.2 | 190826.003 | 0 | 345862 | 0 | 16231.152 | 0 | 0 | 0 | 0 | 0 | 5307.129 | 0 | 0
June | 1012230000000 | 896289.842 | 28-JUN-12:00 | 218037.744 | 151354.248 | 190680.675 | 0 | 314682.015 | 0 | 16231.152 | 0 | 0 | 0 | 0 | 0 | 5304.008 | 0 | 0
July | 803716000000 | 751255.902 | 10-JUL-09:00 | 121132.08 | 95803.848 | 190659.753 | 0 | 322377.778 | 0 | 16231.152 | 0 | 0 | 0 | 0 | 0 | 5051.289 | 0 | 0
August | 906565000000 | 867251.835 | 08-AUG-09:00 | 121132.08 | 95803.848 | 190659.753 | 0 | 438366.063 | 0 | 16233.293 | 0 | 0 | 0 | 0 | 0 | 5056.798 | 0 | 0
September | 992641000000 | 1008851.134 | 25-SEP-14:00 | 218037.744 | 145532.16 | 195068.828 | 0 | 428686.594 | 0 | 16231.152 | 0 | 0 | 0 | 0 | 0 | 5294.656 | 0 | 0
October | 999444000000 | 931625.618 | 19-OCT-10:00 | 218037.744 | 159932.088 | 190868.576 | 0 | 341277.741 | 0 | 16231.152 | 0 | 0 | 0 | 0 | 0 | 5278.316 | 0 | 0
November | 944481000000 | 870673.364 | 20-NOV-12:00 | 218037.744 | 159932.088 | 191259.967 | 0 | 279922.404 | 0 | 16231.576 | 0 | 0 | 0 | 0 | 0 | 5289.586 | 0 | 0
December | 890339000000 | 879984.061 | 19-DEC-12:00 | 218037.744 | 159932.088 | 191259.462 | 0 | 289250.111 | 0 | 16232.604 | 0 | 0 | 0 | 0 | 0 | 5272.053 | 0 | 0
Annual Sum or Average | 11127000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 798207000000 | 751255.902 |  | 121132.08 | 95803.848 | 190659.753 | 0 | 232776.596 | 0 | 16231.152 | 0 | 0 | 0 | 0 | 0 | 5051.289 | 0 | 0
Maximum of Months | 1015150000000 | 1008851.134 |  | 218037.744 | 160954.2 | 195068.828 | 0 | 438366.063 | 0 | 16233.293 | 0 | 0 | 0 | 0 | 0 | 5307.129 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 180921.81 | 11993.85 | 0 | 192915.66
Cost per Total Building Area ($/m2) | 9.23 | 0.61 | 0 | 9.85
Cost per Net Conditioned Building Area ($/m2) | 9.23 | 0.61 | 0 | 9.85
06-Las Vegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16416.52 | 837.92 | 837.92
Net Site Energy | 16416.52 | 837.92 | 837.92
Total Source Energy | 52593.6 | 2684.44 | 2684.44
Net Source Energy | 52593.6 | 2684.44 | 2684.44
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1835.68 | 0 | 0 | 0 | 0
Cooling | 3808 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3450.29 | 0 | 0 | 0 | 0 | 0
Pumps | 318.82 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 85.98 | 0 | 0 | 0 | 815.28
Refrigeration | 166.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13950.4 | 2466.12 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 13950.4 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 13950.4 | 100
Total On-Site and Utility Electric Sources | 13950.4 | 100
Total Electricity End Uses | 13950.4 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 3.24 | 0.25 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 15.4 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 3.24 | 0.25 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 74.2 | 3.24 | 0.25 | 0.318 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 3.24 | 0.25 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 3.24 | 0.25 | 0.318 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 21 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 21 | 3.24 | 0.25 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 3.24 | 0.25 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 3.24 | 0.25 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 6.92 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 53.2 | 3.24 | 0.25 | 0.318 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 53.2 | 3.24 | 0.25 | 0.318 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 12.6 | 3.24 | 0.25 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 49.41 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 33.6 | 3.24 | 0.25 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 36.4 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_NORTH | 33.6 | 3.24 | 0.25 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2691030.13 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7308215.68 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 557804.84 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 278313.79 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 235960.4 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87694.25 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 116266.4 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 26.73 | 63353.43 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 26.62 | 63095.38 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 29.11 | 69008.66 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 37.89 | 89818.39 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 25.63 | 48609.93 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 16.81 | 31881.57 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.25 | 27029.88 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.84 | 9180.25 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 6.17 | 11697.57 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001615 | 74278.37 | 2629.78
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002174 | 99939.32 | 3538.28
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004817 | 221486.45 | 7841.58
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007003 | 321987.04 | 11399.74
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001322 | 60798.62 | 2152.53
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002762 | 126977.82 | 4495.56
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001562 | 71824.26 | 2542.89
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002158 | 99212.11 | 3512.54
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003958 | 181992.62 | 6443.33
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006431 | 295714.82 | 10469.58
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001605 | 73790.27 | 2612.5
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002168 | 99701.07 | 3529.85
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004752 | 218519.15 | 7736.52
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006958 | 319942.79 | 11327.36
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001312 | 60315.36 | 2135.42
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002755 | 126680.99 | 4485.06
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001562 | 71821.66 | 2542.8
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002158 | 99246.01 | 3513.74
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003958 | 181969.5 | 6442.51
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006435 | 295893.96 | 10475.93
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001606 | 73836.58 | 2614.13
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002176 | 100059.08 | 3542.52
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004786 | 220082.63 | 7791.88
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008422 | 387246.14 | 13710.19
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00133 | 61166.25 | 2165.55
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002829 | 130055.64 | 4604.53
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001574 | 72354.96 | 2561.68
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00217 | 99781.33 | 3532.69
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004073 | 187258.46 | 6629.76
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007854 | 361106.61 | 12784.74
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004847 | 222858.29 | 7890.15
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.010091 | 463974.13 | 16426.69
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001359 | 62508.15 | 2213.06
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002252 | 103558.31 | 3666.41
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001434 | 65939.89 | 2334.56
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002457 | 112983.12 | 4000.09
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004638 | 213260.25 | 7550.34
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006991 | 321449.1 | 11380.69
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.010067 | 462869.01 | 16387.57
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001217 | 55947.34 | 1980.78
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002569 | 118112.63 | 4181.7
VAV_POD_1_HEATC | 0.001882 | 86513.18 | 1394.46
VAV_POD_2_HEATC | 0.001885 | 86670.13 | 1396.72
VAV_POD_3_HEATC | 0.001807 | 83073.55 | 1344.44
VAV_OTHER_HEATC | 0.001163 | 53458.72 | 879.76
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.021978 | 26.73 | 23.08 | 12.8 | 7.22 | 0.008017 | 0.004009
VAV_POD_2_COOLC | 0.021904 | 26.62 | 23.1 | 12.8 | 7.22 | 0.008015 | 0.004008
VAV_POD_3_COOLC | 0.023669 | 29.11 | 22.77 | 12.8 | 7.22 | 0.008086 | 0.004043
VAV_OTHER_COOLC | 0.028969 | 37.89 | 21.46 | 12.8 | 7.22 | 0.008183 | 0.004092
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 358493.05
PSZ-AC_2:6_HEATC | 202140.09
PSZ-AC_3:7_HEATC | 199342.45
PSZ-AC_4:8_HEATC | 67703.33
PSZ-AC_5:9_HEATC | 86268.31
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 251629.3118 | 386.9502 | 1491.1187 | 0 | 0.0029 | 7435717.3111 | 103567.8115
February | 209798.3562 | 333.3709 | 1344.2533 | 0 | 0.0025 | 6703785.6542 | 87467.727
March | 252557.8715 | 402.998 | 1634.038 | 0 | 0.0031 | 8149003.9413 | 105469.5559
April | 249435.7794 | 405.6797 | 1685.8692 | 0 | 0.0032 | 8407773.4709 | 104962.2738
May | 292149.2509 | 476.6592 | 1988.7582 | 0 | 0.0037 | 9918396.8879 | 123093.0774
June | 335344.2536 | 547.9935 | 2290.8763 | 0 | 0.0043 | 11425200 | 141381.995
July | 291882.1587 | 476.8683 | 1993.0015 | 0 | 0.0037 | 9939581.8247 | 123047.5693
August | 307084.275 | 501.5689 | 2095.5232 | 0 | 0.0039 | 10450900 | 129442.11
September | 296828.3511 | 484.8964 | 2026.2787 | 0 | 0.0038 | 10105500 | 125127.2324
October | 266220.5538 | 433.0616 | 1800.0965 | 0 | 0.0034 | 8977451.3246 | 112033.951
November | 233884.2756 | 373.928 | 1520.0515 | 0 | 0.0029 | 7580576.3443 | 97746.8948
December | 237265.09 | 369.2249 | 1447.0142 | 0 | 0.0028 | 7215960.1814 | 98109.212
Annual Sum or Average | 3224079.5274 | 5193.1996 | 21316.8794 | 0 | 0.0402 | 106310000 | 1351449.4101
Minimum of Months | 209798.3562 | 333.3709 | 1344.2533 | 0 | 0.0025 | 6703785.6542 | 87467.727
Maximum of Months | 335344.2536 | 547.9935 | 2290.8763 | 0 | 0.0043 | 11425200 | 141381.995
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 975745000000 | 890229.898 | 18-JAN-12:00 | 218037.744 | 160954.2 | 247825.677 | 0 | 233403.107 | 0 | 24736.925 | 0 | 0 | 0 | 0 | 0 | 5272.245 | 0 | 0
February | 879698000000 | 930941.138 | 08-FEB-16:10 | 218037.744 | 146554.272 | 247825.677 | 0 | 288556.121 | 0 | 24709.065 | 0 | 0 | 0 | 0 | 0 | 5258.259 | 0 | 0
March | 1069350000000 | 985797.596 | 31-MAR-15:00 | 218037.744 | 146554.272 | 247825.677 | 0 | 343754.573 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 4928.545 | 0 | 0
April | 1103300000000 | 1142145.435 | 21-APR-15:09 | 218037.744 | 146554.272 | 248046.439 | 0 | 499841.119 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 4969.074 | 0 | 0
May | 1301530000000 | 1248578.259 | 31-MAY-15:00 | 218037.744 | 146554.272 | 248411.157 | 0 | 605949.064 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 4929.235 | 0 | 0
June | 1499260000000 | 1425048.741 | 27-JUN-15:00 | 218037.744 | 146554.272 | 251490.062 | 0 | 779008.707 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 5261.168 | 0 | 0
July | 1304310000000 | 1197347.759 | 24-JUL-15:00 | 121132.08 | 81403.92 | 248054.049 | 0 | 717052.87 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 5008.053 | 0 | 0
August | 1371410000000 | 1188949.159 | 02-AUG-11:00 | 121132.08 | 95803.848 | 247825.677 | 0 | 694559.466 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 4931.301 | 0 | 0
September | 1326090000000 | 1250619.441 | 20-SEP-15:00 | 218037.744 | 146475.648 | 248867.414 | 0 | 607623.736 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 4918.112 | 0 | 0
October | 1178060000000 | 1140223.837 | 03-OCT-15:09 | 218037.744 | 146475.648 | 248305.745 | 0 | 497440.995 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 5266.918 | 0 | 0
November | 994754000000 | 948956.697 | 10-NOV-16:40 | 218037.744 | 146475.648 | 247825.677 | 0 | 282766.607 | 23884.224 | 24707.097 | 0 | 0 | 0 | 0 | 0 | 5259.7 | 0 | 0
December | 946907000000 | 930979.389 | 05-DEC-16:30 | 218037.744 | 146475.648 | 247825.677 | 0 | 264772.162 | 23884.224 | 24730.297 | 0 | 0 | 0 | 0 | 0 | 5253.639 | 0 | 0
Annual Sum or Average | 13950400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 879698000000 | 890229.898 |  | 121132.08 | 81403.92 | 247825.677 | 0 | 233403.107 | 0 | 24696.787 | 0 | 0 | 0 | 0 | 0 | 4918.112 | 0 | 0
Maximum of Months | 1499260000000 | 1425048.741 |  | 218037.744 | 160954.2 | 251490.062 | 0 | 779008.707 | 23884.224 | 24736.925 | 0 | 0 | 0 | 0 | 0 | 5272.245 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 383811.53 | 19157.71 | 0 | 402969.24
Cost per Total Building Area ($/m2) | 19.59 | 0.98 | 0 | 20.57
Cost per Net Conditioned Building Area ($/m2) | 19.59 | 0.98 | 0 | 20.57
07-San Francisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 17267.83 | 881.37 | 881.37
Net Site Energy | 17267.83 | 881.37 | 881.37
Total Source Energy | 43761.75 | 2233.65 | 2233.65
Net Source Energy | 43761.75 | 2233.65 | 2233.65
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4180.14 | 0 | 0 | 0 | 0
Cooling | 1582.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 4278.89 | 0 | 0 | 0 | 0 | 0
Pumps | 197.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 109.24 | 0 | 0 | 0 | 815.28
Refrigeration | 167.34 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12433.99 | 4833.84 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12433.99 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12433.99 | 100
Total On-Site and Utility Electric Sources | 12433.99 | 100
Total Electricity End Uses | 12433.99 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 7 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 7 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 7 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 7 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 7 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 7 | 6.88 | 0.34 | 0.34 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 15.4 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 6.88 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 74.2 | 6.88 | 0.34 | 0.34 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 25.2 | 6.88 | 0.34 | 0.34 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 23.8 | 6.88 | 0.34 | 0.34 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 25.2 | 6.88 | 0.34 | 0.34 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 23.8 | 6.88 | 0.34 | 0.34 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 21 | 6.88 | 0.34 | 0.34 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 21 | 6.88 | 0.34 | 0.34 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 4.2 | 6.88 | 0.34 | 0.34 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 21 | 6.88 | 0.34 | 0.34 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 4.2 | 6.88 | 0.34 | 0.34 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 21 | 6.88 | 0.34 | 0.34 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 53.2 | 6.88 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 19.6 | 6.88 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 53.2 | 6.88 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 19.6 | 6.88 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 33.6 | 6.88 | 0.34 | 0.34 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 72.8 | 6.88 | 0.34 | 0.34 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 33.6 | 6.88 | 0.34 | 0.34 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 72.8 | 6.88 | 0.34 | 0.34 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 6.92 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 53.2 | 6.88 | 0.34 | 0.34 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 53.2 | 6.88 | 0.34 | 0.34 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 12.6 | 6.88 | 0.34 | 0.34 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 49.41 | 6.88 | 0.34 | 0.34 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 33.6 | 6.88 | 0.34 | 0.34 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 36.4 | 6.88 | 0.34 | 0.34 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_NORTH | 33.6 | 6.88 | 0.34 | 0.34 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1829988.97 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 9245130.79 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 669768.32 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 278555.46 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 339147.98 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 89743.03 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 175241.29 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 34.43 | 81600.51 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 34.27 | 81222.98 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 36.03 | 85391.31 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 39.27 | 93088.14 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 40.46 | 76723.7 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 16.83 | 31909.25 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 20.49 | 38850.28 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.42 | 10280.3 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 10.59 | 20074.35 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002417 | 111124.56 | 3934.29
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002837 | 130443.27 | 4618.26
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.008736 | 401678.82 | 14221.17
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.010355 | 476138.19 | 16857.35
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002232 | 102640.56 | 3633.92
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.003078 | 141544.41 | 5011.28
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001873 | 86133.78 | 3049.51
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002264 | 104095.97 | 3685.45
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005903 | 271397.42 | 9608.64
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007408 | 340629.26 | 12059.75
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002408 | 110717.33 | 3919.87
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002833 | 130243.33 | 4611.18
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.008632 | 396895.12 | 14051.81
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.010285 | 472914.05 | 16743.2
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002215 | 101831.03 | 3605.26
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.003064 | 140861.82 | 4987.12
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001873 | 86125.66 | 3049.22
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002264 | 104118.56 | 3686.25
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005901 | 271346.71 | 9606.85
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007411 | 340752.28 | 12064.11
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002409 | 110765.49 | 3921.58
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00284 | 130590.06 | 4623.45
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.008673 | 398804.86 | 14119.42
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.011341 | 521444.28 | 18461.38
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002232 | 102612.71 | 3632.93
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.003135 | 144146.66 | 5103.42
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001883 | 86560.25 | 3064.61
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002275 | 104604.18 | 3703.44
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005996 | 275691.92 | 9760.69
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008508 | 391220.65 | 13850.9
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005277 | 242649.1 | 8590.83
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008596 | 395249.45 | 13993.54
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00194 | 89208.36 | 3158.36
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002523 | 116024.42 | 4107.77
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001558 | 71659.49 | 2537.06
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002127 | 97806.51 | 3462.77
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006368 | 292805.68 | 10366.59
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007944 | 365268.51 | 12932.09
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.012761 | 586766.97 | 20774.09
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001914 | 87997.57 | 3115.49
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002725 | 125292.95 | 4435.91
VAV_POD_1_HEATC | 0.001139 | 52385.36 | 862.1
VAV_POD_2_HEATC | 0.001145 | 52633.79 | 866.05
VAV_POD_3_HEATC | 0.001085 | 49890.59 | 822.35
VAV_OTHER_HEATC | 0.000683 | 31418.85 | 521.58
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.011582 | 34.43 | 20.3 | 12.8 | 7.22 | 0.008553 | 0.0085
VAV_POD_2_COOLC | 0.011538 | 34.27 | 20.31 | 12.8 | 7.22 | 0.008553 | 0.0085
VAV_POD_3_COOLC | 0.012009 | 36.03 | 20.24 | 12.8 | 7.22 | 0.008552 | 0.0085
VAV_OTHER_COOLC | 0.030507 | 39.27 | 19.94 | 12.8 | 7.22 | 0.008479 | 0.00424
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 540241.35
PSZ-AC_2:6_HEATC | 196609.11
PSZ-AC_3:7_HEATC | 273559.92
PSZ-AC_4:8_HEATC | 72387.56
PSZ-AC_5:9_HEATC | 141351.26
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 130774.26 | 114.0571 | 836.0473 | 0 | 0.0005 | 5043300.8128 | 47811.9388
February | 101321.6062 | 87.8237 | 745.3983 | 0 | 0.0004 | 4496951.7201 | 37341.7591
March | 120402.5603 | 104.4849 | 863.9231 | 0 | 0.0004 | 5211913.6448 | 44307.3239
April | 103681.8013 | 89.6299 | 805.6361 | 0 | 0.0004 | 4860544.1311 | 38342.4096
May | 111475.4182 | 96.0754 | 918.4029 | 0 | 0.0004 | 5541095.1695 | 41383.8408
June | 110485.1484 | 95.2298 | 908.8392 | 0 | 0.0004 | 5483387.8614 | 41011.9281
July | 96343.6441 | 83.4147 | 725.6282 | 0 | 0.0004 | 4377750.7149 | 35558.5602
August | 107630.1646 | 93.2144 | 805.6619 | 0 | 0.0004 | 4860577.4941 | 39709.0236
September | 106101.2483 | 91.3147 | 897.1995 | 0 | 0.0004 | 5413252.9648 | 39459.1405
October | 108580.1339 | 93.5635 | 897.5216 | 0 | 0.0004 | 5415121.0654 | 40318.07
November | 111139.9072 | 96.1826 | 844.7334 | 0 | 0.0004 | 5096349.8268 | 41042.957
December | 121561.0809 | 105.8789 | 802.6963 | 0 | 0.0004 | 4842241.0197 | 44521.4894
Annual Sum or Average | 1329496.9734 | 1150.8697 | 10051.6879 | 0 | 0.005 | 60642500 | 490808.441
Minimum of Months | 96343.6441 | 83.4147 | 725.6282 | 0 | 0.0004 | 4377750.7149 | 35558.5602
Maximum of Months | 130774.26 | 114.0571 | 918.4029 | 0 | 0.0005 | 5541095.1695 | 47811.9388
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1034070000000 | 880466.568 | 05-JAN-11:50 | 218037.744 | 160954.2 | 320688.385 | 0 | 157160.738 | 0 | 17083.872 | 0 | 0 | 0 | 0 | 0 | 6541.629 | 0 | 0
February | 922044000000 | 995920.316 | 15-FEB-16:10 | 218037.744 | 146554.272 | 320688.385 | 0 | 288518.144 | 0 | 16831.018 | 0 | 0 | 0 | 0 | 0 | 5290.753 | 0 | 0
March | 1068640000000 | 903523.572 | 01-MAR-12:00 | 218037.744 | 160954.2 | 320688.385 | 0 | 181689.841 | 0 | 16855.775 | 0 | 0 | 0 | 0 | 0 | 5297.626 | 0 | 0
April | 996594000000 | 993888.232 | 13-APR-15:09 | 218037.744 | 146554.272 | 320688.385 | 0 | 286530.6 | 0 | 16806.536 | 0 | 0 | 0 | 0 | 0 | 5270.694 | 0 | 0
May | 1136130000000 | 1057211.025 | 17-MAY-13:00 | 218037.744 | 151354.248 | 320688.385 | 0 | 345031.131 | 0 | 16806.536 | 0 | 0 | 0 | 0 | 0 | 5292.981 | 0 | 0
June | 1124300000000 | 1085016.175 | 15-JUN-12:00 | 218037.744 | 151354.248 | 320688.385 | 0 | 372836.136 | 0 | 16806.536 | 0 | 0 | 0 | 0 | 0 | 5293.125 | 0 | 0
July | 897603000000 | 1000587.566 | 03-JUL-12:00 | 121132.08 | 86203.896 | 320688.385 | 0 | 450714.93 | 0 | 16810.276 | 0 | 0 | 0 | 0 | 0 | 5037.999 | 0 | 0
August | 996601000000 | 979445.116 | 15-AUG-11:00 | 121132.08 | 95803.848 | 320688.385 | 0 | 419868.3 | 0 | 16910.226 | 0 | 0 | 0 | 0 | 0 | 5042.277 | 0 | 0
September | 1109920000000 | 1291450.388 | 28-SEP-15:09 | 218037.744 | 146475.648 | 320688.385 | 0 | 584160.039 | 0 | 16806.536 | 0 | 0 | 0 | 0 | 0 | 5282.036 | 0 | 0
October | 1110300000000 | 1054500.251 | 31-OCT-12:00 | 218037.744 | 159932.088 | 320688.385 | 0 | 333726.796 | 0 | 16816.269 | 0 | 0 | 0 | 0 | 0 | 5298.969 | 0 | 0
November | 1044940000000 | 928184.527 | 16-NOV-15:00 | 218037.744 | 145532.16 | 320688.385 | 0 | 221697.414 | 0 | 16929.105 | 0 | 0 | 0 | 0 | 0 | 5299.719 | 0 | 0
December | 992841000000 | 881732.792 | 14-DEC-16:49 | 218037.744 | 146475.648 | 320688.385 | 0 | 150258.06 | 23884.224 | 17093.429 | 0 | 0 | 0 | 0 | 0 | 5295.302 | 0 | 0
Annual Sum or Average | 12434000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 897603000000 | 880466.568 |  | 121132.08 | 86203.896 | 320688.385 | 0 | 150258.06 | 0 | 16806.536 | 0 | 0 | 0 | 0 | 0 | 5037.999 | 0 | 0
Maximum of Months | 1136130000000 | 1291450.388 |  | 218037.744 | 160954.2 | 320688.385 | 0 | 584160.039 | 23884.224 | 17093.429 | 0 | 0 | 0 | 0 | 0 | 6541.629 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 532708.58 | 41279.61 | 0 | 573988.2
Cost per Total Building Area ($/m2) | 27.19 | 2.11 | 0 | 29.3
Cost per Net Conditioned Building Area ($/m2) | 27.19 | 2.11 | 0 | 29.3
08-Baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 20125.51 | 1027.23 | 1027.23
Net Site Energy | 20125.51 | 1027.23 | 1027.23
Total Source Energy | 53985.27 | 2755.48 | 2755.48
Net Source Energy | 53985.27 | 2755.48 | 2755.48
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 6580.96 | 0 | 0 | 0 | 0
Cooling | 2885.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.16 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3394.9 | 0 | 0 | 0 | 0 | 0
Pumps | 231.4 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 114.34 | 0 | 0 | 0 | 815.28
Refrigeration | 166.32 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12885.76 | 7239.75 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12885.76 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12885.76 | 100
Total On-Site and Utility Electric Sources | 12885.76 | 100
Total Electricity End Uses | 12885.76 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1536742.07 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7345822.37 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 592999.7 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 257703.59 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 307843.52 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 114213.9 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 139821.43 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 24.18 | 57310.15 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 24 | 56891.78 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 26.3 | 62329.31 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 33.87 | 80286.08 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 23.88 | 45282.69 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 15.57 | 29520.62 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 12.4 | 23507.57 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.6 | 8721.61 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.63 | 10677.05 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00171 | 78612.76 | 2783.23
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002209 | 101546.91 | 3595.2
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005047 | 232083.02 | 8216.74
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006885 | 316571.74 | 11208.01
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001417 | 65137.58 | 2306.15
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002599 | 119518.58 | 4231.48
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001571 | 72220.71 | 2556.93
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002097 | 96404.1 | 3413.12
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00367 | 168767.78 | 5975.11
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005713 | 262692.72 | 9300.46
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00169 | 77684.69 | 2750.37
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.0022 | 101142.8 | 3580.89
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004924 | 226419.28 | 8016.22
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006811 | 313185.39 | 11088.12
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001401 | 64436.15 | 2281.32
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002591 | 119111.57 | 4217.07
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001571 | 72225.94 | 2557.11
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002098 | 96470.76 | 3415.48
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003672 | 168831.18 | 5977.35
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00572 | 262999.05 | 9311.31
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001691 | 77745.87 | 2752.54
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002208 | 101541 | 3594.99
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004961 | 228085.45 | 8075.21
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008284 | 380886.37 | 13485.03
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001424 | 65457.24 | 2317.47
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002665 | 122558.74 | 4339.11
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00159 | 73127.84 | 2589.04
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002113 | 97145.72 | 3439.38
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003837 | 176404.72 | 6245.49
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007028 | 323158.46 | 11441.21
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005187 | 238500.6 | 8443.95
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00961 | 441865.03 | 15643.93
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001432 | 65851.64 | 2331.43
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002166 | 99571.67 | 3525.27
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001299 | 59714.4 | 2114.15
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002119 | 97423.85 | 3449.23
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004805 | 220924.99 | 7821.7
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00675 | 310376.41 | 10988.67
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009143 | 420411.42 | 14884.38
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001262 | 58043.67 | 2055
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002342 | 107664.37 | 3811.78
VAV_POD_1_HEATC | 0.003311 | 152247.36 | 2304.3
VAV_POD_2_HEATC | 0.003317 | 152521.23 | 2305.37
VAV_POD_3_HEATC | 0.00324 | 148961.6 | 2288.46
VAV_OTHER_HEATC | 0.002383 | 109569.99 | 1770.56
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.013146 | 24.18 | 21.82 | 12.8 | 7.22 | 0.009857 | 0.0085
VAV_POD_2_COOLC | 0.013096 | 24 | 21.84 | 12.8 | 7.22 | 0.009867 | 0.0085
VAV_POD_3_COOLC | 0.013802 | 26.3 | 21.59 | 12.8 | 7.22 | 0.00978 | 0.0085
VAV_OTHER_COOLC | 0.015074 | 33.87 | 20.75 | 12.8 | 7.22 | 0.009384 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 439692.43
PSZ-AC_2:6_HEATC | 250972.43
PSZ-AC_3:7_HEATC | 228257.22
PSZ-AC_4:8_HEATC | 84686.36
PSZ-AC_5:9_HEATC | 103673.62
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 280466.536 | 450.8987 | 1085.1688 | 0 | 0.0046 | 67460.1622 | 115020.8409
February | 229344.6211 | 381.2967 | 956.8606 | 0 | 0.004 | 59489.5585 | 95206.2295
March | 214094.685 | 382.4892 | 1039.8125 | 0 | 0.0043 | 64658.0605 | 91302.9435
April | 170671.9435 | 324.1308 | 935.0318 | 0 | 0.0038 | 58149.5393 | 74542.1092
May | 190436.9387 | 372.8699 | 1105.1704 | 0 | 0.0045 | 68734.0553 | 84198.9275
June | 223250.6943 | 442.9797 | 1327.9641 | 0 | 0.0054 | 82592.0904 | 99243.0062
July | 194746.5738 | 385.6627 | 1154.2248 | 0 | 0.0047 | 71786.2298 | 86502.5402
August | 210268.247 | 415.9223 | 1243.577 | 0 | 0.005 | 77343.2843 | 93353.2102
September | 188169.0188 | 371.5844 | 1109.4296 | 0 | 0.0045 | 68999.912 | 83484.6871
October | 190370.5804 | 364.6791 | 1060.2763 | 0 | 0.0043 | 65939.4936 | 83432.5195
November | 202662.0427 | 367.4627 | 1014.0944 | 0 | 0.0042 | 63060.8086 | 86920.9887
December | 248804.7133 | 413.3667 | 1036.4869 | 0 | 0.0043 | 64439.9305 | 103258.6583
Annual Sum or Average | 2543286.5944 | 4673.3429 | 13068.0974 | 0 | 0.0534 | 812653.1248 | 1096466.6606
Minimum of Months | 170671.9435 | 324.1308 | 935.0318 | 0 | 0.0038 | 58149.5393 | 74542.1092
Maximum of Months | 280466.536 | 450.8987 | 1327.9641 | 0 | 0.0054 | 82592.0904 | 115020.8409
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1069680000000 | 763202.776 | 09-JAN-11:39 | 218037.744 | 160954.2 | 225237.983 | 0 | 136953.396 | 0 | 14250.5 | 0 | 0 | 0 | 0 | 0 | 7768.954 | 0 | 0
February | 943290000000 | 757327.412 | 15-FEB-12:00 | 218037.744 | 160954.2 | 225237.983 | 0 | 133624.941 | 0 | 14195.261 | 0 | 0 | 0 | 0 | 0 | 5277.284 | 0 | 0
March | 1025240000000 | 974552.864 | 09-MAR-16:10 | 218037.744 | 146554.272 | 225237.983 | 0 | 365299.487 | 0 | 14128.601 | 0 | 0 | 0 | 0 | 0 | 5294.778 | 0 | 0
April | 922043000000 | 957357.881 | 04-APR-15:00 | 218037.744 | 146554.272 | 225237.983 | 0 | 348117.621 | 0 | 14119.334 | 0 | 0 | 0 | 0 | 0 | 5290.927 | 0 | 0
May | 1089870000000 | 1236767.041 | 31-MAY-15:00 | 218037.744 | 146554.272 | 225237.983 | 0 | 627506.905 | 0 | 14119.334 | 0 | 0 | 0 | 0 | 0 | 5310.802 | 0 | 0
June | 1309610000000 | 1490753.232 | 30-JUN-15:00 | 218037.744 | 146554.272 | 225859.43 | 0 | 880872.385 | 0 | 14119.334 | 0 | 0 | 0 | 0 | 0 | 5310.067 | 0 | 0
July | 1138270000000 | 1383243.458 | 25-JUL-11:00 | 121132.08 | 95803.848 | 225237.983 | 0 | 921889.514 | 0 | 14119.334 | 0 | 0 | 0 | 0 | 0 | 5060.699 | 0 | 0
August | 1226390000000 | 1364562.029 | 17-AUG-11:00 | 121132.08 | 95803.848 | 225237.983 | 0 | 903207.769 | 0 | 14119.334 | 0 | 0 | 0 | 0 | 0 | 5061.015 | 0 | 0
September | 1094090000000 | 1170493.35 | 08-SEP-15:09 | 218037.744 | 146475.648 | 225692.038 | 0 | 560879.677 | 0 | 14119.334 | 0 | 0 | 0 | 0 | 0 | 5288.909 | 0 | 0
October | 1045560000000 | 1088568.483 | 03-OCT-10:39 | 218037.744 | 159932.088 | 225237.983 | 0 | 463468.474 | 0 | 14123.605 | 0 | 0 | 0 | 0 | 0 | 7768.589 | 0 | 0
November | 999918000000 | 958904.221 | 03-NOV-11:00 | 218037.744 | 159932.088 | 225237.983 | 0 | 336257.572 | 0 | 14135.246 | 0 | 0 | 0 | 0 | 0 | 5303.588 | 0 | 0
December | 1021790000000 | 727079.474 | 08-DEC-10:00 | 218037.744 | 159932.088 | 225237.983 | 0 | 104361.526 | 0 | 14233.407 | 0 | 0 | 0 | 0 | 0 | 5276.727 | 0 | 0
Annual Sum or Average | 12885800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 922043000000 | 727079.474 |  | 121132.08 | 95803.848 | 225237.983 | 0 | 104361.526 | 0 | 14119.334 | 0 | 0 | 0 | 0 | 0 | 5060.699 | 0 | 0
Maximum of Months | 1309610000000 | 1490753.232 |  | 218037.744 | 160954.2 | 225859.43 | 0 | 921889.514 | 0 | 14250.5 | 0 | 0 | 0 | 0 | 0 | 7768.954 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 272540.05 | 70244.7 | 0 | 342784.75
Cost per Total Building Area ($/m2) | 13.91 | 3.59 | 0 | 17.5
Cost per Net Conditioned Building Area ($/m2) | 13.91 | 3.59 | 0 | 17.5
09-Albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 17252.31 | 880.58 | 880.58
Net Site Energy | 17252.31 | 880.58 | 880.58
Total Source Energy | 47631.53 | 2431.17 | 2431.17
Net Source Energy | 47631.53 | 2431.17 | 2431.17
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3661.86 | 0 | 0 | 0 | 0
Cooling | 2421.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3872.43 | 0 | 0 | 0 | 0 | 0
Pumps | 266.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 111.59 | 0 | 0 | 0 | 815.28
Refrigeration | 165.75 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12934.41 | 4317.9 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12934.41 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12934.41 | 100
Total On-Site and Utility Electric Sources | 12934.41 | 100
Total Electricity End Uses | 12934.41 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2326123.72 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 6891104.6 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 466059.69 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 299217.72 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 244344.75 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 90103.68 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 110872.04 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 27.9 | 66130.65 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 27.71 | 65683.08 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 30.49 | 72264.13 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 39.16 | 92815.86 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 28.15 | 53388.35 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 18.08 | 34276.17 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.76 | 27990.33 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.44 | 10321.61 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 6.7 | 12700.68 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001626 | 74776.55 | 2647.41
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002135 | 98187.01 | 3476.25
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004521 | 207882.87 | 7359.95
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006287 | 289066.61 | 10234.21
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001334 | 61324.3 | 2171.15
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002526 | 116161.76 | 4112.63
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001571 | 72244.49 | 2557.77
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002113 | 97144.38 | 3439.33
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003604 | 165692.34 | 5866.23
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005695 | 261853.84 | 9270.76
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001606 | 73832.81 | 2614
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002126 | 97770.02 | 3461.48
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004416 | 203061.69 | 7189.26
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006222 | 286071.53 | 10128.17
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00132 | 60681.51 | 2148.39
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002519 | 115824.87 | 4100.7
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001571 | 72248.94 | 2557.93
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002114 | 97211.2 | 3441.7
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003603 | 165687.83 | 5866.07
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005702 | 262168.76 | 9281.91
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001607 | 73895.05 | 2616.2
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002135 | 98177.41 | 3475.91
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004453 | 204739.11 | 7248.65
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007692 | 353666.05 | 12521.31
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001342 | 61716.32 | 2185.03
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002595 | 119318.21 | 4224.38
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001591 | 73163.66 | 2590.31
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002129 | 97883.65 | 3465.5
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003767 | 173198.77 | 6131.99
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007015 | 322535.03 | 11419.14
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004947 | 227483.63 | 8053.91
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009389 | 431722.88 | 15284.86
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001269 | 58353.59 | 2065.97
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001978 | 90946.5 | 3219.9
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001265 | 58186.98 | 2060.07
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002105 | 96783.97 | 3426.57
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004381 | 201446.56 | 7132.08
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006271 | 288351.1 | 10208.88
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009019 | 414682.15 | 14681.54
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00119 | 54709.58 | 1936.96
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002272 | 104488.83 | 3699.36
VAV_POD_1_HEATC | 0.002421 | 111321.42 | 1746.42
VAV_POD_2_HEATC | 0.002426 | 111563.72 | 1748.25
VAV_POD_3_HEATC | 0.002349 | 108000.62 | 1718.91
VAV_OTHER_HEATC | 0.00165 | 75876.48 | 1237.29
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.018847 | 27.9 | 21.6 | 12.8 | 7.22 | 0.00796 | 0.00398
VAV_POD_2_COOLC | 0.018731 | 27.71 | 21.61 | 12.8 | 7.22 | 0.007957 | 0.003978
VAV_POD_3_COOLC | 0.02045 | 30.49 | 21.37 | 12.8 | 7.22 | 0.008038 | 0.004019
VAV_OTHER_COOLC | 0.025403 | 39.16 | 20.63 | 12.8 | 7.22 | 0.008142 | 0.004071
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 411895.64
PSZ-AC_2:6_HEATC | 214326.53
PSZ-AC_3:7_HEATC | 215947.74
PSZ-AC_4:8_HEATC | 79632.1
PSZ-AC_5:9_HEATC | 97986.82
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 328756.9237 | 534.8641 | 1281.1845 | 0 | 0.0051 | 1331969.3197 | 136976.4055
February | 272995.4203 | 451.5048 | 1103.7187 | 0 | 0.0044 | 1147523.699 | 114465.4124
March | 300186.8758 | 504.575 | 1257.4865 | 0 | 0.005 | 1307452.424 | 126661.0068
April | 265875.6194 | 457.5876 | 1171.5909 | 0 | 0.0046 | 1218217.6729 | 113231.8192
May | 326984.8001 | 570.2452 | 1481.3836 | 0 | 0.0058 | 1540388.7339 | 139991.364
June | 343085.0952 | 599.4656 | 1560.5075 | 0 | 0.0061 | 1622671.5131 | 146996.3962
July | 291188.4089 | 508.3986 | 1322.3527 | 0 | 0.0052 | 1375027.1246 | 124722.872
August | 300427.8642 | 523.7874 | 1360.2906 | 0 | 0.0053 | 1414471.495 | 128607.4853
September | 307802.7104 | 537.2052 | 1396.7138 | 0 | 0.0054 | 1452349.0182 | 131819.448
October | 289387.8018 | 498.3382 | 1276.7393 | 0 | 0.005 | 1327552.6742 | 123273.1798
November | 291239.892 | 488.2376 | 1212.9783 | 0 | 0.0048 | 1261166.7136 | 122758.5239
December | 326889.5698 | 530.3006 | 1265.6509 | 0 | 0.005 | 1315808.6623 | 136048.745
Annual Sum or Average | 3644820.9817 | 6204.51 | 15690.5974 | 0 | 0.0616 | 16314600 | 1545552.6583
Minimum of Months | 265875.6194 | 451.5048 | 1103.7187 | 0 | 0.0044 | 1147523.699 | 113231.8192
Maximum of Months | 343085.0952 | 599.4656 | 1560.5075 | 0 | 0.0061 | 1622671.5131 | 146996.3962
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1056000000000 | 814910.799 | 25-JAN-14:00 | 218037.744 | 151354.248 | 263147.085 | 0 | 155728.982 | 0 | 21376.609 | 0 | 0 | 0 | 0 | 0 | 5266.131 | 0 | 0
February | 909771000000 | 916999.418 | 14-FEB-16:10 | 218037.744 | 146554.272 | 263072.824 | 0 | 262721.755 | 0 | 21359.811 | 0 | 0 | 0 | 0 | 0 | 5253.012 | 0 | 0
March | 1036560000000 | 921433.553 | 02-MAR-16:10 | 218037.744 | 146554.272 | 263076.241 | 0 | 267161.322 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 5251.049 | 0 | 0
April | 965818000000 | 1008279.238 | 21-APR-15:00 | 218037.744 | 146554.272 | 263367.354 | 0 | 354058.243 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 4908.7 | 0 | 0
May | 1221240000000 | 1104704.695 | 31-MAY-15:00 | 218037.744 | 146554.272 | 263525.19 | 0 | 450294.432 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 4940.133 | 0 | 0
June | 1286470000000 | 1202079.733 | 29-JUN-15:09 | 218037.744 | 146554.272 | 264703.804 | 0 | 546465.614 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 4965.375 | 0 | 0
July | 1090140000000 | 1028551.66 | 31-JUL-14:00 | 121132.08 | 81403.92 | 263644.11 | 0 | 536017.508 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 5001.118 | 0 | 0
August | 1121410000000 | 1023179.661 | 01-AUG-13:00 | 121132.08 | 86203.896 | 262981.671 | 0 | 526475.338 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 5033.751 | 0 | 0
September | 1151440000000 | 1069906.507 | 20-SEP-15:09 | 218037.744 | 146475.648 | 264389.586 | 0 | 414508.118 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 5142.486 | 0 | 0
October | 1052500000000 | 992601.077 | 11-OCT-15:00 | 218037.744 | 146475.648 | 263475.202 | 0 | 337986.989 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 5272.57 | 0 | 0
November | 999868000000 | 897288.68 | 08-NOV-16:10 | 218037.744 | 146475.648 | 262981.27 | 0 | 243171.384 | 0 | 21360.697 | 0 | 0 | 0 | 0 | 0 | 5261.938 | 0 | 0
December | 1043190000000 | 789314.356 | 08-DEC-14:00 | 218037.744 | 150332.136 | 262974.501 | 0 | 131418.953 | 0 | 21378.923 | 0 | 0 | 0 | 0 | 0 | 5172.099 | 0 | 0
Annual Sum or Average | 12934400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 909771000000 | 789314.356 |  | 121132.08 | 81403.92 | 262974.501 | 0 | 131418.953 | 0 | 21352.925 | 0 | 0 | 0 | 0 | 0 | 4908.7 | 0 | 0
Maximum of Months | 1286470000000 | 1202079.733 |  | 218037.744 | 151354.248 | 264703.804 | 0 | 546465.614 | 0 | 21378.923 | 0 | 0 | 0 | 0 | 0 | 5272.57 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 132870.02 | 29865 | 0 | 162735.03
Cost per Total Building Area ($/m2) | 6.78 | 1.52 | 0 | 8.31
Cost per Net Conditioned Building Area ($/m2) | 6.78 | 1.52 | 0 | 8.31
10-Seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 16772.44 | 856.09 | 856.09
Net Site Energy | 16772.44 | 856.09 | 856.09
Total Source Energy | 25022.07 | 1277.16 | 1277.16
Net Source Energy | 25022.07 | 1277.16 | 1277.16
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 5790.73 | 0 | 0 | 0 | 0
Cooling | 861.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3003.19 | 0 | 0 | 0 | 0 | 0
Pumps | 79.61 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 119.47 | 0 | 0 | 0 | 815.28
Refrigeration | 167.01 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10317.79 | 6454.65 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 10317.79 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 10317.79 | 100
Total On-Site and Utility Electric Sources | 10317.79 | 100
Total Electricity End Uses | 10317.79 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1036549.86 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 6792239.21 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 415377.2 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 234241.71 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 176340.75 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75615.94 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 84808.62 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 23.21 | 55022.18 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 22.97 | 54455.09 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 25.44 | 60309.75 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 31.07 | 73650.95 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 21.96 | 41638.68 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.15 | 26833 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 10.65 | 20200.29 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.57 | 8662 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.12 | 9715.05 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001842 | 84674.56 | 2997.85
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002263 | 104045.44 | 3683.66
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005834 | 268233.05 | 9496.61
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007364 | 338582.95 | 11987.3
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001387 | 63762.92 | 2257.48
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002278 | 104746.36 | 3708.47
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001353 | 62214.13 | 2202.65
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001766 | 81214.14 | 2875.33
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002882 | 132514.13 | 4691.57
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004355 | 200254.55 | 7089.88
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001821 | 83752.14 | 2965.19
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002254 | 103635.38 | 3669.14
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005665 | 260474.1 | 9221.91
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007264 | 334016.26 | 11825.62
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001367 | 62860.34 | 2225.53
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002264 | 104106.86 | 3685.83
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001353 | 62213.15 | 2202.61
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001768 | 81273.74 | 2877.44
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002881 | 132485.61 | 4690.56
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004362 | 200580.74 | 7101.43
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001823 | 83811.66 | 2967.3
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002263 | 104035.11 | 3683.29
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005702 | 262186.41 | 9282.53
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008745 | 402098.47 | 14236.03
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001387 | 63784.63 | 2258.25
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002338 | 107482.63 | 3805.35
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001373 | 63125.18 | 2234.9
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001782 | 81956.32 | 2901.61
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003041 | 139813.57 | 4950.01
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00588 | 270353.79 | 9571.69
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004586 | 210870.36 | 7465.72
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008005 | 368059.71 | 13030.91
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001643 | 75532.87 | 2674.19
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002234 | 102733.44 | 3637.21
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.000989 | 45468.96 | 1609.8
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001573 | 72349.5 | 2561.49
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005204 | 239267.39 | 8471.1
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006772 | 311376.35 | 11024.07
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007684 | 353317.75 | 12508.98
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001248 | 57362.27 | 2030.87
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001991 | 91523.93 | 3240.34
VAV_POD_1_HEATC | 0.002483 | 114173.67 | 1784.88
VAV_POD_2_HEATC | 0.002491 | 114541.65 | 1787.54
VAV_POD_3_HEATC | 0.002408 | 110742.53 | 1757.43
VAV_OTHER_HEATC | 0.001754 | 80630.48 | 1311.04
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.008715 | 23.21 | 21.11 | 12.8 | 7.22 | 0.008633 | 0.0085
VAV_POD_2_COOLC | 0.008649 | 22.97 | 21.13 | 12.8 | 7.22 | 0.008635 | 0.0085
VAV_POD_3_COOLC | 0.009402 | 25.44 | 20.92 | 12.8 | 7.22 | 0.008653 | 0.0085
VAV_OTHER_COOLC | 0.010412 | 31.07 | 20.3 | 12.8 | 7.22 | 0.008587 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 349650.67
PSZ-AC_2:6_HEATC | 210081.75
PSZ-AC_3:7_HEATC | 169627.04
PSZ-AC_4:8_HEATC | 72737.06
PSZ-AC_5:9_HEATC | 81579.76
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 105203.4431 | 125.7098 | 193.3558 | 0 | 0.0009 | 2551647.7869 | 39647.0689
February | 76802.7125 | 95.7693 | 166.6722 | 0 | 0.0007 | 2200458.8372 | 29371.9346
March | 85002.9207 | 107.4209 | 193.5743 | 0 | 0.0008 | 2555914.3625 | 32660.7251
April | 62964.2602 | 84.1484 | 172.6192 | 0 | 0.0007 | 2280101.625 | 24683.1565
May | 56194.1915 | 81.7764 | 196.6828 | 0 | 0.0008 | 2599011.7559 | 22744.151
June | 52517.7295 | 79.2984 | 202.1537 | 0 | 0.0008 | 2671663.273 | 21563.7527
July | 44133.2678 | 65.6346 | 163.4706 | 0 | 0.0007 | 2160313.0776 | 18013.5853
August | 48913.0404 | 72.0507 | 176.7542 | 0 | 0.0007 | 2335779.4135 | 19890.3592
September | 52863.1224 | 78.3712 | 194.2332 | 0 | 0.0008 | 2566822.3114 | 21550.4085
October | 61737.8656 | 85.3418 | 187.3417 | 0 | 0.0008 | 2475017.2425 | 24505.7443
November | 84698.1362 | 105.4656 | 182.8553 | 0 | 0.0008 | 2414082.8437 | 32375.456
December | 101129.7443 | 121.0579 | 187.2469 | 0 | 0.0009 | 2471081.2425 | 38134.9693
Annual Sum or Average | 832160.4342 | 1102.0449 | 2216.9598 | 0 | 0.0093 | 29281900 | 325141.3115
Minimum of Months | 44133.2678 | 65.6346 | 163.4706 | 0 | 0.0007 | 2160313.0776 | 18013.5853
Maximum of Months | 105203.4431 | 125.7098 | 202.1537 | 0 | 0.0009 | 2671663.273 | 39647.0689
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 899101000000 | 638358.184 | 27-JAN-12:00 | 218037.744 | 160954.2 | 208983.757 | 0 | 35583.415 | 0 | 9659.377 | 0 | 0 | 0 | 0 | 0 | 5139.692 | 0 | 0
February | 775355000000 | 698421.398 | 22-FEB-11:39 | 218037.744 | 160954.2 | 208983.757 | 0 | 93086.349 | 0 | 9590.298 | 0 | 0 | 0 | 0 | 0 | 7769.05 | 0 | 0
March | 900604000000 | 755544.25 | 29-MAR-15:00 | 218037.744 | 146554.272 | 208983.757 | 0 | 167164.821 | 0 | 9535.765 | 0 | 0 | 0 | 0 | 0 | 5267.891 | 0 | 0
April | 803418000000 | 705941.92 | 14-APR-13:00 | 218037.744 | 151354.248 | 208983.757 | 0 | 112745.321 | 0 | 9545.026 | 0 | 0 | 0 | 0 | 0 | 5275.824 | 0 | 0
May | 915790000000 | 897058.017 | 05-MAY-15:00 | 218037.744 | 146554.272 | 209043.672 | 0 | 308594.363 | 0 | 9535.765 | 0 | 0 | 0 | 0 | 0 | 5292.201 | 0 | 0
June | 941389000000 | 899657.557 | 28-JUN-15:09 | 218037.744 | 146554.272 | 209404.591 | 0 | 310838.182 | 0 | 9535.765 | 0 | 0 | 0 | 0 | 0 | 5287.003 | 0 | 0
July | 761210000000 | 818231.253 | 24-JUL-14:00 | 121132.08 | 81403.92 | 209088.99 | 0 | 392035.232 | 0 | 9535.765 | 0 | 0 | 0 | 0 | 0 | 5035.266 | 0 | 0
August | 823037000000 | 757343.979 | 07-AUG-14:00 | 121132.08 | 81403.92 | 208983.757 | 0 | 331252.79 | 0 | 9535.765 | 0 | 0 | 0 | 0 | 0 | 5035.667 | 0 | 0
September | 904448000000 | 941113.553 | 13-SEP-15:00 | 218037.744 | 146475.648 | 209076.237 | 0 | 352699.635 | 0 | 9535.765 | 0 | 0 | 0 | 0 | 0 | 5288.524 | 0 | 0
October | 872099000000 | 778229.895 | 17-OCT-15:00 | 218037.744 | 146475.648 | 208983.757 | 0 | 189922.224 | 0 | 9536.908 | 0 | 0 | 0 | 0 | 0 | 5273.615 | 0 | 0
November | 850628000000 | 717384.832 | 03-NOV-11:39 | 218037.744 | 159932.088 | 208983.757 | 0 | 113072.35 | 0 | 9589.951 | 0 | 0 | 0 | 0 | 0 | 7768.942 | 0 | 0
December | 870712000000 | 621042.167 | 13-DEC-11:39 | 218037.744 | 159932.088 | 208983.757 | 0 | 16414.384 | 0 | 9905.137 | 0 | 0 | 0 | 0 | 0 | 7769.057 | 0 | 0
Annual Sum or Average | 10317800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 761210000000 | 621042.167 |  | 121132.08 | 81403.92 | 208983.757 | 0 | 16414.384 | 0 | 9535.765 | 0 | 0 | 0 | 0 | 0 | 5035.266 | 0 | 0
Maximum of Months | 941389000000 | 941113.553 |  | 218037.744 | 160954.2 | 209404.591 | 0 | 392035.232 | 0 | 9905.137 | 0 | 0 | 0 | 0 | 0 | 7769.057 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 205937.89 | 54315.78 | 0 | 260253.68
Cost per Total Building Area ($/m2) | 10.51 | 2.77 | 0 | 13.28
Cost per Net Conditioned Building Area ($/m2) | 10.51 | 2.77 | 0 | 13.28
11-Chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 22474.15 | 1147.11 | 1147.11
Net Site Energy | 22474.15 | 1147.11 | 1147.11
Total Source Energy | 54204.41 | 2766.66 | 2766.66
Net Source Energy | 54204.41 | 2766.66 | 2766.66
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 9715.71 | 0 | 0 | 0 | 0
Cooling | 2079.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3478.22 | 0 | 0 | 0 | 0 | 0
Pumps | 156.31 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 126.51 | 0 | 0 | 0 | 815.28
Refrigeration | 165.88 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12087.47 | 10386.68 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12087.47 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12087.47 | 100
Total On-Site and Utility Electric Sources | 12087.47 | 100
Total Electricity End Uses | 12087.47 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1503213.51 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7251446.38 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 592681.81 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 263256.37 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 293812.26 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 115120.75 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 138324.99 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 23.49 | 55679.59 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 23.3 | 55234.14 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 25.63 | 60762.93 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 32.85 | 77871.71 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 23.87 | 45258.41 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 15.26 | 28927.74 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 11.83 | 22436.12 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.64 | 8790.86 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.57 | 10562.78 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001637 | 75266.39 | 2664.76
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002111 | 97058.26 | 3436.28
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004931 | 226735.14 | 8027.41
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006694 | 307782.38 | 10896.83
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001363 | 62651.32 | 2218.13
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002484 | 114233.38 | 4044.36
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00146 | 67125.99 | 2376.55
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001958 | 90040.89 | 3187.84
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003436 | 157965.02 | 5592.65
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005369 | 246847.44 | 8739.47
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001617 | 74349.12 | 2632.28
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002102 | 96651.06 | 3421.87
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004798 | 220609.06 | 7810.52
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006616 | 304195.56 | 10769.84
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001347 | 61935 | 2192.77
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002475 | 113816.5 | 4029.6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00146 | 67130.51 | 2376.71
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00196 | 90105.96 | 3190.14
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003441 | 158200.95 | 5601
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005375 | 247146.39 | 8750.05
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001618 | 74411.51 | 2634.49
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002111 | 97053.11 | 3436.1
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004834 | 222277.96 | 7869.6
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008089 | 371923.15 | 13167.69
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001368 | 62922.64 | 2227.73
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00255 | 117237.13 | 4150.7
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00148 | 68046.1 | 2409.13
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001974 | 90782.87 | 3214.11
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003603 | 165688 | 5866.07
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006684 | 307351.44 | 10881.57
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004853 | 223130.19 | 7899.77
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.009049 | 416079.84 | 14731.03
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001397 | 64213.39 | 2273.43
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002098 | 96462.09 | 3415.18
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001183 | 54394.69 | 1925.81
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001952 | 89763.74 | 3178.03
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004667 | 214581.77 | 7597.12
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006528 | 300165.75 | 10627.17
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008727 | 401253.18 | 14206.1
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001254 | 57672.67 | 2041.86
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002266 | 104201.57 | 3689.19
VAV_POD_1_HEATC | 0.004496 | 206705.23 | 2955.17
VAV_POD_2_HEATC | 0.004502 | 206991.87 | 2954.28
VAV_POD_3_HEATC | 0.004424 | 203434.03 | 2961.04
VAV_OTHER_HEATC | 0.003368 | 154856.14 | 2431.33
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.01288 | 23.49 | 21.71 | 12.8 | 7.22 | 0.010029 | 0.0085
VAV_POD_2_COOLC | 0.012825 | 23.3 | 21.73 | 12.8 | 7.22 | 0.010041 | 0.0085
VAV_POD_3_COOLC | 0.013531 | 25.63 | 21.47 | 12.8 | 7.22 | 0.009935 | 0.0085
VAV_OTHER_COOLC | 0.01468 | 32.85 | 20.68 | 12.8 | 7.22 | 0.009499 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 513376.15
PSZ-AC_2:6_HEATC | 287159.17
PSZ-AC_3:7_HEATC | 254497.79
PSZ-AC_4:8_HEATC | 99716.65
PSZ-AC_5:9_HEATC | 119815.98
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 492146.3719 | 771.8179 | 1950.8983 | 0 | 0.0062 | 448957.6297 | 201415.135
February | 408646.0053 | 655.8388 | 1709.6509 | 0 | 0.0054 | 393466.5107 | 168673.3742
March | 411636.3835 | 684.0042 | 1862.2354 | 0 | 0.0058 | 428622.6687 | 172141.7388
April | 311238.2992 | 546.7542 | 1585.3518 | 0 | 0.0048 | 364940.031 | 132984.4061
May | 365112.7276 | 657.4879 | 1956.2398 | 0 | 0.0059 | 450339.0405 | 157542.1972
June | 428300.2448 | 776.9354 | 2328.7263 | 0 | 0.007 | 536095.3295 | 185348.1395
July | 362797.6959 | 657.6096 | 1969.5568 | 0 | 0.0059 | 453410.384 | 156953.5084
August | 367097.0332 | 663.8738 | 1983.7324 | 0 | 0.006 | 456671.7409 | 158667.3194
September | 360427.0698 | 651.5422 | 1946.0743 | 0 | 0.0059 | 448002.1625 | 155758.662
October | 338368.7423 | 600.2995 | 1758.8251 | 0 | 0.0053 | 404880.9237 | 145139.2435
November | 371019.0438 | 623.3347 | 1719.3863 | 0 | 0.0053 | 395754.4297 | 155808.3877
December | 454643.636 | 722.6133 | 1859.8432 | 0 | 0.0058 | 428020.4742 | 186985.6154
Annual Sum or Average | 4671433.2533 | 8012.1115 | 22630.5207 | 0 | 0.0693 | 5209161.3252 | 1977417.7271
Minimum of Months | 311238.2992 | 546.7542 | 1585.3518 | 0 | 0.0048 | 364940.031 | 132984.4061
Maximum of Months | 492146.3719 | 776.9354 | 2328.7263 | 0 | 0.007 | 536095.3295 | 201415.135
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1041770000000 | 657805.354 | 17-JAN-12:00 | 218037.744 | 160954.2 | 220465.316 | 0 | 39143.708 | 0 | 13927.995 | 0 | 0 | 0 | 0 | 0 | 5276.392 | 0 | 0
February | 913009000000 | 658355.142 | 28-FEB-10:00 | 218037.744 | 160954.2 | 220465.316 | 0 | 39735.304 | 0 | 13887.163 | 0 | 0 | 0 | 0 | 0 | 5275.415 | 0 | 0
March | 994587000000 | 824242.479 | 31-MAR-15:09 | 218037.744 | 146554.272 | 220465.316 | 0 | 220392.333 | 0 | 13821.378 | 0 | 0 | 0 | 0 | 0 | 4971.436 | 0 | 0
April | 846816000000 | 819971.908 | 03-APR-13:00 | 218037.744 | 151354.248 | 220465.316 | 0 | 210970.228 | 0 | 13844.113 | 0 | 0 | 0 | 0 | 0 | 5300.259 | 0 | 0
May | 1044980000000 | 1175949.799 | 30-MAY-15:00 | 218037.744 | 146554.272 | 220488.518 | 0 | 571757.089 | 0 | 13812.092 | 0 | 0 | 0 | 0 | 0 | 5300.085 | 0 | 0
June | 1243970000000 | 1493479.485 | 08-JUN-12:00 | 218037.744 | 151354.248 | 222360.511 | 0 | 882602.262 | 0 | 13812.092 | 0 | 0 | 0 | 0 | 0 | 5312.628 | 0 | 0
July | 1052100000000 | 1238134.513 | 13-JUL-12:00 | 121132.08 | 86203.896 | 220465.316 | 0 | 791465.396 | 0 | 13812.092 | 0 | 0 | 0 | 0 | 0 | 5055.734 | 0 | 0
August | 1059670000000 | 1253850.153 | 04-AUG-15:50 | 121132.08 | 81403.92 | 220465.316 | 0 | 811973.057 | 0 | 13812.092 | 0 | 0 | 0 | 0 | 0 | 5063.688 | 0 | 0
September | 1039560000000 | 1127585.599 | 06-SEP-10:00 | 218037.744 | 159932.088 | 220512.235 | 0 | 509992.418 | 0 | 13812.092 | 0 | 0 | 0 | 0 | 0 | 5299.022 | 0 | 0
October | 939496000000 | 959423.425 | 31-OCT-10:00 | 218037.744 | 159932.088 | 220465.316 | 0 | 341861.501 | 0 | 13820.284 | 0 | 0 | 0 | 0 | 0 | 5306.492 | 0 | 0
November | 918318000000 | 962129.442 | 02-NOV-11:00 | 218037.744 | 159932.088 | 220465.316 | 0 | 344565.511 | 0 | 13824.466 | 0 | 0 | 0 | 0 | 0 | 5304.317 | 0 | 0
December | 993189000000 | 657511.511 | 12-DEC-12:00 | 218037.744 | 159932.088 | 220465.316 | 0 | 39881.678 | 0 | 13913.09 | 0 | 0 | 0 | 0 | 0 | 5281.596 | 0 | 0
Annual Sum or Average | 12087500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 846816000000 | 657511.511 |  | 121132.08 | 81403.92 | 220465.316 | 0 | 39143.708 | 0 | 13812.092 | 0 | 0 | 0 | 0 | 0 | 4971.436 | 0 | 0
Maximum of Months | 1243970000000 | 1493479.485 |  | 218037.744 | 160954.2 | 222360.511 | 0 | 882602.262 | 0 | 13927.995 | 0 | 0 | 0 | 0 | 0 | 5312.628 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 288182.1 | 86371.43 | 0 | 374553.53
Cost per Total Building Area ($/m2) | 14.71 | 4.41 | 0 | 19.12
Cost per Net Conditioned Building Area ($/m2) | 14.71 | 4.41 | 0 | 19.12
12-Boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 19097.53 | 974.76 | 974.76
Net Site Energy | 19097.53 | 974.76 | 974.76
Total Source Energy | 48344.79 | 2467.58 | 2467.58
Net Source Energy | 48344.79 | 2467.58 | 2467.58
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 6078.06 | 0 | 0 | 0 | 0
Cooling | 1875.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3854.62 | 0 | 0 | 0 | 0 | 0
Pumps | 246.62 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 125.38 | 0 | 0 | 0 | 815.28
Refrigeration | 165.64 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12349.64 | 6747.9 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12349.64 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12349.64 | 100
Total On-Site and Utility Electric Sources | 12349.64 | 100
Total Electricity End Uses | 12349.64 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2232964.6 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 6846037.77 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 458834.98 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 290360.49 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 228824.99 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 89752.25 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 107565.05 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 26.89 | 63738.5 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 26.68 | 63230.31 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 29.45 | 69809.16 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 37.52 | 88938.03 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 27.72 | 52560.74 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 17.54 | 33261.55 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 13.82 | 26212.5 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.42 | 10281.35 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 6.5 | 12321.86 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001574 | 72353.35 | 2561.62
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002047 | 94134.91 | 3332.78
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004651 | 213860.83 | 7571.6
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006356 | 292269.98 | 10347.62
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001293 | 59435.47 | 2104.27
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002405 | 110565.05 | 3914.48
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001429 | 65700.59 | 2326.09
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001933 | 88891.17 | 3147.13
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003299 | 151668.34 | 5369.72
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005234 | 240640.89 | 8519.73
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001554 | 71445.44 | 2529.48
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002038 | 93726.02 | 3318.31
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004525 | 208067.72 | 7366.5
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006281 | 288803.8 | 10224.9
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001277 | 58728.75 | 2079.25
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002396 | 110156.67 | 3900.02
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001429 | 65703.06 | 2326.17
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001935 | 88955.66 | 3149.42
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003304 | 151920.59 | 5378.65
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00524 | 240934.22 | 8530.11
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001555 | 71507.57 | 2531.68
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002047 | 94135.55 | 3332.81
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004563 | 209792.61 | 7427.57
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007757 | 356663.14 | 12627.42
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001299 | 59725.88 | 2114.55
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002471 | 113622.25 | 4022.72
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001448 | 66593.76 | 2357.71
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001949 | 89627.25 | 3173.19
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003461 | 159147.35 | 5634.51
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006547 | 301047.72 | 10658.39
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004611 | 212005.76 | 7505.92
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008747 | 402194.68 | 14239.43
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001304 | 59963.23 | 2122.96
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001983 | 91155.39 | 3227.3
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00112 | 51510.13 | 1823.68
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001889 | 86858.27 | 3075.16
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004418 | 203135.52 | 7191.88
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006226 | 286258.47 | 10134.79
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008505 | 391039.18 | 13844.48
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001181 | 54289.19 | 1922.07
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002185 | 100469.03 | 3557.04
VAV_POD_1_HEATC | 0.003616 | 166260.6 | 2449.92
VAV_POD_2_HEATC | 0.003622 | 166535.17 | 2450.14
VAV_POD_3_HEATC | 0.003545 | 162980.49 | 2443.7
VAV_OTHER_HEATC | 0.002644 | 121557.1 | 1951.33
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.018116 | 26.89 | 21.42 | 12.8 | 7.22 | 0.00809 | 0.004045
VAV_POD_2_COOLC | 0.01798 | 26.68 | 21.43 | 12.8 | 7.22 | 0.008086 | 0.004043
VAV_POD_3_COOLC | 0.019698 | 29.45 | 21.2 | 12.8 | 7.22 | 0.008158 | 0.004079
VAV_OTHER_COOLC | 0.024296 | 37.52 | 20.52 | 12.8 | 7.22 | 0.008225 | 0.004112
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 495627.7
PSZ-AC_2:6_HEATC | 251813.88
PSZ-AC_3:7_HEATC | 247173.84
PSZ-AC_4:8_HEATC | 96949.24
PSZ-AC_5:9_HEATC | 116190.4
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 361023.4234 | 570.2792 | 1314.4823 | 0 | 0.0053 | 1366459.97 | 148744.841
February | 299550.2372 | 480.0421 | 1127.8273 | 0 | 0.0045 | 1172478.856 | 124090.9342
March | 318589.1831 | 524.4288 | 1274.6136 | 0 | 0.005 | 1325183.34 | 133339.0383
April | 264575.6427 | 449.5727 | 1134.5914 | 0 | 0.0045 | 1179707.6668 | 112111.4636
May | 288226.7993 | 496.2894 | 1271.3492 | 0 | 0.005 | 1321947.7368 | 122773.7617
June | 307368.4706 | 534.8899 | 1386.3135 | 0 | 0.0054 | 1441524.5332 | 131480.7093
July | 269193.9553 | 468.9388 | 1216.7405 | 0 | 0.0047 | 1265201.286 | 115198.2789
August | 281426.9432 | 489.5415 | 1268.2046 | 0 | 0.0049 | 1318710.5709 | 120363.8583
September | 284421.7888 | 493.1487 | 1273.028 | 0 | 0.005 | 1323715.6652 | 121487.5589
October | 283411.4248 | 484.965 | 1233.6931 | 0 | 0.0048 | 1282773.016 | 120425.094
November | 303382.0001 | 496.8152 | 1199.8024 | 0 | 0.0048 | 1247385.3447 | 126721.2022
December | 355639.2212 | 559.2601 | 1281.2708 | 0 | 0.0051 | 1331915.2162 | 146279.8941
Annual Sum or Average | 3616809.0897 | 6048.1715 | 14981.9167 | 0 | 0.0591 | 15577000 | 1523016.6345
Minimum of Months | 264575.6427 | 449.5727 | 1127.8273 | 0 | 0.0045 | 1172478.856 | 112111.4636
Maximum of Months | 361023.4234 | 570.2792 | 1386.3135 | 0 | 0.0054 | 1441524.5332 | 148744.841
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1083350000000 | 858149.958 | 27-JAN-11:39 | 218037.744 | 160954.2 | 254248.504 | 0 | 196779.216 | 0 | 20540.73 | 0 | 0 | 0 | 0 | 0 | 7589.563 | 0 | 0
February | 929555000000 | 786399.192 | 07-FEB-14:00 | 218037.744 | 151354.248 | 254248.504 | 0 | 136975.071 | 0 | 20523.312 | 0 | 0 | 0 | 0 | 0 | 5260.313 | 0 | 0
March | 1050620000000 | 922403.318 | 30-MAR-15:00 | 218037.744 | 146554.272 | 254266.529 | 0 | 277801.925 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 5243.598 | 0 | 0
April | 935286000000 | 949614.538 | 25-APR-15:09 | 218037.744 | 146554.272 | 254439.616 | 0 | 304815.243 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 5268.413 | 0 | 0
May | 1048060000000 | 1036079.185 | 23-MAY-15:00 | 218037.744 | 146554.272 | 254886.349 | 0 | 390839.482 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 5262.087 | 0 | 0
June | 1142860000000 | 1146260.596 | 28-JUN-11:00 | 218037.744 | 160954.2 | 254945.882 | 0 | 486730.4 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 5093.121 | 0 | 0
July | 1003070000000 | 967935.365 | 18-JUL-13:00 | 121132.08 | 86203.896 | 254286.084 | 0 | 480791.19 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 5022.865 | 0 | 0
August | 1045490000000 | 983254.044 | 30-AUG-13:00 | 121132.08 | 86203.896 | 254248.504 | 0 | 496265.59 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 4904.724 | 0 | 0
September | 1049460000000 | 1072608.567 | 06-SEP-15:00 | 218037.744 | 146475.648 | 254509.324 | 0 | 428173.058 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 4913.543 | 0 | 0
October | 1017000000000 | 1011825.919 | 05-OCT-15:09 | 218037.744 | 146475.648 | 255265.186 | 0 | 366623.969 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 4924.121 | 0 | 0
November | 988942000000 | 877477.24 | 10-NOV-13:00 | 218037.744 | 150332.136 | 254248.504 | 0 | 229207.995 | 0 | 20518.65 | 0 | 0 | 0 | 0 | 0 | 5132.212 | 0 | 0
December | 1055960000000 | 761570.885 | 21-DEC-14:09 | 218037.744 | 150332.136 | 254248.504 | 0 | 113231.01 | 0 | 20537.505 | 0 | 0 | 0 | 0 | 0 | 5183.986 | 0 | 0
Annual Sum or Average | 12349600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 929555000000 | 761570.885 |  | 121132.08 | 86203.896 | 254248.504 | 0 | 113231.01 | 0 | 20499.25 | 0 | 0 | 0 | 0 | 0 | 4904.724 | 0 | 0
Maximum of Months | 1142860000000 | 1146260.596 |  | 218037.744 | 160954.2 | 255265.186 | 0 | 496265.59 | 0 | 20540.73 | 0 | 0 | 0 | 0 | 0 | 7589.563 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 126871.57 | 46698.86 | 0 | 173570.43
Cost per Total Building Area ($/m2) | 6.48 | 2.38 | 0 | 8.86
Cost per Net Conditioned Building Area ($/m2) | 6.48 | 2.38 | 0 | 8.86
13-Minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 26281.11 | 1341.42 | 1341.42
Net Site Energy | 26281.11 | 1341.42 | 1341.42
Total Source Energy | 56897.07 | 2904.1 | 2904.1
Net Source Energy | 56897.07 | 2904.1 | 2904.1
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 13574.54 | 0 | 0 | 0 | 0
Cooling | 1836.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3667.95 | 0 | 0 | 0 | 0 | 0
Pumps | 148.38 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 137.34 | 0 | 0 | 0 | 815.28
Refrigeration | 165.1 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12024.77 | 14256.34 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 12024.77 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 12024.77 | 100
Total On-Site and Utility Electric Sources | 12024.77 | 100
Total Electricity End Uses | 12024.77 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1417958.25 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7357480.02 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 590483.47 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 253298.06 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 290996.54 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 116810.29 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 138012.73 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 23.74 | 56262.97 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 23.53 | 55776.49 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 25.88 | 61345.36 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 32.83 | 77829.14 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 23.78 | 45090.54 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 15.3 | 29015.95 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 11.72 | 22221.1 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.7 | 8919.88 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.56 | 10538.94 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001674 | 76951.25 | 2724.41
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002149 | 98796.37 | 3497.82
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005114 | 235147 | 8325.22
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006912 | 317797.89 | 11251.42
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001343 | 61743.99 | 2186
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002443 | 112327.48 | 3976.88
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001422 | 65376.89 | 2314.62
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001905 | 87587.51 | 3100.98
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003337 | 153437.37 | 5432.35
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005229 | 240416.67 | 8511.79
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001653 | 76012.45 | 2691.17
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00214 | 98383.54 | 3483.2
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00497 | 228497.91 | 8089.82
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006828 | 313928.64 | 11114.43
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001326 | 60953.34 | 2158.01
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002432 | 111825.79 | 3959.12
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001422 | 65380.96 | 2314.77
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001906 | 87649.87 | 3103.18
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003343 | 153706.04 | 5441.86
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005235 | 240709.95 | 8522.17
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001655 | 76075.04 | 2693.39
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002148 | 98787.39 | 3497.5
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005007 | 230210.8 | 8150.46
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008306 | 381894.82 | 13520.73
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001348 | 61958.39 | 2193.6
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002507 | 115260.23 | 4080.71
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001441 | 66253.82 | 2345.67
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00192 | 88303.97 | 3126.34
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003505 | 161178.65 | 5706.42
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006538 | 300604.21 | 10642.69
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004664 | 214467.34 | 7593.07
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008804 | 404789.07 | 14331.29
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001441 | 66267.64 | 2346.16
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002154 | 99037.83 | 3506.37
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001138 | 52343.45 | 1853.18
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001888 | 86819.08 | 3073.77
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004781 | 219829.6 | 7782.92
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006669 | 306652.54 | 10856.83
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008594 | 395169.39 | 13990.71
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001265 | 58181.55 | 2059.88
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002211 | 101664.71 | 3599.37
VAV_POD_1_HEATC | 0.005132 | 235980.6 | 3292.94
VAV_POD_2_HEATC | 0.005139 | 236291.21 | 3290.9
VAV_POD_3_HEATC | 0.005062 | 232735.45 | 3309.3
VAV_OTHER_HEATC | 0.003917 | 180092.32 | 2769.28
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.012115 | 23.74 | 21.57 | 12.8 | 7.22 | 0.009771 | 0.0085
VAV_POD_2_COOLC | 0.012057 | 23.53 | 21.59 | 12.8 | 7.22 | 0.009782 | 0.0085
VAV_POD_3_COOLC | 0.012762 | 25.88 | 21.34 | 12.8 | 7.22 | 0.009699 | 0.0085
VAV_OTHER_COOLC | 0.013924 | 32.83 | 20.63 | 12.8 | 7.22 | 0.009339 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 552750.81
PSZ-AC_2:6_HEATC | 308991.02
PSZ-AC_3:7_HEATC | 272401.48
PSZ-AC_4:8_HEATC | 109345.96
PSZ-AC_5:9_HEATC | 129193.54
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 431704.5117 | 611.636 | 717.6146 | 0 | 0.0056 | 471071.0525 | 170421.2736
February | 346211.3435 | 505.3417 | 623.7959 | 0 | 0.0048 | 409583.0832 | 138089.4043
March | 304638.6176 | 477.184 | 654.7921 | 0 | 0.005 | 430134.2213 | 124616.5524
April | 211811.1006 | 362.3699 | 554.8751 | 0 | 0.0041 | 364655.4967 | 89568.2255
May | 238638.9875 | 426.4599 | 684.3928 | 0 | 0.005 | 449849.1528 | 102651.8453
June | 262924.6443 | 476.4356 | 775.4543 | 0 | 0.0057 | 509728.8705 | 113727.0335
July | 220270.4659 | 398.6848 | 648.1584 | 0 | 0.0047 | 426051.8682 | 95233.273
August | 236180.916 | 426.7375 | 692.5504 | 0 | 0.0051 | 455229.0816 | 102040.9069
September | 216990.2923 | 389.1067 | 626.6507 | 0 | 0.0046 | 411900.5953 | 93467.0694
October | 225679.988 | 384.3932 | 585.6593 | 0 | 0.0043 | 384879.2208 | 95270.0831
November | 291382.6677 | 457.4037 | 629.5027 | 0 | 0.0048 | 413526.5876 | 119288.0521
December | 392152.2985 | 568.4816 | 693.8166 | 0 | 0.0054 | 455534.5886 | 156038.9334
Annual Sum or Average | 3378585.8336 | 5484.2346 | 7887.2627 | 0 | 0.059 | 5182143.8194 | 1400412.6525
Minimum of Months | 211811.1006 | 362.3699 | 554.8751 | 0 | 0.0041 | 364655.4967 | 89568.2255
Maximum of Months | 431704.5117 | 611.636 | 775.4543 | 0 | 0.0057 | 509728.8705 | 170421.2736
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1093080000000 | 643957.645 | 19-JAN-16:00 | 218037.744 | 146554.272 | 220972.172 | 0 | 16184.614 | 23884.224 | 13407.034 | 0 | 0 | 0 | 0 | 0 | 4917.586 | 0 | 0
February | 950407000000 | 638948.225 | 17-FEB-11:39 | 218037.744 | 160954.2 | 220972.172 | 0 | 17998.061 | 0 | 13414.032 | 0 | 0 | 0 | 0 | 0 | 7572.016 | 0 | 0
March | 998094000000 | 734535.048 | 23-MAR-13:00 | 218037.744 | 151354.248 | 220972.172 | 0 | 125842.961 | 0 | 13054.062 | 0 | 0 | 0 | 0 | 0 | 5273.862 | 0 | 0
April | 846156000000 | 824538.762 | 14-APR-15:00 | 218037.744 | 146554.272 | 220972.172 | 0 | 220677.749 | 0 | 13030.845 | 0 | 0 | 0 | 0 | 0 | 5265.98 | 0 | 0
May | 1043840000000 | 1126320.659 | 31-MAY-11:00 | 218037.744 | 160954.2 | 221575.71 | 0 | 507523.833 | 0 | 13030.845 | 0 | 0 | 0 | 0 | 0 | 5198.327 | 0 | 0
June | 1182790000000 | 1368300.34 | 29-JUN-15:09 | 218037.744 | 146554.272 | 221786.379 | 0 | 763586.027 | 0 | 13030.845 | 0 | 0 | 0 | 0 | 0 | 5305.073 | 0 | 0
July | 988621000000 | 1195729.809 | 13-JUL-15:00 | 121132.08 | 81403.92 | 220972.172 | 0 | 754131.525 | 0 | 13030.845 | 0 | 0 | 0 | 0 | 0 | 5059.268 | 0 | 0
August | 1056320000000 | 1147249.725 | 25-AUG-15:00 | 121132.08 | 81403.92 | 220972.172 | 0 | 705653.79 | 0 | 13030.845 | 0 | 0 | 0 | 0 | 0 | 5056.918 | 0 | 0
September | 955784000000 | 1090183.208 | 14-SEP-15:09 | 218037.744 | 146475.648 | 221157.234 | 0 | 486188.017 | 0 | 13030.845 | 0 | 0 | 0 | 0 | 0 | 5293.721 | 0 | 0
October | 893083000000 | 841274.13 | 06-OCT-15:09 | 218037.744 | 146475.648 | 220972.172 | 0 | 237476.253 | 0 | 13037.616 | 0 | 0 | 0 | 0 | 0 | 5274.697 | 0 | 0
November | 959557000000 | 743289.463 | 02-NOV-12:00 | 218037.744 | 159932.088 | 220972.172 | 0 | 126003.718 | 0 | 13063.866 | 0 | 0 | 0 | 0 | 0 | 5279.875 | 0 | 0
December | 1057030000000 | 640889.064 | 26-DEC-16:40 | 218037.744 | 146475.648 | 220972.172 | 0 | 12771.765 | 23884.224 | 13491.585 | 0 | 0 | 0 | 0 | 0 | 5255.927 | 0 | 0
Annual Sum or Average | 12024800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 846156000000 | 638948.225 |  | 121132.08 | 81403.92 | 220972.172 | 0 | 12771.765 | 0 | 13030.845 | 0 | 0 | 0 | 0 | 0 | 4917.586 | 0 | 0
Maximum of Months | 1182790000000 | 1368300.34 |  | 218037.744 | 160954.2 | 221786.379 | 0 | 763586.027 | 23884.224 | 13491.585 | 0 | 0 | 0 | 0 | 0 | 7572.016 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 206987.39 | 112482.84 | 0 | 319470.23
Cost per Total Building Area ($/m2) | 10.56 | 5.74 | 0 | 16.31
Cost per Net Conditioned Building Area ($/m2) | 10.56 | 5.74 | 0 | 16.31
14-Helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 22957.56 | 1171.78 | 1171.78
Net Site Energy | 22957.56 | 1171.78 | 1171.78
Total Source Energy | 53348.14 | 2722.96 | 2722.96
Net Source Energy | 53348.14 | 2722.96 | 2722.96
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 10412.95 | 0 | 0 | 0 | 0
Cooling | 1429.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3834.27 | 0 | 0 | 0 | 0 | 0
Pumps | 225.39 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 138.38 | 0 | 0 | 0 | 815.28
Refrigeration | 165.31 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11861.78 | 11095.78 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 11861.78 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 11861.78 | 100
Total On-Site and Utility Electric Sources | 11861.78 | 100
Total Electricity End Uses | 11861.78 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 3.24 | 0.39 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 15.4 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 3.24 | 0.39 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 74.2 | 3.24 | 0.39 | 0.495 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 3.24 | 0.39 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 3.24 | 0.39 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 21 | 3.24 | 0.39 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 3.24 | 0.39 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 3.24 | 0.39 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 3.92 | 0.49 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 53.2 | 3.24 | 0.39 | 0.495 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 3.24 | 0.39 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_NORTH | 33.6 | 3.24 | 0.39 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2219471.65 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7041627.13 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 427469.71 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 273121.84 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 208306.04 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 86483.61 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 99961.32 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 25.65 | 60805.75 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 25.42 | 60254.85 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 28.08 | 66550.67 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 35.12 | 83236.22 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 25.82 | 48967.77 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 16.5 | 31286.82 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 12.58 | 23862 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.22 | 9906.92 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 6.04 | 11450.83 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001656 | 76129.2 | 2695.3
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002114 | 97195.07 | 3441.13
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005079 | 233536.23 | 8268.19
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006775 | 311520.1 | 11029.16
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00129 | 59327.51 | 2100.45
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002315 | 106458.99 | 3769.11
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001358 | 62443 | 2210.75
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00182 | 83703.59 | 2963.47
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003134 | 144092.81 | 5101.51
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004906 | 225592.44 | 7986.95
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001636 | 75211.42 | 2662.81
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002105 | 96779.7 | 3426.42
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004934 | 226842.69 | 8031.21
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006689 | 307559.52 | 10888.94
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001272 | 58502.37 | 2071.24
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002304 | 105926.31 | 3750.25
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001358 | 62446.94 | 2210.89
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001822 | 83766.62 | 2965.7
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00314 | 144390.77 | 5112.06
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004913 | 225888.56 | 7997.43
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001637 | 75275.74 | 2665.09
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002114 | 97192.01 | 3441.02
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004972 | 228631.98 | 8094.56
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008173 | 375787.62 | 13304.51
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001295 | 59543.14 | 2108.08
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00238 | 109426.8 | 3874.18
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001378 | 63342.93 | 2242.61
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001836 | 84425.24 | 2989.02
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003305 | 151982.43 | 5380.84
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006235 | 286662.68 | 10149.1
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004404 | 202503.68 | 7169.51
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008275 | 380496.28 | 13471.22
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001422 | 65375.03 | 2314.56
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002089 | 96039.87 | 3400.23
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001056 | 48541.14 | 1718.57
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001756 | 80734.79 | 2858.36
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004705 | 216315.72 | 7658.51
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006477 | 297834.62 | 10544.63
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008191 | 376620.27 | 13333.99
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001223 | 56251.45 | 1991.54
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002082 | 95728.02 | 3389.19
VAV_POD_1_HEATC | 0.004676 | 215011.01 | 3033.51
VAV_POD_2_HEATC | 0.004683 | 215325.35 | 3031.94
VAV_POD_3_HEATC | 0.004605 | 211732.98 | 3044.95
VAV_OTHER_HEATC | 0.003557 | 163532.51 | 2531.96
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.01804 | 25.65 | 21.19 | 12.8 | 7.22 | 0.008101 | 0.004051
VAV_POD_2_COOLC | 0.017883 | 25.42 | 21.2 | 12.8 | 7.22 | 0.008098 | 0.004049
VAV_POD_3_COOLC | 0.019774 | 28.08 | 21.13 | 12.8 | 7.22 | 0.008168 | 0.004084
VAV_OTHER_COOLC | 0.023909 | 35.12 | 20.44 | 12.8 | 7.22 | 0.008228 | 0.004114
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 547000.99
PSZ-AC_2:6_HEATC | 288396.02
PSZ-AC_3:7_HEATC | 266553.65
PSZ-AC_4:8_HEATC | 110666.6
PSZ-AC_5:9_HEATC | 127913.02
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 395973.1085 | 584.8833 | 817.1646 | 0 | 0.0059 | 19369300 | 158840.3464
February | 327149.7031 | 493.3617 | 711.7915 | 0 | 0.0051 | 16873800 | 132212.3643
March | 305606.2677 | 490.4306 | 771.8139 | 0 | 0.0055 | 18302700 | 126363.0789
April | 233792.7533 | 387.7178 | 635.7698 | 0 | 0.0045 | 15078700 | 97880.7878
May | 246599.7618 | 425.7011 | 731.1528 | 0 | 0.0051 | 17343700 | 104861.2028
June | 264751.4255 | 463.6969 | 809.0606 | 0 | 0.0056 | 19192700 | 113223.6735
July | 222142.8134 | 390.7348 | 684.8712 | 0 | 0.0048 | 16246900 | 95162.5499
August | 230381.2275 | 401.4752 | 696.7069 | 0 | 0.0048 | 16527200 | 98329.2264
September | 238376.7129 | 414.3979 | 717.2313 | 0 | 0.005 | 17013900 | 101644.0908
October | 248691.21 | 419.0149 | 700.1163 | 0 | 0.0049 | 16605900 | 104755.2417
November | 296972.0235 | 473.3139 | 738.2161 | 0 | 0.0052 | 17505400 | 122477.7837
December | 368219.4361 | 551.3742 | 786.9603 | 0 | 0.0057 | 18654900 | 148430.8163
Annual Sum or Average | 3378656.4432 | 5496.1023 | 8800.8553 | 0 | 0.0622 | 208715000 | 1404181.1624
Minimum of Months | 222142.8134 | 387.7178 | 635.7698 | 0 | 0.0045 | 15078700 | 95162.5499
Maximum of Months | 395973.1085 | 584.8833 | 817.1646 | 0 | 0.0059 | 19369300 | 158840.3464
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1100800000000 | 681009.611 | 20-JAN-08:09 | 218037.744 | 151354.248 | 238868.556 | 0 | 22738.256 | 23884.224 | 20867.722 | 0 | 0 | 0 | 0 | 0 | 5258.862 | 0 | 0
February | 958977000000 | 820352.201 | 02-FEB-14:00 | 218037.744 | 151354.248 | 238868.556 | 0 | 186465.019 | 0 | 20402.159 | 0 | 0 | 0 | 0 | 0 | 5224.476 | 0 | 0
March | 1040180000000 | 878151.733 | 30-MAR-15:00 | 218037.744 | 146554.272 | 238868.556 | 0 | 249057.65 | 0 | 20377.09 | 0 | 0 | 0 | 0 | 0 | 5256.421 | 0 | 0
April | 856961000000 | 863105.904 | 06-APR-15:00 | 218037.744 | 146554.272 | 238868.556 | 0 | 234011.854 | 0 | 20381.024 | 0 | 0 | 0 | 0 | 0 | 5252.455 | 0 | 0
May | 985683000000 | 936346.62 | 16-MAY-15:00 | 218037.744 | 146554.272 | 238868.556 | 0 | 307248.533 | 0 | 20375.606 | 0 | 0 | 0 | 0 | 0 | 5261.91 | 0 | 0
June | 1090770000000 | 1157474.928 | 26-JUN-15:09 | 218037.744 | 146554.272 | 241138.467 | 0 | 526092.276 | 0 | 20375.606 | 0 | 0 | 0 | 0 | 0 | 5276.563 | 0 | 0
July | 923352000000 | 920483.85 | 21-JUL-15:00 | 121132.08 | 81403.92 | 238868.556 | 0 | 454030.723 | 0 | 20375.606 | 0 | 0 | 0 | 0 | 0 | 4672.965 | 0 | 0
August | 939278000000 | 879290.709 | 09-AUG-15:00 | 121132.08 | 81403.92 | 238868.556 | 0 | 412836.153 | 0 | 20375.606 | 0 | 0 | 0 | 0 | 0 | 4674.394 | 0 | 0
September | 966940000000 | 968528.817 | 11-SEP-15:09 | 218037.744 | 146475.648 | 238868.556 | 0 | 339485.454 | 0 | 20375.606 | 0 | 0 | 0 | 0 | 0 | 5285.809 | 0 | 0
October | 943755000000 | 900984.514 | 06-OCT-15:00 | 218037.744 | 146475.648 | 238948.19 | 0 | 272191.039 | 0 | 20375.606 | 0 | 0 | 0 | 0 | 0 | 4956.286 | 0 | 0
November | 994872000000 | 756923.431 | 21-NOV-11:39 | 218037.744 | 159932.088 | 238868.556 | 0 | 111876.296 | 0 | 20439.711 | 0 | 0 | 0 | 0 | 0 | 7769.035 | 0 | 0
December | 1060200000000 | 677192.45 | 22-DEC-16:40 | 218037.744 | 146475.648 | 238868.556 | 0 | 24296.297 | 23884.224 | 20716.922 | 0 | 0 | 0 | 0 | 0 | 4913.059 | 0 | 0
Annual Sum or Average | 11861800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 856961000000 | 677192.45 |  | 121132.08 | 81403.92 | 238868.556 | 0 | 22738.256 | 0 | 20375.606 | 0 | 0 | 0 | 0 | 0 | 4672.965 | 0 | 0
Maximum of Months | 1100800000000 | 1157474.928 |  | 218037.744 | 159932.088 | 241138.467 | 0 | 526092.276 | 23884.224 | 20867.722 | 0 | 0 | 0 | 0 | 0 | 7769.035 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 253937.79 | 89740.87 | 0 | 343678.66
Cost per Total Building Area ($/m2) | 12.96 | 4.58 | 0 | 17.54
Cost per Net Conditioned Building Area ($/m2) | 12.96 | 4.58 | 0 | 17.54
15-Duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 28536.03 | 1456.51 | 1456.51
Net Site Energy | 28536.03 | 1456.51 | 1456.51
Total Source Energy | 57676.76 | 2943.89 | 2943.89
Net Source Energy | 57676.76 | 2943.89 | 2943.89
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 16530.74 | 0 | 0 | 0 | 0
Cooling | 1092.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3726.21 | 0 | 0 | 0 | 0 | 0
Pumps | 116.42 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 153.61 | 0 | 0 | 0 | 815.28
Refrigeration | 164.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11307.21 | 17228.82 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 11307.21 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 11307.21 | 100
Total On-Site and Utility Electric Sources | 11307.21 | 100
Total Electricity End Uses | 11307.21 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 3.24 | 0.49 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 15.4 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 3.24 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 74.2 | 3.24 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 25.2 | 3.24 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 23.8 | 3.24 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 25.2 | 3.24 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 23.8 | 3.24 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 21 | 3.24 | 0.49 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 21 | 3.24 | 0.49 | 0.49 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 4.2 | 3.24 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 21 | 3.24 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 4.2 | 3.24 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 21 | 3.24 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 53.2 | 3.24 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 19.6 | 3.24 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 53.2 | 3.24 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 19.6 | 3.24 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 33.6 | 3.24 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 72.8 | 3.24 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 33.6 | 3.24 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 72.8 | 3.24 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 3.92 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 53.2 | 3.24 | 0.49 | 0.49 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 53.2 | 3.24 | 0.49 | 0.49 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 12.6 | 3.24 | 0.49 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 49.41 | 3.24 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 33.6 | 3.24 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 36.4 | 3.24 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_NORTH | 33.6 | 3.24 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1209296.92 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7223057.46 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 580249.21 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 246861.89 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 227955.47 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 95683.62 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 121223.3 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 23.67 | 56097.41 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 23.41 | 55486.1 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 25.85 | 61279.86 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 32.27 | 76489.04 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 23.37 | 44309.04 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.91 | 28278.67 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 11.09 | 21036.94 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.78 | 9067.71 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.54 | 10513.07 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001713 | 78770.01 | 2788.8
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002156 | 99117.25 | 3509.18
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005208 | 239449.02 | 8477.53
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006792 | 312310.28 | 11057.14
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001362 | 62606.47 | 2216.54
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002328 | 107029.31 | 3789.3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001424 | 65456.44 | 2317.44
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001874 | 86163.16 | 3050.55
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003121 | 143490.61 | 5080.19
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004799 | 220678.11 | 7812.96
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001688 | 77599.67 | 2747.36
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002145 | 98605.6 | 3491.07
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005028 | 231176.53 | 8184.65
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006689 | 307567.74 | 10889.23
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001342 | 61683.05 | 2183.85
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002315 | 106466.02 | 3769.36
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001424 | 65461.69 | 2317.63
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001876 | 86241.28 | 3053.31
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003128 | 143820.96 | 5091.88
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.004807 | 221027.49 | 7825.33
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001689 | 77670.04 | 2749.86
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002154 | 99036.15 | 3506.31
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005066 | 232928.34 | 8246.67
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008171 | 375712.57 | 13301.85
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001366 | 62793.45 | 2223.16
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002392 | 109964.55 | 3893.22
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001447 | 66519.17 | 2355.07
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001892 | 86974.04 | 3079.26
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003324 | 152851.54 | 5411.61
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006119 | 281349.14 | 9960.98
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004712 | 216674.02 | 7671.2
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008421 | 387177.27 | 13707.75
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001462 | 67243.82 | 2380.72
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002076 | 95461 | 3379.73
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00104 | 47799.62 | 1692.31
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001685 | 77469.15 | 2742.74
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.004814 | 221351.41 | 7836.8
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006453 | 296702.26 | 10504.54
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008019 | 368732.19 | 13054.72
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001244 | 57215.22 | 2025.67
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002036 | 93628.33 | 3314.85
VAV_POD_1_HEATC | 0.005397 | 248139.41 | 3411.59
VAV_POD_2_HEATC | 0.005405 | 248521.55 | 3408.21
VAV_POD_3_HEATC | 0.005326 | 244899.72 | 3434.95
VAV_OTHER_HEATC | 0.004165 | 191522.78 | 2903.86
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.010238 | 23.67 | 20.76 | 12.8 | 7.22 | 0.009452 | 0.0085
VAV_POD_2_COOLC | 0.010166 | 23.41 | 20.78 | 12.8 | 7.22 | 0.009462 | 0.0085
VAV_POD_3_COOLC | 0.010887 | 25.85 | 20.61 | 12.8 | 7.22 | 0.009405 | 0.0085
VAV_OTHER_COOLC | 0.012084 | 32.27 | 20.16 | 12.8 | 7.22 | 0.009136 | 0.0085
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 555976.42
PSZ-AC_2:6_HEATC | 312887.5
PSZ-AC_3:7_HEATC | 263965.19
PSZ-AC_4:8_HEATC | 113778.86
PSZ-AC_5:9_HEATC | 131914.83
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 429908.6985 | 608.0639 | 711.2829 | 0 | 0.0056 | 466907.844 | 169614.1113
February | 363663.8658 | 522.5263 | 628.2489 | 0 | 0.0049 | 412456.1669 | 144258.1107
March | 342706.8339 | 517.5971 | 674.0432 | 0 | 0.0052 | 442681.6889 | 138352.0029
April | 232051.4393 | 379.6091 | 551.2791 | 0 | 0.0041 | 362219.0652 | 96465.1399
May | 220066.2402 | 380.1425 | 588.3846 | 0 | 0.0043 | 386692.7824 | 93407.9179
June | 224769.0969 | 404.7851 | 654.7465 | 0 | 0.0048 | 430374.725 | 96983.0448
July | 202342.4399 | 363.6941 | 587.1291 | 0 | 0.0043 | 385926.1145 | 87239.2237
August | 199250.6805 | 351.6945 | 557.1805 | 0 | 0.0041 | 366216.1116 | 85290.4196
September | 205717.7455 | 360.0478 | 565.2956 | 0 | 0.0042 | 371537.8075 | 87766.0299
October | 232883.4486 | 387.5201 | 574.5831 | 0 | 0.0043 | 377561.4118 | 97437.0905
November | 315432.0779 | 479.7471 | 631.2862 | 0 | 0.0048 | 414619.5739 | 127660.6975
December | 407370.2255 | 582.3813 | 694.1678 | 0 | 0.0054 | 455714.29 | 161314.1337
Annual Sum or Average | 3376162.7926 | 5337.8089 | 7417.6274 | 0 | 0.0559 | 4872907.5818 | 1385787.9224
Minimum of Months | 199250.6805 | 351.6945 | 551.2791 | 0 | 0.0041 | 362219.0652 | 85290.4196
Maximum of Months | 429908.6985 | 608.0639 | 711.2829 | 0 | 0.0056 | 466907.844 | 169614.1113
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1083420000000 | 633745.392 | 13-JAN-11:39 | 218037.744 | 160954.2 | 217612.9 | 0 | 18101.493 | 0 | 11460.232 | 0 | 0 | 0 | 0 | 0 | 7578.823 | 0 | 0
February | 957073000000 | 634651.829 | 24-FEB-11:39 | 218037.744 | 160954.2 | 217612.9 | 0 | 19066.317 | 0 | 11393.182 | 0 | 0 | 0 | 0 | 0 | 7587.487 | 0 | 0
March | 1027210000000 | 636026.337 | 16-MAR-10:39 | 218037.744 | 160954.2 | 217612.9 | 0 | 20464.469 | 0 | 11370.452 | 0 | 0 | 0 | 0 | 0 | 7586.572 | 0 | 0
April | 840502000000 | 713297.424 | 04-APR-13:00 | 218037.744 | 151354.248 | 217612.9 | 0 | 109878.612 | 0 | 11139.096 | 0 | 0 | 0 | 0 | 0 | 5274.825 | 0 | 0
May | 897291000000 | 858753.915 | 31-MAY-15:00 | 218037.744 | 146554.272 | 217764.629 | 0 | 260012.15 | 0 | 11118.753 | 0 | 0 | 0 | 0 | 0 | 5266.368 | 0 | 0
June | 998652000000 | 1176938.77 | 14-JUN-15:09 | 218037.744 | 146554.272 | 218250.333 | 0 | 577674.189 | 0 | 11118.753 | 0 | 0 | 0 | 0 | 0 | 5303.48 | 0 | 0
July | 895512000000 | 985817.363 | 06-JUL-15:09 | 121132.08 | 81403.92 | 217612.9 | 0 | 549502.363 | 0 | 11118.753 | 0 | 0 | 0 | 0 | 0 | 5047.348 | 0 | 0
August | 849777000000 | 950323.473 | 11-AUG-14:00 | 121132.08 | 81403.92 | 217612.9 | 0 | 514006.603 | 0 | 11118.753 | 0 | 0 | 0 | 0 | 0 | 5049.218 | 0 | 0
September | 862125000000 | 1006161.793 | 07-SEP-15:09 | 218037.744 | 146475.648 | 217766.285 | 0 | 407462.178 | 0 | 11118.753 | 0 | 0 | 0 | 0 | 0 | 5301.185 | 0 | 0
October | 876103000000 | 727606.572 | 27-OCT-11:00 | 218037.744 | 159932.088 | 217612.9 | 0 | 115590.566 | 0 | 11149.859 | 0 | 0 | 0 | 0 | 0 | 5283.415 | 0 | 0
November | 962093000000 | 706165.734 | 09-NOV-11:39 | 218037.744 | 159932.088 | 217612.9 | 0 | 91623.896 | 0 | 11190.114 | 0 | 0 | 0 | 0 | 0 | 7768.993 | 0 | 0
December | 1057450000000 | 638106.722 | 01-DEC-16:19 | 218037.744 | 146475.648 | 217612.9 | 0 | 15726.343 | 23884.224 | 11453.394 | 0 | 0 | 0 | 0 | 0 | 4916.47 | 0 | 0
Annual Sum or Average | 11307200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 840502000000 | 633745.392 |  | 121132.08 | 81403.92 | 217612.9 | 0 | 15726.343 | 0 | 11118.753 | 0 | 0 | 0 | 0 | 0 | 4916.47 | 0 | 0
Maximum of Months | 1083420000000 | 1176938.77 |  | 218037.744 | 160954.2 | 218250.333 | 0 | 577674.189 | 23884.224 | 11460.232 | 0 | 0 | 0 | 0 | 0 | 7768.993 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 188539.24 | 135585.09 | 0 | 324124.33
Cost per Total Building Area ($/m2) | 9.62 | 6.92 | 0 | 16.54
Cost per Net Conditioned Building Area ($/m2) | 9.62 | 6.92 | 0 | 16.54
16-Fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 39548.07 | 2018.58 | 2018.58
Net Site Energy | 39548.07 | 2018.58 | 2018.58
Total Source Energy | 71020.78 | 3624.99 | 3624.99
Net Source Energy | 71020.78 | 3624.99 | 3624.99
Area (m2)
Total Building Area | 19592
Net Conditioned Building Area | 19592
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 27607.27 | 0 | 0 | 0 | 0
Cooling | 921.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 372.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2493.45 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 3742.46 | 0 | 0 | 0 | 0 | 0
Pumps | 192.25 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 172.84 | 0 | 0 | 0 | 815.28
Refrigeration | 163.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11223.5 | 28324.57 | 0 | 0 | 0 | 815.28
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 11223.5 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 11223.5 | 100
Total On-Site and Utility Electric Sources | 11223.5 | 100
Total Electricity End Uses | 11223.5 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | ASHRAE 90.1-1999_TABLE B-2_UNHEATED_EXT-SLAB | 0.3 | 1.627 | 2.69 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 342 | 90 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 2.62 | 0.49 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 15.4 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 2.62 | 0.49 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 74.2 | 2.62 | 0.49 | 0.49 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 25.2 | 2.62 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 23.8 | 2.62 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 25.2 | 2.62 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 23.8 | 2.62 | 0.49 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 21 | 2.62 | 0.49 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 21 | 2.62 | 0.49 | 0.49 | No | LOBBY_ZN_1_FLR_2_WALL_1
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 4.2 | 2.62 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_1_WALL_3
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 21 | 2.62 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_1_WALL_4
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 4.2 | 2.62 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_2_WALL_3
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 21 | 2.62 | 0.49 | 0.49 | No | BATHROOMS_ZN_1_FLR_2_WALL_4
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 53.2 | 2.62 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 19.6 | 2.62 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 53.2 | 2.62 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_1
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 19.6 | 2.62 | 0.49 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_2
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 33.6 | 2.62 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_1
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 72.8 | 2.62 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_2
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 33.6 | 2.62 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_1
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 72.8 | 2.62 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_2
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 3.3 | 0.49 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 53.2 | 2.62 | 0.49 | 0.49 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 53.2 | 2.62 | 0.49 | 0.49 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 12.6 | 2.62 | 0.49 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 49.41 | 2.62 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_WALL_2
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 33.6 | 2.62 | 0.49 | 0.49 | No | LIBRARY_MEDIA_CENTER_WALL_3
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 36.4 | 2.62 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_NORTH | 33.6 | 2.62 | 0.49 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_3
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2116539.81 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 7440823.18 | 0.8
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 329595.77 | 3.69
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 234773.35 | 3.69
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 150973.39 | 3.69
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 77394.68 | 3.69
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88069.91 | 3.69
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.61 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0 | 0 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0.01 | 2.83 | 0.03 | 1 | Zone Exhaust Fans
VAV_POD_1 FAN | Fan:VariableVolume | 0.32 | 750 | 23.05 | 54640.58 | 1 | Fan Energy
VAV_POD_2 FAN | Fan:VariableVolume | 0.32 | 750 | 22.69 | 53782.32 | 1 | Fan Energy
VAV_POD_3 FAN | Fan:VariableVolume | 0.32 | 750 | 25.09 | 59473.32 | 1 | Fan Energy
VAV_OTHER FAN | Fan:VariableVolume | 0.32 | 750 | 28.66 | 67928.1 | 1 | Fan Energy
PSZ-AC_1:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 19.91 | 37756.05 | 1 | Fan Energy
PSZ-AC_2:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 14.18 | 26893.9 | 1 | Fan Energy
PSZ-AC_3:7 FAN | Fan:ConstantVolume | 0.26 | 500 | 9.12 | 17294.39 | 1 | Fan Energy
PSZ-AC_4:8 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.68 | 8865.76 | 1 | Fan Energy
PSZ-AC_5:9 FAN | Fan:ConstantVolume | 0.26 | 500 | 5.32 | 10088.64 | 1 | Fan Energy
| Maximum Water Flow Rate [m3/s] | Design Coil Load [W] | U-Factor Times Area Value [W/K]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001905 | 87590.62 | 3101.09
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002223 | 102194.84 | 3618.14
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006324 | 290754.87 | 10293.98
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007453 | 342702.19 | 12133.14
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001362 | 62647.13 | 2217.98
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00189 | 86888.26 | 3076.22
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001344 | 61810.22 | 2188.35
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001647 | 75738.31 | 2681.46
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002916 | 134084.02 | 4747.15
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.003983 | 183124.44 | 6483.4
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001876 | 86271.32 | 3054.38
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00221 | 101607.95 | 3597.36
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006061 | 278697.11 | 9867.08
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.007306 | 335918.29 | 11892.96
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001334 | 61359.9 | 2172.41
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00187 | 86002.5 | 3044.86
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001344 | 61817.66 | 2188.61
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001649 | 75810.82 | 2684.03
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.002917 | 134108.03 | 4748
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.003991 | 183518.73 | 6497.36
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001878 | 86352.6 | 3057.26
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00222 | 102058.12 | 3613.3
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.006102 | 280577.67 | 9933.66
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.008801 | 404666.98 | 14326.96
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001365 | 62747.92 | 2221.55
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.00195 | 89650 | 3174
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001369 | 62959.53 | 2229.04
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001666 | 76583.89 | 2711.4
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.003126 | 143712.01 | 5088.03
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.005317 | 244485.92 | 8655.86
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.00429 | 197236.8 | 6983.04
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006477 | 297832.83 | 10544.57
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001768 | 81289.96 | 2878.02
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.002164 | 99490.27 | 3522.39
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.000945 | 43431.46 | 1537.66
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001329 | 61090.93 | 2162.88
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.005547 | 255053.2 | 9029.99
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006627 | 304693.64 | 10787.47
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.006746 | 310195.3 | 10982.26
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | 0.001136 | 52226.61 | 1849.05
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | 0.001569 | 72142.48 | 2554.16
VAV_POD_1_HEATC | 0.007332 | 337144.48 | 4339.15
VAV_POD_2_HEATC | 0.007344 | 337700.08 | 4328.1
VAV_POD_3_HEATC | 0.007264 | 334015.85 | 4394.55
VAV_OTHER_HEATC | 0.00589 | 270837.44 | 3824.61
| Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | Design Inlet Air Temperature [C] | Design Outlet Air Temperature [C] | Design Inlet Water Temperature [C] | Design Inlet Air Humidity Ratio | Design Outlet Air Humidity Ratio
VAV_POD_1_COOLC | 0.017699 | 23.05 | 20.35 | 12.8 | 7.22 | 0.008209 | 0.004105
VAV_POD_2_COOLC | 0.017431 | 22.69 | 20.37 | 12.8 | 7.22 | 0.008205 | 0.004102
VAV_POD_3_COOLC | 0.019199 | 25.09 | 20.22 | 12.8 | 7.22 | 0.008264 | 0.004132
VAV_OTHER_COOLC | 0.021585 | 28.66 | 19.93 | 12.8 | 7.22 | 0.008281 | 0.004141
Nominal Capacity [W]
PSZ-AC_1:5_HEATC | 586667.04
PSZ-AC_2:6_HEATC | 379275.21
PSZ-AC_3:7_HEATC | 268726.48
PSZ-AC_4:8_HEATC | 137759.38
PSZ-AC_5:9_HEATC | 156760.85
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 488432.7646 | 516.1025 | 1522.833 | 0 | 0.0057 | 305356.8013 | 180237.8808
February | 426968.5044 | 453.75 | 1385.4642 | 0 | 0.0052 | 277829.7352 | 157955.9327
March | 396725.1481 | 432.2022 | 1508.9354 | 0 | 0.0055 | 302660.2108 | 148397.5258
April | 250829.272 | 284.487 | 1188.9134 | 0 | 0.0042 | 238534.445 | 95552.0061
May | 192234.1731 | 233.7693 | 1240.4758 | 0 | 0.0042 | 248951.3036 | 75652.7112
June | 198429.7058 | 245.9028 | 1376.6777 | 0 | 0.0047 | 276301.0874 | 78798.6996
July | 157988.8548 | 194.8653 | 1076.8268 | 0 | 0.0037 | 216117.7254 | 62597.3763
August | 170178.8983 | 205.9091 | 1076.4049 | 0 | 0.0037 | 216020.4108 | 66812.9984
September | 190930.6831 | 226.8782 | 1121.0574 | 0 | 0.0039 | 224967.4332 | 74323.2107
October | 304851.2401 | 341.8816 | 1363.8749 | 0 | 0.0049 | 273619.6915 | 115534.8441
November | 424421.3754 | 456.5027 | 1491.4199 | 0 | 0.0055 | 299113.5959 | 157853.787
December | 471281.2073 | 500.6265 | 1524.7408 | 0 | 0.0057 | 305757.7013 | 174316.1105
Annual Sum or Average | 3673271.8271 | 4092.8773 | 15877.6242 | 0 | 0.0568 | 3185230.1413 | 1388033.0834
Minimum of Months | 157988.8548 | 194.8653 | 1076.4049 | 0 | 0.0037 | 216020.4108 | 62597.3763
Maximum of Months | 488432.7646 | 516.1025 | 1524.7408 | 0 | 0.0057 | 305757.7013 | 180237.8808
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1075960000000 | 627906.199 | 18-JAN-08:09 | 218037.744 | 151354.248 | 199650.337 | 0 | 9830.46 | 23884.224 | 20061.614 | 0 | 0 | 0 | 0 | 0 | 5087.572 | 0 | 0
February | 978963000000 | 622643.315 | 27-FEB-11:39 | 218037.744 | 160954.2 | 199650.337 | 0 | 16371.004 | 0 | 19860.973 | 0 | 0 | 0 | 0 | 0 | 7769.056 | 0 | 0
March | 1066460000000 | 618744.81 | 31-MAR-09:20 | 218037.744 | 160954.2 | 199650.337 | 0 | 15118.313 | 0 | 19720.087 | 0 | 0 | 0 | 0 | 0 | 5264.129 | 0 | 0
April | 840502000000 | 623574.172 | 19-APR-10:39 | 218037.744 | 160954.2 | 199650.337 | 0 | 17535.525 | 0 | 19627.311 | 0 | 0 | 0 | 0 | 0 | 7769.055 | 0 | 0
May | 877207000000 | 805472.845 | 30-MAY-10:50 | 218037.744 | 160954.2 | 199966.649 | 0 | 200260.863 | 0 | 19434.348 | 0 | 0 | 0 | 0 | 0 | 6819.041 | 0 | 0
June | 973577000000 | 906413.319 | 20-JUN-15:00 | 218037.744 | 146554.272 | 200239.623 | 0 | 316881.045 | 0 | 19432.378 | 0 | 0 | 0 | 0 | 0 | 5268.257 | 0 | 0
July | 761514000000 | 707031.866 | 21-JUL-16:00 | 121132.08 | 46799.232 | 199650.337 | 0 | 315330.969 | 0 | 19432.378 | 0 | 0 | 0 | 0 | 0 | 4686.87 | 0 | 0
August | 761171000000 | 691363.942 | 15-AUG-15:00 | 121132.08 | 81403.92 | 199650.337 | 0 | 264721.94 | 0 | 19432.378 | 0 | 0 | 0 | 0 | 0 | 5023.287 | 0 | 0
September | 792697000000 | 731296.862 | 07-SEP-15:00 | 218037.744 | 146475.648 | 199650.337 | 0 | 142429.437 | 0 | 19440.994 | 0 | 0 | 0 | 0 | 0 | 5262.702 | 0 | 0
October | 964129000000 | 645554.603 | 03-OCT-14:00 | 218037.744 | 145532.16 | 199650.337 | 0 | 57610.141 | 0 | 19458.296 | 0 | 0 | 0 | 0 | 0 | 5265.926 | 0 | 0
November | 1053960000000 | 630889.896 | 14-NOV-09:20 | 218037.744 | 150332.136 | 199650.337 | 0 | 13882.032 | 23884.224 | 19843.569 | 0 | 0 | 0 | 0 | 0 | 5259.854 | 0 | 0
December | 1077370000000 | 628134.716 | 18-DEC-08:39 | 218037.744 | 150332.136 | 199650.337 | 0 | 10910.587 | 23884.224 | 20061.738 | 0 | 0 | 0 | 0 | 0 | 5257.949 | 0 | 0
Annual Sum or Average | 11223500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 761171000000 | 618744.81 |  | 121132.08 | 46799.232 | 199650.337 | 0 | 9830.46 | 0 | 19432.378 | 0 | 0 | 0 | 0 | 0 | 4686.87 | 0 | 0
Maximum of Months | 1077370000000 | 906413.319 |  | 218037.744 | 160954.2 | 200239.623 | 0 | 316881.045 | 23884.224 | 20061.738 | 0 | 0 | 0 | 0 | 0 | 7769.056 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 291197.46 | 116690.28 | 0 | 407887.74
Cost per Total Building Area ($/m2) | 14.86 | 5.96 | 0 | 20.82
Cost per Net Conditioned Building Area ($/m2) | 14.86 | 5.96 | 0 | 20.82

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 13.7 | 93.5 | 17.5 | 99.6 | 88.5 | 13.5 | 4.1 | 218.1 | 6 | 23.5 | 255.5 | 39.4 | 43.9 | 5.7 | 9.7 | 1.11
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.34 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | 6.92 | 6.92 | 6.92 | 6.92 | 6.92 | 6.92 | 6.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.92 | 3.3
| SHGC | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.61 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
| Visible transmittance | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.775 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation | Carpet over heavy concrete and insulation
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 1659.534 | 1622.2585 | 3034.2695 | 1458.6266 | 1767.1989 | 2691.0301 | 1829.989 | 1536.7421 | 2326.1237 | 1036.5499 | 1503.2135 | 2232.9646 | 1417.9582 | 2219.4716 | 1209.2969 | 2116.5398
| PSZ-AC_1:5_COOLC DXCOIL | 606.326 | 589.1711 | 623.8011 | 589.0188 | 376.8128 | 557.8048 | 669.7683 | 592.9997 | 466.0597 | 415.3772 | 592.6818 | 458.835 | 590.4835 | 427.4697 | 580.2492 | 329.5958
| PSZ-AC_2:6_COOLC DXCOIL | 284.9143 | 284.2538 | 297.2947 | 256.4108 | 206.8889 | 278.3138 | 278.5555 | 257.7036 | 299.2177 | 234.2417 | 263.2564 | 290.3605 | 253.2981 | 273.1218 | 246.8619 | 234.7733
| PSZ-AC_3:7_COOLC DXCOIL | 332.1475 | 326.4431 | 285.8059 | 314.8445 | 176.7456 | 235.9604 | 339.148 | 307.8435 | 244.3448 | 176.3408 | 293.8123 | 228.825 | 290.9965 | 208.306 | 227.9555 | 150.9734
| PSZ-AC_4:8_COOLC DXCOIL | 116.2589 | 113.8846 | 103.9292 | 116.2506 | 73.1721 | 87.6942 | 89.743 | 114.2139 | 90.1037 | 75.6159 | 115.1208 | 89.7523 | 116.8103 | 86.4836 | 95.6836 | 77.3947
| PSZ-AC_5:9_COOLC DXCOIL | 150.8202 | 145.5929 | 141.3679 | 139.6336 | 82.1242 | 116.2664 | 175.2413 | 139.8214 | 110.872 | 84.8086 | 138.325 | 107.565 | 138.0127 | 99.9613 | 121.2233 | 88.0699
Heating (kW)
| HEATSYS1 BOILER | 6657.9797 | 7078.4808 | 8033.4726 | 6595.7841 | 5776.6798 | 7308.2157 | 9245.1308 | 7345.8224 | 6891.1046 | 6792.2392 | 7251.4464 | 6846.0378 | 7357.48 | 7041.6271 | 7223.0575 | 7440.8232
| PSZ-AC_1:5_HEATC | 283.5952 | 363.792 | 324.9701 | 392.3364 | 258.1408 | 358.493 | 540.2414 | 439.6924 | 411.8956 | 349.6507 | 513.3762 | 495.6277 | 552.7508 | 547.001 | 555.9764 | 586.667
| PSZ-AC_2:6_HEATC | 161.5492 | 210.2305 | 197.7523 | 219.4146 | 150.8816 | 202.1401 | 196.6091 | 250.9724 | 214.3265 | 210.0817 | 287.1592 | 251.8139 | 308.991 | 288.396 | 312.8875 | 379.2752
| PSZ-AC_3:7_HEATC | 155.3545 | 201.5669 | 190.5624 | 209.7131 | 128.9792 | 199.3425 | 273.5599 | 228.2572 | 215.9477 | 169.627 | 254.4978 | 247.1738 | 272.4015 | 266.5537 | 263.9652 | 268.7265
| PSZ-AC_4:8_HEATC | 54.3775 | 70.3196 | 62.1169 | 77.4328 | 53.397 | 67.7033 | 72.3876 | 84.6864 | 79.6321 | 72.7371 | 99.7167 | 96.9492 | 109.346 | 110.6666 | 113.7789 | 137.7594
| PSZ-AC_5:9_HEATC | 70.5427 | 89.8984 | 82.6379 | 93.0078 | 59.9297 | 86.2683 | 141.3513 | 103.6736 | 97.9868 | 81.5798 | 119.816 | 116.1904 | 129.1935 | 127.913 | 131.9148 | 156.7609
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| PSZ-AC_1:5_COOLC DXCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| PSZ-AC_2:6_COOLC DXCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| PSZ-AC_3:7_COOLC DXCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| PSZ-AC_4:8_COOLC DXCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| PSZ-AC_5:9_COOLC DXCOIL | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69 | 3.69
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb
Fan Max Flow Rate (m3/s )
| BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83
| VAV_POD_1 FAN | 22.76 | 23.69 | 29.03 | 22.29 | 19.61 | 26.73 | 34.43 | 24.18 | 27.9 | 23.21 | 23.49 | 26.89 | 23.74 | 25.65 | 23.67 | 23.05
| VAV_POD_2 FAN | 22.72 | 23.64 | 28.99 | 22.19 | 19.49 | 26.62 | 34.27 | 24 | 27.71 | 22.97 | 23.3 | 26.68 | 23.53 | 25.42 | 23.41 | 22.69
| VAV_POD_3 FAN | 24.99 | 25.87 | 31.26 | 24.5 | 21.86 | 29.11 | 36.03 | 26.3 | 30.49 | 25.44 | 25.63 | 29.45 | 25.88 | 28.08 | 25.85 | 25.09
| VAV_OTHER FAN | 33.1 | 33.79 | 40.16 | 31.97 | 28.08 | 37.89 | 39.27 | 33.87 | 39.16 | 31.07 | 32.85 | 37.52 | 32.83 | 35.12 | 32.27 | 28.66
| PSZ-AC_1:5 FAN | 24.42 | 23.73 | 25.12 | 23.72 | 21.37 | 25.63 | 40.46 | 23.88 | 28.15 | 21.96 | 23.87 | 27.72 | 23.78 | 25.82 | 23.37 | 19.91
| PSZ-AC_2:6 FAN | 14.89 | 15.23 | 17.96 | 14.43 | 12.5 | 16.81 | 16.83 | 15.57 | 18.08 | 14.15 | 15.26 | 17.54 | 15.3 | 16.5 | 14.91 | 14.18
| PSZ-AC_3:7 FAN | 13.38 | 13.15 | 14.73 | 12.68 | 10.68 | 14.25 | 20.49 | 12.4 | 14.76 | 10.65 | 11.83 | 13.82 | 11.72 | 12.58 | 11.09 | 9.12
| PSZ-AC_4:8 FAN | 4.68 | 4.59 | 4.8 | 4.68 | 4.42 | 4.84 | 5.42 | 4.6 | 5.44 | 4.57 | 4.64 | 5.42 | 4.7 | 5.22 | 4.78 | 4.68
| PSZ-AC_5:9 FAN | 6.07 | 5.86 | 6.39 | 5.62 | 4.96 | 6.17 | 10.59 | 5.63 | 6.7 | 5.12 | 5.57 | 6.5 | 5.56 | 6.04 | 5.54 | 5.32
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.088682 | 0.11446 | 0.082347 | 0.083608 | 0.058535 | 0.099045 | 0.15423 | 0.076142 | 0.036981 | 0.071854 | 0.085829 | 0.036984 | 0.061968 | 0.077069 | 0.060027 | 0.093403
| Total Cost ($/m2) | 20.05 | 23.87 | 17.96 | 18.23 | 9.23 | 19.59 | 27.19 | 13.91 | 6.78 | 10.51 | 6.78 | 6.48 | 10.56 | 12.96 | 9.62 | 14.86
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011453 | 0.0080899 | 0.0082975 | 0.0097084 | 0.0085569 | 0.0077684 | 0.0085397 | 0.0097026 | 0.0069166 | 0.008415 | 0.0028753 | 0.0069205 | 0.00789 | 0.0080878 | 0.0078697 | 0.0041198
| Total Cost ($/m2) | 0.44 | 1.11 | 0.93 | 2.08 | 0.61 | 0.98 | 2.11 | 3.59 | 1.52 | 2.77 | 1.52 | 2.38 | 5.74 | 4.58 | 6.92 | 5.96
Total Utility Costs
| Cost Intensity ($/m2) | 20.48 | 24.98 | 18.89 | 20.31 | 8.31 | 20.57 | 29.3 | 17.5 | 8.31 | 13.28 | 19.12 | 8.86 | 16.31 | 17.54 | 16.54 | 20.82
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1758938.8889 | 1391116.6667 | 1400891.6667 | 860383.3333 | 565961.1111 | 1057777.7778 | 439583.3333 | 801636.1111 | 672736.1111 | 239261.1111 | 577711.1111 | 521019.4444 | 510080.5556 | 397180.5556 | 303586.1111 | 255922.2222
| Interior Lighting | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222
| Exterior Lighting | 104397.2222 | 104358.3333 | 104338.8889 | 104322.2222 | 104241.6667 | 104219.4444 | 104275 | 104211.1111 | 104250 | 104044.4444 | 104227.7778 | 104166.6667 | 104158.3333 | 104136.1111 | 104075 | 103438.8889
| Interior Equipment | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625 | 692625
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 841486.1111 | 864175 | 996675 | 846611.1111 | 696011.1111 | 958413.8889 | 1188580.5556 | 943027.7778 | 1075675 | 834219.4445 | 966172.2222 | 1070727.7778 | 1018875 | 1065075 | 1035058.3333 | 1039572.2222
| Pumps | 57738.8889 | 60038.8889 | 104280.5556 | 54472.2222 | 58050 | 88561.1111 | 54938.8889 | 64277.7778 | 74163.8889 | 22113.8889 | 43419.4444 | 68505.5556 | 41216.6667 | 62608.3333 | 32338.8889 | 53402.7778
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 46450 | 46472.2222 | 46191.6667 | 46330.5556 | 46544.4444 | 46116.6667 | 46483.3333 | 46200 | 46041.6667 | 46391.6667 | 46077.7778 | 46011.1111 | 45861.1111 | 45919.4444 | 45813.8889 | 45283.3333
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4429030.5556 | 4086183.3334 | 4272400 | 3532141.6667 | 3090830.5556 | 3875111.1111 | 3453886.1111 | 3579377.7778 | 3592891.6667 | 2866052.7778 | 3357630.5556 | 3430455.5556 | 3340213.8889 | 3294938.8889 | 3140891.6667 | 3117638.8889
Gas (MJ)
| Heating | 141290 | 2059350 | 1575240 | 3546350 | 763180 | 1835680 | 4180140 | 6580960 | 3661860 | 5790730 | 9715710 | 6078060 | 13574540 | 10412950 | 16530740 | 27607270
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 61910 | 82070 | 72790 | 100040 | 94020 | 85980 | 109240 | 114340 | 111590 | 119470 | 126510 | 125380 | 137340 | 138380 | 153610 | 172840
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 747660 | 2685870 | 2192490 | 4190850 | 1401660 | 2466120 | 4833840 | 7239750 | 4317900 | 6454650 | 10386680 | 6747900 | 14256340 | 11095780 | 17228820 | 28324570
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 16692170 | 17396130 | 17573130 | 16906560 | 12528650 | 16416520 | 17267830 | 20125510 | 17252310 | 16772440 | 22474150 | 19097530 | 26281110 | 22957560 | 28536030 | 39548070
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 323.2023 | 255.6156 | 257.4117 | 158.0941 | 103.9945 | 194.365 | 80.7728 | 147.2994 | 123.6142 | 43.9639 | 106.1535 | 95.7365 | 93.7265 | 72.9813 | 55.7835 | 47.0253
| Interior Lighting (elec) | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078
| Exterior Lighting (elec) | 19.1828 | 19.1757 | 19.1721 | 19.169 | 19.1542 | 19.1502 | 19.1604 | 19.1486 | 19.1558 | 19.118 | 19.1517 | 19.1405 | 19.1389 | 19.1349 | 19.1236 | 19.0067
| Interior Equipment (elec) | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688 | 127.2688
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 154.6218 | 158.7908 | 183.1375 | 155.5635 | 127.891 | 176.1071 | 218.3999 | 173.2799 | 197.6536 | 153.2865 | 177.5327 | 196.7446 | 187.2167 | 195.7059 | 190.1904 | 191.0198
| Pumps (elec) | 10.6094 | 11.0321 | 19.1614 | 10.0092 | 10.6666 | 16.273 | 10.0949 | 11.8109 | 13.6275 | 4.0634 | 7.9783 | 12.5878 | 7.5735 | 11.5042 | 5.9422 | 9.8127
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 8.5351 | 8.5392 | 8.4876 | 8.5132 | 8.5525 | 8.4739 | 8.5412 | 8.4892 | 8.4601 | 8.5244 | 8.4667 | 8.4545 | 8.4269 | 8.4376 | 8.4182 | 8.3207
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 813.8276 | 750.8299 | 785.047 | 649.0256 | 567.9354 | 712.0457 | 634.6463 | 657.7052 | 660.1883 | 526.6328 | 616.9595 | 630.341 | 613.7592 | 605.44 | 577.134 | 572.8614
Gas (MJ/m2)
| Heating (gas) | 7.2116 | 105.1118 | 80.4022 | 181.0101 | 38.9537 | 93.6954 | 213.3595 | 335.9004 | 186.9059 | 295.566 | 495.9019 | 310.2317 | 692.8614 | 531.4899 | 843.7495 | 1409.1093
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.16 | 4.189 | 3.7153 | 5.1062 | 4.7989 | 4.3885 | 5.5757 | 5.8361 | 5.6957 | 6.0979 | 6.4572 | 6.3996 | 7.01 | 7.0631 | 7.8404 | 8.822
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 38.1615 | 137.0901 | 111.9074 | 213.9062 | 71.5425 | 125.8738 | 246.7252 | 369.5258 | 220.391 | 329.4533 | 530.149 | 344.4212 | 727.6613 | 566.3424 | 879.3804 | 1445.7212
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 851.9891 | 887.9201 | 896.9544 | 862.9318 | 639.4778 | 837.9196 | 881.3715 | 1027.231 | 880.5793 | 856.0862 | 1147.1085 | 974.7616 | 1341.4205 | 1171.7824 | 1456.5144 | 2018.5826
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1176.8315 | 1112.2313 | 1010.503 | 757.4619 | 865.4656 | 890.2299 | 880.4666 | 763.2028 | 814.9108 | 638.3582 | 657.8054 | 858.15 | 643.9576 | 681.0096 | 633.7454 | 627.9062
| Feb | 1217.1103 | 1010.4076 | 1051.1483 | 764.7851 | 846.3238 | 930.9411 | 995.9203 | 757.3274 | 916.9994 | 698.4214 | 658.3551 | 786.3992 | 638.9482 | 820.3522 | 634.6518 | 622.6433
| Mar | 1257.8822 | 1093.2402 | 1165.9018 | 868.1593 | 824.0114 | 985.7976 | 903.5236 | 974.5529 | 921.4336 | 755.5443 | 824.2425 | 922.4033 | 734.535 | 878.1517 | 636.0263 | 618.7448
| Apr | 1319.4001 | 1170.1282 | 1194.4514 | 1030.609 | 914.1988 | 1142.1454 | 993.8882 | 957.3579 | 1008.2792 | 705.9419 | 819.9719 | 949.6145 | 824.5388 | 863.1059 | 713.2974 | 623.5742
| May | 1440.8106 | 1471.2532 | 1328.0701 | 1194.5103 | 937.2182 | 1248.5783 | 1057.211 | 1236.767 | 1104.7047 | 897.058 | 1175.9498 | 1036.0792 | 1126.3207 | 936.3466 | 858.7539 | 805.4728
| Jun | 1552.528 | 1440.4802 | 1543.9318 | 1310.713 | 896.2898 | 1425.0487 | 1085.0162 | 1490.7532 | 1202.0797 | 899.6576 | 1493.4795 | 1146.2606 | 1368.3003 | 1157.4749 | 1176.9388 | 906.4133
| Jul | 1282.4203 | 1411.4254 | 1351.6998 | 1266.9644 | 751.2559 | 1197.3478 | 1000.5876 | 1383.2435 | 1028.5517 | 818.2313 | 1238.1345 | 967.9354 | 1195.7298 | 920.4838 | 985.8174 | 707.0319
| Aug | 1358.1359 | 1324.1325 | 1318.6825 | 1168.7024 | 867.2518 | 1188.9492 | 979.4451 | 1364.562 | 1023.1797 | 757.344 | 1253.8502 | 983.254 | 1147.2497 | 879.2907 | 950.3235 | 691.3639
| Sep | 1440.1893 | 1528.5923 | 1422.5372 | 1228.2208 | 1008.8511 | 1250.6194 | 1291.4504 | 1170.4933 | 1069.9065 | 941.1136 | 1127.5856 | 1072.6086 | 1090.1832 | 968.5288 | 1006.1618 | 731.2969
| Oct | 1410.5532 | 1303.0418 | 1199.0055 | 1093.5086 | 931.6256 | 1140.2238 | 1054.5003 | 1088.5685 | 992.6011 | 778.2299 | 959.4234 | 1011.8259 | 841.2741 | 900.9845 | 727.6066 | 645.5546
| Nov | 1273.4288 | 1182.5135 | 1112.0698 | 822.9204 | 870.6734 | 948.9567 | 928.1845 | 958.9042 | 897.2887 | 717.3848 | 962.1294 | 877.4772 | 743.2895 | 756.9234 | 706.1657 | 630.8899
| Dec | 1164.9452 | 1073.3831 | 1002.1583 | 792.7186 | 879.9841 | 930.9794 | 881.7328 | 727.0795 | 789.3144 | 621.0422 | 657.5115 | 761.5709 | 640.8891 | 677.1925 | 638.1067 | 628.1347
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:09 | 26-JAN-16:10 | 24-JAN-16:10 | 26-JAN-12:00 | 18-JAN-12:00 | 05-JAN-11:50 | 09-JAN-11:39 | 25-JAN-14:00 | 27-JAN-12:00 | 17-JAN-12:00 | 27-JAN-11:39 | 19-JAN-16:00 | 20-JAN-08:09 | 13-JAN-11:39 | 18-JAN-08:09
| Feb | 23-FEB-11:00 | 23-FEB-13:00 | 28-FEB-16:00 | 21-FEB-13:00 | 13-FEB-11:00 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-12:00 | 14-FEB-16:10 | 22-FEB-11:39 | 28-FEB-10:00 | 07-FEB-14:00 | 17-FEB-11:39 | 02-FEB-14:00 | 24-FEB-11:39 | 27-FEB-11:39
| Mar | 13-MAR-15:09 | 29-MAR-11:00 | 17-MAR-15:09 | 28-MAR-15:00 | 30-MAR-11:00 | 31-MAR-15:00 | 01-MAR-12:00 | 09-MAR-16:10 | 02-MAR-16:10 | 29-MAR-15:00 | 31-MAR-15:09 | 30-MAR-15:00 | 23-MAR-13:00 | 30-MAR-15:00 | 16-MAR-10:39 | 31-MAR-09:20
| Apr | 03-APR-13:00 | 20-APR-15:09 | 26-APR-15:09 | 13-APR-15:09 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-15:09 | 04-APR-15:00 | 21-APR-15:00 | 14-APR-13:00 | 03-APR-13:00 | 25-APR-15:09 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-13:00 | 19-APR-10:39
| May | 24-MAY-14:00 | 18-MAY-14:09 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-09:09 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-15:00 | 31-MAY-15:00 | 30-MAY-10:50
| Jun | 26-JUN-15:09 | 13-JUN-14:00 | 28-JUN-15:00 | 08-JUN-15:09 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-15:00 | 29-JUN-15:09 | 28-JUN-15:09 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-15:09 | 26-JUN-15:09 | 14-JUN-15:09 | 20-JUN-15:00
| Jul | 10-JUL-12:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-11:00 | 10-JUL-09:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-11:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-12:00 | 18-JUL-13:00 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:09 | 21-JUL-16:00
| Aug | 21-AUG-13:00 | 31-AUG-10:00 | 01-AUG-15:00 | 17-AUG-14:00 | 08-AUG-09:00 | 02-AUG-11:00 | 15-AUG-11:00 | 17-AUG-11:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:50 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-15:00
| Sep | 26-SEP-15:00 | 15-SEP-14:39 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-14:00 | 20-SEP-15:00 | 28-SEP-15:09 | 08-SEP-15:09 | 20-SEP-15:09 | 13-SEP-15:00 | 06-SEP-10:00 | 06-SEP-15:00 | 14-SEP-15:09 | 11-SEP-15:09 | 07-SEP-15:09 | 07-SEP-15:00
| Oct | 06-OCT-15:09 | 30-OCT-12:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:09 | 31-OCT-12:00 | 03-OCT-10:39 | 11-OCT-15:00 | 17-OCT-15:00 | 31-OCT-10:00 | 05-OCT-15:09 | 06-OCT-15:09 | 06-OCT-15:00 | 27-OCT-11:00 | 03-OCT-14:00
| Nov | 01-NOV-11:39 | 27-NOV-16:00 | 13-NOV-16:10 | 22-NOV-16:10 | 20-NOV-12:00 | 10-NOV-16:40 | 16-NOV-15:00 | 03-NOV-11:00 | 08-NOV-16:10 | 03-NOV-11:39 | 02-NOV-11:00 | 10-NOV-13:00 | 02-NOV-12:00 | 21-NOV-11:39 | 09-NOV-11:39 | 14-NOV-09:20
| Dec | 15-DEC-16:10 | 19-DEC-14:00 | 11-DEC-16:10 | 26-DEC-12:00 | 19-DEC-12:00 | 05-DEC-16:30 | 14-DEC-16:49 | 08-DEC-10:00 | 08-DEC-14:00 | 13-DEC-11:39 | 12-DEC-12:00 | 21-DEC-14:09 | 26-DEC-16:40 | 22-DEC-16:40 | 01-DEC-16:19 | 18-DEC-08:39
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28
| Total Building | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28 | 815.28
Emissions
| Carbon Equivalent (kg) | 1228142.9132 | 1411424.6184 | 1329269.0264 | 1163601.1743 | 386488.1839 | 1351449.4101 | 490808.441 | 1096466.6606 | 1545552.6583 | 325141.3115 | 1977417.7271 | 1523016.6345 | 1400412.6525 | 1404181.1624 | 1385787.9224 | 1388033.0834
| CO2 (kg) | 2851565.0016 | 3560069.1024 | 3147290.451 | 2687733.3877 | 1037402.8142 | 3224079.5274 | 1329496.9734 | 2543286.5944 | 3644820.9817 | 832160.4342 | 4671433.2533 | 3616809.0897 | 3378585.8336 | 3378656.4432 | 3376162.7926 | 3673271.8271
| NOX (kg) | 4995.7018 | 4622.4969 | 5230.0712 | 4966.6168 | 891.5875 | 5193.1996 | 1150.8697 | 4673.3429 | 6204.51 | 1102.0449 | 8012.1115 | 6048.1715 | 5484.2346 | 5496.1023 | 5337.8089 | 4092.8773
| SO2 (kg) | 18958.2237 | 19491.8134 | 17180.7592 | 12398.9359 | 8994.3237 | 21316.8794 | 10051.6879 | 13068.0974 | 15690.5974 | 2216.9598 | 22630.5207 | 14981.9167 | 7887.2627 | 8800.8553 | 7417.6274 | 15877.6242
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0865 | 0.055 | 0.0468 | 0.0457 | 0.0042 | 0.0402 | 0.005 | 0.0534 | 0.0616 | 0.0093 | 0.0693 | 0.0591 | 0.059 | 0.0622 | 0.0559 | 0.0568
| Water Environmental Factors (m3) | 2346.3145 | 6648.6989 | 126909 | 22053.3 | 54268.1 | 106310 | 60642.5 | 812.6531 | 16314.6 | 29281.9 | 5209.1613 | 15577 | 5182.1438 | 208715 | 4872.9076 | 3185.2301

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | HoursPerDay | HoursPerWeek | HoursPerYear
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1756.39
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 2956.57
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 2203.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 8.35 | 41.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1833.39
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 8.35 | 41.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 12.35 | 61.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1692.57
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 12.35 | 61.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6205
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 1599.88
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8760
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25 | 0
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5 | 1752
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7800
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5 | 0
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8760
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 8760
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8760
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 8760
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 569400
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8 |  | 35040
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84 |  | 113880
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84 |  | 58692
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 586920
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8 |  | 140160
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84 |  | 2137.86
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 1 to 24 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8 | 3650
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3650
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 1 to 24 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 158410 | bar: 1 1 to 24 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 1 to 24 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 1 to 24 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 140160
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 249660
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 271560
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6152.86
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3650
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 |  | 1051200
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454 |  | 438
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 |  | 1752
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 350400
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 |  | 481800
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 |  | 438
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 |  | 1752
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 350400
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744 |  | 481800
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744 |  | 243.33
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660 |  | 365
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 74668.57
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744 |  | 2774
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744 |  | 251850
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 525600
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 |  | 525600 | bar: 1 1 to 24 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 192720
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17592
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160
Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4
Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6
Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720
Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240
Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4
Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6
Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720
Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696