## BuildingSummary
Building Summary Strip Mall new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Strip Mall
| Available Fuel Types | gas, electricity
| Principal Building Activity | Strip Mall
Form
| Total Floor Area (ft2) | 22500 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 4.0 (0.33 per store)
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 10 stores
| Floor to Ceiling Height (ft) | 17
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 12746.08
| Net Dimensions - Total Area (ft2) | 10906.86
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 22500
| Net Dimensions - Total Area (ft2) | 22500
| Roof to Skin Ratio | 0.64
Window
| Dimensions - Total Area (ft2) | South: 1,338 East: 0.00 North: 0.00 West: 0.00 Total: 1,338
| Operable area (ft2) | 0
Skylights/TDD
| Dimensions - Total Area (ft2) | 0
| Operable area (ft2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (ft2) | 22500
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 6 inch wood
| Dimensions - Total Area (ft2) | 45000
| Thermal Properties (lb/ft2 ) | 16.6
Air Barrier System
| Infiltration (ACH) | 0.33 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºF ) | N/A
| Water Consumption (gal ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (ft2) | Volume (ft3) | Floor-to-Ceiling Height (ft) | Gross Wall Area (ft2) | Window Glass Area (ft2) | People (ft2/per) | People | Lights (W/ft2) | Elec Plug and Process (W/ft2) | Gas Plug and Process (W/ft2) | SWH (gal/h) | Ventilation (cfm/Person) | Ventilation (cfm/ft2) | Ventilation Total (cfm) | Exhaust (cfm) | Infiltration (ACH)
LGStore1 | Yes | 1 | 3750 | 63750 | 17 | 2974.0683 | 223.3511 | 125 | 30 | 2.23 | 0.4 | 0 | 0 | 0 | 0.3 | 1125 | 0 | 0.37663
SMStore1 | Yes | 1 | 1875 | 31875 | 17 | 849.7031 | 111.6217 | 125 | 15 | 2.23 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.30523
SMStore2 | Yes | 1 | 1875 | 31875 | 17 | 849.7031 | 111.6217 | 125 | 15 | 1.7 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.30523
SMStore3 | Yes | 1 | 1875 | 31875 | 17 | 849.7031 | 111.6217 | 125 | 15 | 1.7 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.30523
SMStore4 | Yes | 1 | 1875 | 31875 | 17 | 849.7031 | 111.6217 | 125 | 15 | 1.7 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.30523
LGStore2 | Yes | 1 | 3750 | 63750 | 17 | 1699.5137 | 223.3511 | 125 | 30 | 1.28 | 0.4 | 0 | 0 | 0 | 0.3 | 1125 | 0 | 0.30524
SMStore5 | Yes | 1 | 1875 | 31875 | 17 | 849.7031 | 111.6217 | 125 | 15 | 1.28 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.30523
SMStore6 | Yes | 1 | 1875 | 31875 | 17 | 849.7031 | 111.6217 | 125 | 15 | 1.28 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.30523
SMStore7 | Yes | 1 | 1875 | 31875 | 17 | 849.7031 | 111.6217 | 125 | 15 | 1.28 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.30523
SMStore8 | Yes | 1 | 1875 | 31875 | 17 | 2124.3653 | 111.6217 | 125 | 15 | 1.28 | 0.4 | 0 | 0 | 0 | 0.3 | 562.5 | 0 | 0.44802
Total Conditioned Zones |  |  | 22500 | 382500 |  | 12745.8687 | 1339.6762 |  | 180
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1602.02 | 766.4 | 766.4
Net Site Energy | 1602.02 | 766.4 | 766.4
Total Source Energy | 5292.4 | 2531.86 | 2531.86
Net Source Energy | 5292.4 | 2531.86 | 2531.86
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 9.67 | 0 | 0 | 0 | 0
Cooling | 607.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 59.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 298.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1592.36 | 9.67 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1592.36 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1592.36 | 100
Total On-Site and Utility Electric Sources | 1592.36 | 100
Total Electricity End Uses | 1592.36 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 48850.82 | 2.78
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25634.91 | 2.96
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24778.35 | 2.96
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24454.98 | 2.96
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24006.7 | 2.96
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39290.39 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21029.84 | 2.96
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20880.13 | 2.96
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20786.24 | 2.96
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20117.97 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.02 | 2892.05 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.1 | 1578.38 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.01 | 1440.09 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1406.86 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.97 | 1381.07 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.58 | 2260.32 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.85 | 1209.82 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.84 | 1201.2 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.84 | 1195.8 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.81 | 1157.36 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 29479.44
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 13734.48
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 13476.31
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 13441.88
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 13478.33
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 25994.99
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 13487.12
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 13504.82
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 13872.71
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 16778.72
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19819.3964 | 34.7319 | 131.8454 | 0 | 0.0006 | 16317.4998 | 8537.0371
February | 18354.5556 | 32.2923 | 123.1031 | 0 | 0.0006 | 15235.6361 | 7918.8306
March | 21215.1683 | 37.329 | 142.3196 | 0 | 0.0006 | 17613.9314 | 9153.3922
April | 22400.5859 | 39.5034 | 150.9688 | 0 | 0.0007 | 18684.4551 | 9673.7199
May | 25320.6636 | 44.6557 | 170.6705 | 0 | 0.0008 | 21122.8019 | 10935.0359
June | 26365.8012 | 46.4989 | 177.7151 | 0 | 0.0008 | 21994.6682 | 11386.3912
July | 27965.1656 | 49.3195 | 188.4954 | 0 | 0.0009 | 23328.8772 | 12077.0962
August | 28363.3521 | 50.0218 | 191.1793 | 0 | 0.0009 | 23661.0492 | 12249.0578
September | 26163.5063 | 46.1421 | 176.3515 | 0 | 0.0008 | 21825.9114 | 11299.0277
October | 24519.2386 | 43.2423 | 165.2686 | 0 | 0.0008 | 20454.2435 | 10588.9308
November | 21393.1989 | 37.7281 | 144.1896 | 0 | 0.0007 | 17845.4287 | 9238.8062
December | 19514.6416 | 34.3744 | 131.2073 | 0 | 0.0006 | 16238.6638 | 8423.453
Annual Sum or Average | 281395.2742 | 495.8392 | 1893.314 | 0 | 0.0086 | 234323.1662 | 121480.7787
Minimum of Months | 18354.5556 | 32.2923 | 123.1031 | 0 | 0.0006 | 15235.6361 | 7918.8306
Maximum of Months | 28363.3521 | 50.0218 | 191.1793 | 0 | 0.0009 | 23661.0492 | 12249.0578
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 110886000000 | 101763.284 | 06-JAN-13:00 | 32837.857 | 8089.532 | 15722.949 | 0 | 45112.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 103535000000 | 107590.761 | 25-FEB-13:00 | 32837.857 | 8089.532 | 15722.949 | 0 | 50940.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 119696000000 | 109241.067 | 13-MAR-15:39 | 32837.857 | 8089.532 | 15722.949 | 0 | 52590.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 126971000000 | 114536.262 | 01-APR-15:39 | 32837.857 | 8089.532 | 15722.949 | 0 | 57885.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 143541000000 | 123301.198 | 24-MAY-14:00 | 32837.857 | 8089.532 | 15722.949 | 0 | 66650.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 149466000000 | 128512.052 | 27-JUN-14:00 | 32837.857 | 8089.532 | 15722.949 | 0 | 71861.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 158533000000 | 124666.993 | 13-JUL-14:00 | 32837.857 | 8089.532 | 15722.949 | 0 | 68016.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 160790000000 | 129616.98 | 21-AUG-14:50 | 32837.857 | 8089.532 | 15722.949 | 0 | 72966.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 148319000000 | 123637.819 | 11-SEP-14:00 | 32837.857 | 8089.532 | 15722.949 | 0 | 66987.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 138998000000 | 121168.628 | 06-OCT-14:00 | 32837.857 | 8089.532 | 15722.949 | 0 | 64518.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 121270000000 | 110190.178 | 07-NOV-15:09 | 32837.857 | 8089.532 | 15722.949 | 0 | 53539.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 110351000000 | 100884.47 | 19-DEC-14:30 | 32837.857 | 8089.532 | 15722.949 | 0 | 44234.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1592360000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 103535000000 | 100884.47 |  | 32837.857 | 8089.532 | 15722.949 | 0 | 44234.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 160790000000 | 129616.98 |  | 32837.857 | 8089.532 | 15722.949 | 0 | 72966.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 38275.59 | 110.46 | 0 | 38386.05
Cost per Total Building Area ($/m2) | 18.31 | 0.05 | 0 | 18.36
Cost per Net Conditioned Building Area ($/m2) | 18.31 | 0.05 | 0 | 18.36
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1557.72 | 745.21 | 745.21
Net Site Energy | 1557.72 | 745.21 | 745.21
Total Source Energy | 244.75 | 117.09 | 117.09
Net Source Energy | 244.75 | 117.09 | 117.09
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 224.13 | 0 | 0 | 0 | 0
Cooling | 380.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 266.74 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1333.59 | 224.13 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1333.59 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1333.59 | 100
Total On-Site and Utility Electric Sources | 1333.59 | 100
Total Electricity End Uses | 1333.59 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 43479.8 | 2.78
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22885.36 | 2.96
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21019.47 | 2.96
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20620.29 | 2.96
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20352.62 | 2.96
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33396.55 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17846.16 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17709.27 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17629.73 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20433.36 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.86 | 2662.27 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.01 | 1447.37 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.88 | 1260.98 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.86 | 1222.07 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.84 | 1195.6 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.34 | 1921.26 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.72 | 1026.66 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.71 | 1018.79 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.71 | 1014.21 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.82 | 1175.5 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 47566.31
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 23058.83
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 22943.68
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 22932.3
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 22945.67
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 43847.77
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 22947.62
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 22952.54
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 23119.15
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 26435.68
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23913.7946 | 30.0345 | 116.7032 | 0 | 0.0003 | 39803.1374 | 9349.9163
February | 21169.1785 | 26.5883 | 103.3222 | 0 | 0.0003 | 35239.3898 | 8276.9362
March | 22797.1943 | 29.5324 | 123.8632 | 0 | 0.0004 | 42249.6993 | 9029.3912
April | 23732.7722 | 31.1061 | 134.012 | 0 | 0.0004 | 45713.09 | 9446.5704
May | 28559.0211 | 37.5208 | 162.5122 | 0 | 0.0005 | 55435.2317 | 11379.0899
June | 32055.8601 | 42.1345 | 182.6839 | 0 | 0.0005 | 62316.1785 | 12774.8899
July | 34578.5745 | 45.4504 | 197.0607 | 0 | 0.0006 | 67220.3027 | 13780.2412
August | 34276.9546 | 45.0539 | 195.3418 | 0 | 0.0005 | 66633.9574 | 13660.0397
September | 29618.2997 | 38.9302 | 168.7882 | 0 | 0.0005 | 57576.1347 | 11803.4349
October | 25912.9652 | 33.9814 | 146.5718 | 0 | 0.0004 | 49997.454 | 10316.6628
November | 22095.7808 | 28.7618 | 121.9855 | 0 | 0.0003 | 41609.8248 | 8769.3713
December | 23026.2741 | 29.0518 | 114.2211 | 0 | 0.0003 | 38957.2546 | 9019.9284
Annual Sum or Average | 321736.6697 | 418.1462 | 1767.0658 | 0 | 0.005 | 602751.6551 | 127606.4723
Minimum of Months | 21169.1785 | 26.5883 | 103.3222 | 0 | 0.0003 | 35239.3898 | 8276.9362
Maximum of Months | 34578.5745 | 45.4504 | 197.0607 | 0 | 0.0006 | 67220.3027 | 13780.2412
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 88064500000 | 89856.675 | 03-JAN-13:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 34984.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 77967200000 | 90032.138 | 23-FEB-15:30 | 32837.857 | 8089.532 | 13944.715 | 0 | 35160.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 93477500000 | 95672.911 | 25-MAR-16:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 40800.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 101140000000 | 110182.78 | 29-APR-14:50 | 32837.857 | 8089.532 | 13944.715 | 0 | 55310.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 122651000000 | 116563.718 | 18-MAY-14:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 61691.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 137875000000 | 117165.724 | 13-JUN-14:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 62293.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 148725000000 | 123125.861 | 18-JUL-12:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 68253.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 147428000000 | 122931.778 | 31-AUG-15:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 68059.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 127387000000 | 122034.617 | 16-SEP-14:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 67162.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 110619000000 | 105753.502 | 06-OCT-15:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 50881.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 92061800000 | 93746.226 | 03-NOV-15:09 | 32837.857 | 8089.532 | 13944.715 | 0 | 38874.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 86193000000 | 92257.987 | 02-DEC-14:00 | 32837.857 | 8089.532 | 13944.715 | 0 | 37385.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1333590000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 77967200000 | 89856.675 |  | 32837.857 | 8089.532 | 13944.715 | 0 | 34984.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 148725000000 | 123125.861 |  | 32837.857 | 8089.532 | 13944.715 | 0 | 68253.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 46045.07 | 1803.13 | 0 | 47848.2
Cost per Total Building Area ($/m2) | 22.03 | 0.86 | 0 | 22.89
Cost per Net Conditioned Building Area ($/m2) | 22.03 | 0.86 | 0 | 22.89
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1552.42 | 742.67 | 742.67
Net Site Energy | 1552.42 | 742.67 | 742.67
Total Source Energy | 4600.88 | 2201.04 | 2201.04
Net Source Energy | 4600.88 | 2201.04 | 2201.04
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 149.41 | 0 | 0 | 0 | 0
Cooling | 391.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 325.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1403.01 | 149.41 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1403.01 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1403.01 | 100
Total On-Site and Utility Electric Sources | 1403.01 | 100
Total Electricity End Uses | 1403.01 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 6.88 | 0.25 | 0.25 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.25 | 0.25 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35115.99 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18900.2 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17931.78 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17753.09 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17444.95 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29275.98 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15498.22 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15431.43 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15528.79 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16253.21 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.12 | 3030.51 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.14 | 1631.09 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.08 | 1547.51 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.07 | 1532.09 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.05 | 1505.5 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.73 | 2474.17 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1328.25 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1321.63 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1331.22 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1402.65 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 39174.49
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 19401.5
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 19348.69
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 19343.06
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 19351.65
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 36818.25
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 19352.71
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 19353.28
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 19436.82
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 21813.49
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19420.2659 | 31.2612 | 98.7014 | 0 | 0.0003 | 729026.0621 | 8100.0046
February | 17655.9454 | 28.5328 | 90.5419 | 0 | 0.0002 | 668765.1306 | 7375.4119
March | 21000.7719 | 35.0077 | 115.4319 | 0 | 0.0003 | 852666.139 | 8880.8019
April | 21654.481 | 36.4445 | 121.5358 | 0 | 0.0003 | 897771.5821 | 9192.3393
May | 24769.3718 | 41.8524 | 140.2153 | 0 | 0.0004 | 1035763.0026 | 10531.3469
June | 29238.3764 | 49.4176 | 165.6149 | 0 | 0.0004 | 1223389.12 | 12432.8772
July | 30907.7672 | 52.2391 | 175.0709 | 0 | 0.0005 | 1293239.5975 | 13142.7432
August | 30631.2335 | 51.7718 | 173.5045 | 0 | 0.0005 | 1281668.9026 | 13025.1543
September | 27123.0891 | 45.8424 | 153.6333 | 0 | 0.0004 | 1134881.4899 | 11533.405
October | 22623.8708 | 38.138 | 127.425 | 0 | 0.0003 | 941276.9393 | 9610.1142
November | 19333.0019 | 32.2091 | 106.1307 | 0 | 0.0003 | 783959.4554 | 8173.6593
December | 20100.044 | 31.9744 | 99.3991 | 0 | 0.0003 | 734159.2119 | 8344.9925
Annual Sum or Average | 284458.2188 | 474.691 | 1567.2049 | 0 | 0.0043 | 11576600 | 120342.8502
Minimum of Months | 17655.9454 | 28.5328 | 90.5419 | 0 | 0.0002 | 668765.1306 | 7375.4119
Maximum of Months | 30907.7672 | 52.2391 | 175.0709 | 0 | 0.0005 | 1293239.5975 | 13142.7432
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 88353700000 | 79847.452 | 28-JAN-14:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 21815.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 81050400000 | 85356.038 | 28-FEB-15:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 27324.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 103338000000 | 99335.342 | 17-MAR-15:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 41303.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 108805000000 | 101994.225 | 01-APR-16:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 43962.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 125528000000 | 119993.265 | 27-MAY-15:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 61961.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 148268000000 | 132614.521 | 28-JUN-16:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 74582.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 156733000000 | 131561.846 | 19-JUL-16:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 73529.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 155331000000 | 132551.829 | 01-AUG-16:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 74519.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 137541000000 | 123240.251 | 09-SEP-15:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 65208.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 114077000000 | 101584.613 | 02-OCT-15:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 43552.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 95011300000 | 93312.693 | 13-NOV-15:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 35280.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 88975800000 | 77728.931 | 09-DEC-15:00 | 32837.857 | 8089.532 | 17104.629 | 0 | 19696.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1403010000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 81050400000 | 77728.931 |  | 32837.857 | 8089.532 | 17104.629 | 0 | 19696.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 156733000000 | 132614.521 |  | 32837.857 | 8089.532 | 17104.629 | 0 | 74582.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40857.76 | 1214.96 | 0 | 42072.72
Cost per Total Building Area ($/m2) | 19.55 | 0.58 | 0 | 20.13
Cost per Net Conditioned Building Area ($/m2) | 19.55 | 0.58 | 0 | 20.13
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1607.87 | 769.2 | 769.2
Net Site Energy | 1607.87 | 769.2 | 769.2
Total Source Energy | 4389.24 | 2099.8 | 2099.8
Net Source Energy | 4389.24 | 2099.8 | 2099.8
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 448.79 | 0 | 0 | 0 | 0
Cooling | 208.9 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 264.09 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1159.09 | 448.79 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1159.09 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1159.09 | 100
Total On-Site and Utility Electric Sources | 1159.09 | 100
Total Electricity End Uses | 1159.09 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38512.18 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20452.59 | 2.96
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18617.88 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18203.72 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17934.14 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34546.7 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18265.84 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18289.94 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18587.18 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22921.96 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.72 | 2451.79 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.94 | 1346.26 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.81 | 1160.41 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.78 | 1120.12 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.77 | 1093.35 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.39 | 1987.42 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.74 | 1051.99 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.74 | 1052.19 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.75 | 1069.29 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1328.88 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 52943.03
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 25332.06
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 25143.72
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 25126.14
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 25151.5
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 48462.86
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 25154.3
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 25157.57
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 25430.93
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 29482.39
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22695.0309 | 36.9987 | 80.4842 | 0 | 0.0003 | 143104.5825 | 9369.2324
February | 19459.814 | 32.4465 | 72.5502 | 0 | 0.0003 | 129006.5939 | 8100.3068
March | 18670.9946 | 33.7473 | 82.4336 | 0 | 0.0003 | 146612.5095 | 8013.5584
April | 18165.3866 | 34.0805 | 86.3147 | 0 | 0.0003 | 153527.9659 | 7911.7262
May | 20029.4169 | 38.5858 | 100.1138 | 0 | 0.0004 | 178081.9097 | 8816.6873
June | 22363.966 | 43.1841 | 112.2773 | 0 | 0.0004 | 199719.2081 | 9853.6442
July | 24375.4495 | 47.0681 | 122.3751 | 0 | 0.0004 | 217681.1601 | 10739.8962
August | 24439.0048 | 47.1917 | 122.6984 | 0 | 0.0004 | 218256.2955 | 10767.9789
September | 21236.951 | 41.0014 | 106.5871 | 0 | 0.0004 | 189597.4747 | 9356.4739
October | 18244.0837 | 34.4751 | 87.8989 | 0 | 0.0003 | 156348.0964 | 7968.8024
November | 17765.4366 | 31.8192 | 77.0073 | 0 | 0.0003 | 136958.6773 | 7597.9887
December | 21030.9395 | 35.2867 | 79.4892 | 0 | 0.0003 | 141347.9437 | 8774.6757
Annual Sum or Average | 248476.4743 | 455.8852 | 1130.2299 | 0 | 0.0042 | 2010242.4174 | 107270.9713
Minimum of Months | 17765.4366 | 31.8192 | 72.5502 | 0 | 0.0003 | 129006.5939 | 7597.9887
Maximum of Months | 24439.0048 | 47.1917 | 122.6984 | 0 | 0.0004 | 218256.2955 | 10767.9789
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 82512700000 | 62865.072 | 23-JAN-16:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 8275.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 74384000000 | 68445.386 | 18-FEB-16:19 | 32837.857 | 8089.532 | 13661.706 | 0 | 13856.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 84535400000 | 76955.489 | 28-MAR-15:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 22366.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 88522800000 | 93820.221 | 15-APR-15:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 39231.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 102680000000 | 100481.653 | 15-MAY-14:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 45892.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 115156000000 | 108834.676 | 19-JUN-14:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 54245.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 125513000000 | 120004.874 | 03-JUL-14:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 65415.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 125845000000 | 112538.28 | 17-AUG-14:30 | 32837.857 | 8089.532 | 13661.706 | 0 | 57949.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 109320000000 | 103915.613 | 11-SEP-13:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 49326.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 90148800000 | 95179.435 | 12-OCT-15:00 | 32837.857 | 8089.532 | 13661.706 | 0 | 40590.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 78969100000 | 70314.878 | 22-NOV-15:20 | 32837.857 | 8089.532 | 13661.706 | 0 | 15725.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 81499900000 | 60498.23 | 13-DEC-15:30 | 32837.857 | 8089.532 | 13661.706 | 0 | 5909.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1159090000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 74384000000 | 60498.23 |  | 32837.857 | 8089.532 | 13661.706 | 0 | 5909.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 125845000000 | 120004.874 |  | 32837.857 | 8089.532 | 13661.706 | 0 | 65415.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32894.33 | 4255.43 | 0 | 37149.76
Cost per Total Building Area ($/m2) | 15.74 | 2.04 | 0 | 17.77
Cost per Net Conditioned Building Area ($/m2) | 15.74 | 2.04 | 0 | 17.77
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1079.62 | 516.49 | 516.49
Net Site Energy | 1079.62 | 516.49 | 516.49
Total Source Energy | 3106.93 | 1486.34 | 1486.34
Net Source Energy | 3106.93 | 1486.34 | 1486.34
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 117.07 | 0 | 0 | 0 | 0
Cooling | 69.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 207.1 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 962.55 | 117.07 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 962.55 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 962.55 | 100
Total On-Site and Utility Electric Sources | 962.55 | 100
Total Electricity End Uses | 962.55 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25848.25 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13067.96 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11058.1 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10595.06 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10296.73 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18031.72 | 3.05
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9198.94 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9143.53 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9193.22 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10255.96 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.56 | 2230.7 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.79 | 1127.76 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.67 | 954.31 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.64 | 914.35 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.62 | 888.61 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.08 | 1540.35 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.55 | 788.17 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.55 | 782.72 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.55 | 787.62 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.62 | 885.09 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 34019.5
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 16596.23
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 16367
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 16333.75
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 16381.52
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 31485.46
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 16390.15
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 16390.81
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 16676.97
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 18870.41
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8093.2657 | 6.9989 | 62.4462 | 0 | 0 | 376747.1079 | 2991.6137
February | 7149.5691 | 6.176 | 56.3828 | 0 | 0 | 340170.7097 | 2646.4996
March | 7718.2456 | 6.65 | 63.944 | 0 | 0 | 385801.1562 | 2866.3883
April | 7150.7067 | 6.1495 | 61.2956 | 0 | 0 | 369830.1479 | 2661.8821
May | 7224.7952 | 6.196 | 65.0167 | 0 | 0 | 392292.6654 | 2698.8772
June | 7032.5187 | 6.0237 | 64.6127 | 0 | 0 | 389859.7622 | 2631.0974
July | 7505.5335 | 6.4236 | 69.899 | 0 | 0 | 421759.5026 | 2810.937
August | 8076.1799 | 6.912 | 75.2111 | 0 | 0 | 453811.5674 | 3024.6455
September | 7434.2279 | 6.3634 | 69.0784 | 0 | 0 | 416807.3916 | 2783.7542
October | 7236.952 | 6.2017 | 65.9676 | 0 | 0 | 398033.165 | 2705.9859
November | 7113.0867 | 6.1146 | 61.4412 | 0 | 0 | 370710.2683 | 2649.3059
December | 7788.3486 | 6.7202 | 62.7633 | 0 | 0 | 378671.1844 | 2887.049
Annual Sum or Average | 89523.4295 | 76.9296 | 778.0587 | 0 | 0.0004 | 4694494.6286 | 33358.0359
Minimum of Months | 7032.5187 | 6.0237 | 56.3828 | 0 | 0 | 340170.7097 | 2631.0974
Maximum of Months | 8093.2657 | 6.9989 | 75.2111 | 0 | 0 | 453811.5674 | 3024.6455
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 77247300000 | 72190.576 | 26-JAN-13:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 20363.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 69747800000 | 67434.856 | 13-FEB-11:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 15607.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 79103700000 | 70050.964 | 31-MAR-14:39 | 32837.857 | 8089.532 | 10899.691 | 0 | 18223.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 75829100000 | 77526.472 | 11-APR-15:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 25699.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 80434700000 | 73673.012 | 30-MAY-14:09 | 32837.857 | 8089.532 | 10899.691 | 0 | 21845.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 79935900000 | 73277.817 | 30-JUN-14:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 21450.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 86476500000 | 76668.611 | 10-JUL-14:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 24841.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 93048400000 | 84144.888 | 08-AUG-14:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 32317.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 85461200000 | 82247.932 | 23-SEP-13:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 30420.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 81611800000 | 75448.142 | 19-OCT-10:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 23621.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 76009500000 | 71335.029 | 20-NOV-13:39 | 32837.857 | 8089.532 | 10899.691 | 0 | 19507.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 77641800000 | 72729.69 | 19-DEC-12:00 | 32837.857 | 8089.532 | 10899.691 | 0 | 20902.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 962548000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 69747800000 | 67434.856 |  | 32837.857 | 8089.532 | 10899.691 | 0 | 15607.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 93048400000 | 84144.888 |  | 32837.857 | 8089.532 | 10899.691 | 0 | 32317.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 35516.88 | 1015.97 | 0 | 36532.84
Cost per Total Building Area ($/m2) | 16.99 | 0.49 | 0 | 17.48
Cost per Net Conditioned Building Area ($/m2) | 16.99 | 0.49 | 0 | 17.48
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1507.37 | 721.12 | 721.12
Net Site Energy | 1507.37 | 721.12 | 721.12
Total Source Energy | 4826.64 | 2309.05 | 2309.05
Net Source Energy | 4826.64 | 2309.05 | 2309.05
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 227.45 | 0 | 0 | 0 | 0
Cooling | 291.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 302.59 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1279.92 | 227.45 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1279.92 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1279.92 | 100
Total On-Site and Utility Electric Sources | 1279.92 | 100
Total Electricity End Uses | 1279.92 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.25 | 0.318 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.25 | 0.318 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34054.11 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18486.28 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16698.35 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16292.75 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15956.64 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25782.33 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13876.55 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13793.17 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13851.41 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14870.08 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.06 | 2938.87 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.12 | 1595.37 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.01 | 1441.07 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1406.06 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.96 | 1377.06 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.56 | 2225.02 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.84 | 1197.55 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.83 | 1190.35 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.84 | 1195.38 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.9 | 1283.29 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 44120.48
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 21450.52
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 21298.18
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 21276.06
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 21302.15
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 40732.47
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 21306.31
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 21314.46
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 21476.59
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 24641.12
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22677.9358 | 34.4006 | 129.9401 | 0 | 0.0003 | 647949.0946 | 9284.8201
February | 18545.4268 | 29.327 | 117.4941 | 0 | 0.0002 | 585937.2538 | 7717.0938
March | 21179.4831 | 33.5298 | 134.5336 | 0 | 0.0003 | 670913.8731 | 8817.0602
April | 21798.4132 | 35.5398 | 148.1481 | 0 | 0.0003 | 738848.0541 | 9181.7972
May | 24725.6524 | 40.4673 | 169.4992 | 0 | 0.0003 | 845335.9809 | 10430.8997
June | 30129.7178 | 49.4105 | 207.4723 | 0 | 0.0004 | 1034721.2302 | 12720.9415
July | 32509.0677 | 53.3125 | 223.8569 | 0 | 0.0004 | 1116435.9566 | 13725.5225
August | 32699.3332 | 53.6245 | 225.1671 | 0 | 0.0004 | 1122970.1094 | 13805.8538
September | 27705.3803 | 45.4348 | 190.7788 | 0 | 0.0004 | 951466.3119 | 11697.377
October | 22549.0651 | 36.7787 | 153.3912 | 0 | 0.0003 | 764996.7677 | 9499.5459
November | 19491.8814 | 31.1018 | 126.1049 | 0 | 0.0002 | 628889.6159 | 8139.8432
December | 21852.5956 | 33.5931 | 129.3885 | 0 | 0.0002 | 645217.3561 | 8993.1031
Annual Sum or Average | 295863.9525 | 476.5205 | 1955.7749 | 0 | 0.0037 | 9753681.6044 | 124013.8579
Minimum of Months | 18545.4268 | 29.327 | 117.4941 | 0 | 0.0002 | 585937.2538 | 7717.0938
Maximum of Months | 32699.3332 | 53.6245 | 225.1671 | 0 | 0.0004 | 1122970.1094 | 13805.8538
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85026500000 | 62260.387 | 18-JAN-14:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 5482.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 76889100000 | 69499.725 | 08-FEB-15:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 12722.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 88040000000 | 79424.566 | 31-MAR-15:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 22647.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 96954600000 | 98615.357 | 21-APR-14:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 41837.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 110928000000 | 107941.876 | 31-MAY-15:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 51164.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 135780000000 | 123209.681 | 27-JUN-15:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 66432.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 146503000000 | 122249.271 | 24-JUL-15:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 65471.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 147361000000 | 121412.583 | 04-AUG-14:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 64635.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 124855000000 | 118814.846 | 01-SEP-14:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 62037.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 100386000000 | 98263.508 | 03-OCT-14:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 41486.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 82525400000 | 71458.126 | 10-NOV-15:20 | 32837.857 | 8089.532 | 15850.002 | 0 | 14680.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 84668000000 | 69179.967 | 05-DEC-14:00 | 32837.857 | 8089.532 | 15850.002 | 0 | 12402.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1279920000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 76889100000 | 62260.387 |  | 32837.857 | 8089.532 | 15850.002 | 0 | 5482.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 147361000000 | 123209.681 |  | 32837.857 | 8089.532 | 15850.002 | 0 | 66432.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 35422.47 | 1732.91 | 0 | 37155.38
Cost per Total Building Area ($/m2) | 16.95 | 0.83 | 0 | 17.77
Cost per Net Conditioned Building Area ($/m2) | 16.95 | 0.83 | 0 | 17.77
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1287.43 | 615.9 | 615.9
Net Site Energy | 1287.43 | 615.9 | 615.9
Total Source Energy | 3264.78 | 1561.86 | 1561.86
Net Source Energy | 3264.78 | 1561.86 | 1561.86
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 359.37 | 0 | 0 | 0 | 0
Cooling | 26.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 215.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 928.06 | 359.37 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 928.06 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 928.06 | 100
Total On-Site and Utility Electric Sources | 928.06 | 100
Total Electricity End Uses | 928.06 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 6.88 | 0.39 | 0.39 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 6.88 | 0.39 | 0.39 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 6.88 | 0.39 | 0.39 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 6.88 | 0.39 | 0.39 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 6.88 | 0.39 | 0.39 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26452.33 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12302.17 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10966.52 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10812.86 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10741.11 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18811.97 | 3.05
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9844.86 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9845.4 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9900.41 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11528.9 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.6 | 2282.84 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.74 | 1061.68 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.66 | 946.41 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.65 | 933.15 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.65 | 926.96 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.14 | 1623.47 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.59 | 849.61 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.59 | 849.66 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.6 | 854.41 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.7 | 994.94 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 39510.2
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 19548.87
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 19486.42
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 19480.25
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 19489.5
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 37106.23
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 19490.69
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 19491.45
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 19568.57
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 21893.52
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10592.8548 | 9.2692 | 62.2768 | 0 | 0 | 375646.8671 | 3856.209
February | 7987.4252 | 6.9365 | 56.4096 | 0 | 0 | 340306.4923 | 2936.5648
March | 9095.2464 | 7.9045 | 63.1622 | 0 | 0 | 381038.718 | 3340.5855
April | 8076.3067 | 6.995 | 60.3794 | 0 | 0 | 364270.0161 | 2979.4385
May | 7748.8507 | 6.6827 | 63.0585 | 0 | 0 | 380454.1174 | 2874.2791
June | 7339.6031 | 6.3162 | 62.1542 | 0 | 0 | 375007.9476 | 2729.8791
July | 7370.8663 | 6.3323 | 64.3664 | 0 | 0 | 388362.0493 | 2747.4485
August | 7657.0559 | 6.5789 | 66.7295 | 0 | 0 | 402619.7394 | 2853.709
September | 7483.853 | 6.4286 | 65.4738 | 0 | 0 | 395043.9383 | 2789.9319
October | 7704.8008 | 6.6366 | 64.16 | 0 | 0 | 387105.7196 | 2862.3941
November | 7921.7164 | 6.8571 | 59.9441 | 0 | 0 | 361646.746 | 2924.6064
December | 10179.6194 | 8.8948 | 62.1342 | 0 | 0 | 374798.7526 | 3712.7524
Annual Sum or Average | 99158.1987 | 85.8325 | 750.2486 | 0 | 0.0004 | 4526301.1037 | 36607.7983
Minimum of Months | 7339.6031 | 6.3162 | 56.4096 | 0 | 0 | 340306.4923 | 2729.8791
Maximum of Months | 10592.8548 | 9.2692 | 66.7295 | 0 | 0 | 402619.7394 | 3856.209
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 77021700000 | 56000.467 | 02-JAN-16:00 | 32837.857 | 8089.532 | 11323.123 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 69775600000 | 65177.155 | 15-FEB-15:00 | 32837.857 | 8089.532 | 11323.123 | 0 | 12926.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 78127300000 | 56000.467 | 01-MAR-17:00 | 32837.857 | 8089.532 | 11323.123 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 74689000000 | 69521.606 | 29-APR-14:50 | 32837.857 | 8089.532 | 11323.123 | 0 | 17271.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 78007400000 | 70961.837 | 17-MAY-13:00 | 32837.857 | 8089.532 | 11323.123 | 0 | 18711.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 76890700000 | 72833.583 | 16-JUN-14:50 | 32837.857 | 8089.532 | 11323.123 | 0 | 20583.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 79628800000 | 81708.672 | 03-JUL-12:00 | 32837.857 | 8089.532 | 11323.123 | 0 | 29458.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 82552200000 | 76016.498 | 15-AUG-12:09 | 32837.857 | 8089.532 | 11323.123 | 0 | 23765.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 80998800000 | 92646.491 | 28-SEP-14:00 | 32837.857 | 8089.532 | 11323.123 | 0 | 40395.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 79371200000 | 71355.616 | 13-OCT-15:00 | 32837.857 | 8089.532 | 11323.123 | 0 | 19105.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 74151200000 | 56213.747 | 08-NOV-17:10 | 32837.857 | 8089.532 | 11323.123 | 0 | 213.28 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 76847800000 | 56000.467 | 01-DEC-16:49 | 32837.857 | 8089.532 | 11323.123 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 928062000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 69775600000 | 56000.467 |  | 32837.857 | 8089.532 | 11323.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 82552200000 | 92646.491 |  | 32837.857 | 8089.532 | 11323.123 | 0 | 40395.978 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 38981.95 | 3092.53 | 0 | 42074.48
Cost per Total Building Area ($/m2) | 18.65 | 1.48 | 0 | 20.13
Cost per Net Conditioned Building Area ($/m2) | 18.65 | 1.48 | 0 | 20.13
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1937.75 | 927.01 | 927.01
Net Site Energy | 1937.75 | 927.01 | 927.01
Total Source Energy | 4944.94 | 2365.64 | 2365.64
Net Source Energy | 4944.94 | 2365.64 | 2365.64
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 798.89 | 0 | 0 | 0 | 0
Cooling | 174.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 278.79 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1138.86 | 798.89 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1138.86 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1138.86 | 100
Total On-Site and Utility Electric Sources | 1138.86 | 100
Total Electricity End Uses | 1138.86 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38629.75 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20595.37 | 2.96
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18695.71 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18232.81 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18335.76 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 36601.02 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19355.27 | 2.96
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19396.98 | 2.96
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19642.61 | 2.96
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24389.65 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.71 | 2449.81 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.94 | 1348.37 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.81 | 1161.86 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.78 | 1119.2 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.78 | 1115.66 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.47 | 2105.6 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.78 | 1115.77 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.78 | 1115.88 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.79 | 1130.01 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.99 | 1410.94 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 59117.95
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 28330.15
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 28175.68
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 28163.42
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 28181.79
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 54303.67
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 28183.73
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 28185.48
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 28418.3
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 32943.69
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 25820.8127 | 39.1416 | 86.8196 | 0 | 0.0004 | 5396.1073 | 10372.5642
February | 21285.1506 | 33.3076 | 77.3201 | 0 | 0.0003 | 4806.2316 | 8645.7674
March | 18842.0293 | 32.5577 | 85.4141 | 0 | 0.0004 | 5310.8521 | 7934.4054
April | 15427.2302 | 28.6293 | 80.8235 | 0 | 0.0003 | 5026.1888 | 6676.7548
May | 16151.4101 | 31.6959 | 94.1293 | 0 | 0.0004 | 5854.2223 | 7147.6887
June | 19143.9049 | 38.2391 | 115.2726 | 0 | 0.0005 | 7169.3963 | 8533.3203
July | 21120.7723 | 42.2235 | 127.3726 | 0 | 0.0005 | 7921.9724 | 9417.757
August | 21577.2789 | 43.121 | 130.0423 | 0 | 0.0005 | 8088.0093 | 9619.9329
September | 16796.9566 | 33.3935 | 100.2699 | 0 | 0.0004 | 6236.2548 | 7472.756
October | 16393.6022 | 31.2087 | 90.2264 | 0 | 0.0004 | 5611.1967 | 7166.8632
November | 17254.5437 | 30.5385 | 82.2145 | 0 | 0.0003 | 5112.1936 | 7332.0997
December | 23250.2342 | 36.5007 | 85.1101 | 0 | 0.0004 | 5290.5185 | 9454.7524
Annual Sum or Average | 233063.9256 | 420.5572 | 1155.0149 | 0 | 0.0047 | 71823.1436 | 99774.662
Minimum of Months | 15427.2302 | 28.6293 | 77.3201 | 0 | 0.0003 | 4806.2316 | 6676.7548
Maximum of Months | 25820.8127 | 43.121 | 130.0423 | 0 | 0.0005 | 8088.0093 | 10372.5642
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85562900000 | 58750.454 | 02-JAN-16:49 | 32837.857 | 8089.532 | 14073.11 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 76209600000 | 58750.454 | 01-FEB-17:30 | 32837.857 | 8089.532 | 14073.11 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 84211000000 | 77755.694 | 09-MAR-15:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 22755.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 79697300000 | 80248.971 | 04-APR-15:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 25248.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 92826900000 | 95335.628 | 31-MAY-15:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 40335.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 113681000000 | 119668.151 | 30-JUN-14:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 64667.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 125614000000 | 123506.292 | 25-JUL-12:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 68505.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 128247000000 | 125366.209 | 17-AUG-14:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 70365.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 98884600000 | 106432.364 | 09-SEP-14:39 | 32837.857 | 8089.532 | 14073.11 | 0 | 51431.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 88973400000 | 92705.32 | 03-OCT-14:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 37704.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 81061000000 | 83538.827 | 04-NOV-13:00 | 32837.857 | 8089.532 | 14073.11 | 0 | 28538.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 83888600000 | 58750.454 | 01-DEC-16:40 | 32837.857 | 8089.532 | 14073.11 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1138860000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 76209600000 | 58750.454 |  | 32837.857 | 8089.532 | 14073.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 128247000000 | 125366.209 |  | 32837.857 | 8089.532 | 14073.11 | 0 | 70365.71 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24895.66 | 7710.11 | 0 | 32605.77
Cost per Total Building Area ($/m2) | 11.91 | 3.69 | 0 | 15.6
Cost per Net Conditioned Building Area ($/m2) | 11.91 | 3.69 | 0 | 15.6
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1621.35 | 775.65 | 775.65
Net Site Energy | 1621.35 | 775.65 | 775.65
Total Source Energy | 4298.29 | 2056.29 | 2056.29
Net Source Energy | 4298.29 | 2056.29 | 2056.29
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 485.77 | 0 | 0 | 0 | 0
Cooling | 149 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 300.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1135.57 | 485.77 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1135.57 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1135.57 | 100
Total On-Site and Utility Electric Sources | 1135.57 | 100
Total Electricity End Uses | 1135.57 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33778.71 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15226.99 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14124.36 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14113.36 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14130.07 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26558.94 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14131.85 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14133.17 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14334.04 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17793.97 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.04 | 2915.1 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.92 | 1314.09 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.85 | 1218.93 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.85 | 1217.98 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.85 | 1219.42 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.6 | 2292.04 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.85 | 1219.58 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.85 | 1219.69 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.87 | 1237.03 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.07 | 1535.62 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 50671.56
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 24282.01
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 24186.74
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 24173.78
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 24193.49
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 46397.21
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 24195.58
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 24197.14
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 24370.46
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 28409.08
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 28691.0077 | 45.2618 | 104.1443 | 0 | 0.0004 | 108261.9061 | 11815.1608
February | 24158.128 | 39.1092 | 93.0937 | 0 | 0.0004 | 96782.3545 | 10046.4078
March | 25983.5751 | 42.9141 | 104.7269 | 0 | 0.0004 | 108882.9005 | 10888.8821
April | 23854.1826 | 40.821 | 103.8505 | 0 | 0.0004 | 107982.0321 | 10136.1794
May | 26866.7182 | 46.8636 | 121.7685 | 0 | 0.0005 | 126618.6878 | 11503.3111
June | 28629.5196 | 50.218 | 131.2712 | 0 | 0.0005 | 136501.709 | 12285.4984
July | 31318.7144 | 54.9499 | 143.6823 | 0 | 0.0006 | 149407.4091 | 13440.9475
August | 30745.2559 | 53.9416 | 141.0396 | 0 | 0.0005 | 146659.4285 | 13194.6247
September | 26721.3171 | 46.8201 | 122.2468 | 0 | 0.0005 | 127117.3734 | 11461.6668
October | 24689.0228 | 42.3762 | 108.1703 | 0 | 0.0004 | 112474.4642 | 10503.3397
November | 24938.2831 | 40.9731 | 99.3525 | 0 | 0.0004 | 103293.6954 | 10429.7873
December | 28958.2726 | 45.5205 | 104.2325 | 0 | 0.0004 | 108352.3589 | 11909.2406
Annual Sum or Average | 325553.9971 | 549.7689 | 1377.5789 | 0 | 0.0054 | 1432334.3195 | 137615.046
Minimum of Months | 23854.1826 | 39.1092 | 93.0937 | 0 | 0.0004 | 96782.3545 | 10046.4078
Maximum of Months | 31318.7144 | 54.9499 | 143.6823 | 0 | 0.0006 | 149407.4091 | 13440.9475
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85831300000 | 60233.591 | 25-JAN-17:30 | 32837.857 | 8089.532 | 15389.486 | 0 | 166.761 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 76730200000 | 69753.107 | 14-FEB-15:00 | 32837.857 | 8089.532 | 15389.486 | 0 | 13436.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 86323700000 | 70942.717 | 25-MAR-15:50 | 32837.857 | 8089.532 | 15389.486 | 0 | 14625.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 85609500000 | 87575.034 | 22-APR-13:00 | 32837.857 | 8089.532 | 15389.486 | 0 | 31258.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 100385000000 | 92137.119 | 31-MAY-16:00 | 32837.857 | 8089.532 | 15389.486 | 0 | 35820.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 108220000000 | 103154.763 | 29-JUN-14:09 | 32837.857 | 8089.532 | 15389.486 | 0 | 46837.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 118452000000 | 107894.338 | 31-JUL-14:00 | 32837.857 | 8089.532 | 15389.486 | 0 | 51577.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 116273000000 | 105208.512 | 01-AUG-14:09 | 32837.857 | 8089.532 | 15389.486 | 0 | 48891.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 100780000000 | 93743.508 | 02-SEP-14:00 | 32837.857 | 8089.532 | 15389.486 | 0 | 37426.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 89171100000 | 83692.147 | 13-OCT-14:00 | 32837.857 | 8089.532 | 15389.486 | 0 | 27375.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 81892500000 | 65614.145 | 08-NOV-15:39 | 32837.857 | 8089.532 | 15389.486 | 0 | 9297.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 85903100000 | 60066.83 | 01-DEC-16:00 | 32837.857 | 8089.532 | 15389.486 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1135570000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 76730200000 | 60066.83 |  | 32837.857 | 8089.532 | 15389.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 118452000000 | 107894.338 |  | 32837.857 | 8089.532 | 15389.486 | 0 | 51577.462 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11840.96 | 3330.16 | 0 | 15171.12
Cost per Total Building Area ($/m2) | 5.66 | 1.59 | 0 | 7.26
Cost per Net Conditioned Building Area ($/m2) | 5.66 | 1.59 | 0 | 7.26
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1680.46 | 803.93 | 803.93
Net Site Energy | 1680.46 | 803.93 | 803.93
Total Source Energy | 2458.89 | 1176.32 | 1176.32
Net Source Energy | 2458.89 | 1176.32 | 1176.32
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 720.73 | 0 | 0 | 0 | 0
Cooling | 35.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 238.66 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 959.73 | 720.73 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 959.73 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 959.73 | 100
Total On-Site and Utility Electric Sources | 959.73 | 100
Total Electricity End Uses | 959.73 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.704 | 0.79 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27665.3 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12917.91 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11742.52 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11606.6 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11587.71 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22149.59 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11785.34 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11803.29 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11927.48 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14483.15 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.67 | 2387.52 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.78 | 1110.83 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.69 | 992.6 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.69 | 978.98 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.68 | 976.41 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.28 | 1827.65 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.68 | 976.54 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.68 | 976.9 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.69 | 987.74 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.85 | 1217.89 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 49402.48
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 23759.02
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 23689.2
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 23677.32
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 23690.55
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 45335.98
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 23692.59
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 23698.56
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 23823.85
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 27498.31
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 11097.3663 | 12.7566 | 17.1792 | 0 | 0.0001 | 226588.1396 | 4128.2021
February | 8215.4015 | 9.8575 | 15.3595 | 0 | 0.0001 | 202703.6971 | 3100.4293
March | 8620.52 | 10.5255 | 17.2782 | 0 | 0.0001 | 228066.9247 | 3272.7969
April | 6575.3806 | 8.5077 | 16.2394 | 0 | 0.0001 | 214458.8675 | 2547.6898
May | 5185.6271 | 7.3999 | 17.215 | 0 | 0.0001 | 227464.8859 | 2083.1577
June | 4457.2573 | 6.7363 | 17.1961 | 0 | 0.0001 | 227263.8294 | 1830.8014
July | 4402.872 | 6.8955 | 18.5278 | 0 | 0.0001 | 244891.7705 | 1834.3219
August | 4480.6639 | 7.0489 | 19.0564 | 0 | 0.0001 | 251880.8738 | 1870.106
September | 4869.8357 | 7.1946 | 17.7328 | 0 | 0.0001 | 234338.1486 | 1982.5689
October | 5978.6587 | 8.066 | 16.8752 | 0 | 0.0001 | 222913.6848 | 2351.8709
November | 8712.3097 | 10.4779 | 16.4431 | 0 | 0.0001 | 217009.1776 | 3290.5507
December | 11078.8044 | 12.7343 | 17.144 | 0 | 0.0001 | 226123.8498 | 4121.189
Annual Sum or Average | 83674.6972 | 108.2008 | 206.2464 | 0 | 0.0009 | 2723703.8493 | 32413.6846
Minimum of Months | 4402.872 | 6.7363 | 15.3595 | 0 | 0.0001 | 202703.6971 | 1830.8014
Maximum of Months | 11097.3663 | 12.7566 | 19.0564 | 0 | 0.0001 | 251880.8738 | 4128.2021
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 79840800000 | 57110.394 | 02-JAN-16:30 | 32837.857 | 8089.532 | 12433.05 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 71424800000 | 57110.394 | 01-FEB-17:10 | 32837.857 | 8089.532 | 12433.05 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 80361800000 | 62038.429 | 29-MAR-15:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 8677.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 75566900000 | 66173.73 | 29-APR-14:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 12813.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 80149700000 | 74233.901 | 04-MAY-14:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 20873.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 80078900000 | 79489.422 | 28-JUN-14:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 26128.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 86290300000 | 87731.376 | 24-JUL-14:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 34370.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 88753000000 | 84476.471 | 07-AUG-14:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 31116.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 82571600000 | 101201.164 | 02-SEP-15:50 | 32837.857 | 8089.532 | 12433.05 | 0 | 47840.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 78546000000 | 64538.537 | 17-OCT-14:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 11178.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 76465500000 | 57577.306 | 04-NOV-14:00 | 32837.857 | 8089.532 | 12433.05 | 0 | 4216.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 79677200000 | 57110.394 | 01-DEC-16:19 | 32837.857 | 8089.532 | 12433.05 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 959727000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 71424800000 | 57110.394 |  | 32837.857 | 8089.532 | 12433.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 88753000000 | 101201.164 |  | 32837.857 | 8089.532 | 12433.05 | 0 | 47840.725 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20410.03 | 6077.23 | 0 | 26487.26
Cost per Total Building Area ($/m2) | 9.76 | 2.91 | 0 | 12.67
Cost per Net Conditioned Building Area ($/m2) | 9.76 | 2.91 | 0 | 12.67
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2218.41 | 1061.28 | 1061.28
Net Site Energy | 2218.41 | 1061.28 | 1061.28
Total Source Energy | 5134.26 | 2456.21 | 2456.21
Net Source Energy | 5134.26 | 2456.21 | 2456.21
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1113.38 | 0 | 0 | 0 | 0
Cooling | 131.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 287.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1105.03 | 1113.38 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1105.03 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1105.03 | 100
Total On-Site and Utility Electric Sources | 1105.03 | 100
Total Electricity End Uses | 1105.03 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39490.14 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19293.45 | 2.96
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18693.2 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18940.25 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19142.84 | 2.96
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37516.52 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19970.1 | 2.96
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19964.88 | 2.96
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20169.3 | 2.96
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25534.23 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.74 | 2484.72 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.88 | 1253.79 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.8 | 1148.1 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.8 | 1147.54 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.8 | 1148.77 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.51 | 2158.27 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.8 | 1148.85 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.8 | 1148.55 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.81 | 1160.31 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.03 | 1468.95 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 65334.33
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 31282.59
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 31153.1
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 31144.15
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 31163.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 60093.82
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 31165.13
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 31160.31
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 31349.12
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 36306.28
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44320.2551 | 67.3856 | 162.9768 | 0 | 0.0005 | 37501.8277 | 17935.7096
February | 37101.7102 | 57.858 | 145.1103 | 0 | 0.0005 | 33393.4569 | 15152.8838
March | 36968.1366 | 60.0201 | 158.7981 | 0 | 0.0005 | 36547.6479 | 15324.9698
April | 29906.8333 | 51.7721 | 147.7475 | 0 | 0.0005 | 34009.6666 | 12705.2629
May | 32026.9378 | 57.6198 | 171.2753 | 0 | 0.0005 | 39428.6032 | 13814.1411
June | 36564.2894 | 66.514 | 199.9228 | 0 | 0.0006 | 46024.4133 | 15841.1281
July | 40747.8488 | 74.1896 | 223.1889 | 0 | 0.0007 | 51380.605 | 17659.8609
August | 39126.2966 | 71.2156 | 214.1773 | 0 | 0.0006 | 49305.9969 | 16955.019
September | 32435.8491 | 58.8173 | 176.2309 | 0 | 0.0005 | 40570.0412 | 14034.6773
October | 30757.3522 | 54.2346 | 157.8849 | 0 | 0.0005 | 36344.6027 | 13161.2555
November | 33635.2979 | 55.6327 | 150.6181 | 0 | 0.0005 | 34666.7226 | 14041.2276
December | 42005.8096 | 64.9546 | 160.9879 | 0 | 0.0005 | 37046.2765 | 17103.1087
Annual Sum or Average | 435596.6163 | 740.214 | 2068.9189 | 0 | 0.0064 | 476219.8606 | 183729.2441
Minimum of Months | 29906.8333 | 51.7721 | 145.1103 | 0 | 0.0005 | 33393.4569 | 12705.2629
Maximum of Months | 44320.2551 | 74.1896 | 223.1889 | 0 | 0.0007 | 51380.605 | 17935.7096
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 87020200000 | 58945.208 | 02-JAN-16:40 | 32837.857 | 8089.532 | 14267.864 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 77487000000 | 58945.208 | 01-FEB-16:00 | 32837.857 | 8089.532 | 14267.864 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 84806100000 | 66689.347 | 31-MAR-14:00 | 32837.857 | 8089.532 | 14267.864 | 0 | 11494.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 78916900000 | 71518.023 | 07-APR-14:00 | 32837.857 | 8089.532 | 14267.864 | 0 | 16322.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 91491100000 | 96049.441 | 30-MAY-15:00 | 32837.857 | 8089.532 | 14267.864 | 0 | 40854.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 106796000000 | 115953.709 | 08-JUN-12:00 | 32837.857 | 8089.532 | 14267.864 | 0 | 60758.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 119225000000 | 117867.819 | 13-JUL-14:00 | 32837.857 | 8089.532 | 14267.864 | 0 | 62672.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 114411000000 | 115861.942 | 04-AUG-15:30 | 32837.857 | 8089.532 | 14267.864 | 0 | 60666.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 94139700000 | 97983.211 | 05-SEP-14:00 | 32837.857 | 8089.532 | 14267.864 | 0 | 42787.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 84334900000 | 79581.494 | 31-OCT-13:30 | 32837.857 | 8089.532 | 14267.864 | 0 | 24386.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 80441500000 | 77158.051 | 02-NOV-15:09 | 32837.857 | 8089.532 | 14267.864 | 0 | 21962.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 85963100000 | 58945.208 | 01-DEC-16:19 | 32837.857 | 8089.532 | 14267.864 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1105030000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 77487000000 | 58945.208 |  | 32837.857 | 8089.532 | 14267.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 119225000000 | 117867.819 |  | 32837.857 | 8089.532 | 14267.864 | 0 | 62672.566 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16063.02 | 9212.45 | 0 | 25275.47
Cost per Total Building Area ($/m2) | 7.68 | 4.41 | 0 | 12.09
Cost per Net Conditioned Building Area ($/m2) | 7.68 | 4.41 | 0 | 12.09
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 1851.83 | 885.91 | 885.91
Net Site Energy | 1851.83 | 885.91 | 885.91
Total Source Energy | 4473.16 | 2139.94 | 2139.94
Net Source Energy | 4473.16 | 2139.94 | 2139.94
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 750.77 | 0 | 0 | 0 | 0
Cooling | 98.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 316.65 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1101.06 | 750.77 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1101.06 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1101.06 | 100
Total On-Site and Utility Electric Sources | 1101.06 | 100
Total Electricity End Uses | 1101.06 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32186.78 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15098.35 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14987.94 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14980.29 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14997.31 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28081.97 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14998.44 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14994.1 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15154.67 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19006.12 | 3.05
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.94 | 2777.72 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.91 | 1302.99 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.91 | 1293.46 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.9 | 1292.8 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.91 | 1294.27 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.7 | 2423.47 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.91 | 1294.37 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.91 | 1293.99 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.92 | 1307.85 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.15 | 1640.23 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 58493.93
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 28087.95
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 27959.42
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 27950.52
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 27970.33
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 53717.04
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 27971.65
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 27966.59
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 28153.51
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 32541.82
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 31981.7552 | 48.8526 | 107.4259 | 0 | 0.0004 | 111660.4632 | 13013.3104
February | 27015.1143 | 42.1034 | 95.2755 | 0 | 0.0004 | 99038.3945 | 11074.5352
March | 28029.6437 | 45.1627 | 106.854 | 0 | 0.0004 | 111086.2889 | 11635.4202
April | 24279.5073 | 40.7647 | 101.4585 | 0 | 0.0004 | 105489.5678 | 10240.0009
May | 25085.7245 | 43.1128 | 110.2096 | 0 | 0.0004 | 114595.3449 | 10677.5669
June | 26006.949 | 45.37 | 117.9049 | 0 | 0.0005 | 122601.2275 | 11135.7911
July | 29147.6998 | 51.1403 | 133.7198 | 0 | 0.0005 | 139048.0181 | 12509.1776
August | 28921.9724 | 50.7111 | 132.5045 | 0 | 0.0005 | 137783.9921 | 12409.0443
September | 25673.7848 | 44.5634 | 115.1744 | 0 | 0.0004 | 119760.5685 | 10971.0249
October | 25294.2983 | 42.7941 | 107.4608 | 0 | 0.0004 | 111732.6903 | 10699.9227
November | 26719.6773 | 42.8736 | 100.8947 | 0 | 0.0004 | 104889.5823 | 11074.1412
December | 32079.6965 | 48.8456 | 106.9076 | 0 | 0.0004 | 111120.4154 | 13037.808
Annual Sum or Average | 330235.8231 | 546.2941 | 1335.7901 | 0 | 0.0053 | 1388806.5533 | 138477.7435
Minimum of Months | 24279.5073 | 40.7647 | 95.2755 | 0 | 0.0004 | 99038.3945 | 10240.0009
Maximum of Months | 32079.6965 | 51.1403 | 133.7198 | 0 | 0.0005 | 139048.0181 | 13037.808
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 88525800000 | 60783.71 | 27-JAN-17:10 | 32837.857 | 8089.532 | 15921.14 | 0 | 185.227 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 78518800000 | 60601.282 | 11-FEB-17:30 | 32837.857 | 8089.532 | 15921.14 | 0 | 2.798 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 88070500000 | 73924.243 | 30-MAR-15:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 17075.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 83633400000 | 80716.007 | 25-APR-14:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 23867.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 90852600000 | 88239.416 | 23-MAY-15:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 31390.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 97199700000 | 98428.595 | 28-JUN-13:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 41580.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 110239000000 | 102584.969 | 17-JUL-14:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 45736.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 109237000000 | 104203.083 | 30-AUG-13:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 47354.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 94947600000 | 98243.027 | 02-SEP-14:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 41394.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 88583000000 | 87848.488 | 05-OCT-14:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 30999.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 83157700000 | 66119.548 | 10-NOV-13:00 | 32837.857 | 8089.532 | 15921.14 | 0 | 9271.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 88097600000 | 60598.484 | 01-DEC-16:40 | 32837.857 | 8089.532 | 15921.14 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1101060000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 78518800000 | 60598.484 |  | 32837.857 | 8089.532 | 15921.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 110239000000 | 104203.083 |  | 32837.857 | 8089.532 | 15921.14 | 0 | 47354.553 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11486.98 | 5168.04 | 0 | 16655.02
Cost per Total Building Area ($/m2) | 5.5 | 2.47 | 0 | 7.97
Cost per Net Conditioned Building Area ($/m2) | 5.5 | 2.47 | 0 | 7.97
13-minneapolia
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2672.72 | 1278.62 | 1278.62
Net Site Energy | 2672.72 | 1278.62 | 1278.62
Total Source Energy | 5562.26 | 2660.96 | 2660.96
Net Source Energy | 5562.26 | 2660.96 | 2660.96
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1545.37 | 0 | 0 | 0 | 0
Cooling | 114.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 327.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1127.36 | 1545.37 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1127.36 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1127.36 | 100
Total On-Site and Utility Electric Sources | 1127.36 | 100
Total Electricity End Uses | 1127.36 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41221.87 | 2.78
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18555.72 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19421.45 | 2.96
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19657.5 | 2.96
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19852.09 | 2.96
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41203.49 | 2.78
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21693.29 | 2.96
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21739.81 | 2.96
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21906.96 | 2.96
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26963.93 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.93 | 2759.37 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.89 | 1277.13 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.89 | 1268.74 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.89 | 1268.2 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.89 | 1269.52 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.67 | 2392.29 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.89 | 1269.59 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.89 | 1269.17 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.9 | 1281.32 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.14 | 1627.8 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 72519.53
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 34624.65
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 34490.9
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 34482.26
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 34503.29
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 66669.96
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 34504.49
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 34497.77
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 34691.39
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 40103.01
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 41595.5561 | 56.372 | 60.8069 | 0 | 0.0005 | 39899.0795 | 16175.6875
February | 33525.3016 | 47.0162 | 54.1582 | 0 | 0.0004 | 35548.408 | 13188.4747
March | 28589.6035 | 43.7258 | 58.0098 | 0 | 0.0004 | 38101.3197 | 11593.9552
April | 21034.9781 | 35.5126 | 53.5599 | 0 | 0.0004 | 35196.7313 | 8849.6785
May | 21746.3245 | 38.9403 | 62.622 | 0 | 0.0005 | 41161.5724 | 9361.8067
June | 23471.7519 | 42.7377 | 69.8953 | 0 | 0.0005 | 45944.9867 | 10172.2567
July | 25251.9954 | 46.0483 | 75.4214 | 0 | 0.0005 | 49577.8025 | 10950.3846
August | 25360.1526 | 46.2616 | 75.7969 | 0 | 0.0006 | 49824.6614 | 10998.8249
September | 19970.4495 | 35.975 | 58.2072 | 0 | 0.0004 | 38260.5225 | 8617.8136
October | 21832.62 | 36.9048 | 55.7392 | 0 | 0.0004 | 36629.1019 | 9189.6128
November | 27338.5921 | 41.6966 | 55.0941 | 0 | 0.0004 | 36185.6665 | 11075.5566
December | 37912.7456 | 52.8474 | 60.1981 | 0 | 0.0005 | 39510.7046 | 14883.6886
Annual Sum or Average | 327630.0708 | 524.0384 | 739.509 | 0 | 0.0056 | 485840.5571 | 135057.7404
Minimum of Months | 19970.4495 | 35.5126 | 53.5599 | 0 | 0.0004 | 35196.7313 | 8617.8136
Maximum of Months | 41595.5561 | 56.372 | 75.7969 | 0 | 0.0006 | 49824.6614 | 16175.6875
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 92582800000 | 60360.489 | 02-JAN-16:40 | 32837.857 | 8089.532 | 15683.145 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 82487400000 | 60360.489 | 01-FEB-17:19 | 32837.857 | 8089.532 | 15683.145 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 88411200000 | 60360.489 | 01-MAR-17:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 81671400000 | 71142.481 | 01-APR-16:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 14531.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 95512300000 | 121039.568 | 27-MAY-14:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 64429.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 106612000000 | 117398.781 | 29-JUN-14:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 60788.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 115042000000 | 122864.661 | 15-JUL-14:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 66254.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 115614000000 | 115524.088 | 25-AUG-15:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 58913.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 88780700000 | 100091.978 | 14-SEP-14:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 43481.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 84995100000 | 85834.213 | 07-OCT-14:00 | 32837.857 | 8089.532 | 15683.145 | 0 | 29223.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 83966100000 | 60710.608 | 02-NOV-15:09 | 32837.857 | 8089.532 | 15683.145 | 0 | 4100.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 91681600000 | 60360.489 | 01-DEC-16:30 | 32837.857 | 8089.532 | 15683.145 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1127360000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 81671400000 | 60360.489 |  | 32837.857 | 8089.532 | 15683.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 115614000000 | 122864.661 |  | 32837.857 | 8089.532 | 15683.145 | 0 | 66254.127 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 19743.73 | 12178.83 | 0 | 31922.56
Cost per Total Building Area ($/m2) | 9.45 | 5.83 | 0 | 15.27
Cost per Net Conditioned Building Area ($/m2) | 9.45 | 5.83 | 0 | 15.27
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2303.65 | 1102.06 | 1102.06
Net Site Energy | 2303.65 | 1102.06 | 1102.06
Total Source Energy | 5140.85 | 2459.36 | 2459.36
Net Source Energy | 5140.85 | 2459.36 | 2459.36
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1202.44 | 0 | 0 | 0 | 0
Cooling | 62.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.86 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 352.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1101.21 | 1202.44 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1101.21 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1101.21 | 100
Total On-Site and Utility Electric Sources | 1101.21 | 100
Total Electricity End Uses | 1101.21 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.477 | 0.51 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.39 | 0.495 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.39 | 0.495 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35268.03 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16384.81 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16275.58 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16268.63 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16285.98 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30649.11 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16286.93 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16281.12 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16439.23 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20777.9 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.13 | 3043.63 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.99 | 1414.01 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1404.58 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1403.98 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1405.48 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.85 | 2645.02 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1405.56 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.98 | 1405.06 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.99 | 1418.71 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.26 | 1793.13 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 69386.33
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 33247.27
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 33112.96
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 33104.41
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 33125.75
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 63889.4
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 33126.92
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 33119.78
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 33314.2
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 38535.38
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37250.1537 | 53.0464 | 69.7301 | 0 | 0.0005 | 1652390.1878 | 14751.587
February | 30620.8815 | 44.7835 | 61.5791 | 0 | 0.0004 | 1459514.4353 | 12240.1278
March | 27935.2656 | 43.9382 | 67.3262 | 0 | 0.0005 | 1596406.9414 | 11464.5705
April | 23285.0132 | 38.211 | 61.8579 | 0 | 0.0004 | 1467035.5493 | 9709.5163
May | 22442.2053 | 38.4326 | 65.4222 | 0 | 0.0005 | 1551834.4871 | 9513.1904
June | 23352.9303 | 40.9485 | 71.5355 | 0 | 0.0005 | 1696988.9394 | 9991.6825
July | 24990.5664 | 44.3007 | 78.2902 | 0 | 0.0005 | 1857295.4255 | 10738.8147
August | 24624.7457 | 43.5301 | 76.7026 | 0 | 0.0005 | 1819616.1315 | 10569.8149
September | 22341.874 | 38.8513 | 67.2654 | 0 | 0.0005 | 1595645.1499 | 9527.7436
October | 23562.9397 | 39.2284 | 64.6263 | 0 | 0.0005 | 1532785.3421 | 9879.6689
November | 27125.9747 | 42.2937 | 64.0316 | 0 | 0.0005 | 1518218.8749 | 11096.5125
December | 35109.1914 | 50.8263 | 68.7195 | 0 | 0.0005 | 1628637.8848 | 13983.8453
Annual Sum or Average | 322641.7413 | 518.3906 | 817.0863 | 0 | 0.0058 | 19376400 | 133467.0742
Minimum of Months | 22341.874 | 38.211 | 61.5791 | 0 | 0.0004 | 1459514.4353 | 9513.1904
Maximum of Months | 37250.1537 | 53.0464 | 78.2902 | 0 | 0.0005 | 1857295.4255 | 14751.587
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 93909300000 | 62016.507 | 02-JAN-16:49 | 32837.857 | 8089.532 | 17339.163 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 82947700000 | 62016.507 | 01-FEB-17:30 | 32837.857 | 8089.532 | 17339.163 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 90727600000 | 68895.926 | 30-MAR-16:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 10629.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 83375100000 | 63598.03 | 06-APR-16:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 5331.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 88194500000 | 81927.87 | 16-MAY-16:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 23661.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 96443900000 | 105582.792 | 30-JUN-14:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 47316.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 105555000000 | 103481.95 | 21-JUL-15:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 45215.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 103413000000 | 98680.675 | 09-AUG-16:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 40414.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 90684300000 | 93320.856 | 01-SEP-16:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 35054.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 87111900000 | 77016.439 | 06-OCT-15:00 | 32837.857 | 8089.532 | 17339.163 | 0 | 18749.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 86284000000 | 62016.507 | 01-NOV-17:10 | 32837.857 | 8089.532 | 17339.163 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 92559400000 | 62016.507 | 01-DEC-16:40 | 32837.857 | 8089.532 | 17339.163 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1101210000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 82947700000 | 62016.507 |  | 32837.857 | 8089.532 | 17339.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 105555000000 | 105582.792 |  | 32837.857 | 8089.532 | 17339.163 | 0 | 47316.239 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 23444.35 | 9656.6 | 0 | 33100.95
Cost per Total Building Area ($/m2) | 11.22 | 4.62 | 0 | 15.84
Cost per Net Conditioned Building Area ($/m2) | 11.22 | 4.62 | 0 | 15.84
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 2940.76 | 1406.85 | 1406.85
Net Site Energy | 2940.76 | 1406.85 | 1406.85
Total Source Energy | 5743 | 2747.43 | 2747.43
Net Source Energy | 5743 | 2747.43 | 2747.43
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1861.15 | 0 | 0 | 0 | 0
Cooling | 48.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 344.83 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1079.61 | 1861.15 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1079.61 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1079.61 | 100
Total On-Site and Utility Electric Sources | 1079.61 | 100
Total Electricity End Uses | 1079.61 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.357 | 0.38 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 3.24 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 3.24 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 3.24 | 0.49 | 0.49 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 3.24 | 0.49 | 0.49 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 3.24 | 0.49 | 0.49 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39118.36 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16997.66 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18726.97 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18804.26 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18863.51 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37084.53 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19514.51 | 2.96
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19551.34 | 2.96
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19686.95 | 2.96
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24143.13 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.99 | 2846.35 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1328.75 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.92 | 1321.29 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.92 | 1320.82 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1322.17 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.75 | 2494.46 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1322.24 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1321.66 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 0.93 | 1332.05 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.17 | 1666.94 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 74161.21
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 35606.11
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 35489.76
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 35482.47
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 35503.56
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 68670.12
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 35504.57
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 35495.47
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 35657.61
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 40772.3
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42113.4523 | 57.1878 | 61.9348 | 0 | 0.0005 | 40640.0272 | 16387.9726
February | 35696.6686 | 49.292 | 55.1609 | 0 | 0.0004 | 36201.3346 | 13969.1307
March | 32752.5624 | 47.9936 | 59.6214 | 0 | 0.0005 | 39148.4358 | 13081.5092
April | 23838.9947 | 38.1849 | 53.9867 | 0 | 0.0004 | 35468.2708 | 9832.3029
May | 21103.2143 | 36.3314 | 56.0247 | 0 | 0.0004 | 36819.5301 | 8945.6423
June | 20217.8675 | 36.5273 | 59.2755 | 0 | 0.0004 | 38963.0993 | 8734.7709
July | 22500.5623 | 40.9153 | 66.827 | 0 | 0.0005 | 43927.8989 | 9746.1872
August | 22369.7935 | 40.4404 | 65.6667 | 0 | 0.0005 | 43164.3227 | 9666.8848
September | 20079.71 | 35.2921 | 55.6611 | 0 | 0.0004 | 36583.5589 | 8580.8698
October | 23113.8592 | 38.134 | 55.9609 | 0 | 0.0004 | 36770.7431 | 9639.3865
November | 29879.6664 | 44.4784 | 56.653 | 0 | 0.0004 | 37203.5687 | 12000.4457
December | 39950.5162 | 55.1 | 61.5196 | 0 | 0.0005 | 40373.9752 | 15627.4819
Annual Sum or Average | 333616.8673 | 519.8772 | 708.2923 | 0 | 0.0054 | 465264.7652 | 136212.5846
Minimum of Months | 20079.71 | 35.2921 | 53.9867 | 0 | 0.0004 | 35468.2708 | 8580.8698
Maximum of Months | 42113.4523 | 57.1878 | 66.827 | 0 | 0.0005 | 43927.8989 | 16387.9726
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94302100000 | 60954.073 | 02-JAN-16:30 | 32837.857 | 8089.532 | 16276.729 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 84002500000 | 60954.073 | 01-FEB-17:10 | 32837.857 | 8089.532 | 16276.729 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 90841000000 | 60954.073 | 01-MAR-17:49 | 32837.857 | 8089.532 | 16276.729 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 82301500000 | 60982.151 | 04-APR-14:00 | 32837.857 | 8089.532 | 16276.729 | 0 | 3778.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 85436900000 | 77428.729 | 31-MAY-15:00 | 32837.857 | 8089.532 | 16276.729 | 0 | 20224.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 90410900000 | 98561.681 | 14-JUN-14:00 | 32837.857 | 8089.532 | 16276.729 | 0 | 41357.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 101931000000 | 107671.879 | 08-JUL-15:09 | 32837.857 | 8089.532 | 16276.729 | 0 | 50467.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 100160000000 | 109041.747 | 12-AUG-14:00 | 32837.857 | 8089.532 | 16276.729 | 0 | 51837.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 84889400000 | 89620.632 | 07-SEP-14:00 | 32837.857 | 8089.532 | 16276.729 | 0 | 32416.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 85323700000 | 82027.064 | 07-OCT-14:00 | 32837.857 | 8089.532 | 16276.729 | 0 | 24822.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 86328100000 | 60954.073 | 01-NOV-16:49 | 32837.857 | 8089.532 | 16276.729 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 93684800000 | 60954.073 | 01-DEC-16:19 | 32837.857 | 8089.532 | 16276.729 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1079610000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 82301500000 | 60954.073 |  | 32837.857 | 8089.532 | 16276.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 101931000000 | 109041.747 |  | 32837.857 | 8089.532 | 16276.729 | 0 | 51837.629 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18395.89 | 14634.6 | 0 | 33030.48
Cost per Total Building Area ($/m2) | 8.8 | 7 | 0 | 15.8
Cost per Net Conditioned Building Area ($/m2) | 8.8 | 7 | 0 | 15.8
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 4209.58 | 2013.85 | 2013.85
Net Site Energy | 4209.58 | 2013.85 | 2013.85
Total Source Energy | 7367.57 | 3524.61 | 3524.61
Net Source Energy | 7367.57 | 3524.61 | 3524.61
Area (m2)
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3092.36 | 0 | 0 | 0 | 0
Cooling | 23.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 407.64 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1117.22 | 3092.36 | 0 | 0 | 0 | 0
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 1117.22 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 1117.22 | 100
Total On-Site and Utility Electric Sources | 1117.22 | 100
Total Electricity End Uses | 1117.22 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
LGSTORE1_WALL_2 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
LGSTORE2_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 0 | 90 | N
LGSTORE2_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 78.94 | 180 | 90 | S
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 348.39 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS | 0.3 | 0.364 | 0.38 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOFS | 0.3 | 0.273 | 0.29 | 174.19 | 270 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
LGSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.9 | 2.62 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
LGSTORE1_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.9 | 2.62 | 0.49 | 0.49 | No | LGSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE1_WALL_1
SMSTORE1_WALL_1_DOOR | WINDOW_SOUTH | 3.9 | 2.62 | 0.49 | 0.49 | No | SMSTORE1_WALL_1
SMSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE2_WALL_1
SMSTORE2_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | SMSTORE2_WALL_1
SMSTORE3_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE3_WALL_1
SMSTORE3_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | SMSTORE3_WALL_1
SMSTORE4_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE4_WALL_1
SMSTORE4_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | SMSTORE4_WALL_1
LGSTORE2_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_3 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_WINDOW_4 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_1 | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
LGSTORE2_WALL_1_DOOR_2 | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | LGSTORE2_WALL_1
SMSTORE5_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE5_WALL_1
SMSTORE5_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | SMSTORE5_WALL_1
SMSTORE6_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE6_WALL_1
SMSTORE6_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | SMSTORE6_WALL_1
SMSTORE7_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE7_WALL_1
SMSTORE7_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | SMSTORE7_WALL_1
SMSTORE8_WALL_1_WINDOW_1 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_WINDOW_2 | WINDOW_SOUTH | 3.24 | 2.62 | 0.49 | 0.49 | No | SMSTORE8_WALL_1
SMSTORE8_WALL_1_DOOR | WINDOW_SOUTH | 3.88 | 2.62 | 0.49 | 0.49 | No | SMSTORE8_WALL_1
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37499.38 | 2.96
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17106.37 | 3.05
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17009.02 | 3.05
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17002.92 | 3.05
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17018.32 | 3.05
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32307.75 | 2.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17019.14 | 3.05
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17013.81 | 3.05
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17153.94 | 3.05
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22084.98 | 2.96
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 2.27 | 3236.2 | 1 | General
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.03 | 1476.28 | 1 | General
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.03 | 1467.88 | 1 | General
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.03 | 1467.35 | 1 | General
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.03 | 1468.68 | 1 | General
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.95 | 2788.16 | 1 | General
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.03 | 1468.75 | 1 | General
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.03 | 1468.29 | 1 | General
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.04 | 1480.39 | 1 | General
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.35 | 500 | 1.33 | 1905.93 | 1 | General
Nominal Capacity [W]
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 91284.84
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 43461.27
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 43325.4
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 43316.89
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 43338.39
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 84266.24
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 43339.53
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 43332.08
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 43527.67
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 50268.78
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 52558.9095 | 54.5956 | 144.1857 | 0 | 0.0006 | 28905.4396 | 19250.1304
February | 45238.9056 | 47.2434 | 129.3651 | 0 | 0.0005 | 25936.2825 | 16607.813
March | 39100.2408 | 42.113 | 138.5951 | 0 | 0.0005 | 27796.4707 | 14551.2385
April | 26212.6821 | 29.6382 | 122.3251 | 0 | 0.0004 | 24541.9562 | 9971.4432
May | 19000.9694 | 23.1 | 122.4773 | 0 | 0.0004 | 24579.9692 | 7476.7362
June | 18159.3724 | 22.5852 | 127.6893 | 0 | 0.0004 | 25627.6601 | 7223.8135
July | 18765.3185 | 23.4136 | 133.514 | 0 | 0.0005 | 26796.9426 | 7476.3636
August | 18849.3601 | 23.3153 | 129.8608 | 0 | 0.0004 | 26063.1073 | 7478.5772
September | 20124.321 | 23.9847 | 119.6564 | 0 | 0.0004 | 24012.2366 | 7844.7561
October | 29604.3622 | 33.0822 | 129.9749 | 0 | 0.0005 | 26074.9147 | 11201.5028
November | 42791.098 | 45.4116 | 137.5225 | 0 | 0.0005 | 27577.2144 | 15820.6787
December | 49458.0753 | 51.8398 | 145.4114 | 0 | 0.0006 | 29154.827 | 18186.0109
Annual Sum or Average | 379863.6151 | 420.3227 | 1580.5778 | 0 | 0.0057 | 317067.0209 | 143089.0639
Minimum of Months | 18159.3724 | 22.5852 | 119.6564 | 0 | 0.0004 | 24012.2366 | 7223.8135
Maximum of Months | 52558.9095 | 54.5956 | 145.4114 | 0 | 0.0006 | 29154.827 | 19250.1304
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 101851000000 | 62905.253 | 19-JAN-15:39 | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 91389300000 | 62905.253 | 27-FEB-17:00 | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 97943900000 | 62905.253 | 01-MAR-17:00 | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 86476200000 | 59155.299 | 01-APR-09:09 | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 86610200000 | 73439.039 | 24-MAY-14:00 | 32837.857 | 8089.532 | 18227.909 | 0 | 14283.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 90301800000 | 87110.028 | 20-JUN-16:00 | 32837.857 | 8089.532 | 18227.909 | 0 | 27954.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 94421900000 | 92135.696 | 29-JUL-16:00 | 32837.857 | 8089.532 | 18227.909 | 0 | 32980.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 91836200000 | 85571.419 | 15-AUG-16:00 | 32837.857 | 8089.532 | 18227.909 | 0 | 26416.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 84609700000 | 62033.437 | 02-SEP-15:00 | 32837.857 | 8089.532 | 18227.909 | 0 | 2878.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 91877800000 | 62905.253 | 23-OCT-08:09 | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 97171300000 | 62905.253 | 14-NOV-15:50 | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 102730000000 | 62905.253 | 01-DEC-09:09 | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1117220000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 84609700000 | 59155.299 |  | 32837.857 | 8089.532 | 18227.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 102730000000 | 92135.696 |  | 32837.857 | 8089.532 | 18227.909 | 0 | 32980.398 | 3749.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29872.46 | 12720.73 | 0 | 42593.2
Cost per Total Building Area ($/m2) | 14.29 | 6.09 | 0 | 20.38
Cost per Net Conditioned Building Area ($/m2) | 14.29 | 6.09 | 0 | 20.38

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.39 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 48.8508 | 43.4798 | 35.116 | 38.5122 | 25.8483 | 34.0541 | 26.4523 | 38.6298 | 33.7787 | 27.6653 | 39.4901 | 32.1868 | 41.2219 | 35.268 | 39.1184 | 37.4994
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 25.6349 | 22.8854 | 18.9002 | 20.4526 | 13.068 | 18.4863 | 12.3022 | 20.5954 | 15.227 | 12.9179 | 19.2934 | 15.0983 | 18.5557 | 16.3848 | 16.9977 | 17.1064
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 24.7783 | 21.0195 | 17.9318 | 18.6179 | 11.0581 | 16.6984 | 10.9665 | 18.6957 | 14.1244 | 11.7425 | 18.6932 | 14.9879 | 19.4215 | 16.2756 | 18.727 | 17.009
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 24.455 | 20.6203 | 17.7531 | 18.2037 | 10.5951 | 16.2928 | 10.8129 | 18.2328 | 14.1134 | 11.6066 | 18.9402 | 14.9803 | 19.6575 | 16.2686 | 18.8043 | 17.0029
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 24.0067 | 20.3526 | 17.4449 | 17.9341 | 10.2967 | 15.9566 | 10.7411 | 18.3358 | 14.1301 | 11.5877 | 19.1428 | 14.9973 | 19.8521 | 16.286 | 18.8635 | 17.0183
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 39.2904 | 33.3965 | 29.276 | 34.5467 | 18.0317 | 25.7823 | 18.812 | 36.601 | 26.5589 | 22.1496 | 37.5165 | 28.082 | 41.2035 | 30.6491 | 37.0845 | 32.3077
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 21.0298 | 17.8462 | 15.4982 | 18.2658 | 9.1989 | 13.8765 | 9.8449 | 19.3553 | 14.1319 | 11.7853 | 19.9701 | 14.9984 | 21.6933 | 16.2869 | 19.5145 | 17.0191
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 20.8801 | 17.7093 | 15.4314 | 18.2899 | 9.1435 | 13.7932 | 9.8454 | 19.397 | 14.1332 | 11.8033 | 19.9649 | 14.9941 | 21.7398 | 16.2811 | 19.5513 | 17.0138
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 20.7862 | 17.6297 | 15.5288 | 18.5872 | 9.1932 | 13.8514 | 9.9004 | 19.6426 | 14.334 | 11.9275 | 20.1693 | 15.1547 | 21.907 | 16.4392 | 19.6869 | 17.1539
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 20.118 | 20.4334 | 16.2532 | 22.922 | 10.256 | 14.8701 | 11.5289 | 24.3896 | 17.794 | 14.4832 | 25.5342 | 19.0061 | 26.9639 | 20.7779 | 24.1431 | 22.085
Heating (kW)
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 29.4794 | 47.5663 | 39.1745 | 52.943 | 34.0195 | 44.1205 | 39.5102 | 59.118 | 50.6716 | 49.4025 | 65.3343 | 58.4939 | 72.5195 | 69.3863 | 74.1612 | 91.2848
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 13.7345 | 23.0588 | 19.4015 | 25.3321 | 16.5962 | 21.4505 | 19.5489 | 28.3301 | 24.282 | 23.759 | 31.2826 | 28.0879 | 34.6247 | 33.2473 | 35.6061 | 43.4613
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 13.4763 | 22.9437 | 19.3487 | 25.1437 | 16.367 | 21.2982 | 19.4864 | 28.1757 | 24.1867 | 23.6892 | 31.1531 | 27.9594 | 34.4909 | 33.113 | 35.4898 | 43.3254
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 13.4419 | 22.9323 | 19.3431 | 25.1261 | 16.3337 | 21.2761 | 19.4803 | 28.1634 | 24.1738 | 23.6773 | 31.1441 | 27.9505 | 34.4823 | 33.1044 | 35.4825 | 43.3169
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 13.4783 | 22.9457 | 19.3516 | 25.1515 | 16.3815 | 21.3022 | 19.4895 | 28.1818 | 24.1935 | 23.6906 | 31.1638 | 27.9703 | 34.5033 | 33.1257 | 35.5036 | 43.3384
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 25.995 | 43.8478 | 36.8182 | 48.4629 | 31.4855 | 40.7325 | 37.1062 | 54.3037 | 46.3972 | 45.336 | 60.0938 | 53.717 | 66.67 | 63.8894 | 68.6701 | 84.2662
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 13.4871 | 22.9476 | 19.3527 | 25.1543 | 16.3901 | 21.3063 | 19.4907 | 28.1837 | 24.1956 | 23.6926 | 31.1651 | 27.9717 | 34.5045 | 33.1269 | 35.5046 | 43.3395
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 13.5048 | 22.9525 | 19.3533 | 25.1576 | 16.3908 | 21.3145 | 19.4915 | 28.1855 | 24.1971 | 23.6986 | 31.1603 | 27.9666 | 34.4978 | 33.1198 | 35.4955 | 43.3321
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 13.8727 | 23.1192 | 19.4368 | 25.4309 | 16.677 | 21.4766 | 19.5686 | 28.4183 | 24.3705 | 23.8239 | 31.3491 | 28.1535 | 34.6914 | 33.3142 | 35.6576 | 43.5277
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 16.7787 | 26.4357 | 21.8135 | 29.4824 | 18.8704 | 24.6411 | 21.8935 | 32.9437 | 28.4091 | 27.4983 | 36.3063 | 32.5418 | 40.103 | 38.5354 | 40.7723 | 50.2688
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 2.78 | 2.78 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.78 | 2.96 | 2.96 | 2.96
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 3.05
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 3.05
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 3.05 | 3.05
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.78 | 2.96 | 2.96 | 2.96
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 2.96 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 2.96 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 2.96 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05 | 2.96 | 3.05
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 2.96 | 2.96 | 3.05 | 2.96 | 3.05 | 3.05 | 3.05 | 2.96 | 3.05 | 3.05 | 2.96 | 3.05 | 2.96 | 2.96 | 2.96 | 2.96
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | None
Fan Max Flow Rate (m3/s )
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 2.02 | 1.86 | 2.12 | 1.72 | 1.56 | 2.06 | 1.6 | 1.71 | 2.04 | 1.67 | 1.74 | 1.94 | 1.93 | 2.13 | 1.99 | 2.27
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 1.1 | 1.01 | 1.14 | 0.94 | 0.79 | 1.12 | 0.74 | 0.94 | 0.92 | 0.78 | 0.88 | 0.91 | 0.89 | 0.99 | 0.93 | 1.03
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 1.01 | 0.88 | 1.08 | 0.81 | 0.67 | 1.01 | 0.66 | 0.81 | 0.85 | 0.69 | 0.8 | 0.91 | 0.89 | 0.98 | 0.92 | 1.03
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 0.98 | 0.86 | 1.07 | 0.78 | 0.64 | 0.98 | 0.65 | 0.78 | 0.85 | 0.69 | 0.8 | 0.9 | 0.89 | 0.98 | 0.92 | 1.03
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 0.97 | 0.84 | 1.05 | 0.77 | 0.62 | 0.96 | 0.65 | 0.78 | 0.85 | 0.68 | 0.8 | 0.91 | 0.89 | 0.98 | 0.93 | 1.03
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.58 | 1.34 | 1.73 | 1.39 | 1.08 | 1.56 | 1.14 | 1.47 | 1.6 | 1.28 | 1.51 | 1.7 | 1.67 | 1.85 | 1.75 | 1.95
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 0.85 | 0.72 | 0.93 | 0.74 | 0.55 | 0.84 | 0.59 | 0.78 | 0.85 | 0.68 | 0.8 | 0.91 | 0.89 | 0.98 | 0.93 | 1.03
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 0.84 | 0.71 | 0.93 | 0.74 | 0.55 | 0.83 | 0.59 | 0.78 | 0.85 | 0.68 | 0.8 | 0.91 | 0.89 | 0.98 | 0.93 | 1.03
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 0.84 | 0.71 | 0.93 | 0.75 | 0.55 | 0.84 | 0.6 | 0.79 | 0.87 | 0.69 | 0.81 | 0.92 | 0.9 | 0.99 | 0.93 | 1.04
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 0.81 | 0.82 | 0.98 | 0.93 | 0.62 | 0.9 | 0.7 | 0.99 | 1.07 | 0.85 | 1.03 | 1.15 | 1.14 | 1.26 | 1.17 | 1.33
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.086533 | 0.1243 | 0.10484 | 0.10217 | 0.13284 | 0.099632 | 0.15121 | 0.078697 | 0.037538 | 0.076559 | 0.052331 | 0.037558 | 0.063048 | 0.076643 | 0.061342 | 0.096258
| Total Cost ($/m2) | 18.31 | 22.03 | 19.55 | 15.74 | 16.99 | 16.95 | 18.65 | 11.91 | 5.66 | 9.76 | 7.68 | 5.5 | 9.45 | 11.22 | 8.8 | 14.29
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011423 | 0.008045 | 0.0081317 | 0.009482 | 0.0086783 | 0.0076189 | 0.0086054 | 0.009651 | 0.0068554 | 0.008432 | 0.0082743 | 0.0068837 | 0.0078809 | 0.0080308 | 0.0078632 | 0.0041136
| Total Cost ($/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Utility Costs
| Cost Intensity ($/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 168741.6666 | 105761.1111 | 108713.8889 | 58027.7778 | 19277.7778 | 80913.8889 | 7341.6667 | 48341.6667 | 41388.8889 | 9758.3333 | 36502.7778 | 27333.3333 | 31683.3333 | 17386.1111 | 13563.8889 | 6663.8889
| Interior Lighting | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725
| Exterior Lighting | 16391.6667 | 16386.1111 | 16380.5556 | 16380.5556 | 16366.6667 | 16363.8889 | 16372.2222 | 16361.1111 | 16366.6667 | 16336.1111 | 16363.8889 | 16355.5556 | 16352.7778 | 16350 | 16341.6667 | 16241.6667
| Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 82986.1111 | 74094.4444 | 90427.7778 | 73358.3333 | 57527.7778 | 84052.7778 | 59880.5555 | 77441.6667 | 83477.7778 | 66294.4444 | 79883.3333 | 87958.3333 | 90916.6667 | 97952.7778 | 95786.1111 | 113233.3333
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 442322.2221 | 370441.6666 | 389724.9999 | 321969.4444 | 267375 | 355533.3333 | 257794.4444 | 316349.9999 | 315436.1111 | 266591.6666 | 306952.7777 | 305849.9999 | 313155.5555 | 305891.6666 | 299891.6666 | 310338.8888
Gas (MJ)
| Heating | 9670 | 224130 | 149410 | 448790 | 117070 | 227450 | 359370 | 798890 | 485770 | 720730 | 1113380 | 750770 | 1545370 | 1202440 | 1861150 | 3092360
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 9670 | 224130 | 149410 | 448790 | 117070 | 227450 | 359370 | 798890 | 485770 | 720730 | 1113380 | 750770 | 1545370 | 1202440 | 1861150 | 3092360
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1602020 | 1557720 | 1552420 | 1607870 | 1079620 | 1507370 | 1287430 | 1937750 | 1621350 | 1680460 | 2218410 | 1851830 | 2672720 | 2303650 | 2940760 | 4209580
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 290.611 | 182.1444 | 187.2297 | 99.9369 | 33.2007 | 139.3519 | 12.644 | 83.2552 | 71.281 | 16.806 | 62.866 | 47.0741 | 54.5658 | 29.9428 | 23.3601 | 11.4767
| Interior Lighting (elec) | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822
| Exterior Lighting (elec) | 28.2301 | 28.2206 | 28.211 | 28.211 | 28.1871 | 28.1823 | 28.1966 | 28.1775 | 28.1871 | 28.1344 | 28.1823 | 28.1679 | 28.1632 | 28.1584 | 28.144 | 27.9718
| Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 142.9207 | 127.6073 | 155.7369 | 126.3395 | 99.0757 | 144.7577 | 103.1278 | 133.3719 | 143.7675 | 114.1739 | 137.577 | 151.484 | 156.5789 | 168.6967 | 164.9652 | 195.0132
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 761.7781 | 637.9837 | 671.1939 | 554.5036 | 460.4797 | 612.3082 | 443.9799 | 544.8257 | 543.2518 | 459.1307 | 528.6415 | 526.7423 | 539.3241 | 526.8141 | 516.4807 | 534.4732
Gas (MJ/m2)
| Heating (gas) | 4.6261 | 107.2228 | 71.4771 | 214.6992 | 56.0058 | 108.8111 | 171.921 | 382.1855 | 232.3903 | 344.7941 | 532.6362 | 359.1651 | 739.2983 | 575.2421 | 890.3661 | 1479.3716
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4.6261 | 107.2228 | 71.4771 | 214.6992 | 56.0058 | 108.8111 | 171.921 | 382.1855 | 232.3903 | 344.7941 | 532.6362 | 359.1651 | 739.2983 | 575.2421 | 890.3661 | 1479.3716
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 766.3994 | 745.2065 | 742.671 | 769.198 | 516.4855 | 721.1193 | 615.9009 | 927.0112 | 775.6468 | 803.9248 | 1061.2777 | 885.9074 | 1278.6176 | 1102.0561 | 1406.8468 | 2013.8448
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 101.7633 | 89.8567 | 79.8475 | 62.8651 | 72.1906 | 62.2604 | 56.0005 | 58.7505 | 60.2336 | 57.1104 | 58.9452 | 60.7837 | 60.3605 | 62.0165 | 60.9541 | 62.9053
| Feb | 107.5908 | 90.0321 | 85.356 | 68.4454 | 67.4349 | 69.4997 | 65.1772 | 58.7505 | 69.7531 | 57.1104 | 58.9452 | 60.6013 | 60.3605 | 62.0165 | 60.9541 | 62.9053
| Mar | 109.2411 | 95.6729 | 99.3353 | 76.9555 | 70.051 | 79.4246 | 56.0005 | 77.7557 | 70.9427 | 62.0384 | 66.6893 | 73.9242 | 60.3605 | 68.8959 | 60.9541 | 62.9053
| Apr | 114.5363 | 110.1828 | 101.9942 | 93.8202 | 77.5265 | 98.6154 | 69.5216 | 80.249 | 87.575 | 66.1737 | 71.518 | 80.716 | 71.1425 | 63.598 | 60.9822 | 59.1553
| May | 123.3012 | 116.5637 | 119.9933 | 100.4817 | 73.673 | 107.9419 | 70.9618 | 95.3356 | 92.1371 | 74.2339 | 96.0494 | 88.2394 | 121.0396 | 81.9279 | 77.4287 | 73.439
| Jun | 128.5121 | 117.1657 | 132.6145 | 108.8347 | 73.2778 | 123.2097 | 72.8336 | 119.6682 | 103.1548 | 79.4894 | 115.9537 | 98.4286 | 117.3988 | 105.5828 | 98.5617 | 87.11
| Jul | 124.667 | 123.1259 | 131.5618 | 120.0049 | 76.6686 | 122.2493 | 81.7087 | 123.5063 | 107.8943 | 87.7314 | 117.8678 | 102.585 | 122.8647 | 103.4819 | 107.6719 | 92.1357
| Aug | 129.617 | 122.9318 | 132.5518 | 112.5383 | 84.1449 | 121.4126 | 76.0165 | 125.3662 | 105.2085 | 84.4765 | 115.8619 | 104.2031 | 115.5241 | 98.6807 | 109.0417 | 85.5714
| Sep | 123.6378 | 122.0346 | 123.2403 | 103.9156 | 82.2479 | 118.8148 | 92.6465 | 106.4324 | 93.7435 | 101.2012 | 97.9832 | 98.243 | 100.092 | 93.3209 | 89.6206 | 62.0334
| Oct | 121.1686 | 105.7535 | 101.5846 | 95.1794 | 75.4481 | 98.2635 | 71.3556 | 92.7053 | 83.6921 | 64.5385 | 79.5815 | 87.8485 | 85.8342 | 77.0164 | 82.0271 | 62.9053
| Nov | 110.1902 | 93.7462 | 93.3127 | 70.3149 | 71.335 | 71.4581 | 56.2137 | 83.5388 | 65.6141 | 57.5773 | 77.1581 | 66.1195 | 60.7106 | 62.0165 | 60.9541 | 62.9053
| Dec | 100.8845 | 92.258 | 77.7289 | 60.4982 | 72.7297 | 69.18 | 56.0005 | 58.7505 | 60.0668 | 57.1104 | 58.9452 | 60.5985 | 60.3605 | 62.0165 | 60.9541 | 62.9053
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-13:00 | 28-JAN-14:00 | 23-JAN-16:00 | 26-JAN-13:00 | 18-JAN-14:00 | 02-JAN-16:00 | 02-JAN-16:49 | 25-JAN-17:30 | 02-JAN-16:30 | 02-JAN-16:40 | 27-JAN-17:10 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 19-JAN-15:39
| Feb | 25-FEB-13:00 | 23-FEB-15:30 | 28-FEB-15:00 | 18-FEB-16:19 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-15:00 | 01-FEB-17:30 | 14-FEB-15:00 | 01-FEB-17:10 | 01-FEB-16:00 | 11-FEB-17:30 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 27-FEB-17:00
| Mar | 13-MAR-15:39 | 25-MAR-16:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:39 | 31-MAR-15:00 | 01-MAR-17:00 | 09-MAR-15:00 | 25-MAR-15:50 | 29-MAR-15:00 | 31-MAR-14:00 | 30-MAR-15:00 | 01-MAR-17:00 | 30-MAR-16:00 | 01-MAR-17:49 | 01-MAR-17:00
| Apr | 01-APR-15:39 | 29-APR-14:50 | 01-APR-16:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-14:50 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 06-APR-16:00 | 04-APR-14:00 | 01-APR-09:09
| May | 24-MAY-14:00 | 18-MAY-14:00 | 27-MAY-15:00 | 15-MAY-14:00 | 30-MAY-14:09 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-16:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-16:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:50 | 30-JUN-14:00 | 29-JUN-14:09 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 19-JUL-16:00 | 03-JUL-14:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-14:00 | 15-JUL-14:00 | 21-JUL-15:00 | 08-JUL-15:09 | 29-JUL-16:00
| Aug | 21-AUG-14:50 | 31-AUG-15:00 | 01-AUG-16:00 | 17-AUG-14:30 | 08-AUG-14:00 | 04-AUG-14:00 | 15-AUG-12:09 | 17-AUG-14:00 | 01-AUG-14:09 | 07-AUG-14:00 | 04-AUG-15:30 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
| Sep | 11-SEP-14:00 | 16-SEP-14:00 | 09-SEP-15:00 | 11-SEP-13:00 | 23-SEP-13:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:39 | 02-SEP-14:00 | 02-SEP-15:50 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 02-SEP-15:00
| Oct | 06-OCT-14:00 | 06-OCT-15:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-15:00 | 03-OCT-14:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 23-OCT-08:09
| Nov | 07-NOV-15:09 | 03-NOV-15:09 | 13-NOV-15:00 | 22-NOV-15:20 | 20-NOV-13:39 | 10-NOV-15:20 | 08-NOV-17:10 | 04-NOV-13:00 | 08-NOV-15:39 | 04-NOV-14:00 | 02-NOV-15:09 | 10-NOV-13:00 | 02-NOV-15:09 | 01-NOV-17:10 | 01-NOV-16:49 | 14-NOV-15:50
| Dec | 19-DEC-14:30 | 02-DEC-14:00 | 09-DEC-15:00 | 13-DEC-15:30 | 19-DEC-12:00 | 05-DEC-14:00 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 121480.7787 | 127606.4723 | 120342.8502 | 107270.9713 | 33358.0359 | 124013.8579 | 36607.7983 | 99774.662 | 137615.046 | 32413.6846 | 183729.2441 | 138477.7435 | 135057.7404 | 133467.0742 | 136212.5846 | 143089.0639
| CO2 (kg) | 281395.2742 | 321736.6697 | 284458.2188 | 248476.4743 | 89523.4295 | 295863.9525 | 99158.1987 | 233063.9256 | 325553.9971 | 83674.6972 | 435596.6163 | 330235.8231 | 327630.0708 | 322641.7413 | 333616.8673 | 379863.6151
| NOX (kg) | 495.8392 | 418.1462 | 474.691 | 455.8852 | 76.9296 | 476.5205 | 85.8325 | 420.5572 | 549.7689 | 108.2008 | 740.214 | 546.2941 | 524.0384 | 518.3906 | 519.8772 | 420.3227
| SO2 (kg) | 1893.314 | 1767.0658 | 1567.2049 | 1130.2299 | 778.0587 | 1955.7749 | 750.2486 | 1155.0149 | 1377.5789 | 206.2464 | 2068.9189 | 1335.7901 | 739.509 | 817.0863 | 708.2923 | 1580.5778
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0086 | 0.005 | 0.0043 | 0.0042 | 0.0004 | 0.0037 | 0.0004 | 0.0047 | 0.0054 | 0.0009 | 0.0064 | 0.0053 | 0.0056 | 0.0058 | 0.0054 | 0.0057
| Water Environmental Factors (m3) | 234.3232 | 602.7517 | 11576.6 | 2010.2424 | 4694.4946 | 9753.6816 | 4526.3011 | 71.8231 | 1432.3343 | 2723.7038 | 476.2199 | 1388.8066 | 485.8406 | 19376.4 | 465.2648 | 317.067

## Picture
DOE Commercial Building Benchmark - Strip Mall

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400 | 16800 | 876000