## BuildingSummary
Building Summary Super Market new construction version 1.0_3.0
|  | Value | Data Source
Program
| Building Name | Benchmark Super Market
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Sales
Form
| Total Floor Area (ft2) | 45001.6 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.362 East: 0.00 North: 0.00 West: 0.00 Total: 0.109
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Office, DryStorage, Deli, Sales, Produce, Bakery
| Floor to Ceiling Height (ft) | 20
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 17320.85
| Net Dimensions - Total Area (ft2) | 15440.29
| Wall to Skin Ratio | 0.28
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (ft2) | 45001.6
| Net Dimensions - Total Area (ft2) | 45001.6
| Roof to Skin Ratio | 0.72
Window
| Dimensions - Total Area (ft2) | South: 1,880.5 East: 0.00 North: 0.00 West: 0.00 Total: 1,880.5
| Operable area (ft2) | 0
Skylights/TDD
| Dimensions - Total Area (ft2) | 0
| Operable area (ft2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (ft2) | 45001.6
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 6 inch wood
| Dimensions - Total Area (ft2) | 90003
| Thermal Properties (lb/ft2 ) | 16.6
Air Barrier System
| Infiltration (ACH) | 0.25 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºF ) | N/A
| Water Consumption (gal ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (ft2) | Volume (ft3) | Floor-to-Ceiling Height (ft) | Gross Wall Area (ft2) | Window Glass Area (ft2) | People (ft2/per) | People | Lights (W/ft2) | Elec Plug and Process (W/ft2) | Gas Plug and Process (W/ft2) | SWH (gal/h) | Ventilation (cfm/Person) | Ventilation (cfm/ft2) | Ventilation Total (cfm) | Exhaust (cfm) | Infiltration (ACH)
Office | Yes | 1 | 956.2649 | 19130.663 | 20.0056 | 1238.7108 | 0 | 200 | 4.7813 | 1.1 | 0.75 | 0 | 0 | 20 | 0 | 95.6265 | 0 | 0.40969
DryStorage | Yes | 1 | 6693.9618 | 133914.2881 | 20.0052 | 5136.9684 | 0 | 300 | 22.3132 | 0.8 | 0.75 | 0 | 0 | 0 | 0.15 | 1004.0943 | 0 | 0.31547
Deli | Yes | 1 | 2418.8636 | 48389.5734 | 20.0051 | 1490.0481 | 0 | 125 | 19.3509 | 1.7 | 5 | 2.5 | 5 | 0 | 0.3 | 725.6591 | 0 | 0.28845
Sales | Yes | 1 | 25025.4217 | 500641.9507 | 20.0053 | 3482.3402 | 1880.4551 | 125 | 200.2034 | 1.7 | 0.5 | 0 | 0 | 0 | 0.3 | 7507.6265 | 0 | 0.20333
Produce | Yes | 1 | 7657.0079 | 153181.2657 | 20.0054 | 3941.5286 | 0 | 125 | 61.2561 | 1.7 | 0.5 | 0 | 0 | 0 | 0.3 | 2297.1024 | 0 | 0.27037
Bakery | Yes | 1 | 2250.0857 | 45013.8441 | 20.0054 | 2035.7783 | 0 | 125 | 18.0007 | 1.7 | 2.5 | 5 | 5 | 0 | 0.3 | 675.0257 | 2500 | 0.33998
Total Conditioned Zones |  |  | 45001.6055 | 900271.5851 |  | 17325.3743 | 1880.4551 |  | 325.9056 | [6 empty] | 12305.1344 | 2500
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## Query (hidden)
1-miami
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8867.81 | 2121.08 | 2121.08
Net Site Energy | 8867.81 | 2121.08 | 2121.08
Total Source Energy | 28524.57 | 6822.76 | 6822.76
Net Source Energy | 28524.57 | 6822.76 | 6822.76
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 89.2 | 0 | 0 | 0 | 0
Cooling | 1093.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 885.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 15.87 | 0 | 0 | 0 | 87.12
Refrigeration | 4808.77 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8467.83 | 399.98 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 8467.83 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 8467.83 | 100
Total On-Site and Utility Electric Sources | 8467.83 | 100
Total Electricity End Uses | 8467.83 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 2.61 | 4.28 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 6.88 | 0.25 | 0.25 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12198.97 | 2.73
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 89675.56 | 2.73
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53676.97 | 2.73
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 181291.07 | 2.73
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 101043.87 | 2.73
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 71401.9 | 2.73
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.7 | 1325.69 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.67 | 6952.65 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.03 | 5742.67 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 7.3 | 13843.76 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.19 | 7936.67 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.88 | 5460.16 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 5023.96
PSZ-AC:2_HEATC | 40079.11
PSZ-AC:3_HEATC | 26602.5
PSZ-AC:4_HEATC | 84794.77
PSZ-AC:5_HEATC | 45783.49
PSZ-AC:6_HEATC | 33444.15
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 115149.8374 | 200.4687 | 755.6081 | 0 | 0.0034 | 93514.89 | 49467.3187
February | 104874.9674 | 183.0519 | 691.8927 | 0 | 0.0032 | 85629.7552 | 45100.5315
March | 118534.6609 | 207.1324 | 783.8865 | 0 | 0.0036 | 97015.2453 | 50998.6501
April | 121434.9638 | 212.8851 | 808.4553 | 0 | 0.0037 | 100056.4371 | 52315.0853
May | 134554.8821 | 236.101 | 897.4979 | 0 | 0.0041 | 111076.733 | 57988.8417
June | 135426.5065 | 237.688 | 903.7656 | 0 | 0.0041 | 111852.4901 | 58370.2626
July | 143080.2868 | 251.1749 | 955.2649 | 0 | 0.0044 | 118226.2261 | 61674.4955
August | 143512.6823 | 251.9091 | 957.956 | 0 | 0.0044 | 118559.2566 | 61858.3857
September | 134695.0085 | 236.4128 | 898.9515 | 0 | 0.0041 | 111256.6948 | 58055.8394
October | 131661.3551 | 230.9914 | 877.9434 | 0 | 0.004 | 108656.5989 | 56738.5875
November | 118371.2078 | 207.4375 | 787.4548 | 0 | 0.0036 | 97457.31 | 50987.514
December | 113267.6325 | 198.0077 | 749.6776 | 0 | 0.0034 | 92781.5449 | 48740.4778
Annual Sum or Average | 1514563.991 | 2653.2605 | 10068.3543 | 0 | 0.0459 | 1246083.182 | 652295.9898
Minimum of Months | 104874.9674 | 183.0519 | 691.8927 | 0 | 0.0032 | 85629.7552 | 45100.5315
Maximum of Months | 143512.6823 | 251.9091 | 957.956 | 0 | 0.0044 | 118559.2566 | 61858.3857
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 635486000000 | 413019.414 | 23-JAN-18:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 53940.173 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 238893.244 | 0 | 0
February | 581902000000 | 425983.702 | 23-FEB-11:00 | 62886.42 | 35805.575 | 42104.392 | 0 | 73183.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212003.437 | 0 | 0
March | 659273000000 | 438404.172 | 13-MAR-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 78100.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244448.225 | 0 | 0
April | 679939000000 | 454118.862 | 03-APR-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 93569.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244693.221 | 0 | 0
May | 754828000000 | 470028.863 | 18-MAY-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 105750.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248422.123 | 0 | 0
June | 760100000000 | 499414.201 | 27-JUN-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 130313.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253245.032 | 0 | 0
July | 803413000000 | 487106.556 | 13-JUL-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 120785.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250464.935 | 0 | 0
August | 805676000000 | 489349.425 | 21-AUG-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 121799.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251693.929 | 0 | 0
September | 756051000000 | 471233.816 | 13-SEP-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 107577.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247800.638 | 0 | 0
October | 738382000000 | 471227.077 | 06-OCT-17:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 107581.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247789.579 | 0 | 0
November | 662277000000 | 442545.639 | 01-NOV-18:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 76467.82 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 245891.823 | 0 | 0
December | 630502000000 | 415610.787 | 15-DEC-18:10 | 41924.28 | 31827.177 | 42104.392 | 0 | 53245.065 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 242179.725 | 0 | 0
Annual Sum or Average | 8467830000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 581902000000 | 413019.414 |  | 41924.28 | 31827.177 | 42104.392 | 0 | 53245.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212003.437 | 0 | 0
Maximum of Months | 805676000000 | 499414.201 |  | 62886.42 | 35805.575 | 42104.392 | 0 | 130313.321 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 253245.032 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 187042.1 | 4579.77 | 0 | 191621.87
Cost per Total Building Area ($/m2) | 44.74 | 1.1 | 0 | 45.83
Cost per Net Conditioned Building Area ($/m2) | 44.74 | 1.1 | 0 | 45.83
2-houston
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8956.4 | 2142.27 | 2142.27
Net Site Energy | 8956.4 | 2142.27 | 2142.27
Total Source Energy | 1334.91 | 319.3 | 319.3
Net Source Energy | 1334.91 | 319.3 | 319.3
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 909.7 | 0 | 0 | 0 | 0
Cooling | 729.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.11 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 930.93 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 17.83 | 0 | 0 | 0 | 87.12
Refrigeration | 4392.87 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7733.95 | 1222.44 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 7733.95 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 7733.95 | 100
Total On-Site and Utility Electric Sources | 7733.95 | 100
Total Electricity End Uses | 7733.95 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 2.61 | 4.28 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 6.88 | 0.25 | 0.25 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11674.62 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 77638.04 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 50362.38 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 224140.4 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88152.43 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64347.48 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.68 | 1296.3 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.36 | 6367.75 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.96 | 5606.73 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 9.03 | 17115.83 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.85 | 7300.38 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.83 | 5370.71 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4913.88
PSZ-AC:2_HEATC | 49423.41
PSZ-AC:3_HEATC | 30098.19
PSZ-AC:4_HEATC | 138398.65
PSZ-AC:5_HEATC | 56593.88
PSZ-AC:6_HEATC | 43427.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 139170.7924 | 177.5308 | 717.5428 | 0 | 0.002 | 244741.1303 | 54766.6904
February | 123514.8961 | 157.234 | 632.2634 | 0 | 0.0018 | 215652.2843 | 48563.7915
March | 139680.2467 | 180.9413 | 758.8333 | 0 | 0.0021 | 258837.7454 | 55323.0108
April | 146826.2645 | 191.8591 | 820.9167 | 0 | 0.0023 | 280021.8987 | 58367.4134
May | 166303.5628 | 217.8729 | 937.6967 | 0 | 0.0026 | 319859.0487 | 66182.6981
June | 175595.194 | 230.2499 | 992.946 | 0 | 0.0028 | 338706.0953 | 69906.7355
July | 187487.2192 | 245.8787 | 1060.6867 | 0 | 0.003 | 361813.4455 | 74645.6556
August | 185325.2564 | 243.0075 | 1047.9526 | 0 | 0.0029 | 357469.5438 | 73780.2682
September | 166387.3842 | 218.1253 | 940.166 | 0 | 0.0026 | 320701.9624 | 66234.4318
October | 156081.6224 | 204.1081 | 874.8342 | 0 | 0.0025 | 298414.2909 | 62066.6403
November | 137945.4001 | 179.1901 | 756.3577 | 0 | 0.0021 | 257995.5636 | 54699.8483
December | 137515.4717 | 175.32 | 707.6192 | 0 | 0.002 | 241355.8775 | 54102.502
Annual Sum or Average | 1861833.3105 | 2421.3176 | 10247.8154 | 0 | 0.0289 | 3495568.8864 | 738639.686
Minimum of Months | 123514.8961 | 157.234 | 632.2634 | 0 | 0.0018 | 215652.2843 | 48563.7915
Maximum of Months | 187487.2192 | 245.8787 | 1060.6867 | 0 | 0.003 | 361813.4455 | 74645.6556
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 541490000000 | 391807.927 | 20-JAN-18:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 30136.854 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 239688.976 | 0 | 0
February | 477131000000 | 374504.423 | 15-FEB-18:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 18617.248 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 233905.078 | 0 | 0
March | 572679000000 | 401447.665 | 25-MAR-17:10 | 34936.9 | 27848.78 | 43900.492 | 0 | 52538.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242223.389 | 0 | 0
April | 619549000000 | 430485.813 | 29-APR-17:10 | 34936.9 | 27848.78 | 43900.492 | 0 | 80446.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243353.32 | 0 | 0
May | 707689000000 | 477478.484 | 26-MAY-17:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 109208.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250618.525 | 0 | 0
June | 749388000000 | 482236.814 | 13-JUN-17:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 113956.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250628.704 | 0 | 0
July | 800513000000 | 498753.25 | 05-JUL-17:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 127713.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253387.659 | 0 | 0
August | 790902000000 | 496664.626 | 31-AUG-17:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 126307.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252705.517 | 0 | 0
September | 709554000000 | 471270.483 | 15-SEP-17:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 101203.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252415.252 | 0 | 0
October | 660242000000 | 431390.362 | 06-OCT-17:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 71530.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242207.728 | 0 | 0
November | 570816000000 | 410937.703 | 27-NOV-18:10 | 41924.28 | 31827.177 | 43900.492 | 0 | 41597.552 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 247358.055 | 0 | 0
December | 534000000000 | 389772.872 | 02-DEC-11:00 | 62886.42 | 35805.575 | 43900.492 | 0 | 35763.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211417.151 | 0 | 0
Annual Sum or Average | 7733950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 477131000000 | 374504.423 |  | 34936.9 | 27848.78 | 43900.492 | 0 | 18617.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211417.151 | 0 | 0
Maximum of Months | 800513000000 | 498753.25 |  | 62886.42 | 35805.575 | 43900.492 | 0 | 127713.642 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 253387.659 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 233544.92 | 9892.09 | 0 | 243437.02
Cost per Total Building Area ($/m2) | 55.86 | 2.37 | 0 | 58.23
Cost per Net Conditioned Building Area ($/m2) | 55.86 | 2.37 | 0 | 58.23
3-phoenix
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8322.23 | 1990.59 | 1990.59
Net Site Energy | 8322.23 | 1990.59 | 1990.59
Total Source Energy | 24072.31 | 5757.83 | 5757.83
Net Source Energy | 24072.31 | 5757.83 | 5757.83
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 775.26 | 0 | 0 | 0 | 0
Cooling | 773.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1026.36 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 16.7 | 0 | 0 | 0 | 87.12
Refrigeration | 3755.43 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7235.36 | 1086.87 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 7235.36 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 7235.36 | 100
Total On-Site and Utility Electric Sources | 7235.36 | 100
Total Electricity End Uses | 7235.36 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 2.61 | 4.28 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 6.88 | 0.25 | 0.25 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14519.21 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70440.62 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54287.58 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 144768.04 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 78563.08 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53125.62 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.88 | 1663.21 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.26 | 8069.16 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.28 | 6218.78 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 8.56 | 16233.52 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.75 | 8999.6 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.21 | 6085.68 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 6009.26
PSZ-AC:2_HEATC | 48017.12
PSZ-AC:3_HEATC | 29190.5
PSZ-AC:4_HEATC | 110747.05
PSZ-AC:5_HEATC | 54132.1
PSZ-AC:6_HEATC | 41517.24
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 107121.1153 | 172.4046 | 544.2095 | 0 | 0.0015 | 4019628.0157 | 44676.0787
February | 95522.2357 | 154.5124 | 490.8937 | 0 | 0.0013 | 3625869.9702 | 39917.0571
March | 111794.407 | 184.868 | 603.7026 | 0 | 0.0016 | 4459321.642 | 47124.8808
April | 110806.4928 | 184.7472 | 609.3118 | 0 | 0.0017 | 4500831.7855 | 46861.4266
May | 123774.4494 | 207.457 | 688.4947 | 0 | 0.0019 | 5085790.7439 | 52455.7983
June | 139901.0894 | 235.291 | 784.0177 | 0 | 0.0021 | 5791441.9748 | 59371.6287
July | 160540.3235 | 270.2668 | 901.5904 | 0 | 0.0024 | 6659950.4147 | 68157.2479
August | 157219.3796 | 264.6405 | 882.6835 | 0 | 0.0024 | 6520285.4202 | 66743.7577
September | 141061.6239 | 237.2995 | 790.9309 | 0 | 0.0021 | 5842511.6177 | 59869.8633
October | 120329.8088 | 201.1458 | 665.4445 | 0 | 0.0018 | 4915496.5523 | 50941.5863
November | 107096.7228 | 177.1077 | 578.3922 | 0 | 0.0016 | 4272364.2971 | 45145.465
December | 108271.5048 | 173.2143 | 542.5179 | 0 | 0.0015 | 4007076.8062 | 45050.519
Annual Sum or Average | 1483439.153 | 2462.9548 | 8082.1894 | 0 | 0.022 | 59700600 | 626315.3096
Minimum of Months | 95522.2357 | 154.5124 | 490.8937 | 0 | 0.0013 | 3625869.9702 | 39917.0571
Maximum of Months | 160540.3235 | 270.2668 | 901.5904 | 0 | 0.0024 | 6659950.4147 | 68157.2479
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 487155000000 | 330257.593 | 27-JAN-18:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 10393.075 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 193670.175 | 0 | 0
February | 439434000000 | 350914.54 | 28-FEB-18:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 29549.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199500.615 | 0 | 0
March | 540444000000 | 392429.376 | 17-MAR-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 60116.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210448.758 | 0 | 0
April | 545475000000 | 395800.762 | 26-APR-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 65335.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208600.896 | 0 | 0
May | 616368000000 | 445630.934 | 30-MAY-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 107078.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216688.608 | 0 | 0
June | 701889000000 | 515055.54 | 28-JUN-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 168038.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225153.074 | 0 | 0
July | 807147000000 | 521736.712 | 11-JUL-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 156801.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243070.558 | 0 | 0
August | 790221000000 | 515540.081 | 01-AUG-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 163839.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229836.095 | 0 | 0
September | 708078000000 | 486714.836 | 08-SEP-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 124696.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240153.853 | 0 | 0
October | 595730000000 | 419113.543 | 13-OCT-17:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 70287.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226962.066 | 0 | 0
November | 517786000000 | 366319.39 | 13-NOV-18:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 32658.359 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 207466.688 | 0 | 0
December | 485634000000 | 348521.516 | 13-DEC-18:10 | 41924.28 | 31827.177 | 48112.738 | 0 | 7001.124 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 215326.049 | 0 | 0
Annual Sum or Average | 7235360000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 439434000000 | 330257.593 |  | 41924.28 | 31827.177 | 48112.738 | 0 | 7001.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193670.175 | 0 | 0
Maximum of Months | 807147000000 | 521736.712 |  | 41924.28 | 31827.177 | 48112.738 | 0 | 168038.271 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 243070.558 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 152776.44 | 9065.39 | 0 | 161841.83
Cost per Total Building Area ($/m2) | 36.54 | 2.17 | 0 | 38.71
Cost per Net Conditioned Building Area ($/m2) | 36.54 | 2.17 | 0 | 38.71
4-atlanta
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8770.3 | 2097.76 | 2097.76
Net Site Energy | 8770.3 | 2097.76 | 2097.76
Total Source Energy | 25120.84 | 6008.63 | 6008.63
Net Source Energy | 25120.84 | 6008.63 | 6008.63
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1614.25 | 0 | 0 | 0 | 0
Cooling | 376.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.09 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 898.55 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.73 | 0 | 0 | 0 | 87.12
Refrigeration | 3885.92 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6841.41 | 1928.9 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6841.41 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6841.41 | 100
Total On-Site and Utility Electric Sources | 6841.41 | 100
Total Electricity End Uses | 6841.41 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.25 | 0.318 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10605.15 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 69088.47 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 49047.68 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 234116.8 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 72109.08 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 61017.28 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.6 | 1129.98 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.88 | 5458.21 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.96 | 5618.54 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 9.43 | 17877.65 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.03 | 5745.96 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.86 | 5417.63 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4183.89
PSZ-AC:2_HEATC | 47610.38
PSZ-AC:3_HEATC | 31129.84
PSZ-AC:4_HEATC | 155941.61
PSZ-AC:5_HEATC | 50120.38
PSZ-AC:6_HEATC | 47256.49
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 113169.5139 | 196.2868 | 459.1396 | 0 | 0.0017 | 816519.933 | 47808.9523
February | 101225.4083 | 178.3731 | 424.4205 | 0 | 0.0016 | 754807.601 | 43021.9554
March | 109117.4615 | 199.4699 | 492.7563 | 0 | 0.0018 | 876415.886 | 47040.183
April | 110174.9381 | 206.5122 | 522.5773 | 0 | 0.0019 | 929506.3042 | 47967.9059
May | 123566.4982 | 235.7673 | 606.4581 | 0 | 0.0022 | 1078744.2085 | 54181.9377
June | 129497.7322 | 248.3359 | 641.7042 | 0 | 0.0023 | 1141450.0601 | 56898.2869
July | 140216.8753 | 269.2102 | 696.382 | 0 | 0.0025 | 1238712.5739 | 61637.4341
August | 139664.1908 | 268.0714 | 693.2564 | 0 | 0.0025 | 1233152.0823 | 61387.3088
September | 128706.4476 | 246.6953 | 637.1793 | 0 | 0.0023 | 1133400.0753 | 56539.2384
October | 115328.5135 | 217.1619 | 551.8737 | 0 | 0.002 | 981625.0938 | 50303.0798
November | 106541.4654 | 193.7486 | 476.161 | 0 | 0.0018 | 846889.5045 | 45836.1883
December | 111887.5026 | 197.1315 | 468.9796 | 0 | 0.0017 | 834053.0713 | 47550.7315
Annual Sum or Average | 1429096.5476 | 2656.7641 | 6670.8879 | 0 | 0.0245 | 11865300 | 620173.2021
Minimum of Months | 101225.4083 | 178.3731 | 424.4205 | 0 | 0.0016 | 754807.601 | 43021.9554
Maximum of Months | 140216.8753 | 269.2102 | 696.382 | 0 | 0.0025 | 1238712.5739 | 61637.4341
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 470798000000 | 354828.629 | 24-JAN-18:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 9717.534 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 224938.74 | 0 | 0
February | 435215000000 | 339365.852 | 21-FEB-18:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 7282.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216241.536 | 0 | 0
March | 505333000000 | 359241.178 | 29-MAR-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 15272.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228126.208 | 0 | 0
April | 535945000000 | 392891.733 | 14-APR-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 43498.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233550.901 | 0 | 0
May | 621994000000 | 433651.526 | 31-MAY-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 70648.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247160.922 | 0 | 0
June | 658149000000 | 445389.095 | 19-JUN-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 86221.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243324.904 | 0 | 0
July | 714230000000 | 478426.523 | 03-JUL-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 112309.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250274.518 | 0 | 0
August | 711024000000 | 452723.025 | 14-AUG-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 87203.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249677.711 | 0 | 0
September | 653508000000 | 423327.508 | 06-SEP-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 63656.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243829.25 | 0 | 0
October | 565996000000 | 384636.021 | 20-OCT-17:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 28373.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240419.824 | 0 | 0
November | 488308000000 | 351577.067 | 28-NOV-18:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 8966.652 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 222438.06 | 0 | 0
December | 480907000000 | 351253.569 | 04-DEC-18:10 | 41924.28 | 31827.177 | 42090.75 | 0 | 10172.342 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 220908.872 | 0 | 0
Annual Sum or Average | 6841410000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 435215000000 | 339365.852 |  | 41924.28 | 31827.177 | 42090.75 | 0 | 7282.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216241.536 | 0 | 0
Maximum of Months | 714230000000 | 478426.523 |  | 41924.28 | 31827.177 | 42090.75 | 0 | 112309.797 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 250274.518 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 188001.65 | 19014.39 | 0 | 207016.04
Cost per Total Building Area ($/m2) | 44.97 | 4.55 | 0 | 49.52
Cost per Net Conditioned Building Area ($/m2) | 44.97 | 4.55 | 0 | 49.52
5-losangeles
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 7592.61 | 1816.07 | 1816.07
Net Site Energy | 7592.61 | 1816.07 | 1816.07
Total Source Energy | 21111.73 | 5049.69 | 5049.69
Net Source Energy | 21111.73 | 5049.69 | 5049.69
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 877.64 | 0 | 0 | 0 | 0
Cooling | 87.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 735.28 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.36 | 0 | 0 | 0 | 87.12
Refrigeration | 3897.72 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6400.7 | 1191.91 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6400.7 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6400.7 | 100
Total On-Site and Utility Electric Sources | 6400.7 | 100
Total Electricity End Uses | 6400.7 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.25 | 0.318 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7532.73 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34667.81 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45533.09 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 127423.29 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38795.2 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43972.21 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.46 | 862.89 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.09 | 3971.29 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.75 | 5215.93 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 7.7 | 14596.67 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.34 | 4444.09 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.66 | 5037.13 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 3290.6
PSZ-AC:2_HEATC | 25298.66
PSZ-AC:3_HEATC | 25101.65
PSZ-AC:4_HEATC | 92986.5
PSZ-AC:5_HEATC | 28310.6
PSZ-AC:6_HEATC | 32088.49
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 51505.1837 | 44.5702 | 392.0686 | 0 | 0.0002 | 2365386.4393 | 19022.2166
February | 46737.0233 | 40.4075 | 362.3135 | 0 | 0.0002 | 2185897.8584 | 17281.1666
March | 51393.2261 | 44.3508 | 413.1436 | 0 | 0.0002 | 2492623.2852 | 19047.7668
April | 49622.0258 | 42.7659 | 409.0027 | 0 | 0.0002 | 2467678.7959 | 18422.1176
May | 52020.004 | 44.7307 | 446.9815 | 0 | 0.0002 | 2696889.0505 | 19367.9338
June | 51204.5156 | 43.9925 | 446.5996 | 0 | 0.0002 | 2694608.4081 | 19084.5265
July | 53971.8598 | 46.3145 | 480.6767 | 0 | 0.0002 | 2900252.1851 | 20146.277
August | 55359.1067 | 47.4947 | 494.8621 | 0 | 0.0002 | 2985848.4764 | 20669.6845
September | 52073.4885 | 44.6931 | 462.4029 | 0 | 0.0002 | 2789988.8769 | 19433.4948
October | 52176.9737 | 44.8388 | 453.1409 | 0 | 0.0002 | 2734069.4061 | 19441.0533
November | 49783.93 | 42.8963 | 411.9563 | 0 | 0.0002 | 2485505.4506 | 18487.1644
December | 50999.8804 | 44.0623 | 400.8568 | 0 | 0.0002 | 2418457.6673 | 18874.1425
Annual Sum or Average | 616847.2174 | 531.1173 | 5174.0052 | 0 | 0.0024 | 31217200 | 229277.5444
Minimum of Months | 46737.0233 | 40.4075 | 362.3135 | 0 | 0.0002 | 2185897.8584 | 17281.1666
Maximum of Months | 55359.1067 | 47.4947 | 494.8621 | 0 | 0.0002 | 2985848.4764 | 20669.6845
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 484993000000 | 321431.283 | 10-JAN-18:10 | 41924.28 | 31827.177 | 34970.791 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 208378.887 | 0 | 0
February | 448191000000 | 334688.845 | 13-FEB-11:39 | 62886.42 | 35805.575 | 34970.791 | 0 | 16167.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184858.95 | 0 | 0
March | 511081000000 | 332044.562 | 04-MAR-11:39 | 62886.42 | 35805.575 | 34970.791 | 0 | 15505.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182876.443 | 0 | 0
April | 505967000000 | 341489.274 | 11-APR-17:10 | 41924.28 | 31827.177 | 34970.791 | 0 | 26577.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206189.559 | 0 | 0
May | 552964000000 | 362408.728 | 30-MAY-17:10 | 41924.28 | 31827.177 | 34970.791 | 0 | 20206.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233479.828 | 0 | 0
June | 552496000000 | 361854.096 | 28-JUN-17:10 | 41924.28 | 31827.177 | 34970.791 | 0 | 20443.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232688.34 | 0 | 0
July | 594661000000 | 367307.966 | 10-JUL-17:10 | 41924.28 | 31827.177 | 34970.791 | 0 | 28809.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229776.691 | 0 | 0
August | 612211000000 | 388391.724 | 08-AUG-17:10 | 41924.28 | 31827.177 | 34970.791 | 0 | 38712.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240957.419 | 0 | 0
September | 572053000000 | 373360.287 | 09-SEP-10:00 | 62886.42 | 35805.575 | 34970.791 | 0 | 28643.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211054.305 | 0 | 0
October | 560587000000 | 357012.019 | 05-OCT-10:50 | 62886.42 | 35805.575 | 34970.791 | 0 | 20346.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203002.507 | 0 | 0
November | 509622000000 | 343462.997 | 20-NOV-11:50 | 62886.42 | 35805.575 | 34970.791 | 0 | 16617.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193182.657 | 0 | 0
December | 495875000000 | 330468.02 | 04-DEC-11:50 | 62886.42 | 35805.575 | 34970.791 | 0 | 9326.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187479.023 | 0 | 0
Annual Sum or Average | 6400700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 448191000000 | 321431.283 |  | 41924.28 | 31827.177 | 34970.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182876.443 | 0 | 0
Maximum of Months | 612211000000 | 388391.724 |  | 62886.42 | 35805.575 | 34970.791 | 0 | 38712.056 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 240957.419 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 218057.42 | 10151.98 | 0 | 228209.4
Cost per Total Building Area ($/m2) | 52.16 | 2.43 | 0 | 54.59
Cost per Net Conditioned Building Area ($/m2) | 52.16 | 2.43 | 0 | 54.59
6-lasvegas
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 7938.64 | 1898.83 | 1898.83
Net Site Energy | 7938.64 | 1898.83 | 1898.83
Total Source Energy | 24700.6 | 5908.11 | 5908.11
Net Source Energy | 24700.6 | 5908.11 | 5908.11
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1174.31 | 0 | 0 | 0 | 0
Cooling | 469.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 929.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.06 | 0 | 0 | 0 | 87.12
Refrigeration | 3372.21 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6451.35 | 1487.29 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6451.35 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6451.35 | 100
Total On-Site and Utility Electric Sources | 6451.35 | 100
Total Electricity End Uses | 6451.35 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.25 | 0.318 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11849.88 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53947.14 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 52510.27 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 149714.92 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56596.34 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 50904.12 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.72 | 1357.43 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.26 | 6179.79 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.17 | 6015.19 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 9.04 | 17150.23 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.42 | 6483.26 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.08 | 5831.2 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4781.58
PSZ-AC:2_HEATC | 44461.9
PSZ-AC:3_HEATC | 29105.71
PSZ-AC:4_HEATC | 126481.14
PSZ-AC:5_HEATC | 47813.33
PSZ-AC:6_HEATC | 43004.47
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 117654.226 | 180.8338 | 696.3337 | 0 | 0.0013 | 3472382.5207 | 48415.5636
February | 103748.9746 | 163.2255 | 649.4144 | 0 | 0.0012 | 3238565.2694 | 43084.6702
March | 115041.7962 | 181.4524 | 724.4273 | 0 | 0.0014 | 3612664.8116 | 47822.1648
April | 114829.7286 | 185.3273 | 762.6571 | 0 | 0.0014 | 3803475.5658 | 48171.5238
May | 125374.8232 | 203.2625 | 841.3049 | 0 | 0.0016 | 4195736.0054 | 52690.4543
June | 138405.7269 | 225.8068 | 942.0757 | 0 | 0.0018 | 4698348.8915 | 58314.2628
July | 155463.149 | 253.9215 | 1060.8653 | 0 | 0.002 | 5290790.004 | 65530.7422
August | 156356.2614 | 255.3216 | 1066.4084 | 0 | 0.002 | 5318432.9038 | 65901.1094
September | 134088.8455 | 218.5794 | 910.9584 | 0 | 0.0017 | 4543153.2567 | 56476.2646
October | 121210.1831 | 195.7296 | 806.018 | 0 | 0.0015 | 4019725.9907 | 50859.0332
November | 110796.6485 | 175.0926 | 700.8528 | 0 | 0.0013 | 3495113.7572 | 46092.4
December | 116072.0612 | 179.4423 | 696.7471 | 0 | 0.0013 | 3474486.8272 | 47872.6111
Annual Sum or Average | 1509042.4242 | 2417.9953 | 9858.0631 | 0 | 0.0186 | 49162900 | 631230.8001
Minimum of Months | 103748.9746 | 163.2255 | 649.4144 | 0 | 0.0012 | 3238565.2694 | 43084.6702
Maximum of Months | 156356.2614 | 255.3216 | 1066.4084 | 0 | 0.002 | 5318432.9038 | 65901.1094
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 455660000000 | 312600.684 | 23-JAN-18:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 190659.195 | 0 | 0
February | 424978000000 | 326347.158 | 10-FEB-18:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 204405.669 | 0 | 0
March | 474068000000 | 331547.071 | 31-MAR-17:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 16521.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197414.549 | 0 | 0
April | 499107000000 | 389873.301 | 21-APR-17:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 56672.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215589.318 | 0 | 0
May | 550581000000 | 404580.699 | 31-MAY-17:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 75130.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211839.03 | 0 | 0
June | 616536000000 | 454754.038 | 27-JUN-17:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 123764.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213378.048 | 0 | 0
July | 694279000000 | 461722.713 | 25-JUL-17:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 118176.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225934.42 | 0 | 0
August | 697906000000 | 468224.888 | 02-AUG-17:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 107639.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242974.238 | 0 | 0
September | 596171000000 | 433820.736 | 01-SEP-17:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 94906.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221302.683 | 0 | 0
October | 527485000000 | 379649.15 | 06-OCT-10:50 | 62886.42 | 35805.575 | 43859.884 | 0 | 35166.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201930.605 | 0 | 0
November | 458643000000 | 321911.897 | 21-NOV-18:10 | 41924.28 | 31827.177 | 43859.884 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 199970.408 | 0 | 0
December | 455936000000 | 312916.093 | 05-DEC-11:39 | 62886.42 | 35805.575 | 43859.884 | 0 | 5380.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164983.475 | 0 | 0
Annual Sum or Average | 6451350000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 424978000000 | 312600.684 |  | 41924.28 | 31827.177 | 43859.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164983.475 | 0 | 0
Maximum of Months | 697906000000 | 468224.888 |  | 62886.42 | 35805.575 | 43859.884 | 0 | 123764.648 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 242974.238 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 170606.29 | 11624.31 | 0 | 182230.6
Cost per Total Building Area ($/m2) | 40.81 | 2.78 | 0 | 43.59
Cost per Net Conditioned Building Area ($/m2) | 40.81 | 2.78 | 0 | 43.59
7-sanfrancisco
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8024.56 | 1919.39 | 1919.39
Net Site Energy | 8024.56 | 1919.39 | 1919.39
Total Source Energy | 20713.87 | 4954.53 | 4954.53
Net Source Energy | 20713.87 | 4954.53 | 4954.53
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1742.09 | 0 | 0 | 0 | 0
Cooling | 28.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 744.37 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.98 | 0 | 0 | 0 | 87.12
Refrigeration | 3513.27 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5966.57 | 2057.99 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 5966.57 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 5966.57 | 100
Total On-Site and Utility Electric Sources | 5966.57 | 100
Total Electricity End Uses | 5966.57 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 6.88 | 0.34 | 0.34 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6463.92 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36648.1 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42473.44 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 133534.29 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 40264.43 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41480.13 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.39 | 740.46 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.21 | 4198.13 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.57 | 4865.44 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 8.07 | 15296.7 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.43 | 4612.39 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.51 | 4751.66 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 2862.34
PSZ-AC:2_HEATC | 29560.7
PSZ-AC:3_HEATC | 25248.68
PSZ-AC:4_HEATC | 107710
PSZ-AC:5_HEATC | 32477.66
PSZ-AC:6_HEATC | 33458.26
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 56532.9211 | 49.1987 | 380.6477 | 0 | 0.0002 | 2296280.0249 | 20727.4801
February | 48691.8877 | 42.2161 | 356.269 | 0 | 0.0002 | 2149345.1375 | 17939.3068
March | 53723.6881 | 46.6013 | 389.0395 | 0 | 0.0002 | 2347030.3297 | 19780.803
April | 50594.356 | 43.7898 | 383.7405 | 0 | 0.0002 | 2315136.2869 | 18681.5687
May | 51602.6296 | 44.5424 | 412.8666 | 0 | 0.0002 | 2490944.4445 | 19119.3966
June | 49885.6825 | 43.0047 | 409.1003 | 0 | 0.0002 | 2468259.6158 | 18513.6673
July | 51090.0525 | 43.981 | 430.0567 | 0 | 0.0002 | 2594739.6359 | 18994.4389
August | 51934.9475 | 44.693 | 439.9049 | 0 | 0.0002 | 2654168.8063 | 19316.905
September | 50299.9493 | 43.2854 | 426.1701 | 0 | 0.0002 | 2571300.4033 | 18709.1252
October | 51901.895 | 44.7621 | 422.1747 | 0 | 0.0002 | 2547129.8443 | 19251.3715
November | 51684.4755 | 44.7521 | 388.6505 | 0 | 0.0002 | 2344745.3465 | 19073.8413
December | 56401.5663 | 49.0567 | 384.7133 | 0 | 0.0002 | 2320829.0886 | 20694.4221
Annual Sum or Average | 624344.0511 | 539.8835 | 4823.3338 | 0 | 0.0024 | 29099900 | 230802.3267
Minimum of Months | 48691.8877 | 42.2161 | 356.269 | 0 | 0.0002 | 2149345.1375 | 17939.3068
Maximum of Months | 56532.9211 | 49.1987 | 439.9049 | 0 | 0.0002 | 2654168.8063 | 20727.4801
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 470824000000 | 322806.17 | 05-JAN-18:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 209416.992 | 0 | 0
February | 440696000000 | 330746.704 | 15-FEB-18:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 2267.591 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 215089.934 | 0 | 0
March | 481229000000 | 315281.615 | 27-MAR-17:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206222.585 | 0 | 0
April | 474690000000 | 328739.177 | 29-APR-10:50 | 62886.42 | 35805.575 | 35307.573 | 0 | 8963.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185775.689 | 0 | 0
May | 510737000000 | 341627.337 | 25-MAY-17:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 9276.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223291.797 | 0 | 0
June | 506086000000 | 350046.544 | 16-JUN-10:50 | 62886.42 | 35805.575 | 35307.573 | 0 | 19662.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196384.954 | 0 | 0
July | 532019000000 | 367786.484 | 03-JUL-10:50 | 62886.42 | 35805.575 | 35307.573 | 0 | 27564.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206222.352 | 0 | 0
August | 544204000000 | 362166.652 | 15-AUG-10:50 | 62886.42 | 35805.575 | 35307.573 | 0 | 22325.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205841.761 | 0 | 0
September | 527213000000 | 371358.828 | 28-SEP-17:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 40928.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221371.487 | 0 | 0
October | 522257000000 | 344826.593 | 16-OCT-17:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 14107.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221660.015 | 0 | 0
November | 480761000000 | 331622.462 | 16-NOV-18:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 218233.283 | 0 | 0
December | 475857000000 | 322713.069 | 14-DEC-18:10 | 41924.28 | 31827.177 | 35307.573 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 209323.89 | 0 | 0
Annual Sum or Average | 5966570000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 440696000000 | 315281.615 |  | 41924.28 | 31827.177 | 35307.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185775.689 | 0 | 0
Maximum of Months | 544204000000 | 371358.828 |  | 62886.42 | 35805.575 | 35307.573 | 0 | 40928.31 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 223291.797 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 239647.71 | 17480.19 | 0 | 257127.9
Cost per Total Building Area ($/m2) | 57.32 | 4.18 | 0 | 61.5
Cost per Net Conditioned Building Area ($/m2) | 57.32 | 4.18 | 0 | 61.5
8-baltimore
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 9391.49 | 2246.34 | 2246.34
Net Site Energy | 9391.49 | 2246.34 | 2246.34
Total Source Energy | 26464.28 | 6329.97 | 6329.97
Net Source Energy | 26464.28 | 6329.97 | 6329.97
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2550.09 | 0 | 0 | 0 | 0
Cooling | 308.26 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 927.88 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.22 | 0 | 0 | 0 | 87.12
Refrigeration | 3608.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6525.27 | 2866.22 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6525.27 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6525.27 | 100
Total On-Site and Utility Electric Sources | 6525.27 | 100
Total Electricity End Uses | 6525.27 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.39 | 0.495 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10279.49 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73976.89 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 47622.9 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 239202.59 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76350.75 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 59034.41 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.56 | 1061.92 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.05 | 5777 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.86 | 5431.24 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 9.63 | 18266.01 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.19 | 6053.38 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.76 | 5240.22 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4091.46
PSZ-AC:2_HEATC | 56094.38
PSZ-AC:3_HEATC | 32886.96
PSZ-AC:4_HEATC | 177361.93
PSZ-AC:5_HEATC | 58777.94
PSZ-AC:6_HEATC | 50882.29
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 108596.8188 | 182.775 | 465.3817 | 0 | 0.0019 | 28934.4719 | 45284.7145
February | 94756.9462 | 161.8432 | 419.1117 | 0 | 0.0017 | 26058.6685 | 39729.4411
March | 98178.4086 | 177.1695 | 486.6026 | 0 | 0.002 | 30258.771 | 42031.0263
April | 91166.783 | 170.4951 | 484.8618 | 0 | 0.002 | 30152.6555 | 39575.9508
May | 100496.2818 | 195.6334 | 576.9452 | 0 | 0.0023 | 35881.7093 | 44329.1587
June | 110796.897 | 219.3119 | 656.1047 | 0 | 0.0026 | 40805.9542 | 49204.3827
July | 119669.693 | 237.5193 | 712.2058 | 0 | 0.0029 | 44295.316 | 53203.6902
August | 120374.5168 | 238.8111 | 715.8091 | 0 | 0.0029 | 44519.3908 | 53507.2528
September | 103342.7025 | 203.3655 | 605.3846 | 0 | 0.0024 | 37651.1001 | 45785.0673
October | 98269.6731 | 187.4847 | 543.1019 | 0 | 0.0022 | 33775.731 | 42998.2351
November | 96139.4123 | 175.6246 | 488.2831 | 0 | 0.002 | 30364.0346 | 41353.2977
December | 104439.9709 | 178.6825 | 463.6007 | 0 | 0.0019 | 28824.934 | 43816.8167
Annual Sum or Average | 1246228.1039 | 2328.7158 | 6617.3929 | 0 | 0.027 | 411522.737 | 540819.0339
Minimum of Months | 91166.783 | 161.8432 | 419.1117 | 0 | 0.0017 | 26058.6685 | 39575.9508
Maximum of Months | 120374.5168 | 238.8111 | 715.8091 | 0 | 0.0029 | 44519.3908 | 53507.2528
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 458797000000 | 326132.282 | 09-JAN-11:20 | 62886.42 | 35805.575 | 42672.551 | 0 | 5831.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178935.844 | 0 | 0
February | 413197000000 | 314293.412 | 13-FEB-11:20 | 62886.42 | 35805.575 | 42672.551 | 0 | 2338.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170590.781 | 0 | 0
March | 479795000000 | 365513.142 | 09-MAR-18:10 | 41924.28 | 31827.177 | 42672.551 | 0 | 16544.428 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 228214.558 | 0 | 0
April | 478113000000 | 366777.669 | 04-APR-17:10 | 41924.28 | 31827.177 | 42672.551 | 0 | 22278.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228075.65 | 0 | 0
May | 568955000000 | 410384.108 | 15-MAY-17:10 | 41924.28 | 31827.177 | 42672.551 | 0 | 48444.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245515.873 | 0 | 0
June | 647036000000 | 482535.955 | 30-JUN-17:10 | 41924.28 | 31827.177 | 42672.551 | 0 | 112079.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254032.123 | 0 | 0
July | 702364000000 | 483889.828 | 25-JUL-10:00 | 62886.42 | 35805.575 | 42672.551 | 0 | 115167.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227357.393 | 0 | 0
August | 705917000000 | 483719.314 | 17-AUG-17:10 | 41924.28 | 31827.177 | 42672.551 | 0 | 113009.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254285.884 | 0 | 0
September | 597011000000 | 414840.108 | 08-SEP-17:10 | 41924.28 | 31827.177 | 42672.551 | 0 | 64924.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233491.567 | 0 | 0
October | 535562000000 | 386280.636 | 20-OCT-17:10 | 41924.28 | 31827.177 | 42672.551 | 0 | 35563.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234293.315 | 0 | 0
November | 481464000000 | 371799.108 | 04-NOV-11:00 | 62886.42 | 35805.575 | 42672.551 | 0 | 25781.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204653.353 | 0 | 0
December | 457060000000 | 326010.635 | 23-DEC-11:20 | 62886.42 | 35805.575 | 42672.551 | 0 | 4356.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180289.937 | 0 | 0
Annual Sum or Average | 6525270000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 413197000000 | 314293.412 |  | 41924.28 | 31827.177 | 42672.551 | 0 | 2338.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170590.781 | 0 | 0
Maximum of Months | 705917000000 | 483889.828 |  | 62886.42 | 35805.575 | 42672.551 | 0 | 115167.889 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 254285.884 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 126858.83 | 27937.15 | 0 | 154795.98
Cost per Total Building Area ($/m2) | 30.34 | 6.68 | 0 | 37.03
Cost per Net Conditioned Building Area ($/m2) | 30.34 | 6.68 | 0 | 37.03
9-albuquerque
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8332.34 | 1993.01 | 1993.01
Net Site Energy | 8332.34 | 1993.01 | 1993.01
Total Source Energy | 22806.56 | 5455.08 | 5455.08
Net Source Energy | 22806.56 | 5455.08 | 5455.08
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 1858.52 | 0 | 0 | 0 | 0
Cooling | 215.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1022.03 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.93 | 0 | 0 | 0 | 87.12
Refrigeration | 3240.58 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6157.97 | 2174.37 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6157.97 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6157.97 | 100
Total On-Site and Utility Electric Sources | 6157.97 | 100
Total Electricity End Uses | 6157.97 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.39 | 0.495 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10112.38 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54752.8 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 52948.14 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 179923.46 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 57635.62 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51085.73 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.61 | 1158.4 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.31 | 6272.07 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.2 | 6065.35 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 10.87 | 20610.7 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.48 | 6602.31 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.09 | 5852 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 3668.9
PSZ-AC:2_HEATC | 46639.65
PSZ-AC:3_HEATC | 28468.03
PSZ-AC:4_HEATC | 159013.3
PSZ-AC:5_HEATC | 50937.39
PSZ-AC:6_HEATC | 45148.7
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 142287.5394 | 232.0023 | 557.2661 | 0 | 0.0022 | 579359.3984 | 59334.1131
February | 125316.0137 | 206.8824 | 504.6127 | 0 | 0.002 | 524637.3038 | 52507.3298
March | 137004.069 | 229.0449 | 567.1943 | 0 | 0.0022 | 589723.072 | 57685.8307
April | 130670.8909 | 222.905 | 565.0499 | 0 | 0.0022 | 587524.6338 | 55455.5356
May | 143570.1136 | 248.3431 | 639.4153 | 0 | 0.0025 | 664870.908 | 61266.6827
June | 153408.7124 | 267.1915 | 693.1374 | 0 | 0.0027 | 720743.6084 | 65644.6666
July | 172296.3373 | 300.8661 | 782.6877 | 0 | 0.0031 | 813865.4591 | 73803.1368
August | 170960.6623 | 298.3356 | 775.5477 | 0 | 0.003 | 806439.8409 | 73211.5658
September | 151078.9747 | 262.7836 | 680.7157 | 0 | 0.0027 | 707824.9486 | 64613.4062
October | 139164.8509 | 237.9185 | 604.616 | 0 | 0.0024 | 628667.8846 | 59111.6954
November | 132898.3192 | 220.9226 | 543.3864 | 0 | 0.0021 | 564960.6937 | 55833.6773
December | 142795.9259 | 232.3352 | 556.5728 | 0 | 0.0022 | 578634.8588 | 59497.4611
Annual Sum or Average | 1741452.4094 | 2959.5307 | 7470.2021 | 0 | 0.0293 | 7767252.6101 | 737965.101
Minimum of Months | 125316.0137 | 206.8824 | 504.6127 | 0 | 0.002 | 524637.3038 | 52507.3298
Maximum of Months | 172296.3373 | 300.8661 | 782.6877 | 0 | 0.0031 | 813865.4591 | 73803.1368
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 459323000000 | 307359.222 | 02-JAN-11:20 | 62886.42 | 35805.575 | 47403.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161263.607 | 0 | 0
February | 415939000000 | 310019.218 | 14-FEB-18:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 184533.993 | 0 | 0
March | 467540000000 | 318941.388 | 20-MAR-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 6970.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190815.816 | 0 | 0
April | 465797000000 | 352843.71 | 21-APR-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 29874.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201813.96 | 0 | 0
May | 527118000000 | 379094.796 | 31-MAY-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 47820.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210119.412 | 0 | 0
June | 571414000000 | 404217.696 | 29-JUN-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 64396.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218665.746 | 0 | 0
July | 645242000000 | 419507.925 | 20-JUL-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 67428.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230924.399 | 0 | 0
August | 639355000000 | 432064.238 | 01-AUG-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 75565.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235343.527 | 0 | 0
September | 561172000000 | 379006.487 | 13-SEP-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 40429.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217421.737 | 0 | 0
October | 498415000000 | 362442.957 | 11-OCT-17:10 | 41924.28 | 31827.177 | 47403.62 | 0 | 25586.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215701.61 | 0 | 0
November | 447908000000 | 314973.036 | 10-NOV-11:20 | 62886.42 | 35805.575 | 47403.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168877.421 | 0 | 0
December | 458749000000 | 306048.373 | 22-DEC-11:20 | 62886.42 | 35805.575 | 47403.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159952.758 | 0 | 0
Annual Sum or Average | 6157970000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 415939000000 | 306048.373 |  | 41924.28 | 31827.177 | 47403.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159952.758 | 0 | 0
Maximum of Months | 645242000000 | 432064.238 |  | 62886.42 | 35805.575 | 47403.62 | 0 | 75565.633 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 235343.527 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63359.28 | 15141.64 | 0 | 78500.92
Cost per Total Building Area ($/m2) | 15.15 | 3.62 | 0 | 18.78
Cost per Net Conditioned Building Area ($/m2) | 15.15 | 3.62 | 0 | 18.78
10-seattle
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8822.58 | 2110.26 | 2110.26
Net Site Energy | 8822.58 | 2110.26 | 2110.26
Total Source Energy | 13456.86 | 3218.73 | 3218.73
Net Source Energy | 13456.86 | 3218.73 | 3218.73
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2624.74 | 0 | 0 | 0 | 0
Cooling | 41.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 827.98 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.99 | 0 | 0 | 0 | 87.12
Refrigeration | 3330.91 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5880.93 | 2941.65 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 5880.93 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 5880.93 | 100
Total On-Site and Utility Electric Sources | 5880.93 | 100
Total Electricity End Uses | 5880.93 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.856 | 0.98 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.39 | 0.495 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8027.25 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43368.24 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43619.73 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 177790.1 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46818.3 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 42485.68 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.48 | 919.54 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.62 | 4967.94 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.64 | 4996.75 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 8.87 | 16823.38 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.83 | 5363.16 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.57 | 4866.84 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 3513.86
PSZ-AC:2_HEATC | 41717.11
PSZ-AC:3_HEATC | 28433.58
PSZ-AC:4_HEATC | 141270.21
PSZ-AC:5_HEATC | 45035.82
PSZ-AC:6_HEATC | 40868.14
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 45361.1906 | 56.5874 | 98.594 | 0 | 0.0004 | 1301673.9744 | 17350.227
February | 37542.1255 | 48.0249 | 89.2077 | 0 | 0.0004 | 1177990.4207 | 14487.1381
March | 40307.3161 | 52.3444 | 100.7728 | 0 | 0.0004 | 1330851.2693 | 15637.9767
April | 35454.2862 | 47.6733 | 99.0546 | 0 | 0.0004 | 1308443.4425 | 13929.8558
May | 32759.5958 | 46.7623 | 108.8442 | 0 | 0.0004 | 1438178.9855 | 13161.6222
June | 30142.5257 | 44.4614 | 109.3096 | 0 | 0.0004 | 1444517.1931 | 12263.8427
July | 30684.047 | 46.365 | 118.3281 | 0 | 0.0005 | 1563827.7083 | 12602.5041
August | 30931.1293 | 47.2111 | 122.2993 | 0 | 0.0005 | 1616364.5902 | 12754.6165
September | 31416.6681 | 45.9793 | 111.6224 | 0 | 0.0004 | 1475036.9214 | 12743.5307
October | 35700.1148 | 49.2251 | 107.5388 | 0 | 0.0004 | 1420704.1051 | 14157.2368
November | 40306.7229 | 51.9182 | 98.0545 | 0 | 0.0004 | 1294878.3514 | 15592.1741
December | 45291.6534 | 56.7129 | 99.7982 | 0 | 0.0004 | 1317615.1071 | 17346.3651
Annual Sum or Average | 435897.3752 | 593.2654 | 1263.4242 | 0 | 0.0052 | 16690100 | 172027.0899
Minimum of Months | 30142.5257 | 44.4614 | 89.2077 | 0 | 0.0004 | 1177990.4207 | 12263.8427
Maximum of Months | 45361.1906 | 56.7129 | 122.2993 | 0 | 0.0005 | 1616364.5902 | 17350.227
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 458659000000 | 314310.801 | 14-JAN-11:20 | 62886.42 | 35805.575 | 38780.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176838.402 | 0 | 0
February | 415078000000 | 305966.677 | 24-FEB-18:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 189104.668 | 0 | 0
March | 468940000000 | 317002.937 | 30-MAR-17:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204471.076 | 0 | 0
April | 461044000000 | 327189.078 | 29-APR-17:10 | 34936.9 | 27848.78 | 38780.404 | 0 | 6261.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219361.296 | 0 | 0
May | 506758000000 | 357357.953 | 05-MAY-17:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 18250.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226575.329 | 0 | 0
June | 508991000000 | 357067.044 | 28-JUN-17:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 26434.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218100.604 | 0 | 0
July | 551032000000 | 388272.668 | 31-JUL-17:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 43135.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232604.891 | 0 | 0
August | 569544000000 | 379997.016 | 18-AUG-17:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 35512.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231953.014 | 0 | 0
September | 519745000000 | 396434.135 | 02-SEP-17:10 | 34936.9 | 27848.78 | 38780.404 | 0 | 68216.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226651.291 | 0 | 0
October | 500600000000 | 327280.403 | 05-OCT-17:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214748.542 | 0 | 0
November | 456264000000 | 332098.716 | 03-NOV-18:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 215236.707 | 0 | 0
December | 464276000000 | 309392.249 | 28-DEC-18:10 | 41924.28 | 31827.177 | 38780.404 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 192530.241 | 0 | 0
Annual Sum or Average | 5880930000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 415078000000 | 305966.677 |  | 34936.9 | 27848.78 | 38780.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176838.402 | 0 | 0
Maximum of Months | 569544000000 | 396434.135 |  | 62886.42 | 35805.575 | 38780.404 | 0 | 68216.76 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 232604.891 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 116144.1 | 24640.41 | 0 | 140784.51
Cost per Total Building Area ($/m2) | 27.78 | 5.89 | 0 | 33.67
Cost per Net Conditioned Building Area ($/m2) | 27.78 | 5.89 | 0 | 33.67
11-chicago
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 9988.12 | 2389.05 | 2389.05
Net Site Energy | 9988.12 | 2389.05 | 2389.05
Total Source Energy | 26503.56 | 6339.36 | 6339.36
Net Source Energy | 26503.56 | 6339.36 | 6339.36
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3315.13 | 0 | 0 | 0 | 0
Cooling | 189.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 68.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1054.01 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.52 | 0 | 0 | 0 | 87.12
Refrigeration | 3431.22 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6355.55 | 3632.57 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6355.55 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6355.55 | 100
Total On-Site and Utility Electric Sources | 6355.55 | 100
Total Electricity End Uses | 6355.55 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.698 | 0.78 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.39 | 0.495 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12237.07 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87884.71 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 47325.91 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 276778.23 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 90703.65 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58628.91 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.65 | 1227.93 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.54 | 6711.06 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.86 | 5421.31 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 11.15 | 21135.36 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.69 | 6990.25 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.76 | 5234.92 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4680.78
PSZ-AC:2_HEATC | 69830.69
PSZ-AC:3_HEATC | 36071.59
PSZ-AC:4_HEATC | 239743.05
PSZ-AC:5_HEATC | 77398.82
PSZ-AC:6_HEATC | 59380.89
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 197956.5051 | 325.2631 | 873.5183 | 0 | 0.0027 | 201048.1499 | 82431.7882
February | 173557.1781 | 288.703 | 787.016 | 0 | 0.0024 | 181144.5531 | 72609.1243
March | 185952.4772 | 315.507 | 880.302 | 0 | 0.0027 | 202625.5475 | 78386.1655
April | 173429.1679 | 303.4908 | 876.3611 | 0 | 0.0027 | 201732.2969 | 73989.8039
May | 191989.9562 | 344.2047 | 1019.5096 | 0 | 0.0031 | 234695.66 | 82695.5832
June | 212291.7155 | 384.3437 | 1149.7454 | 0 | 0.0035 | 264681.5425 | 91797.8558
July | 235003.7764 | 426.311 | 1277.8363 | 0 | 0.0039 | 294170.3098 | 101699.9677
August | 230230.6762 | 417.4068 | 1250.4109 | 0 | 0.0038 | 287856.3921 | 99610.8952
September | 201431.2717 | 363.5776 | 1084.3098 | 0 | 0.0033 | 249616.2435 | 86996.1187
October | 185274.229 | 327.7501 | 957.3842 | 0 | 0.0029 | 220388.2259 | 79380.8605
November | 179743.1097 | 307.8598 | 868.2212 | 0 | 0.0027 | 199849.1511 | 76044.8264
December | 194089.8556 | 321.8292 | 873.9569 | 0 | 0.0027 | 201153.8014 | 81100.7863
Annual Sum or Average | 2360949.9185 | 4126.2467 | 11898.5719 | 0 | 0.0362 | 2738961.8737 | 1006743.7755
Minimum of Months | 173429.1679 | 288.703 | 787.016 | 0 | 0.0024 | 181144.5531 | 72609.1243
Maximum of Months | 235003.7764 | 426.311 | 1277.8363 | 0 | 0.0039 | 294170.3098 | 101699.9677
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 466517000000 | 310435.835 | 17-JAN-18:10 | 41924.28 | 31827.177 | 47563.62 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 184790.61 | 0 | 0
February | 420332000000 | 310162.965 | 28-FEB-11:20 | 62886.42 | 35805.575 | 47563.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163907.35 | 0 | 0
March | 470177000000 | 337681.692 | 14-MAR-17:10 | 41924.28 | 31827.177 | 47563.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216366.614 | 0 | 0
April | 468105000000 | 336360.59 | 10-APR-10:09 | 62886.42 | 35805.575 | 47563.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190104.975 | 0 | 0
May | 544594000000 | 417336.058 | 30-MAY-17:10 | 41924.28 | 31827.177 | 47563.62 | 0 | 51553.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244467.209 | 0 | 0
June | 614174000000 | 456723.002 | 08-JUN-12:00 | 62886.42 | 35805.575 | 47563.62 | 0 | 109148.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201319.076 | 0 | 0
July | 682600000000 | 477301.065 | 14-JUL-10:00 | 62886.42 | 35805.575 | 47563.62 | 0 | 105446.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225599.329 | 0 | 0
August | 667949000000 | 474283.38 | 04-AUG-17:10 | 41924.28 | 31827.177 | 47563.62 | 0 | 99775.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253192.538 | 0 | 0
September | 579216000000 | 419666.849 | 06-SEP-10:00 | 62886.42 | 35805.575 | 47563.62 | 0 | 57356.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216054.829 | 0 | 0
October | 511394000000 | 375331.213 | 31-OCT-11:00 | 62886.42 | 35805.575 | 47563.62 | 0 | 27382.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201693.464 | 0 | 0
November | 463735000000 | 375213.046 | 02-NOV-18:10 | 41924.28 | 31827.177 | 47563.62 | 0 | 17055.231 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 232512.59 | 0 | 0
December | 466762000000 | 318622.413 | 12-DEC-18:10 | 41924.28 | 31827.177 | 47563.62 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 192977.188 | 0 | 0
Annual Sum or Average | 6355550000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 420332000000 | 310162.965 |  | 41924.28 | 31827.177 | 47563.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163907.35 | 0 | 0
Maximum of Months | 682600000000 | 477301.065 |  | 62886.42 | 35805.575 | 47563.62 | 0 | 109148.311 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 253192.538 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 169357.3 | 30587.6 | 0 | 199944.89
Cost per Total Building Area ($/m2) | 40.51 | 7.32 | 0 | 47.82
Cost per Net Conditioned Building Area ($/m2) | 40.51 | 7.32 | 0 | 47.82
12-boulder
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 8948.65 | 2140.42 | 2140.42
Net Site Energy | 8948.65 | 2140.42 | 2140.42
Total Source Energy | 23340.96 | 5582.9 | 5582.9
Net Source Energy | 23340.96 | 5582.9 | 5582.9
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 2535.58 | 0 | 0 | 0 | 0
Cooling | 141.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1163.78 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.46 | 0 | 0 | 0 | 87.12
Refrigeration | 3110.39 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6095.7 | 2852.95 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6095.7 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6095.7 | 100
Total On-Site and Utility Electric Sources | 6095.7 | 100
Total Electricity End Uses | 6095.7 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.698 | 0.78 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.39 | 0.495 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11886.48 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 64712.69 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51606.87 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 208866.19 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 67594.45 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 49919.99 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.72 | 1361.63 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.91 | 7413.01 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.12 | 5911.7 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 12.62 | 23926.16 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.08 | 7743.12 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.02 | 5718.46 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4312.86
PSZ-AC:2_HEATC | 60208.75
PSZ-AC:3_HEATC | 31578.98
PSZ-AC:4_HEATC | 213607.57
PSZ-AC:5_HEATC | 66632.22
PSZ-AC:6_HEATC | 53922.94
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 151308.7415 | 243.521 | 575.3289 | 0 | 0.0023 | 598114.6754 | 62783.0138
February | 133191.7449 | 216.2914 | 516.8794 | 0 | 0.0021 | 537364.9321 | 55454.8294
March | 143826.481 | 237.5654 | 579.8225 | 0 | 0.0023 | 602832.6063 | 60275.4067
April | 134564.2954 | 227.1536 | 568.9336 | 0 | 0.0022 | 591546.7579 | 56873.1308
May | 143822.0549 | 246.5227 | 628.3257 | 0 | 0.0025 | 653325.1224 | 61152.8863
June | 148879.747 | 258.0696 | 665.9967 | 0 | 0.0026 | 692514.058 | 63585.6718
July | 167990.8303 | 293.0541 | 761.5395 | 0 | 0.003 | 791872.9418 | 71930.0638
August | 163910.7965 | 285.4812 | 740.579 | 0 | 0.0029 | 770074.6745 | 70138.4126
September | 142354.901 | 245.7246 | 631.2074 | 0 | 0.0025 | 656332.8784 | 60697.4401
October | 140037.2412 | 237.6411 | 598.8324 | 0 | 0.0024 | 622642.5108 | 59308.7506
November | 139075.5489 | 228.8097 | 555.7532 | 0 | 0.0022 | 577801.6383 | 58195.2687
December | 151379.8839 | 242.9062 | 571.6519 | 0 | 0.0023 | 594286.5042 | 62740.9938
Annual Sum or Average | 1760342.2666 | 2962.7405 | 7394.8504 | 0 | 0.0291 | 7688709.3 | 743135.8682
Minimum of Months | 133191.7449 | 216.2914 | 516.8794 | 0 | 0.0021 | 537364.9321 | 55454.8294
Maximum of Months | 167990.8303 | 293.0541 | 761.5395 | 0 | 0.003 | 791872.9418 | 71930.0638
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 474193000000 | 315639.628 | 23-JAN-11:20 | 62886.42 | 35805.575 | 52916.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164030.763 | 0 | 0
February | 426029000000 | 311584.532 | 11-FEB-11:20 | 62886.42 | 35805.575 | 52916.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159975.668 | 0 | 0
March | 477933000000 | 338252.358 | 30-MAR-17:10 | 41924.28 | 31827.177 | 52916.869 | 0 | 16601.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194982.162 | 0 | 0
April | 468985000000 | 345230.29 | 26-APR-17:10 | 41924.28 | 31827.177 | 52916.869 | 0 | 21363.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197198.756 | 0 | 0
May | 517964000000 | 377317.24 | 24-MAY-17:10 | 41924.28 | 31827.177 | 52916.869 | 0 | 35282.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215366.65 | 0 | 0
June | 549033000000 | 391908.231 | 28-JUN-10:50 | 62886.42 | 35805.575 | 52916.869 | 0 | 42712.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197587.078 | 0 | 0
July | 627806000000 | 412978.494 | 19-JUL-10:50 | 62886.42 | 35805.575 | 52916.869 | 0 | 52196.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209172.757 | 0 | 0
August | 610524000000 | 412872.812 | 30-AUG-10:50 | 62886.42 | 35805.575 | 52916.869 | 0 | 52660.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208602.956 | 0 | 0
September | 520349000000 | 389983.332 | 01-SEP-17:10 | 41924.28 | 31827.177 | 52916.869 | 0 | 47304.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216010.695 | 0 | 0
October | 493638000000 | 352646.833 | 05-OCT-17:10 | 41924.28 | 31827.177 | 52916.869 | 0 | 25742.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200236.06 | 0 | 0
November | 458088000000 | 315508.159 | 10-NOV-11:39 | 62886.42 | 35805.575 | 52916.869 | 0 | 2148.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161750.725 | 0 | 0
December | 471158000000 | 309845.293 | 30-DEC-11:20 | 62886.42 | 35805.575 | 52916.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158236.429 | 0 | 0
Annual Sum or Average | 6095700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 426029000000 | 309845.293 |  | 41924.28 | 31827.177 | 52916.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158236.429 | 0 | 0
Maximum of Months | 627806000000 | 412978.494 |  | 62886.42 | 35805.575 | 52916.869 | 0 | 52660.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216010.695 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 62720.53 | 19908.54 | 0 | 82629.07
Cost per Total Building Area ($/m2) | 15 | 4.76 | 0 | 19.76
Cost per Net Conditioned Building Area ($/m2) | 15 | 4.76 | 0 | 19.76
13-minneapolis
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 10805.91 | 2584.66 | 2584.66
Net Site Energy | 10805.91 | 2584.66 | 2584.66
Total Source Energy | 26656.58 | 6375.96 | 6375.96
Net Source Energy | 26656.58 | 6375.96 | 6375.96
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 4151.93 | 0 | 0 | 0 | 0
Cooling | 165.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1135.06 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.65 | 0 | 0 | 0 | 87.12
Refrigeration | 3354.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6335.41 | 4470.5 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6335.41 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6335.41 | 100
Total On-Site and Utility Electric Sources | 6335.41 | 100
Total Electricity End Uses | 6335.41 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.591 | 0.65 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.39 | 0.495 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12615.98 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88782.24 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 47288.05 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 297081.26 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 90993.88 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54996.68 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.69 | 1304.13 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.78 | 7176.69 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.86 | 5416.97 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 11.96 | 22685.74 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.94 | 7472.57 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.76 | 5240.15 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4924.75
PSZ-AC:2_HEATC | 76878.64
PSZ-AC:3_HEATC | 37917.8
PSZ-AC:4_HEATC | 272539.55
PSZ-AC:5_HEATC | 85293.25
PSZ-AC:6_HEATC | 64237.37
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 155486.7642 | 236.5735 | 311.4762 | 0 | 0.0024 | 204573.4883 | 62936.771
February | 132246.1655 | 205.6405 | 279.3368 | 0 | 0.0021 | 183489.1501 | 53952.834
March | 132002.7146 | 216.006 | 313.8071 | 0 | 0.0023 | 206187.8865 | 54880.5047
April | 117752.0391 | 202.6212 | 312.2782 | 0 | 0.0023 | 205229.4515 | 49905.3702
May | 128689.0355 | 229.5348 | 367.638 | 0 | 0.0027 | 241645.5529 | 55314.3225
June | 137165.3256 | 248.0156 | 402.8005 | 0 | 0.0029 | 264770.6006 | 59279.0525
July | 147648.2362 | 267.5557 | 435.4909 | 0 | 0.0032 | 286260.9671 | 63865.433
August | 147677.5311 | 267.5085 | 435.251 | 0 | 0.0032 | 286102.9149 | 63868.5264
September | 125595.2484 | 224.9981 | 361.9953 | 0 | 0.0026 | 237940.4875 | 54078.3333
October | 122170.0907 | 210.072 | 323.5014 | 0 | 0.0024 | 212604.6951 | 51763.3307
November | 127363.6902 | 207.9957 | 301.4141 | 0 | 0.0023 | 198043.0692 | 52911.7533
December | 147837.4884 | 229.0959 | 309.7011 | 0 | 0.0023 | 203430.5787 | 60238.2715
Annual Sum or Average | 1621634.3294 | 2745.6174 | 4154.6905 | 0 | 0.0308 | 2730278.8423 | 682994.5031
Minimum of Months | 117752.0391 | 202.6212 | 279.3368 | 0 | 0.0021 | 183489.1501 | 49905.3702
Maximum of Months | 155486.7642 | 267.5557 | 435.4909 | 0 | 0.0032 | 286260.9671 | 63868.5264
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 474697000000 | 308161.047 | 30-JAN-11:20 | 62886.42 | 35805.575 | 50139.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159330.02 | 0 | 0
February | 425773000000 | 307609.118 | 21-FEB-11:20 | 62886.42 | 35805.575 | 50139.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158778.091 | 0 | 0
March | 478443000000 | 319672.052 | 28-MAR-17:10 | 41924.28 | 31827.177 | 50139.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195781.563 | 0 | 0
April | 476219000000 | 360062.288 | 01-APR-17:10 | 34936.9 | 27848.78 | 50139.032 | 0 | 15095.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232042.171 | 0 | 0
May | 560720000000 | 449461.154 | 27-MAY-17:10 | 34936.9 | 27848.78 | 50139.032 | 0 | 89513.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247023.087 | 0 | 0
June | 614380000000 | 468581.964 | 29-JUN-17:10 | 41924.28 | 31827.177 | 50139.032 | 0 | 95424.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249266.502 | 0 | 0
July | 664247000000 | 467528.585 | 13-JUL-17:10 | 41924.28 | 31827.177 | 50139.032 | 0 | 90576.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253061.417 | 0 | 0
August | 663880000000 | 467575.909 | 25-AUG-17:10 | 41924.28 | 31827.177 | 50139.032 | 0 | 93100.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250585.128 | 0 | 0
September | 552123000000 | 402893.202 | 14-SEP-17:10 | 41924.28 | 31827.177 | 50139.032 | 0 | 45245.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233756.817 | 0 | 0
October | 493333000000 | 348314.092 | 07-OCT-17:10 | 34936.9 | 27848.78 | 50139.032 | 0 | 18376.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217012.822 | 0 | 0
November | 459544000000 | 322040.837 | 02-NOV-18:10 | 41924.28 | 31827.177 | 50139.032 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 193820.2 | 0 | 0
December | 472045000000 | 311837.768 | 02-DEC-11:20 | 62886.42 | 35805.575 | 50139.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163006.742 | 0 | 0
Annual Sum or Average | 6335410000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 425773000000 | 307609.118 |  | 34936.9 | 27848.78 | 50139.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158778.091 | 0 | 0
Maximum of Months | 664247000000 | 468581.964 |  | 62886.42 | 35805.575 | 50139.032 | 0 | 95424.973 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 253061.417 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 95856.19 | 35193.88 | 0 | 131050.07
Cost per Total Building Area ($/m2) | 22.93 | 8.42 | 0 | 31.35
Cost per Net Conditioned Building Area ($/m2) | 22.93 | 8.42 | 0 | 31.35
14-helena
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 9864.14 | 2359.4 | 2359.4
Net Site Energy | 9864.14 | 2359.4 | 2359.4
Total Source Energy | 24774.26 | 5925.73 | 5925.73
Net Source Energy | 24774.26 | 5925.73 | 5925.73
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 3671.79 | 0 | 0 | 0 | 0
Cooling | 85.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1102.86 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.86 | 0 | 0 | 0 | 87.12
Refrigeration | 3004.87 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5873.58 | 3990.57 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 5873.58 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 5873.58 | 100
Total On-Site and Utility Electric Sources | 5873.58 | 100
Total Electricity End Uses | 5873.58 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.591 | 0.65 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.39 | 0.495 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11512.41 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 61533.46 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 48587.83 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 191811.24 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 63238.97 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 47181.53 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.7 | 1318.78 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.72 | 7048.82 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.94 | 5565.86 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 11.59 | 21972.48 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.82 | 7244.19 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.85 | 5404.77 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4456.85
PSZ-AC:2_HEATC | 69568.4
PSZ-AC:3_HEATC | 34836.8
PSZ-AC:4_HEATC | 245446.48
PSZ-AC:5_HEATC | 76946.52
PSZ-AC:6_HEATC | 60374.68
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 150039.8248 | 232.3182 | 348.3232 | 0 | 0.0025 | 8258601.9185 | 61220.9307
February | 130608.4821 | 205.4733 | 314.9379 | 0 | 0.0022 | 7467667.1109 | 53605.7365
March | 132626.1338 | 216.6538 | 348.7579 | 0 | 0.0025 | 8271059.9143 | 55207.7627
April | 122121.0319 | 203.3097 | 334.9366 | 0 | 0.0024 | 7943918.7479 | 51203.7855
May | 125571.0023 | 214.6358 | 364.5878 | 0 | 0.0025 | 8648077.0898 | 53189.94
June | 129969.3534 | 226.0456 | 391.4328 | 0 | 0.0027 | 9285436.6366 | 55429.2082
July | 138291.2517 | 242.8588 | 424.957 | 0 | 0.003 | 10081000 | 59204.4698
August | 138595.9722 | 242.8738 | 424.0123 | 0 | 0.0029 | 10058500 | 59284.6458
September | 125433.9427 | 216.9963 | 373.5739 | 0 | 0.0026 | 8861622.7187 | 53382.7043
October | 125789.5206 | 211.1945 | 351.426 | 0 | 0.0025 | 8335295.1149 | 52913.7458
November | 129326.1549 | 209.5074 | 333.7309 | 0 | 0.0024 | 7914388.8241 | 53664.3876
December | 146287.6156 | 228.5031 | 346.8262 | 0 | 0.0025 | 8223488.3441 | 59882.729
Annual Sum or Average | 1594660.286 | 2650.3703 | 4357.5023 | 0 | 0.0306 | 103349000 | 668190.0459
Minimum of Months | 122121.0319 | 203.3097 | 314.9379 | 0 | 0.0022 | 7467667.1109 | 51203.7855
Maximum of Months | 150039.8248 | 242.8738 | 424.957 | 0 | 0.003 | 10081000 | 61220.9307
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 469356000000 | 308101.676 | 23-JAN-11:20 | 62886.42 | 35805.575 | 49397.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160012.008 | 0 | 0
February | 424405000000 | 317420.446 | 02-FEB-18:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 189941.168 | 0 | 0
March | 470064000000 | 324140.394 | 30-MAR-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 8429.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192562.127 | 0 | 0
April | 451472000000 | 319675.03 | 06-APR-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 6031.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190494.099 | 0 | 0
May | 491491000000 | 351875.151 | 16-MAY-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 24825.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203900.997 | 0 | 0
June | 527714000000 | 403548.712 | 23-JUN-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 56985.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223414.306 | 0 | 0
July | 572929000000 | 408383.48 | 21-JUL-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 67237.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217996.876 | 0 | 0
August | 571651000000 | 401349.827 | 11-AUG-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 51844.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226356.105 | 0 | 0
September | 503627000000 | 381996.8 | 01-SEP-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 42181.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216666.64 | 0 | 0
October | 473715000000 | 342997.4 | 06-OCT-17:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 17583.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202265.221 | 0 | 0
November | 449794000000 | 309342.905 | 07-NOV-18:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 181863.627 | 0 | 0
December | 467360000000 | 306376.635 | 29-DEC-18:10 | 41924.28 | 31827.177 | 49397.673 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 178897.357 | 0 | 0
Annual Sum or Average | 5873580000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 424405000000 | 306376.635 |  | 41924.28 | 31827.177 | 49397.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160012.008 | 0 | 0
Maximum of Months | 572929000000 | 408383.48 |  | 62886.42 | 35805.575 | 49397.673 | 0 | 67237.473 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 226356.105 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 114762.79 | 32934.75 | 0 | 147697.54
Cost per Total Building Area ($/m2) | 27.45 | 7.88 | 0 | 35.33
Cost per Net Conditioned Building Area ($/m2) | 27.45 | 7.88 | 0 | 35.33
15-duluth
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 11390.28 | 2724.43 | 2724.43
Net Site Energy | 11390.28 | 2724.43 | 2724.43
Total Source Energy | 26525.34 | 6344.57 | 6344.57
Net Source Energy | 26525.34 | 6344.57 | 6344.57
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 5062.54 | 0 | 0 | 0 | 0
Cooling | 58.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1179.56 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 25.51 | 0 | 0 | 0 | 87.12
Refrigeration | 3089.17 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6007.31 | 5382.97 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 6007.31 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 6007.31 | 100
Total On-Site and Utility Electric Sources | 6007.31 | 100
Total Electricity End Uses | 6007.31 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.512 | 0.55 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 3.24 | 0.49 | 0.49 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12867.37 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 89804 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 45132.66 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 267285 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 78216.05 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43703.77 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.71 | 1343.9 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.92 | 7430.51 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.73 | 5170.06 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 12.53 | 23767.95 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 4.09 | 7749.62 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.64 | 5006.38 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 4977.77
PSZ-AC:2_HEATC | 79379.7
PSZ-AC:3_HEATC | 37420.21
PSZ-AC:4_HEATC | 282685.2
PSZ-AC:5_HEATC | 88161.99
PSZ-AC:6_HEATC | 62818.55
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 156632.347 | 238.0491 | 312.9002 | 0 | 0.0024 | 205507.2971 | 63374.9072
February | 137229.4652 | 211.0106 | 282.1169 | 0 | 0.0021 | 185302.91 | 55758.5
March | 139172.7947 | 221.6009 | 310.8659 | 0 | 0.0023 | 204226.9089 | 57274.7717
April | 120581.9096 | 201.0594 | 298.8415 | 0 | 0.0022 | 196372.082 | 50489.9668
May | 119560.541 | 207.4191 | 322.5641 | 0 | 0.0024 | 211996.3569 | 50832.9998
June | 121938.4002 | 218.2903 | 350.9451 | 0 | 0.0026 | 230676.5444 | 52488.8004
July | 138230.3213 | 249.475 | 404.4097 | 0 | 0.003 | 265826.6031 | 59694.7437
August | 134625.9144 | 241.6924 | 389.7052 | 0 | 0.0028 | 256156.2352 | 58016.0808
September | 121226.4893 | 213.0721 | 336.0548 | 0 | 0.0025 | 220874.0192 | 51805.3889
October | 123121.9712 | 208.4922 | 315.5484 | 0 | 0.0023 | 207364.5706 | 51859.1829
November | 132517.6135 | 213.2817 | 303.4169 | 0 | 0.0023 | 199344.4446 | 54753.6324
December | 152417.9445 | 234.097 | 312.4686 | 0 | 0.0024 | 205237.3859 | 61904.1964
Annual Sum or Average | 1597255.7119 | 2657.5397 | 3939.8373 | 0 | 0.0293 | 2588885.358 | 668253.1711
Minimum of Months | 119560.541 | 201.0594 | 282.1169 | 0 | 0.0021 | 185302.91 | 50489.9668
Maximum of Months | 156632.347 | 249.475 | 404.4097 | 0 | 0.003 | 265826.6031 | 63374.9072
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 476864000000 | 305964.702 | 13-JAN-11:20 | 62886.42 | 35805.575 | 51311.206 | 0 | 161.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155800.359 | 0 | 0
February | 429981000000 | 311089.875 | 21-FEB-11:20 | 62886.42 | 35805.575 | 51311.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161086.674 | 0 | 0
March | 473893000000 | 312445.241 | 30-MAR-10:20 | 62886.42 | 35805.575 | 51311.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162442.04 | 0 | 0
April | 455667000000 | 319472.332 | 14-APR-10:20 | 62886.42 | 35805.575 | 51311.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169469.132 | 0 | 0
May | 491922000000 | 347651.854 | 31-MAY-17:10 | 41924.28 | 31827.177 | 51311.206 | 0 | 19971.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202618.014 | 0 | 0
June | 535268000000 | 425489.721 | 14-JUN-17:10 | 41924.28 | 31827.177 | 51311.206 | 0 | 57595.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242831.557 | 0 | 0
July | 616831000000 | 448813.394 | 06-JUL-17:10 | 41924.28 | 31827.177 | 51311.206 | 0 | 79153.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244597.697 | 0 | 0
August | 594391000000 | 431865.46 | 11-AUG-17:10 | 41924.28 | 31827.177 | 51311.206 | 0 | 62992.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243810.244 | 0 | 0
September | 512522000000 | 376502.531 | 08-SEP-17:10 | 41924.28 | 31827.177 | 51311.206 | 0 | 16702.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234737.054 | 0 | 0
October | 481174000000 | 337855.677 | 07-OCT-17:10 | 34936.9 | 27848.78 | 51311.206 | 0 | 10043.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213715.338 | 0 | 0
November | 462564000000 | 328848.456 | 09-NOV-11:20 | 62886.42 | 35805.575 | 51311.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178845.255 | 0 | 0
December | 476238000000 | 310007.127 | 02-DEC-11:20 | 62886.42 | 35805.575 | 51311.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160003.926 | 0 | 0
Annual Sum or Average | 6007310000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 429981000000 | 305964.702 |  | 34936.9 | 27848.78 | 51311.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155800.359 | 0 | 0
Maximum of Months | 616831000000 | 448813.394 |  | 62886.42 | 35805.575 | 51311.206 | 0 | 79153.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244597.697 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 90511.25 | 42374.3 | 0 | 132885.56
Cost per Total Building Area ($/m2) | 21.65 | 10.14 | 0 | 31.78
Cost per Net Conditioned Building Area ($/m2) | 21.65 | 10.14 | 0 | 31.78
16-fairbanks
| Total Energy (GJ) | Energy Per Total Building Area (MJ/m2) | Energy Per Conditioned Building Area (MJ/m2)
Total Site Energy | 13850.7 | 3312.93 | 3312.93
Net Site Energy | 13850.7 | 3312.93 | 3312.93
Total Source Energy | 29426.47 | 7038.49 | 7038.49
Net Source Energy | 29426.47 | 7038.49 | 7038.49
Area (m2)
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
| Electricity (GJ) | Natural Gas (GJ) | Other Fuel (GJ) | District Cooling (GJ) | District Heating (GJ) | Water (m3)
Heating | 0 | 7761.27 | 0 | 0 | 0 | 0
Cooling | 19.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 933.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 67.51 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 678.54 | 294.92 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1175.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 27.77 | 0 | 0 | 0 | 87.12
Refrigeration | 2891.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5766.74 | 8083.96 | 0 | 0 | 0 | 87.12
| Electricity (GJ) | Percent Electricity (%)
Fuel-Fired Power Generation | 0 | 0
High Temperature Geothermal* | 0 | 0
Photovoltaic Power | 0 | 0
Wind Power* | 0 | 0
Net Decrease in On-Site Storage | 0 | 0
Total On-Site Electric Sources | 0 | 0
Electricity Coming From Utility | 5766.74 | 100
Surplus Electricity Going To Utility | 0 | 0
Net Electricity From Utility | 5766.74 | 100
Total On-Site and Utility Electric Sources | 5766.74 | 100
Total Electricity End Uses | 5766.74 | 100
| Construction | Reflectance | U-Factor with Film (W/m2-K) | U-Factor no Film (W/m2-K) | Gross Area (m2) | Azimuth (deg) | Tilt (deg) | Cardinal Direction
OFFICE_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 60.34 | 0 | 90 | N
OFFICE_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 54.71 | 90 | 90 | E
OFFICE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 88.84 | 0 | 180
OFFICE_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 88.84 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 621.89 | 180 | 0
DELI_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 224.72 | 0 | 180
DELI_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 224.72 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 2324.94 | 0 | 180
SALES_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 2324.94 | 180 | 0
PRODUCE_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 267.12 | 270 | 90 | W
PRODUCE_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 98.96 | 180 | 90 | S
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 711.36 | 180 | 0
BAKERY_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS | 0.08 | 0.454 | 0.49 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 1.627 | 2.69 | 209.04 | 0 | 180
BAKERY_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 209.04 | 180 | 0
| Construction | Area of Opening (m2) | U-Factor | SHGC | Visible Transmittance | Shade Control | Parent Surface
SALES_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 174.7 | 2.62 | 0.49 | 0.49 | No | SALES_WALL_SOUTH
| Type | Nominal Capacity (W) | Nominal Efficiency (W/W)
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12175.18 | 2.78
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 65171.36 | 2.78
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44375.8 | 2.78
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 192775.87 | 2.78
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 66167.16 | 2.78
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 43101.66 | 2.78
| Type | Total Efficiency (W/W) | Delta Pressure (pa) | Max Flow Rate (m3/s) | Rated Power (W) | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.35 | 250 | 1.18 | 842.79 | 1 | Zone Exhaust Fans
PSZ-AC:1 FAN | Fan:ConstantVolume | 0.26 | 500 | 0.74 | 1394.7 | 1 | Fan Energy
PSZ-AC:2 FAN | Fan:ConstantVolume | 0.26 | 500 | 3.94 | 7465.55 | 1 | Fan Energy
PSZ-AC:3 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.68 | 5083.36 | 1 | Fan Energy
PSZ-AC:4 FAN | Fan:ConstantVolume | 0.26 | 500 | 11.65 | 22082.98 | 1 | Fan Energy
PSZ-AC:5 FAN | Fan:ConstantVolume | 0.26 | 500 | 4 | 7579.62 | 1 | Fan Energy
PSZ-AC:6 FAN | Fan:ConstantVolume | 0.26 | 500 | 2.6 | 4937.41 | 1 | Fan Energy
Nominal Capacity [W]
PSZ-AC:1_HEATC | 5419.7
PSZ-AC:2_HEATC | 97340.73
PSZ-AC:3_HEATC | 43871.72
PSZ-AC:4_HEATC | 342661.93
PSZ-AC:5_HEATC | 107844.35
PSZ-AC:6_HEATC | 76719.2
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 167647.9321 | 184.3688 | 673.8174 | 0 | 0.0024 | 135163.2127 | 62975.8257
February | 147638.913 | 163.0794 | 608.36 | 0 | 0.0022 | 122036.7427 | 55569.6373
March | 142929.45 | 161.7681 | 670.3524 | 0 | 0.0024 | 134492.8064 | 54395.7777
April | 115587.2805 | 134.8911 | 627.2418 | 0 | 0.0022 | 125862.2715 | 44616.1091
May | 103961.6363 | 126.0739 | 663.5295 | 0 | 0.0023 | 133162.6783 | 40859.6279
June | 105855.2883 | 130.6384 | 723.0662 | 0 | 0.0025 | 145118.6865 | 41952.908
July | 113939.1228 | 141.1675 | 789.8471 | 0 | 0.0027 | 158523.2956 | 45241.7688
August | 111625.5846 | 137.3645 | 754.216 | 0 | 0.0026 | 151369.1573 | 44179.0133
September | 106935.0835 | 128.6136 | 660.2022 | 0 | 0.0023 | 132491.314 | 41864.2029
October | 125047.1803 | 145.0594 | 660.3445 | 0 | 0.0023 | 132501.1851 | 48133.4759
November | 147194.2413 | 164.6757 | 650.2004 | 0 | 0.0023 | 130440.8542 | 55723.505
December | 161939.6393 | 179.2517 | 675.1546 | 0 | 0.0024 | 135437.6697 | 61010.1375
Annual Sum or Average | 1550301.3523 | 1796.9518 | 8156.3322 | 0 | 0.0285 | 1636599.8739 | 596521.9892
Minimum of Months | 103961.6363 | 126.0739 | 608.36 | 0 | 0.0022 | 122036.7427 | 40859.6279
Maximum of Months | 167647.9321 | 184.3688 | 789.8471 | 0 | 0.0027 | 158523.2956 | 62975.8257
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 476262000000 | 307373.64 | 03-JAN-11:09 | 62886.42 | 35805.575 | 49386.399 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 154965.099 | 0 | 0
February | 430010000000 | 303819.057 | 27-FEB-11:20 | 62886.42 | 35805.575 | 49386.399 | 0 | 191.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155548.858 | 0 | 0
March | 473900000000 | 307244.489 | 09-MAR-11:20 | 62886.42 | 35805.575 | 49386.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159166.095 | 0 | 0
April | 443489000000 | 306599.583 | 14-APR-10:20 | 62886.42 | 35805.575 | 49386.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158521.189 | 0 | 0
May | 469213000000 | 331067.144 | 30-MAY-17:10 | 41924.28 | 31827.177 | 49386.399 | 0 | 7233.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200696.16 | 0 | 0
June | 511341000000 | 370427.129 | 21-JUN-17:10 | 41924.28 | 31827.177 | 49386.399 | 0 | 24692.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222596.467 | 0 | 0
July | 558574000000 | 379374.802 | 29-JUL-17:10 | 34936.9 | 27848.78 | 49386.399 | 0 | 39253.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227949.311 | 0 | 0
August | 533366000000 | 371289.084 | 15-AUG-17:10 | 41924.28 | 31827.177 | 49386.399 | 0 | 28577.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219573.744 | 0 | 0
September | 466847000000 | 321932.199 | 01-SEP-17:10 | 41924.28 | 31827.177 | 49386.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198794.342 | 0 | 0
October | 466882000000 | 313594.486 | 02-OCT-10:20 | 62886.42 | 35805.575 | 49386.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165516.092 | 0 | 0
November | 459622000000 | 304762.556 | 14-NOV-18:10 | 41924.28 | 31827.177 | 49386.399 | 0 | 394.636 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 176899.917 | 0 | 0
December | 477229000000 | 308517.38 | 18-DEC-11:09 | 62886.42 | 35805.575 | 49386.399 | 0 | 0 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 156108.839 | 0 | 0
Annual Sum or Average | 5766740000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 430010000000 | 303819.057 |  | 34936.9 | 27848.78 | 49386.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154965.099 | 0 | 0
Maximum of Months | 558574000000 | 379374.802 |  | 62886.42 | 35805.575 | 49386.399 | 0 | 39253.412 | 4330.148 | 0 | 0 | 0 | 0 | 0 | 0 | 227949.311 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 142552.16 | 33450.16 | 0 | 176002.33
Cost per Total Building Area ($/m2) | 34.1 | 8 | 0 | 42.1
Cost per Net Conditioned Building Area ($/m2) | 34.1 | 8 | 0 | 42.1

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago-O'Hare | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck | Insulation Entirely Above Deck
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.88 | 6.88 | 6.88 | 3.24 | 3.24 | 3.24 | 6.88 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 2.62
| SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.34 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.49 | 0.49
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 12.199 | 11.6746 | 14.5192 | 10.6052 | 7.5327 | 11.8499 | 6.4639 | 10.2795 | 10.1124 | 8.0273 | 12.2371 | 11.8865 | 12.616 | 11.5124 | 12.8674 | 12.1752
| PSZ-AC:2_COOLC DXCOIL | 89.6756 | 77.638 | 70.4406 | 69.0885 | 34.6678 | 53.9471 | 36.6481 | 73.9769 | 54.7528 | 43.3682 | 87.8847 | 64.7127 | 88.7822 | 61.5335 | 89.804 | 65.1714
| PSZ-AC:3_COOLC DXCOIL | 53.677 | 50.3624 | 54.2876 | 49.0477 | 45.5331 | 52.5103 | 42.4734 | 47.6229 | 52.9481 | 43.6197 | 47.3259 | 51.6069 | 47.288 | 48.5878 | 45.1327 | 44.3758
| PSZ-AC:4_COOLC DXCOIL | 181.2911 | 224.1404 | 144.768 | 234.1168 | 127.4233 | 149.7149 | 133.5343 | 239.2026 | 179.9235 | 177.7901 | 276.7782 | 208.8662 | 297.0813 | 191.8112 | 267.285 | 192.7759
| PSZ-AC:5_COOLC DXCOIL | 101.0439 | 88.1524 | 78.5631 | 72.1091 | 38.7952 | 56.5963 | 40.2644 | 76.3508 | 57.6356 | 46.8183 | 90.7036 | 67.5944 | 90.9939 | 63.239 | 78.216 | 66.1672
| PSZ-AC:6_COOLC DXCOIL | 71.4019 | 64.3475 | 53.1256 | 61.0173 | 43.9722 | 50.9041 | 41.4801 | 59.0344 | 51.0857 | 42.4857 | 58.6289 | 49.92 | 54.9967 | 47.1815 | 43.7038 | 43.1017
Heating (kW)
| PSZ-AC:1_HEATC | 5.024 | 4.9139 | 6.0093 | 4.1839 | 3.2906 | 4.7816 | 2.8623 | 4.0915 | 3.6689 | 3.5139 | 4.6808 | 4.3129 | 4.9248 | 4.4569 | 4.9778 | 5.4197
| PSZ-AC:2_HEATC | 40.0791 | 49.4234 | 48.0171 | 47.6104 | 25.2987 | 44.4619 | 29.5607 | 56.0944 | 46.6397 | 41.7171 | 69.8307 | 60.2088 | 76.8786 | 69.5684 | 79.3797 | 97.3407
| PSZ-AC:3_HEATC | 26.6025 | 30.0982 | 29.1905 | 31.1298 | 25.1016 | 29.1057 | 25.2487 | 32.887 | 28.468 | 28.4336 | 36.0716 | 31.579 | 37.9178 | 34.8368 | 37.4202 | 43.8717
| PSZ-AC:4_HEATC | 84.7948 | 138.3987 | 110.7471 | 155.9416 | 92.9865 | 126.4811 | 107.71 | 177.3619 | 159.0133 | 141.2702 | 239.7431 | 213.6076 | 272.5396 | 245.4465 | 282.6852 | 342.6619
| PSZ-AC:5_HEATC | 45.7835 | 56.5939 | 54.1321 | 50.1204 | 28.3106 | 47.8133 | 32.4777 | 58.7779 | 50.9374 | 45.0358 | 77.3988 | 66.6322 | 85.2933 | 76.9465 | 88.162 | 107.8444
| PSZ-AC:6_HEATC | 33.4442 | 43.4276 | 41.5172 | 47.2565 | 32.0885 | 43.0045 | 33.4583 | 50.8823 | 45.1487 | 40.8681 | 59.3809 | 53.9229 | 64.2374 | 60.3747 | 62.8186 | 76.7192
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 2.73 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| PSZ-AC:2_COOLC DXCOIL | 2.73 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| PSZ-AC:3_COOLC DXCOIL | 2.73 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| PSZ-AC:4_COOLC DXCOIL | 2.73 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| PSZ-AC:5_COOLC DXCOIL | 2.73 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| PSZ-AC:6_COOLC DXCOIL | 2.73 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
| Heating Efficiency (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
HVAC Control
| Economizer | None | None | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | None | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb | Fixed Dry Bulb
Fan Max Flow Rate (m3/s )
| BAKERY EXHAUST FAN | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18 | 1.18
| PSZ-AC:1 FAN | 0.7 | 0.68 | 0.88 | 0.6 | 0.46 | 0.72 | 0.39 | 0.56 | 0.61 | 0.48 | 0.65 | 0.72 | 0.69 | 0.7 | 0.71 | 0.74
| PSZ-AC:2 FAN | 3.67 | 3.36 | 4.26 | 2.88 | 2.09 | 3.26 | 2.21 | 3.05 | 3.31 | 2.62 | 3.54 | 3.91 | 3.78 | 3.72 | 3.92 | 3.94
| PSZ-AC:3 FAN | 3.03 | 2.96 | 3.28 | 2.96 | 2.75 | 3.17 | 2.57 | 2.86 | 3.2 | 2.64 | 2.86 | 3.12 | 2.86 | 2.94 | 2.73 | 2.68
| PSZ-AC:4 FAN | 7.3 | 9.03 | 8.56 | 9.43 | 7.7 | 9.04 | 8.07 | 9.63 | 10.87 | 8.87 | 11.15 | 12.62 | 11.96 | 11.59 | 12.53 | 11.65
| PSZ-AC:5 FAN | 4.19 | 3.85 | 4.75 | 3.03 | 2.34 | 3.42 | 2.43 | 3.19 | 3.48 | 2.83 | 3.69 | 4.08 | 3.94 | 3.82 | 4.09 | 4
| PSZ-AC:6 FAN | 2.88 | 2.83 | 3.21 | 2.86 | 2.66 | 3.08 | 2.51 | 2.76 | 3.09 | 2.57 | 2.76 | 3.02 | 2.76 | 2.85 | 2.64 | 2.6
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.079519 | 0.10871 | 0.076015 | 0.098928 | 0.12264 | 0.095202 | 0.14459 | 0.069988 | 0.03704 | 0.071097 | 0.09593 | 0.037042 | 0.054469 | 0.07034 | 0.054241 | 0.088991
| Total Cost ($/m2) | 44.74 | 55.86 | 36.54 | 44.97 | 52.16 | 40.81 | 57.32 | 30.34 | 15.15 | 27.78 | 40.51 | 15 | 22.93 | 27.45 | 21.65 | 34.1
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01145 | 0.0080921 | 0.0083408 | 0.0098576 | 0.0085174 | 0.0078158 | 0.0084938 | 0.009747 | 0.0069637 | 0.0083764 | 0.0084204 | 0.0069782 | 0.0078725 | 0.0082531 | 0.0078719 | 0.0041378
| Total Cost ($/m2) | 1.1 | 2.37 | 2.17 | 4.55 | 2.43 | 2.78 | 4.18 | 6.68 | 3.62 | 5.89 | 7.32 | 4.76 | 8.42 | 7.88 | 10.14 | 8
Total Utility Costs
| Cost Intensity ($/m2) | 45.83 | 58.23 | 38.71 | 49.52 | 54.59 | 43.59 | 61.5 | 37.03 | 18.78 | 33.67 | 47.82 | 19.76 | 31.35 | 35.33 | 31.78 | 42.1
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 303658.3333 | 202702.7778 | 214769.4444 | 104597.2222 | 24266.6667 | 130483.3333 | 7933.3333 | 85627.7778 | 59725 | 11619.4444 | 52775 | 39233.3333 | 45852.7778 | 23772.2222 | 16205.5556 | 5511.1111
| Interior Lighting | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778 | 259377.7778
| Exterior Lighting | 18927.7778 | 18919.4444 | 18916.6667 | 18913.8889 | 18900 | 18894.4444 | 18905.5556 | 18894.4444 | 18900 | 18863.8889 | 18897.2222 | 18886.1111 | 18883.3333 | 18880.5556 | 18869.4444 | 18752.7778
| Interior Equipment | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333 | 188483.3333
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 245955.5556 | 258591.6667 | 285100 | 249597.2222 | 204244.4444 | 258075 | 206769.4444 | 257744.4444 | 283897.2222 | 229994.4444 | 292780.5556 | 323272.2222 | 315294.4444 | 306350 | 327655.5556 | 326513.8889
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 1335769.4445 | 1220241.6667 | 1043175 | 1079422.2222 | 1082700 | 936725 | 975908.3333 | 1002447.2222 | 900161.1111 | 925252.7778 | 953116.6667 | 863997.2222 | 931938.8889 | 834686.1111 | 858102.7778 | 803230.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2352175 | 2148319.4445 | 2009822.2222 | 1900391.6667 | 1777972.2222 | 1792041.6667 | 1657380.5556 | 1812575 | 1710547.2222 | 1633591.6667 | 1765430.5556 | 1693250 | 1759836.1111 | 1631550 | 1668697.2222 | 1601872.2222
Gas (MJ)
| Heating | 89200 | 909700 | 775260 | 1614250 | 877640 | 1174310 | 1742090 | 2550090 | 1858520 | 2624740 | 3315130 | 2535580 | 4151930 | 3671790 | 5062540 | 7761270
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920 | 294920
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 15870 | 17830 | 16700 | 19730 | 19360 | 18060 | 20980 | 21220 | 20930 | 21990 | 22520 | 22460 | 23650 | 23860 | 25510 | 27770
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 399980 | 1222440 | 1086870 | 1928900 | 1191910 | 1487290 | 2057990 | 2866220 | 2174370 | 2941650 | 3632570 | 2852950 | 4470500 | 3990570 | 5382970 | 8083960
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 8867810 | 8956400 | 8322230 | 8770300 | 7592610 | 7938640 | 8024560 | 9391490 | 8332340 | 8822580 | 9988120 | 8948650 | 10805910 | 9864140 | 11390280 | 13850700
| On-Site Production (MJ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 261.4745 | 174.5436 | 184.9339 | 90.0667 | 20.8956 | 112.3568 | 6.8312 | 73.7325 | 51.4281 | 10.0053 | 45.4436 | 33.7831 | 39.483 | 20.4698 | 13.9543 | 4.7455
| Interior Lighting (elec) | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453 | 223.3453
| Exterior Lighting (elec) | 16.2984 | 16.2912 | 16.2888 | 16.2864 | 16.2744 | 16.2697 | 16.2792 | 16.2697 | 16.2744 | 16.2433 | 16.272 | 16.2625 | 16.2601 | 16.2577 | 16.2481 | 16.1477
| Interior Equipment (elec) | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995 | 162.2995
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 211.7877 | 222.6684 | 245.4943 | 214.9235 | 175.8711 | 222.2236 | 178.0453 | 221.9389 | 244.4586 | 198.0439 | 252.1079 | 278.3637 | 271.4941 | 263.7922 | 282.1381 | 281.155
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 1150.2061 | 1050.7273 | 898.2585 | 929.4703 | 932.2927 | 806.5964 | 840.3364 | 863.1885 | 775.1119 | 796.7178 | 820.7109 | 743.9718 | 802.4751 | 718.7326 | 738.8962 | 691.6468
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2025.4139 | 1849.8777 | 1730.6203 | 1636.3917 | 1530.9786 | 1543.0935 | 1427.1394 | 1560.7744 | 1472.9202 | 1406.6552 | 1520.1792 | 1458.0259 | 1515.3619 | 1404.8972 | 1436.8839 | 1379.3422
| Gas (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heating (gas) | 21.3357 | 217.5905 | 185.4339 | 386.1112 | 209.922 | 280.8823 | 416.6892 | 609.9541 | 444.538 | 627.8096 | 792.9434 | 606.4835 | 993.097 | 878.2527 | 1210.9051 | 1856.4123
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417 | 70.5417
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7959 | 4.2647 | 3.9945 | 4.7192 | 4.6307 | 4.3198 | 5.0182 | 5.0756 | 5.0062 | 5.2598 | 5.3865 | 5.3722 | 5.6568 | 5.7071 | 6.1017 | 6.6423
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 95.6709 | 292.3945 | 259.9676 | 461.3721 | 285.0921 | 355.7438 | 492.2491 | 685.569 | 520.0859 | 703.611 | 868.8717 | 682.395 | 1069.2955 | 954.5014 | 1287.5485 | 1933.5963
| Purchased Cooling (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Purchased Heating (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2121.0848 | 2142.2745 | 1990.5879 | 2097.7614 | 1816.0706 | 1898.8373 | 1919.3884 | 2246.3434 | 1993.0061 | 2110.2662 | 2389.0509 | 2140.4208 | 2584.6574 | 2359.3962 | 2724.4325 | 3312.9385
| On-Site Production (MJ/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 413.0194 | 391.8079 | 330.2576 | 354.8286 | 321.4313 | 312.6007 | 322.8062 | 326.1323 | 307.3592 | 314.3108 | 310.4358 | 315.6396 | 308.161 | 308.1017 | 0 | 307.3736
| Feb | 425.9837 | 374.5044 | 350.9145 | 339.3659 | 334.6888 | 326.3472 | 330.7467 | 314.2934 | 310.0192 | 305.9667 | 310.163 | 311.5845 | 307.6091 | 317.4204 | 0 | 303.8191
| Mar | 438.4042 | 401.4477 | 392.4294 | 359.2412 | 332.0446 | 331.5471 | 315.2816 | 365.5131 | 318.9414 | 317.0029 | 337.6817 | 338.2524 | 319.6721 | 324.1404 | 0 | 307.2445
| Apr | 454.1189 | 430.4858 | 395.8008 | 392.8917 | 341.4893 | 389.8733 | 328.7392 | 366.7777 | 352.8437 | 327.1891 | 336.3606 | 345.2303 | 360.0623 | 319.675 | 0 | 306.5996
| May | 470.0289 | 477.4785 | 445.6309 | 433.6515 | 362.4087 | 404.5807 | 341.6273 | 410.3841 | 379.0948 | 357.358 | 417.3361 | 377.3172 | 449.4612 | 351.8752 | 0 | 331.0671
| Jun | 499.4142 | 482.2368 | 515.0555 | 445.3891 | 361.8541 | 454.754 | 350.0465 | 482.536 | 404.2177 | 357.067 | 456.723 | 391.9082 | 468.582 | 403.5487 | 0 | 370.4271
| Jul | 487.1066 | 498.7532 | 521.7367 | 478.4265 | 367.308 | 461.7227 | 367.7865 | 483.8898 | 419.5079 | 388.2727 | 477.3011 | 412.9785 | 467.5286 | 408.3835 | 0 | 379.3748
| Aug | 489.3494 | 496.6646 | 515.5401 | 452.723 | 388.3917 | 468.2249 | 362.1667 | 483.7193 | 432.0642 | 379.997 | 474.2834 | 412.8728 | 467.5759 | 401.3498 | 0 | 371.2891
| Sep | 471.2338 | 471.2705 | 486.7148 | 423.3275 | 373.3603 | 433.8207 | 371.3588 | 414.8401 | 379.0065 | 396.4341 | 419.6668 | 389.9833 | 402.8932 | 381.9968 | 0 | 321.9322
| Oct | 471.2271 | 431.3904 | 419.1135 | 384.636 | 357.012 | 379.6492 | 344.8266 | 386.2806 | 362.443 | 327.2804 | 375.3312 | 352.6468 | 348.3141 | 342.9974 | 0 | 313.5945
| Nov | 442.5456 | 410.9377 | 366.3194 | 351.5771 | 343.463 | 321.9119 | 331.6225 | 371.7991 | 314.973 | 332.0987 | 375.213 | 315.5082 | 322.0408 | 309.3429 | 0 | 304.7626
| Dec | 415.6108 | 389.7729 | 348.5215 | 351.2536 | 330.468 | 312.9161 | 322.7131 | 326.0106 | 306.0484 | 309.3922 | 318.6224 | 309.8453 | 311.8378 | 306.3766 | 0 | 308.5174
Time of Peak Electrical Demand
| Jan | 23-JAN-18:10 | 20-JAN-18:10 | 27-JAN-18:10 | 24-JAN-18:10 | 10-JAN-18:10 | 23-JAN-18:10 | 05-JAN-18:10 | 09-JAN-11:20 | 02-JAN-11:20 | 14-JAN-11:20 | 17-JAN-18:10 | 23-JAN-11:20 | 30-JAN-11:20 | 23-JAN-11:20 | 13-JAN-11:20 | 03-JAN-11:09
| Feb | 23-FEB-11:00 | 15-FEB-18:10 | 28-FEB-18:10 | 21-FEB-18:10 | 13-FEB-11:39 | 10-FEB-18:10 | 15-FEB-18:10 | 13-FEB-11:20 | 14-FEB-18:10 | 24-FEB-18:10 | 28-FEB-11:20 | 11-FEB-11:20 | 21-FEB-11:20 | 02-FEB-18:10 | 21-FEB-11:20 | 27-FEB-11:20
| Mar | 13-MAR-17:10 | 25-MAR-17:10 | 17-MAR-17:10 | 29-MAR-17:10 | 04-MAR-11:39 | 31-MAR-17:10 | 27-MAR-17:10 | 09-MAR-18:10 | 20-MAR-17:10 | 30-MAR-17:10 | 14-MAR-17:10 | 30-MAR-17:10 | 28-MAR-17:10 | 30-MAR-17:10 | 30-MAR-10:20 | 09-MAR-11:20
| Apr | 03-APR-17:10 | 29-APR-17:10 | 26-APR-17:10 | 14-APR-17:10 | 11-APR-17:10 | 21-APR-17:10 | 29-APR-10:50 | 04-APR-17:10 | 21-APR-17:10 | 29-APR-17:10 | 10-APR-10:09 | 26-APR-17:10 | 01-APR-17:10 | 06-APR-17:10 | 14-APR-10:20 | 14-APR-10:20
| May | 18-MAY-17:10 | 26-MAY-17:10 | 30-MAY-17:10 | 31-MAY-17:10 | 30-MAY-17:10 | 31-MAY-17:10 | 25-MAY-17:10 | 15-MAY-17:10 | 31-MAY-17:10 | 05-MAY-17:10 | 30-MAY-17:10 | 24-MAY-17:10 | 27-MAY-17:10 | 16-MAY-17:10 | 31-MAY-17:10 | 30-MAY-17:10
| Jun | 27-JUN-17:10 | 13-JUN-17:10 | 28-JUN-17:10 | 19-JUN-17:10 | 28-JUN-17:10 | 27-JUN-17:10 | 16-JUN-10:50 | 30-JUN-17:10 | 29-JUN-17:10 | 28-JUN-17:10 | 08-JUN-12:00 | 28-JUN-10:50 | 29-JUN-17:10 | 23-JUN-17:10 | 14-JUN-17:10 | 21-JUN-17:10
| Jul | 13-JUL-17:10 | 05-JUL-17:10 | 11-JUL-17:10 | 03-JUL-17:10 | 10-JUL-17:10 | 25-JUL-17:10 | 03-JUL-10:50 | 25-JUL-10:00 | 20-JUL-17:10 | 31-JUL-17:10 | 14-JUL-10:00 | 19-JUL-10:50 | 13-JUL-17:10 | 21-JUL-17:10 | 06-JUL-17:10 | 29-JUL-17:10
| Aug | 21-AUG-17:10 | 31-AUG-17:10 | 01-AUG-17:10 | 14-AUG-17:10 | 08-AUG-17:10 | 02-AUG-17:10 | 15-AUG-10:50 | 17-AUG-17:10 | 01-AUG-17:10 | 18-AUG-17:10 | 04-AUG-17:10 | 30-AUG-10:50 | 25-AUG-17:10 | 11-AUG-17:10 | 11-AUG-17:10 | 15-AUG-17:10
| Sep | 13-SEP-17:10 | 15-SEP-17:10 | 08-SEP-17:10 | 06-SEP-17:10 | 09-SEP-10:00 | 01-SEP-17:10 | 28-SEP-17:10 | 08-SEP-17:10 | 13-SEP-17:10 | 02-SEP-17:10 | 06-SEP-10:00 | 01-SEP-17:10 | 14-SEP-17:10 | 01-SEP-17:10 | 08-SEP-17:10 | 01-SEP-17:10
| Oct | 06-OCT-17:10 | 06-OCT-17:10 | 13-OCT-17:10 | 20-OCT-17:10 | 05-OCT-10:50 | 06-OCT-10:50 | 16-OCT-17:10 | 20-OCT-17:10 | 11-OCT-17:10 | 05-OCT-17:10 | 31-OCT-11:00 | 05-OCT-17:10 | 07-OCT-17:10 | 06-OCT-17:10 | 07-OCT-17:10 | 02-OCT-10:20
| Nov | 01-NOV-18:10 | 27-NOV-18:10 | 13-NOV-18:10 | 28-NOV-18:10 | 20-NOV-11:50 | 21-NOV-18:10 | 16-NOV-18:10 | 04-NOV-11:00 | 10-NOV-11:20 | 03-NOV-18:10 | 02-NOV-18:10 | 10-NOV-11:39 | 02-NOV-18:10 | 07-NOV-18:10 | 09-NOV-11:20 | 14-NOV-18:10
| Dec | 15-DEC-18:10 | 02-DEC-11:00 | 13-DEC-18:10 | 04-DEC-18:10 | 04-DEC-11:50 | 05-DEC-11:39 | 14-DEC-18:10 | 23-DEC-11:20 | 22-DEC-11:20 | 28-DEC-18:10 | 12-DEC-18:10 | 30-DEC-11:20 | 02-DEC-11:20 | 29-DEC-18:10 | 02-DEC-11:20 | 18-DEC-11:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
| Total Building | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
Emissions
| Carbon Equivalent (kg) | 652295.9898 | 738639.686 | 626315.3096 | 620173.2021 | 229277.5444 | 631230.8001 | 230802.3267 | 540819.0339 | 737965.101 | 172027.0899 | 1006743.7755 | 743135.8682 | 682994.5031 | 668190.0459 | 668253.1711 | 596521.9892
| CO2 (kg) | 1514563.991 | 1861833.3105 | 1483439.153 | 1429096.5476 | 616847.2174 | 1509042.4242 | 624344.0511 | 1246228.1039 | 1741452.4094 | 435897.3752 | 2360949.9185 | 1760342.2666 | 1621634.3294 | 1594660.286 | 1597255.7119 | 1550301.3523
| NOX (kg) | 2653.2605 | 2421.3176 | 2462.9548 | 2656.7641 | 531.1173 | 2417.9953 | 539.8835 | 2328.7158 | 2959.5307 | 593.2654 | 4126.2467 | 2962.7405 | 2745.6174 | 2650.3703 | 2657.5397 | 1796.9518
| SO2 (kg) | 10068.3543 | 10247.8154 | 8082.1894 | 6670.8879 | 5174.0052 | 9858.0631 | 4823.3338 | 6617.3929 | 7470.2021 | 1263.4242 | 11898.5719 | 7394.8504 | 4154.6905 | 4357.5023 | 3939.8373 | 8156.3322
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0459 | 0.0289 | 0.022 | 0.0245 | 0.0024 | 0.0186 | 0.0024 | 0.027 | 0.0293 | 0.0052 | 0.0362 | 0.0291 | 0.0308 | 0.0306 | 0.0293 | 0.0285
| Water Environmental Factors (m3) | 1246.0832 | 3495.5689 | 59700.6 | 11865.3 | 31217.2 | 49162.9 | 29099.9 | 411.5227 | 7767.2526 | 16690.1 | 2738.9619 | 7688.7093 | 2730.2788 | 103349 | 2588.8854 | 1636.5999

## Picture
DOE Commercial Building Benchmark - Super Market
Sales
Bakery
Deli
Produce
Office
DryStorage

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.3 | 72.2 | 3764.71
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.9
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 5.8
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | 7.6 | 49 | 2555
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 3.4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.9 | 91.6 | 4776.29
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | 9.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 56 | 2920
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 115.5 | 6022.5
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 3225.6 | 168192
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4368 | 227760
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Deli Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Deli Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Deli Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Deli Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Deli_Case:2_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:2_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:2_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Deli_Case:2_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:1_MEATDISPLAYCASE_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:1_MEATDISPLAYCASE_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:1_MEATDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 3.97 | 206.83
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 5.13 | 267.67
Sales_Case:3_GLASSDOORFROZENFOOD_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:3_GLASSDOORFROZENFOOD_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:5_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:5_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:5_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:5_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:6_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:6_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:6_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:6_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:7_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:7_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:7_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:7_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Bakery Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bakery Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bakery Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Bakery Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bakery_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Bakery_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Bakery_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Bakery_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720