## BuildingSummary
Building Summary Large Hotel new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Large Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 11344.93 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 3.8 1st floor, 5.1 other floors
| Number of Floors | 6 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.3254
| East | 0.2112
| North | 0.2311
| West | 0.2112
| Total | 0.2663
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 3.96 1st floor, 3.05 other floors
| Floor to Floor Height (m) | 3.96 1st floor, 3.05 other floors
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4462.84
| Net Dimensions - Total Area (m2) | 3248.53
| Wall to Skin Ratio | 0.75127
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1477.55
| Net Dimensions - Total Area (m2) | 1477.55
| Roof to Skin Ratio | 0.24873
Window Dimensions (m2)
| South | 609.46
| East | 85.84
| North | 432.93
| West | 85.84
| Total Area (m2) | 1214.07
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1978.83
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15687.82
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 22690.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.31 | See Benchmark Technical Report
HVAC
| System Type | FCU in rooms, CV ventilation, MZVAV in common areas | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Air cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas boiler
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 7180

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 1978.83 | 4826.41 | 2.439 | 0 | 0 | 37.1613 | 53.2498 | 10.76 | 5.38 | 0 | 0 | 0 | 0.25398 | 502.5718 | 0 | 0
Retail_1_Flr_1 | Yes | 1 | 67.07 | 265.76 | 3.9624 | 68.84 | 23.3 | 6.1939 | 10.8285 | 16.14 | 10.76 | 0 | 0 | 0 | 1.5239 | 102.2043 | 0 | 0.55659
Retail_2_Flr_1 | Yes | 1 | 77.67 | 307.76 | 3.9624 | 26.57 | 0 | 6.1939 | 12.5399 | 16.14 | 10.76 | 0 | 0 | 0 | 1.5239 | 118.3571 | 0 | 0.093963
Mech_Flr_1 | Yes | 1 | 164.24 | 650.8 | 3.9625 | 62.8 | 0 | 0 | 0 | 16.14 | 5.38 | 0 | 0 | 0 | 0.25398 | 41.7127 | 0 | 0.10502
Storage_Flr_1 | Yes | 1 | 94.76 | 375.47 | 3.9623 | 36.23 | 0 | 46.4516 | 2.04 | 9.684 | 2.69 | 0 | 0 | 0 | 0.76195 | 72.1998 | 0 | 0.10502
Laundry_Flr_1 | Yes | 1 | 78.04 | 309.22 | 3.9623 | 85.75 | 0 | 23.2258 | 3.3601 | 6.456 | 61.6768 | 535.8521 | 592.7936 | 7.0785 | 0 | 23.7842 | 235.9735 | 0.30182
Cafe_Flr_1 | Yes | 1 | 188.86 | 748.35 | 3.9625 | 152.17 | 65.62 | 1.3935 | 135.5247 | 13.988 | 5.38 | 0 | 0 | 9.438 | 0 | 1279.0819 | 0 | 0.49598
Lobby_Flr_1 | Yes | 1 | 1308.19 | 5183.56 | 3.9624 | 434.79 | 85.24 | 3.0965 | 422.479 | 11.836 | 8.07 | 0 | 0 | 9.438 | 0 | 3987.3572 | 0 | 0.096077
Room_1_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.36556
Room_2_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.3656
Room_3_Mult19_Flr_3 | Yes | 76 | 24.52 | 74.75 | 3.0485 | 11.15 | 3.68 | 16.3467 | 1.5 | 11.836 | 10.52 | 0 | 89.9032 | 0 | 0 | 14.157 | 0 | 0.16235
Room_4_Mult19_Flr_3 | Yes | 76 | 24.53 | 74.77 | 3.0481 | 11.15 | 3.68 | 16.3533 | 1.5 | 11.836 | 10.52 | 0 | 89.9032 | 0 | 0 | 14.157 | 0 | 0.1623
Room_5_Flr_3 | Yes | 4 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.36556
Room_6_Flr_3 | Yes | 4 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.18 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.3656
Corridor_Flr_3 | Yes | 4 | 389.4 | 1186.91 | 3.048 | 48.31 | 15.94 | 92.9031 | 4.1915 | 5.38 | 0 | 0 | 0 | 0 | 0.25398 | 98.8976 | 0 | 0.044299
Room_1_Flr_6 | Yes | 1 | 39.02 | 118.94 | 3.0482 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.72262
Room_2_Flr_6 | Yes | 1 | 39.02 | 118.93 | 3.0479 | 39.95 | 13.19 | 26.0133 | 1.5 | 11.836 | 6.75 | 0 | 4.7317 | 0 | 0 | 14.157 | 0 | 0.72268
Room_3_Mult9_Flr_6 | Yes | 9 | 24.53 | 74.77 | 3.0481 | 63.18 | 6.75 | 16.3533 | 1.5 | 11.836 | 10.52 | 0 | 42.5858 | 0 | 0 | 14.157 | 0 | 1.2767
Banquet_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.55 | 32.21 | 1.3935 | 237.997 | 13.988 | 67.816 | 0 | 0 | 9.438 | 0 | 2246.2157 | 0 | 0.46211
Dining_Flr_6 | Yes | 1 | 331.66 | 1010.89 | 3.048 | 97.55 | 32.21 | 1.3935 | 237.997 | 13.988 | 67.816 | 0 | 0 | 9.438 | 0 | 2246.2157 | 0 | 0.46211
Kitchen_Flr_6 | Yes | 1 | 103.3 | 314.87 | 3.0481 | 87.33 | 26.38 | 18.5806 | 5.5596 | 12.912 | 508.0443 | 2419.2587 | 503.4582 | 7.0785 | 0 | 39.3533 | 2831.682 | 0.65892
Corridor_Flr_6 | Yes | 1 | 412.12 | 1256.16 | 3.048 | 137.5 | 28.22 | 92.9031 | 4.436 | 5.38 | 0 | 0 | 0 | 0 | 0.25398 | 104.6679 | 0 | 0.4762
Building Total Conditioned Zones |  |  | 11344.93 | 35185.06 |  | 4462.84 | 1214.31 |  | 1411.2773 |  |  |  | 15229.9891
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.692 | 1.9531 | 1.9531 | 1.9531 | 1.9531 | 2.2026 | 2.4752
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.262 | 0.262 | 0.262 | 0.34 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366 | 0.44366
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 1743.5339 | 1740.8339 | 1576.2883 | 1641.6819 | 1186.2223 | 2182.1463 | 1166.3988 | 1707.0985 | 1983.6456 | 1303.3808 | 1704.5233 | 1210.0744 | 1653.2387 | 1677.9844 | 1513.4335 | 1290.0688
Heating (kW)
| HEATSYS1 BOILER | 880.054 | 1150.7433 | 1041.0534 | 1200.7618 | 886.3861 | 1074.3994 | 955.9769 | 1302.0107 | 1160.9319 | 1125.26 | 1506.1182 | 1343.9116 | 1626.1562 | 1568.3018 | 1666.3478 | 1961.2453
HVAC Efficiency
| Air Conditioning (COP) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
HVAC Control - Economizer
| ROOM_1_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_2_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_3_MULT19_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_4_MULT19_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_5_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_6_FLR_3 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_1_FLR_6 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_2_FLR_6 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| ROOM_3_MULT9_FLR_6 FAN COILFAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| VAV WITH REHEAT_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| FLR_3_DOAS_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| FLR_6_DOAS_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| LAUNDRY_FLR_1 EXHAUST FAN | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
| ROOM_1_FLR_3 FAN COILFAN | 0.96 | 1.04 | 1.3 | 1.02 | 0.95 | 1.22 | 1.15 | 1.25 | 1.48 | 1.26 | 1.26 | 1.44 | 1.28 | 1.4 | 1.42 | 1.44
| ROOM_2_FLR_3 FAN COILFAN | 1.04 | 1.09 | 1.33 | 1.03 | 0.87 | 1.21 | 0.97 | 1.22 | 1.47 | 1.08 | 1.21 | 1.39 | 1.21 | 1.3 | 1.33 | 1.25
| ROOM_3_MULT19_FLR_3 FAN COILFAN | 7.9 | 8.24 | 10.28 | 8.68 | 8.75 | 10.05 | 10.29 | 9.68 | 10.83 | 11.04 | 10.03 | 11.36 | 10.47 | 11.67 | 11.2 | 12.8
| ROOM_4_MULT19_FLR_3 FAN COILFAN | 9.15 | 9.32 | 10.78 | 8.74 | 7.7 | 9.69 | 6.96 | 8.48 | 10.25 | 7.57 | 8.46 | 9.81 | 8.6 | 9.46 | 8.7 | 9.01
| ROOM_5_FLR_3 FAN COILFAN | 0.79 | 0.86 | 1.12 | 0.89 | 0.81 | 1.04 | 0.89 | 1.06 | 1.2 | 1.04 | 1.06 | 1.17 | 1.09 | 1.17 | 1.18 | 1.27
| ROOM_6_FLR_3 FAN COILFAN | 0.83 | 0.86 | 1.09 | 0.84 | 0.72 | 0.97 | 0.73 | 0.97 | 1.14 | 0.86 | 0.96 | 1.06 | 0.97 | 1.02 | 1.05 | 1.07
| ROOM_1_FLR_6 FAN COILFAN | 0.31 | 0.33 | 0.41 | 0.33 | 0.3 | 0.39 | 0.35 | 0.39 | 0.47 | 0.39 | 0.39 | 0.45 | 0.39 | 0.43 | 0.44 | 0.42
| ROOM_2_FLR_6 FAN COILFAN | 0.33 | 0.35 | 0.43 | 0.34 | 0.28 | 0.4 | 0.3 | 0.39 | 0.47 | 0.34 | 0.38 | 0.44 | 0.38 | 0.41 | 0.42 | 0.38
| ROOM_3_MULT9_FLR_6 FAN COILFAN | 1.23 | 1.49 | 2 | 1.57 | 1.55 | 1.91 | 1.85 | 1.81 | 1.97 | 2.06 | 1.86 | 2.06 | 1.95 | 2.17 | 2.08 | 2.41
| DINING_FLR_6 EXHAUST FAN | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
| KITCHEN_FLR_6 EXHAUST FAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VAV WITH REHEAT_FAN | 34.16 | 35.15 | 37.94 | 35.84 | 33.7 | 37.88 | 32.91 | 35.47 | 41.71 | 34.81 | 35.83 | 41.45 | 36.18 | 39.77 | 36.51 | 35.82
| FLR_3_DOAS_FAN | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
| FLR_6_DOAS_FAN | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.07672 | 0.10717 | 0.075917 | 0.096673 | 0.12363 | 0.094119 | 0.14737 | 0.072329 | 0.037019 | 0.073245 | 0.093574 | 0.037031 | 0.058262 | 0.074143 | 0.058238 | 0.093617
| Total Cost ($/m2) | 21.54 | 25.96 | 17.71 | 19.22 | 21.86 | 20.68 | 21.48 | 13.43 | 6.9 | 10.85 | 15.96 | 6.11 | 9.76 | 11.56 | 8.68 | 13.46
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011453 | 0.0081763 | 0.0085448 | 0.010643 | 0.008404 | 0.0080835 | 0.0084229 | 0.010013 | 0.0071657 | 0.0083058 | 0.0087953 | 0.007157 | 0.0079607 | 0.0086253 | 0.007955 | 0.0041732
| Total Cost ($/m2) | 5.74 | 5.39 | 4.93 | 8.48 | 5.61 | 5.36 | 6.76 | 9.75 | 6.18 | 7.95 | 10.09 | 7.31 | 10.6 | 10.62 | 12.18 | 8.54
Total Utility Costs
| Cost Intensity ($/m2) | 27.28 | 31.35 | 22.64 | 27.7 | 27.47 | 26.04 | 28.24 | 23.18 | 13.08 | 18.81 | 26.06 | 13.42 | 20.36 | 22.18 | 20.87 | 21.99
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1765741.6667 | 1332322.2222 | 1198561.1111 | 845211.1111 | 610858.3333 | 1050625 | 258563.8889 | 690686.1111 | 659527.7778 | 271088.8889 | 519927.7778 | 424150 | 479200 | 328394.4444 | 265300 | 191430.5556
| Interior Lighting | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111 | 403711.1111
| Exterior Lighting | 15691.6667 | 15686.1111 | 15683.3333 | 15680.5556 | 15669.4444 | 15663.8889 | 15672.2222 | 15663.8889 | 15669.4444 | 15638.8889 | 15666.6667 | 15658.3333 | 15655.5556 | 15652.7778 | 15644.4444 | 15547.2222
| Interior Equipment | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333 | 739008.3333
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 208244.4444 | 210152.7778 | 246497.2222 | 209600 | 198063.8889 | 238847.2222 | 202175 | 216791.6667 | 255075 | 216886.1111 | 218522.2222 | 251183.3333 | 222852.7778 | 244875 | 230344.4444 | 240788.8889
| Pumps | 31322.2222 | 26005.5556 | 22163.8889 | 21050 | 17755.5556 | 24727.7778 | 13572.2222 | 19383.3333 | 20888.8889 | 14069.4444 | 17880.5556 | 16450 | 18852.7778 | 16822.2222 | 17038.8889 | 19813.8889
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21088.8889 | 20975 | 20836.1111 | 20913.8889 | 20975 | 20761.1111 | 20875 | 20825 | 20772.2222 | 20830.5556 | 20777.7778 | 20730.5556 | 20727.7778 | 20677.7778 | 20658.3333 | 20547.2222
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3184805.5556 | 2747858.3333 | 2646458.3333 | 2255175 | 2006038.8889 | 2493344.4444 | 1653577.7778 | 2106066.6667 | 2114652.7778 | 1681230.5556 | 1935488.8889 | 1870888.8889 | 1900005.5556 | 1769138.8889 | 1691700 | 1630844.4444
Gas (MJ)
| Heating | 29600 | 823350 | 466400 | 1417190 | 141310 | 742230 | 839670 | 2672640 | 1548010 | 2088650 | 3976800 | 2575770 | 5493900 | 4249790 | 6810540 | 11490850
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850 | 1788850
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3870430 | 4870730 | 4296160 | 5834140 | 5646860 | 4988580 | 6471290 | 6591400 | 6447820 | 6985330 | 7256070 | 7221360 | 7830350 | 7934640 | 8777610 | 9924300
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5688870 | 7482940 | 6551410 | 9040190 | 7577020 | 7519670 | 9099810 | 11052900 | 9784680 | 10862830 | 13021710 | 11585980 | 15113110 | 13973290 | 17377000 | 23204010
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 17154170 | 17375230 | 16078660 | 17158810 | 14798760 | 16495710 | 15052690 | 18634740 | 17397430 | 16915270 | 19989480 | 18321180 | 21953130 | 20342190 | 23467130 | 29075050
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 560.2915 | 422.7622 | 380.3182 | 268.1959 | 193.8329 | 333.3762 | 82.0455 | 219.1632 | 209.2763 | 86.0198 | 164.9795 | 134.588 | 152.0561 | 104.2036 | 84.183 | 60.7433
| Interior Lighting (elec) | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025 | 128.1025
| Exterior Lighting (elec) | 4.9792 | 4.9774 | 4.9765 | 4.9756 | 4.9721 | 4.9703 | 4.973 | 4.9703 | 4.9721 | 4.9624 | 4.9712 | 4.9686 | 4.9677 | 4.9668 | 4.9642 | 4.9333
| Interior Equipment (elec) | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964 | 234.4964
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 66.0785 | 66.6841 | 78.2166 | 66.5087 | 62.8481 | 75.7892 | 64.1526 | 68.7907 | 80.9384 | 68.8206 | 69.3398 | 79.7036 | 70.7139 | 77.7018 | 73.0911 | 76.4053
| Pumps (elec) | 9.9389 | 8.2519 | 7.0329 | 6.6794 | 5.6341 | 7.8464 | 4.3066 | 6.1506 | 6.6283 | 4.4644 | 5.6737 | 5.2198 | 5.9822 | 5.3379 | 5.4066 | 6.2872
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 6.6918 | 6.6556 | 6.6116 | 6.6362 | 6.6556 | 6.5878 | 6.6239 | 6.608 | 6.5913 | 6.6098 | 6.593 | 6.5781 | 6.5772 | 6.5613 | 6.5551 | 6.5199
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1010.578 | 871.9292 | 839.7538 | 715.5948 | 636.5408 | 791.1688 | 524.7006 | 668.2808 | 671.0053 | 533.4751 | 614.1544 | 593.656 | 602.8951 | 561.3695 | 536.7972 | 517.487
Gas (MJ/m2)
| Heating (gas) | 2.609 | 72.572 | 41.1096 | 124.9144 | 12.4554 | 65.4219 | 74.0104 | 235.5726 | 136.4452 | 184.0984 | 350.5243 | 227.0343 | 484.245 | 374.5863 | 600.2967 | 1012.83
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734 | 157.6734
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 341.1486 | 429.3174 | 378.6734 | 514.2345 | 497.7273 | 439.7049 | 570.3944 | 580.9812 | 568.3257 | 615.7031 | 639.5667 | 636.5073 | 690.1851 | 699.3775 | 773.6788 | 874.7507
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 501.4301 | 659.5636 | 577.4564 | 796.8232 | 667.856 | 662.801 | 802.0782 | 974.2281 | 862.4442 | 957.4749 | 1147.7635 | 1021.215 | 1332.1043 | 1231.638 | 1531.6488 | 2045.2549
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1512.0081 | 1531.4928 | 1417.2101 | 1512.417 | 1304.3968 | 1453.9699 | 1326.7788 | 1642.5089 | 1533.4496 | 1490.9509 | 1761.9188 | 1614.871 | 1934.9995 | 1793.0075 | 2068.4469 | 2562.7419
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 519.0175 | 487.3995 | 403.9378 | 420.9667 | 395.2893 | 312.0339 | 311.8454 | 316.8245 | 315.6211 | 288.8347 | 292.8045 | 316.8209 | 288.1346 | 291.5568 | 289.4075 | 292.101
| Feb | 519.9258 | 450.4859 | 422.2271 | 366.9956 | 380.0043 | 355.4875 | 360.8884 | 297.1606 | 331.6969 | 324.0939 | 291.2406 | 312.0286 | 287.7745 | 309.6656 | 292.0649 | 291.4824
| Mar | 551.8914 | 507.7522 | 515.6468 | 436.2384 | 378.2588 | 414.0618 | 321.7035 | 434.086 | 391.4927 | 381.5985 | 378.7882 | 391.7964 | 333.1774 | 388.9466 | 299.6152 | 303.1842
| Apr | 578.4744 | 565.5297 | 532.3968 | 468.1148 | 421.3407 | 539.2042 | 369.8749 | 438.8049 | 463.2003 | 369.3724 | 370.8068 | 416.0445 | 428.1991 | 383.4383 | 333.2547 | 335.1831
| May | 617.7582 | 663.1754 | 618.8133 | 569.4503 | 427.8852 | 607.3997 | 383.8294 | 500.5624 | 516.1669 | 419.7421 | 499.4736 | 455.6354 | 600.5106 | 439.7903 | 423.5419 | 414.2054
| Jun | 702.1521 | 658.2197 | 705.4893 | 619.9584 | 423.406 | 763.9392 | 394.3694 | 688.8669 | 561.4669 | 443.8825 | 539.7627 | 481.0186 | 627.6515 | 575.6874 | 519.8434 | 475.4887
| Jul | 654.3808 | 705.9934 | 700.4312 | 690.0641 | 428.6643 | 762.0664 | 469.9101 | 705.6556 | 664.4578 | 477.3333 | 629.2909 | 578.6054 | 656.9693 | 614.3535 | 583.5524 | 480.7908
| Aug | 676.1627 | 737.631 | 699.9788 | 614.5807 | 472.2845 | 756.6045 | 386.9204 | 698.8535 | 591.5158 | 453.926 | 662.5028 | 506.0183 | 625.9024 | 519.8659 | 548.9836 | 446.5124
| Sep | 632.8102 | 648.0888 | 643.505 | 539.0018 | 440.9238 | 691.5816 | 456.0402 | 512.87 | 518.1264 | 544.9681 | 521.2808 | 467.9703 | 473.9098 | 488.4994 | 471.242 | 356.5807
| Oct | 625.5814 | 572.8825 | 530.0736 | 476.4677 | 426.4112 | 515.4194 | 396.774 | 489.3571 | 464.7437 | 386.3112 | 451.1742 | 405.1442 | 424.1321 | 408.258 | 394.8991 | 305.635
| Nov | 565.1723 | 530.6568 | 425.5982 | 411.723 | 399.76 | 380.6151 | 342.2141 | 443.8561 | 368.6261 | 322.2702 | 425.5584 | 317.9992 | 312.4481 | 312.406 | 301.5826 | 291.347
| Dec | 517.9138 | 506.7072 | 391.355 | 405.8896 | 396.2758 | 354.4248 | 300.3964 | 290.5143 | 309.5043 | 286.9617 | 292.7618 | 304.0929 | 287.5457 | 292.4242 | 289.3519 | 291.1714
Time of Peak Electrical Demand
| Jan | 06-JAN-20:00 | 06-JAN-20:10 | 27-JAN-20:10 | 24-JAN-20:00 | 26-JAN-20:10 | 18-JAN-20:19 | 15-JAN-20:10 | 08-JAN-20:00 | 26-JAN-20:10 | 02-JAN-20:10 | 17-JAN-20:30 | 24-JAN-20:10 | 25-JAN-20:10 | 30-JAN-20:00 | 25-JAN-20:40 | 12-JAN-20:10
| Feb | 23-FEB-20:10 | 20-FEB-20:10 | 27-FEB-20:10 | 20-FEB-20:00 | 12-FEB-20:10 | 27-FEB-20:10 | 15-FEB-20:10 | 15-FEB-20:10 | 14-FEB-18:19 | 21-FEB-20:10 | 27-FEB-20:00 | 10-FEB-20:00 | 07-FEB-20:00 | 03-FEB-20:10 | 28-FEB-20:10 | 09-FEB-20:00
| Mar | 13-MAR-19:10 | 25-MAR-17:19 | 17-MAR-19:10 | 28-MAR-19:10 | 29-MAR-19:00 | 30-MAR-19:10 | 26-MAR-19:10 | 09-MAR-20:00 | 25-MAR-17:19 | 29-MAR-19:10 | 31-MAR-19:10 | 26-MAR-19:10 | 19-MAR-19:00 | 30-MAR-17:19 | 22-MAR-19:10 | 29-MAR-19:30
| Apr | 03-APR-19:10 | 30-APR-19:10 | 01-APR-17:10 | 14-APR-19:10 | 11-APR-19:10 | 21-APR-18:10 | 13-APR-19:10 | 05-APR-19:10 | 21-APR-19:10 | 14-APR-19:10 | 28-APR-18:10 | 26-APR-19:10 | 02-APR-19:00 | 06-APR-19:10 | 04-APR-18:10 | 25-APR-19:10
| May | 19-MAY-19:10 | 26-MAY-19:10 | 28-MAY-19:10 | 31-MAY-18:10 | 30-MAY-19:10 | 31-MAY-18:10 | 25-MAY-19:19 | 15-MAY-17:19 | 31-MAY-18:10 | 04-MAY-19:19 | 30-MAY-17:19 | 23-MAY-19:10 | 27-MAY-17:19 | 25-MAY-19:10 | 31-MAY-19:10 | 24-MAY-19:10
| Jun | 27-JUN-18:10 | 13-JUN-18:10 | 27-JUN-19:10 | 08-JUN-19:10 | 28-JUN-19:10 | 27-JUN-19:10 | 16-JUN-19:10 | 30-JUN-17:19 | 28-JUN-19:10 | 27-JUN-19:10 | 19-JUN-19:10 | 27-JUN-19:10 | 29-JUN-18:10 | 26-JUN-18:10 | 14-JUN-19:10 | 15-JUN-19:00
| Jul | 11-JUL-19:10 | 03-JUL-18:10 | 11-JUL-19:10 | 03-JUL-18:10 | 10-JUL-19:10 | 25-JUL-19:10 | 02-JUL-19:10 | 24-JUL-18:10 | 30-JUL-19:10 | 24-JUL-19:10 | 13-JUL-17:19 | 17-JUL-19:30 | 13-JUL-18:10 | 21-JUL-19:19 | 06-JUL-18:10 | 29-JUL-17:19
| Aug | 21-AUG-18:10 | 06-AUG-19:10 | 11-AUG-19:19 | 14-AUG-19:10 | 16-AUG-19:30 | 04-AUG-19:00 | 14-AUG-19:10 | 17-AUG-18:10 | 01-AUG-18:10 | 08-AUG-19:10 | 04-AUG-19:10 | 29-AUG-18:10 | 25-AUG-19:10 | 09-AUG-17:19 | 13-AUG-19:10 | 15-AUG-19:10
| Sep | 01-SEP-19:00 | 16-SEP-17:19 | 08-SEP-19:10 | 05-SEP-19:10 | 25-SEP-19:10 | 01-SEP-18:30 | 28-SEP-19:00 | 09-SEP-17:10 | 02-SEP-17:19 | 02-SEP-17:10 | 06-SEP-19:10 | 01-SEP-18:10 | 22-SEP-19:10 | 01-SEP-17:19 | 08-SEP-19:10 | 02-SEP-18:10
| Oct | 06-OCT-19:10 | 29-OCT-19:10 | 02-OCT-19:10 | 20-OCT-19:10 | 05-OCT-19:00 | 03-OCT-17:19 | 16-OCT-19:10 | 02-OCT-19:00 | 02-OCT-19:10 | 17-OCT-19:10 | 30-OCT-20:00 | 01-OCT-19:10 | 08-OCT-19:10 | 05-OCT-18:10 | 07-OCT-17:10 | 03-OCT-19:10
| Nov | 01-NOV-20:00 | 27-NOV-20:10 | 06-NOV-20:10 | 22-NOV-20:00 | 09-NOV-20:00 | 09-NOV-20:10 | 02-NOV-20:00 | 03-NOV-20:00 | 09-NOV-20:00 | 02-NOV-20:00 | 02-NOV-20:10 | 03-NOV-20:10 | 02-NOV-20:19 | 21-NOV-20:10 | 02-NOV-20:00 | 22-NOV-20:10
| Dec | 15-DEC-20:19 | 02-DEC-20:10 | 13-DEC-20:00 | 04-DEC-20:00 | 18-DEC-20:10 | 05-DEC-19:10 | 06-DEC-20:00 | 06-DEC-20:49 | 08-DEC-20:10 | 28-DEC-20:00 | 11-DEC-20:00 | 21-DEC-20:10 | 20-DEC-20:19 | 01-DEC-20:10 | 18-DEC-20:10 | 07-DEC-20:00
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19
| Total Building | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19 | 44342.19
Emissions
| Carbon Equivalent (kg) | 976017.7618 | 1051520 | 917040.751 | 857695.3453 | 371071.7378 | 976542.8586 | 357341.0498 | 767647.1958 | 1040280 | 318337.3844 | 1266720 | 973181.1721 | 922888.7585 | 898486.1025 | 892411.881 | 877330.4563
| CO2 (kg) | 2318870 | 2689820 | 2220100 | 2047630 | 1020670 | 2383560 | 990036.3873 | 1850360 | 2522590 | 856833.6225 | 3059320 | 2384420 | 2286720 | 2231710 | 2240300 | 2358480
| NOX (kg) | 3835.9379 | 3377.0268 | 3485.315 | 3472.0855 | 894.0298 | 3622.0614 | 871.9463 | 3071.0579 | 3994.3689 | 981.181 | 4951.268 | 3672.4766 | 3450.8574 | 3330.1432 | 3257.9815 | 2537.7165
| SO2 (kg) | 13633.7638 | 13109.2893 | 10643.697 | 7918.0829 | 5839.3659 | 13717.405 | 4814.1524 | 7690.9462 | 9236.8849 | 1302.3686 | 13047.1384 | 8172.9035 | 4488.3665 | 4727.5594 | 3997.3417 | 8307.875
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0627 | 0.0376 | 0.0296 | 0.0299 | 0.0034 | 0.0265 | 0.0032 | 0.0322 | 0.037 | 0.0062 | 0.0407 | 0.0331 | 0.0344 | 0.0343 | 0.031 | 0.0306
| Water for Electricity (m3) | 1687.18 | 4471.09 | 78611.5 | 14080.4 | 35221.6 | 68402.4 | 29033.1 | 478.1562 | 9602.21 | 17176.8 | 3002.8 | 8495.33 | 2947.74 | 112065 | 2624.57 | 1666.2

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17154.17 | 1512.01 | 1512.01
Net Site Energy | 17154.17 | 1512.01 | 1512.01
Total Source Energy | 44242.64 | 3899.65 | 3899.65
Net Source Energy | 44242.64 | 3899.65 | 3899.65
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 29.6 | 0 | 0 | 0 | 0
Cooling | 6356.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 749.68 | 0 | 0 | 0 | 0 | 0
Pumps | 112.76 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 3870.43 | 0 | 0 | 0 | 44342.19
Refrigeration | 75.92 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11465.3 | 5688.87 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 6.49 | 0.25 | 0.25 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 6.49 | 0.25 | 0.25 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 6.49 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 6.49 | 0.25 | 0.25 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 6.49 | 0.61 | 0.61 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 6.49 | 0.25 | 0.25 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 6.49 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 6.49 | 0.378 | 0.378
North Total or Average |  |  | 432.93 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 781.15 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1743533.89 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 880054.01 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14658.76 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15647.7 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 139436.19 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 158231.91 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12666.36 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13074.96 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4580.55 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4902.09 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 22293.01 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 938554.84 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 414454.3 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5033.22 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.96 | 609.02 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.04 | 659.28 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 7.9 | 5025.69 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 9.15 | 5824.91 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.79 | 504.91 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.83 | 525.16 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.31 | 195.34 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.33 | 211.92 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.23 | 784.29 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 34.16 | 77212.84 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4890.01 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15977.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 165971.2707 | 268.0715 | 924.8016 | 0 | 0.0043 | 114438.5138 | 69208.1417
February | 151364.4888 | 245.4171 | 850.795 | 0 | 0.0039 | 105281.4966 | 63211.2736
March | 171816.1065 | 279.9827 | 976.817 | 0 | 0.0045 | 120877.3193 | 71892.9557
April | 181207.7767 | 298.664 | 1056.7907 | 0 | 0.0049 | 130776.7284 | 76161.09
May | 209618.2534 | 349.3219 | 1252.6406 | 0 | 0.0058 | 155016.2428 | 88485.9162
June | 213368.6853 | 357.5336 | 1290.4928 | 0 | 0.0059 | 159702.1668 | 90265.6501
July | 233792.4419 | 393.3723 | 1426.7337 | 0 | 0.0065 | 176563.7029 | 99067.7857
August | 231032.692 | 388.2089 | 1405.7996 | 0 | 0.0065 | 173972.5929 | 97846.2602
September | 216462.9554 | 362.3239 | 1306.1013 | 0 | 0.006 | 161633.431 | 91535.1363
October | 204955.2742 | 340.1466 | 1213.7203 | 0 | 0.0056 | 150198.6174 | 86376.7968
November | 176160.7767 | 288.808 | 1015.2547 | 0 | 0.0047 | 125635.3781 | 73885.7802
December | 163118.1856 | 264.0874 | 913.8164 | 0 | 0.0042 | 113079.7213 | 68080.9754
Annual Sum or Average | 2318870 | 3835.9379 | 13633.7638 | 0 | 0.0627 | 1687180 | 976017.7618
Minimum of Months | 151364.4888 | 245.4171 | 850.795 | 0 | 0.0039 | 105281.4966 | 63211.2736
Maximum of Months | 233792.4419 | 393.3723 | 1426.7337 | 0 | 0.0065 | 176563.7029 | 99067.7857
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 777673000000 | 519017.546 | 06-JAN-20:00 | 115409.096 | 136430.368 | 27641.377 | 0 | 228996.938 | 3589.95 | 4553.845 | 0 | 0 | 0 | 0 | 0 | 2395.972 | 0 | 0
February | 715446000000 | 519925.809 | 23-FEB-20:10 | 115409.096 | 136430.368 | 28746.27 | 0 | 228304.337 | 3589.95 | 4523.206 | 0 | 0 | 0 | 0 | 0 | 2922.582 | 0 | 0
March | 821429000000 | 551891.4 | 13-MAR-19:10 | 115409.096 | 136430.368 | 29011.313 | 0 | 259624.677 | 3589.95 | 4902.42 | 0 | 0 | 0 | 0 | 0 | 2923.577 | 0 | 0
April | 888701000000 | 578474.4 | 03-APR-19:10 | 115409.096 | 136430.368 | 30982.002 | 0 | 283873.766 | 3589.95 | 5264.067 | 0 | 0 | 0 | 0 | 0 | 2925.152 | 0 | 0
May | 1053420000000 | 617758.232 | 19-MAY-19:10 | 115409.096 | 136430.368 | 30971.332 | 0 | 323042.453 | 3589.95 | 5913.925 | 0 | 0 | 0 | 0 | 0 | 2401.108 | 0 | 0
June | 1085260000000 | 702152.127 | 27-JUN-18:10 | 102647.053 | 127075.755 | 31473.221 | 0 | 431599.605 | 0 | 6990.762 | 0 | 0 | 0 | 0 | 0 | 2365.731 | 0 | 0
July | 1199850000000 | 654380.79 | 11-JUL-19:10 | 115409.096 | 136430.368 | 30148.171 | 0 | 363779.85 | 0 | 6212.433 | 0 | 0 | 0 | 0 | 0 | 2400.872 | 0 | 0
August | 1182240000000 | 676162.691 | 21-AUG-18:10 | 102647.053 | 127075.755 | 31386.88 | 0 | 405535.974 | 0 | 6592.433 | 0 | 0 | 0 | 0 | 0 | 2924.597 | 0 | 0
September | 1098390000000 | 632810.23 | 01-SEP-19:00 | 115409.096 | 136430.368 | 31030.171 | 0 | 337869.543 | 3589.95 | 6081.242 | 0 | 0 | 0 | 0 | 0 | 2399.859 | 0 | 0
October | 1020680000000 | 625581.43 | 06-OCT-19:10 | 115409.096 | 136430.368 | 31136.645 | 0 | 330627.206 | 3589.95 | 5989.127 | 0 | 0 | 0 | 0 | 0 | 2399.037 | 0 | 0
November | 853762000000 | 565172.306 | 01-NOV-20:00 | 115409.096 | 136430.368 | 29224.896 | 0 | 272573.72 | 3589.95 | 5020.951 | 0 | 0 | 0 | 0 | 0 | 2923.325 | 0 | 0
December | 768440000000 | 517913.759 | 15-DEC-20:19 | 115409.096 | 136430.368 | 27944.657 | 0 | 227597.251 | 3589.95 | 4546.918 | 0 | 0 | 0 | 0 | 0 | 2395.52 | 0 | 0
Annual Sum or Average | 11465300000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 715446000000 | 517913.759 |  | 102647.053 | 127075.755 | 27641.377 | 0 | 227597.251 | 0 | 4523.206 | 0 | 0 | 0 | 0 | 0 | 2365.731 | 0 | 0
Maximum of Months | 1199850000000 | 702152.127 |  | 115409.096 | 136430.368 | 31473.221 | 0 | 431599.605 | 3589.95 | 6990.762 | 0 | 0 | 0 | 0 | 0 | 2925.152 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 244338.39 | 65156.09 | 0 | 309494.47
Cost per Total Building Area ($/m2) | 21.54 | 5.74 | 0 | 27.28
Cost per Net Conditioned Building Area ($/m2) | 21.54 | 5.74 | 0 | 27.28

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17375.23 | 1531.49 | 1531.49
Net Site Energy | 17375.23 | 1531.49 | 1531.49
Total Source Energy | 8171.37 | 720.24 | 720.24
Net Source Energy | 8171.37 | 720.24 | 720.24
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 823.35 | 0 | 0 | 0 | 0
Cooling | 4796.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 756.55 | 0 | 0 | 0 | 0 | 0
Pumps | 93.62 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4870.73 | 0 | 0 | 0 | 44342.19
Refrigeration | 75.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9892.29 | 7482.94 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 6.49 | 0.25 | 0.25 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 6.49 | 0.25 | 0.25 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 6.49 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 6.49 | 0.25 | 0.25 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 6.49 | 0.61 | 0.61 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 6.49 | 0.25 | 0.25 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 6.49 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 6.49 | 0.378 | 0.378
North Total or Average |  |  | 432.93 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 781.15 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1740833.89 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1150743.28 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15361.73 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15979.3 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 146456.27 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 155392.52 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13214.17 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13166.31 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4827.62 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5043.04 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 24867.27 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 917811.99 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 423394.78 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5318.9 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.04 | 659.45 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.09 | 691.45 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.24 | 5241 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 9.32 | 5933.39 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.86 | 548.76 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.86 | 546.41 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.33 | 212.78 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.35 | 224.13 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.49 | 945.8 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 35.15 | 79441.14 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6394.09 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15952.33 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 183737.1016 | 221.9557 | 773.297 | 0 | 0.0023 | 263698.6022 | 70702.8837
February | 153490.5173 | 184.3751 | 631.3976 | 0 | 0.0019 | 215304.019 | 58929.4872
March | 185797.1984 | 229.3821 | 851.1237 | 0 | 0.0025 | 290266.7992 | 72132.0933
April | 208831.7984 | 262.294 | 1019.3011 | 0 | 0.0029 | 347645.9774 | 81651.4862
May | 249573.0338 | 316.7347 | 1263.9491 | 0 | 0.0036 | 431102.8245 | 98002.4049
June | 271627.1337 | 347.0533 | 1408.2678 | 0 | 0.004 | 480337.8066 | 106962.8941
July | 305031.3998 | 391.1652 | 1601.5082 | 0 | 0.0045 | 546255.8423 | 120301.5826
August | 294817.4096 | 377.6405 | 1541.9073 | 0 | 0.0044 | 525924.6702 | 116218.2945
September | 254967.99 | 324.9568 | 1310.5331 | 0 | 0.0037 | 446998.2087 | 100298.1702
October | 222944.9287 | 281.3368 | 1106.6268 | 0 | 0.0032 | 377436.1755 | 87339.3127
November | 186631.3322 | 231.9621 | 876.6565 | 0 | 0.0025 | 298982.8206 | 72655.7513
December | 172368.6919 | 208.1705 | 724.7212 | 0 | 0.0021 | 247133.6913 | 66321.5546
Annual Sum or Average | 2689820 | 3377.0268 | 13109.2893 | 0 | 0.0376 | 4471090 | 1051520
Minimum of Months | 153490.5173 | 184.3751 | 631.3976 | 0 | 0.0019 | 215304.019 | 58929.4872
Maximum of Months | 305031.3998 | 391.1652 | 1601.5082 | 0 | 0.0045 | 546255.8423 | 120301.5826
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 583434000000 | 487399.473 | 06-JAN-20:10 | 115409.096 | 136430.368 | 26209.68 | 0 | 199549.466 | 3589.95 | 3817.547 | 0 | 0 | 0 | 0 | 0 | 2393.366 | 0 | 0
February | 476361000000 | 450485.927 | 20-FEB-20:10 | 108704.859 | 134943.936 | 25725.72 | 0 | 171334.32 | 3589.95 | 3306.963 | 0 | 0 | 0 | 0 | 0 | 2880.18 | 0 | 0
March | 642216000000 | 507752.167 | 25-MAR-17:19 | 87035.741 | 134092.705 | 26983.643 | 0 | 253094.13 | 0 | 4257.43 | 0 | 0 | 0 | 0 | 0 | 2288.518 | 0 | 0
April | 769167000000 | 565529.695 | 30-APR-19:10 | 108704.859 | 134943.936 | 28506.915 | 0 | 281711.519 | 3589.95 | 5185.069 | 0 | 0 | 0 | 0 | 0 | 2887.448 | 0 | 0
May | 953816000000 | 663175.364 | 26-MAY-19:10 | 115409.096 | 136430.368 | 31376.772 | 0 | 367987.943 | 3589.95 | 5978.74 | 0 | 0 | 0 | 0 | 0 | 2402.495 | 0 | 0
June | 1062750000000 | 658219.699 | 13-JUN-18:10 | 102647.053 | 127075.755 | 32072.178 | 0 | 388220.529 | 0 | 5839.877 | 0 | 0 | 0 | 0 | 0 | 2364.307 | 0 | 0
July | 1208590000000 | 705993.402 | 03-JUL-18:10 | 102647.053 | 127075.755 | 31497.731 | 0 | 435526.963 | 0 | 6319.836 | 0 | 0 | 0 | 0 | 0 | 2926.065 | 0 | 0
August | 1163610000000 | 737631.026 | 06-AUG-19:10 | 108704.859 | 134943.936 | 31374.938 | 0 | 449125.02 | 3589.95 | 7002.286 | 0 | 0 | 0 | 0 | 0 | 2890.038 | 0 | 0
September | 988984000000 | 648088.779 | 16-SEP-17:19 | 87035.741 | 134092.705 | 29461.089 | 0 | 388867.671 | 0 | 6341.1 | 0 | 0 | 0 | 0 | 0 | 2290.474 | 0 | 0
October | 835078000000 | 572882.472 | 29-OCT-19:10 | 108704.859 | 134943.936 | 27429.487 | 0 | 290075.313 | 3589.95 | 5253.833 | 0 | 0 | 0 | 0 | 0 | 2885.094 | 0 | 0
November | 661500000000 | 530656.751 | 27-NOV-20:10 | 115409.096 | 136430.368 | 27029.817 | 0 | 240714.735 | 3589.95 | 4561.898 | 0 | 0 | 0 | 0 | 0 | 2920.887 | 0 | 0
December | 546784000000 | 506707.221 | 02-DEC-20:10 | 102000.622 | 131971.07 | 25764.109 | 0 | 236220.907 | 3589.95 | 4313.558 | 0 | 0 | 0 | 0 | 0 | 2847.004 | 0 | 0
Annual Sum or Average | 9892290000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 476361000000 | 450485.927 |  | 87035.741 | 127075.755 | 25725.72 | 0 | 171334.32 | 0 | 3306.963 | 0 | 0 | 0 | 0 | 0 | 2288.518 | 0 | 0
Maximum of Months | 1208590000000 | 737631.026 |  | 115409.096 | 136430.368 | 32072.178 | 0 | 449125.02 | 3589.95 | 7002.286 | 0 | 0 | 0 | 0 | 0 | 2926.065 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 294482.41 | 61183.06 | 0 | 355665.47
Cost per Total Building Area ($/m2) | 25.96 | 5.39 | 0 | 31.35
Cost per Net Conditioned Building Area ($/m2) | 25.96 | 5.39 | 0 | 31.35

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16078.66 | 1417.21 | 1417.21
Net Site Energy | 16078.66 | 1417.21 | 1417.21
Total Source Energy | 37288.84 | 3286.73 | 3286.73
Net Source Energy | 37288.84 | 3286.73 | 3286.73
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 466.4 | 0 | 0 | 0 | 0
Cooling | 4314.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.46 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 887.39 | 0 | 0 | 0 | 0 | 0
Pumps | 79.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4296.16 | 0 | 0 | 0 | 44342.19
Refrigeration | 75.01 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9527.25 | 6551.41 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 6.49 | 0.25 | 0.25 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 6.49 | 0.25 | 0.25 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 6.49 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 6.49 | 0.25 | 0.25 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 6.49 | 0.61 | 0.61 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.25 | 0.25 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.25 | 0.25 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.25 | 0.25 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.25 | 0.25 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 6.49 | 0.25 | 0.25 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 6.49 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.25 | 0.25 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 6.49 | 0.378 | 0.378
North Total or Average |  |  | 432.93 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 781.15 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1576288.26 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1041053.36 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 16760.9 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17075.4 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 147846.03 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 148021.12 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14611.75 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14210.67 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5233.94 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5353.47 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 26824.45 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 743659.83 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 430869.93 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5820.76 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.3 | 827.07 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.33 | 844.43 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.28 | 6538.89 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.78 | 6860.61 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.12 | 711.74 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.09 | 691.16 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.41 | 263.6 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.43 | 270.84 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 2 | 1275.23 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 37.94 | 85747.14 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5784.6 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14444.5 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 141386.9875 | 206.9446 | 569.2065 | 0 | 0.0016 | 4203140 | 56883.0515
February | 130297.8486 | 191.6448 | 531.2988 | 0 | 0.0015 | 3923290 | 52515.8088
March | 163130.5748 | 249.9129 | 737.3506 | 0 | 0.0021 | 5445520 | 66757.7462
April | 171334.503 | 268.2173 | 815.9283 | 0 | 0.0023 | 6026180 | 70695.0859
May | 197173.2553 | 314.4587 | 980.876 | 0 | 0.0027 | 7244770 | 81942.2116
June | 226311.8065 | 366.6842 | 1167.4587 | 0 | 0.0032 | 8623190 | 94633.6456
July | 253163.7269 | 412.7209 | 1324.2775 | 0 | 0.0036 | 9781630 | 106117.742
August | 246109.4458 | 400.3208 | 1280.8673 | 0 | 0.0035 | 9460940 | 103069.8244
September | 218121.7219 | 351.6792 | 1112.6589 | 0 | 0.0031 | 8218330 | 91033.4778
October | 181436.0278 | 286.1712 | 879.5173 | 0 | 0.0024 | 6495950 | 75079.5597
November | 149849.3415 | 229.6626 | 678.0165 | 0 | 0.0019 | 5007330 | 61332.4251
December | 141787.4524 | 206.8979 | 566.2406 | 0 | 0.0016 | 4181200 | 56980.1724
Annual Sum or Average | 2220100 | 3485.315 | 10643.697 | 0 | 0.0296 | 78611500 | 917040.751
Minimum of Months | 130297.8486 | 191.6448 | 531.2988 | 0 | 0.0015 | 3923290 | 52515.8088
Maximum of Months | 253163.7269 | 412.7209 | 1324.2775 | 0 | 0.0036 | 9781630 | 106117.742
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 509397000000 | 403937.753 | 27-JAN-20:10 | 115409.096 | 136430.368 | 29967.335 | 0 | 114088.597 | 3589.95 | 2111.599 | 0 | 0 | 0 | 0 | 0 | 2340.808 | 0 | 0
February | 475480000000 | 422227.085 | 27-FEB-20:10 | 115409.096 | 136430.368 | 30266.227 | 0 | 131417.18 | 3589.95 | 2241.678 | 0 | 0 | 0 | 0 | 0 | 2872.586 | 0 | 0
March | 659965000000 | 515646.796 | 17-MAR-19:10 | 115409.096 | 136430.368 | 32871.033 | 0 | 222007.684 | 3589.95 | 2981.306 | 0 | 0 | 0 | 0 | 0 | 2357.359 | 0 | 0
April | 730338000000 | 532396.752 | 01-APR-17:10 | 87035.741 | 134092.705 | 31930.874 | 0 | 273844.264 | 0 | 3239.951 | 0 | 0 | 0 | 0 | 0 | 2253.217 | 0 | 0
May | 878024000000 | 618813.301 | 28-MAY-19:10 | 108704.859 | 134943.936 | 36089.815 | 0 | 332454.794 | 0 | 3767.905 | 0 | 0 | 0 | 0 | 0 | 2851.992 | 0 | 0
June | 1045080000000 | 705489.294 | 27-JUN-19:10 | 115409.096 | 136430.368 | 40746.11 | 0 | 402946.505 | 0 | 7571.956 | 0 | 0 | 0 | 0 | 0 | 2385.259 | 0 | 0
July | 1185480000000 | 700431.244 | 11-JUL-19:10 | 115409.096 | 136430.368 | 39718.972 | 0 | 400715.116 | 0 | 5751.64 | 0 | 0 | 0 | 0 | 0 | 2406.053 | 0 | 0
August | 1146610000000 | 699978.818 | 11-AUG-19:19 | 115409.096 | 136430.368 | 37296.228 | 0 | 399327.578 | 3589.95 | 5520.997 | 0 | 0 | 0 | 0 | 0 | 2404.602 | 0 | 0
September | 996014000000 | 643505.043 | 08-SEP-19:10 | 115409.096 | 136430.368 | 37258.476 | 0 | 343419.158 | 3589.95 | 4994.729 | 0 | 0 | 0 | 0 | 0 | 2403.267 | 0 | 0
October | 787272000000 | 530073.596 | 02-OCT-19:10 | 115409.096 | 136430.368 | 34135.187 | 0 | 233574.398 | 3589.95 | 4025.581 | 0 | 0 | 0 | 0 | 0 | 2909.016 | 0 | 0
November | 606859000000 | 425598.233 | 06-NOV-20:10 | 115409.096 | 136430.368 | 30357.6 | 0 | 134602.304 | 3589.95 | 2321.554 | 0 | 0 | 0 | 0 | 0 | 2887.361 | 0 | 0
December | 506737000000 | 391354.99 | 13-DEC-20:00 | 115409.096 | 136430.368 | 29726.054 | 0 | 100376.88 | 3589.95 | 2923.47 | 0 | 0 | 0 | 0 | 0 | 2899.173 | 0 | 0
Annual Sum or Average | 9527250000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 475480000000 | 391354.99 |  | 87035.741 | 134092.705 | 29726.054 | 0 | 100376.88 | 0 | 2111.599 | 0 | 0 | 0 | 0 | 0 | 2253.217 | 0 | 0
Maximum of Months | 1185480000000 | 705489.294 |  | 115409.096 | 136430.368 | 40746.11 | 0 | 402946.505 | 3589.95 | 7571.956 | 0 | 0 | 0 | 0 | 0 | 2909.016 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 200910.59 | 55980.77 | 0 | 256891.37
Cost per Total Building Area ($/m2) | 17.71 | 4.93 | 0 | 22.64
Cost per Net Conditioned Building Area ($/m2) | 17.71 | 4.93 | 0 | 22.64

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17158.81 | 1512.42 | 1512.42
Net Site Energy | 17158.81 | 1512.42 | 1512.42
Total Source Energy | 37182.94 | 3277.39 | 3277.39
Net Source Energy | 37182.94 | 3277.39 | 3277.39
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1417.19 | 0 | 0 | 0 | 0
Cooling | 3042.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.45 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 754.56 | 0 | 0 | 0 | 0 | 0
Pumps | 75.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5834.14 | 0 | 0 | 0 | 44342.19
Refrigeration | 75.29 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8118.63 | 9040.19 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.262 | 0.318 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.262 | 0.318 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.262 | 0.318 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.262 | 0.318 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.402 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.262 | 0.318 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.262 | 0.318 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.262 | 0.318 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.402 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.262 | 0.318 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.262 | 0.318 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.312 | 0.381
North Total or Average |  |  | 432.93 | 3.18 | 0.402 | 0.495
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1641681.9 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1200761.75 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14511.12 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14607.87 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 143794.73 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 139276.5 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12927.97 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12327.48 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4572.95 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4660.18 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 24591.11 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 865789.04 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 399580.82 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5042.12 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.02 | 649.95 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.03 | 656.43 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.68 | 5524.06 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.74 | 5560.37 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.89 | 564.7 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.84 | 533.19 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.33 | 210.14 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.34 | 215.28 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.57 | 997.25 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 35.84 | 80999.02 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6672.01 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15043.74 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 147746.7508 | 222.5844 | 434.3464 | 0 | 0.0017 | 772055.8898 | 59306.2926
February | 135065.4946 | 207.5924 | 417.2263 | 0 | 0.0016 | 741687.4768 | 54595.7828
March | 145645.7698 | 235.8227 | 508.5809 | 0 | 0.0019 | 904259.0837 | 59977.8545
April | 155715.8913 | 262.727 | 595.7031 | 0 | 0.0023 | 1059300 | 65103.6649
May | 182891.5585 | 319.7249 | 754.307 | 0 | 0.0028 | 1341460 | 77495.03
June | 198701.9465 | 354.0673 | 852.3739 | 0 | 0.0032 | 1515940 | 84813.2848
July | 223693.0912 | 403.1217 | 981.7489 | 0 | 0.0036 | 1746080 | 95898.0979
August | 217862.1391 | 392.0007 | 953.1536 | 0 | 0.0035 | 1695220 | 93341.7462
September | 198075.6226 | 353.3929 | 851.8521 | 0 | 0.0032 | 1515020 | 84586.7327
October | 160654.3299 | 275.9551 | 638.5955 | 0 | 0.0024 | 1135630 | 67620.5394
November | 136785.5176 | 221.6647 | 478.5638 | 0 | 0.0018 | 850890.8915 | 56346.5163
December | 144792.7845 | 223.4318 | 451.6315 | 0 | 0.0018 | 802861.258 | 58609.8032
Annual Sum or Average | 2047630 | 3472.0855 | 7918.0829 | 0 | 0.0299 | 14080400 | 857695.3453
Minimum of Months | 135065.4946 | 207.5924 | 417.2263 | 0 | 0.0016 | 741687.4768 | 54595.7828
Maximum of Months | 223693.0912 | 403.1217 | 981.7489 | 0 | 0.0036 | 1746080 | 95898.0979
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 445160000000 | 420966.693 | 24-JAN-20:00 | 115409.096 | 136430.368 | 25721.591 | 0 | 134703.472 | 3589.95 | 2721.94 | 0 | 0 | 0 | 0 | 0 | 2390.275 | 0 | 0
February | 427650000000 | 366995.647 | 20-FEB-20:00 | 108704.859 | 134943.936 | 26036.778 | 0 | 88538.602 | 3589.95 | 2300.577 | 0 | 0 | 0 | 0 | 0 | 2880.945 | 0 | 0
March | 521387000000 | 436238.388 | 28-MAR-19:10 | 115409.096 | 136430.368 | 27819.395 | 0 | 146970.546 | 3589.95 | 3641.687 | 0 | 0 | 0 | 0 | 0 | 2377.346 | 0 | 0
April | 610782000000 | 468114.75 | 14-APR-19:10 | 115409.096 | 136430.368 | 28654.539 | 0 | 178002.798 | 3589.95 | 3629.91 | 0 | 0 | 0 | 0 | 0 | 2398.088 | 0 | 0
May | 773476000000 | 569450.325 | 31-MAY-18:10 | 102647.053 | 127075.755 | 30148.386 | 0 | 301439.284 | 0 | 5216.017 | 0 | 0 | 0 | 0 | 0 | 2923.829 | 0 | 0
June | 874077000000 | 619958.439 | 08-JUN-19:10 | 115409.096 | 136430.368 | 31228.352 | 0 | 328213.138 | 0 | 5749.587 | 0 | 0 | 0 | 0 | 0 | 2927.896 | 0 | 0
July | 1006770000000 | 690064.071 | 03-JUL-18:10 | 102647.053 | 127075.755 | 33798.298 | 0 | 417197.789 | 0 | 6419.283 | 0 | 0 | 0 | 0 | 0 | 2925.892 | 0 | 0
August | 977445000000 | 614580.739 | 14-AUG-19:10 | 115409.096 | 136430.368 | 32247.247 | 0 | 321865.196 | 0 | 5702.08 | 0 | 0 | 0 | 0 | 0 | 2926.751 | 0 | 0
September | 873544000000 | 539001.82 | 05-SEP-19:10 | 115409.096 | 136430.368 | 30652.262 | 0 | 245653.37 | 3589.95 | 4867.226 | 0 | 0 | 0 | 0 | 0 | 2399.548 | 0 | 0
October | 654793000000 | 476467.708 | 20-OCT-19:10 | 115409.096 | 136430.368 | 27464.753 | 0 | 187364.572 | 3589.95 | 3812.528 | 0 | 0 | 0 | 0 | 0 | 2396.441 | 0 | 0
November | 490616000000 | 411723.019 | 22-NOV-20:00 | 115409.096 | 136430.368 | 26695.02 | 0 | 124001.794 | 3589.95 | 2677.363 | 0 | 0 | 0 | 0 | 0 | 2919.429 | 0 | 0
December | 462922000000 | 405889.625 | 04-DEC-20:00 | 115409.096 | 136430.368 | 26054.127 | 0 | 118902.653 | 3589.95 | 2586.108 | 0 | 0 | 0 | 0 | 0 | 2917.323 | 0 | 0
Annual Sum or Average | 8118630000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 427650000000 | 366995.647 |  | 102647.053 | 127075.755 | 25721.591 | 0 | 88538.602 | 0 | 2300.577 | 0 | 0 | 0 | 0 | 0 | 2377.346 | 0 | 0
Maximum of Months | 1006770000000 | 690064.071 |  | 115409.096 | 136430.368 | 33798.298 | 0 | 417197.789 | 3589.95 | 6419.283 | 0 | 0 | 0 | 0 | 0 | 2927.896 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 218014.75 | 96216.47 | 0 | 314231.22
Cost per Total Building Area ($/m2) | 19.22 | 8.48 | 0 | 27.7
Cost per Net Conditioned Building Area ($/m2) | 19.22 | 8.48 | 0 | 27.7

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14798.76 | 1304.4 | 1304.4
Net Site Energy | 14798.76 | 1304.4 | 1304.4
Total Source Energy | 30625.4 | 2699.39 | 2699.39
Net Source Energy | 30625.4 | 2699.39 | 2699.39
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 141.31 | 0 | 0 | 0 | 0
Cooling | 2199.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.41 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 713.03 | 0 | 0 | 0 | 0 | 0
Pumps | 63.92 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 5646.86 | 0 | 0 | 0 | 44342.19
Refrigeration | 75.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7221.74 | 7577.02 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.262 | 0.318 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.262 | 0.318 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.262 | 0.318 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.262 | 0.318 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.402 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.262 | 0.318 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.262 | 0.318 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.262 | 0.318 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.402 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.262 | 0.318 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.262 | 0.318 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.312 | 0.381
North Total or Average |  |  | 432.93 | 3.18 | 0.402 | 0.495
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1186222.27 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 886386.09 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12385.18 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 11386.67 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 119212.45 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 100963.68 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 10756.46 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 9512.32 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 3866.31 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 3601.74 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 20553.76 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 568828.93 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 320847.33 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4307.44 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.95 | 603.56 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.87 | 552.66 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.75 | 5566.97 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 7.7 | 4902.52 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.81 | 518.42 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.72 | 455.03 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.3 | 191.04 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.28 | 177.55 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.55 | 985.42 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 33.7 | 76159.01 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4925.19 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10870.09 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 81026.9082 | 71.2671 | 411.0047 | 0 | 0.0003 | 2478790 | 29297.5086
February | 73024.4567 | 64.2174 | 372.4075 | 0 | 0.0002 | 2246020 | 26410.0881
March | 81617.8324 | 71.686 | 432.0524 | 0 | 0.0003 | 2605840 | 29566.244
April | 79878.731 | 70.0654 | 439.5051 | 0 | 0.0003 | 2650890 | 28987.076
May | 85743.2038 | 75.0735 | 496.0804 | 0 | 0.0003 | 2992260 | 31189.3889
June | 85065.2186 | 74.3916 | 507.9651 | 0 | 0.0003 | 3064030 | 30990.9969
July | 93710.7122 | 81.8105 | 584.9643 | 0 | 0.0003 | 3528620 | 34218.1381
August | 95600.1792 | 83.4285 | 602.3958 | 0 | 0.0003 | 3633800 | 34925.2687
September | 91111.3808 | 79.5574 | 565.8482 | 0 | 0.0003 | 3413290 | 33260.1827
October | 90330.7589 | 78.9912 | 540.3427 | 0 | 0.0003 | 3259340 | 32912.192
November | 81339.6447 | 71.3109 | 453.9646 | 0 | 0.0003 | 2738140 | 29536.8161
December | 82222.2967 | 72.2304 | 432.835 | 0 | 0.0003 | 2610550 | 29777.8377
Annual Sum or Average | 1020670 | 894.0298 | 5839.3659 | 0 | 0.0034 | 35221600 | 371071.7378
Minimum of Months | 73024.4567 | 64.2174 | 372.4075 | 0 | 0.0002 | 2246020 | 26410.0881
Maximum of Months | 95600.1792 | 83.4285 | 602.3958 | 0 | 0.0003 | 3633800 | 34925.2687
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 508245000000 | 395289.282 | 26-JAN-20:10 | 115409.096 | 136430.368 | 26158.398 | 0 | 108645.184 | 3589.95 | 2181.694 | 0 | 0 | 0 | 0 | 0 | 2874.592 | 0 | 0
February | 460519000000 | 380004.264 | 12-FEB-20:10 | 108704.859 | 134943.936 | 25326.901 | 0 | 101549.082 | 3589.95 | 3031.634 | 0 | 0 | 0 | 0 | 0 | 2857.903 | 0 | 0
March | 534295000000 | 378258.823 | 29-MAR-19:00 | 115409.096 | 136430.368 | 26596.561 | 0 | 91375.267 | 3589.95 | 1980.392 | 0 | 0 | 0 | 0 | 0 | 2877.189 | 0 | 0
April | 543532000000 | 421340.742 | 11-APR-19:10 | 115409.096 | 136430.368 | 27277.292 | 0 | 133770.39 | 3589.95 | 2523.338 | 0 | 0 | 0 | 0 | 0 | 2340.307 | 0 | 0
May | 613526000000 | 427885.191 | 30-MAY-19:10 | 115409.096 | 136430.368 | 27277.527 | 0 | 139525.276 | 3589.95 | 3254.649 | 0 | 0 | 0 | 0 | 0 | 2398.325 | 0 | 0
June | 628242000000 | 423405.976 | 28-JUN-19:10 | 115409.096 | 136430.368 | 27464.25 | 0 | 134423.211 | 3589.95 | 3164.76 | 0 | 0 | 0 | 0 | 0 | 2924.341 | 0 | 0
July | 723500000000 | 428664.26 | 10-JUL-19:10 | 115409.096 | 136430.368 | 28355.131 | 0 | 138678.541 | 3589.95 | 3276.524 | 0 | 0 | 0 | 0 | 0 | 2924.65 | 0 | 0
August | 745065000000 | 472284.515 | 16-AUG-19:30 | 115409.096 | 136430.368 | 28973.641 | 0 | 180914.459 | 3589.95 | 4043.806 | 0 | 0 | 0 | 0 | 0 | 2923.195 | 0 | 0
September | 699853000000 | 440923.798 | 25-SEP-19:10 | 115409.096 | 136430.368 | 29613.72 | 0 | 149438.277 | 3589.95 | 3520.44 | 0 | 0 | 0 | 0 | 0 | 2921.947 | 0 | 0
October | 668287000000 | 426411.234 | 05-OCT-19:00 | 115409.096 | 136430.368 | 27814.036 | 0 | 136988.765 | 3589.95 | 3257.257 | 0 | 0 | 0 | 0 | 0 | 2921.762 | 0 | 0
November | 561421000000 | 399759.993 | 09-NOV-20:00 | 115409.096 | 136430.368 | 26386.445 | 0 | 112294.849 | 3589.95 | 2729.936 | 0 | 0 | 0 | 0 | 0 | 2919.349 | 0 | 0
December | 535260000000 | 396275.836 | 18-DEC-20:10 | 115409.096 | 136430.368 | 26092.621 | 0 | 109682.858 | 3589.95 | 2198.753 | 0 | 0 | 0 | 0 | 0 | 2872.19 | 0 | 0
Annual Sum or Average | 7221740000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 460519000000 | 378258.823 |  | 108704.859 | 134943.936 | 25326.901 | 0 | 91375.267 | 3589.95 | 1980.392 | 0 | 0 | 0 | 0 | 0 | 2340.307 | 0 | 0
Maximum of Months | 745065000000 | 472284.515 |  | 115409.096 | 136430.368 | 29613.72 | 0 | 180914.459 | 3589.95 | 4043.806 | 0 | 0 | 0 | 0 | 0 | 2924.65 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 248006.27 | 63677.08 | 0 | 311683.35
Cost per Total Building Area ($/m2) | 21.86 | 5.61 | 0 | 27.47
Cost per Net Conditioned Building Area ($/m2) | 21.86 | 5.61 | 0 | 27.47

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16495.71 | 1453.97 | 1453.97
Net Site Energy | 16495.71 | 1453.97 | 1453.97
Total Source Energy | 40318.77 | 3553.79 | 3553.79
Net Source Energy | 40318.77 | 3553.79 | 3553.79
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 742.23 | 0 | 0 | 0 | 0
Cooling | 3782.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 859.85 | 0 | 0 | 0 | 0 | 0
Pumps | 89.02 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 4988.58 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.74 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8976.04 | 7519.67 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.262 | 0.318 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.262 | 0.318 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.262 | 0.318 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.262 | 0.318 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.402 | 0.495 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.262 | 0.318 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.262 | 0.318 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.262 | 0.318 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.262 | 0.318 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.262 | 0.318 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.402 | 0.495 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.262 | 0.318 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.262 | 0.318 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.312 | 0.381
North Total or Average |  |  | 432.93 | 3.18 | 0.402 | 0.495
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2182146.31 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1074399.36 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 21191.21 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 21069.96 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 199478.15 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 183872.44 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12775.53 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 11969.17 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6581.75 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 6640.23 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 34425.47 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 1078263.69 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 670032.8 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 9488.26 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.22 | 774.34 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.21 | 772.91 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.05 | 6396.74 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 9.69 | 6166.76 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.04 | 662.13 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.97 | 618.18 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.39 | 247.94 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.4 | 251.53 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.91 | 1216.29 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 37.88 | 85624.91 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5969.88 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19996.35 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 155456.8835 | 217.1341 | 715.1429 | 0 | 0.0014 | 3565290 | 61705.5637
February | 141765.7195 | 204.0998 | 709.3904 | 0 | 0.0014 | 3536930 | 56903.981
March | 158396.5984 | 230.0756 | 811.7131 | 0 | 0.0016 | 4047200 | 63790.7594
April | 183721.435 | 278.4719 | 1050.6296 | 0 | 0.002 | 5238980 | 75196.6323
May | 208848.9433 | 322.1468 | 1246.8509 | 0 | 0.0024 | 6217670 | 86062.0931
June | 251653.7341 | 395.7031 | 1573.1816 | 0 | 0.003 | 7845290 | 104483.7173
July | 282732.5805 | 447.558 | 1795.5347 | 0 | 0.0034 | 8954260 | 117697.667
August | 276508.7946 | 437.158 | 1750.8598 | 0 | 0.0033 | 8731450 | 115049.8437
September | 234708.5162 | 367.5055 | 1452.6557 | 0 | 0.0028 | 7244180 | 97286.8665
October | 187180.2542 | 285.9814 | 1091.7159 | 0 | 0.0021 | 5443950 | 76847.9275
November | 149695.4299 | 219.766 | 789.0151 | 0 | 0.0016 | 3934130 | 60528.6329
December | 152889.1553 | 216.4611 | 730.7153 | 0 | 0.0015 | 3643080 | 60989.1741
Annual Sum or Average | 2383560 | 3622.0614 | 13717.405 | 0 | 0.0265 | 68402400 | 976542.8586
Minimum of Months | 141765.7195 | 204.0998 | 709.3904 | 0 | 0.0014 | 3536930 | 56903.981
Maximum of Months | 282732.5805 | 447.558 | 1795.5347 | 0 | 0.0034 | 8954260 | 117697.667
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 467852000000 | 312033.885 | 18-JAN-20:19 | 115409.096 | 136430.368 | 28581.864 | 0 | 23884.859 | 3589.95 | 1270.987 | 0 | 0 | 0 | 0 | 0 | 2866.761 | 0 | 0
February | 464130000000 | 355487.538 | 27-FEB-20:10 | 115409.096 | 136430.368 | 29446.326 | 0 | 65953.248 | 3589.95 | 1791.841 | 0 | 0 | 0 | 0 | 0 | 2866.708 | 0 | 0
March | 531089000000 | 414061.798 | 30-MAR-19:10 | 115409.096 | 136430.368 | 30145.919 | 0 | 123174.352 | 3589.95 | 2445.672 | 0 | 0 | 0 | 0 | 0 | 2866.44 | 0 | 0
April | 687480000000 | 539204.183 | 21-APR-18:10 | 102647.053 | 127075.755 | 32620.394 | 0 | 269222.279 | 0 | 5316.42 | 0 | 0 | 0 | 0 | 0 | 2322.282 | 0 | 0
May | 815908000000 | 607399.699 | 31-MAY-18:10 | 102647.053 | 127075.755 | 34930.819 | 0 | 331326.426 | 0 | 8540.667 | 0 | 0 | 0 | 0 | 0 | 2878.98 | 0 | 0
June | 1029490000000 | 763939.229 | 27-JUN-19:10 | 115409.096 | 136430.368 | 99072.33 | 0 | 392840.611 | 3589.95 | 14174.126 | 0 | 0 | 0 | 0 | 0 | 2422.749 | 0 | 0
July | 1175010000000 | 762066.356 | 25-JUL-19:10 | 115409.096 | 136430.368 | 98420.789 | 0 | 391283.947 | 3589.95 | 14500.741 | 0 | 0 | 0 | 0 | 0 | 2431.465 | 0 | 0
August | 1145780000000 | 756604.468 | 04-AUG-19:00 | 115409.096 | 136430.368 | 94003.004 | 0 | 390879.865 | 3589.95 | 13868.541 | 0 | 0 | 0 | 0 | 0 | 2423.644 | 0 | 0
September | 950611000000 | 691581.593 | 01-SEP-18:30 | 102647.053 | 127075.755 | 98050.817 | 0 | 344668.276 | 3589.95 | 13150.001 | 0 | 0 | 0 | 0 | 0 | 2399.741 | 0 | 0
October | 714377000000 | 515419.443 | 03-OCT-17:19 | 77122.967 | 134092.705 | 31037.111 | 0 | 262337.876 | 3589.95 | 4994.396 | 0 | 0 | 0 | 0 | 0 | 2244.438 | 0 | 0
November | 516253000000 | 380615.142 | 09-NOV-20:10 | 115409.096 | 136430.368 | 29335.379 | 0 | 90905.442 | 3589.95 | 2070.941 | 0 | 0 | 0 | 0 | 0 | 2873.967 | 0 | 0
December | 478059000000 | 354424.832 | 05-DEC-19:10 | 102647.053 | 127075.755 | 28496.006 | 0 | 88272.463 | 3589.95 | 2039.241 | 0 | 0 | 0 | 0 | 0 | 2304.364 | 0 | 0
Annual Sum or Average | 8976040000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 464130000000 | 312033.885 |  | 77122.967 | 127075.755 | 28496.006 | 0 | 23884.859 | 0 | 1270.987 | 0 | 0 | 0 | 0 | 0 | 2244.438 | 0 | 0
Maximum of Months | 1175010000000 | 763939.229 |  | 115409.096 | 136430.368 | 99072.33 | 0 | 392840.611 | 3589.95 | 14500.741 | 0 | 0 | 0 | 0 | 0 | 2878.98 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 234671.87 | 60785.37 | 0 | 295457.24
Cost per Total Building Area ($/m2) | 20.68 | 5.36 | 0 | 26.04
Cost per Net Conditioned Building Area ($/m2) | 20.68 | 5.36 | 0 | 26.04

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15052.69 | 1326.78 | 1326.78
Net Site Energy | 15052.69 | 1326.78 | 1326.78
Total Source Energy | 28361.16 | 2499.82 | 2499.82
Net Source Energy | 28361.16 | 2499.82 | 2499.82
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 839.67 | 0 | 0 | 0 | 0
Cooling | 930.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 727.83 | 0 | 0 | 0 | 0 | 0
Pumps | 48.86 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6471.29 | 0 | 0 | 0 | 44342.19
Refrigeration | 75.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5952.88 | 9099.81 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 6.49 | 0.34 | 0.34 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 6.49 | 0.34 | 0.34 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 6.49 | 0.34 | 0.34 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.34 | 0.34 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.391 | 0.39 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 6.49 | 0.391 | 0.39 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 6.49 | 0.34 | 0.34 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 6.49 | 0.61 | 0.61 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.391 | 0.39 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 6.49 | 0.34 | 0.34 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 6.49 | 0.61 | 0.61 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 6.49 | 0.391 | 0.39 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 6.49 | 0.34 | 0.34 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 6.49 | 0.34 | 0.34 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.34 | 0.34 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.391 | 0.39 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 6.49 | 0.391 | 0.39 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 6.49 | 0.34 | 0.34 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 6.49 | 0.61 | 0.61 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 6.49 | 0.61 | 0.61 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 6.49 | 0.391 | 0.39 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 6.49 | 0.34 | 0.34 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 6.49 | 0.61 | 0.61 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 6.49 | 0.34 | 0.34 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 6.49 | 0.443 | 0.443
North Total or Average |  |  | 432.93 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 781.15 | 6.49 | 0.351 | 0.351
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1166398.84 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 955976.93 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14761.8 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12540.1 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 135606.93 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 86229.61 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 11435.9 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 9398.35 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4471.97 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 3838.62 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 23846.84 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 525347.89 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 333928.83 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 4991.99 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.15 | 734.21 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.97 | 619.73 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.29 | 6546.62 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 6.96 | 4426.59 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.89 | 565.72 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.73 | 461.86 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.35 | 224.49 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.3 | 192.33 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.85 | 1175.65 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 32.91 | 74387.93 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5311.87 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10688.43 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 88282.2391 | 78.1652 | 355.3644 | 0 | 0.0003 | 2142650 | 31638.8345
February | 75776.3964 | 66.9006 | 339.3512 | 0 | 0.0002 | 2046370 | 27261.6854
March | 83631.5823 | 73.8706 | 368.2874 | 0 | 0.0003 | 2220820 | 30068.6618
April | 80084.4412 | 70.6038 | 376.5834 | 0 | 0.0003 | 2271010 | 28866.301
May | 82506.9025 | 72.5984 | 413.227 | 0 | 0.0003 | 2492160 | 29816.5172
June | 79839.0253 | 70.1534 | 417.3023 | 0 | 0.0003 | 2516850 | 28905.5939
July | 84162.4514 | 73.8458 | 458.9694 | 0 | 0.0003 | 2768260 | 30529.0637
August | 83958.0084 | 73.6653 | 458.0583 | 0 | 0.0003 | 2762770 | 30455.5258
September | 83437.3665 | 73.176 | 461.0314 | 0 | 0.0003 | 2780730 | 30284.4016
October | 83521.5394 | 73.3787 | 438.4286 | 0 | 0.0003 | 2644280 | 30244.5738
November | 78896.2079 | 69.5417 | 373.5969 | 0 | 0.0002 | 2253020 | 28445.9397
December | 85940.2268 | 76.0468 | 353.9522 | 0 | 0.0003 | 2134200 | 30823.9514
Annual Sum or Average | 990036.3873 | 871.9463 | 4814.1524 | 0 | 0.0032 | 29033100 | 357341.0498
Minimum of Months | 75776.3964 | 66.9006 | 339.3512 | 0 | 0.0002 | 2046370 | 27261.6854
Maximum of Months | 88282.2391 | 78.1652 | 461.0314 | 0 | 0.0003 | 2780730 | 31638.8345
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 439325000000 | 311845.445 | 15-JAN-20:10 | 108704.859 | 134943.936 | 25007.953 | 0 | 35255.239 | 3589.95 | 1499.427 | 0 | 0 | 0 | 0 | 0 | 2844.081 | 0 | 0
February | 419582000000 | 360888.402 | 15-FEB-20:10 | 115409.096 | 136430.368 | 26378.296 | 0 | 73907.276 | 3589.95 | 2267.345 | 0 | 0 | 0 | 0 | 0 | 2906.071 | 0 | 0
March | 455351000000 | 321703.523 | 26-MAR-19:10 | 108704.859 | 134943.936 | 25323.894 | 0 | 44340.406 | 3589.95 | 1940.391 | 0 | 0 | 0 | 0 | 0 | 2860.086 | 0 | 0
April | 465643000000 | 369874.9 | 13-APR-19:10 | 115409.096 | 136430.368 | 27330.942 | 0 | 82334.122 | 3589.95 | 1901.939 | 0 | 0 | 0 | 0 | 0 | 2878.483 | 0 | 0
May | 510987000000 | 383829.359 | 25-MAY-19:19 | 115409.096 | 136430.368 | 27098.22 | 0 | 96012.616 | 3589.95 | 2366.938 | 0 | 0 | 0 | 0 | 0 | 2922.171 | 0 | 0
June | 516048000000 | 394369.447 | 16-JUN-19:10 | 115409.096 | 136430.368 | 28061.695 | 0 | 108838.034 | 0 | 3254.947 | 0 | 0 | 0 | 0 | 0 | 2375.308 | 0 | 0
July | 567598000000 | 469910.111 | 02-JUL-19:10 | 108704.859 | 134943.936 | 28800.393 | 0 | 190767.598 | 0 | 3806.225 | 0 | 0 | 0 | 0 | 0 | 2887.1 | 0 | 0
August | 566472000000 | 386920.373 | 14-AUG-19:10 | 115409.096 | 136430.368 | 27503.452 | 0 | 98468.761 | 3589.95 | 2607.369 | 0 | 0 | 0 | 0 | 0 | 2911.376 | 0 | 0
September | 570155000000 | 456040.21 | 28-SEP-19:00 | 115409.096 | 136430.368 | 29747.451 | 0 | 164654.999 | 3589.95 | 3311.258 | 0 | 0 | 0 | 0 | 0 | 2897.088 | 0 | 0
October | 542176000000 | 396773.978 | 16-OCT-19:10 | 115409.096 | 136430.368 | 26725.243 | 0 | 108800.758 | 3589.95 | 2914.161 | 0 | 0 | 0 | 0 | 0 | 2904.401 | 0 | 0
November | 461953000000 | 342214.128 | 02-NOV-20:00 | 115409.096 | 136430.368 | 25875.479 | 0 | 56067.472 | 3589.95 | 1929.085 | 0 | 0 | 0 | 0 | 0 | 2912.679 | 0 | 0
December | 437592000000 | 300396.366 | 06-DEC-20:00 | 115409.096 | 136430.368 | 25419.248 | 0 | 15301.707 | 3589.95 | 1348.237 | 0 | 0 | 0 | 0 | 0 | 2897.76 | 0 | 0
Annual Sum or Average | 5952880000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 419582000000 | 300396.366 |  | 108704.859 | 134943.936 | 25007.953 | 0 | 15301.707 | 0 | 1348.237 | 0 | 0 | 0 | 0 | 0 | 2375.308 | 0 | 0
Maximum of Months | 570155000000 | 469910.111 |  | 115409.096 | 136430.368 | 29747.451 | 0 | 190767.598 | 3589.95 | 3806.225 | 0 | 0 | 0 | 0 | 0 | 2922.171 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 243688.56 | 76646.44 | 0 | 320335
Cost per Total Building Area ($/m2) | 21.48 | 6.76 | 0 | 28.24
Cost per Net Conditioned Building Area ($/m2) | 21.48 | 6.76 | 0 | 28.24

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18634.74 | 1642.51 | 1642.51
Net Site Energy | 18634.74 | 1642.51 | 1642.51
Total Source Energy | 39182.42 | 3453.63 | 3453.63
Net Source Energy | 39182.42 | 3453.63 | 3453.63
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2672.64 | 0 | 0 | 0 | 0
Cooling | 2486.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 780.45 | 0 | 0 | 0 | 0 | 0
Pumps | 69.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6591.4 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.97 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7581.84 | 11052.9 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.402 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.402 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.501 | 0.622 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.437 | 0.54
North Total or Average |  |  | 432.93 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1707098.51 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1302010.68 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17709.07 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17267.23 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 158764.76 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 139109.24 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15258.9 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14209.58 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5467.98 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5385.28 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 28087.35 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 867281.32 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 432512.41 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 6045.38 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.25 | 797.15 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.22 | 774.37 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 9.68 | 6159.82 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.48 | 5397.64 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.06 | 672.2 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.97 | 619.93 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.39 | 250.5 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.39 | 246.89 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.81 | 1151.81 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 35.47 | 80177.01 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7234.6 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15643.2 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 154453.2848 | 220.0486 | 441.5539 | 0 | 0.0019 | 27436.546 | 60757.9397
February | 134364.3914 | 194.1827 | 399.3335 | 0 | 0.0018 | 24814.8251 | 53107.3653
March | 137876.1804 | 211.9253 | 479.7139 | 0 | 0.0021 | 29817.2522 | 55653.6575
April | 127514.1439 | 206.5038 | 501.6689 | 0 | 0.0021 | 31187.2288 | 52431.6328
May | 151325.9974 | 261.1637 | 684.2339 | 0 | 0.0028 | 42543.9741 | 63694.5761
June | 176058.0859 | 316.6892 | 866.9701 | 0 | 0.0036 | 53911.0821 | 75278.7854
July | 197759.6217 | 361.3367 | 1004.8192 | 0 | 0.0041 | 62485.0123 | 85070.9958
August | 197115.1905 | 360.5751 | 1003.841 | 0 | 0.0041 | 62424.3307 | 84831.8038
September | 156145.1344 | 278.2373 | 754.3742 | 0 | 0.0031 | 46908.5514 | 66523.6763
October | 142117.0116 | 241.3611 | 621.0085 | 0 | 0.0026 | 38611.2499 | 59460.9593
November | 130934.0285 | 208.215 | 493.9918 | 0 | 0.0021 | 30708.2475 | 53487.8905
December | 144699.9285 | 210.8196 | 439.4373 | 0 | 0.0019 | 27307.9131 | 57347.9132
Annual Sum or Average | 1850360 | 3071.0579 | 7690.9462 | 0 | 0.0322 | 478156.2132 | 767647.1958
Minimum of Months | 127514.1439 | 194.1827 | 399.3335 | 0 | 0.0018 | 24814.8251 | 52431.6328
Maximum of Months | 197759.6217 | 361.3367 | 1004.8192 | 0 | 0.0041 | 62485.0123 | 85070.9958
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 435045000000 | 316824.489 | 08-JAN-20:00 | 108704.859 | 134943.936 | 25905.105 | 0 | 38951.584 | 3589.95 | 1870.836 | 0 | 0 | 0 | 0 | 0 | 2858.22 | 0 | 0
February | 393474000000 | 297160.551 | 15-FEB-20:10 | 115409.096 | 136430.368 | 26474.712 | 0 | 11211.392 | 3589.95 | 1170.616 | 0 | 0 | 0 | 0 | 0 | 2874.418 | 0 | 0
March | 472794000000 | 434086.012 | 09-MAR-20:00 | 115409.096 | 136430.368 | 27634.884 | 0 | 145234.304 | 3589.95 | 2868.541 | 0 | 0 | 0 | 0 | 0 | 2918.868 | 0 | 0
April | 494517000000 | 438804.887 | 05-APR-19:10 | 115409.096 | 136430.368 | 28789.663 | 0 | 148168.543 | 3589.95 | 3513.913 | 0 | 0 | 0 | 0 | 0 | 2903.354 | 0 | 0
May | 674594000000 | 500562.377 | 15-MAY-17:19 | 77122.967 | 134092.705 | 28068.53 | 0 | 254511.07 | 0 | 4478.437 | 0 | 0 | 0 | 0 | 0 | 2288.668 | 0 | 0
June | 854836000000 | 688866.895 | 30-JUN-17:19 | 77122.967 | 134092.705 | 30253.186 | 0 | 439199.135 | 0 | 5907.398 | 0 | 0 | 0 | 0 | 0 | 2291.505 | 0 | 0
July | 990788000000 | 705655.641 | 24-JUL-18:10 | 102647.053 | 127075.755 | 32091.964 | 0 | 434382.155 | 0 | 6533.424 | 0 | 0 | 0 | 0 | 0 | 2925.291 | 0 | 0
August | 989825000000 | 698853.461 | 17-AUG-18:10 | 102647.053 | 127075.755 | 32416.768 | 0 | 427269.11 | 0 | 6520.873 | 0 | 0 | 0 | 0 | 0 | 2923.902 | 0 | 0
September | 743801000000 | 512870.012 | 09-SEP-17:10 | 87035.741 | 134092.705 | 30238.786 | 0 | 255051.732 | 0 | 4162.519 | 0 | 0 | 0 | 0 | 0 | 2288.529 | 0 | 0
October | 612236000000 | 489357.13 | 02-OCT-19:00 | 115409.096 | 136430.368 | 27803.145 | 0 | 199351.25 | 3589.95 | 3853.373 | 0 | 0 | 0 | 0 | 0 | 2919.948 | 0 | 0
November | 486922000000 | 443856.141 | 03-NOV-20:00 | 115409.096 | 136430.368 | 27718.743 | 0 | 155256.827 | 3589.95 | 3057.254 | 0 | 0 | 0 | 0 | 0 | 2393.903 | 0 | 0
December | 433005000000 | 290514.326 | 06-DEC-20:49 | 115409.096 | 136430.368 | 25943.85 | 0 | 4994.148 | 3589.95 | 1281.035 | 0 | 0 | 0 | 0 | 0 | 2865.878 | 0 | 0
Annual Sum or Average | 7581840000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 393474000000 | 290514.326 |  | 77122.967 | 127075.755 | 25905.105 | 0 | 4994.148 | 0 | 1170.616 | 0 | 0 | 0 | 0 | 0 | 2288.529 | 0 | 0
Maximum of Months | 990788000000 | 705655.641 |  | 115409.096 | 136430.368 | 32416.768 | 0 | 439199.135 | 3589.95 | 6533.424 | 0 | 0 | 0 | 0 | 0 | 2925.291 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 152329.26 | 110668.54 | 0 | 262997.8
Cost per Total Building Area ($/m2) | 13.43 | 9.75 | 0 | 23.18
Cost per Net Conditioned Building Area ($/m2) | 13.43 | 9.75 | 0 | 23.18

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17397.43 | 1533.45 | 1533.45
Net Site Energy | 17397.43 | 1533.45 | 1533.45
Total Source Energy | 35943.97 | 3168.18 | 3168.18
Net Source Energy | 35943.97 | 3168.18 | 3168.18
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1548.01 | 0 | 0 | 0 | 0
Cooling | 2374.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.41 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 918.27 | 0 | 0 | 0 | 0 | 0
Pumps | 75.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6447.82 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.78 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7612.75 | 9784.68 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.402 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.402 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.501 | 0.622 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.437 | 0.54
North Total or Average |  |  | 432.93 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1983645.58 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1160931.86 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17827.27 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17701.21 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 141194.13 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 125607.06 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12593.01 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 11940.2 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5527.27 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5544.26 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 24209.24 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 869053.9 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 564894.5 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 8982.05 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.48 | 940.42 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.47 | 934.24 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.83 | 6892.77 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.25 | 6522.65 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.2 | 764.37 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.14 | 723.9 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.47 | 297.5 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.47 | 299.34 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.97 | 1252.8 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 41.71 | 93765.66 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6450.7 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18177.37 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 185920.1355 | 273.6254 | 568.3723 | 0 | 0.0023 | 590687.4077 | 74633.3195
February | 167353.6539 | 249.8206 | 530.6659 | 0 | 0.0022 | 551533.9228 | 67525.5243
March | 185934.5222 | 282.4573 | 616.1041 | 0 | 0.0025 | 640376.7268 | 75503.3278
April | 190437.6727 | 299.7127 | 687.3946 | 0 | 0.0028 | 714567.0076 | 78353.5065
May | 226578.0455 | 366.7898 | 873.0474 | 0 | 0.0035 | 907640.414 | 94223.4842
June | 243889.8156 | 401.0612 | 973.5631 | 0 | 0.0039 | 1012190 | 102035.395
July | 276214.9943 | 458.6562 | 1126.6216 | 0 | 0.0045 | 1171350 | 115994.5264
August | 263459.4378 | 436.6241 | 1069.9861 | 0 | 0.0042 | 1112460 | 110554.4051
September | 227493.7052 | 373.365 | 904.1409 | 0 | 0.0036 | 940004.2308 | 95103.8235
October | 196084.9821 | 313.0994 | 732.1289 | 0 | 0.0029 | 761105.7527 | 81118.3198
November | 174313.0318 | 266.5194 | 586.8868 | 0 | 0.0024 | 610023.3826 | 70952.5143
December | 184912.2235 | 272.6376 | 567.9733 | 0 | 0.0023 | 590277.4332 | 74277.3265
Annual Sum or Average | 2522590 | 3994.3689 | 9236.8849 | 0 | 0.037 | 9602210 | 1040280
Minimum of Months | 167353.6539 | 249.8206 | 530.6659 | 0 | 0.0022 | 551533.9228 | 67525.5243
Maximum of Months | 276214.9943 | 458.6562 | 1126.6216 | 0 | 0.0045 | 1171350 | 115994.5264
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 468304000000 | 315621.102 | 26-JAN-20:10 | 115409.096 | 136430.368 | 31250.205 | 0 | 24759.732 | 3589.95 | 1314.927 | 0 | 0 | 0 | 0 | 0 | 2866.823 | 0 | 0
February | 437263000000 | 331696.863 | 14-FEB-18:19 | 77122.967 | 134092.705 | 31226.919 | 0 | 81046.591 | 3589.95 | 2384.636 | 0 | 0 | 0 | 0 | 0 | 2233.095 | 0 | 0
March | 507698000000 | 391492.713 | 25-MAR-17:19 | 87035.741 | 134092.705 | 31988.958 | 0 | 133427.765 | 0 | 2714.963 | 0 | 0 | 0 | 0 | 0 | 2232.581 | 0 | 0
April | 566517000000 | 463200.315 | 21-APR-19:10 | 115409.096 | 136430.368 | 35204.548 | 0 | 166789.536 | 3589.95 | 3437.291 | 0 | 0 | 0 | 0 | 0 | 2339.527 | 0 | 0
May | 719588000000 | 516166.852 | 31-MAY-18:10 | 102647.053 | 127075.755 | 37217.017 | 0 | 239922.798 | 0 | 6421.998 | 0 | 0 | 0 | 0 | 0 | 2882.232 | 0 | 0
June | 802473000000 | 561466.936 | 28-JUN-19:10 | 115409.096 | 136430.368 | 39304.174 | 0 | 259830.358 | 0 | 7616.446 | 0 | 0 | 0 | 0 | 0 | 2876.494 | 0 | 0
July | 928659000000 | 664457.825 | 30-JUL-19:10 | 108704.859 | 134943.936 | 106149.021 | 0 | 295089.972 | 3589.95 | 13029.573 | 0 | 0 | 0 | 0 | 0 | 2950.514 | 0 | 0
August | 881971000000 | 591515.777 | 01-AUG-18:10 | 102647.053 | 127075.755 | 38785.133 | 0 | 308730.047 | 0 | 11921.746 | 0 | 0 | 0 | 0 | 0 | 2356.044 | 0 | 0
September | 745247000000 | 518126.374 | 02-SEP-17:19 | 87035.741 | 134092.705 | 35816.666 | 0 | 248564.781 | 0 | 10345.912 | 0 | 0 | 0 | 0 | 0 | 2270.57 | 0 | 0
October | 603414000000 | 464743.702 | 02-OCT-19:10 | 115409.096 | 136430.368 | 35032.256 | 0 | 167784.588 | 3589.95 | 3607.265 | 0 | 0 | 0 | 0 | 0 | 2890.179 | 0 | 0
November | 483634000000 | 368626.147 | 09-NOV-20:00 | 115409.096 | 136430.368 | 32179.271 | 0 | 76209.599 | 3589.95 | 1935.799 | 0 | 0 | 0 | 0 | 0 | 2872.064 | 0 | 0
December | 467979000000 | 309504.341 | 08-DEC-20:10 | 115409.096 | 136430.368 | 30835.209 | 0 | 19647.392 | 3589.95 | 1249.589 | 0 | 0 | 0 | 0 | 0 | 2342.736 | 0 | 0
Annual Sum or Average | 7612750000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 437263000000 | 309504.341 |  | 77122.967 | 127075.755 | 30835.209 | 0 | 19647.392 | 0 | 1249.589 | 0 | 0 | 0 | 0 | 0 | 2232.581 | 0 | 0
Maximum of Months | 928659000000 | 664457.825 |  | 115409.096 | 136430.368 | 106149.021 | 0 | 308730.047 | 3589.95 | 13029.573 | 0 | 0 | 0 | 0 | 0 | 2950.514 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 78281.95 | 70113.93 | 0 | 148395.88
Cost per Total Building Area ($/m2) | 6.9 | 6.18 | 0 | 13.08
Cost per Net Conditioned Building Area ($/m2) | 6.9 | 6.18 | 0 | 13.08

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16915.27 | 1490.95 | 1490.95
Net Site Energy | 16915.27 | 1490.95 | 1490.95
Total Source Energy | 22405.55 | 1974.88 | 1974.88
Net Source Energy | 22405.55 | 1974.88 | 1974.88
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2088.65 | 0 | 0 | 0 | 0
Cooling | 975.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 780.79 | 0 | 0 | 0 | 0 | 0
Pumps | 50.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 6985.33 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.99 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6052.43 | 10862.83 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.402 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.402 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.501 | 0.622 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.437 | 0.54
North Total or Average |  |  | 432.93 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1303380.78 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1125260.04 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 16113.72 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13903.35 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 148561.97 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 97279.62 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13393.69 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 11156.43 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4913.12 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4287.81 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 26965.02 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 590715.55 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 370615.25 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5475.25 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.26 | 799.22 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.08 | 684.16 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 11.04 | 7027.86 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 7.57 | 4819.37 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.04 | 659.24 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.86 | 544.77 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.39 | 246.06 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.34 | 213.75 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 2.06 | 1310.67 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 34.81 | 78678.54 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6252.49 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11943.68 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 85465.4984 | 92.0942 | 93.0368 | 0 | 0.0005 | 1225400 | 31134.3471
February | 71601.0453 | 78.4026 | 85.9134 | 0 | 0.0004 | 1132080 | 26217.3252
March | 78380.9852 | 86.4403 | 97.9675 | 0 | 0.0005 | 1291140 | 28765.5938
April | 69368.3493 | 78.4215 | 98.965 | 0 | 0.0005 | 1304950 | 25663.674
May | 67507.9764 | 79.2812 | 115.2285 | 0 | 0.0005 | 1520300 | 25292.7351
June | 64198.8254 | 77.2781 | 121.6034 | 0 | 0.0006 | 1604890 | 24254.6013
July | 67016.5734 | 82.4704 | 138.4364 | 0 | 0.0006 | 1827460 | 25511.991
August | 67114.5288 | 82.8713 | 140.4291 | 0 | 0.0006 | 1853830 | 25579.312
September | 63396.6733 | 76.4902 | 121.2185 | 0 | 0.0005 | 1599850 | 23970.5737
October | 65671.5723 | 75.9868 | 104.8293 | 0 | 0.0005 | 1382810 | 24482.8433
November | 73100.9318 | 80.7006 | 91.8997 | 0 | 0.0005 | 1211200 | 26836.7485
December | 84010.6628 | 90.7438 | 92.8408 | 0 | 0.0005 | 1222910 | 30627.6396
Annual Sum or Average | 856833.6225 | 981.181 | 1302.3686 | 0 | 0.0062 | 17176800 | 318337.3844
Minimum of Months | 63396.6733 | 75.9868 | 85.9134 | 0 | 0.0004 | 1132080 | 23970.5737
Maximum of Months | 85465.4984 | 92.0942 | 140.4291 | 0 | 0.0006 | 1853830 | 31134.3471
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 431784000000 | 288834.657 | 02-JAN-20:10 | 115409.096 | 136430.368 | 25911.048 | 0 | 2958.988 | 3589.95 | 1668.884 | 0 | 0 | 0 | 0 | 0 | 2866.324 | 0 | 0
February | 398900000000 | 324093.876 | 21-FEB-20:10 | 115409.096 | 136430.368 | 27422.219 | 0 | 37424.011 | 3589.95 | 1476.705 | 0 | 0 | 0 | 0 | 0 | 2341.527 | 0 | 0
March | 454946000000 | 381598.481 | 29-MAR-19:10 | 115409.096 | 136430.368 | 28499.79 | 0 | 92170.104 | 3589.95 | 2606.051 | 0 | 0 | 0 | 0 | 0 | 2893.122 | 0 | 0
April | 459813000000 | 369372.438 | 14-APR-19:10 | 115409.096 | 136430.368 | 28232.241 | 0 | 81463.651 | 3589.95 | 1892.204 | 0 | 0 | 0 | 0 | 0 | 2354.928 | 0 | 0
May | 535695000000 | 419742.072 | 04-MAY-19:19 | 115409.096 | 136430.368 | 29889.492 | 0 | 128106.6 | 3589.95 | 3409.477 | 0 | 0 | 0 | 0 | 0 | 2907.089 | 0 | 0
June | 565501000000 | 443882.53 | 27-JUN-19:10 | 115409.096 | 136430.368 | 30897.44 | 0 | 154330.618 | 0 | 4440.186 | 0 | 0 | 0 | 0 | 0 | 2374.821 | 0 | 0
July | 643926000000 | 477333.305 | 24-JUL-19:10 | 115409.096 | 136430.368 | 32418.69 | 0 | 186307.996 | 0 | 3841.379 | 0 | 0 | 0 | 0 | 0 | 2925.776 | 0 | 0
August | 653215000000 | 453926.001 | 08-AUG-19:10 | 115409.096 | 136430.368 | 30931.641 | 0 | 165130.755 | 0 | 3625.161 | 0 | 0 | 0 | 0 | 0 | 2398.98 | 0 | 0
September | 563725000000 | 544968.051 | 02-SEP-17:10 | 87035.741 | 134092.705 | 30507.851 | 0 | 286057.299 | 0 | 5006.245 | 0 | 0 | 0 | 0 | 0 | 2268.21 | 0 | 0
October | 487247000000 | 386311.23 | 17-OCT-19:10 | 115409.096 | 136430.368 | 28159.306 | 0 | 98343.784 | 3589.95 | 2026.526 | 0 | 0 | 0 | 0 | 0 | 2352.201 | 0 | 0
November | 426778000000 | 322270.221 | 02-NOV-20:00 | 115409.096 | 136430.368 | 27033.809 | 0 | 35152.454 | 3589.95 | 1754.62 | 0 | 0 | 0 | 0 | 0 | 2899.924 | 0 | 0
December | 430904000000 | 286961.722 | 28-DEC-20:00 | 115409.096 | 136430.368 | 26637.394 | 0 | 848.287 | 3589.95 | 1154.883 | 0 | 0 | 0 | 0 | 0 | 2891.743 | 0 | 0
Annual Sum or Average | 6052430000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 398900000000 | 286961.722 |  | 87035.741 | 134092.705 | 25911.048 | 0 | 848.287 | 0 | 1154.883 | 0 | 0 | 0 | 0 | 0 | 2268.21 | 0 | 0
Maximum of Months | 653215000000 | 544968.051 |  | 115409.096 | 136430.368 | 32418.69 | 0 | 286057.299 | 3589.95 | 5006.245 | 0 | 0 | 0 | 0 | 0 | 2925.776 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 123141.55 | 90224.74 | 0 | 213366.28
Cost per Total Building Area ($/m2) | 10.85 | 7.95 | 0 | 18.81
Cost per Net Conditioned Building Area ($/m2) | 10.85 | 7.95 | 0 | 18.81

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19989.48 | 1761.92 | 1761.92
Net Site Energy | 19989.48 | 1761.92 | 1761.92
Total Source Energy | 38927.39 | 3431.15 | 3431.15
Net Source Energy | 38927.39 | 3431.15 | 3431.15
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3976.8 | 0 | 0 | 0 | 0
Cooling | 1871.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.4 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 786.68 | 0 | 0 | 0 | 0 | 0
Pumps | 64.37 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7256.07 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.8 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6967.76 | 13021.71 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.402 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.402 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.501 | 0.622 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.437 | 0.54
North Total or Average |  |  | 432.93 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1704523.28 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1506118.24 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17570.29 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 16918.34 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 161023.21 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 137750.41 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15075.24 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13836.23 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5391.68 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5265.22 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 28461.97 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 864742.23 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 432530.14 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5958.31 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.26 | 801.18 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.21 | 768.37 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.03 | 6379.64 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.46 | 5386.24 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.06 | 673.95 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.96 | 610.72 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.39 | 250.04 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.38 | 244.07 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.86 | 1186.26 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 35.83 | 80979.62 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8368.72 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15619.6 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 244647.1411 | 356.9395 | 809.5392 | 0 | 0.0026 | 186250.2507 | 97567.9884
February | 213810.9662 | 316.0281 | 731.9513 | 0 | 0.0024 | 168408.4151 | 85660.1249
March | 225076.693 | 341.4872 | 823.3171 | 0 | 0.0026 | 189448.257 | 91015.667
April | 210436.5158 | 335.1673 | 865.0337 | 0 | 0.0027 | 199078.2883 | 86614.9923
May | 252051.2843 | 419.9883 | 1147.2411 | 0 | 0.0035 | 264057.3533 | 105516.1302
June | 299679.2719 | 512.9643 | 1445.64 | 0 | 0.0044 | 332760.2542 | 126756.294
July | 343551.4397 | 594.1543 | 1693.807 | 0 | 0.0052 | 389892.8076 | 145895.6587
August | 329417.6967 | 569.1126 | 1620.5379 | 0 | 0.005 | 373026.3233 | 139836.3064
September | 268116.0874 | 457.124 | 1282.5106 | 0 | 0.0039 | 295208.1457 | 113232.5481
October | 227107.6901 | 373.7415 | 1005.6294 | 0 | 0.0031 | 231455.6676 | 94626.1844
November | 209409.2244 | 325.6966 | 813.8452 | 0 | 0.0026 | 187284.2534 | 85443.1017
December | 236011.2453 | 348.8642 | 808.0859 | 0 | 0.0026 | 185925.6109 | 94556.4847
Annual Sum or Average | 3059320 | 4951.268 | 13047.1384 | 0 | 0.0407 | 3002800 | 1266720
Minimum of Months | 209409.2244 | 316.0281 | 731.9513 | 0 | 0.0024 | 168408.4151 | 85443.1017
Maximum of Months | 343551.4397 | 594.1543 | 1693.807 | 0 | 0.0052 | 389892.8076 | 145895.6587
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 432180000000 | 292804.47 | 17-JAN-20:30 | 115409.096 | 136430.368 | 26472.117 | 0 | 7343.961 | 3589.95 | 1203.331 | 0 | 0 | 0 | 0 | 0 | 2355.647 | 0 | 0
February | 390779000000 | 291240.612 | 27-FEB-20:00 | 115409.096 | 136430.368 | 26618.496 | 0 | 5152.015 | 3589.95 | 1161.448 | 0 | 0 | 0 | 0 | 0 | 2879.239 | 0 | 0
March | 439600000000 | 378788.198 | 31-MAR-19:10 | 115409.096 | 136430.368 | 27891.909 | 0 | 91140.817 | 3589.95 | 1970.967 | 0 | 0 | 0 | 0 | 0 | 2355.092 | 0 | 0
April | 461946000000 | 370806.814 | 28-APR-18:10 | 102647.053 | 127075.755 | 28430.681 | 0 | 108229.889 | 0 | 2109.948 | 0 | 0 | 0 | 0 | 0 | 2313.488 | 0 | 0
May | 612725000000 | 499473.607 | 30-MAY-17:19 | 77122.967 | 134092.705 | 28389.924 | 0 | 253205.838 | 0 | 4374.168 | 0 | 0 | 0 | 0 | 0 | 2288.004 | 0 | 0
June | 772145000000 | 539762.724 | 19-JUN-19:10 | 115409.096 | 136430.368 | 29957.268 | 0 | 250413.97 | 0 | 4626.846 | 0 | 0 | 0 | 0 | 0 | 2925.176 | 0 | 0
July | 904717000000 | 629290.909 | 13-JUL-17:19 | 77122.967 | 134092.705 | 31087.126 | 0 | 379049.249 | 0 | 5647.732 | 0 | 0 | 0 | 0 | 0 | 2291.131 | 0 | 0
August | 865579000000 | 662502.775 | 04-AUG-19:10 | 115409.096 | 136430.368 | 32365.352 | 0 | 365727.295 | 3589.95 | 6579.007 | 0 | 0 | 0 | 0 | 0 | 2401.707 | 0 | 0
September | 685008000000 | 521280.817 | 06-SEP-19:10 | 115409.096 | 136430.368 | 30758.291 | 0 | 227461.734 | 3589.95 | 4707.004 | 0 | 0 | 0 | 0 | 0 | 2924.373 | 0 | 0
October | 537075000000 | 451174.154 | 30-OCT-20:00 | 115409.096 | 136430.368 | 28226.76 | 0 | 161350.28 | 3589.95 | 3247.382 | 0 | 0 | 0 | 0 | 0 | 2920.318 | 0 | 0
November | 434579000000 | 425558.433 | 02-NOV-20:10 | 115409.096 | 136430.368 | 28054.98 | 0 | 136410.581 | 3589.95 | 2743.945 | 0 | 0 | 0 | 0 | 0 | 2919.512 | 0 | 0
December | 431426000000 | 292761.776 | 11-DEC-20:00 | 115409.096 | 136430.368 | 26479.897 | 0 | 6806.118 | 3589.95 | 1166.938 | 0 | 0 | 0 | 0 | 0 | 2879.41 | 0 | 0
Annual Sum or Average | 6967760000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 390779000000 | 291240.612 |  | 77122.967 | 127075.755 | 26472.117 | 0 | 5152.015 | 0 | 1161.448 | 0 | 0 | 0 | 0 | 0 | 2288.004 | 0 | 0
Maximum of Months | 904717000000 | 662502.775 |  | 115409.096 | 136430.368 | 32365.352 | 0 | 379049.249 | 3589.95 | 6579.007 | 0 | 0 | 0 | 0 | 0 | 2925.176 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 181110.76 | 114530.26 | 0 | 295641.02
Cost per Total Building Area ($/m2) | 15.96 | 10.09 | 0 | 26.06
Cost per Net Conditioned Building Area ($/m2) | 15.96 | 10.09 | 0 | 26.06

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18321.18 | 1614.87 | 1614.87
Net Site Energy | 18321.18 | 1614.87 | 1614.87
Total Source Energy | 34999.29 | 3084.92 | 3084.92
Net Source Energy | 34999.29 | 3084.92 | 3084.92
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2575.77 | 0 | 0 | 0 | 0
Cooling | 1526.94 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 904.26 | 0 | 0 | 0 | 0 | 0
Pumps | 59.22 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7221.36 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6735.2 | 11585.98 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.402 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.402 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.501 | 0.622 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.437 | 0.54
North Total or Average |  |  | 432.93 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1210074.41 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1343911.64 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15128.53 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14632.62 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 125460.5 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 104126.9 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12354.04 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 11253.44 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4680.16 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4590.72 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 22053.95 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 545826.92 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 344741.5 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5225.13 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.44 | 915.87 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.39 | 885.41 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 11.36 | 7225.87 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 9.81 | 6239.69 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.17 | 746.79 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.06 | 677.61 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.45 | 286.42 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.44 | 282.03 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 2.06 | 1308.77 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 41.45 | 93193.94 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7467.42 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11088.66 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 195673.4775 | 280.5522 | 557.9869 | 0 | 0.0023 | 579823.8104 | 77819.9991
February | 174180.8175 | 252.036 | 509.1443 | 0 | 0.0021 | 529093.0922 | 69497.8575
March | 190081.3596 | 280.8464 | 587.0293 | 0 | 0.0024 | 610087.2883 | 76411.3191
April | 183709.0408 | 281.1152 | 619.764 | 0 | 0.0025 | 644198.709 | 74799.586
May | 197282.3927 | 309.7816 | 708.2936 | 0 | 0.0028 | 736286.4888 | 81100.6921
June | 207642.0204 | 333.4844 | 785.7331 | 0 | 0.0031 | 816846.5214 | 86088.7887
July | 245686.6067 | 401.5247 | 967.252 | 0 | 0.0038 | 1005610 | 102542.7532
August | 229593.352 | 373.844 | 896.4266 | 0 | 0.0036 | 931962.3863 | 95690.5493
September | 200771.8211 | 322.5391 | 760.215 | 0 | 0.003 | 790318.5756 | 83249.0749
October | 189387.2447 | 295.729 | 670.9889 | 0 | 0.0027 | 697494.0888 | 77692.717
November | 177012.1286 | 263.607 | 557.8741 | 0 | 0.0023 | 579806.3776 | 71360.6783
December | 193396.5014 | 277.4171 | 552.1956 | 0 | 0.0023 | 573807.2303 | 76927.1569
Annual Sum or Average | 2384420 | 3672.4766 | 8172.9035 | 0 | 0.0331 | 8495330 | 973181.1721
Minimum of Months | 174180.8175 | 252.036 | 509.1443 | 0 | 0.0021 | 529093.0922 | 69497.8575
Maximum of Months | 245686.6067 | 401.5247 | 967.252 | 0 | 0.0038 | 1005610 | 102542.7532
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 459691000000 | 316820.85 | 24-JAN-20:10 | 115409.096 | 136430.368 | 31415.318 | 0 | 26354.605 | 3589.95 | 1281.105 | 0 | 0 | 0 | 0 | 0 | 2340.408 | 0 | 0
February | 419471000000 | 312028.649 | 10-FEB-20:00 | 115409.096 | 136430.368 | 31193.255 | 0 | 21815.887 | 3589.95 | 1249.256 | 0 | 0 | 0 | 0 | 0 | 2340.838 | 0 | 0
March | 483685000000 | 391796.431 | 26-MAR-19:10 | 108704.859 | 134943.936 | 32103.737 | 0 | 107394.673 | 3589.95 | 2228.604 | 0 | 0 | 0 | 0 | 0 | 2830.673 | 0 | 0
April | 510728000000 | 416044.542 | 26-APR-19:10 | 115409.096 | 136430.368 | 34263.164 | 0 | 120953.879 | 3589.95 | 2531.339 | 0 | 0 | 0 | 0 | 0 | 2866.746 | 0 | 0
May | 583737000000 | 455635.427 | 23-MAY-19:10 | 115409.096 | 136430.368 | 35790.435 | 0 | 162396.994 | 0 | 3242.194 | 0 | 0 | 0 | 0 | 0 | 2366.339 | 0 | 0
June | 647606000000 | 481018.561 | 27-JUN-19:10 | 115409.096 | 136430.368 | 37289.535 | 0 | 185918.368 | 0 | 3604.316 | 0 | 0 | 0 | 0 | 0 | 2366.877 | 0 | 0
July | 797257000000 | 578605.438 | 17-JUL-19:30 | 115409.096 | 136430.368 | 86531.474 | 0 | 226852.908 | 3589.95 | 6856.569 | 0 | 0 | 0 | 0 | 0 | 2935.072 | 0 | 0
August | 738871000000 | 506018.325 | 29-AUG-18:10 | 102647.053 | 127075.755 | 38419.975 | 0 | 231485.916 | 0 | 4067.282 | 0 | 0 | 0 | 0 | 0 | 2322.345 | 0 | 0
September | 626574000000 | 467970.268 | 01-SEP-18:10 | 102647.053 | 127075.755 | 36206.507 | 0 | 196120.957 | 0 | 3592.305 | 0 | 0 | 0 | 0 | 0 | 2327.692 | 0 | 0
October | 552982000000 | 405144.231 | 01-OCT-19:10 | 108704.859 | 134943.936 | 33283.834 | 0 | 118204.518 | 3589.95 | 3553.299 | 0 | 0 | 0 | 0 | 0 | 2863.836 | 0 | 0
November | 459677000000 | 317999.236 | 03-NOV-20:10 | 115409.096 | 136430.368 | 31179.392 | 0 | 27757.551 | 3589.95 | 1292.635 | 0 | 0 | 0 | 0 | 0 | 2340.244 | 0 | 0
December | 454921000000 | 304092.873 | 21-DEC-20:10 | 115409.096 | 136430.368 | 30759.808 | 0 | 13821.666 | 3589.95 | 1215.237 | 0 | 0 | 0 | 0 | 0 | 2866.747 | 0 | 0
Annual Sum or Average | 6735200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 419471000000 | 304092.873 |  | 102647.053 | 127075.755 | 30759.808 | 0 | 13821.666 | 0 | 1215.237 | 0 | 0 | 0 | 0 | 0 | 2322.345 | 0 | 0
Maximum of Months | 797257000000 | 578605.438 |  | 115409.096 | 136430.368 | 86531.474 | 0 | 231485.916 | 3589.95 | 6856.569 | 0 | 0 | 0 | 0 | 0 | 2935.072 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 69280.33 | 82920.42 | 0 | 152200.75
Cost per Total Building Area ($/m2) | 6.11 | 7.31 | 0 | 13.42
Cost per Net Conditioned Building Area ($/m2) | 6.11 | 7.31 | 0 | 13.42

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21953.13 | 1935 | 1935
Net Site Energy | 21953.13 | 1935 | 1935
Total Source Energy | 40012.66 | 3526.81 | 3526.81
Net Source Energy | 40012.66 | 3526.81 | 3526.81
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5493.9 | 0 | 0 | 0 | 0
Cooling | 1725.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 802.27 | 0 | 0 | 0 | 0 | 0
Pumps | 67.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7830.35 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.62 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6840.02 | 15113.11 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.402 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.402 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.501 | 0.622 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.437 | 0.54
North Total or Average |  |  | 432.93 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1653238.75 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1626156.19 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17383.31 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 16526.15 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 161115.44 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 133217.33 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15135.15 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13673.29 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5298.82 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5107.48 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 28658.9 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 822772.84 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 428486.2 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5863.83 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.28 | 812.56 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.21 | 767.29 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 10.47 | 6660.13 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.6 | 5474.81 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.09 | 693.98 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.97 | 618.95 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.39 | 251.26 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.38 | 241.77 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.95 | 1242.32 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 36.18 | 81773.78 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9035.71 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15149.64 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 218861.4199 | 286.0735 | 285.636 | 0 | 0.0023 | 187343.6325 | 84103.716
February | 185325.4714 | 246.9112 | 257.0826 | 0 | 0.0021 | 168655.4853 | 71663.2042
March | 179769.5717 | 252.3775 | 291.2774 | 0 | 0.0023 | 191190.8186 | 70744.8594
April | 161253.3806 | 242.6477 | 314.2375 | 0 | 0.0024 | 206372.2201 | 65012.8865
May | 186502.2305 | 298.5002 | 421.5921 | 0 | 0.0032 | 276977.3343 | 76899.6018
June | 205914.1987 | 340.5207 | 501.1326 | 0 | 0.0037 | 329287.2268 | 85950.4509
July | 226913.4891 | 380.3562 | 568.8737 | 0 | 0.0042 | 373822.1593 | 95204.084
August | 221322.282 | 371.1839 | 555.5072 | 0 | 0.0041 | 365039.5484 | 92877.3321
September | 171914.8718 | 280.3971 | 405.6933 | 0 | 0.003 | 266557.7367 | 71386.1469
October | 157480.666 | 241.7604 | 322.4816 | 0 | 0.0025 | 211813.5716 | 63949.6655
November | 167051.4653 | 237.462 | 280.2416 | 0 | 0.0022 | 183967.0691 | 66020.8594
December | 204415.8863 | 272.6668 | 284.6108 | 0 | 0.0023 | 186717.4973 | 79075.9519
Annual Sum or Average | 2286720 | 3450.8574 | 4488.3665 | 0 | 0.0344 | 2947740 | 922888.7585
Minimum of Months | 157480.666 | 237.462 | 257.0826 | 0 | 0.0021 | 168655.4853 | 63949.6655
Maximum of Months | 226913.4891 | 380.3562 | 568.8737 | 0 | 0.0042 | 373822.1593 | 95204.084
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 434717000000 | 288134.555 | 25-JAN-20:10 | 115409.096 | 136430.368 | 25567.115 | 0 | 0 | 3589.95 | 4273.795 | 0 | 0 | 0 | 0 | 0 | 2864.231 | 0 | 0
February | 391352000000 | 287774.517 | 07-FEB-20:00 | 115409.096 | 136430.368 | 25756.265 | 0 | 0 | 3589.95 | 4250.284 | 0 | 0 | 0 | 0 | 0 | 2338.554 | 0 | 0
March | 443644000000 | 333177.412 | 19-MAR-19:00 | 108704.859 | 134943.936 | 27711.252 | 0 | 53370.015 | 3589.95 | 1991.187 | 0 | 0 | 0 | 0 | 0 | 2866.214 | 0 | 0
April | 478871000000 | 428199.088 | 02-APR-19:00 | 108704.859 | 134943.936 | 28330.359 | 0 | 146768.123 | 3589.95 | 2979.492 | 0 | 0 | 0 | 0 | 0 | 2882.369 | 0 | 0
May | 642705000000 | 600510.568 | 27-MAY-17:19 | 87035.741 | 134092.705 | 30725.945 | 0 | 341415.463 | 0 | 4949.644 | 0 | 0 | 0 | 0 | 0 | 2291.069 | 0 | 0
June | 764086000000 | 627651.461 | 29-JUN-18:10 | 102647.053 | 127075.755 | 33683.338 | 0 | 355543.542 | 0 | 5776.463 | 0 | 0 | 0 | 0 | 0 | 2925.31 | 0 | 0
July | 867426000000 | 656969.297 | 13-JUL-18:10 | 102647.053 | 127075.755 | 31785.599 | 0 | 386368.655 | 0 | 6168.334 | 0 | 0 | 0 | 0 | 0 | 2923.901 | 0 | 0
August | 847047000000 | 625902.403 | 25-AUG-19:10 | 115409.096 | 136430.368 | 32530.531 | 0 | 329631.916 | 3589.95 | 5909.675 | 0 | 0 | 0 | 0 | 0 | 2400.867 | 0 | 0
September | 618527000000 | 473909.818 | 22-SEP-19:10 | 115409.096 | 136430.368 | 28729.873 | 0 | 183660.531 | 3589.95 | 3694.3 | 0 | 0 | 0 | 0 | 0 | 2395.7 | 0 | 0
October | 491497000000 | 424132.108 | 08-OCT-19:10 | 108704.859 | 134943.936 | 28821.613 | 0 | 142252.475 | 3589.95 | 2936.287 | 0 | 0 | 0 | 0 | 0 | 2882.989 | 0 | 0
November | 426882000000 | 312448.127 | 02-NOV-20:19 | 115409.096 | 136430.368 | 28031.501 | 0 | 24635.154 | 3589.95 | 1462.594 | 0 | 0 | 0 | 0 | 0 | 2889.464 | 0 | 0
December | 433264000000 | 287545.655 | 20-DEC-20:19 | 115409.096 | 136430.368 | 24969.9 | 0 | 0 | 3589.95 | 4293.106 | 0 | 0 | 0 | 0 | 0 | 2853.235 | 0 | 0
Annual Sum or Average | 6840020000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 391352000000 | 287545.655 |  | 87035.741 | 127075.755 | 24969.9 | 0 | 0 | 0 | 1462.594 | 0 | 0 | 0 | 0 | 0 | 2291.069 | 0 | 0
Maximum of Months | 867426000000 | 656969.297 |  | 115409.096 | 136430.368 | 33683.338 | 0 | 386368.655 | 3589.95 | 6168.334 | 0 | 0 | 0 | 0 | 0 | 2925.31 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 110697.56 | 120311.02 | 0 | 231008.58
Cost per Total Building Area ($/m2) | 9.76 | 10.6 | 0 | 20.36
Cost per Net Conditioned Building Area ($/m2) | 9.76 | 10.6 | 0 | 20.36

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20342.19 | 1793.01 | 1793.01
Net Site Energy | 20342.19 | 1793.01 | 1793.01
Total Source Energy | 37397.13 | 3296.27 | 3296.27
Net Source Energy | 37397.13 | 3296.27 | 3296.27
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4249.79 | 0 | 0 | 0 | 0
Cooling | 1182.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 881.55 | 0 | 0 | 0 | 0 | 0
Pumps | 60.56 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 7934.64 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6368.9 | 13973.29 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.402 | 0.495 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.402 | 0.495 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.501 | 0.622 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.402 | 0.495 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.622 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.402 | 0.495 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.402 | 0.495 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.402 | 0.495 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.622 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.501 | 0.622 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.437 | 0.54
North Total or Average |  |  | 432.93 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1677984.41 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1568301.77 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15381.36 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 14361.65 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 183542.4 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 135228.37 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 12915.97 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 11275.88 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4734.87 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4481.22 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 32576 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 906521.77 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 356868.43 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5290.07 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.4 | 888.46 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.3 | 828.58 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 11.67 | 7425.36 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 9.46 | 6021.52 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.17 | 744.27 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.02 | 650.78 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.43 | 276.29 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.41 | 262.92 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 2.17 | 1379.71 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 39.77 | 89412.35 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8714.24 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15376.4 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 205131.061 | 276.3734 | 327.0506 | 0 | 0.0025 | 7746380 | 79712.8047
February | 177640.7593 | 243.2187 | 297.2645 | 0 | 0.0022 | 7041960 | 69405.5757
March | 183028.756 | 262.5616 | 349.5551 | 0 | 0.0026 | 8283840 | 72667.366
April | 166239.5198 | 244.9138 | 340.7698 | 0 | 0.0025 | 8077140 | 66623.8081
May | 175798.2333 | 269.7182 | 399.1399 | 0 | 0.0029 | 9462970 | 71491.0781
June | 191520.5443 | 304.3542 | 472.8607 | 0 | 0.0034 | 11212800 | 78901.1318
July | 217089.8374 | 351.966 | 561.2283 | 0 | 0.004 | 13309500 | 90109.5292
August | 204232.6791 | 329.7846 | 523.1572 | 0 | 0.0037 | 12406400 | 84643.6268
September | 177902.9558 | 281.7949 | 435.9158 | 0 | 0.0031 | 10336600 | 73202.2371
October | 167993.2115 | 254.9454 | 371.3004 | 0 | 0.0027 | 8802400 | 68046.5878
November | 168101.1108 | 241.4996 | 322.3197 | 0 | 0.0024 | 7638490 | 66774.7386
December | 197027.2312 | 269.013 | 326.9973 | 0 | 0.0025 | 7746110 | 76907.6188
Annual Sum or Average | 2231710 | 3330.1432 | 4727.5594 | 0 | 0.0343 | 112065000 | 898486.1025
Minimum of Months | 166239.5198 | 241.4996 | 297.2645 | 0 | 0.0022 | 7041960 | 66623.8081
Maximum of Months | 217089.8374 | 351.966 | 561.2283 | 0 | 0.004 | 13309500 | 90109.5292
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 440245000000 | 291556.775 | 30-JAN-20:00 | 115409.096 | 136430.368 | 29341.818 | 0 | 2645.912 | 3589.95 | 1274.103 | 0 | 0 | 0 | 0 | 0 | 2865.528 | 0 | 0
February | 400211000000 | 309665.56 | 03-FEB-20:10 | 115409.096 | 136430.368 | 30320.586 | 0 | 20333.628 | 3589.95 | 1241.968 | 0 | 0 | 0 | 0 | 0 | 2339.963 | 0 | 0
March | 470791000000 | 388946.599 | 30-MAR-17:19 | 77122.967 | 134092.705 | 30919.868 | 0 | 141748.474 | 0 | 2828.466 | 0 | 0 | 0 | 0 | 0 | 2234.119 | 0 | 0
April | 459043000000 | 383438.335 | 06-APR-19:10 | 115409.096 | 136430.368 | 31675.241 | 0 | 91388.173 | 3589.95 | 2079.48 | 0 | 0 | 0 | 0 | 0 | 2866.027 | 0 | 0
May | 537803000000 | 439790.345 | 25-MAY-19:10 | 115409.096 | 136430.368 | 33440.28 | 0 | 148450.493 | 0 | 3165.197 | 0 | 0 | 0 | 0 | 0 | 2894.91 | 0 | 0
June | 637252000000 | 575687.378 | 26-JUN-18:10 | 102647.053 | 127075.755 | 71245.08 | 0 | 258974.566 | 0 | 12846.179 | 0 | 0 | 0 | 0 | 0 | 2898.745 | 0 | 0
July | 756411000000 | 614353.462 | 21-JUL-19:19 | 115409.096 | 136430.368 | 93043.45 | 0 | 255035.907 | 0 | 12060.449 | 0 | 0 | 0 | 0 | 0 | 2374.193 | 0 | 0
August | 705087000000 | 519865.92 | 09-AUG-17:19 | 77122.967 | 134092.705 | 33901.544 | 0 | 266250.714 | 0 | 6238.979 | 0 | 0 | 0 | 0 | 0 | 2259.01 | 0 | 0
September | 587453000000 | 488499.435 | 01-SEP-17:19 | 77122.967 | 134092.705 | 33022.507 | 0 | 236600.351 | 0 | 5403.609 | 0 | 0 | 0 | 0 | 0 | 2257.295 | 0 | 0
October | 500261000000 | 408257.969 | 05-OCT-18:10 | 102647.053 | 127075.755 | 31564.64 | 0 | 137775.399 | 3589.95 | 2722.546 | 0 | 0 | 0 | 0 | 0 | 2882.627 | 0 | 0
November | 434114000000 | 312405.953 | 21-NOV-20:10 | 115409.096 | 136430.368 | 30451.343 | 0 | 22893.693 | 3589.95 | 1290.728 | 0 | 0 | 0 | 0 | 0 | 2340.774 | 0 | 0
December | 440230000000 | 292424.157 | 01-DEC-20:10 | 115409.096 | 136430.368 | 29391.229 | 0 | 4064.83 | 3589.95 | 1198.129 | 0 | 0 | 0 | 0 | 0 | 2340.554 | 0 | 0
Annual Sum or Average | 6368900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 400211000000 | 291556.775 |  | 77122.967 | 127075.755 | 29341.818 | 0 | 2645.912 | 0 | 1198.129 | 0 | 0 | 0 | 0 | 0 | 2234.119 | 0 | 0
Maximum of Months | 756411000000 | 614353.462 |  | 115409.096 | 136430.368 | 93043.45 | 0 | 266250.714 | 3589.95 | 12846.179 | 0 | 0 | 0 | 0 | 0 | 2898.745 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 131169.76 | 120524.2 | 0 | 251693.97
Cost per Total Building Area ($/m2) | 11.56 | 10.62 | 0 | 22.18
Cost per Net Conditioned Building Area ($/m2) | 11.56 | 10.62 | 0 | 22.18

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 23467.13 | 2068.45 | 2068.45
Net Site Energy | 23467.13 | 2068.45 | 2068.45
Total Source Energy | 39907.44 | 3517.53 | 3517.53
Net Source Energy | 39907.44 | 3517.53 | 3517.53
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6810.54 | 0 | 0 | 0 | 0
Cooling | 955.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 56.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 829.24 | 0 | 0 | 0 | 0 | 0
Pumps | 61.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 8777.61 | 0 | 0 | 0 | 44342.19
Refrigeration | 74.37 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6090.12 | 17377 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.357 | 0.38 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.357 | 0.38 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 3.18 | 0.501 | 0.49 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 3.18 | 0.501 | 0.49 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 3.18 | 0.501 | 0.49 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.49 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.501 | 0.49 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.651 | 0.64 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 3.18 | 0.501 | 0.49 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 3.18 | 0.501 | 0.49 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 3.18 | 0.651 | 0.64 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.501 | 0.49 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 3.18 | 0.501 | 0.49 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 3.18 | 0.651 | 0.64 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 3.18 | 0.501 | 0.49 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 3.18 | 0.651 | 0.64 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 3.18 | 0.651 | 0.64 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.49 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.501 | 0.49 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.651 | 0.64 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 3.18 | 0.501 | 0.49 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 3.18 | 0.501 | 0.49 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.651 | 0.64 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 3.18 | 0.651 | 0.64 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 3.18 | 0.651 | 0.64 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 3.18 | 0.501 | 0.49 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 3.18 | 0.501 | 0.49 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 3.18 | 0.651 | 0.64 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 3.18 | 0.651 | 0.64 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 3.18 | 0.555 | 0.543
North Total or Average |  |  | 432.93 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 781.15 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1513433.49 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1666347.83 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 18163.47 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17118.78 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 156705.31 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 121754.71 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15320.48 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13789.03 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5511.2 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5263.75 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 28260.19 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 709994.09 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 415431.68 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 6120.8 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.42 | 904.21 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.33 | 847.87 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 11.2 | 7125.86 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 8.7 | 5536.49 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.18 | 753.07 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.05 | 671.31 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.44 | 276.89 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.42 | 264.17 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 2.08 | 1326.26 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 36.51 | 82511.75 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9259.03 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13868.52 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 224209.6604 | 291.4667 | 287.4144 | 0 | 0.0024 | 188496.5576 | 86006.2336
February | 195629.5429 | 256.9533 | 259.3739 | 0 | 0.0021 | 170129.3089 | 75295.3271
March | 195799.967 | 265.9728 | 288.2397 | 0 | 0.0023 | 189136.2368 | 76201.6624
April | 166886.3855 | 239.273 | 286.6258 | 0 | 0.0022 | 188171.4344 | 66151.1574
May | 168256.8079 | 254.8227 | 333.214 | 0 | 0.0025 | 218844.0894 | 67992.9033
June | 177301.7096 | 282.0712 | 395.2475 | 0 | 0.003 | 259661.1914 | 72943.1699
July | 207101.897 | 338.2711 | 490.3025 | 0 | 0.0037 | 322151.8698 | 86043.4323
August | 190556.022 | 308.3898 | 441.8313 | 0 | 0.0033 | 290290.6546 | 78896.2112
September | 159389.9294 | 249.3309 | 341.4981 | 0 | 0.0026 | 224329.0547 | 65168.448
October | 162103.1985 | 241.2982 | 307.3352 | 0 | 0.0024 | 201824.3533 | 65104.2746
November | 178097.5701 | 247.2297 | 279.4494 | 0 | 0.0022 | 183407.9617 | 69819.1827
December | 214964.2124 | 282.9021 | 286.81 | 0 | 0.0023 | 188129.9282 | 82789.8786
Annual Sum or Average | 2240300 | 3257.9815 | 3997.3417 | 0 | 0.031 | 2624570 | 892411.881
Minimum of Months | 159389.9294 | 239.273 | 259.3739 | 0 | 0.0021 | 170129.3089 | 65104.2746
Maximum of Months | 224209.6604 | 338.2711 | 490.3025 | 0 | 0.0037 | 322151.8698 | 86043.4323
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 437392000000 | 289407.512 | 25-JAN-20:40 | 115409.096 | 136430.368 | 26660.739 | 0 | 0 | 3589.95 | 4453.167 | 0 | 0 | 0 | 0 | 0 | 2864.191 | 0 | 0
February | 394772000000 | 292064.872 | 28-FEB-20:10 | 115409.096 | 136430.368 | 27976.226 | 0 | 5104.002 | 3589.95 | 1214.616 | 0 | 0 | 0 | 0 | 0 | 2340.613 | 0 | 0
March | 438876000000 | 299615.17 | 22-MAR-19:10 | 115409.096 | 136430.368 | 28544.739 | 0 | 11481.646 | 3589.95 | 1293.353 | 0 | 0 | 0 | 0 | 0 | 2866.018 | 0 | 0
April | 436638000000 | 333254.746 | 04-APR-18:10 | 102647.053 | 127075.755 | 29274.52 | 0 | 70153.906 | 0 | 1795.652 | 0 | 0 | 0 | 0 | 0 | 2307.862 | 0 | 0
May | 507811000000 | 423541.905 | 31-MAY-19:10 | 115409.096 | 136430.368 | 31957.147 | 0 | 134395.527 | 0 | 2462.742 | 0 | 0 | 0 | 0 | 0 | 2887.025 | 0 | 0
June | 602524000000 | 519843.436 | 14-JUN-19:10 | 115409.096 | 136430.368 | 33207.785 | 0 | 227312.513 | 0 | 4557.445 | 0 | 0 | 0 | 0 | 0 | 2926.229 | 0 | 0
July | 747529000000 | 583552.403 | 06-JUL-18:10 | 102647.053 | 127075.755 | 35135.125 | 0 | 310106.381 | 0 | 5663.825 | 0 | 0 | 0 | 0 | 0 | 2924.265 | 0 | 0
August | 673598000000 | 548983.598 | 13-AUG-19:10 | 108704.859 | 134943.936 | 32766.56 | 0 | 264601.12 | 0 | 5079.318 | 0 | 0 | 0 | 0 | 0 | 2887.805 | 0 | 0
September | 520539000000 | 471242.029 | 08-SEP-19:10 | 115409.096 | 136430.368 | 30724.614 | 0 | 178835.585 | 3589.95 | 3855.401 | 0 | 0 | 0 | 0 | 0 | 2397.014 | 0 | 0
October | 468318000000 | 394899.096 | 07-OCT-17:10 | 87035.741 | 134092.705 | 29553.628 | 0 | 138586.812 | 0 | 3357.892 | 0 | 0 | 0 | 0 | 0 | 2272.319 | 0 | 0
November | 425584000000 | 301582.625 | 02-NOV-20:00 | 115409.096 | 136430.368 | 28736.779 | 0 | 13361.259 | 3589.95 | 1183.305 | 0 | 0 | 0 | 0 | 0 | 2871.869 | 0 | 0
December | 436541000000 | 289351.929 | 18-DEC-20:10 | 115409.096 | 136430.368 | 26808.688 | 0 | 0 | 3589.95 | 4249.456 | 0 | 0 | 0 | 0 | 0 | 2864.371 | 0 | 0
Annual Sum or Average | 6090120000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 394772000000 | 289351.929 |  | 87035.741 | 127075.755 | 26660.739 | 0 | 0 | 0 | 1183.305 | 0 | 0 | 0 | 0 | 0 | 2272.319 | 0 | 0
Maximum of Months | 747529000000 | 583552.403 |  | 115409.096 | 136430.368 | 35135.125 | 0 | 310106.381 | 3589.95 | 5663.825 | 0 | 0 | 0 | 0 | 0 | 2926.229 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 98521.71 | 138234.21 | 0 | 236755.92
Cost per Total Building Area ($/m2) | 8.68 | 12.18 | 0 | 20.87
Cost per Net Conditioned Building Area ($/m2) | 8.68 | 12.18 | 0 | 20.87

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 29075.05 | 2562.74 | 2562.74
Net Site Energy | 29075.05 | 2562.74 | 2562.74
Total Source Energy | 46310.14 | 4081.88 | 4081.88
Net Source Energy | 46310.14 | 4081.88 | 4081.88
Area [m2]
Total Building Area | 11345.29
Net Conditioned Building Area | 11345.29
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11490.85 | 0 | 0 | 0 | 0
Cooling | 689.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1453.36 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 55.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2660.43 | 1788.85 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 866.84 | 0 | 0 | 0 | 0 | 0
Pumps | 71.33 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 9924.3 | 0 | 0 | 0 | 44342.19
Refrigeration | 73.97 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5871.04 | 23204.01 | 0 | 0 | 0 | 44342.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 1978.83 | Yes | 4826.41 | 1 | 0 | 0 | 10.76 | 37.17 | 5.38
RETAIL_1_FLR_1 | 67.07 | Yes | 265.76 | 1 | 68.84 | 23.3 | 16.14 | 6.19 | 10.76
RETAIL_2_FLR_1 | 77.67 | Yes | 307.76 | 1 | 26.57 | 0 | 16.14 | 6.19 | 10.76
MECH_FLR_1 | 164.24 | Yes | 650.8 | 1 | 62.8 | 0 | 16.14 |  | 5.38
STORAGE_FLR_1 | 94.76 | Yes | 375.47 | 1 | 36.23 | 0 | 9.68 | 46.51 | 2.69
LAUNDRY_FLR_1 | 78.04 | Yes | 309.22 | 1 | 85.75 | 0 | 6.46 | 23.2 | 597.53
CAFE_FLR_1 | 188.86 | Yes | 748.35 | 1 | 152.17 | 65.62 | 13.99 | 1.39 | 5.38
LOBBY_FLR_1 | 1308.19 | Yes | 5183.56 | 1 | 434.79 | 85.24 | 11.84 | 3.1 | 8.07
ROOM_1_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_3_MULT19_FLR_3 | 24.52 | Yes | 74.75 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_4_MULT19_FLR_3 | 24.53 | Yes | 74.77 | 76 | 11.15 | 3.68 | 11.84 | 16.35 | 10.52
ROOM_5_FLR_3 | 39.02 | Yes | 118.94 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
ROOM_6_FLR_3 | 39.02 | Yes | 118.93 | 4 | 39.95 | 13.18 | 11.84 | 26.01 | 6.75
CORRIDOR_FLR_3 | 389.4 | Yes | 1186.91 | 4 | 48.31 | 15.94 | 5.38 | 92.59 | 0
ROOM_1_FLR_6 | 39.02 | Yes | 118.94 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_2_FLR_6 | 39.02 | Yes | 118.93 | 1 | 39.95 | 13.19 | 11.84 | 26.01 | 6.75
ROOM_3_MULT9_FLR_6 | 24.53 | Yes | 74.77 | 9 | 20.44 | 6.75 | 11.84 | 16.35 | 10.52
BANQUET_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
DINING_FLR_6 | 331.66 | Yes | 1010.89 | 1 | 97.55 | 32.21 | 13.99 | 1.39 | 67.82
KITCHEN_FLR_6 | 103.3 | Yes | 314.87 | 1 | 87.33 | 26.38 | 12.91 | 18.59 | 2942.57
CORRIDOR_FLR_6 | 412.12 | Yes | 1256.16 | 1 | 85.47 | 28.22 | 5.38 | 92.59 | 292.0721
Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Conditioned Total | 11345.29 |  | 35184.81 |  | 4025.82 | 1214.08 | 10.7634 | 8.04 | 51.7542
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 2.254 | 3.4 | 211.13 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 2.254 | 3.4 | 55.76 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 1978.83 | 0 | 180
RETAIL_1_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.89 | 180 | 90 | S
RETAIL_1_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 22.95 | 270 | 90 | W
RETAIL_1_FLR_1_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 67.07 | 180 | 0
RETAIL_2_FLR_1_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.57 | 270 | 90 | W
MECH_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 62.8 | 0 | 90 | N
STORAGE_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 36.23 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 18.12 | 0 | 90 | N
LAUNDRY_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 67.63 | 90 | 90 | E
CAFE_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 22.95 | 90 | 90 | E
CAFE_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 129.23 | 180 | 90 | S
CAFE_FLR_1_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 188.86 | 180 | 0
LOBBY_FLR_1_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 213.77 | 0 | 90 | N
LOBBY_FLR_1_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 12.08 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 167.88 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 41.06 | 270 | 90 | W
LOBBY_FLR_1_CEILING_2 | ROOFS | 0.3 | 0.273 | 0.29 | 245.35 | 180 | 0
ROOM_1_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 55.74 | 180 | 90 | S
ROOM_1_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 104.06 | 270 | 90 | W
ROOM_2_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 55.74 | 0 | 90 | N
ROOM_2_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 104.05 | 270 | 90 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 847.14 | 180 | 90 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 847.37 | 0 | 90 | N
ROOM_5_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 104.06 | 90 | 90 | E
ROOM_5_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 55.74 | 180 | 90 | S
ROOM_6_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 55.74 | 0 | 90 | N
ROOM_6_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 104.05 | 90 | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 70.6 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.01 | 0 | 90 | N
CORRIDOR_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_3_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 70.6 | 180 | 90 | S
ROOM_1_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 13.94 | 180 | 90 | S
ROOM_1_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.01 | 270 | 90 | W
ROOM_1_FLR_6_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 39.02 | 180 | 0
ROOM_2_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 13.94 | 0 | 90 | N
ROOM_2_FLR_6_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.01 | 270 | 90 | W
ROOM_2_FLR_6_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 39.02 | 180 | 0
ROOM_3_MULT9_FLR_6_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 183.96 | 180 | 90 | S
ROOM_3_MULT9_FLR_6_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 220.77 | 180 | 0
BANQUET_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 97.55 | 0 | 90 | N
BANQUET_FLR_6_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 331.66 | 180 | 0
DINING_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 97.55 | 0 | 90 | N
DINING_FLR_6_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 331.66 | 180 | 0
KITCHEN_FLR_6_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 21.37 | 0 | 90 | N
KITCHEN_FLR_6_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 52.03 | 90 | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 13.94 | 180 | 90 | S
KITCHEN_FLR_6_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 103.3 | 270 | 0
CORRIDOR_FLR_6_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 17.65 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 15.79 | 0 | 90 | N
CORRIDOR_FLR_6_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 52.03 | 180 | 90 | S
CORRIDOR_FLR_6_CEILING_1 | ROOFS | 0.3 | 0.273 | 0.29 | 244.71 | 90 | 0
CORRIDOR_FLR_6_CEILING_2 | ROOFS | 0.3 | 0.273 | 0.29 | 167.42 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
RETAIL_1_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 23.3 | 23.3 | 2.58 | 0.504 | 0.49 | No | RETAIL_1_FLR_1_WALL_SOUTH | 180 | S
CAFE_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 65.62 | 65.62 | 2.58 | 0.504 | 0.49 | No | CAFE_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 85.24 | 85.24 | 2.58 | 0.504 | 0.49 | No | LOBBY_FLR_1_WALL_1_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 2.58 | 0.504 | 0.49 | No | ROOM_1_FLR_3_WALL_SOUTH | 180 | S
ROOM_1_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 2.58 | 0.504 | 0.49 | No | ROOM_1_FLR_3_WALL_WEST | 270 | W
ROOM_2_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 2.58 | 0.654 | 0.64 | No | ROOM_2_FLR_3_WALL_NORTH | 0 | N
ROOM_2_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 8.58 | 34.33 | 2.58 | 0.504 | 0.49 | No | ROOM_2_FLR_3_WALL_WEST | 270 | W
ROOM_3_MULT19_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 3.68 | 279.51 | 2.58 | 0.504 | 0.49 | No | ROOM_3_MULT19_FLR_3_WALL_SOUTH | 180 | S
ROOM_4_MULT19_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 3.68 | 279.6 | 2.58 | 0.654 | 0.64 | No | ROOM_4_MULT19_FLR_3_WALL_NORTH | 0 | N
ROOM_5_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 2.58 | 0.504 | 0.49 | No | ROOM_5_FLR_3_WALL_EAST | 90 | E
ROOM_5_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 18.39 | 2.58 | 0.504 | 0.49 | No | ROOM_5_FLR_3_WALL_SOUTH | 180 | S
ROOM_6_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 18.39 | 2.58 | 0.654 | 0.64 | No | ROOM_6_FLR_3_WALL_NORTH | 0 | N
ROOM_6_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 8.58 | 34.33 | 2.58 | 0.504 | 0.49 | No | ROOM_6_FLR_3_WALL_EAST | 90 | E
CORRIDOR_FLR_3_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.82 | 23.29 | 2.58 | 0.654 | 0.64 | No | CORRIDOR_FLR_3_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 2.15 | 8.59 | 2.58 | 0.654 | 0.64 | No | CORRIDOR_FLR_3_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_3_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 2.15 | 8.58 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_FLR_3_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_3_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 5.82 | 23.29 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_FLR_3_WALL_2_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 2.58 | 0.504 | 0.49 | No | ROOM_1_FLR_6_WALL_SOUTH | 180 | S
ROOM_1_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 2.58 | 0.504 | 0.49 | No | ROOM_1_FLR_6_WALL_WEST | 270 | W
ROOM_2_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 2.58 | 0.654 | 0.64 | No | ROOM_2_FLR_6_WALL_NORTH | 0 | N
ROOM_2_FLR_6_WALL_WEST_WINDOW | WINDOW_WEST | 8.59 | 8.59 | 2.58 | 0.504 | 0.49 | No | ROOM_2_FLR_6_WALL_WEST | 270 | W
ROOM_3_MULT9_FLR_6_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.75 | 60.74 | 2.58 | 0.504 | 0.49 | No | ROOM_3_MULT9_FLR_6_WALL_SOUTH | 180 | S
BANQUET_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 2.58 | 0.654 | 0.64 | No | BANQUET_FLR_6_WALL_NORTH | 0 | N
DINING_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 32.21 | 32.21 | 2.58 | 0.654 | 0.64 | No | DINING_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.6 | 4.6 | 2.58 | 0.654 | 0.64 | No | KITCHEN_FLR_6_WALL_NORTH | 0 | N
KITCHEN_FLR_6_WALL_EAST_WINDOW | WINDOW_EAST | 17.18 | 17.18 | 2.58 | 0.504 | 0.49 | No | KITCHEN_FLR_6_WALL_EAST | 90 | E
KITCHEN_FLR_6_WALL_1_SOUTH_WINDOW | WINDOW_SOUTH | 4.6 | 4.6 | 2.58 | 0.504 | 0.49 | No | KITCHEN_FLR_6_WALL_1_SOUTH | 180 | S
CORRIDOR_FLR_6_WALL_1_NORTH_WINDOW | WINDOW_NORTH | 5.83 | 5.83 | 2.58 | 0.654 | 0.64 | No | CORRIDOR_FLR_6_WALL_1_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_NORTH_WINDOW | WINDOW_NORTH | 5.21 | 5.21 | 2.58 | 0.654 | 0.64 | No | CORRIDOR_FLR_6_WALL_2_NORTH | 0 | N
CORRIDOR_FLR_6_WALL_2_SOUTH_WINDOW | WINDOW_SOUTH | 17.18 | 17.18 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_FLR_6_WALL_2_SOUTH | 180 | S
Total or Average |  |  | 1214.08 | 2.58 | 0.557 | 0.543
North Total or Average |  |  | 432.93 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 781.15 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1290068.78 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 1961245.29 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
ROOM_1_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 17743.7 | - | - | - | -
ROOM_2_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15351.9 | - | - | - | -
ROOM_3_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 160537.32 | - | - | - | -
ROOM_4_MULT19_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 106176.78 | - | - | - | -
ROOM_5_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 15630.3 | - | - | - | -
ROOM_6_FLR_3 FAN COILCOOL COIL | Coil:Cooling:Water | 13201.76 | - | - | - | -
ROOM_1_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 5186.1 | - | - | - | -
ROOM_2_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 4665.28 | - | - | - | -
ROOM_3_MULT9_FLR_6 FAN COILCOOL COIL | Coil:Cooling:Water | 29736.12 | - | - | - | -
VAV WITH REHEAT_COOLC | Coil:Cooling:Water | 508323.32 | - | - | - | -
FLR_3_DOAS_COOLC | Coil:Cooling:Water | 407715.79 | - | - | - | -
FLR_6_DOAS_COOLC | Coil:Cooling:Water | 5800.39 | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RETAIL_2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
STORAGE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAUNDRY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CAFE_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_4_MULT19_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_5_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_6_FLR_3 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_1_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_2_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
ROOM_3_MULT9_FLR_6 FAN COILHEAT COIL | Coil:Heating:Water | -99999 | -
BANQUET_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_6 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV WITH REHEAT_HEATC | Coil:Heating:Water | -99999 | -
FLR_3_DOAS_HEATC | Coil:Heating:Water | -99999 | -
FLR_6_DOAS_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
LAUNDRY_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.24 | 29.46 | 1 | Zone Exhaust Fans
ROOM_1_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.44 | 916.81 | 1 | General
ROOM_2_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.25 | 793.76 | 1 | General
ROOM_3_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 12.8 | 8147.91 | 1 | General
ROOM_4_MULT19_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 9.01 | 5735.17 | 1 | General
ROOM_5_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.27 | 806.35 | 1 | General
ROOM_6_FLR_3 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 1.07 | 681.7 | 1 | General
ROOM_1_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.42 | 269.39 | 1 | General
ROOM_2_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 0.38 | 243.42 | 1 | General
ROOM_3_MULT9_FLR_6 FAN COILFAN | Fan:ConstantVolume | 0.52 | 330.9 | 2.41 | 1531.98 | 1 | General
DINING_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.38 | 297.5 | 1 | Zone Exhaust Fans
KITCHEN_FLR_6 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV WITH REHEAT_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 35.82 | 80966.46 | 1 | Fan Energy
FLR_3_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100.4 | 1 | Fan Energy
FLR_6_DOAS_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 50.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1080.82 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10897.63 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11821.69 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 259426.5869 | 265.686 | 632.3262 | 0 | 0.0025 | 126734.867 | 94433.3496
February | 226183.9764 | 232.3951 | 567.07 | 0 | 0.0022 | 113662.4762 | 82448.7657
March | 213301.9444 | 223.4352 | 624.23 | 0 | 0.0024 | 125156.3948 | 78411.0021
April | 175024.5954 | 188.8843 | 628.2161 | 0 | 0.0023 | 125996.5467 | 65193.3144
May | 165239.1428 | 185.5226 | 743.6958 | 0 | 0.0026 | 149200.7796 | 62656.1872
June | 171607.692 | 196.7229 | 857.0884 | 0 | 0.003 | 171969.1514 | 65694.2786
July | 179710.7966 | 207.4674 | 928.0093 | 0 | 0.0032 | 186205.2591 | 69020.2603
August | 164418.0459 | 187.9904 | 810.9163 | 0 | 0.0029 | 162702.8852 | 62866.4669
September | 151927.9372 | 169.2377 | 655.7578 | 0 | 0.0023 | 131552.1653 | 57402.618
October | 181499.0158 | 194.7365 | 627.7105 | 0 | 0.0023 | 125888.3064 | 67430.2599
November | 221585.0668 | 229.9987 | 604.2603 | 0 | 0.0023 | 121136.9124 | 81130.7328
December | 248554.291 | 255.6397 | 628.5944 | 0 | 0.0025 | 125996.5637 | 90643.2208
Annual Sum or Average | 2358480 | 2537.7165 | 8307.875 | 0 | 0.0306 | 1666200 | 877330.4563
Minimum of Months | 151927.9372 | 169.2377 | 567.07 | 0 | 0.0022 | 113662.4762 | 57402.618
Maximum of Months | 259426.5869 | 265.686 | 928.0093 | 0 | 0.0032 | 186205.2591 | 94433.3496
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 446564000000 | 292100.996 | 12-JAN-20:10 | 115409.096 | 136430.368 | 26543.743 | 0 | 0 | 3589.95 | 7404.208 | 0 | 0 | 0 | 0 | 0 | 2723.631 | 0 | 0
February | 400502000000 | 291482.447 | 09-FEB-20:00 | 115409.096 | 136430.368 | 27568.403 | 0 | 0 | 3589.95 | 5629.352 | 0 | 0 | 0 | 0 | 0 | 2855.278 | 0 | 0
March | 441002000000 | 303184.217 | 29-MAR-19:30 | 115409.096 | 136430.368 | 29803.643 | 0 | 13790.289 | 3589.95 | 1294.558 | 0 | 0 | 0 | 0 | 0 | 2866.313 | 0 | 0
April | 443962000000 | 335183.129 | 25-APR-19:10 | 115409.096 | 136430.368 | 31144.493 | 0 | 48414.75 | 0 | 1444.085 | 0 | 0 | 0 | 0 | 0 | 2340.338 | 0 | 0
May | 525725000000 | 414205.434 | 24-MAY-19:10 | 115409.096 | 136430.368 | 33023.592 | 0 | 124073.288 | 0 | 2400.326 | 0 | 0 | 0 | 0 | 0 | 2868.763 | 0 | 0
June | 605952000000 | 475488.717 | 15-JUN-19:00 | 115409.096 | 136430.368 | 35886.455 | 0 | 181714.612 | 0 | 3167.963 | 0 | 0 | 0 | 0 | 0 | 2880.222 | 0 | 0
July | 656114000000 | 480790.795 | 29-JUL-17:19 | 87035.741 | 134092.705 | 32998.899 | 0 | 220306.967 | 0 | 4069.523 | 0 | 0 | 0 | 0 | 0 | 2286.961 | 0 | 0
August | 573301000000 | 446512.408 | 15-AUG-19:10 | 115409.096 | 136430.368 | 33186.027 | 0 | 155422.16 | 0 | 3677.24 | 0 | 0 | 0 | 0 | 0 | 2387.517 | 0 | 0
September | 463538000000 | 356580.738 | 02-SEP-18:10 | 102000.622 | 124102.889 | 30415.615 | 0 | 95145.09 | 0 | 2064.534 | 0 | 0 | 0 | 0 | 0 | 2851.987 | 0 | 0
October | 443581000000 | 305634.987 | 03-OCT-19:10 | 115409.096 | 136430.368 | 29929.524 | 0 | 16700.835 | 3589.95 | 1231.936 | 0 | 0 | 0 | 0 | 0 | 2343.278 | 0 | 0
November | 426839000000 | 291346.997 | 22-NOV-20:10 | 115409.096 | 136430.368 | 27429.337 | 0 | 0 | 3589.95 | 5624.511 | 0 | 0 | 0 | 0 | 0 | 2863.735 | 0 | 0
December | 443963000000 | 291171.39 | 07-DEC-20:00 | 115409.096 | 136430.368 | 27780.05 | 0 | 0 | 3589.95 | 5097.919 | 0 | 0 | 0 | 0 | 0 | 2864.008 | 0 | 0
Annual Sum or Average | 5871040000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 400502000000 | 291171.39 |  | 87035.741 | 124102.889 | 26543.743 | 0 | 0 | 0 | 1231.936 | 0 | 0 | 0 | 0 | 0 | 2286.961 | 0 | 0
Maximum of Months | 656114000000 | 480790.795 |  | 115409.096 | 136430.368 | 35886.455 | 0 | 220306.967 | 3589.95 | 7404.208 | 0 | 0 | 0 | 0 | 0 | 2880.222 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 152674.5 | 96835.44 | 0 | 249509.94
Cost per Total Building Area ($/m2) | 13.46 | 8.54 | 0 | 21.99
Cost per Net Conditioned Building Area ($/m2) | 13.46 | 8.54 | 0 | 21.99

## Picture
DOE Commercial Building Benchmark - Large Hotel

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.19 | 49.33 | 2572.21
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.38
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | 15.19 | 90.86 | 4737.7
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | 14.91
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Laundry_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Laundry_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Laundry_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_5_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_1_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_2_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720